## Sheet1
Utility Name | Notified of Incident | County Name | Incident City | Incident Date | Cause of Incident | Facility Damage | Material Damaged | Damaged Caused By | Pipe Diameter | MAOP of Operator | Operating Pressure | Gas Leak | Operator Caused Fire | Non-Operator Caused Fire | Natural Gas Explosion | Injured Employees | Non-Employees Injured | Non-Employees Injured NA | Employee Fatalities | Non-Employee Fatalities | Non-Employee Fatalities NA | Cost Damage | Cost Damage NA | Customers Effected | Customers Effected NA | Damage Party Name | Damage Party City | Damage Party State | Damage Party Work Operator | Damage Done To SUOF | Underground Service Alert | Valid USA Ticket | Property Mark Facility | Properly Timely Mark Facility | Standby Provided | Delineations Found | Struck Within Delineations | Summary
Alpine Gas | N | CALAVERAS | VALLEY SPRINGS | 2021-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 60 | 38 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 125 |  | 1 |  | TOM BUCK | VALLEY SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner while trenching struck gas line. Homeowner called USA, prior to excavation but did not hand dig to expose facilities prior to excavation.
Alpine Gas | N | CALAVERAS | VALLEY SPRINGS | 2021-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 39 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 125 |  | 1 |  | ROBERT OLMO | VALLEY SPRINGS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner while hand digging in proximity to the gas meter nicked gas line. Homeowner had not called USA, prior to excavation. Gas not blowing but a leak was detected.
Alpine Gas | N | CALAVERAS | VALLEY SPRINGS | 2021-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 60 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 125 |  | 2 |  | JEFF ANDREASSON | VALLEY SPRINGS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Yes | Yes | Operator & Homeowner severed marked gas line with back hoe. Unsafe practices appears to be cause of struck gas line. Homeowner or Contractator called USA, did not hand dig to expose facilities prior to excavation.
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2021-04-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 12 | 9 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8965 |  | 0 |  | NA | NA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2021-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3395 |  | 1 |  | PK REMODELING | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2021-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 461 |  | 1 |  | HOMEOWNER | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2021-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1555 |  | 1 |  | HOMEOWNER | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2021-02-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2697 |  | 3 |  | DPI INC. | LIVERMORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2021-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 15 | 12 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | RANGER PIPELINES | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2021-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 12 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1650 |  | 2 |  | RANGER PIPELINES | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 0.43 | 0.34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 113 |  | 1 |  | RANGER PIPELINE | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2021-07-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 45 |  | 0 |  | JANCO INDUSTRIES INC. | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2021-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1675 |  | 1 |  | DPI INC | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2021-08-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TENNYSON ELECTRIC | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2021-01-21 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MILLER PIPELINE | ALAMEDA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2021-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2021-04-08 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 15 | 12 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RANGER PIPELINE | SAN FRANCISCO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-02-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 165 |  | 4 |  | REUBEN BORG FENCE | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1739 |  | 1 |  | HOMEOWNER | BERKELEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator Error
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | CASTRO VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2076 |  | 2 |  | CAMERON C HABEL CONST. INC. | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1921 |  | 1 |  | RATCLIFF CONSTRUCTION | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-05-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 3 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 122322 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5514 |  | 0 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-10-05 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7491 |  | 2 |  | HOMEOWNER | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 3 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 91510 |  | 2159 |  | MARCOS PLUMBING | DALY CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4453 |  | 2 |  | RANGER PIPELINES | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 370 |  | 1 |  | KATO PLUMBING | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2653 |  | 1 |  | TRUE MAGIC LANDSCAPING | PINOLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4227 |  | 0 |  | SPOSETO ENGINEERING INC | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 742 |  | 1 |  | NCM CONCRETE | SAN MATEO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2242 |  | 1 |  | LINDA VISTA LANDSCAPE | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 975 |  | 1 |  | COMPLETE TRECARE | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1144 |  | 1 |  | CRATUS INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2585 |  | 0 |  | ERA CONSTRUCTION | SAN PABLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2021-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 3 | 25 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 19107 |  | 1 |  | ELM CONSTRUCTION | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | CASTRO VALLEY | 2021-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 402 |  | 0 |  | A1 CONSTRUCTION GENERAL ENGINEERING | CASTRO VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | CASTRO VALLEY | 2021-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4953 |  | 1 |  | HOMEOWNER | CASTRO VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | DUBLIN | 2021-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | C & J FENCING | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | DUBLIN | 2021-08-13 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 379 |  | 0 |  | M C H ELECTRIC INC | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | DUBLIN | 2021-05-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4376 |  | 0 |  | GOLD COAST PIPELINES | PITTSBURG | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | EMERYVILLE | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SAN MIGUEL CONSTRUCTION | PASADENA | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2021-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2021-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1412 |  | 1 |  | KLEVEN CONSTRUCTION | TEMPE | AZ | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2021-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NORCAL CUSTOMS BUILDERS | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2021-05-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Farm Equipment | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2021-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3541 |  | 6 |  | SPEN CON | DANVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2021-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 626 |  | 1 |  | TIMES UP TERMITE | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2021-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 58 | 50 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | FREMONT | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2021-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2021-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6786 |  | 1 |  | O.C. JONES & SONS INC | BERKELEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 275 |  | 1 |  | THREE RIVERS LANDSCAPE | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2021-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 58 | 50 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | REDWOOD LANDSCAPING | NA |  | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2021-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2021-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 278 |  | 2 |  | GENARO FRIMS | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2021-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25 |  | 3 |  | TIER FENCING INC | PATTERSON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2021-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1930 |  | 1 |  | EXPRESS PLUMBING | SAN MATEO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect Facility Records / Maps
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2021-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1829 |  | 1 |  | JW UNDERGROUND | PORTLAND | OR | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2021-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | AAA MECA CONSTRUCTION | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2021-02-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1405 |  | 0 |  | SANSEI GARDENS | FREMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2021-01-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1780 |  | 1 |  | HOMEOWNER | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2021-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 24 |  | 1 |  | HOMEOWNER | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2021-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 271 |  | 1 |  | HAWKLEY MASONARY | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 557 |  | 1 |  | AB PLUMBING | FREMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CITY OF HAYWARD | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 565 |  | 1 |  | HOMEOWNER | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2021-09-21 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3736 |  | 4 |  | PG&E | LIVERMORE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | No | Mapping error
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2376 |  | 1 |  | HOMEOWNER | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | NEWARK | 2021-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BORG FENCE | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | NEWARK | 2021-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1416 |  | 0 |  | BLAZONA CONCRETE | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | NEWARK | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 997 |  | 2 |  | HOMEOWNER | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | NEWARK | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3203 |  | 1 |  | HOMEOWNER | NEWARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Facility Not Marked Due to Locator error
Pacific Gas and Electric | N | ALAMEDA | NEWARK | 2021-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | L.S. CONSTRUCTION | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1622 |  | 3 |  | BAILLIE COMMUNICATIONS INC | DANVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2973 |  | 1 |  | CASTLEWOOD PARKER LLC | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.5 | 0.3 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 210 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-10-07 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6017 |  | 1 |  | ALVAH CONTRACTORS INC | SOUTH SAN FRANCISCO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.43 | 0.33 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 841 |  | 1 |  | CITY OF OAKLAND | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 54 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 790 |  | 1 |  | HOMEOWNER | SAN CARLOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20 |  | 1 |  | DIAMONDS CONCRETE CONSTRUCTION | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3983 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5194 |  | 1 |  | CITY OF OAKLAND | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | Sheered riser with ladder
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | TIERRA GROUP INC | BELLEVUE | WA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-04-11 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 0.43 | 0.33 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5594 |  | 1 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | Vehicle Impact
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-04-10 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 339 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 4 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PENHALL COMPANY | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1154 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1101 |  | 0 |  | HOMEOWNER | CONCORD | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1791 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-06-07 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1143 |  | 1 |  | ARB INC | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4615 |  | 1 |  | AFFINITY GROUNDWORKS | MARTINEZ | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY COULD NOT BE FOUND OR LOCATED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 379 |  | 1 |  | SMART COMMUNICATIONS SYSTEM | APOLLO BEACH | FL | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 100 |  | 1 |  | ELDEN PLUMBING AND HEATING | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 0.43 | 0.33 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 268 |  | 2 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-04-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3713 |  | 2 |  | EBMUD | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-05-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3119 |  | 0 |  | EBMUD | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6153 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 0.43 | 0.33 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 346 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-01-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 216 |  | 1 |  | ANSTIRMAN CONSTRUCTION | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1457 |  | 1 |  | ANDES CONTRACTOR | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8733 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-05-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2596 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  | 1 |  | ARIA CONSTRUCTION | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1782 |  | 1 |  | STAY CONSTRUCTION | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 54 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 153 |  | 2 |  | REMY''S QUALITY CONSTRUCTION | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7121 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3927 |  | 1 |  | OVER-ALL CONCRETE CO | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 54 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2291 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 42 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-06-22 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1113 |  | 2 |  | MILLER PIPELINE | ALAMEDA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 18671 |  | 1 |  | HOMEOWNER | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4762 |  | 1 |  | SMART COMMUNICATIONS SYSTEM | APOLLO BEACH | FL | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 108 |  | 1 |  | MR AND MRS DEMOLITION | EL CERRITO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1144 |  | 1 |  | ALAN J CULL PLUMBING INC. | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2910 |  | 1 |  | EBMUD | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 171 |  | 1 |  | MONTCLAIR CONSTRUCTION | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 289 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2690 |  | 1 |  | GMBC CONSTRUCTION | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 323 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-06-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 50 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1654 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 3 | 50 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 32633 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1038 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1067 |  | 1 |  | J&B FENCE | PLEASANT HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-07-14 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 361 |  | 1 |  | ARB INC | FAIRFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-12-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4125 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 54 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1775 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1177 |  | 1 |  | R&R PAVING | SAN RAMON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12666 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2300 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2021-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 264 |  | 4 |  | ERGEON INC. | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2021-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 311 |  | 1 |  | ON SITE CONTRACTORS INC | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3434 |  | 1 |  | C. DELEON PLUMBING | EL SOBRANTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2021-02-10 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1841 |  | 1 |  | UTILITY CONSTRUCTION SERVICES | SOUTH SAN FRANCISCO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2021-09-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DURAN & VENABLES INC. | MILPITAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2021-07-27 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CITY OF PLEASANTON | PLEASANTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 365 |  | 0 |  | SEQUOIA CIVIL CONSTRUCTION | PLEASANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2021-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11 |  | 1 |  | UNIVERSAL PAVERS | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2021-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1898 |  | 1 |  | LA POINTE CO | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1922 |  | 1 |  | MORGENROTH DEVELOPMENT CONTRCTOR | PLEASANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2021-02-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2065 |  | 0 |  | LUU CONSTRUCTION | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2021-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HOMEOWNER | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1193 |  | 1 |  | NA | NA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1327 |  | 1 |  | AMK UNDERGROUND | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2021-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 3 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15588 |  | 1 |  | DE SILVA GATES CONSTRUCTION | DUBLIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2021-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 451 |  | 1 |  | STAR ROOTER AND PLUMBING | SAN LORENZO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2021-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 229 |  | 0 |  | BMT CONSTRUCTION | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2021-12-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2592 |  | 1 |  | ROOTER HERO PLUMBING | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | UNION CITY | 2021-03-30 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1327 |  | 1 |  | PG&E | FREMONT | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | UNION CITY | 2021-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 189 |  | 1 |  | GM CONSTRUCTION | NORTH HIGHLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | AMADOR | IONE | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | IONE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | AMADOR | JACKSON | 2021-03-12 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PG&E | SAN FRANCISCO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect information or marks
Pacific Gas and Electric | N | AMADOR | SUTTER CREEK | 2021-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2110 |  | 2 |  | COBABE BROTHERS PLUMBING | EL DORADO HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | BIGGS | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 263 |  | 1 |  | HOMEOWNER | BIGGS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2021-10-06 | Third party excavation damage | Main | Steel | Directional Drilling | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 30786 |  | 2 |  | PIONEER UNDERGROUND | LINCOLN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | CHICO | 2021-09-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1273 |  | 4 |  | RIVERA CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | CHICO | 2021-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2996 |  | 0 |  | STEEL GUARD FENCE CO | TRACY | CA | N | N | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2021-09-01 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1898 |  | 0 |  | HENKELS & MCCOY | POMONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | CHICO | 2021-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 366 |  | 1 |  | KROEKER INC | FRESNO | CA | N | Y | No | No | No | No | No | No | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | BUTTE | CHICO | 2021-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | SMD CONSTRUCTION | CHICO | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | OROVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2021-11-08 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1899 |  | 0 |  | HENKLE & MCCOY | LIVERMORE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2021-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1959 |  | 0 |  | REYNOSO BROS CONSTRUCTION | OROVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2021-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 836 |  | 1 |  | ACE PLUMBING | PALERMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | PALERMO | 2021-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 54 |  | 1 |  | ROTO ROOTER | OROVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-08-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2516 |  | 4 |  | ALPINE LANDSCAPING | CHICO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 28 |  | 0 |  | FIBERCO INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-05-24 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 457 |  | 1 |  | KW EMERSON | SAN ANDREAS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-08-13 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1594 |  | 1 |  | C&C UTILITY | CHICO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-03-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 677 |  | 1 |  | ADVANCED TELECOMMUNICATION | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-11-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 882 |  | 0 |  | BROWN GENERAL ENGINEERING | DURHAM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-10-06 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 215 |  | 0 |  | VETERAN PIPELINE CONSTRUCTION | BENICIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-04-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 302 |  | 0 |  | ADVANCED TELECOMMUNICATION | PLAIN CITY UTAH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-03-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1748 |  | 1 |  | DUDDLEY''S EXCAVATING | GERBER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-01-13 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | KW EMERSON | SAN ANDREAS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-03-04 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2269 |  | 5 |  | OUTBACK | RED BLUFF | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 0 |  | RAINWATER CONSTRUCTION | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-10-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 694 |  | 0 |  | OLEKSANDR HUZOVATY | LOOMIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with Agreement | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15501 |  | 6 |  | BADGER DAYLIGHTNING | REDDING | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1852 |  | 0 |  | DUDLEYS EXCAVATING | GERBER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-05-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 389 |  | 0 |  | EXPERTS IN YOUR HOME | CHICO | CA | N | Y | No | No | No | No | No | No | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1203 |  | 0 |  | STAN''S SEPTIC | MAGALIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-09-08 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4473 |  | 2 |  | TEICHERT PIPELINES | SACRAMENTO | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-07-08 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 437 |  | 0 |  | DARS COX CONSTRUCTION | REDDING | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-07-09 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1332 |  | 0 |  | KW EMERSON | SAN ANDREAS | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-07-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2943 |  | 0 |  | ADVANCED TELECOMMUNICATIONS | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 6 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 434 |  | 1 |  | SANTOS EXCAVATING | CHICO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-02-23 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ARB | FAIRFIELD | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-08-23 | Operator excavation damage | Main | Polyethylene Pipe | Vacuum Equipment with no Agreement | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | OUTBACK CONSTRUCTION | RED BLUFF | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 412 |  | 2 |  | ALL AMERICAN CONSTRUCTION | LIVE OAK | CA | N | Y | No | No | No | No | No | No | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-02-26 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | NA | NA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-05-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 890 |  | 0 |  | DUDLEYS EXCAVTING | GERBER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-05-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1094 |  | 0 |  | FRANKLIN CONST | CHICO | CA | N | Y | No | No | No | No | No | No | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2021-09-08 | Operator excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FAIRBANKS PAVING | OROVILLE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | CALAVERAS | SAN ANDREAS | 2021-09-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 376 |  | 1 |  | HOMEOWNER | SAN ANDREAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CALAVERAS | VALLEY SPRINGS | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VULCAN CONSTRUCTION | FRESNO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | COLUSA | COLUSA | 2021-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2534 |  | 1 |  | FERNANDO MORALES LANDSCAPING | COLUSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | COLUSA | WILLIAMS | 2021-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 331 |  | 2 |  | J K COMMUNICATIONS AND CONSTRUCTION | PHOENIX | AZ | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | COLUSA | WILLIAMS | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 24 |  | 2 |  | J K COMMUNICATIONS & CONST | PHOENIX | AZ | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | COLUSA | WILLIAMS | 2021-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | HOMEOWNER | ORIVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | No | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2021-07-19 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 240 |  | 4 |  | HOMEOWNER | ALAMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2021-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 454 |  | 0 |  | UNITED HOME CONTRACTORS | PLEASANT HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 918 |  | 2 |  | HOMEOWNER | ALAMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2021-02-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2524 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2021-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1097 |  | 1 |  | BIFULCO BUILDERS INC | ALAMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | THE POOL SMITH | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2021-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2311 |  | 0 |  | HOMEOWNER | ALAMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2021-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 182 |  | 1 |  | S&S EXCAVATION | DELHI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 221 |  | 1 |  | HOMEOWNER | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 34 |  | 1 |  | HOMEOWNER | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2021-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 616 |  | 1 |  | HOMEOWNER | ANTIOCH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2021-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2284 |  | 1 |  | SILVA ENTERPRISES | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LILI''S GARDEN | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2021-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1010 |  | 1 |  | BAY AREA UNDERPINNING | FAIRFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2021-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1132 |  | 0 |  | GARNEY CONSTRUCTION | TRACY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | BAY POINT | 2021-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1348 |  | 1 |  | JW BACKHOE AND CONSTRUCTION INC | KNIGHTSEN | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | BAY POINT | 2021-06-07 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3486 |  | 1 |  | UNDERGROUND CONSTRUCTION | BENICIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | BLACKHAWK | 2021-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 398 |  | 1 |  | HOMEOWNER | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | BLACKHAWK | 2021-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 931 |  | 1 |  | HOMEOWNER | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | BRENTWOOD | 2021-05-12 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | PEREZ NURSERY | BRENTWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | BRENTWOOD | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1443 |  | 1 |  | EAST CONTRA COSTA IRRIGATION DISTRICT | BRENTWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | BRENTWOOD | 2021-07-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 32 |  | 1 |  | TEICHERT CONSTRUCTION | PLEASANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | BRENTWOOD | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1580 |  | 0 |  | TEICHERT CONSTRUCTION | PLEASANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | CONTRA COSTA | BRENTWOOD | 2021-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1114 |  | 1 |  | UNITED SITE SERVICES | ANTIOCH | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | BRENTWOOD | 2021-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12353 |  | 2 |  | TEICHERT PIPELINES | PLEASANTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 50 |  | 12 |  | SCHYER AND THOMPSON CONSTRUCTION | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 31 |  | 1 |  | TITAN BUILDING SERVICES | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2021-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 50 |  | 0 |  | HINES PLUMBING LLC | PITTSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2021-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3451 |  | 7 |  | HOMEOWNER | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2021-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9 |  | 0 |  | HOMEOWNER | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CALIFORNIA TRENCHLESS | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2021-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | ALAN MCCAY CONSTRUCTION | MORAGA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2021-08-12 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 224 |  | 1 |  | KEREX ENGINEERING | PLEASANT HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9340 |  | 1 |  | KJ WOODS CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2021-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | LIAISON LANDSCAPING | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1093 |  | 1 |  | A&J FENCING | CONCORD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2021-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 958 |  | 1 |  | ADVANCED TRENCHLESS | MARTINEZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2021-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 62 |  | 1 |  | HOMEOWNER | DANVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2021-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1315 |  | 1 |  | A&J FENCING | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2021-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2029 |  | 1 |  | BLACK DIAMOND PAVER & LANDSCAPE INC. | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DETERIORATED OR FRAGILE FACILITY
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2021-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2362 |  | 1 |  | LEAP FROG PLUMBING | WALNUT CREEK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 50 |  | 1 |  | HOMEOWNER | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DISCOVERY BAY | 2021-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1625 |  | 1 |  | HOMEOWNER | DISCOVERY BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | EL CERRITO | 2021-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1375 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | EL CERRITO | 2021-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1403 |  | 1 |  | ARB INC | LAKE FOREST | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | EL CERRITO | 2021-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20601 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | CONTRA COSTA | EL CERRITO | 2021-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1600 |  | 1 |  | COMPLETE TREE CARE | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | EL SOBRANTE | 2021-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 289 |  | 1 |  | EL SOBRANTE SEWER REPAIR | EL SOBRANTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | EL SOBRANTE | 2021-09-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | PROMPT PLUMBING SERVICES | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | HERCULES | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 918 |  | 1 |  | HOMEOWNER | HERCULES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | HERCULES | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 49 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BEAST BAY PLUMBING | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | HERCULES | 2021-08-12 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ARB INC | FAIRFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | CONTRA COSTA | KENSINGTON | 2021-06-02 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MILLER PIPELINE | ALAMEDA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | KENSINGTON | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | XCEDE CONSTRUCTION | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | KENSINGTON | 2021-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 212 |  | 0 |  | NURTURE SOURCE PARTNERS | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 65 |  | 1 |  | GHS LANDSCAPING | EL SOBRANTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-04-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 312 |  | 1 |  | KR DESIGN AND CONSTRUCTION | CONCORD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2351 |  | 1 |  | HOMEOWNER | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 223 |  | 0 |  | DIABLO GENERAL ENGINEERING | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-11-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3750 |  | 0 |  | RON''S HAULING | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 795 |  | 1 |  | HOMEOWNER | LAFAYETTE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 162 |  | 1 |  | HOMEOWNER | LAFFAETTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-07-08 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 544 |  | 2 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-07-08 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | VIT PLUMBING & LEAK DETECTION | CONCORD | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10604 |  | 1 |  | NA | NA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-06-28 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1267 |  | 2 |  | SUMMIT LANE CONSTRUCTION | HERBER CITY | UT | N | Y | Yes | Yes | No | Yes | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-08-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1630 |  | 1 |  | HOMEOWNER | LAFAYETTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2694 |  | 1 |  | HOMEOWNER | LAFAYETTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-07-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 505 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GENTEC SERVICES INC | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 258 |  | 1 |  | HOMEOWNER | LAFAYETTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 793 |  | 1 |  | ARON AMBRUS CONSTRUCTION | BRENTWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2021-07-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | APEX GRADING | LAFAYETTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2021-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 35 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  | 11487 |  | 1 |  | HOMEOWNER | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | UNKNOWN CAUSE OF FIRE
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 199 |  | 1 |  | HOMEOWNER | MARTINEZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2021-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2021-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 32 |  | 1 |  | HOMEOWNER | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | AFFINITY CONSTRUCTION | WALNUT CREEK | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2021-02-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | QGL INC | MARTINEZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2021-08-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CENCAL DIRECTIONAL DRILLING INC. | EL DORADO HILLS | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | No | Incorrect Information or Marks
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2021-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2021-02-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TAKEHARA LANDSCAPE INC | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2021-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 189 |  | 1 |  | HOMEOWNER | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2021-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 159 |  | 1 |  | HOMEOWNER | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2021-05-29 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4900 |  | 1 |  | HOMEOWNER | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 739 |  | 0 |  | FMK CONSTRUCTION INC | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2021-03-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 476 |  | 1 |  | MICHAEL JAMES CONSTRUCTION | WALNUT CREEK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2021-03-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 997 |  | 1 |  | HOMEOWNER | ORINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1164 |  | 1 |  | LAS PALMAS LANDSCAPE SERVICES | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2021-04-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | AMERICAN UNDERGROUND | BYRON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 34 |  | 1 |  | LAZ N GENERAL CONSTRUCTION | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2021-07-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 223 |  | 1 |  | HOMEOWNER | ORINDA | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 732 |  | 1 |  | AJ NETCON | CAMARILLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2021-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 1 |  | ROXY DESIGNS | PLEASANT HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 117 |  | 1 |  | JCP ROOTER & PLUMBING | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1249 |  | 1 |  | NEXT GENERATION PLUMBING | OAKLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 17 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 861 |  | 1 |  | GARNEY CONSTRUCTION | TRACY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2114 |  | 2 |  | GARNEY CONSTRUCTION | TRACY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-06-16 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 17 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15118 |  | 11 |  | GARNEY CONSTRUCTION | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 17 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 733 |  | 1 |  | HOMEOWNER | PITTSBURG | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1782 |  | 1 |  | HOMEOWNER | ALAMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 1 |  | GARNEY CONSTRUCTION | TRACY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-03-25 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 17 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15339 |  | 1 |  | HOMEOWNER | ALVISO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2959 |  | 1 |  | HOMEOWNER | PITTSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 333 |  | 1 |  | HOMEOWNER | PITTSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 152 |  | 2 |  | BAYSIDE FENCEING | BRENTWOOD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1640 |  | 1 |  | GARNEY CONSTRUCTION | TRACY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1361 |  | 3 |  | GARNEY PACIFIC INC. | TRACY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1.25 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11560 |  | 1 |  | MCK SERVICES | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DETERIORATED OR FRAGILE FACILITY
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 17 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 741 |  | 1 |  | GARNEY CONSTRUCTION | TRACY | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2021-07-29 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1631 |  | 0 |  | MILLER PIPELINE | ALAMEDA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2021-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2541 |  | 1 |  | CALLADO CONCRETE | BRENTWOOD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2021-04-14 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 204 |  | 6 |  | IRISH CONSTRUCTION | PITTSBURG | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 75 |  | 1 |  | HOMEOWNER | PLEASANT HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | C&J FENCING | SAN RAMON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-12-17 | Operator excavation damage | Main | Steel | Miscellaneous/Other | 3 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5667 |  | 0 |  | PENHALL COMPANY | SAN LEANDRO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1779 |  | 1 |  | VERTICAL CONCRETE | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2216 |  | 1 |  | W R FORDE ASSOCIATES | RICHMOND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DARCY & HARTY CONSTRUCTION INC. | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 325 |  | 1 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-10-04 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 24501 |  | 3 |  | PRECISION DIRECTIONAL BORING | MARTINEZ | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3539 |  | 0 |  | HOMEOWNER | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2208 |  | 2 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 0 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1681 |  | 0 |  | NA | NA | [10 empty] | USA NOT CALLED | bar: N to Yes
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 264 |  | 1 |  | HOMEOWNER | HERCULES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1220 |  | 2 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 109 |  | 1 |  | 1 DEGREE CONSTRUCTION | PLEASANTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3071 |  | 1 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1468 |  | 1 |  | HOMEOWNER | RICMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-07-03 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 3 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SMI DEMOLITION CO. | LARKSPUR | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2021-07-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1254 |  | 1 |  | TERRA NOVA ENGINEERING | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to expose facility with hand tools
Pacific Gas and Electric | N | CONTRA COSTA | RODEO | 2021-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2532 |  | 1 |  | HOMEOWNER | EL SOBRANTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN PABLO | 2021-08-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2157 |  | 1 |  | EBMUD | SAN PABLO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | C&J FENCING | SAN RAMON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2021-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GIBSON DEVELOPMENT | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1313 |  | 1 |  | SEFNCO | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2021-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1.25 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 7 |  | HOMEOWNER | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2021-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | AMM FENCING | DUBLIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 518 |  | 1 |  | HOMEOWNER | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-06-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 845 |  | 1 |  | JC LANDSCAPING | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 878 |  | 1 |  | FALCON PAVING | PITTSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 771 |  | 1 |  | TAK COMMUNICATIONS CA | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 392 |  | 1 |  | BAY AREA ASPHALT & CEMENT WORKS | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-12-08 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 16924 |  | 1 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2596 |  | 1 |  | ABLE TO PLUMBING & ROOTER | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 32 |  | 0 |  | HOMEOWNER | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 68 |  | 1 |  | GENESIS LANDSCAPING | ANTIOCH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DR LEMMINGS CONSTRUCTION | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 105 |  | 1 |  | GREENGO LANDSCAPING | WALNUT CREEK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | THE LANDSCAPE COMPANY | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-07-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | JCA LANDSCAPING | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-11-04 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 31 |  | 1 |  | UNDERGROUND CONSTRUCTION COMPANY | BENICIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2979 |  | 2 |  | GOLDEN PALM LANDSCAPE | BRENTWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2021-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 211 |  | 1 |  | GENESIS LANDSCAPE INC. | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2021-04-05 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | EL DORADO HILLS | CA | N | Y | No | No | No | No | No | No | No | Vehicle Impact
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2021-04-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 277 |  | 1 |  | PROCIDA LANDSCAPING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | EL DORADO HILLS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7442 |  | 2 |  | 21ST CENTURY PLUMBING HEATING & AIR | EL DORADO HILLS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2021-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6542 |  | 1 |  | KERRY KING CONSTRUCTION | RESCUE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | BIOLA | 2021-12-09 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 4 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 23123 |  | 11 |  | JERRYS TRENCHING SERVICE | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2021-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 562 |  | 1 |  | AJ EXCAVATION | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2021-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2137 |  | 5 |  | NOVA PLUMBING SERVICE | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2021-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BRINER AND SON | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2021-06-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2102 |  | 0 |  | AC CONSTRUCTION | MERCED | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2021-06-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3692 |  | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2021-06-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 532 |  | 0 |  | LCCLARD MASONRY CONSTRUCTION | HANFORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2021-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 32 |  | 4 |  | PREMIER PLUMBING | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2021-08-06 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 445 |  | 1 |  | PG&E | FRESNO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Struck Facility while exposing with hand tools
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2021-02-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2396 |  | 0 |  | M&L PLUMBING | FRESNO CA | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2021-09-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3541 |  | 1 |  | HOMEOWNER | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | DYNAMIC ELECTRIC | CLOVIS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Facility Marked Inaccurately
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2021-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HOMEOWNER | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2411 |  | 1 |  | CALIFORNIA TURF AND LANDSCAPING | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FIREBAUGH | 2021-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 0 |  | VALLEY UNIQUE ELECTRIC | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FIREBAUGH | 2021-11-19 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3757 |  | 0 |  | BUSH CONSTRUCTION | HANFORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FIREBAUGH | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 172 |  | 1 |  | HOMEOWNER | FIREBAUGH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FIREBAUGH | 2021-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 274 |  | 0 |  | MP NEXLEVEL | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FIREBAUGH | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ROLFE CONSTRUCTION | ATWATER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FOWLER | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 34 |  | 1 |  | M&M POOL | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FOWLER | 2021-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2427 |  | 0 |  | 3G CONSTRUCTION | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FOWLER | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1084 |  | 1 |  | CR CONSTRUCTION | FOWLER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-03-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2565 |  | 0 |  | ZENGERS BACKHOE SERVICE | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 158 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-08-17 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 809 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-02-10 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3462 |  | 6 |  | FRESNO CITY WATER COMPANY | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-10-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7668 |  | 1 |  | SNAKE N LATERALS/JOHNATHAN MARTINEZ | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-08-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 77 |  | 0 |  | PACIFIC UTILITY AND TRENCHING | PORTERVILLE | CA | N | Y | No | Yes | No | Yes | No | No | No | Marking Inadequate
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2438 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9727 |  | 0 |  | GOLDEN STATE UTILITY | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1607 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-02-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1289 |  | 1 |  | PREMIER LANDSCAPE | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1030 |  | 0 |  | EMMETS EXCAVATION | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS/MAPS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 78 |  | 2 |  | BLANCA BERNAL | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 230 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PROFESSIONAL PLUMBER | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 3 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8877 |  | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-08-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 257 |  | 1 |  | HOMEOWNER | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-08-23 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2020 |  | 0 |  | LYLES UTILITY | FRESNO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 92 |  | 0 |  | RESTORATION GRADING | CARUTHERS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 35 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-08-16 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 10 |  | LASAR UNDERGROUND | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 65 |  | 2 |  | CROWN CUMMUNIATIONS | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-09-30 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | LYLES UTILITY | VISALIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-07-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.43 | 0.34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 250 |  | 1 |  | MAS UNLIMITED FENCE | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1227 |  | 2 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-11-09 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3763 |  | 1 |  | TOSTED ASPHALT INC | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HAYDON CONSTRUCTION(RAUL DIAZ) | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1734 |  | 0 |  | WEST VALLEY CONSTRUCTION | FRESNO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1577 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 268 |  | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2561 |  | 0 |  | CENTRAL VALLEY REPAIR | FRESNO | CA | N | Y | No | No | No | No | No | No | No | Hit riser with forklift
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 547 |  | 2 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PREMIER POOLS | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-07-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 243 |  | 0 |  | BROWNING CONSTRUCTION COMPANY | FRESNO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1180 |  | 0 |  | FRESNO PLUMBING & HEATING | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3153 |  | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 283 |  | 2 |  | ACCU BORE DRILLING | BENICIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-08-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2053 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1367 |  | 1 |  | FLOYD JOHNSTON CONSTRUCTION | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | FAILED TO PROTECT EXPOSED FACILITY
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 828 |  | 1 |  | TRI COUNTY EXAVATION | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 252 |  | 1 |  | BROWNING CONSTRUCTION COMPANY | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | AC ELECTRIC | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-06-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1357 |  | 7 |  | IMPERIAL ELECTRIC SERVICE | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-10-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 64 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2021-01-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | LANDSCAPE CONCEPTS | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | KERMAN | 2021-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 78 |  | 2 |  | SEBASTIAN CORP | FRESNO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | KERMAN | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 53 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1859 |  | 0 |  | V KROEKER INC DEMOLITION | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | KERMAN | 2021-09-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 53 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1882 |  | 1 |  | WEST SCAPES | HANFORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | KERMAN | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 53 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1008 |  | 1 |  | CALIFORNIA SHINE CONSTRUCTION | FRESNO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | FRESNO | MENDOTA | 2021-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 81 |  | 1 |  | BASCO CONSTRUCTORS | CHATSWORTH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | SAN JOAQUIN | 2021-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2958 |  | 0 |  | ROLFE CONSTRUCTION | ATWATER | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | SAN JOAQUIN | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3009 |  | 0 |  | AMERICAN PLUMBING SOLUTIONS | FOWLER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Struck Facility while exposing with hand tools
Pacific Gas and Electric | N | FRESNO | SAN JOAQUIN | 2021-08-23 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1223 |  | 0 |  | AMERICAN PLUMBING SOLUTIONS | FOWLER | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | SAN JOAQUIN | 2021-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1190 |  | 0 |  | ROLFE CONSTRUCTION | ATWATER | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | SAN JOAQUIN | 2021-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2292 |  | 1 |  | ROLFE CONSTRUCTION | ATWATER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | SAN JOAQUIN | 2021-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2594 |  | 0 |  | ROLFE CONSTRUCTION | ATWATER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Mapping error
Pacific Gas and Electric | N | FRESNO | SAN JOAQUIN | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5516 |  | 1 |  | ROLFE CONSTRUCTION | ATWATER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Locator error
Pacific Gas and Electric | N | FRESNO | SAN JOAQUIN | 2021-09-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2363 |  | 1 |  | ROLFE CONSTRUCTION | ATWATER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | FRESNO | SANGER | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CHARLES TESTERMAN ENGINEERING | SQUAW VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | SANGER | 2021-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 1 |  | HOMEOWNER | SANGER | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | SELMA | 2021-03-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6417 |  | 1 |  | CONSOLIDATED IRRIGATION | SELMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | SELMA | 2021-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 124 |  | 1 |  | HOMEOWNER | SELMA | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | FRESNO | SELMA | 2021-11-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 32 |  | 0 |  | DCW CONTRACTORS | VISALIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | TRANQUILLITY | 2021-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 85 |  | 2 |  | HOMEOWNER | TRANQUILITY | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | GLENN | ORLAND | 2021-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LAMON | YUBA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | GLENN | WILLOWS | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1810 |  | 1 |  | DYNAMIC IRONWORKS | RIO LINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | ARCATA | 2021-03-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11907 |  | 20 |  | MERCER FRASIER CO. | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | ARCATA | 2021-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 909 |  | 2 |  | HOMEOWNER | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | ARCATA | 2021-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | ARCATA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | BLUE LAKE | 2021-08-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 464 |  | 5 |  | BLUE LAKE RANCHERIA | BLUELAKE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 557 |  | 1 |  | MERCER FRASER CO | EUREKA | CA | N | Y | No | No | No | No | No | No | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2021-10-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2021-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2547 |  | 1 |  | CITY OF EUERKA | EUREKA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2021-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2131 |  | 2 |  | MERCER FRASER CO | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2021-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 208 |  | 1 |  | HOMEOWNER | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2021-09-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 0 |  | CALIFORNIA HIGHWAY CONSTRUCTION | WOODLAND HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2021-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3570 |  | 1 |  | HOMEOWNER | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | FORTUNA | 2021-03-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6735 |  | 1 |  | CITY OF FORTUNA | FORTUNA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | HUMBOLDT | FORTUNA | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FORTUNA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | MCKINLEYVILLE | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1330 |  | 1 |  | HOMEOWNER | MCKINLEYVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | MCKINLEYVILLE | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8073 |  | 1 |  | MILLER FARMS | MCKINLEYVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | MCKINLEYVILLE | 2021-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 475 |  | 1 |  | PARTHENON CONSTRUCTION | MCKINLEYVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | MCKINLEYVILLE | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2003 |  | 6 |  | DANIELSON CONSTRUCTION | LOLETA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 351 |  | 1 |  | NR DEVELOPMENT | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 627 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-01-06 | Third party excavation damage | Main | Steel | Grader/Scraper | 2 | 51 | 47 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | BOWMAN ASPHALT | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Vacuum Equipment with no Agreement | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BADGER DAYLIGHTING | BENICIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-09-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 773 |  | 1 |  | LDD CONSTRUCTION | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-03-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4591 |  | 2 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1517 |  | 2 |  | RUDOLPHO DELEON | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1454 |  | 0 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ABANDONED/DEACTIVATED FACILTY ISSUE
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4226 |  | 1 |  | VAST NETWORK | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 299 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SIERRA CONSTRUCTION AND EXCAVATION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 26 |  | 2 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 701 |  | 2 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | Yes | Yes | No | Yes | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-07-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1704 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1648 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 226 |  | 0 |  | KANGAROOTER PLUMBING | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-02-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 54 |  | 0 |  | CSI CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO PROTECT EXPOSED FACILITY
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 768 |  | 2 |  | MARTIN CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 241 |  | 1 |  | GARNEY CONSTRUCTION | TRACY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-09-22 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14773 |  | 0 |  | CAMARILLO DRLLING | NUEVO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 24 |  | 2 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1799 |  | 2 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-02-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2601 |  | 2 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 880 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 52 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-09-24 | Operator excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1172 |  | 0 |  | PG&E | BAKERSFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-03-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1144 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 52 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2021-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 396 |  | 8 |  | COAST TO COAST COMMUNICATIONS | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BEAR VALLEY SPRINGS | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | OUTSOURCE UTILITY CONTRACTORS | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | INYOKERN | 2021-08-12 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | SOUTHERN CALIFORNIA EDISON | RIDGECREST | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | MARICOPA | 2021-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DALINGHAUS CONSTRUCTION | LAKE ELSINORE | CA | N | Y | Yes | No | Yes | Yes | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | RIDGECREST | 2021-02-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4304 |  | 6 |  | IWV CONSTRUCTION | RIDGECREST | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | RIDGECREST | 2021-07-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1586 |  | 0 |  | IWV WATER DISTRICT | RIDGECREST | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | RIDGECREST | 2021-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6569 |  | 0 |  | HOMEOWNER | RIDGECREST | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | RIDGECREST | 2021-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 1 |  | IWV WATER DISTRICT | RIDGECREST | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | TEHACHAPI | 2021-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 21 |  | 1 |  | HOMEOWNER | TEHACHAPI | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KINGS | AVENAL | 2021-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BROUGH CONSTRUCTION | ARROYO GRANDE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KINGS | AVENAL | 2021-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3554 |  | 0 |  | HOMEOWNER | AVENAL | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | KINGS | AVENAL | 2021-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | AVENAL | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | KINGS | AVENAL | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1526 |  | 1 |  | HOMEOWNER | AVENAL | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | KINGS | AVENAL | 2021-03-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2140 |  | 1 |  | HOMEOWNER | AVENAL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KINGS | AVENAL | 2021-03-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2873 |  | 1 |  | HOMEOWNER | AVENAL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KINGS | AVENAL | 2021-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2075 |  | 1 |  | S&S CUSTOMIZING | REEDLY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KINGS | KETTLEMAN CITY | 2021-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 15 | 9 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2822 |  | 1 |  | HOMEOWNER | KETTELMAN CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | MADERA | CHOWCHILLA | 2021-06-19 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 43 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2543 |  | 1 |  | PACIFIC GAS & ELECTRIC | MODESTO | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | CHOWCHILLA | 2021-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 31 |  | 1 |  | PREMIUM PLUMBING | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2021-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1090 |  | 0 |  | ALL WEATHER HEATING & AIR | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2021-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | MADERA | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | MADERA | MADERA | 2021-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1477 |  | 1 |  | LASAR UNDERGROUND CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MADERA | MADERA | 2021-07-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | HOMEOWNER | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 905 |  | 1 |  | HOMEOWNER | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2021-12-10 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1225 |  | 1 |  | WESTECH SYSTEMS INC | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2021-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 68 |  | 1 |  | B & B PLUMBING | ATWATER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | BELVEDERE | 2021-01-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 292 |  | 14 |  | REDWOOD ENGINEERING | BELVEDERE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TJ BUILT CONSTRUCTION | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2021-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | CORTE MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2021-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MARIN LANDSCAPE MANAGEMENT | NOVATO | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 452 |  | 1 |  | JOHN C HILL CONSTRUCTION | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2021-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | H&R PULU CONCRETE | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 135 |  | 0 |  | BEST EVER CITY FLOORING | FAIRFAX | CA | N | Y | No | No | No | No | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2021-08-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GLENN E NEWCOMER CONSTRUCTION | SAUSALITO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2021-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 250 |  | 1 |  | MCKUIN PIPELINE | HOLLISTER | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2021-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2554 |  | 1 |  | HOMEOWNER | FAIRFAX | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2021-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3261 |  | 0 |  | HOMEOWNER | FAIRFAX | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2021-09-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1273 |  | 1 |  | S&S LANDSCAPING | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3272 |  | 10 |  | GHILOTTI BROTHERS | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 62 |  | 1 |  | BELLOWS PLUMBING & HVAC | SOQUEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2021-07-21 | Operator excavation damage | Main | Steel | Directional Drilling | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15181 |  | 8 |  | PG&E | SAN RAFAEL | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2021-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 320 |  | 0 |  | GOLTERMANN CONSTRUCTION | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2021-02-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 936 |  | 0 |  | GOLTERMANN CONSTRCTION | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2021-08-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 107 |  | 1 |  | CAL ENGINEERING COMPANY | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2021-02-08 | Third party excavation damage | Riser | Steel | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 54 |  | 0 |  | ABACUS | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | LARKSPUR | 2021-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2262 |  | 1 |  | MESSANO''S ELECTRIC | CARMICHAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | LARKSPUR | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 12 |  | MAGGIORA & GHILOTTI INC | SAN RAFAEL | CA | N | Y | Yes | No | Yes | No | No | No | No | INSUFFICIENT INFORMATION TO USA
Pacific Gas and Electric | N | MARIN | LARKSPUR | 2021-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | LARKSPUR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9 |  | 0 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SILVA CONTRACTORS INC | PINOLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 269 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-05-12 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2124 |  | 1 |  | NA | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-07-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-07-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 29 |  | 1 |  | HTH CONSTRUCTION | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-10-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HTH CONSTRUCTION | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2157 |  | 1 |  | HURRICANE HAULING AND DEMOLITION INC | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DUNAMIS INTERNATIONAL | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FLOYD CONSTRUCTION | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXPIRED USA TICKET
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-06-03 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-09-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2595 |  | 0 |  | TURBIN STRUCURAL ENGINEERING | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 485 |  | 1 |  | DE LUNA CONSRTUCTION | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2770 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 62121 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2021-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2441 |  | 0 |  | BROC BUILT | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2021-02-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 563 |  | 8 |  | ARB | PITTSBURG | CA | Y | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | NOVATO | 2021-04-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARB INC | LAKE FOREST | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | MARIN | NOVATO | 2021-05-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 39 |  | 1 |  | HOMEOWNER | NOVATO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | NOVATO | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 18 |  | 2 |  | HOMEOWNER | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 160 |  | 1 |  | ROBERT LOPEZ CONSTRUCTION | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 2 |  | DNG CONSTRUCTION | PHOENIX | AZ | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1370 |  | 0 |  | ALL ACCESS BOBCAT | COTATI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2021-03-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | HOMEOWNER | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2021-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 420 |  | 0 |  | CEMCON | PITTSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | ROSS | 2021-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CURTIS HILL LANDSCAPING | ROSS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | ROSS | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SEWER CONNECTION | EL SOBRANTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 766 |  | 1 |  | CHAN DRAINAGE | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1430 |  | 1 |  | GONZALEZ LANDSCAPING | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4522 |  | 2 |  | RANGER PIPELINE | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2021-04-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SAN ANSELMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2021-03-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ROLLO & RIDLEY GEOTECHNICAL ENGINEERS | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2021-02-09 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2231 |  | 0 |  | DUNAMIS INTERNATIONAL | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1509 |  | 0 |  | BRODRICK GENERAL ENGINERING | SONOMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2341 |  | 1 |  | W.R. FORDE ASSOCIATES | RICHMOND | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-08-25 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1159 |  | 1 |  | ARB INC | PITTSBURG | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-08-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4450 |  | 1 |  | FISNEY CONSTUCTION | BURLINGAME | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2361 |  | 0 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6821 |  | 2 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-04-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1911 |  | 1 |  | ROTO ROOTER | NOVATO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 169 |  | 1 |  | SCHLEICHER CONSTRUCTION | FAIRFAX | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1868 |  | 1 |  | GHS LANDSCAPING | EL SOBRANTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2355 |  | 1 |  | ALLMON DEVELOPMENTS | ROHNERT PARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1063 |  | 1 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-12-02 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 34488 |  | 16 |  | GHILOTTI BROS INC | SAN RAFAEL | CA | N | Y | Yes | Yes | No | No | No | No | No | Excavated Prior to Receiving a Positive Response From All Utilities
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-05-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SAXX & BROOK CONSTRUCTION | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | WESTLAND CONSTRACTORS, INC | OAKLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Struck Facility while exposing with hand tools
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 234 |  | 2 |  | MARIN COUNTY ARBORISTS | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4718 |  | 0 |  | GHILOTTI BROTHERS | SAN RAFAEL | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2021-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 977 |  | 1 |  | LANDCO ENVIRONMENTS INC | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2021-09-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1301 |  | 1 |  | MARR B OLSEN INC | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2021-12-09 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2537 |  | 1 |  | OSMOSE UTILITIES SERVICES INC | PEACHTREE | GA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1005 |  | 1 |  | J COMPANY PLUMBING | SUN VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7202 |  | 1 |  | MAGGIORA & GHILOTTI INC | SAN RAFAEL | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | MARIN | TIBURON | 2021-05-13 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1202 |  | 1 |  | VETERAN PIPELNE CONSTRCTION | BENCIA | CA | Y | Y | Yes | Yes | No | Yes | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | MARIN | TIBURON | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ROBINSON CONSTRUCTION | PENNGROVE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | TIBURON | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 108 |  | 5 |  | GLADIATOR REPIPE INC | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | TIBURON | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 977 |  | 1 |  | HOMEOWNER | TIBURON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | REDWOOD VALLEY | 2021-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5003 |  | 1 |  | STATE WIDE UTILITY | MURRIETA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | MENDOCINO | REDWOOD VALLEY | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 70 |  | 1 |  | STATE WIDE UTILITY | MURRIETA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | MENDOCINO | REDWOOD VALLEY | 2021-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1225 |  | 1 |  | HOMEOWNER | REDWOOD VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MENDOCINO | REDWOOD VALLEY | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | REDWOOD VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | REDWOOD VALLEY | 2021-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 912 |  | 1 |  | HOMEOWNER | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2021-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2348 |  | 1 |  | HOMEOWNER | UKIAH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2021-08-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | CUPPLES EXCAVATING | HOPLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2021-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 305 |  | 1 |  | HOMEOWNER | UKIAH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2021-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 2 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | UKIAH | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 34 |  | 1 |  | CONCRETE PETE CONSTRUCTION | UKIAH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 5 |  | CABLEMAN | FAIRFIELD | CA | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MENDOCINO | WILLITS | 2021-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1539 |  | 4 |  | DISABLED VETERANS CONSTRUCTION | CARMICHAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | ATWATER | 2021-05-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 907 |  | 1 |  | LODUCA COMPANY | STOCKTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | ATWATER | 2021-06-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 193 |  | 0 |  | CENTRAL VALLEY LANDSCAPING | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | ATWATER | 2021-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 26 |  | 2 |  | WILKINSON ELECTRIC | OAKDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | ATWATER | 2021-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | ATWATER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | DELHI | 2021-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 88 |  | 1 |  | HOMEOWNER | DELHI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | DELHI | 2021-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 590 |  | 1 |  | HOMEOWNER | DELHI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | DOS PALOS | 2021-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1801 |  | 1 |  | HOMEOWNER | DOS PALOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | HILMAR | 2021-01-22 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 0 |  | SOUTH COAST WHOLESALE | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | LIVINGSTON | 2021-06-12 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 4 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7674 |  | 2 |  | SPECTRUM | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | LOS BANOS | 2021-04-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 52 |  | 0 |  | TRUE GREENSCAPES | TULARE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | LOS BANOS | 2021-03-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1785 |  | 0 |  | SABBATINI PLUMBING | HOLLISTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | LOS BANOS | 2021-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | EAKINS PROPERTIES | MOUNTAIN VIEW | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavated Prior to Receiving a Positive Response From All Utilities
Pacific Gas and Electric | N | MERCED | LOS BANOS | 2021-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1660 |  | 1 |  | R/ C SOLUTION PLUMBING | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | MERCED | 2021-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 34 |  | 2 |  | HOMEOWNER | MERCED | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | MERCED | 2021-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 1 |  | HOMEOWNER | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | MERCED | 2021-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1368 |  | 0 |  | RB ENVIRONMENTAL INC | STOCKTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | MERCED | 2021-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | DYANMIC TRADES | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | MERCED | 2021-05-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 32 |  | 2 |  | RAY''S GARDENING | HILMAR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | MERCED | 2021-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 98 |  | 2 |  | LAWLER EXCAVATION | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | MERCED | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 1 |  | HOMEOWNER | MERCED | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | SOUTH DOS PALOS | 2021-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2739 |  | 1 |  | HOMEOWNER | DOS PALOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | AROMAS | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 53 |  | 1 |  | MONTEREY COUNTY PW | SALINAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2021-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | CARMEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SAROYAN MASTERBUILDER | SEASIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2021-11-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1107 |  | 1 |  | HOMEOWNER | CARMEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1436 |  | 1 |  | HOMEOWNER | MARINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2021-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12 |  | 1 |  | AFTER HOUR PLUMBING & DRAIN | SEASIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2021-02-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | LEWIS BUILDER | CARMEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL VALLEY | 2021-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 13 |  | 1 |  | AC LANDSCAPE | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL-BY-THE-SEA | 2021-01-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | CARMEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL-BY-THE-SEA | 2021-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | EASY DRAINS | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL-BY-THE-SEA | 2021-04-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 335 |  | 1 |  | MCNAMEE CONSTRUCTION | MONTEREY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | CARMEL-BY-THE-SEA | 2021-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 144 |  | 1 |  | HOMEOWNER | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL-BY-THE-SEA | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2229 |  | 0 |  | STOKER AND ALLAIRE | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL-BY-THE-SEA | 2021-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 215 |  | 1 |  | HOMEOWNER | CARMEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CASTROVILLE | 2021-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1130 |  | 1 |  | HOMEOWNER | CASTROVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | GREENFIELD | 2021-07-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 383 |  | 1 |  | HOMEOWNER | GREENFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | KING CITY | 2021-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | TEICHERT CONSTRUCTION | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | KING CITY | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1372 |  | 0 |  | SEATEC UNDERGROUND CONSTRUCTION | SALINAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | KING CITY | 2021-04-26 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 940 |  | 2 |  | INTEGRATED HOME SOLUTIONS | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | KING CITY | 2021-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 234 |  | 1 |  | HOMEOWNER | KING CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MARINA | 2021-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 110 |  | 1 |  | RANDAZZO ENTERPRISE INC | CASTROVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | MARINA | 2021-07-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 351 |  | 3 |  | SMITH & DENISON CONSTRUCTION | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2021-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1137 |  | 1 |  | MR ROOTER | SALINAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2021-09-21 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1539 |  | 0 |  | MILLER PIPELINE | ALAMEDA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2021-06-01 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2064 |  | 1 |  | MILLER PIPELINE | ALAMEDA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DETERIORATED OR FRAGILE FACILITY
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2021-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 2 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ANRAK CORP | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2021-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 881 |  | 0 |  | ALDACOS CONCRETE | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 732 |  | 2 |  | SAN PAOLO CONCRETE | SEASIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5055 |  | 3 |  | TEICHERT CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | PACIFIC GROVE | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 29 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 756 |  | 1 |  | EASY PLUMBING | MONTEREY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | PACIFIC GROVE | 2021-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3668 |  | 2 |  | MONTEREY PENINSULA ENGINEERING | MARINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | MONTEREY | PACIFIC GROVE | 2021-07-20 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MILLER PIPELINE | ALAMEDA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2021-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 316 |  | 1 |  | TREE MOVERS | MOUNTAIN VIEW | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2021-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 115 |  | 1 |  | HOMEOWNER | APTOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2021-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 35 |  | 1 |  | JR FENCING | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2021-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1056 |  | 1 |  | HOMEOWNER | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2021-08-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 11 |  | GRANITE ROCK | STOCKTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | MONTEREY | PRUNEDALE | 2021-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PEMBERTON ENGINEERING | SALINAS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO PROTECT EXPOSED FACILITY
Pacific Gas and Electric | N | MONTEREY | PRUNEDALE | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2530 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | PRUNEDALE | 2021-06-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4075 |  | 3 |  | CYPRESS WATER SERVICES,INC | CASTROVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | PRUNEDALE | 2021-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2109 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 305 |  | 0 |  | BLANCAS CONSTRUCTION | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2021-05-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10493 |  | 0 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2021-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 279 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 38 |  | 1 |  | HOMEOWNER | SPRECKELS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2021-02-04 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 683 |  | 1 |  | PG&E | SALINAS | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 38 |  | 1 |  | LEAK DETECTION SPECIALIST | CARMEL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 403 |  | 1 |  | COLLINS ELECTRIC | MARINA | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2021-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1506 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2021-11-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 824 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2021-07-21 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CUPERTINO ELECTRIC | SAN FRANCISCO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | No | Incorrect Information or Marks
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2021-07-15 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CUPERTINO ELECTRIC | SAN FRANCISCO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | No | Incorrect Information or Marks
Pacific Gas and Electric | N | MONTEREY | SEASIDE | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 156 |  | 1 |  | HOMEOWNER | SEASIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SEASIDE | 2021-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2101 |  | 1 |  | SPER CONTRACTING | TRACY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | SEASIDE | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 760 |  | 1 |  | HOMEOWNER | SEASIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SEASIDE | 2021-06-16 | Third party excavation damage | Main | Steel | Grader/Scraper | 6 | 15 | 12 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5945 |  | 17 |  | GILLIAM & SONS, INC. | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | SEASIDE | 2021-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MONTEREY BAY COMMUNITY | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | MONTEREY | SEASIDE | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BAY VIEW COMMUNITY | SEASIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SEASIDE | 2021-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 298 |  | 1 |  | BAY VIEW COMMUNITY | SEASIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SEASIDE | 2021-07-12 | Operator excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2941 |  | 2 |  | PG&E | SAN JOSE | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | SOLEDAD | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 94 |  | 2 |  | HOMEOWNER | SOLEDAD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SOLEDAD | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2748 |  | 2 |  | HOMEOWNER | SOLEDAD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | AMERICAN CANYON | 2021-01-13 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 293 |  | 0 |  | GHILOTTI BROTHERS | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | AMERICAN CANYON | 2021-12-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 13 |  | PRESTON PIPELINES | MILPITAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | NAPA | ANGWIN | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HOMEOWNER | ANGWIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | CALISTOGA | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5073 |  | 0 |  | NORTHWEST GENERAL ENGINEERING | CALISTOGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | CALISTOGA | 2021-08-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 19268 |  | 108 |  | CALISTOGA DEPARTMENT OF PUBLIC WORKS | CALISTOGA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | CALISTOGA | 2021-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 42 |  | 1 |  | HOMEOWNER | CALISTOGA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | DEER PARK | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3677 |  | 1 |  | BLUE SKY WEST LANDSCAPING LLC | SAINT HELENA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | DEER PARK | 2021-01-05 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PINNACLE POWER SERVICES | VALLEJO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | NAPA | 2021-05-19 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 519 |  | 4 |  | J K COMMUNICATIONS | PHOENIX | AZ | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | NAPA | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1272 |  | 0 |  | CADWIN- DORWARD | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2021-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8414 |  | 2 |  | HOMEOWNER | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2021-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1597 |  | 1 |  | NUNEZ VINEYARD | NAPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | NAPA | 2021-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 417 |  | 1 |  | HOMEOWNER | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2021-09-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3323 |  | 1 |  | HOMEOWNER | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2021-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1006 |  | 1 |  | CAPITAL RENOVATIONS | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2021-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 45 |  | 1 |  | CUSTOM LANSCAPE | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2021-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1110 |  | 0 |  | M K B CONSTRUCTION | CLOVERDALE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | NAPA | NAPA | 2021-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 498 |  | 1 |  | HOMEOWNER | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2021-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ADVANCE LANDSCAPING | AMERICAN CANYON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | SAINT HELENA | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1168 |  | 1 |  | BELLA MAISON LLC | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | SAINT HELENA | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2075 |  | 1 |  | GONZALES LANDSCAPE & DESIGN | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | ST HELENA | 2021-09-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | KAISER CONSTRUCTION | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | NAPA | YOUNTVILLE | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 213 |  | 1 |  | R J L CONSTRUCTION | PACIFIC GROVE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | YOUNTVILLE | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ROB HOWELL CONSTRUCTION | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2021-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3049 |  | 1 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | Storm uprooted tree and damaged pipe line service
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2021-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2021-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2021-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NAVI & SONS PLUMBING | WHITTIER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2021-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1847 |  | 1 |  | HOMEOWNER | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2021-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1578 |  | 1 |  | BEAM EASY LIVING CENTER | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2021-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 136 |  | 1 |  | HOMEOWNER | GRASS VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1215 |  | 2 |  | URKE SERVICES | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2021-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 20 | 16 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 393 |  | 0 |  | WESTERN WATER FEATURES | EL DORADO HILLS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 16 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | MERRIL MAGEN-WESTON | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | NEVADA CITY | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 322 |  | 1 |  | RODRIGUEZ AND SONS LANDSCAPES | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | NEVADA CITY | 2021-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | NEVADA CITY | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | NEVADA | NEVADA CITY | 2021-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 1 |  | HOMEOWNER | NEVADA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | NEVADA CITY | 2021-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 50 |  | 1 |  | HOMEOWNER | NEVADA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | NEVADA CITY | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 348 |  | 1 |  | ANDREENA HUNT | NEVADA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | NEVADA CITY | 2021-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 658 |  | 1 |  | MEDICS ELECTRIC | FOREST HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NEVADA | PENN VALLEY | 2021-12-09 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1949 |  | 1 |  | MICHELS PACIFIC ENERGY INC | SANTA CLARA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | AUBURN | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 187 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TMW PLUMBING | WEIMAR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 586 |  | 1 |  | HOMEOWNER | AUBURN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2021-02-12 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2021-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 211 |  | 1 |  | CHARIS POOLS AND LANDSCAPE | APPLEGATE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2021-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1326 |  | 0 |  | GRAY ELECTRIC | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2021-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 136 |  | 1 |  | ARGUETA BALTHAZAR | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2021-09-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 698 |  | 0 |  | PRESTON PIPELINES | WEST SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2021-08-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 54 |  | 1 |  | BRCO | ROCKLIN | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2021-01-21 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 106 |  | 2 |  | SAN JUAN WATER | GRANITE BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2021-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | FRENCH CONNECTION PLUMBING | CARMICHAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2021-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 42 |  | 2 |  | FRENCH CONNECTION PLUMBING | CARMICHAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 81 |  | 1 |  | E&C INNOVATIONS | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | LINCOLN | 2021-05-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 312 |  | 1 |  | HOMEOWNER | LINCOLN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | LINCOLN | 2021-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 895 |  | 1 |  | HOMEOWNER | LINCOLN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | LINCOLN | 2021-02-04 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 94 |  | 0 |  | LUND CONSTRUCTION | NORTH HIGHLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | LINCOLN | 2021-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 452 |  | 0 |  | PACIFIC EXCAVATION INC | LINCOLN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | LOOMIS | 2021-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5753 |  | 1 |  | HOMEOWNER | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | LOOMIS | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1640 |  | 1 |  | ROOTER HERO | MISSION HILLS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | MEADOW VISTA | 2021-03-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1525 |  | 1 |  | OSBORN GENERAL ENGINEERING | MEADOW VISTA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | NEWCASTLE | 2021-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1852 |  | 1 |  | VITALITY ELECTRIC | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2021-06-17 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6569 |  | 0 |  | HOMEOWNER | AUBURN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2021-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | QUALITY FIRST | CITRUS HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2021-01-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2816 |  | 0 |  | ASH CONSTRUCTION | LINCOLN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2021-01-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ASH CONSTRUCTION | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 743 |  | 1 |  | JACK LIEW CONSTRUCTION | LOOMIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2021-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | ROCKLIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2021-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2016 |  | 3 |  | NA | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-08-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8084 |  | 0 |  | MARQUES GENERAL ENGINEERING | RIO LINDA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 921 |  | 1 |  | LIFESCAPING OUTDOORS | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 367 |  | 1 |  | HOMEOWNER | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2811 |  | 1 |  | SLC | VACAVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 458 |  | 2 |  | PINEDA LANDSCAPING | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 188 |  | 1 |  | CASCADING FALLS INC. | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-06-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | LUND CONSTRUCTION | ROSEVILLE | CA | N | Y | Yes | No | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 154 |  | 1 |  | GOMEZ LAWN & GARDEN | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CENTRAL VALLEY ENGINEERING AND ASPHALT | ROSEVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 808 |  | 1 |  | HOMEOWNER | ROSVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-07-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 93 |  | 1 |  | PACIFIC PARKS LANDSCAPING | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-05-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25 |  | 0 |  | RCI ELECTRIC DBA RAYCO | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-04-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 0 |  | LUND CONSTRUCTION | NORTH HIGHLANDS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-06-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3920 |  | 7 |  | TEICHERT CONSTRUCTION | ROCKLIN | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | INFINITY PLANNING | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 322 |  | 1 |  | PREMIER POOL | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-05-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 47 |  | 1 |  | HOMEOWNER | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2021-01-16 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5374 |  | 0 |  | LUPTIN EXCAVATION | SSACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2021-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3341 |  | 1 |  | CALIFORNIA UTILITY COMPANY | SARATOGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2021-02-01 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2226 |  | 1 |  | TEICHERT PIPELINES | SACRAMENTO | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2021-02-18 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 162 |  | 2 |  | TEICHERT PIPELINES | SACRAMENTO | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1434 |  | 1 |  | TRIFECTA CONNECTIONS LLC | EL DORADO HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 233 |  | 2 |  | GHITA UNDERGROUND ENGINEERING INC. | ROCKLIN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2021-02-03 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1626 |  | 0 |  | SIERRA VALLEY CONSTRUCTION | LINCOLN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9 |  | 2 |  | QUATTUOR CONSTRUCTION INC | YUBA CITY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2021-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 1 |  | NV COMMUNICATIONS | MCCLELLAN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2750 |  | 2 |  | GHITA UNDERGROUND ENGINEERING INC. | LINCOLN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 260 |  | 2 |  | PMG BUILDERS INC | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | ANTELOPE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 483 |  | 1 |  | TAK COMMUNICATIONS CA | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2021-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | QUEST MEDIA | ROSEVILLE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Incorrect Facility Records/Maps
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2021-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1608 |  | 1 |  | HOMEOWNER | CARMICHAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2021-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 337 |  | 1 |  | HOMEOWNER | CARMICHAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2021-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PARKER ELECTRIC | RANCHO CORDOVA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2021-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 154 |  | 0 |  | CAL WEST CONCRETE | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2021-04-29 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 551 |  | 3 |  | CAYAFAS EXCAVATING | CAMERON PARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2021-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NV COMMUNICATIONS | GARDNERVILLE | NV | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2021-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5334 |  | 1 |  | NV COMMUNICATIONS | MCCLELLAN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2021-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LITTLETON CONSTRUCTION | CITRUS HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2021-02-17 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 2 |  | TEICHERT PIPELINES | CHINO | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2021-08-12 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CEC 1 | ROCKLIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2021-11-29 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1389 |  | 4 |  | PGE | SACRAMENTO | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2021-07-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25 |  | 0 |  | SMUD | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2021-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2621 |  | 1 |  | CABLETECH | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1047 |  | 1 |  | WEBER GENERAL ENGINEERING | VACAVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WEBER GENERAL ENGINEERING | VACAVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Vacuum Equipment with Agreement | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7740 |  | 2 |  | CABLECOM | BROTHELL | WA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SACRAMENTO COUNTY WATER | ELK GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-04-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 462 |  | 0 |  | HUMPHREY PLUMBING | TURLOCK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | UNITED PAVING | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 189 |  | 1 |  | CABLECOM | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-06-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5961 |  | 2 |  | HOMEOWNER | VALLEY SPRINGS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 38 |  | 1 |  | LIFESCAPING OUTDOORS | ELK GROVE | CA | N | Y | No | No | No | No | No | No | No | Did not wait for positive response from all operators
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 26 |  | 1 |  | RADIANT SERVICES COMPANY | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-09-13 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3244 |  | 1 |  | TEICHERT PIPELINES | SACRAMENTO | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 259 |  | 1 |  | HOMEOWNER | OAK HILLS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-05-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2070 |  | 1 |  | HOMEOWNER | ELK GROVE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 73 |  | 1 |  | HOMEOWNER | ELK GROVE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2364 |  | 1 |  | HOMEOWNER | ELK GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | No | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2021-11-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 713 |  | 0 |  | MOZINGO CONSTRUCTION | OAKDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | ELVERTA | 2021-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3349 |  | 1 |  | HOMEOWNER | ELVERTA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2021-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ROJO CONSTRUCTION | ORANGEVALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2021-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1063 |  | 1 |  | HOMEOWNER | FAIR OAKS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2021-10-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 609 |  | 1 |  | HOMEOWNER | CARMICHAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LIFESCAPING OUTDOORS | FOLSOM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2021-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 162 |  | 1 |  | HOMEOWNER | FOLSOM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2021-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4882 |  | 0 |  | HOMEOWNER | FOLSOM | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2021-10-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | PRO IDEA LANDSCAPE | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2021-09-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4276 |  | 0 |  | HOMEOWNER | FOLSOM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | GALT | 2021-05-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 140 |  | 0 |  | Q&M SERVICES | FAIRFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | GALT | 2021-08-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | HOMEOWNER | LODI | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | GOLD RIVER | 2021-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 67 |  | 1 |  | THE GROWING COMPANY | RANCHO CORDOVA | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2021-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1728 |  | 1 |  | FORESITE | ELK GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2021-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3079 |  | 2 |  | SUPERIOR FENCE CONSTRUCTION AND REPAI | ROSEVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2021-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2704 |  | 2 |  | HOMEOWNER | NORTH HIGHLANDS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ORANGEVALE | 2021-07-28 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 56 |  | 4 |  | SACRAMENTO AREA SEWER DISTRICT | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ORANGEVALE | 2021-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 90 |  | 1 |  | LEGACY PLUMBING | ORANGEVALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ORANGEVALE | 2021-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3509 |  | 1 |  | HOMEOWNER | ORANGEVALE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ORANGEVALE | 2021-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1420 |  | 1 |  | HOMEOWNER | ELDORADO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ORANGEVALE | 2021-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3817 |  | 1 |  | HOMEOWNER | ORANGEVALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ORANGEVALE | 2021-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1075 |  | 1 |  | BALDONI CONSTRUCTION | NEWCASTLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible
Pacific Gas and Electric | N | SACRAMENTO | ORANGEVALE | 2021-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2771 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | RANCHO CORDOVA | 2021-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2187 |  | 1 |  | HOMEOWNER | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | RANCHO CORDOVA | 2021-01-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 13015 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | UNKNOWN HOW DAMAGE OCCURRED
Pacific Gas and Electric | N | SACRAMENTO | RANCHO CORDOVA | 2021-08-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ON SITE ENGINEERING AND ASPHALT | LOOMIS | CA | N | Y | No | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | RANCHO CORDOVA | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RAWLES ENGINEERING | FOLSOM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | RANCHO CORDOVA | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | AVAIL SERVICES INC. | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | RANCHO CORDOVA | 2021-08-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 57 |  | 1 |  | TEICHERT CONSTRUCTION | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | RIO LINDA | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | RIO LINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | RIO LINDA | 2021-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3153 |  | 2 |  | HOMEOWNER | RIO LINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 285 |  | 2 |  | MBJ CONCRETE | LINCOLN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 4 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9208 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1900 |  | 1 |  | JVM LANDSCAPE AND CONSTRUCTION | EL DORADO HILLS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-09-15 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5683 |  | 10 |  | MBS ENGINEERING CO | SAN RAMONE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-11-12 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 219 |  | 1 |  | ANVIL BUILDERS | SAN FRANCISCO | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-10-27 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PRECISION DIRECTIONAL BORING | SAUSOLITO | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-08-17 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 0 |  | ANVIL BUILDERS | SAN FRANCISCO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-08-26 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 1.25 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 60061 |  | 26 |  | DPI INC. | PLEASANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2432 |  | 1 |  | JDL LAND MGMT | ELK GROVE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 132 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 153 |  | 0 |  | CLARK & SULLIVAN BUILDERS | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SOUTHWEST GRADING | LOOMIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Facility Embedded in Concrete
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-10-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | HOMEOWNER | ROCKLIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-07-28 | Operator excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 24410 |  | 11 |  | ANVIL BUILDERS | SAN FRANCISCO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | OJEDA LAWN SERVICE | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-11-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9675 |  | 1 |  | EXPRESS SEWER & DRAIN | RANCHO CORDOVA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Installation error
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-09-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 671 |  | 0 |  | SUBTERRA | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Unmapped and unmarked
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-09-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1785 |  | 0 |  | ANVIL BUILDERS | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 4 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20393 |  | 1 |  | MARTIN BROTHERS CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5 |  | 1 |  | FENCE WORLD | SAC | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 253 |  | 1 |  | 5 STAR PLUMBING | NORTH HIGHLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1155 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-03-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2792 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 135 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ANVIL BUILDERS | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.5 | 0.3 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GUILLEN FENCE | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CITY OF SACRAMENTO | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1513 |  | 1 |  | CITY OF SACRAMENTO | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-04-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4637 |  | 4 |  | CITY OF SACRAMENTO | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 13869 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1757 |  | 1 |  | THE TRENCHLESS COMPANY | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 17023 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Farm Equipment | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | EPIC POOLS AND LANDSCAPING | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1.25 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 32 |  | 1 |  | BIONDI PAVING | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 900 |  | 0 |  | PRIORITY 1 ELECTRIC | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | Inadequate Excavation Practices
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-06-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MARQUES GENERAL ENGINEERING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 19 |  | 2 |  | SCHMITZ CONSTRUCTION | LOOMIS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-02-25 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3457 |  | 0 |  | FIBERCO INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1992 |  | 1 |  | FLOREZ PAVING | SACRAMENTO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-08-05 | Third party excavation damage | Main | Steel | Not Available | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | Other
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3178 |  | 1 |  | GREEN SOURCE CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 144 |  | 2 |  | SEA HORSE FENCING | NORTH HIGHLANDS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-03-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2138 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1745 |  | 5 |  | BENSON FENCE | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3948 |  | 1 |  | FLOREZ PAVING | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9912 |  | 1 |  | FLOREZ PAVING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6790 |  | 1 |  | FLOREZ PAVING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOMEOWNER | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-08-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-06-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1993 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25 |  | 3 |  | ROOTER HERO PLUMBING | CITRUS HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-05-10 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 2 | 60 | 44 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  | 34830 |  | 27 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | ARSON
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-02-22 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3213 |  | 1 |  | TEICHERT PIPELINES | SACRAMENTO | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3380 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-01-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6355 |  | 0 |  | CSI ENGINEERING | CARMICHAEL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 3 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9686 |  | 1 |  | NAVAJO PIPELINES | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | MARYSVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-04-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Vacuum Equipment with Agreement | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10073 |  | 1 |  | P31 ENTERPRISES | OROVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-04-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 185 |  | 1 |  | CUMMINGS | RESCUE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NAVAJO PIPELINES | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 283 |  | 1 |  | NAVAJO PIPELINE | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-07-14 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1529 |  | 1 |  | ANVIL BUILDERS | SAN FRANCISCO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-06-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1890 |  | 0 |  | ENVIRONMENTAL LANDSCAPE SOLUTIONS | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-07-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 30 |  | 0 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-01-12 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 6 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | VANGUARD CONSTRUCTION | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 189 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1845 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-04-27 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | MONZINGO CONSTRUCTION | OAKDALE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-03-29 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1012 |  | 0 |  | PG&E | SACRAMENTO | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 228 |  | 2 |  | FRANK GASSAWAY & SONS INC | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-06-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 365 |  | 1 |  | FLOREZ PAVING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-07-14 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 225 |  | 0 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-01-27 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ALVAH CONTRACTORS | SOUTH SAN FRANCISCO | CA | Y | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DEVIL MOUNTAIN LANDSCAPING AND CONSTRUCTION | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-01-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SACRAMENTO SUBURBAN WATER DISTRICT | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | EXCAVATED PRIOR TO POSITIVE CONTACT
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3210 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | G AND T FENCING | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2793 |  | 2 |  | NV COMMUNICATIONS | MCCLELLAN PARK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MONTGOMERY STRUCTURAL LIFTING | RANCHO CORDOVA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | JERICHO WRECKING | NORTH HIGHLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CABLECOM | MCCLELLAN AVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3313 |  | 0 |  | VINTAGE ROOF TILE | RIO LINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 127 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-06-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 34 |  | 1 |  | ARROW CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1377 |  | 1 |  | FIBERCO | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-01-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 35 |  | 0 |  | DOMINGO VILLANUEVA | NEWARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1897 |  | 0 |  | SUN COUNTRY BUILDERS | CARLSBAD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1678 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SUN STONE SOLAR | FAIR OAKS | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | EXCAVATED OUTSIDE OF DELINEATED AREA
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3368 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2731 |  | 1 |  | HOMEOWNER | CARMICHAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3052 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2493 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ROONEY''S PLUMBING CO | ELK GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2347 |  | 1 |  | SAC CITY ST DEPT | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-06-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 679 |  | 0 |  | HOMEOWNER | RIO LINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2021-03-23 | Third party excavation damage | Transmission Line in an HCA area | Steel | Vacuum Equipment with no Agreement | 6 | 150 | 120 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | NA | NA |  | N | Y | No | No | No | No | No | No | No | UNKNOWN
Pacific Gas and Electric | N | SAN BENITO | HOLLISTER | 2021-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 44 |  | 1 |  | LIVE-LOVE-LEAL | HOLLISTER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN BENITO | HOLLISTER | 2021-07-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 215 |  | 2 |  | J.C. GUZMAN GRADING,CONSTRUCTION | BYRON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN BENITO | HOLLISTER | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 130 |  | 0 |  | MCH ELECTRIC | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN BENITO | HOLLISTER | 2021-12-02 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 60304 |  | 53 |  | PGE | MERCED | CA | Y | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN BENITO | SAN JUAN BAUTISTA | 2021-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3071 |  | 0 |  | HOMEOWNER | SAN JUAN BATISTA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN BERNARDINO | TRONA | 2021-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5187 |  | 0 |  | SAN BERNADINO FIRE | SAN BERNADINO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | INNOVATIVE COMMUNICATIONS INC. | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-01-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 163 |  | 1 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-05-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1458 |  | 1 |  | NA | NA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-08-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2277 |  | 0 |  | KEVIN LIN CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1423 |  | 1 |  | CRATUS INC. | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3799 |  | 0 |  | EVANS BROTHERS INC. | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6939 |  | 2 |  | TREDWAY MADE INC | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-10-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 23 |  | 1 |  | ACE PLUMBING | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-05-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 192 |  | 1 |  | CRAFTSMAN LANDSCAPES | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2539 |  | 1 |  | M SQUARED CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 161 |  | 1 |  | SAN FRANCISCO SEWER DEPARTMENT | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  | 1 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1939 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 203 |  | 1 |  | KENNEALLY CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-04-09 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 172 |  | 1 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | Vehicle Impact
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 4 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PRECISION ENGINERING | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 9.2 | 7 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 73 |  | 1 |  | SYSTEM PAVERS | FREMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2407 |  | 1 |  | SF WATER DEPT | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3386 |  | 1 |  | NTK CONSTRUCTION | SAN FRANCISCO CA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-02-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 11 | 9 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3601 |  | 0 |  | HARTY PIPELINES | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.43 | 0.36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3173 |  | 1 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ESQUIVEL GRADING AND PAVING | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 163 |  | 1 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-09-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1860 |  | 1 |  | TONY GARDENING SERVICE | SAN BRUNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | J FLORES CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 4 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14802 |  | 1 |  | PRECISION ENG | SAN FRANCISCO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 68 |  | 1 |  | JDB & SONS CONSTRUCTION INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-08-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CRATUS INC | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-02-24 | Operator excavation damage | Main | Steel | Hand Tools | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 24048 |  | 4 |  | TTR SUBSTATION | FRESNO | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | R SANTOS CONST | RODEO CA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NORWOOD CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1714 |  | 1 |  | SF WATER DEPARTMENT | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-11-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 0.5 | 0.3 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1048 |  | 1 |  | PRECISION ENG | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | No | No | No | No | Facility was not located or marked
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2796 |  | 1 |  | MITCHELL ENGINEERING | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 371 |  | 1 |  | FASTNET ENGINEERING & CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-06-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1581 |  | 0 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 50 |  | 1 |  | J FLORES CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7412 |  | 1 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2021-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2216 |  | 3 |  | INFINITY PLUMBING AND ROOTER. | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | INADEQUATE MARKING LOCATOR ERROR
Pacific Gas and Electric | N | SAN JOAQUIN | CLEMENTS | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2040 |  | 2 |  | HOMEOWNER | CLEMENTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | ESCALON | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1173 |  | 1 |  | GUEVARA CONCRETE INC | ESCALON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Excavated outside delineations
Pacific Gas and Electric | N | SAN JOAQUIN | ESCALON | 2021-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | ESCALON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LATHROP | 2021-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1193 |  | 0 |  | IMPERIAL ELECTRIC SERVICE | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | LATHROP | 2021-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2275 |  | 0 |  | PACIFIC COAST LANDSCAPE | BRENTWOOD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LATHROP | 2021-04-15 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SMITH & DENISON CONSTRUCTION | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 182 |  | 2 |  | COUNTY OF SAN JOAQUIN | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | Vehicle impact
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2021-09-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8768 |  | 10 |  | WULFF ELECTRIC | VACAVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2021-09-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3054 |  | 1 |  | HOMEOWNER | LODI | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2021-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 45 |  | 1 |  | CRYSTAL PLUMBING | LODI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2021-07-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 148 |  | 0 |  | AGAVE BUILDERS LLC | ELK GROVE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2021-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2339 |  | 8 |  | GOES LANDSCAPING | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2021-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 240 |  | 2 |  | HOMEOWNER | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2021-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 261 |  | 2 |  | SEFNCO | LATHROP | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1548 |  | 0 |  | ERGEON INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2021-07-15 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4967 |  | 1 |  | GRIFFIN SOIL GROUP | STOCKTON | CA | N | Y | Yes | Yes | No | Yes | No | No | No | Excavated Prior to Positive Response From All Utilities Noted on Ticket
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2021-02-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5555 |  | 0 |  | UNITED PAVING | CERES | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2021-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 49 |  | 2 |  | HOMEOWNER | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2021-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 61 |  | 1 |  | HOMEOWNER | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2021-03-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1569 |  | 1 |  | HOMEOWNER | RIPON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2021-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 226 |  | 5 |  | SEFNCO | LATHROP | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2021-07-01 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 157 |  | 0 |  | JAVELIN UTILITY | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2021-03-29 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2313 |  | 0 |  | RUBICON INC | PLACERVILE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2021-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 215 |  | 1 |  | RAYMUS DEVELOPEMENT | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MORADA | 2021-08-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 159 |  | 1 |  | MHK CONSTRUCTION | DENAIR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MORADA | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1849 |  | 0 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MORADA | 2021-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 162 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | RIPON | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HENSEN GENERAL ENGINEERING | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | RIPON | 2021-05-28 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | D A WOOD CONSTRUCTION | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | RIPON | 2021-01-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 208 |  | 1 |  | HOMEOWNER | RIPON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 0 |  | RC PLUMBING | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-08-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 215 |  | 0 |  | LANDSCAPE DEVELOPMENT | VALENCIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.43 | 0.33 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 467 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 146 |  | 1 |  | HOMEOWNER | MORENO VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-07-20 | Operator excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MICHELS PACIFIC ENERGY | BROWNSVILLE | WI | Y | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Incorrect Facility Records/Maps
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 142 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 19 |  | 3 |  | SAGE ELECTRIC COMPANEY | ROCKLIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 565 |  | 2 |  | A1 CONSTRUCTION GENERAL ENGINEERING INC. | CASTRO VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-09-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 752 |  | 1 |  | KNIFE RIVER | STOCKTON | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Incorrect Facility Records/Maps
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 445 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-09-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 997 |  | 1 |  | KNIFE RIVER | STOCKTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2120 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 913 |  | 1 |  | ROTO-ROOTER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 118 |  | 0 |  | A B ENVIRONMENTAL | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.43 | 0.31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1095 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2660 |  | 1 |  | ECOFORCE SOLUTIONS | SANTA ANA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 146 |  | 0 |  | AAA BACKHOE | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-07-14 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 60 |  | 1 |  | VULCAN | FRESNO | CA | Y | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-01-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5725 |  | 13 |  | G&N CONSTRUCTION | STOCKTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 900 |  | 4 |  | NORYMAR MAINTENANCE INC | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 193 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25 |  | 1 |  | PACIFIC EXCAVATION | ELK GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-02-24 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2248 |  | 2 |  | PG&E | STOCKTON | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1064 |  | 1 |  | PINASCO PLUMBING | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 222 |  | 3 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-05-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 19 |  | 2 |  | LANDSCAPE DEVELOPMENT | GOLD RIVER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.43 | 0.31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 215 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-01-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3159 |  | 0 |  | OCHOA BACKHOE SERVICES | LINCOLN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1643 |  | 6 |  | PREFERRED PLUMBING | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2038 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2021-09-28 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 859 |  | 5 |  | HOMEOWNER | STOCKTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect Facility Records/Maps
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2021-09-25 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7535 |  | 2 |  | GALVAO SONS INC | TRACY | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2021-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2806 |  | 2 |  | HOMEOWNER | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 161 |  | 2 |  | HOMEOWNER | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1348 |  | 1 |  | BOCKMAN & WOODY ELECTRIC COMPANY INC. | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2021-10-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 323 |  | 0 |  | IKE''S LANDSCAPE | DAVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2021-06-23 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 28 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PG&E GAS | MODESTO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2021-07-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2771 |  | 0 |  | THEIS ENGINEERING INC. | FOLSOM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect Facility Records / Maps
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 244 |  | 0 |  | JIMENEZ & SONS CONSTR | STOCKTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | WOODBRIDGE | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2476 |  | 1 |  | HOMEOWNER | LODI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | ATHERTON | 2021-03-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5369 |  | 1 |  | IN AND OUT PLUMBING | SOUTH SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 155 |  | 1 |  | HOCKER CONSTRUCTION | BURLINGAME | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2021-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1443 |  | 1 |  | MARSH FENCE & DECK | SAN BRUNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2021-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7989 |  | 1 |  | FINCON | HALFMOON BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2021-08-31 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | VETERAN PIPELINE CONSTRUCTION | BENICIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2021-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 244 |  | 0 |  | PAUL FITZGERALD LANDSCAPES INC | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2021-03-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5444 |  | 0 |  | RG DEVELOPMENTS INC | BURLINGAME | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2021-12-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1836 |  | 1 |  | HOMESCAPENOW | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2021-05-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 43 |  | 0 |  | BAY BUILDERS AND REMODLEING | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2020 |  | 0 |  | TESTING ENGINERS | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2021-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Directional Drilling | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5373 |  | 1 |  | SIERRA TRAFFIC MARKINGS, INC | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | DALY CITY | 2021-06-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1976 |  | 0 |  | MCH ELECTRIC | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILURE TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN MATEO | DALY CITY | 2021-01-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TENNYSON ELECTRIC | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | DALY CITY | 2021-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 132 |  | 1 |  | HOMEOWNER | DALY CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | EAST PALO ALTO | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 196 |  | 0 |  | TEICHERT CONSTRUCTION | PLEASANTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | EAST PALO ALTO | 2021-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2188 |  | 1 |  | TEICHERT PIPELINES | PLEASANTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | EL GRANADA | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 0 |  | MICHELS PACIFIC ENERGY INC | SAN CARLOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2021-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 743 |  | 2 |  | ERGEON FENCING | PALO ALTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 314 |  | 4 |  | GAIA LANDSCAPE LABORER | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2021-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 135 |  | 1 |  | CARRANZA GARDENING | FOSTER CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2021-06-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2513 |  | 1 |  | SALAS LANDSCAPE | HOLLISTER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2021-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 38 |  | 1 |  | CLG CONSTRUCTION | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2021-03-10 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 1.25 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6941 |  | 23 |  | OVERAA CONSTRUCTION | RICHMOND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | HALF MOON BAY | 2021-10-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | HALF MOON BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HALF MOON BAY | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 175 |  | 1 |  | HOMEOWNER | HALF MOON BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | HALF MOON BAY | 2021-07-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 286 |  | 1 |  | TIM POND CONSTRUCTION | HALFMOON BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2021-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1318 |  | 1 |  | HOMEOWNER | HILLSBOROUGH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2021-05-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 45 |  | 1 |  | GARY POLLACK CONSTRUCTION &EXCAVATION | WOODSIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 313 |  | 1 |  | RG DEVELOPMENTS | HILLSBOROUGH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2777 |  | 1 |  | DURHAM FENCE INC | MILLBRAE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2021-10-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | CAMPBELL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2021-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 503 |  | 0 |  | BABEL CONSTRUCTION | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2021-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2378 |  | 1 |  | DE LA VEGA CONSTRUCTION | BURLINGAME | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2021-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 59 |  | 1 |  | ST FRANCIS ELECTRIC | RWC | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 1.25 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CAMPANELLA CORP | HAYWARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Mapping error
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2140 |  | 1 |  | BAYSHORE PLUMBING | REDWOOD CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1127 |  | 0 |  | URBANSCAPES | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2021-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1962 |  | 1 |  | SWIMMING POOL PERFECTIONS | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2021-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 54 |  | 1 |  | A GOOD PLUMBER | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 214 |  | 1 |  | CK WATER SYSTEM AND LANDSCAPE | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2021-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2109 |  | 1 |  | OSCAR GARDNER | MENLO PARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MILLBRAE | 2021-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2714 |  | 1 |  | HOMEOWNER | MILLBRAE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MILLBRAE | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1243 |  | 0 |  | DISCOUNT PLUMBING ROOTER INC. | BURLINGAME | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MILLBRAE | 2021-03-17 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 613 |  | 1 |  | VETERANS PIPELINE CONSTRUCTIO | BENICIA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MILLBRAE | 2021-09-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3496 |  | 1 |  | CALIFORNIA UTILITY COMPANY | SARATOGA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Locator error
Pacific Gas and Electric | N | SAN MATEO | MILLBRAE | 2021-08-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10754 |  | 0 |  | DISCOUNT PLUMBING ROOTER INC. | BURLINGAME | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SAN MATEO | MONTARA | 2021-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5 |  | 1 |  | HOMEOWNER | HALF MOON BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MOSS BEACH | 2021-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2631 |  | 1 |  | SIMMS PLUMBING AND HEATING | PASCADERO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MOSS BEACH | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12 |  | 1 |  | HOMEOWNER | CORTE MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MOSS BEACH | 2021-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1149 |  | 0 |  | ANDREINI BROTHERS CO. | HALFMOON BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | PACIFICA | 2021-10-15 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | EXPRESS PLUMBING | SAN MATEO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | SAN MATEO | PACIFICA | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GARDEN ROUTE COMPANY | SOUTH SAN FRANCISCO | CA | N | Y | Yes | No | No | Yes | No | Yes | No | Locator error
Pacific Gas and Electric | N | SAN MATEO | PORTOLA VALLEY | 2021-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | PORTOLA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | PORTOLA VALLEY | 2021-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1553 |  | 1 |  | HOMEOWNER | PORTOLA VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | PORTOLA VALLEY | 2021-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1075 |  | 1 |  | GREEN ORIGINS LANDSCAPING INC | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-12-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 609 |  | 1 |  | WEST VALLEY CONSTRUCTION | REDWOOD CITY | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1197 |  | 0 |  | VMP CONCRETE INC | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CASEY CONSTRUCTION | EMERALD HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4373 |  | 1 |  | CASEY CONSTRUCTION | EMERALD HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3010 |  | 1 |  | EG CONCRETE | REDWOOD CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-04-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1458 |  | 0 |  | CASEY CONSTRUCTION | EMERALD HILLS | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 98 |  | 1 |  | CASTLE PLUMBING & ROOTER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 54 |  | 1 |  | HOMEOWNER | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2800 |  | 2 |  | GEERS EXCAVATION | SAN JOSE | CA | N | Y | Yes | No | No | No | No | No | No | FAILED TO DELINEATE JOB SITE
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14497 |  | 0 |  | CASEY CONSTRUCTION | EMERALD HILLS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-01-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1468 |  | 0 |  | CASEY CONSTRUCTION | EMARALD HILLS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 173 |  | 1 |  | ALL FENCE COMPANY | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-04-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 418 |  | 0 |  | IDB ENTERPRICE INC | TARZANA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-03-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1050 |  | 1 |  | CASEY CONSTRUCTION | EMERALD HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 19285 |  | 1 |  | HE TURTLE LANDSCAPE | REDWOOD CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2859 |  | 1 |  | HOMEOWNER | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 1 |  | CASEY CONSTRUCTION | EMERALD HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-07-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 59 |  | 0 |  | M.S. CONSTRUCTION | GILROY | CA | N | Y | Yes | Yes | Yes | No | No | No | No | Failed to Expose Facility with hand tools
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2021-12-14 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5167 |  | 7 |  | WEST VALLEY CONSTRUCTION | REDWOOD CITY | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2021-06-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1431 |  | 2 |  | SMITH & DENISON CONSTRUCTION | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2262 |  | 1 |  | O''GRADY PAVING | MOUNTAIN VIEW,CA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2021-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2208 |  | 0 |  | B K CONSTRUCTION | FOSTER CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2021-03-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1536 |  | 2 |  | REDGWICK CONSTRUCTION | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2021-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1469 |  | 1 |  | EXTERIOR PAVERS DESIGNS INC | REDWOOD CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2021-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3531 |  | 1 |  | SCENIC SCAPES INC | SAN CARLOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2021-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 180 |  | 1 |  | ROTO-ROOTER | EAST PALO ALTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2021-06-25 | Third party excavation damage | Main | Steel | Hand Tools | 1.25 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 737 |  | 0 |  | HOMEOWNER | SAN CARLOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 201 |  | 2 |  | IDEAL ENGINEERING | BURLINGAME | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2021-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 302 |  | 0 |  | M&G HAULING | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2021-04-13 | Third party excavation damage | Main | Steel | Augur | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 50 |  | 1 |  | RHINO''S GENERAL CONSTRUCTION | REDWOOD CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2021-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2411 |  | 0 |  | ALFARO ENGINEERING INC | SAN MATEO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2021-07-14 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 2 | 60 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 277 |  | 0 |  | HOMEOWNER | SAN CARLOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2021-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1019 |  | 1 |  | HOMEOWNER | SAN MATEO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2021-08-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1836 |  | 1 |  | LINDSTROM CO | SAN MATEO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2021-01-11 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 163 |  | 0 |  | W BRADLEY ELECTRIC | NOVATO CA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2021-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 59 |  | 0 |  | BAY AREA POOLS | BURLINGAME | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 195 |  | 1 |  | INTERSTATE GRADING AND PAVING INC | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2021-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 38 |  | 1 |  | CASTRO HOME BUILDER | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2021-08-26 | Operator excavation damage | Main | Steel | Miscellaneous/Other | 2 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 17106 |  | 0 |  | CONCRETE DEMO WORKS | SAN JOSE | CA | Y | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | TURNAROUND COMMUNICATIONS INC | MARTINEZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2021-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 155 |  | 2 |  | ZLC CORP | CONCORD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SOUTH SAN FRANCISCO | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2452 |  | 1 |  | HOMEOWNER | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SOUTH SAN FRANCISCO | 2021-03-12 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 16 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4709 |  | 9 |  | EVANS BROTHERS INC | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SOUTH SAN FRANCISCO | 2021-08-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 10 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1948 |  | 0 |  | WONG ELECTRIC INC. | PALO ALTO | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN MATEO | SOUTH SAN FRANCISCO | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ESCON BUILDERS | UNION CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SOUTH SAN FRANCISCO | 2021-01-04 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 50 | 46 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | SOUTH SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SAN MATEO | SOUTH SAN FRANCISCO | 2021-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1.25 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9409 |  | 0 |  | DOLAN CONCRETE | SANTA CLARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | WEST MENLO PARK | 2021-07-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 373 |  | 2 |  | GEER EXCAVAVATOR INC | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | WEST MENLO PARK | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1477 |  | 1 |  | ALL FENCE COMPANY | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | WOODSIDE | 2021-08-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2090 |  | 1 |  | ANSHUTZ LANDSCAPING | GILROY CA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | WOODSIDE | 2021-08-16 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4830 |  | 1 |  | WEST VALLEY | REDWOOD CITY | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY COULD NOT BE FOUND OR LOCATED
Pacific Gas and Electric | N | SAN MATEO | WOODSIDE | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1825 |  | 0 |  | NEXT LEVEL NETWORKS | SUNNYVALE. CA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | WOODSIDE | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NEXT LEVEL NETWORKS | SUNNYVALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | WOODSIDE | 2021-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | WOODSIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | WOODSIDE | 2021-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 43 |  | 1 |  | SJC CONCRETE CONSTRUCTION | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | CAMPBELL | 2021-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 185 |  | 0 |  | HARBOUR CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | CAMPBELL | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1527 |  | 0 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2021-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 761 |  | 1 |  | GS HOMEBUILDER | CUPERTINO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15903 |  | 0 |  | CALIFORNIA UTILITY COMPANY | SARATOGA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2021-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9547 |  | 0 |  | CALIFORNIA UTILITY COMPANY | SARATOGA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CALIFORNIA UTILITY COMPANY | LOS GATOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | GILROY | 2021-07-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 187 |  | 1 |  | MOUNTAIN CASCADE | LIVERMORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SANTA CLARA | GILROY | 2021-09-15 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 3 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27854 |  | 0 |  | DALEO INC. | GILROY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Mapping error
Pacific Gas and Electric | N | SANTA CLARA | GILROY | 2021-07-26 | Operator excavation damage | Main | Polyethylene Pipe | Vacuum Equipment with Agreement | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5232 |  | 4 |  | DALEO INC. | GILROY | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 226 |  | 1 |  | HOMEOWNER | LOS ALTOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS | 2021-08-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 722 |  | 1 |  | HOMEOWNER | PALO ALTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS HILLS | 2021-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 528 |  | 1 |  | SITEWORKS LANDSCAPE | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS HILLS | 2021-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1794 |  | 1 |  | POST AND TRELLIS | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS HILLS | 2021-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 729 |  | 1 |  | TOVAR | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2021-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2475 |  | 1 |  | HOMEOWNER | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2021-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | BRW CONSTRUCTION | NA |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 22922 |  | 3 |  | OSCAR''S EXPERT TREE SERVICE | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LEWIS & TIBBITS | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 968 |  | 1 |  | TERRY MECHNICAL | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4367 |  | 0 |  | TECHCON | GILROY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2021-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 465 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2021-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 891 |  | 1 |  | JR CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2021-06-18 | Third party excavation damage | Main | Steel | Boring Equipment | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 41046 |  | 72 |  | ACCU BORE DRILLING | BENICIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2021-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1566 |  | 1 |  | HOMEOWNER | LOS GATOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2021-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2466 |  | 1 |  | ENGINEER SOIL REPAIR | WALNUT CREEK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2021-01-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2837 |  | 0 |  | MOUNTAIN CASCADE INC | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4929 |  | 1 |  | MCGUIRE & HESTER | ALAMEDA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2021-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 895 |  | 2 |  | EXPRESS CONCRETE DESIGN | SAN MARTIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2021-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 215 |  | 0 |  | BAY AREA ASPHALT & CEMENT WORKS | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MONTE SERENO | 2021-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 22 |  | 1 |  | HOMEOWNER | LOS GATOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2021-06-24 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 1.25 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5272 |  | 5 |  | HOMEOWNER | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2021-06-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9318 |  | 4 |  | HOMEOWNER | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2021-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1672 |  | 1 |  | HOMEOWNER | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2021-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | LOS BANOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 207 |  | 1 |  | REDGWICK CONSTRUCTION | OAKLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2021-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 325 |  | 0 |  | HUDSON EXCAVATION | BRENTWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Failed to expose facility with hand tools
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2021-08-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 134 |  | 0 |  | FLOWRITE | GILROY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Did not wait for positive response from all operators
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2021-01-06 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | LEWIS & TIBBITS | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2021-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 491 |  | 0 |  | MODS KITCHEN | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2021-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 372 |  | 2 |  | COASTAL LUMBER | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2021-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CORAL POOL AND SPA | CAMPBELL | CA | N | Y | Yes | No | Yes | Yes | No | No | No | Excavated outside delineated area
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2021-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1805 |  | 4 |  | TRENCH FREE | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2021-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 94 |  | 1 |  | ATR LANDSCAPE | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PROCON CONCRETE | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GALANTE BROS. GENERAL ENGINEERING | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 252 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WESTERN GENERAL CONSTRUCTION INC. | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1359 |  | 1 |  | AB/JDD PLUMBING HEATING | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | A N CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-06-24 | Third party excavation damage | Main | Steel | Hand Tools | 4 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 22937 |  | 0 |  | STEVE P. RADOS INC | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 58 |  | 2 |  | STEVE P RADOS INC | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SIMPLY GREEN PLUMBING | LOS GATOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-01-08 | Third party excavation damage | Main | Steel | Augur | 2 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SURESITE COMMUNICATIONS | NA | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-07-06 | Operator excavation damage | Main | Steel | Trencher | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CAL WEST CONCRETE | WOODLAND | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3823 |  | 1 |  | ONE DAY REPIPE | SAN JOSE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | BHOGEL BROTHERS CONSTRUCTION | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | TECHCON | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-02-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 323 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 413 |  | 0 |  | DARRINS TRACTOR SERVICE | PACIFICA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 268 |  | 1 |  | TECHCON | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3988 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-04-15 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2125 |  | 2 |  | LEWIS AND TIBBITS | SAN JOSE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 244 |  | 1 |  | APPIAN ENGINEERING | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-06-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4166 |  | 100 |  | WEST VALLEY CONSTRUCTION | CAMPBELL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1504 |  | 1 |  | MERAS GROUP | LENEXA | KS | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-03-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1211 |  | 1 |  | TJC HOME BUILDER | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 289 |  | 2 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1408 |  | 0 |  | N V COMMUNICATIONS | GARDNERVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3382 |  | 2 |  | ALWAYS PAVING | NEWARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-04-29 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WEST VALLEY CONSTRUCTION | CAMPBELL | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-07-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 233 |  | 12 |  | DATALINX COMMUNICATION | LANCASTER | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-06-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 805 |  | 1 |  | BENNYS TREE AND FENCING SERVICE | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1506 |  | 2 |  | BAY AREA TRENCHLESS | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 525 |  | 1 |  | LOMBARDO DIAMOND CORE DRILLING | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CALIFORNIA UTILITY COMPANY | LOS GATOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-09-21 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 3 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10564 |  | 0 |  | ELECTRIC TECH CONSTRUCTION | CONCORD | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2099 |  | 1 |  | WEST VALLEY CONSTRUCTION | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1714 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3871 |  | 0 |  | CALIFORNIA UTILITY COMPANY | LOS GATOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3342 |  | 1 |  | MEZA''S FENCE | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3212 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3856 |  | 2 |  | CABLECOM LLC | BOTHELL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 233 |  | 2 |  | SILICON VALLEY BUILDERS GROUP | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-03-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1693 |  | 0 |  | STARZ TELECOM | MILPITAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-02-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 216 |  | 0 |  | BLACKWELL GENERAL ENGINEERING INC | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | No | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1228 |  | 1 |  | JOHN CONSTRUCTION | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1332 |  | 2 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 43 |  | 9 |  | CITY OF SAN JOSE DOT(SEWER DEPARTMENT | SAN JOSE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 902 |  | 4 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 0.43 | 0.33 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 872 |  | 1 |  | CITY OF SAN JOSE DOT | SAN JOSE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15325 |  | 0 |  | CALIFORNIA UTILITY COMPANY | LOS GATOS | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2021-01-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SANSEI GARDENS | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2021-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.43 | 0.34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SMART PLUMBING INC | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12726 |  | 1 |  | PACWEST CONSTRUCTION | CHOWCHILLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2021-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 820 |  | 0 |  | INLAND TIRE | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Truck drove over exposed stub
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2021-10-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 311 |  | 0 |  | CITY OF SANTA CLARA | SANTA CLARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2563 |  | 0 |  | CALFORNIA UTILITY COMPANY | LOS GATOS | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2021-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 47 |  | 1 |  | IRISH CONSTRUCTION | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2021-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 115 |  | 1 |  | FURLO & FURLO | LOS GATOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2021-06-07 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DALEO CONSTRUCTION | GILROY | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2021-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 823 |  | 0 |  | MCTIGHE LANDSCAPING | SARATOGA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2021-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GOGO ROOTER | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2021-07-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7 |  | 0 |  | MISSION CITY CONSTRUCTION | SANTA CLARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2021-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2147 |  | 0 |  | MT SQUARED | MILPITAS | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2021-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 5 |  | FREEDOM UNDERGROUND PLUMBING | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2021-10-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 287 |  | 0 |  | MANIGLIA LANDSCAPE | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2021-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | DEL SAL FRAMING | NA |  | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2021-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14218 |  | 4 |  | GEER EXCAVATING | SAN JOSE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 878 |  | 1 |  | HOMEOWNER | APTOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2021-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 759 |  | 2 |  | TINO''S PLUMBING | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2021-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 672 |  | 0 |  | TESTORFF CONSTRUCTION | APTOS | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2021-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 331 |  | 1 |  | JERRY GLOVER CONSTRUCTION | APTOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2021-04-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 78 |  | 18 |  | SOQUEL CREEK WATER DISTRICT | SOQUEL | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 209 |  | 1 |  | LINDEX CONSTRUCTION | SOQUEL | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2021-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PFISTER CONSTRUCTION | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | APTOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2021-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 658 |  | 5 |  | PACIFIC UNDERGROUND CONSTRUCTION | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2021-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PACIFIC UNDERGROUND CONSTRUCTION | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 832 |  | 1 |  | SANCHEZ LANDSCAPE SERVICES | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | BEN LOMOND | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 675 |  | 1 |  | HOMEOWNER | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | BOULDER CREEK | 2021-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | OULDER CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | BOULDER CREEK | 2021-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1582 |  | 1 |  | HOMEOWNER | BOULDER CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | CAPITOLA | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 30 | 27 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LANDSCAPE 4U INC | CAPITOLA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | CORRALITOS | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 234 |  | 1 |  | CCOI | AROMAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | FELTON | 2021-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DAVEY TREE | SOQUEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 71 |  | 2 |  | DIAMOND D CONCRETE | CAPITOLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2021-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1036 |  | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2021-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2021-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Directional Drilling | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DURDEN CONSTRUCTION | SAN JUAN BAUTISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2021-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 2 | 60 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11121 |  | 1 |  | ECO- FLOW PLUMBING | SANTA CRUZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DETERIORATED OR FRAGILE FACILITY
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2021-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2021-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1169 |  | 2 |  | BELLOWS PLUMBING | SOQUEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2021-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MCGUIRE HESTER & HESTER | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2021-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1011 |  | 1 |  | HUNT CONSTRUCTION | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1361 |  | 1 |  | GREEN STATE ELECTRIC | SCOTTS VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2021-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 590 |  | 2 |  | ANDERSON PACIFIC ENGINEERING CONST. | SANTA CLARA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2242 |  | 1 |  | CALYPSO CONSTRUCTION | APTOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2021-03-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 645 |  | 1 |  | HOMEOWNER | SASNTA CRUZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SCOTTS VALLEY | 2021-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 115 |  | 1 |  | HOMEOWNER | SCOTTS VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SCOTTS VALLEY | 2021-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 772 |  | 2 |  | HOMEOWNER | SCOTTS VALLEY | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SCOTTS VALLEY | 2021-10-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 260 |  | 0 |  | MARKETSHARE | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SOQUEL | 2021-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 6 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PACIFIC UNDERGROUND CONSTRUCTION | SAN JOSE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SANTA CRUZ | SOQUEL | 2021-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DUNCAN PLUMBING | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | TWIN LAKES | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 483 |  | 1 |  | PROFESSIONAL LANDSCAPING LLC | FELTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2021-11-19 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3844 |  | 4 |  | MCKIM CORPORATION | GILROY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2021-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 37494 |  | 0 |  | HOMEOWNER | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 107 |  | 1 |  | HOMEOWNER | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2021-04-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 20 |  | IRON MOUNTAIN GENERAL ENG | REDDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SHASTA | REDDING | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 108 |  | 1 |  | GARDNER PLUMBING | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1034 |  | 0 |  | EDDIE AXNER EXCAVATING | REDDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SHASTA | REDDING | 2021-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 563 |  | 0 |  | LIVING STONE ELECTRIC | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 438 |  | 1 |  | HOMEOWNER | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 979 |  | 1 |  | HOMEOWNER | REDDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SOLANO | BENICIA | 2021-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1402 |  | 0 |  | MACY''S LAWN AND GARDEN SERVICE | FORT BRAGG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | BENICIA | 2021-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | VINCE''S LANDSCAPING | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | BENICIA | 2021-04-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3870 |  | 5 |  | ROBERT CARTER | VALLEJO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SOLANO | BENICIA | 2021-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1086 |  | 1 |  | HOMEOWNER | BENICIA | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SOLANO | BENICIA | 2021-08-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | BENICIA | 2021-01-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | G&G DECK AND FENCING | PLEASANT HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | BENICIA | 2021-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2104 |  | 1 |  | HOMEOWNER | BENICIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | DIXON | 2021-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2348 |  | 0 |  | CONCRETUM OPERIS INC | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SOLANO | DIXON | 2021-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3629 |  | 0 |  | HOMEOWNER | DIXON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2021-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 668 |  | 1 |  | HOMEOWNER | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2021-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 863 |  | 1 |  | CAVALRY CONSTRUCTION SERVICES INC. | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2021-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 234 |  | 1 |  | HOMEOWNER | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2021-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1162 |  | 1 |  | PACIFIC COAST CONCRETE | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1721 |  | 1 |  | HOMEOWNER | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2021-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BRYAN MACMILLAN | BENECIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2021-06-16 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4499 |  | 0 |  | MIKE BROWN ELECTRIC CO. | COTATI | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2021-08-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | KDW | LIVERMORE CALIFORNIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2021-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 242 |  | 2 |  | BENICIA PLUMBING | BENICIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2021-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6116 |  | 16 |  | QUAIL RUN APARTMENT LP JASON ALLEN | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2021-12-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3885 |  | 0 |  | CULTIVATED LANDSCAPE MANAGEMENT | NORTH HIGHLANDS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2021-10-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6205 |  | 0 |  | MARQUES GENERAL ENGINEERING | RIO LINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2021-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3247 |  | 1 |  | HOMEOWNER | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2021-05-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 208 |  | 1 |  | HOMEOWNER | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2021-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4193 |  | 1 |  | HOMEOWNER | ALAMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2021-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 1 |  | BECERRAS LANDSCAPING LLC | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2021-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 557 |  | 2 |  | HOMEOWNER | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2021-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1553 |  | 1 |  | MORALES MAINTENANCE | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | CLOVERDALE | 2021-10-21 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 271 |  | 1 |  | UNDERGROUND CONSTRUCTION COMPANY | BENICIA | CA | Y | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | GEYSERVILLE | 2021-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 317 |  | 1 |  | HOMEOWNER | GEYSERVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | GLEN ELLEN | 2021-01-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 293 |  | 2 |  | LEAK DETECTION PROS. | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2021-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ENGELKE CONSTRUCTION | HEALDSBURG | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2021-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ENGELKE CONSTRUCTION | HEALDSBURG | CA | N | Y | Yes | No | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3702 |  | 1 |  | ENGELKE CONSTRUCTION INC | HEALDSBURG | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 979 |  | 1 |  | PIAZZA CONSTRUCTION | PETALUMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2021-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | HEALDSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2021-02-02 | Operator excavation damage | Main | Steel | Miscellaneous/Other | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 269 |  | 3 |  | HENKELS AND MCCOY | SACREMENTO | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2021-03-25 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 587 |  | 20 |  | HENKELS AND MCCOY | HEALDSBURG | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2021-08-25 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5 |  | 0 |  | HENKELS & MCCOY | POMONA | CA | Y | Y | Yes | No | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2021-08-18 | Operator excavation damage | Main | Steel | Trencher | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8307 |  | 1 |  | HENKELS & MCCOY | POMONA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2021-06-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALLEN LANDSCAPING INC. | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PENNGROVE | 2021-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 158 |  | 0 |  | HARRIS COMPANY | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2021-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 536 |  | 1 |  | W R FORDE | RICHMOND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2021-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 857 |  | 1 |  | GARNEY PACIFIC | KANSAS CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2021-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 31 |  | 1 |  | HOMEOWNER | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2021-11-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 271 |  | 1 |  | HOMEOWNER | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2021-12-10 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1111 |  | 0 |  | HOMEOWNER | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2021-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 683 |  | 0 |  | HOMEOWNER | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2021-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 725 |  | 1 |  | W R FORDE ASSOCIATES | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2021-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2060 |  | 1 |  | HOMEOWNER | PETALUMA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6692 |  | 3 |  | W R FORDE ASSOCIATES | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2021-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 269 |  | 0 |  | HOMEOWNER | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2021-08-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3750 |  | 0 |  | GRANGER CONSTRUCTION | TRACY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2021-07-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 303 |  | 0 |  | CALIFORNIA RETAINING WALLS | BENICIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | ROHNERT PARK | 2021-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 630 |  | 3 |  | TURN AROUND COMMUNICATIONS | WEST COVINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2004 |  | 2 |  | REDWOOD RESIDENTIAL FENCE CO | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12745 |  | 2 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6640 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-04-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 426 |  | 1 |  | SERRES CORPORATION | SONOMA | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 323 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1047 |  | 1 |  | A&C NOMA CONSTRUCTION | COTATI | CA | N | Y | Yes | Yes | No | No | No | No | No | Excavated Prior to Receiving a Positive Response From All Utilities
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2163 |  | 0 |  | THOR ELECTRIC | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 336 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5337 |  | 1 |  | GO PLUMB | FORESTVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2987 |  | 1 |  | ERGEON INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Directional Drilling | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9 |  | 1 |  | MCKUIN PIPELINE | HOLLISTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-12-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2893 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 132 |  | 2 |  | NORTHWEST GENERAL ENGINEERING | SANTA ROSA | CA | N | Y | Yes | No | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-02-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4778 |  | 1 |  | CITY OF SANTA ROSA | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-06-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1799 |  | 1 |  | RCX INC | WINDSOR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 108 |  | 0 |  | REPUBLIC SERVICES | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-03-31 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 245 |  | 1 |  | SYBLON REID CL#758610 | FOLSOM | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2101 |  | 1 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-06-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1170 |  | 1 |  | SIKES ASPHALT | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1479 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 269 |  | 20 |  | RCX INC | WINDSOR | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1399 |  | 1 |  | ENVOY CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 938 |  | 1 |  | REDWOOD RESIDENTIAL FENCE | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 215 |  | 2 |  | NORTHWEST GENERAL ENGINEERING | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3242 |  | 6 |  | SONIC TELECOM | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2021-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 726 |  | 1 |  | SONIC TELECOM | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1597 |  | 1 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2021-03-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2340 |  | 1 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2021-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 2 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 173 |  | 0 |  | CULVERT OPPS | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2021-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 998 |  | 1 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2021-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 209 |  | 1 |  | HOMEOWNER | SEBASTOPOL | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2021-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1545 |  | 1 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2021-10-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 141 |  | 1 |  | HOMEOWNER | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2021-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1340 |  | 0 |  | DAVID JAMES BACKHOE | GRATON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SONOMA | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 104 |  | 1 |  | HOMEOWNER | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2021-06-15 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2178 |  | 2 |  | ARB INC | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | PIPE EMBEDDED IN CONCRETE PORTION OF ROADWAY
Pacific Gas and Electric | N | SONOMA | SONOMA | 2021-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2356 |  | 0 |  | GREENER EXCAVATIONS | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SONOMA | 2021-04-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 208 |  | 2 |  | APE''S PLUMBING | BOYES HOT SPRINGS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2021-09-13 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2563 |  | 0 |  | VETERAN PIPELINE CONSTRUCTION | BENICIA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | No | Locator Error Mismark
Pacific Gas and Electric | N | SONOMA | SONOMA | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 2 |  | HOMEOWNER | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2021-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 316 |  | 1 |  | ST FRANCIS ELECTRIC | SAN LEANDRO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SONOMA | 2021-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | DANIEL DAVIES INC | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2021-02-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 296 |  | 2 |  | HOMEOWNER | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2021-01-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 620 |  | 0 |  | LANDMARK LANDSCAPING | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | WINDSOR | 2021-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 686 |  | 1 |  | CENTURY FENCING COMPANY | WINDSOR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | WINDSOR | 2021-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 216 |  | 4 |  | 707 FENCE COMPANY | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2021-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 2 |  | HOMEOWNER | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2021-11-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 52 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  | 3899 |  | 0 |  | BDS PLUMBING | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1631 |  | 0 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2021-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 886 |  | 1 |  | CITY OF CERES | CERES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2021-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 211 |  | 1 |  | HOMEOWNER | CERES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | CERES | 2021-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 1 |  | HOMEOWNER | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2021-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | LEA''S DEMOLITION | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2021-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1374 |  | 0 |  | INDERJIT S TOOR CONSTRUCTION INC | MODESTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | CERES | 2021-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1981 |  | 2 |  | HOMEOWNER | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2021-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 801 |  | 4 |  | TRIPLE J CONSTRUCTION | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2433 |  | 1 |  | TENNYSON ELECTRIC | LIVERMORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | STANISLAUS | CERES | 2021-06-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1077 |  | 9 |  | SUN VALLEY PUMPING | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2021-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 756 |  | 1 |  | HOMEOWNER | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | DENAIR | 2021-05-04 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | HOMEOWNER | DENAIR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | EMPIRE | 2021-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 193 |  | 1 |  | HOMEOWNER | EMPIRE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | HUGHSON | 2021-04-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 26 |  | 1 |  | GATEWAY PACIFIC CONTRACTORS INC | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | KEYES | 2021-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | KEYES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | KEYES | 2021-04-16 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6129 |  | 11 |  | TURLOCK IRRIGATION DISTRICT | TURLOCK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1324 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1640 |  | 0 |  | TAK COMMUNICATIONS | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 721 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1596 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2329 |  | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 614 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1045 |  | 1 |  | ON POINT ELECTRIC | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-07-26 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 299 |  | 0 |  | BZ CONSTRUCTION | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 207 |  | 1 |  | CITY OF MODESTO | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 214 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1523 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 166 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 153 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2907 |  | 0 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Farm Equipment | 0.75 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3795 |  | 3 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-01-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2495 |  | 0 |  | SANDOVAL FENCING JOSE | LATHROP | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 38 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 161 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MCPHERSON PROPERTY SERVICES | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1549 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 295 |  | 2 |  | LASAR UNDERGROUND | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1524 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-01-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 28 |  | 1 |  | ALCCON GENERAL ENGINEERING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-03-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CALIFORNIA GOLDEN PLUMBING | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1101 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 280 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1519 |  | 2 |  | LASAR CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-07-09 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 3 |  | VETERAN PIPELINE CONSTRUCTION | BENICIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | TEICHERT PIPELINES | STOCKTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect facility records/maps
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1170 |  | 1 |  | HENSEL AND CASTILLO FENCING INC | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7 |  | 2 |  | IZUMI CONSTRUCTION | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 208 |  | 1 |  | FIRST CHOICE ELECTRIC | EMPIRE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | YARD CREATIONS LANDSCAPE SERVICE | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1186 |  | 1 |  | CITY OF MODESTO | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-04-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | BAY CITIES PAVING | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-01-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1050 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-06-01 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5695 |  | 3 |  | PACIFIC GAS & ELECTRIC | MODESTO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 85 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-05-10 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4802 |  | 0 |  | VETERAN PIPELNE CONSTRCTION | BENCIA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 107 |  | 1 |  | HOMEOWNER | WEST MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  | 2413 |  | 2 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | Housefire
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-02-27 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | SNELSON | CERES | CA | Y | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-12-06 | Third party excavation damage | Main | Steel | Hand Tools | 4 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1730 |  | 0 |  | CITY OF MODESTO | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 691 |  | 0 |  | UNITED PAVING | STOCKTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1114 |  | 1 |  | CITY OF MODESTO | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 161 |  | 1 |  | HOMEOWNER | WEST MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | NEWMAN | 2021-09-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1247 |  | 0 |  | PACIFIC SOUTHWEST | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2021-06-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 26 |  | ROLFE CONSTRUCTION | ATWATER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2021-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2332 |  | 1 |  | MP NEXLEVEL | MERCED | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | RIVERBANK | 2021-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3222 |  | 0 |  | MOZINGO CONSTRUCTION | OAKDALE | CA | N | Y | Yes | No | No | Yes | Yes | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | STANISLAUS | RIVERBANK | 2021-12-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10957 |  | 0 |  | MOZINGO CONSTRUCTION | OAKDALE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect Facility Records / Maps
Pacific Gas and Electric | N | STANISLAUS | SALIDA | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 256 |  | 1 |  | MIKE HALLETT FENCING | RIPON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | SALIDA | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 481 |  | 1 |  | HOMEOWNER | RIPON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | SALIDA | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 286 |  | 1 |  | GOLDEN BAY FENCE PLUS IRON WORKS | STOCKTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2021-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 347 |  | 1 |  | GOLDEN STATE LANDSCAPING | DELHI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2021-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 46 |  | 0 |  | TURLOCK PETROLEUM INC | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 168 |  | 1 |  | TNT INDUSTRIAL | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2021-12-17 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2501 |  | 0 |  | INDERJIT S TOOR CONSTRUCTION INC | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2021-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 136 |  | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2021-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1505 |  | 1 |  | MICHAEL WHEELER CONSTRUCTION INC | OAKDALE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2021-03-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1601 |  | 0 |  | PHASE 1 CONSTRUCTION | ATWATER | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | WATERFORD | 2021-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2424 |  | 1 |  | HOMEOWNER | WATERFORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SUTTER | LIVE OAK | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3582 |  | 1 |  | DE SILVA GATES CONSTRUCTION | DUBLIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SUTTER | LIVE OAK | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 387 |  | 0 |  | MILTON GOLLEN BUSCH | LIVE OAK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SUTTER | LIVE OAK | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 208 |  | 1 |  | MJD ENGINEERING | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2021-05-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 99 |  | 2 |  | CITY OF YUBA | YUBA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2021-09-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4265 |  | 1 |  | HOMEOWNER | YUBA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Excavated outside delineations
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2021-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | YUBA CITY | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2021-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Farm Equipment | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | THIARA COMPANY | YUBA CITY | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 426 |  | 0 |  | ROTOCO INC | VISTA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2021-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1164 |  | 1 |  | UNDERGROUND CONSTRUCTION | BENCIA | CA | N | Y | Yes | Yes | No | Yes | Yes | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15 |  | 1 |  | HOMEOWNER | YUBA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | TEHAMA | CORNING | 2021-08-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 537 |  | 1 |  | HOMEOWNER | CORNING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | TEHAMA | RED BLUFF | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 447 |  | 1 |  | HOMEOWNER | RED BLUFF | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | TEHAMA | RED BLUFF | 2021-03-05 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1902 |  | 1 |  | HOMEOWNER | RED BLUFF | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | TRINITY | MAD RIVER | 2021-12-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4028 |  | 1 |  | HOMEOWNER | MAD RIVER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | DAVIS | 2021-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 2 |  | PLUMBING DOCTOR | DAVIS | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | DAVIS | 2021-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3402 |  | 1 |  | ABIDE BUILDERS INC | WEST SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | DAVIS | 2021-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 51 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  | 2339 |  | 1 |  | CENCAL ENTERPRISES | LAGUNA NIGUEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | DAVIS | 2021-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | DAVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | DAVIS | 2021-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | KNIGHT WORKS ELECTRIC | DAVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | DAVIS | 2021-05-24 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 2 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2960 |  | 0 |  | FIBERCO | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | YOLO | DAVIS | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 262 |  | 1 |  | WARD & SON CONSTRUCTION | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2021-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | WEBER GENERAL ENGINEERING | VACAVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3868 |  | 1 |  | HOMEOWNER | WEST SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ST FRANCIS ELECTRIC | SAN LEANDRO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2021-05-13 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NORTH STATE ELECTRIC | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1392 |  | 0 |  | BARON BONNER GENERAL ENGINEERING | MARYSVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2021-04-21 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25830 |  | 0 |  | HOMEOWNER | WEST SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2021-01-28 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 31418 |  | 4 |  | ALVAH CONTRACTORS | SOUTH SAN FRANCISCO | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WOODLAND | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 752 |  | 1 |  | WAHLUND CONSTRUCTION | EUREKA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Locator error
Pacific Gas and Electric | N | YOLO | WOODLAND | 2021-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8356 |  | 2 |  | WAHLUND CONSTRUCTION | EUREKA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | YOLO | WOODLAND | 2021-06-23 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5352 |  | 0 |  | HOMEOWNER | WOODLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WOODLAND | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1911 |  | 1 |  | P31 ENTERPRISES | OROVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | YOLO | WOODLAND | 2021-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2010 |  | 1 |  | HOMEOWNER | WOODLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WOODLAND | 2021-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WAHLUND CONSTRUCTION | EUREKA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YUBA | MARYSVILLE | 2021-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3295 |  | 1 |  | HOMEOWNER | MARYSVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YUBA | MARYSVILLE | 2021-05-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 890 |  | 0 |  | KO UNDERGROUND | WINTERS | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | YUBA | MARYSVILLE | 2021-04-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 232 |  | 0 |  | D. GOODMAN PLUMBCO | MARYSVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YUBA | MARYSVILLE | 2021-01-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 350 |  | 1 |  | HOMEOWNER | MARYSVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YUBA | OLIVEHURST | 2021-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 54 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 193 |  | 1 |  | WESTERN ENGINEERING | LOOMIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YUBA | OLIVEHURST | 2021-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | OLIVEHURST | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YUBA | OLIVEHURST | 2021-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 2 | 60 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8841 |  | 0 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YUBA | WHEATLAND | 2021-07-12 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6271 |  | 0 |  | HICKMAN UTILITY INC | ROCKLIN | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | Y | MONTEREY | SALINAS | 2021-10-16 | Third party excavation damage | Main | Steel | Farm Equipment | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 94645 |  | 10 |  | FERNANDEZ BROTHERS INC | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | Y | SACRAMENTO | ISLETON | 2021-04-16 | Third party excavation damage | Transmission Line in a non-HCA area | Steel | Farm Equipment | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 112152 |  | 1 |  | GREENFIELD TURF INC | GREENFIELD | CA | N | Y | No | No | No | No | Yes | No | No | USA NOT CALLED
Pacific Gas and Electric | Y | SANTA CLARA | SAN JOSE | 2021-08-25 | Third party excavation damage | Main | Steel | Boring Equipment | 3 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 932688 |  | 43 |  | LITEWAVE CONSTRUCTION | SAN JOSE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | Y | SONOMA | SONOMA | 2021-09-23 | Operator excavation damage | Main | Steel | Miscellaneous/Other | 8 | 200 | 200 | Y | Y | N | N | 0 | 0 |  | 0 | 0 |  | 295362 |  | 0 |  | PG&E | BERKELEY | CA | Y | Y | No | No | No | No | No | No | No | Welding on pipe created a pin hole and ignited gas leak
San Diego Gas and Electric | N | ORANGE | SAN CLEMENTE | 2021-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | RICHARD STONEBRAKER | OCEANSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE Service hit by Mini X
San Diego Gas and Electric | N | SAN DIEGO | BONITA | 2021-12-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3233 |  | 3 |  | ISIDRO CERVANTES | SAN DIEGO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | While digging to upgrade electric service contractor hit 2 inch PE main
San Diego Gas and Electric | N | SAN DIEGO | BONITA | 2021-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MIGUEL SIMPSON | CHULA VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Trenching on side of house
San Diego Gas and Electric | N | SAN DIEGO | CARDIFF BY THE SEA | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MICHAEL CONWAY | CARDIFF | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit 0.5 inch PE service with shovel.
San Diego Gas and Electric | N | SAN DIEGO | CARDIFF BY THE SEA | 2021-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | KYLE ANDERSON | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.75 inch Steel service hit with trencher
San Diego Gas and Electric | N | SAN DIEGO | CARDIFF BY THE SEA | 2021-12-24 | Third party excavation damage | Not Available | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | PHILL ROSS | CARDIFF BY THE SEA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
San Diego Gas and Electric | N | SAN DIEGO | CARDIFF BY THE SEA | 2021-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | DAVID FLAHIVE | RAMONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE service hit with excavator while trenching to relocate utilities due to utility relocation.
San Diego Gas and Electric | N | SAN DIEGO | CARDIFF BY THE SEA | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | DOMINIC GRIPPO | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inch PE service hit with mini x.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2021-03-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | MANUEL GARCIA | CERRITOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 inch PE service. EFV tripped.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2021-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | PRIME ELECTRICAL SERVICES | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 inch PE service hit with
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2021-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | DEREK ORME | CARLSBAD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE service hit with shovel while digging for post hole.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2021-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MARTEN COLVINGA | CARLSBAD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE service hit with pick axe
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2021-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1385 |  | 1 |  | KEHOE TESTING ENGINEERING | HUNGTINGTON BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | 1 0.5 inch steel main hit with drill. Current USA.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2021-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | GEOVANI AGUILAR | CARLSBAD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch PE Service hit with shovel.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2021-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | RODS CONSTRUCTION SERVICE | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging post holes for a fence and hit 0.5 inch poly line
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2021-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | DON LOPEZ | CARLSBAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE Service hit with shovel while trenching for panel upgrade.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2021-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | CHARLIE SCOTT | OCEANSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a post hole digger to install a barrier post hit the 0.5 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | PRATT EQUIPMENT CORP | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE stub hit with shovel.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2021-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | VICENTES YARD SERVICE | OCEANSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to install electric for new gate
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2021-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | CIROS LNADSCAPE | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with mini ex to install a gas line when they hit the 0.5 inch poly service. No USA
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ZACH ADDISON | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2021-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JASON STEWART | CARLSBAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE Service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2021-01-07 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3933 |  | 13 |  | COREY MORGAN | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Directional boring
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2021-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JIM TORRESCANO | NATIONAL CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 0.5 inch poly while digging with hand tools
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2021-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1651 |  | 4 |  | ESH LANDSCAPE AND CONSTRUCTION | ESCONDIDO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor hit 0.5 inch poly line while landscaping
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | PATTERSON BROTHERS | LAKESIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 inch poly service with mini ex
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | MEGA ENGINEERING | LAKESIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Grading for compaction
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1755 |  | 1 |  | ART MORALES | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SDG&E was notified of a third party damage at 2175 Proctor Valley Rd. Third party contractor damaged a 1 inch plastic service line. SDG&E crews responded and controlled the leak. There were no injuries or fatalities resulting from this incident. The investigation showed the third party contractor was working without a USA Ticket. This incident was reported to CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2021-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1651 |  | 4 |  | CARL CLEM | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 0.50 inch poly with excavator
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | ANTHINY FERRIER | CORONADO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Digging with excavator to locate gas
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2021-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | COASTAL DEVELOPMENT | CORONADO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 inch PE service hit with excavator
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2021-11-10 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | DAVE HITZMAN | LAKESIDE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hand digging for new gas install
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2021-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | RESICOM | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Edwardo Torres stated while digging Earthwork to put conduit in for panel upgrade he hit 0.5 in PE Gas service w shovel on 2 spots. Gerc 22, Jesse Daggett made repair w 1 ft of 0.5 in PE Premade 0.5 in PE Driscoplex to make repair.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2021-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | CONSTRUCTION GENETICS | TEMECULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inchPE hit wJackhammer
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MOI DELGADO | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.50 inch PE with shovel
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | RAMONA PACIFIC | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber was digging by hand with no USA ticket and damaged 0.5 inch poly
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2021-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3374 |  | 10 |  | COASTAL DEVELOPMENT | CORONADO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While grading with bob cat 3rd party contractor hit 0.75 inch steel service stub
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2021-04-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | ENHANCED BRICK AND BLOCK | CORONADO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging for a drain with hand tools and without a USA ticket a 1 inch poly line with a excess flow valve was hit.
San Diego Gas and Electric | N | SAN DIEGO | DEL MAR | 2021-01-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | GRANT GOODMAN | DEL MAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | DEL MAR | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | T MAC CONSTRUCTION | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE service was hit with pick axe while trenching for electric upgrade.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-05-26 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | A VIDOCICH | LAKESIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | MiniX hit 2 inch poly main
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1651 |  | 4 |  | PAUL GIESE | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Customer was digging to upgrade electric panel conduit installation.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1651 |  | 4 |  | ANDRE BOTTER | LAKESIDE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | failed to exercise adequate caution while exposing pipe and or facilities in place
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JOHN BRADLEY | EL CAJON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | While digging to install sewer lateral customer hit 0.5 inch poly with back hoe
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | JOSE FLORES | LEMON GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Installing solar
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | RAOZ GENERAL ENGINEERING | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor failed to use hand tools to expose PE service
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | NORTH COUNTY FENCE AND FABRICATION | NA |  | N | Y | Yes | No | Yes | No | No | Yes | No | Failure to maintain a valid USA ticket. Failure to use caution while digging near service.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | CHRIS MAGARRO | EL CAJON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | RUSS BROWN | EL CAJON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Grading
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ERIKA RODRIGUEZ | CARLSBAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Grading with bob cat in back yard
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | JOHN MERKLINGER | CARLSBAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | excavator did not exercise sufficient caution
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | HOME OWNER | EL CAJON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to call Dig alert
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MIKE KAMEL | EL CAJON | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | While hand digging home owner hit 0.5 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-09-07 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | EVAN CRAIG | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While trenching to put in conduit for electric solar customer hit 0.50 inch PE gas service with shovel.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SHEAR FORCE CONSTRUCTION | SAN DIEGO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | the customer failed to exercise caution when exposing line
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SHEAR FORCE CONSTRUCTION | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | failed to have sufficient care while digging around GAS line
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SUNSHINE COMMUNICATIONS INC | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 0.5 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | RICHARD EDWARDS | EL CAJON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch unmarked poly service hit with a shovel
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SIM ENGINEERING | FALLBROOK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | While digging with an excavatorand expired USA ticket a 3rd party contractor hit 0.5 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | JC CABLE | SANTEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor did not call USA
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | GABE ZERMENO | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor failed to pot by hand
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MIKE ZEPEDA | SPRING VALLEY | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Custome Thought An Abandoned Gas Line Was The Service They Were Looking For
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | CARROLL CONSTRUCTION | FALLBROOK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with a shovel to install a electric conduit when they hit the 0.5 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-10-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | BENS ASPHALT | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2 inch PE main hit with backhoe
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1732 |  | 2 |  | HOME OWNER | ENCINITAS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor working for homeowner hit a 0.5 inch poly service while grading with a backhoe
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1791 |  | 6 |  | GARRY ADALIAN | CARLSBAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inch PE Service hit with electric clay digger
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | GERARDO GONZALEZ | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | KACEN HORNER | ENCINITAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE Service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-07-09 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5167 |  | 25 |  | GRANITE CONSTRUCTION | CARLSBAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 inch Steel Main leaking approximately 30 feet from excavation point. Looks like contractors hit pipe and separated screw fitting.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ALONSO RODRIGUEZ | ENCINITAS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer had no valid USA ticket
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | INTERNATIONAL GARDENS | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was installing drains when they drove a stake into the 0.5 inch poly service causing a bnb
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MARK DONNALLY | ENCINITAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch Gas Service hit with digging bar while trenching for drain.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | REMCON | SAN DIEGO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 1 inch PE service hit with digging bar. Expired USA. Service marked correctly
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | HENKELS MCCOY | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE Service hit with Grundo
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | PERRY ELECTRIC | SANTEE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor trenching with a mini ex to install a conduit hit a 0.75 inch steel stub
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | LUIS LOPEZ | SAN MARCOS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 0.5 inch PE Service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2021-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | DEL MAR ELECTRIC | SOLANA BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2021-12-03 | Third party excavation damage | A service line with an excess flow valve installed | Material not known | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ROBERT CRANFORD | ESCONDIDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE service severed while grading with bobcat
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ROCKY HARPUR | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE Service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2021-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | Excavation was for emergency reasons. | Excavation was for emergency reasons. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2021-04-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | SCHILLING CORPORATION | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to maintain mark out on jobsite
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2021-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | HOMELAND ELECTRIC INC | JURUPA VALLEY | CA | N | Y | Yes | No | No | No | No | Yes | Yes | 0.5 inch PE Service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | JAVIER MARTINEZ | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.75 inch Steel Service hit with excavator, no leak.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | NA | VALLEY CENTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2021-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | NIJINSKY GOVARI | ESCONDIDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to use caution while potting for gas service.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2021-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | TRUE MARK HOMES | NEWPORT BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with mini ex to install irrigation hit the 1 inch poly service. No usa
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2021-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | DANIEL GRAHAM | ESCONDIDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE Service hit with shovel. No USA Ticket.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2021-08-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | REMEDY PLUMBING | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2021-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1931 |  | 8 |  | GARY MOLENAAR | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE service hit with pick axe
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2021-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ISMAEL VELASCO | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | SUZANNA VELASCO | ESCONDIDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2021-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | NPC CONSTRUCTION | FALLBROOK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation. Contractor believed USA mark out done by GC covered him. I explained to him that he needed his own USA ticket to legally excavate.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2021-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 2 |  | DRAVES PIPELINE | FALLBROOK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 09-09-2021, SDG&E was notified of a third party damage at 1332 East Fallbrook Street. The third party contractor struck a 0.5inch plastic service line with a hand shovel, causing a release of gas. SDG&E personnel were sent to the scene and safely controlled the gas. There were no injuries or fatalities resulting from this incident. The investigation showed the contractor did not have a valid USA ticket. This incident was reported to the CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | LUIS MORENO | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | failure to notify USA prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2021-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | JOHN RYAN | FALLBROOK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 1 inch PE service with backhoe
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2021-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | KENDALL CONSTRUCTION INC | FALLBROOK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2021-10-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | MURRIETA DEVELOPMENT | TEMECULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | JIM FULLER | FALLBROOK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging for tree
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2021-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | FRANCISO PABLO | FALLBROOK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE service hit with post hole digger
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2021-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | EAGLEVIEW CONCRETE | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA TICKET
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2021-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MURRIETA DEVELOPMENT | TEMECULA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Digging with equipment for a sewer line lateral
San Diego Gas and Electric | N | SAN DIEGO | IMPERIAL BEACH | 2021-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MORGANS DEMOLITION | SPRING VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Customer was digging so that the service would be retired from service
San Diego Gas and Electric | N | SAN DIEGO | IMPERIAL BEACH | 2021-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JOSEPH SANCHEZ | IMPERIAL BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit poly while hand digging
San Diego Gas and Electric | N | SAN DIEGO | IMPERIAL BEACH | 2021-08-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | NOAH ROJAS | FALLBROOK | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party contractor stated start date for work was going to be 90.501. They dug before that 83021.
San Diego Gas and Electric | N | SAN DIEGO | JAMUL | 2021-08-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2977 |  | 0 |  | A. VIDOVICH CONSTRUCTION | LAKESIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 8-10-2021, a third-party contractor damaged a 2-inch plastic gas main stub with a mini excavator at 3435 Stonefield Dr, Jamul, San Diego, CA when excavating to install conduit. SDG&E crew responded and controlled the release of gas, there were no injuries resulting from this incident. The investigation showed that the contractor had an expired USA ticket B203460249 and failed to contact SDG&E when stub was not located while potholing the area prior to excavating. This incident was reported to the CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2021-12-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ZSOLT NAMENYI | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Facilities were mark but not hand exposed, hence being damaged by the excavator.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2021-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | DON TOMAS | SAN DIEGO | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inch poly with shovel. Contractor was digging for electric trench.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ROED CONSTRUCTION | RAMONA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Pot holing by hand for foundation for room addition,
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2021-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | DEBI BRIGHT | LA JOLLA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ROBERTO CHAVEZ | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | unmarked 0.50 inch poly service hit with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ANDREW BISHOP | LA JOLLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Excavated outside delineation.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2021-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | HERRERA BROS CONCRETE | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2021-03-02 | Third party excavation damage | Main | Steel | Trencher | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1315 |  |  | NA | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | SDGE locator was unable to locate 1.5 inch steel stub that was not displayed in GIS.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2021-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | SMITH ELECTRIC CONTRACTORS | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Excavated outside of delineated work area.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2021-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | MARK O CONNER | SPRING VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | poly pipe hit by contractor with shovel, legacy development
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2021-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | SARA ANDRADE | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Did not notify DigAlert or get USA markout before excavating with a miniX
San Diego Gas and Electric | N | SAN DIEGO | LA MESA | 2021-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | HOME OWNER | LA MESA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
San Diego Gas and Electric | N | SAN DIEGO | LA MESA | 2021-03-29 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2366 |  | 3 |  | SDGE | SAN DIEGO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SDGE was notified of a first party damage to a 0.75 inch steel gas service. SDGE crews were pot holing to install new gas service when they struck the 3/4 inch steel service with a backhoe. SDGE crew was able to controlled gas at 14:44. There were no injuries resulted from this incident. This incident was reported to CPUC when SDG&E became aware of major media Fox 5 was on scene.
San Diego Gas and Electric | N | SAN DIEGO | LA MESA | 2021-02-24 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | ADRIAN RICO | SAN DIEGO | CA | Y | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Gas Construction, digging to install poly gas main.
San Diego Gas and Electric | N | SAN DIEGO | LA MESA | 2021-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | BUILDERS EXPRESS | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer stated while digging to make repair on sewer lateral he smell gas. After further investigation it was determined to be nicked by shovel. Customer Michael takes full responsibility.
San Diego Gas and Electric | N | SAN DIEGO | LA MESA | 2021-06-29 | Operator excavation damage | Main | Steel | Not Available | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3417 |  |  | NA | SDGE | NA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
San Diego Gas and Electric | N | SAN DIEGO | LA MESA | 2021-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SIMS GRADING | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no usa ticket
San Diego Gas and Electric | N | SAN DIEGO | LAKESIDE | 2021-06-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | HAMANN COMPANIES | EL CAJON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | the contractor was digging on an expired ticket and did not call when they did not find the pipe after potting
San Diego Gas and Electric | N | SAN DIEGO | LAKESIDE | 2021-02-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | JOSE THORNE | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to install water service
San Diego Gas and Electric | N | SAN DIEGO | LAKESIDE | 2021-07-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | PACIFIC PRODUCTION PLUMBING | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging without valid USA ticket
San Diego Gas and Electric | N | SAN DIEGO | LAKESIDE | 2021-07-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | NEW WEST INVESTMENT GROUP | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No call to Dig alert
San Diego Gas and Electric | N | SAN DIEGO | LEMON GROVE | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | SUNLIGHT SOLAR INC | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | the contractor failed to use adequate caution while digging around the gas service
San Diego Gas and Electric | N | SAN DIEGO | LEMON GROVE | 2021-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | AGI GENERAL | STANTON | CA | N | Y | Yes | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1 inch poly service while digging for concrete ramp with expired USA ticket
San Diego Gas and Electric | N | SAN DIEGO | NATIONAL CITY | 2021-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | C AND W DIVING | NATIONAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | NATIONAL CITY | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | SYMBOLIC BUILDERS | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hand digging for foundation.
San Diego Gas and Electric | N | SAN DIEGO | NATIONAL CITY | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | PRECISION HOME DESIGN AND REMODEL | LA JOLLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While digging up gas service by hand 3rd party contractor hit 0.5 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | NATIONAL CITY | 2021-05-18 | Third party excavation damage | Main | Steel | Boring Equipment | 6 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 95506 |  | 11 |  | ESPINOSA CABLE CONSTRUCTION | RAMONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On the 18th of May 2021, a third party contractor damaged a 6 inch steel gas main by directional bore. Crews responded, controlled the gas and made repairs. There was no ignition or injuries resulting from this incident. Investigation revealed the line was not marked correctly due to GIS discrepancy. This incident was rescinded from DOT but remains reportable to CPUC when SDG&E became aware of area odor, public attention, and media coverage.
San Diego Gas and Electric | N | SAN DIEGO | NATIONAL CITY | 2021-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | WILL WENNERHOLM | CARDIFF BY THE SEA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party contractor hit 1 inch poly service with excavator. Expired ticket and failed to pothole.
San Diego Gas and Electric | N | SAN DIEGO | NATIONAL CITY | 2021-08-02 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3514 |  | 12 |  | SDGE | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company crew hit 12 inch poly inserted in 0.75 inch steel
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-11-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | RYAN LEITZELL | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch PE Service hit with hand tool while installing low voltage electric.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | PACIFIC PRODUCTION PLUMBING | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch PE Service cut with sawzaw while working on water service.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | JAY PETERSON | OCEANSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.75 inch steel service hit with 0.75 inch steel service
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-04-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MARK BLESSING | OCEANSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with a shovel when they hit the 0.5 inch poly service.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | MIGUEL MOZO | OCEANSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit 0.5 inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-09-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JEREMIAH AMES | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging with shovel
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-04-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | CHRIS TAUNT | OCEANSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | BRAD TAFF | SAN DIEGO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | hit 0.5 inch PE service with boring drill
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | GREGG SHARP | CHULA VISTA | CA | N | Y | Yes | No | Yes | No | No | Yes | Yes | Hit 0.5 inch PE Service with shovel. No USA
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1942 |  | 5 |  | DRAIN PATROL | CARLSBAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging for water leak with no mark out
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1651 |  | 4 |  | BRAD TAFF | SAN DIEGO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | FRANSISCO ESTRADA | OCEANSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2281 |  | 13 |  | NICK MELENDEZ | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inch PE service
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1651 |  | 4 |  | BRAD TAFF | SAN DIEGO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | PRO TEC BUILDING SERVICES INC | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inch PE service hit with jackhammer.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | LARRY BENSON | VISTA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE Service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-07-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4000 |  | 8 |  | PATTERSON BROTHERS LIGHTING | LAKESIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On 7-7-2021, SDG&E was notified of a third-party damage at 4147 Oceanside Blvd. Oceanside, CA. The third-party contractor damaged a 2-inch plastic gas main with a mini excavator while digging to install street light footing. The company crew responded, controlled the gas, and replaced the damaged section of the main. There were no injuries or further damages resulting from this incident. The investigation showed that the contractor had a valid USA ticket A211670049, however, the damaged plastic main was not marked prior to excavation.This incident was reported to the CPUC due to the release of gas and when SDG&E became aware of major media coverage.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-09-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3093 |  | 1 |  | AL TAMASOBI | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to tie into the gas main. Customer already knew the gas main was there.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2021-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | GREG TRABERT | OCEANSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch poly hit with a shovel outside delineated area.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2021-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | NA | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to use caution while digging near gas facility.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2021-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | PEDRO FUERTE | POWAY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut 0.75 inch Steel Service with Saw
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2021-08-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | EXECUTIVE LANDSCAPE | FALLBROOK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2021-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | JOSE GONZALEZ | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 inch PE Stub hit with backhoe
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2021-10-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | TE ROBERTS INCORPORATED | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to protect gas facilities while excavating.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2021-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1861 |  | 7 |  | CHRISTOPHER RAMSEY | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use adequate caution while digging near gas facility
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | AVIDOVICH CONSTRUCTION | LAKESIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while digging near gas facility.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2021-11-17 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | GABRIEL PEREZ | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to use caution while digging near gas service.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2021-07-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | VELSA CONSTRUCTION INC | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor did not have valid USA markout
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2021-11-09 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JAVIER MARIN | SPRING VALLEY | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while installing a new gas service.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2021-09-02 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to use caution while digging near gas facility
San Diego Gas and Electric | N | SAN DIEGO | RANCHO LA COSTA | 2021-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | RAFAEL ALVAREZ | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inch PE service hit with pole hole digger
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2021-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | TOMMY HINSON | RANCHO SANTA FE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to installs drainage when they severed the 0.5 inch poly service.
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2021-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1732 |  | 2 |  | NATHAN BENTLEY | THORNTON | KY | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1.25 inch PE Service hit with boring drill
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2021-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | FALLBROOK WINERY | FALLBROOK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE Service with auger
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2021-03-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | JERRY TEAGUE | BONSALL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 inch PE Main hit with mini X. No USA Markout.
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | KONSTIN GALKIN | RANCHO SANTA FE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch PE service hit with Mini X
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1581 |  | 3 |  | RAMON MORENO | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit 0.5 inch poly service with electric jackhammer shovel at Property line
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-12-30 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | JASON PITMAN | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | MiniX Operator Bruce King with JP Plumbing was trenching to install Sewer for soon to be Starbucks. While trenching the MiniX made contact with 11 4 inch PE Gas Main causing the BandB.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-11-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14925 |  | 128 |  | CITY OF SAN DIEGO WATER DEPT. | SAN DIEGO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On 11/29/2021, SDG&E was notified of a third-party damage at 10373 Azuaga Street, San Diego, CA. The third-party contractor damaged a 2-inch plastic gas main with a backhoe while installing a water tee. SDG&E crews responded, controlled the release of gas, and made permanent repairs by replacing the damaged section of the main. The investigation of the incident revealed SDG&E did not properly mark the gas line. There were no injuries or further damages resulting from this incident. This incident was reported to the CPUC due to the release of gas and when SDG&E became aware of major media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | JOHN SASS | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit 0.5 inch poly with mini x
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | LUGOS ELECTRIC | CHULA VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch poly hit with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2421 |  | 15 |  | ALFREDO GUITIERREZ | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 0.5feet poly with shovel will potting for gas line. crew controlled leak by squeezing main. 15 customers out of gas
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | CHARLES CULBERTSON | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Ticket
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-04-11 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | CITY OF SAN DIEGO | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | City Water Authority pulling cable through existing pipe location. with muddy conditions cable rubbed poly pipe.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | PATRICIA MESSICK | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | ALEX GUTIERREZ | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | DigAlert not notified, no mark out
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1651 |  | 4 |  | BRANDON VICARS | SAN DIEGO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | failure to use caution while hand digging to find service
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1791 |  | 6 |  | SNOW ENGINEERING CORP | LAKESIDE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor hit 0.50? poly with shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | TM KIROVSKI | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE Service with shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3417 |  |  | NA | CUSTODIO ARANA | SOUTH EL MONTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator grabbed 1 inch Steel Service while removing storm drain
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-08-10 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | SEBASTIAN GUTIERREZ | LAKESIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 inch PE Main hit with excavator. No USA Markout.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | PROCELL | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SMITH AND ELECTRIC CONTRACTORS | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inchPE Gas service hit by Claydigger
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1872 |  | 4 |  | ROY DUNNING | SAN DIEGO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 1 inch PE service hit with pick axe
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | JOE CASTILLO | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inch poly line with shovel causing gas to blowleak. contractor was digging for electric trench for solar.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | MIKE HURRELL | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MICHAEL JOHNSTON | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While Tring To Dig Sewer Trench And Expose Gas Service Hit 0.50 inch Dupont Where It Comes Out Of 1 0.50 inch Stl Casing.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | NA | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-06-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | RIVERS LANDSCAPE CONSTRUCTION | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failed to notify USA prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3437 |  | 0 |  | DIG DUG UNDERGROUND CONSTRUCTION | MORENO VALLEY | CA | N | Y | No | No | No | No | No | No | No | On 7-28-2021, a third-party contractor damaged a 1 1/2-inch steel gas service with a backhoe at 1677 National Avenue, San Diego, CA while grading for building footing. SDG&E crew responded and controlled the release of gas, there were no injuries resulting from this incident. The investigation showed that the contractor did not have a valid USA ticket. This incident was reported to the CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-09-17 | Operator excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | TONY PATRON | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Investigating a gas leak, crew member punctured gas main with probe.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-10-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SEAN CROWLEY | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use adequate caution
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ANDRES | CHULA VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while digging near gas facility
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | PAUL HERNANDEZ | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging landscaping with no USA a contractor hit 0.5 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | DANIEL RIVERA | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failed to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | CY KACKSTETTER | SOLANA BEACH | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Bobcat hit 0.5 inch poly line. Expired USA Ticket.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | HENRY EARTHWORX | CARDIFF | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inch poly claimed to be hit with a shovel. Upon investigation was hit with an excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | CONSTRUCTION TESTING AND ENGINEERING | ESCONDIDO | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor had valid USA , However the service was not marked out.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2071 |  | 10 |  | RANCHO PAVING CABLE | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While trenching hit 0.50 inch PE with clay digger
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ASCENSION MONDO | NA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was cutting root and hit 0.5 inch poly service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-06-03 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1315 |  |  | NA | BRUNO BUILDERS | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging with an excavator without potting
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | PK MECHANICAL | WILDOMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to maintain visible mark out on jobsite.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9674 |  | 100 |  | MICHAEL LIVERSEDGE | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to maintain marks
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | PK MECHANICAL SYSTEM INC | WILDOMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Lance Carr stated PK Mechanical System was trenching for Water Main. Contractors hit 0.75 inch stll. gas service with Backhoe. USA given to me by Lance Carr has been expired for some time. No other USA info.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | RCS PRO BUILD | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor sawed 0.75 inch steel service, with No USA
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | FRANCISCO SILVA | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | the Contractor did not call in USA ticket
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 9 |  | ESPINOZA CABLE | RAMONA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | While trenching with a rock wheel 3rd party contractor hit 0.5 inch PE inserted in 0.75 inch steel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | PETER ZAMORA | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Rancho Paving boring conduit and hit 0.5 inch poly service. Contractor had valid dig alert ticket. However, mark out said Mark Out by Measurement Pot and Find pictures included.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | LEGEND FENCE CORP 787570 | LEMON GROVE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Never contacted Dig Alert
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4004 |  | 19 |  | DAVID BALLMAN | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor crew was grading asphalt and hit 0.75 inch stl service 11 inch deep
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | DAVE EVANS | EL CAJON | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | While a contractor was trenching with a rock wheel a 0.75 inch steel line was hit
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-02-08 | Third party excavation damage | Main | Steel | Not Available | 20 | 400 | 320 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DAVE EVANS | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | while pot holing with pressure device wrap was knocked off 20 inch steel main
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2553 |  | 5 |  | GERRY LOZA | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 2-3-21, a third-party contractor damaged a 0.75-inch steel gas service at 3560 Mount Acadia Blvd. San Diego, CA 92111 when excavating to relocate overhead power. Crew responded and controlled the release of gas, and made permanent repairs by replacing a section of the main. The investigation of the incident showed there was a valid USA ticket for the contractor and the 3/4-inch steel gas service was properly marked. This incident was reported to the CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-01-08 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JOSE ENRIQUEZ | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas service installation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | DMI GENERAL ENGINEERING | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to maintain clear marks
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | KATHERYN WESTER | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install sewer lateral 0.5 inch poly line was hit with hand tools
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4214 |  | 22 |  | SC VALLEY ENGINEERING INC | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor sawcut through out 0.75 inch steel service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | TYLER WELCH | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch pE hit by contractor while digging for gas houseline, no USA
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JACK NOOREN | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging for a foundation with hand tools and no USA a homeowner hit 0.5 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-12-28 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4171 |  | 40 |  | SDG&E | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | FJ WILLERT CONTRACTING CONSTRUCTION INC | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating to re compact to pour concrete
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | TIRSO LARA | NA | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 2 inch poly main with a digging bar
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3891 |  | 36 |  | ROAZ CONSTRUCTION | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | excavating for underground utilities
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-10-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2222 |  | 9 |  | MARCOS HERNANDEZ | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging to replace a fence post and hit 1 inch poly service with shovel causing a B and B. contractor had no USA
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1581 |  | 3 |  | BOB LANOUNE | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to install water drain
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | SMART LANDSCAPE 930038 | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hand Tool hit 0.5 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-11-12 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3934 |  | 18 |  | DAVID HITZMAN | LAKESIDE | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | 2nd party contractor hit 7 foot stub. This was a mapping error.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | DR DEMO | CHULA VISTA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor was picking up concrete foundation with a bobcat breaker attachment and snapped a 0.5 inch poly line inserted in 0.75 inch stl. The gas line was in the concrete
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | WILLIAM ALBREKTSEN | SAN DIEGO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | While digging to repair sewer lateral customer hit 0.5 inch poly with hand tools
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Material not known | Backhoe/Trackhoe | 0 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MORELLO CONCRETE INC | SANTEE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Backhoe yanked steel service. Bent pipe no leak
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MACON DESIGN | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While landscaping contractor hit 12 inch poly service with hand tools
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MANUEL RAMIREZ | VISTA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | While digging to install a drain 0.5 inch poly was struck by contractor
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | JESSICA MARSHALL | SANTEE | CA | N | Y | Yes | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating for a swimming pool a 3rd party contractor pulled a 0.75 inch steel ine and broke the riser
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | HOMEOWNER | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to use caution
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | MOON VALLEY NURSERIES | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-01-27 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5845 |  |  | NA | SCHILLING CONSTRUCTION | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged Cap and Missing Threads upon crew arrival.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4143 |  | 16 |  | BURTECH PIPELINE | ENCINITAS | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor had an expired USA Ticket at the time the damage occurred. EXP 71221
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-06-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5845 |  |  | NA | SOUTHLAND PAVING | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | WHile grading with an excavator contractor hit 3 inch poly main
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2362 |  | 11 |  | BILL GANT | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | handing post hole for wall
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | JUSTIN KIDWELL | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while trenching for a wall customer hit 0.5 inch PE service
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | CELESTINO GARCIA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ESPINOZA CABLE CONSTRUCTION | RAMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Trenching with back ho to clean out trench
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SMITH ELECTRICAL | EL CAJON | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Was Installing 3 Inch Conduit For A Panel Upgrade When They Hit The 0.50 Inch Poly Service. They Were Digging With A USA Ticket That Was Not Valid Yet.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-05-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3749 |  | 0 |  | CONTRACTING CONCRETE CONSTRUCTORS INC | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 5-25-2021, a third-party contractor damaged a 3-inch plastic gas main at 5505 Morehouse Drive San Diego, CA 92121 when excavating to install retaining wall. SDG&E Crew responded and controlled the release of gas. The investigation of the incident showed the concrete contractor did not pot hole before excavating. This incident was reported to the CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | SEMPRA SOLARIS | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit 0.5 inch poly with electric jack hammer while digging for electric solar trench. USA was accurate and is believed to be valid.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | REMCON DESIGN BUILD | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging with an excavator, had line exposed, there were flags for mark out, still hit service with the excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | SOCAL SHADE SAILS | DEL MAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-03-12 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1678 |  | 3 |  | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | A contractor damaged a 0.5 inch plastic service line. SDG&E crews responded and controlled the leak. There were no injuries or fatalities resulting from this incident. Investigation of the incident determined the contractor failed to use caution while digging with hand tools to pot hole. This incident was reported to CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JOEL LANGUREN | SAN DIEGO | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to renew ticket Maintain Valid ticket
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-03-05 | Operator excavation damage | Miscellaneous/Other | Steel | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 600 |  | 19 |  | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | A 2nd party contractor damaged a 1 inch steel gas drip line while excavating with a backhoe to remove existing drip line facilities. SDG&E crews responded and controlled the leak. There were no injuries resulting from this incident. Investigation of the incident determined the contractor failed to use hand tools where required. This incident was reported to CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | PIPERIN CONSTRUCTION | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator digging outside of their delineation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JIM VOLOMI | LA MESA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA TICKET
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | CALIFORNIA POOLS | LA MESA | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | the contractor failed to use proper caution while digging near Marked out gas service
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | FREEDOM ELECTRIC | SANTEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Mini X
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | SMITH ELECTRICAL | EL CAJON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | While trenching to install solar 3rd party contractor hit 0.50 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-04-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1802 |  | 3 |  | FARO LAFATA | NA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | locator unable to locate 1 inch PE line
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | BURTECH | ENCINITAS | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | No current USA ticket, USA not maintained, did not pothole as needed to protect the service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3234 |  | 8 |  | ABE COHEN | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Ticket, Hit 0.75 inch steel service with an excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | IRRISCAPE CONSYRUCTION | TEMECULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While trenching for irrigation pipe 2 inch poly was hit
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-03-26 | Operator excavation damage | Main | Steel | Not Available | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7562 |  | 33 |  | GEORGE LIZARRAGA | SAN DIEGO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company crew was saw cutting asphalt and cut 2 inch steel main
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1958 |  | 6 |  | LIZ SANCHEZ | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 1-26-21, a third-party contractor damaged a 0.5-inch plastic gas service at 7606 Canyon Point Ln. San Diego, CA 92126 when excavating to install electrical conduit for solar. Crew responded and controlled the release of gas as of 15:54. There were no injuries resulted from this incident. The investigation showed the contractor was working without a USA Ticket. This incident was reported to the CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | LOGAN BOUTILIER | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While digging a trench for new sewer lateral homeowner hit 0.5 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | ARCE ELECTRIC CO | LAKESIDE | CA | N | Y | Yes | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to maintain current USA ticket.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-04-27 | Operator excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3373 |  | 5 |  | SDGE | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Leak investigation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | ERIC REYNOLDS | SOLANA BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor failed to pot the gas line and augured right through the 0.5 inch poly. the mark out was off by roughly 16 inch which is within the acceptable 2 foot mark.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | TESLA | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | OPTION ONE SOLAR | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while excavating near gas facility.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JOSH MALO | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner Josh Malo stated he was digging around Palm tree when he hit 0.5? PEDuPont gas service with shovel. He said he thought it was a palm tree root. Also stated He did not call in a USA. However he did show me pictures of an old USA ticket from 2 years ago that thought was still valid. I told him USA Tickets are only valid for 28 days.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-09-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1931 |  | 8 |  | SMART SOALR | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was trenching with a shovel to install an electric conduit when they hit the 0.50 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SEMPER SOLARIS | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while digging near facility.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | GASPAR ESTEBAN | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | Y | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | LUIS SOTO | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE Service hit with drill
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | CARLOS VALDEZ | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE stub hit with hand tools.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-09-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | EVOLUTION CONCRETE | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch poly service hit with an auger.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2021-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5845 |  |  | NA | SCHILLING PARADISE | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3 inch poly main hit with an excavator, contractor not able to provide USA ticket number.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2021-01-01 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5845 |  |  | NA | JOSE ALVAREZ | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Reportedly hit 3 inch PE main with shovel while planting tree.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | STONEBROOK LANDSCAPES | SAN MARCOS | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch PE Service hit with Mini Excavator while trenching for drain installation
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2021-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | SIERRA LANDSCAPE | SOUTH EL MONTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2021-03-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | SCHILLING CORPORATION | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 inch PE Main hit with Backhoe. No USA Markout
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2021-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | EDWIN STOLL | LAKESIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 1.25 inch PE service with backhoe. No USA.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2021-11-08 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | ANGEL SANCHEZ | ESCONDIDO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while digging near gas service.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2021-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | AC SPRAGGINS ENGINEERING UNDERGROUND INC | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was trenching with a mini ex when he severed the 1 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2021-12-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | UNKNOWN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA notification
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SCOTT STEARNS | SAN MARCOS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA
San Diego Gas and Electric | N | SAN DIEGO | SAN YSIDRO | 2021-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3051 |  | 24 |  | KTA CONSTRUCTION LIC 398284 | ALPINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While pot holing contractor hit 0.5 inch poly gas service
San Diego Gas and Electric | N | SAN DIEGO | SAN YSIDRO | 2021-07-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3793 |  | 11 |  | KTA CONSTRUCTION | ALPINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was installing water main
San Diego Gas and Electric | N | SAN DIEGO | SAN YSIDRO | 2021-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | KTA CONSTRUCTION | ALPINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While trenching for a water main install 3rd party contractor hit 0.50 inch poly service.
San Diego Gas and Electric | N | SAN DIEGO | SANTEE | 2021-10-05 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | ERNIE CRUZ | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor failed to exercise caution while digging
San Diego Gas and Electric | N | SAN DIEGO | SANTEE | 2021-07-19 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3836 |  | 3 |  | MAN GENERAL ENGINEERING INC. | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 7-19-2021, a third-party contractor damaged a 2-inch plastic gas main with a directional boring at 9820 Mission Gorge Road, Santee, CA when excavating to install communication conduit. SDG&E crew responded and controlled the release of gas, there were no injuries resulting from this incident. The investigation showed that the contractor had a valid USA ticket A211950987, however, contractor failed to pothole the area prior to excavating. This incident was reported to the CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2021-07-19 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JESSE MORENO | SAN DIEGO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.50 inch PE service hit with shovel while hand exposing.
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2021-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3417 |  |  | NA | PACIFIC WEST COMMUNICATION | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit properly marked 1 inch Steel Service
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2021-07-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JESSE MORENO | SPRING VALLEY | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.50 inch PE service hit with clay digger
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2021-09-29 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | HENKELS AND MCCOY | SAN DIEGO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging weld hole for a grundo shot when they hit the 0.50 inch poly service with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2021-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | PACIFIC WEST COMMUNICATION | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.75 inch Steel service hit with trencher
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2021-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | BELL CONSTRUCTION | ENCINITAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE cut with sawzaw
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2021-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SECRETARIA SILVIA | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inch PE service cut with poly cutters
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2021-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JOSE ALVAREZ | CARLSBAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2021-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | RUDY GARCIA | MESA | AZ | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inch PE service cut with sawzaw
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2021-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | CAL CAMPBELL | ENCINITAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE Service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | SHASTA LANDSCAPING | SPRING VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer did not have valid USA for Location
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2021-04-22 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1872 |  | 4 |  | SHELDON CROMWELL | LAKESIDE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | inadequate excavation practices, lack of caution
San Diego Gas and Electric | N | SAN DIEGO | VALLEY CENTER | 2021-02-10 | Third party excavation damage | Not Available | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | PACIFIC PRODUCTION PLUMBING | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 2 inch PE Main with Backhoe
San Diego Gas and Electric | N | SAN DIEGO | VALLEY CENTER | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2814 |  | 2 |  | TOM VEYSEY | VALLEY CENTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ROBERT BOCKSTAHLER | VISTA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE Service with Post Hole Digger
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | DAVID VARELA JR | VISTA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE Service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JAVIER LEON | OCEANSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inch PE service hit with pick axe
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | VISTA IRRIGATION DISTRICT | VISTA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 0.75 inch Steel Service hit with Backhoe
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ERIKA DONICA | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 0.5 inch PE service with
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | BRIDGETTE SPITERI | VISTA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE Service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | REAGAN HELMS | VISTA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch Service hit with trencher. No USA
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | WESTERN OUTDOOR DESIGN | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE Service hit with shovel while digging to install drain
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-05-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SALVATORE CIRINCIONE | VISTA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | BRUCE BAKER | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE Service hit with hand tool
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ERIC STEPHENS | VISTA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inch PE Service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JDN CONSTRUCTION INC | FALLBROOK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE service hit with backhoe
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JOHN STEVENSON PLUMBING HEATING AIR CONDITIONING | CARLSBAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE Service hit with mini excavator was not marked.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-02-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | BLOCK CONSTRUCTION | OCEANSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 inch PE Service hit with shovel while exposing to install gas line for pool and ACU.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | SCHIMENTI | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | the contractor dug without a USA ticket and failed to us caution
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MICHAEL YOUNG | VISTA | CA | N | Y | Yes | No | No | No | No | Yes | No | 0.5 inch PE service hit with shovel. USA Ticket was expired. Marks not visible
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MC LANDSCAPING | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inch PE service hit with jackhammer
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2021-09-14 | Third party excavation damage | Main | Material not known | Not Available | 0 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was working on 2 inch poly main for a tie in when they noticed gauges in the pipe from back fill material
Southern California Gas Company | N | FRESNO | DEL REY | 2021-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | DEL REY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged 1 2 service while excavating to bury a dog
Southern California Gas Company | N | FRESNO | FRESNO | 2021-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | FRESNO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer claimed they call DigAlert but it feets been a while. While digging to install a fence post, homeowner damaged a 0.5 inch plastic line, crew made permanent repairs.
Southern California Gas Company | N | FRESNO | KINGSBURG | 2021-07-01 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | CABLECOM RALLY COMMUNICATIONS | FRESNO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 2 plastic main crew made permanent repairs
Southern California Gas Company | N | FRESNO | KINGSBURG | 2021-06-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DCW CONTRACTORS | VISALIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Augering to install street lights
Southern California Gas Company | N | FRESNO | PARLIER | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CITY OF PARLIER | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged live riser while working to demo building crew made permanent repairs
Southern California Gas Company | N | FRESNO | REEDLEY | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | DAWSON MAULDIN LLC | SELMA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party using an auger to drill hole to install fence and accidently hit service.
Southern California Gas Company | N | FRESNO | REEDLEY | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | IMMANUEL SCHOOL | REEDLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 inch steel service, crew made permanent repairs, contractor dug before USA ticket was valid.
Southern California Gas Company | N | FRESNO | REEDLEY | 2021-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | REEDLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 0.5 inch service while removing tree stump, no usa was called.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2021-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TOM WATSON INC | EL CENTRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 1 inch service trenching for electrical. Did not call USA. Service was already marked due to prior USA for different contractor.ï¿½
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TOM WATSON | EL CENTRO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging and hit the 1 2 stub with the backhoe no USA
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | POWER PLUS | DESERT HOT SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hand digging to install electrical when he hit a 0.5 inch stub.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MUNOZ TRENCHING | HUNTINGTON PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching to install footings and hit the service line. No USA.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2021-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was hand digging to install fencing and hit the service line no USA
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2021-12-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | CHRISTOPHER CAMARILLO | EL CENTRO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to install a sprinkler system and hit the service line.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2021-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GINO CAMARENA | BRAWLEY |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a backhoe and struck the service line.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RAUL GARCIA | BRAWLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | primary contractor failed to mark house service when trenching for new main. struck service when digging with backhoe.ï¿½
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2021-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | A R CONSTRUCTION | BRAWLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading when he hit two service stubs no USA.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | KAY CONSTRUCTION | SANTEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with a backhoe to install a water line when he hit the service line.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | A R CONSTRUCTION | BRAWLEY | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor was grading and hit the service lin.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | CORNELIO ANDRADE | CALEXICO |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging in yard did not notify USA and struck Service.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-07-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SPECTRUM CONSTRUCTION GROUP INC | IRVINE | CA | N | Y | Yes | No | No | Yes | No | Yes | No | Contractor was using a backhoe to install conduit when he hit our 2 main USA ticket was not valid and the prior USA ticket had expired Expired ticket was A211651065
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-08-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RAMCO RE LLC | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to install conduits when he hit the service line with the backhoe no USA
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ENRIQUE SILVA | CALEXICO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was hand digging to install a new sewer line and hit the service line no USA.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-09-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 8 |  | GUSTAVO RODRIGUEZ | EL CENTRO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging near the riser to reinforce the foundation and hit the gas line no USA
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | A R CONSTRUCTION | BRAWLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging a trench to install a waterline and hit the service with an excavator.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-09-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | GABRIEL BAILON | CALEXICO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage report completed and forwarded
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BEATRIZ ALVAREZ | CALEXICO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging a hole for a tree and hit the service line no USA.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | A R CONSTRUCTION | BRAWLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was using a probe to locate the main and struck the service USA was current and located properly
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | A R CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor digging to replace a water line with an excavator and struck the service line.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-05-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | LANCO UNDERGROUND | ALPINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to install communication conduit and hit the main with a backhoe while exposed.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | A R CONSTRUCTION | BRAWLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was trenching to install a new water pipeline and hit the gas service line with a backhoe.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | A R CONSTRUCTION | BRAWLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor digging with a mini excavator and hit the service line.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2021-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JORGE COTA | CALEXICO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was hand digging doing some landscaping when he hit the service line no USA
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | IMPERIAL IRRIGATION DISTRICT | IMPERIAL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | IID was using an auger to install a new power pole when they hit the service line.ï¿½
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2021-11-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SANDRA RODILES | EL CENTRO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged the service while excavating. It appears that a cut was made to verify if the pipe was live.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2021-07-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SUN LANDSCAPE | IMPERIAL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor was digging with a backhoe to install a water line and hit the 2 main No USA
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | EL CENTRO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was using an auger to install fencing and hit the service line no USA.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2021-02-03 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | AM ORTEGA CONST | NA |  | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was replacing a SCG service and had difficulty locating the service and hit the existing line with the accubore.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2021-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | MICHAEL WILLIAM MORDAH CONSTRUCTION | EL CENTRO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging for sewer repair and damaged 2 inch PLA main. No USA
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2021-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | EXECUTIVE LANDSCAPING INC | FALLBROOK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 week prior landscapers hit service with trencher. Service had EFV which slowed leak, and they backfilled trench. Odor reported by developer
Southern California Gas Company | N | IMPERIAL | HOLTVILLE | 2021-12-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JOSE GARCIA | HEBER |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Demo building, no USA.
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2021-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PYRAMID CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading and hit three service lines.ï¿½
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2021-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RADCO | BRAWLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was potholing for the main and they hit the punch tee with the backhoe failed to hand expose the main USA current and line marked correctly
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2021-08-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GEORGE LANE | OCOTILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Nielsen Construction 3rd party contactor damaged 2? service with backhoe while trenching for installation of electrical pipe Damaged service line was inside of an open trench Contractor did not obtain USA ticket prior to trenching Fire dept left the scene after ETR arrived Area near damage was vacant and blocked to prevent pedestrian traffic ETR monitored ambient readings and underground samples gas not migrating to foundation Gas Ops controlled leak at 6 46 a m and permanent repairs were made There were two outages caused from the damage Gas was restored after Gas Ops completed repairs There were no evacuations street closures injuries or media on site Cause of damage not Gas Company related
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2021-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SELF | IMPERIAL BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2021-10-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DUGGINS CONSTRUCTION INC | IMPERIAL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ETD had to locate service line by measurements, Locating wire gave no usable signal.ï¿½
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2021-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | IMPERIAL | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging to install a new wood fence and hit the service with a shovel no USA.ï¿½
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2021-12-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KRUSE ELECTRIC | FONTANA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor struck our plasticï¿½service while installing water main
Southern California Gas Company | N | IMPERIAL | NILAND | 2021-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MARTHA SANCHEZ | NILAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | H O was trenching to install sewer when he hit the service line to the branch with a shovel.
Southern California Gas Company | N | KERN | ARVIN | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MARIO GARDNER | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gardner hot SVC while doing yard work
Southern California Gas Company | N | KERN | ARVIN | 2021-07-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ACCURATE TRENCHING | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Accurate Trenching damaged 1 PE stub while excavating for Utilities
Southern California Gas Company | N | KERN | ARVIN | 2021-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LIBERTY PLUMBING | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator hit SVC with backhoe while exposing septic USA was good and marked
Southern California Gas Company | N | KERN | ARVIN | 2021-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | ARVIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner was excavating with mini excavator and had struck service while digging. USA was valid all marks were visible and hit within delineationï¿½
Southern California Gas Company | N | KERN | ARVIN | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | ARVIN | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | land digging to fix sewer line and hit our line
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BUILT WRIGHT | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cory Wright with Built Wright Construction damaged the service while trenching for a gas houseline to the backyard
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JEFF GRAHAM | BAKERSFIELD |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit service with pick.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | BAKERSFIELD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner Ralph Gonzalez hit SCG service line with a pick while excavating to install a French drain
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KENNY OLIVER | BAKERSFIELD |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner hit 0.5 inch plastic service with shovel while digging to install irrigation. No USA.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | MARANATHA LANDSCAPING | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HIt Service with shovel No USA
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | BAKERSFIELD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging hole for fence post and hit serviceï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-03-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ACCURATE TRENCHING | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck the 1 feet feet PE stub while excavating to install utilities.ï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-09-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BRAIDEN SHEPHARD | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Balfanz Homes employee Braiden Shepard was excavating to move communication lines when he damaged the service NO USA
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-06-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ACCURATE TRENCHING | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Accurate Trenching failed to hand expose before machine excavating.ï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CHRIS | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscape company hit service with shovelï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ACCURATE TRENCHING | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Accurate trench failed to hand expose before machine excavating
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | UNDERGROUND EXPRESS | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The locator foundï¿½no wire to connect the receiver to, he then marked the serviceï¿½by measurements. He spoke with the contractor that the service was located by measure, recommended to pothole prior to digging and to call if cannot find the service. As he recommends for all located services. The contractor explained that he begins to trench several feet away from the mark and then potholes for the service. By not following the proper sequence in potholing the consequenceï¿½was that the PLA service was damaged six feet north of the markingï¿½whileï¿½trenching. The pothole for the service was not done inï¿½proper practice of two feet on each side of the markï¿½instead found a hole of an eighteen inch hole representing the pothole.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-10-20 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | COMCAST CO | BAKERSFIELD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | contractor was digging with a backhoe trenching for electrical and hit our 0.5 inch ips service. paint was laid down indicating our line location but contractor never pothole to verify. while digging along the side of our line they snagged the service causing the damage.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | A MARC OF EXCELLENCE | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator struck line while digging to install electrical. Excavator failed to expose line by hand digging.ï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ALFONSO GOICOCHEA | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper had dug trench for sprinklers and hit service while doing soï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | UNDERGROUND EXPRESS | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While Pot holing for service they it service with shovelï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | UNDER GROUND EXPRESS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Boring Company was boring in communications and had hit our service. all was marked out and pipe was not exposed as required prior to boring operationsï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-07-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WILLIE REYNEVELD | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading to put on new Road and hit 2 Main No USA was on file
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-06-28 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 15 |  | RAMIREZ MANAGEMENT | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor, Ramirez Management struck SCG gas main while fixing sprinkler system for Taco Bell.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOSE ORTIZ | BAKERSFIELD |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Handymen working for homeowner damaged 0.5 inch CTS gas line. USA was called and valid. Locator marks were beyond 2 foot, tracer wire issues confirmed due to continuity issues with inserted pipe.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | R J PERFORMANCE | SAN FERNANDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | R J Performance damaged the 1 Service while it was exposed
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SIMMONS CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor for Business was installing electrical and hit 1 inch Service with shovel. USA was good and markedï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | THE PLUMBING DOC | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | SOUTHWEST CONSTRUCTION | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Southwest Construction failed to call in a USA before working
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | BAKERSFIELD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Homewoner while digging hole for tree hit service
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | BAKERSFIELD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging to remove tree stump and hit service
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-01-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | CHUCK BENNETT | BAKERSFIELD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor was digging for Septic tank on an expired USA Ticket and hit 2 inch Main with excavatorï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging for Landscaping and Pot holes to expose and hit service with shovelï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2021-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EMPIRE ELECTRICAL SOLUTIONS | SAN LUIS OBISPO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Empire Electrical Solutions damaged the 0.5 feet feet plastic service while trenching for electrical. No USA was called in. Crew repaired the service and shaded pipe with warning Mesh. Crew aerated until conditions were made non Haz.ï¿½
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2021-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BRANDON MCGINNIS | CALIFORNIA CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 2 service by homeowner No USA
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | ARI JET COMMUNICATIONS | POMONA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was pot holing 0.5 inch plastic service with a shovel when damage ocurred. Service was marked correctly.
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2021-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | CALIFORNIA CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage by homeowner while excavating with no USA to install post in private property
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2021-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 1 |  | MUSA WADUD | CALIFORNIA CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic stub with no EFV was hit up at property.
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ACCURATE TRENCHING | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 2 service by 3rd party contractor trenching for foundation footings w No USA
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2021-08-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HIGH DESERT DEVELOPMENT | CALIFORNIA CITY | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Damaged 2 plastic main by 3rd party contractor USA was not valid
Southern California Gas Company | N | KERN | DELANO | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | J M PIPELINE | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Big ben
Southern California Gas Company | N | KERN | FRAZIER PARK | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | FRAZIER PARK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor was digging a trench to install new sewer line for back ADU.ï¿½ They hit our plastic 0.5 inche service with shovel while digging.ï¿½ No USA was called in.ï¿½ Permanent repairs made.ï¿½
Southern California Gas Company | N | KERN | IRVINE | 2021-03-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CORNERSTONE CONCRETE TROY DIXON | NEWPORT BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, contractor hit gas line.
Southern California Gas Company | N | KERN | LOST HILLS | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SPECIALTY CONSTRUCTION | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Specialty Construction damaged abandoned service on the North side of HWY 46 across from 21155 HWY 46. Service history shows full abandonment. As found conditions show 3 foot pup. Service history incorrect. No way of locating stub by company locator.ï¿½
Southern California Gas Company | N | KERN | LOST HILLS | 2021-09-24 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 50 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SIERRA CONSTRUCTION AND EXCAVATION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Main was nicked by backhoe main was not leaking and installed full encirclement clamp on pipe filled out damage report supervision notified will continue to monitor situation per weekend temp repairs made perm repairs will start 9 27 21 Permanent repairs made by ARB 54 474688
Southern California Gas Company | N | KERN | MCFARLAND | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | SERDA PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber digging to repair water line hit service with shovel.ï¿½ No USA called inï¿½
Southern California Gas Company | N | KERN | MEADOW VIEW | 2021-06-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | EXPRESS ELECTRIC | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Express Electric struck SCG gas main with backhoe while trenching to install gas, electric, and street lights.ï¿½ Doing work for Wallace and Smith Contractors.
Southern California Gas Company | N | KERN | ROSAMOND | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WALLACE AND SMITH CONSTRUCTION | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit Service with auger preparing to set post to protect MSA, New Construction
Southern California Gas Company | N | KERN | ROSAMOND | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | ROSAMOND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating with a Backhoe to bury large dog H O hit Gas service No USA
Southern California Gas Company | N | KERN | ROSAMOND | 2021-03-23 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TEICHERT PIPLINES INC | CHINO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company Contractor Teichert Pipelines was excavating by means of hand tools when they struck our service.
Southern California Gas Company | N | KERN | ROSAMOND | 2021-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | ROSAMOND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging to install light post when he his our service.ï¿½
Southern California Gas Company | N | KERN | ROSAMOND | 2021-11-23 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BILL IRVINE | ROSAMOND |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeï¿½owner was digging trenchï¿½with shovel for water line improvement when he damage plastic service, No USA.
Southern California Gas Company | N | KERN | ROSAMOND | 2021-09-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GROUNDWORK ENGINEERING | PALMDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged Stub,ï¿½ No actual address new development. Lot numbers only , no physical addresses.
Southern California Gas Company | N | KERN | SHAFTER | 2021-09-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SIM EBLING | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Sib Ebling failed to notify USA before excavating for a fence post resulting in damage to a 1 2 plastic service
Southern California Gas Company | N | KERN | TAFT | 2021-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RAMON MIRANDA | TAFT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging for irrigation hit service no USA
Southern California Gas Company | N | KERN | TEHACHAPI | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | L A PLUS | LA HABRA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The contractor was trenching to install a natural gas pool line. The contractor then damaged a plastic gas service to the house, they did not have a USA and are fully responsible.
Southern California Gas Company | N | KERN | TEHACHAPI | 2021-10-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SOUTHERN SIERRA CONSTRUCTION | TEHACHAPI | CA | N | Y | Yes | No damage to SUOF. | Yes | Yes | No damage to SUOF. | Yes | Yes | 3rd party contractor damaged a 0.5? plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | KERN | TEHACHAPI | 2021-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TYLER HOLBROOK | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Tyler Holbrook was hired to remove a fence post for the property owner. Tyler was tugging on the postï¿½to loosen itï¿½and pull it up. when he pulled it up he said he heard a hissing sound, uncovered the dirt and the the gas blew the dirt out of the hole.ï¿½ ï¿½
Southern California Gas Company | N | KERN | TEHACHAPI | 2021-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PJ SIMONOVICH | TEHACHAPI | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Struck service with backhoe while digging for sewer.
Southern California Gas Company | N | KERN | TEHACHAPI | 2021-12-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AARON SWANSON | TEHACHAPI |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCE Contractor dug prior to USA Ticket becoming valid. Investigation found ticket was completed on 11 9 as no conflict. Notes indicate ETD was at a different location than the damage based on coordinates and direction provided on the ticket.
Southern California Gas Company | N | KERN | TEHACHAPI | 2021-01-07 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 2 |  | OUTSOURCE UTILITIES CONTRACTORS CORP | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damage occurred to the 2 inch main due to a 2 feet jog near location of damage. Edison contractor drove ground rod through main.ï¿½ï¿½
Southern California Gas Company | N | KERN | TEHACHAPI | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | OUTSOURCE UTILITY CONTRACTOR CORP | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator replacing pole anchor struck gas service. Unmarked.ï¿½
Southern California Gas Company | N | KERN | TEHACHAPI | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALLIED PLUS | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor struck gas service when hand digging to expose gas line,ï¿½electric communications and joint trench.
Southern California Gas Company | N | KERN | WASCO | 2021-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 0 | 0 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | UNDERGROUND CONSTRUCTION | BENICIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service with excavator while installing electrical. USA was Validï¿½
Southern California Gas Company | N | KERN | WASCO | 2021-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | WASCO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit service while digging to repair Sewerï¿½
Southern California Gas Company | N | KINGS | ARMONA | 2021-03-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MATTOS UNDERGROUND | LATON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 1 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | KINGS | CORCORAN | 2021-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | NA | CORCORAN | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ï¿½Damaged 0.5 inch plastic gas line, crew made permanent repairs, contractor was educated about USA law.
Southern California Gas Company | N | KINGS | CORCORAN | 2021-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 31 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HERNANDEZ ELECTRIC | FRESNO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 0.5 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | KINGS | HANFORD | 2021-07-26 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 2 |  | LEO TIDWELL EXCAVATION | PASO ROBLES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged unmarked 2 plastic main crew made permanent repairs
Southern California Gas Company | N | KINGS | HANFORD | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | HANFORD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hand digging to install sewer line. No USA called in.
Southern California Gas Company | N | KINGS | HANFORD | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | LEO TIDWELL EXCAVATION | PASO ROBLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a ï¿½? service crew made permanent repairs
Southern California Gas Company | N | KINGS | HANFORD | 2021-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | INFINITY ENERGY | ROCKLIN | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 2 plastic gas service crew made permanent repairs contractor was educated about USA law
Southern California Gas Company | N | KINGS | HANFORD | 2021-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | IRISH ELECTRIC | TULARE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 1 2 gas line while potholing crew made permanent repairs
Southern California Gas Company | N | KINGS | HANFORD | 2021-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NICK CHAMPI ENTERPRISES | HANFORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 1 inch plastic service while using hand tools to remove stump. Crew made permanent repairs.
Southern California Gas Company | N | KINGS | HANFORD | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | NA | HANFORD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing fence digging for fence pole
Southern California Gas Company | N | KINGS | HANFORD | 2021-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | HANFORD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service while digging to install fence, USA was not called in.
Southern California Gas Company | N | KINGS | HANFORD | 2021-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 400 | 285 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | CAL WEST RAIN INC | KERMAN |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner hit his service with an excavator he rented to do landscaping with.ï¿½
Southern California Gas Company | N | KINGS | HANFORD | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | 99 PIPELINE | PORTERVILLE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 1 inch stub that was not on record, there was no way of knowing it existed.
Southern California Gas Company | N | KINGS | LEMOORE | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LEMOORE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer had ticket but over 28 days, customer damaged 1 inch service while trenching for water line.
Southern California Gas Company | N | LOS ANGELES | ACTON | 2021-05-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | LA COUNTY WATERWORKS | LANCASTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LA County Water hit exposed 4 inch PA Main with backhoe.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | POWEL CONSTRUCTION | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was using trencher to cut for planting of trees.ï¿½ No USA.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2021-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | POWELL CONSTRUCTORS | FONTANA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Powell Construction Hit a 0.50 inch plastic service while while preforming road work for city of Agoura. USA ticket was expired.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2021-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ELSA VAHDAT | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor did not call in a USA ticket and damaged our line while digging to installï¿½a drain.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2021-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | T D CONSTRUCTION UNLIMITED INC | PALMDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inch plastic CTS service with shovelï¿½while potholing.ï¿½
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2021-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARGOT MOSS | AGOURA HILLS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR TRYING TO EXPOSE GAS LINE AND FAILED TO USE CAUTION
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper damaged our service while hand digging to install plants. Contractor did not have a USA ticket.ï¿½
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2021-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | Y | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HUGO LARA | CHATSWORTH | CA | N | Y | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No USA was called in and contractorï¿½DAMAGED BY BACKHOE WHILE DIGGING FOR WALL FOOTING
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2021-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EVERETT KEENE PLUMBING | WESTLAKE VILLAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber was digging for house line repair when the hit a 0.50 inch plastic service. NO USA
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2021-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Not Gas Co related The contractor performing irrigation work for the customer damaged 1 2 plastic service with a shovel
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SHANA KLINE | AGOURA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Tenants son in law was digging in front yard to locate the drain because the toiletï¿½was backing up and he hit the 0.5 inch cts service with a shovel.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-09-17 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor working on for Gas Coï¿½DIMP project main replacement damaged unknown service 6north of W Shorb st on Atlantic Blvd. with Backhoe.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALHAMBRA WATER | ALHAMBRA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Water Company Exposed none marked 2 inch stl main and proceeded to drill into it to verify if live rather than calling USAï¿½to have all utilities verify. *** Company Locator inch NO SCG inch location based on how work area was delineate.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-03-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SONG AND SONS | ARCADIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No current USA for job site. Contractor damaged 2 inch plastic gas main with backhoe. Contractor states USA ticket had been called in prior to work.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FIRE PRO TECH | BURBANK |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | plastic service was struck during sewer line installation
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was digging to install anchor and hit a 1 inch service feeding address to the south of usa address location.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | L MATYAS | ALHAMBRA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working to install electrical line and ended up hitting and damaging 0.5 inch IPS service.ï¿½
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ILB INC | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 2 inch PX main not marked by company locatorï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-01-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | RAMONA INCORPORATED | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor fail to contact SCG ETD to verify pipe that was exposed , markings on the ground say plastic mainsvc contractor found steel and started using excavator to causing damage to plastic mainï¿½
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | RYAN ZHEN | BALDWIN PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor dug on private property and struck 0.5 inch plastic service .... NO USAï¿½
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-03-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RAMONA INC | ARCADIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was hand exposing for gas service found steel portion and assumed it was actual service proceeded to hand dig and struck plastic service 18 inch from actual mark.ï¿½
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-03-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RAMONA INC | ARCADIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Digging to expose service and damaged 0.5 inch plastic while digging directly over Gas Markï¿½
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  |  | NA | ERIC LEI CONSTRUCTION | ROSEMEAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | La Hacienda employee cut 1 inch IPS service while excavating to install drains, crew failed to call for USA markings.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | INTERNATIONAL LINE BUILDERS INC | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | No | No | Contractor pulling bore back to run conduits hit 0.5 inch ips service with machine. Contractor did not excavate service.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ILB INC | RIVERSIDE |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor installing sewer line for property owner, Gas svc was already exposed when broke. upon arrival contractor had left and waiting for property owner to respond with company name
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HILLSIDE STRUCTURAL AND FOUNDATIONS | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to maintain safe digging practices while digging over utilities that were marked
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-10-20 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GRBCON INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GENTRY BROTHERS CORP | BALDWIN PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor failed to notify Locator of work to be done ï¿½at address as agreed when positive response was made prior to ticket becoming legal job was dividedï¿½into phases.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VCI CONSTRUCTION LLC | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor had damaged gas service with drill headï¿½of bore machine.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2021-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARTINEZ CONCRETE | SAN GABRIEL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was using a miniï¿½excavator and hit Gas line. No USA was called.ï¿½
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2021-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CJ DEBOER ENGINEERING | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was working on sewer line and hit our plastic service with a mini excavator.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2021-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOHN CHAVEZ | ALTADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was installing water line cut casing with sawsallï¿½ ï¿½into plastic 1 2 cts service Use double squeeze to out of casing performed alteration
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2021-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | WESTERN ROOTER | ARCADIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | western rooter hit 0.5 plastic service while hand digging to expose sewer drain. NO USA
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2021-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TERAN IRON WORKS INC | BALDWIN PARK |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service whileï¿½
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2021-05-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JESUS CASTANEDA | SOUTH EL MONTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor struck plastic service while digging trench for wall.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2021-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DOCTOR ROOTER INC | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor for the cityï¿½of Thousand Oaksï¿½broke Plastic service while digging
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARK DAVIDSON | ALTADENA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber working for home owner saw saw through 0.75 inch steel service thinking it was water line.ï¿½
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2021-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GRAND POWER CONSTRUCTION INC | SOUTH EL MONTE |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging hole. Contractor struck plastic gas line.
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2021-10-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | PACIFIC MASONRY | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging with an auger to install fencing and damaged service.ï¿½
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2021-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WESTERN ROOTER | ARCADIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew was backfilling and hot cap with comp wheelï¿½
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ANGEL AGUILAR | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber hit gas service while trying to unclog sewer lateral. Plumber tried to make repairs to service but was instruct not to do it again. Crew altered service for permanent repairs.
Southern California Gas Company | N | LOS ANGELES | AZUSA | 2021-12-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BALENTE MARTINEZ | AZUSA |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Hitline , mismark due to tracing wire issue . Crew arrived and controlled gas release . Will couch employee to use all available tools and or ask for a pothole when all else fails .
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2021-03-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | GLS ENGINEERING | SAN GABRIEL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractorï¿½broke 1 inch plastic gas service and USA was not notified.
Southern California Gas Company | N | LOS ANGELES | BELL | 2021-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GOLDEN STATE WATER | NUEVO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor hit svc while installing a water main
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2021-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | FLEX ELECTRIC | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2021-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | NA | LYNWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hired by homeowner damaged 0.5 Cts service with shovel while trenching for sewer lateral. No USA
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2021-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | GOLDEN STATE WATER | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | hit svc
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | D CORP | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit svc while excavating service was marked correctly.
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | D CORP | NUEVO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor hit svc the service was correctly marked on one side of the street but not on the other side. The service veered off about 28 inch.
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JUAN SANCHEZ | GARDENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck plastic gas facility with mini backhoe while trenching for electrical light installation
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2021-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | H AND R HOME IMPROVEMENTS | LONG BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2021-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | ANTHONY OTANEZ | LAKEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor cut 0.75 steel service with sawzall
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2021-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | BELLFLOWER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Home owner nicked plastic service by hand while excavating for new sewer. USA marks accurate, damaged within 2 feet of marks.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2021-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | AZTEC CONCRETE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor cut 0.5 plastic service with sawzall
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TITAN BROTHERS PLUMBING ROOTER SERVICES | CHATSWORTH | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No USA at the time of incident
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2021-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TURN AROUND COMMUNICATIONS JOSE HERNANDEZ | WALNUT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor installing communications on private property hit our 0.5 inch plastic service.ï¿½ Contractor did not call in a USA ticket.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2021-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | BELLFLOWER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner was digging to install new houseline and hit our service line while hand digging.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2021-05-26 | Third party excavation damage | Main | Steel | Probing Device | 2 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 32 |  | HW POWER INCORP | NA |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | contractor struck 2 inch steel main with grounding rodï¿½
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2021-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ROOTER HERO PLUMBING | MISSION HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing contractor while making sewer repair cut thru 0.5 plastic service in 0.75 casing with sawzall.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | W A RASIC | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged an unmarked stubbed service
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TORO ENTERPRISES | BEVERLY HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 0.5 inch IPS service with backhoe
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TYLER DVELOPMENT | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping company was trenching when they damaged the 1 PLA service No USA was called in
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EZEQUIL GODINEZ | INGLEWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Call toï¿½USA for this work.ï¿½ Trencher struck PE service
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TORO | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor used backhoe to discover pipe
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-01-11 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 3 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MIDLAND CONTRACTORS | VAN NUYS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | main hit with backhoe while doing sewer work
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EXCLUSIVE POOLS | GRANADA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading property with a uniloader and damaged our 0.5 plastic service that was in casing in copper.ï¿½ No valid USA.ï¿½ Permanent repairs were made.ï¿½ Service is really shallow.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | H L DRMOLITION | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The USA ticket was not L M it wasï¿½sent back to the customer for no delineation The contractor began the excavation prior to calling back in the USA ticket Upon arrival I spoke with the foremen and the lead sub contractor I explained to them thatï¿½theyï¿½each need there own USA ticket I also informed themï¿½that they need to delineate the area in order for all utilities canï¿½be marked They delineated while I was there and where going to call in for USA tickets They where using a backhoe when the 1 2 IPS was damaged
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DYNAELECTRIC | LOS ALAMITOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator and contractor had a mutual agreement Contractor trenched prior to locator completing L M at the address Contractor damaged 1 2 PLA service
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CRUZ CONCRETE AND STONE INC | SANTA CLARITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA While replacing drainage pipe contractor cut through gas service with sawzall
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RT SERVICES INC | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No call for USA Contractor hit 1 2 cts service with shovel while digging
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JACK S POOL AND SPA | PANORAMA CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA contractor cut 1 2 service while digging line for pool
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EXCELLENT FIRE PROTECTION | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to install reclaimed water pipes
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SHIELDS SEWER CONTRACTING | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party crew damaged 3 4 STL service by next to the valve casing The crew assumed that the valve was a water shut off The crew was working with expired USA and permit
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RALPH HERNANDEZ CO | SANTA ANA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor hit plastic service while digging with excavator contractor did not pot hole for our service before digging ETD got bad signal when locating plastic service went off measurements in SVC history Plastic service was in casing with no locating wire
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RICHARDS CONSTRUCTION CO | SOMIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged SL while digging to install fiber optics
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SDR BUILDERS | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party crew hit 1 inch service while trenching.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | EDISON | SANTA MONICA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Matt Hilton Public Works inspector II from city of Beverly Hills confirmed with SCE that they excavated at the wrong address. No USA, damaged 0.5 inch CTS service.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ASHAI DESIGN | BEVERLY HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was excavating to install a power conduit. He hit the 1 inch plastic service with a backhoe. USA was not notified.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-02-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ASHAI DESIGN | BEVERLY HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service cut by contractor installing electrical conduit
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HITECK | SHERMAN OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | excavator hit main while digging for electrical lineï¿½
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-01-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WAR CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | damaged service to pool house
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SOUTHERN CALIFORNIA ELECTRICAL FIRM | TORRANCE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Per LCT Lupe Castillo, Third Party contractor was digging with Backhoe to install power when plastic service was hit. unmarked.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | BEVERLY HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor for 1332 Laurel Way wasï¿½digging to repair drain on side of property and damaged service to 9656 Lawlen way with a hammer
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2021-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | STERN SERVICE COMPANY | CHATSWORTH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit 0.5 inch IPS service with saw zaw while tryingï¿½to repair sewer.ï¿½
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARROW SPRINKLER AND LANDSCAPE INC | SUN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor remodeling back yard and pulled on tree stump and pulled gas serviceï¿½
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1.25 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PROFESSIONAL CONCRETE CUTTING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | saw cutter cut through gas service, did not call for USA
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | GLENDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner, Aram Papazian, was grading property with backhoe and struck SCG service line.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | E MANDZHOYAN | BURBANK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer hit 1 2 while digging footing for brick wall advised customer to call 811 to avoid these problems
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BURBANK WATER POWER | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | BWP hit plastic service while excavating with Backhoe to install Water Main Service was not marked properly due to no visible locating wire GIS and measurements were off Leak was repaired by SCG Crew
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MARINE AVAG AGAZARYAN | BURBANK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While placing a new sewer line, homeowner contractor failed to pot hole a marked service line damaging the pipe with a track hoe.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-04-05 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ARB | NA |  | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor did not try or look for meter on school property
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EXTREME HOME ADDITIONS | BURBANK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1 2 plastic service with shovel while installing landscaping Crew repaired service
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CHAMPION BUILDERS | AGOURA HILLS |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3644 |  | 5 |  | LOS ANGELES SIGNAL CONSTRUCTION | SAN DIMAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 4-14-2021, a third-party contractor damaged a 2-inch plastic gas service at 2585 North Hollywood Way, Burbank, CA 91505 when excavating to abandon a signal pole. Crew responded and controlled the release of gas, and made permanent repairs by replacing a section of the service. The investigation of the incident showed there was no valid USA ticket for the contractor. This incident was reported to the CPUC when SoCalGas became aware of media coverage.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-06-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OVERTON MOORE PROPERTIES | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor kinked 2 inch gas service on 6 15 21 and called Field Planner next day. Contractor does not call for USA in private property.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | BURBANK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor hit a 0.5 inch IPS service with a Jackhammer while trenching. No USA ticket.ï¿½
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | UNKNOWN PER LCT | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit plastic service with post hole digger
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VART CONSTRUCTION INC | GLENDALE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | Expired USA Exp 5 26 2021, Trenching To Install Sewer Line, Failed To Expose Gas Line With Caution
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-04-08 | Third party excavation damage | Riser | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | KOMPLETE INC | BURBANK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor thouht it was a water line.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BURBANK WATER POWER | BURBANK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Contractor hit 1 2 plastic service while excavating to install a water lateral They saw the mark for a steel service but missed the plastic service and accidentally cut it with a backhoe ï¿½
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2021-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MHER KHANOYAN | BURBANK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 2 CTS service by homeowner digging w no USA to install irrigation
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2021-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WAY TO GO BUILDERS INC | WEST HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Way To Go Builders struck SCG 1 2 PA service line with hand tools while trenching for electrical conduit for property owner Sean Rajaee ï¿½ Contractor installed plastic compression fitting and bent back service line to restrict blow SCG crew completed permanent repairs ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2021-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ERIC KAUFMAN | CALABASAS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew arrived and cold pitched steel to control the gas away from damaged area in trench already dug by plumber. Crew made repairs to restore service.ï¿½"
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SERENITY SCAPES | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper digging to plant trees with no USA
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2021-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SIMI VALLEY PLUMBING | SIMI VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner digging with excavator and claims service was struck with shovel.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2021-08-27 | Third party excavation damage | Not Available | Polyethylene Pipe | Miscellaneous/Other | 2 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | CALABASAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Not Gas Co related Gas Service was damaged with hand digging tools No gas leak or blowing gas The damaging contractor was not on site upon Gas Co s arrival
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2021-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | CALABASAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for developer when the hit a SCG 1 inch PLA Stub. Contractor left the scene. Developer should be billed.ï¿½
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2021-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BRIONES COMMUNICATIONS INC | SANTA CLARITA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was removing a stump using a stump grinder when the grinded into the 0.75 steel service.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TIDWELL | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Tidwell was potholing and struck with clay spade due to hard soil.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2021-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALL WATER POOL AND CONSTRUCTION | SAN FERNANDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Drunk driver hit a MSA
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2021-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALL WATER POOLS CONSTRUCTION | SAN FERNANDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2 inch plastic main was hit while Doty Bros was trenching for water main. Line was notï¿½marked out due to not being identified in GIS. Line was not shown on GIS map nor was there any service history.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2021-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BRIGHT VIEW LANDSCAPE SERVICE | SAN FERNANDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscapers installing irrigation lines with no USA
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2021-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WAGEMN INC | WINNETKA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. party contractor was hand digging and hit 1 feet service. No USA was called in
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2021-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | HIDDEN HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Damaged 1 inch Plastic service wile cutting roots with a Hack Saw to repair the water service to the Home.ï¿½
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2021-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FILIBERTO | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber digging for sewer lineï¿½
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2021-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CANOGA PARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damage 1 2 SVC while digging for sewer No USA Called in
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2021-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CANOGA PARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner digging for water leak failed to call USA
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2021-12-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | LADWP | NORTHRIDGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | PEï¿½service hit during installation of new fencingï¿½
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2021-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOSE NAVARRETE | CANOGA PARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Valid USA , Landscape company was digging at service location with a shovel and hit the 1 inch IPS Service. Seems as Warning Mesh was ignored and removed prior to hitting the plastic service.
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2021-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | J I HOME DESIGN | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR HIT SERVICE
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2021-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARTIN CONSTRUCTION INC | YUCAIPA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck 0.5 inchï¿½ IPS service while hand digging to repair an irrigation leak. They did not have a valid USA ticket prior to beginning work.ï¿½
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NIC CONSTRUCTION | CANYON COUNTRY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called Contractor hit 1 2 CTS service while digging for electrical work
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RJS ELECTRIC | CASTAIC | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 2 svc with backhoe installing electric lines
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2021-08-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 50001 |  |  | NA | GRIFFIN STRUCTURES | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No gas complaint Sent APL out to investigate the EFV at the smc EFV functioning correctly fish taped service discovered a blockage and tested service and failed the pressure test dug up and blockage point and discovered the damage portion of pipe
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | BLUE JAY CONSTRUCTION INC | CANYON COUNTRY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor was hand digging to install post for carport when they struck and broken our 0.5 inch service.
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CANYON COUNTRY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, Contractor hit 0.5 IPS service while installing a rod into the ground to support a shade awning
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2021-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FERREIRA CONSTRUCTION | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was aware of gas line and marks. hit service with backhoe
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2021-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | GLEN SWANSON | CANYON COUNTRY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | cust hit serviceï¿½
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2021-12-20 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | N V LANDSCAPE | SYLMAR |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer getting work done to he is house NO USAï¿½
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2021-11-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ADVANCED DESIGN CONST | SANTA CLARITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While 3rd party contractor was excavating and installing a shoring box for the sewer lateral installation, they slicedï¿½our 1 inch service in half.
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2021-03-04 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | FENCEWORKS | SANTA PAULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | company hired by homeowner to install fence post. never called USA and augeredï¿½ through 2 inch plastic mainï¿½
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2021-06-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TEJON CONSTRUCTION | NA |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | tejon hit the end of a 2 inch main with a backhoeï¿½
Southern California Gas Company | N | LOS ANGELES | CARSON | 2021-12-06 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 49 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | HAMPTON TETTER ELECTRIC | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | NO USA REQUESTED, CUSTOMER DIGGING FOR A FENCE
Southern California Gas Company | N | LOS ANGELES | CARSON | 2021-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 49 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | CARSON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner was cutting roots and confused gas service for a root. usa was not called by home owner.ï¿½
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | AK CONSTRUCTION | NORTHRIDGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Worker for AK Construction was hand digging with shovel to install a fence post and hit 1 2 plastic service
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2021-11-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TEJON CONSTRUCTION | PALMDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Locator used ALL company tools to locate out ALL mains and services on this street. 2 inch stub was NOT showing up onï¿½GIS, SAP or Service History. 2 inch stub was cut back at the main, and we submitted for a service ID at this location so we can close out order.
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SULLY MILLER | BREA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | water company punched thru 1 2 cts line with depth probe
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2021-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | CASTAIC | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Home owner digging for irrigation hit 0.5 feet cts gas line. Line tapped back upon arrival. Crew made repairs to damaged area.ï¿½
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2021-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RS1 PLUMBING | BURBANK | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | contractor hit service line in casing when trying to repair the sewer. contractor failed to pothole service as agreed upon with locator and sign form 5153a agreeing to pothole looking for service line that was not able to be located.ï¿½
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2021-01-19 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARIZONA PIPELINE | MONROVIA | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to exposeï¿½Main and struck service. No locate wire was present with existing service.
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2021-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ROGER SANCHEZ | CHATSWORTH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner was trenching with a shovel to install new sewer lateral and struck the 1 2 plastic service line no USA was called in Company crew arrived and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2021-05-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | CHATSWORTH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 0.5 inch IPS service w a shovel and clamped themselves. Homes are in construction stagenew track homes Nobody onsite except oneï¿½worker who left once showing the damage locationwould not give any info..~K.Rodriguez~
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2021-07-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LANDS HOMES | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor hit 1 2 IPS Svc No USA called in
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2021-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | MARIO MORENO | VAN NUYS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor for homeowner was excavating for sewer installation.ï¿½ Contractor had a current USA but failed to prevent damage to gas line even though it was properly marked.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2021-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MEDEARIS CONSTRUCTION | TEMECULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Trenching with machine and hit svcï¿½
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2021-01-08 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HENKELS AND MCCOY | CHINO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG Contractor digging at PL to open trench install new PE service damaged existing 0.5 inch PA service.ï¿½ Existing service was exposed rest of private property but did not practice proper digging techniques while exposing service at PL and managed to nick service on side of pipe.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GORDON TAYLOR PLUMBING | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbers digging to install water service with no USA
Southern California Gas Company | N | LOS ANGELES | CITY OF COMMERCE | 2021-12-18 | Third party excavation damage | Not Available | Material not known | Not Available | 0 | 0 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | service line was damaged while excavating sewer lateral
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | VALVERDE CONSTRUCTION | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | crew trenching with with back hoe and failed to properly hand expose line before digging with hoe line was marked correctly and clearly
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2021-12-12 | Third party excavation damage | Main | Material not known | Trencher | 2 | 50 | 47 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LCE GENERAL CONTRACTOR | BURBANK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck gas line marked incorrectly Locator notes Weak signal for 244 81st St. Weak locator location and measurements match.ï¿½
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2021-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | VALVERDE CONSTRUCTION INC | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1 2in CTS pipe hit Service was marked with measurements but company records were off Verified this myself Also hooked up to riser no wire on plastic service could not get a signal no way for the locator to mar this other than measurements contactor could have pot holed and called if they didnt find it but marks were further away down the trench line than this damage aalrayess
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | CALIFORNIA LANDSCAPE DESIGN | UPLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor did not call USA because work was only being done in the backyard ï¿½ but they dug right next two meter assuming service ran straight to the street but it was in fact a branch service ï¿½
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | GOLD COAST PLUMBING SOLUTIONS | UPLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor hit plastic service while digging trench for sewer. Contractor claims service was not marked on private property but mark was visible at curb and flag was found a few feet away from damage in the bushes. USA was called but expired.ï¿½
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2021-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | VALVERDE CONSTRUCTION INC | SANTA FE SPRINGS |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor while pot holing damaged the PLA pipe. The pipe was marked within the delineation.
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2021-08-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | VALVERDE CONSTRUCTION | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | SoCalGas locaterï¿½mismarked 2 inchï¿½PE MAINï¿½and 3rd party contractor hit the main with a backhoe. Locater was getting signal from the old main and not the plastic main.ï¿½Contractor did not follow up with locater about markings before digging.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2021-10-06 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 3 |  | DOMINGUEZ GENERAL ENGINEERING CO | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor potholing for utilities dug into 0.5 inch cts service with shovel. Did not have valid USA ticket
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2021-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CITY OF COMPTON WATER | COMPTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | city of compton municipality struck gas service while trneching for new water service.ï¿½
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2021-08-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | COMPTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damage to 2 plastic was found after digging for a leak that was already coded no known information on when main was damaged or who the damage was caused by
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2021-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GABRIEL ESTRADA | COMPTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.5 inch CTS service with shovelï¿½
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2021-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | COMPTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner digging holes for fence Did not have USA
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2021-10-11 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | RESOURCE ENVIROMENTAL CO | CERRITOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | compton unified school district contractor struck 2 inch steel main when digging for new utility.ï¿½
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2021-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | COMPTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner was digging for sewer line and struck our service. No USA
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DOMINGUEZ GENERAL ENGINEERING INC | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | service line struck while water contractor was trenching for new water service installation.ï¿½
Southern California Gas Company | N | LOS ANGELES | COVINA | 2021-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | DRAINTEK PLUMBING | STUDIO CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was splitting existing sewer line to install PE sewer and the splitter damaged the gas service. They had no USA and did not pothole the spot where the two services crossed.ï¿½
Southern California Gas Company | N | LOS ANGELES | COVINA | 2021-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | STEPHEN DORECK EQUIPMENT RENTALS INC | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Developer Owner said his workers were digging for gas lines and struck service with pick.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | COVINA | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CITY OF COVINA WATER DISTRIBUTION | COVINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Landscape company was putting a hole down for a post near house foundation and hit 0.5 inch PLA service with Sharp shooter digging shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | COVINA | 2021-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | COVINA | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | Home owner was cutting roots out and mistakenly cut through our 0.75 inch steel service with a Sawzall. He was not injured.ï¿½
Southern California Gas Company | N | LOS ANGELES | COVINA | 2021-11-19 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DORECK CONSTRUTION | PICO RIVERA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PLA Service was damaged by a shovel during trenching.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2021-07-26 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 3 |  | JORGE CARILLO | MONTEBELLO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Contractor should be billed for incident even though the marks were off due to the main was exposed at the time of the incident
Southern California Gas Company | N | LOS ANGELES | COVINA | 2021-06-30 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | WATER COMPANY CITY OF AZUSA | AZUSA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | water company was excavating water leak with vacuum truck and hand digging. Did not call USA and his 2in plastic main with probe causing small hole in main.ï¿½
Southern California Gas Company | N | LOS ANGELES | COVINA | 2021-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | NA | COVINA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner didn t call USA prior to digging for fence EFV tripped after damage
Southern California Gas Company | N | LOS ANGELES | COVINA | 2021-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SAMUEL RANGEL | COVINA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching to install gas HL, contractor did not have a USA and damaged 0.5 in plastic service.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor hit cut back steel service due to locater not knowing of service in area.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2021-11-05 | Third party excavation damage | Main | Steel | Augur | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 13 |  | CAL EX ENGINEERING | NEWHALL | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service with shovel whileï¿½ digging trench.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2021-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DOMINGUEZ GE | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit buried facilities while exposing it by hand digging.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2021-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LA CITY HOUSING AUTHORITY | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was working on property digging up trench to put in new sewer and struck 0.5 inch CTS pipe with back hoe in the process of digging trench.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2021-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | DANIEL JIMENEZ | CULVER CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging to install water lines, when digging with backhoe contractor struck gas line.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2021-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | LATLONG INFRASTRUCTURE | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Installing fiber optics using micro trench method.ï¿½
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | S S PLUMBING | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service while digging for sewer install. Hit with shovel.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2021-04-02 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | J A SALAZAR CONSTRUCTION | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While replacing water service, contractors pogo feetd through 2 inch plastic main during excavation.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2021-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SOUTHERN CALIFORNIA EDISON | CULVER CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 0.75 inch steel service with jackhammer while breaking out concrete on side of the house. No valid USA.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FACILITIES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch service damaged with shovel
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | LAT LONG INFRUSTRUCTURE LLC | CULVER CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service with hand tool while trenching to install communications conduit.
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2021-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VIDEO VOICE DATA | GARDEN GROVE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 0.5 inch service with shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2021-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RICKY AGAYO | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | 3rd party contractor hit service with a sharp shooter shovel and damaged our serviceï¿½
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SYSTEM PAVERS | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | grading driveway to install pavers
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | DIAMOND BAR | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | service had Bare wire hard to locate ETD had good signal into private property but communication cable over powered bare wire signal
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2021-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ERIM MEZA | DOWNEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT marks were there. But no number given
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NEIGHBOR | DOWNEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing Fence
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2021-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NEW BEGINNING CONSTRUCTION | WHITTIER |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor pulled 0.5 inch plastic service out of the ground and left exposed
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TECHIERT PIPELINE INC | CHINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching to install water main struck a 0.5 pe gas service marked 7 feet form its actual location
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2021-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SILVA DESIGN CONSTRUCTION INC | PASADENA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator damaged 0.5 inch CTS service with backhoe. Failed to pot hole service. Marks found across street and under spoil pile . Marks correctly
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CALIFORNIA POOL SERVICE | ARTESIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Pool company working for customer hit gas service.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CALIFORNIA POOL INC | ARTESIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was requested, digging for a pool
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2021-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WILLIAMS PIPELINE CONTRACTORS INC | SOMIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck a plastic service with a shovel while digging to expose the service.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WILLIAMS PIPELINE CONTRACTORS INC | MISSION HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per ETD on scene the contractor claims to have struck the plastic gas service with a shovel while exposing the pipe.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2021-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | REGAL WEST CONCRETE | ARTESIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging and hit gas service. contractor did not pot hole andï¿½verify marks on ground.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working at property damages a 0.5 inch plastic service and backfilled, did not report it.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2021-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | WINSTON OSSER | DOWNEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner had his gardener installing a new irrigation line While digging the trench for theï¿½install the Gardener damaged the 0.50 plastic service.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GUILLERMO MEZA | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck 2 inch plastic while using auger attachment for bobcat.
Southern California Gas Company | N | LOS ANGELES | DUARTE | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | DOTY BROS | ROSEMEAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water crew damaged service while excavating water leak. lines were marked but crew failed to pot hole prior to digging with back hoe.ï¿½
Southern California Gas Company | N | LOS ANGELES | DUARTE | 2021-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SPECTRUM | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to call in USA to have gas utilities marked and proceeded to shoot accu bore shot from neighbors yard to address where damage was caused to gas service.
Southern California Gas Company | N | LOS ANGELES | DUARTE | 2021-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LEGACY COMMUNICATIONS | ONTARIO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Company started digging to install cable lines before usa ticket was valid.ï¿½
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2021-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VIKI LO | MONTEREY PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 inch cts gas service will digging for new constructionï¿½
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2021-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TREE SMITH ENTERPRISES | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service with tree stump grinder failed to pot hole for gas service
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2021-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALL CITIES ENGINEERING | EL MONTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 0.5 inch plastic service while installing water main and did not report the damage to the Gas Co. Customer called later in day due to having no gas.ï¿½
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ALL CITIES ENGINEERING | JURUPA VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Backhoe operator hooked on to service at smc and tore it off the 0.75 inch transition fitting failedï¿½to hand expose gas serviceï¿½
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2021-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CARMEL LANDSCAPING | EL SEGUNDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service was accurately marked with flags Landscapers were using an auger to set plants and drilled through our 1 PE service line Flags were in place and accurate Landscaper could not provide a USA number and I could not find anything in the system but there was a delineation with utilities located
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2021-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | EL SEGUNDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged cause by home owner with shovel when digging for footings on new driveway
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2021-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | HARRY GIBBONS | EL SEGUNDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damaged by customer no dig alert called
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2021-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | HUNTOON BROS | EL SEGUNDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Worker used sawzall to cut roots from excavation, but didn feett see plastic pipe below the tree roots
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-05-25 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARIZONA PIPELINE | CHATSWORTH | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG Contractor APL hit 0.5 inch IPS service at SMC while excavating. APL used improper techniques while digging exposing SMC.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-01-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LA DWP | NORTHRIDGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LA DWP damaged marked PE Service with backhoe . Service was new no meter installed as of 1 8 21. Per Supervisor D.Real due to heavy accumulation of water in ditch from up street, SCG crew installed PE Cap to eliminate code 1. Another crew returned on 1 11 21 to reinstate service once water issues resolved.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-04-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | E T DEVELOPMENT | ENCINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install curb and sidewalk, contractor hit 1 inch IPS service. No Valid USA
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MTJ DEMOLITION | TARZANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Building contractor hit 0.75 inch steel service thought it was abandoned. Cut back service for safety and pushed out abandonment order w planning
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | LADWP | NORTHRIDGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP was digging with backhoe to work on water main in the street and hit our 1 2 inch plastic service DWP had valid USA ticket number Gas service was correctly mark on time and visible DWP did not expose gas by had to verify
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | REAL PRIME CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractors were digging on hillside to plant a tree and hit our plastic service No USA was called in
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-07-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 8 |  | NA | ENCINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging on a empty lot trenching to install sewer lateral and hit our 2 inch plastic main that was in the parkway Contractor did not have a valid USA Company crew pinched 2 inch plastic main that fed the cul de sac and was able to make permanent repairs
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ZARP INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor failed to pothole gasï¿½
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | ENCINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowners gardenerï¿½hit 0.5 inch IPS while digging for irrigation. NO USA was called in
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BERKUS DEVELOPMENT | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Cust was demo most of the house and nicked the 3 4 inch steel service Cust has valid USA ticket and facility was marked out correctly Repair was made with a 3 4 inch clamp and advised contractor to have owner call in to have abandonment done why they rebuild Leak repair completed same day
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | L BARRAZA | ENCINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to install new sewer line and hit plastic service in casing.ï¿½ No USA was called in in.ï¿½
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DANIEL KANG | ENCINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to expose gas line and hit service. All marks were visible and USA was good.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ACCESS EXCAVATING | CALABASAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor performing subgrade and cutting down driveway to bring up with base material hit gas service They had no USA and assumed lines were deeper Crew performed service alteration to mitigate damage Third party contractor indicated they will not be going deeper than current excavation
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-11-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | CIRCA DEVELOPMENT INC | GRANADA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging 3rd. party contractor gas line with Jack Hammer. No USA called in
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SB CONSTRUCTION AND REMODELING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging out for Dticket with no USA provided USA was for temporary power pole
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2021-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | NA | GARDENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Customer damaged Gas Service while trying to expose gas line.ï¿½Marks are visible.ï¿½
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | J J FENCHING CONTRUCTION | COMPTON | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Could not distinguish the poly pipe from tree roots where footer was being installed
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HHS CONSTRUCTION | GARDENA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service line was in copper casing and locate reads were going to meter right next door about 8ft away and employee assumed it was a standard and branch like the other homes in the area Employee could not access service history but when using indirect method the locater accurately followed the line out to the street where there was a faded G on the curb as well
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2021-10-13 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BOUDREAU PIPELINE CORP | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage, exposed 0.5 inch IPS service damaged while backfilling.
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2021-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | BOUDREAU PIPELINE | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Boudreau Pipeline was excavating for a storm drain trench when they hitï¿½a 0.75 steel service, causing the dresser to be pulled apart at the SMC
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | GLENDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home Owner was digging a hole to Plant a new tree and struck the 1 2 Plastic service with a shovel No USA was called in company crew arrived and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner had work done at there house and service was hit by a hand tool with no USA
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-06-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Day laborers hired by property owner hit plastic service by hand digging. There was no USA.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | ROOTER GUARD | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | See finish remarks.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SIPAN DESIGN DEVELOPMENT INC | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per Rafi Nazaryan they were digging a trench for a new sewer and hit the plastic service.ï¿½ They did not call Dig Alert.ï¿½ He assumed the service ran under the house and came from another direction.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-11-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GINA CANDARE | GLENDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor building wall between homes for DR Horton. No USA, contractor at fault.ï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARVINS CONTRACTOR | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. party contractor hit service while jackhammer concrete that was poured around service. expired USA
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARPA DESIGN BUILD | GLENDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LCT spoke with Armen Kalafian, employee of contractor He just said the guy should not have been excavating.ï¿½ He should feetve been digging by hand within 24 inches.ï¿½ He said they called dig alert.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | GLENDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Code 1 found by leak survey. Investigation found that the fence post installed struck our service causing a leak. There was no USA. Owner of 1453 Highland Ave. said he installed fence.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-03-04 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARIZONA PIPELINE | NORTH HILLS | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor APL was replacing a gas service to install 1 inchIPS.ï¿½APL crew member was hand excavating to find the service and a clear bore path,ï¿½while doing so,ï¿½the labor hit the 0.5 inch IPS service with shovel and cut into it.ï¿½Evacuation took place due to damage being 2 feet away fromï¿½building. Evacuations took place when workers from tea shop started to arrive for their shift.ï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ACE CONSTRUCTION | NORTH HOLLYWOOD |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating when he damaged the CTS service. No USA was called in.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-09-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | GLENDALE WATER AND POWER | GLENDALE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | GWP damaged mismarked 2 PLA Main while trenching to install electrical conduits Gas crew arrived and completed permanent repairs Three outages total with no evacuations Street was closed off
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | GLENDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner cut through 3 4 service with a sawzal no USA called in
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | PSC | LAKE FOREST | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | City of Riverside Water Department Called in emergency USA and dug prior to positive response. EE upon arrival to emergency ticket discovered damage had just occurred.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-05-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FRAMEWORK CONSTRUCTION | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was paving driveway.ï¿½ They used pick and shovel and damaged the service line.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | GLENDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor plumber hit 0.5 inch service line with a shovel.ï¿½ Owner said he will take responsible for the incident and saidï¿½ he did not call 811.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MARTIN HERNANDEZ | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor grading and damaged service with no USA
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EXCEL PAVING | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor installing electrical conduit for Glendale Water and Power h it service while digging with backhoe.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | GLENDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner was trenching with backhoe and hit service line.ï¿½ Work was being performed for an ADV.ï¿½ USA tix expired several months ago and not renewed.ï¿½ Old markings were still present and correct.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-02-25 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | ARIZONA PIPELINE | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | APL was replacing a service and struck the line within 24 inches of the delineation.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2021-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROBERTO S WROUGHT IRON | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party contractor was digging up a concrete slab with a shovel and hit the 1 2 plastic service running to the home no USA was called in Company crew arrived and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2021-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALEGIS CONSTRUCTION | MISSION VIEJO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching service for Gas company to come back and install new service order.ï¿½ Damaged our plastic 0.5 service with shovel.ï¿½ Valid USA but failed to dig cautiously damaging our facilityï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 47 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | STEVE S MITCHELL | GLENDORA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew arrived in a timely manner Contractor customer should be billed for the damage
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2021-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VCI | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1 2 ips gas service with sharp shooter
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2021-11-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | INTERNATIONAL LINE BUILDERS | RIVERSIDE |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor was moving a slab of concrete when it was dropped on the 2 inch plastic main. The contractor failed to protect facilities in place and is fully responsible.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2021-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PICTURE PERFECT CONSTRUCTION INC | GLENDORA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Hit plastic service while doing road work.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2021-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner building addon hit 0.5 inch cts service with a mini excavator while trenching for new utility installation. No valid USA on file
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOSE LUIS CORDOVA | GRANADA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor was cutting out roots when he went into 0.75 inch steel line
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2021-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was gardening on his property As he was cutting down some bushes sliced into our 1 2 inch plastic service The plastic services is on the side of a hill exposed due to earth movement permanent repairs were made with only a coupling House was put on bypass as repairs were being made so no services were interrupted Crews also made the necessary repairs to address the AOC of the exposed service Dug it down and now the service is not exposed anymore
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | L M ELECTRIC | GRANADA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging with no USA and hit 0.5 inch service
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GEORGE PAWN | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Land owner hired someone to install fence. Service damaged when digging for fence pole No USA
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | KEOUGH ELECTRIC | SUN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 1 2 plastic while digging No USA
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2021-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MASOUD SHEIKHBAHADEI | GRANADA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2in steel main was marked correctly. Contractor crew was digging with back hoe but did not hand dig before to verify marks. Damage Cause small leak was repaired with 360 clamp.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | MORFF ELECTRIC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd. party contractor hit 0.5 inch CTS service
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HAKOB MOVSISYAN | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line with shovel excavating with shovel to install cement footings.ï¿½
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2021-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | SAHAK SAHAKYAN | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor didn t call USA installing brick wall
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2021-12-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOME OWNER | GRANADA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging using power toolï¿½when they hit service with. Contractor stopped and contacted SCG.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RAFAEL GARCIA | PACOIMA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating for new sewer run damaged 0.5 inch Adyl A plastic gas service.ï¿½ At IC arrival no one was onsite.ï¿½ Contractor returned to site and informed accidental damage caused with shovel and employee bent back pipe and inchsecured inch it using steel wire used to tie rebar.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2021-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HOVHANNES POGHOSYAN | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was digging holes to install a new fence and struck the 1 2 plastic gas line with a shovel no USA was called in company crew arrived and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2021-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to replace drainage.
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2021-07-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | HACIENDA HEIGHTS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner of home hired contractors to do work and they claimed they found leaking gas line.ï¿½ damage was made right before the meter.
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | HACIENDA HEIGHTS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner Hit our 0.5 inch ips plastic service while hand digging and did not call in a USA.ï¿½
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2021-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BESS TEST LAB INC | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit our pla service while performing work for the La County Dept of Public Works Crew informed them that they need to be more careful while hand digging around our pla utilities
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2021-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | HACIENDA HEIGHTS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit plastic service by home owner. On Call Crew called out to make repairs.
Southern California Gas Company | N | LOS ANGELES | HARBOR CITY | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Unable to identify if line was marked. LADWP was excavating to replace bad cable and laying new conduit for cable.ï¿½ ï¿½Existing main job and project not finished and old system is still live.
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2021-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GREEN GROUNDS LANDSCAPE SERVICES | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was excavating in private property to install power conduits and extend sewer lateral. He hit the 0.5 cts service with a sharp shootershovel. USA was not notified.
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2021-08-15 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Trencher | 0.5 | 30 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | A VARGAS | HAWTHORNE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner responsible for damage
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2021-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SAMUEL OLIVAS | COMPTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Marked correctly, but could not tell the difference from the tree roots, or the plastic pipe.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TITAN AND CO | MANHATTAN BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor hit service of neighbor at 245 Longfellow Ave with backhoe.
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2021-02-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ERICKSON AND HALL | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors struck underground P.E., service which installing some type of anchor for fencing.ï¿½
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HARTER CONSTRUCTION | HERMOSA BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor using mini ex to excavate right by the riser Hit 1 2 cts service Locate marks on the ground but contractor could not provide the USA number
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JC CAZMER CONSTRUCTION | REDONDO BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was already exposed for about 20 ft in open trench Contractor installed their facilities and in the process struck our plastic pipe which were already exposed Accurate marks out on the street and going up to where damage occurred
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2021-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DIAMOND ENVIRONMENTAL | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company Pillar Homes was hand excavating to install sewer irrigation when they struck our known marked 0.5 inch PLA gas service at 620 12th st in Manhattanï¿½Beach. Also No USA ticket.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2021-02-11 | Operator excavation damage | Main | Steel | Boring Equipment | 2 | 30 | 26 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SE PIPELINE | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | At a tie in hole. the bore pipe worked its way down to make contact with existing gas main. Minimal damage occurred, and this section will be removed during the new pipe installation.ï¿½
Southern California Gas Company | N | LOS ANGELES | HIDDEN HILLS | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MARK HANE | HIDDEN HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner son working on retaining wall and hit line by accident but had not called USA to make out line.ï¿½
Southern California Gas Company | N | LOS ANGELES | HUNTINGTON PARK | 2021-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged CTS service with backhoe.
Southern California Gas Company | N | LOS ANGELES | HUNTINGTON PARK | 2021-05-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit svc svc marked correctly
Southern California Gas Company | N | LOS ANGELES | HUNTINGTON PARK | 2021-06-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | MUNGUIA PLUMBING | HUNTINGTON PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit Line W Shovel While Digging For Sprinklrs. Phoned By Adanï¿½Munguia From Munguia Plumbing 562 5052794
Southern California Gas Company | N | LOS ANGELES | HUNTINGTON PARK | 2021-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DORECK CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit svc, svc was marked correctly
Southern California Gas Company | N | LOS ANGELES | HUNTINGTON PARK | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DORECK CONSTRUCTIONS | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit svc, svc marked correctly
Southern California Gas Company | N | LOS ANGELES | HUNTINGTON PARK | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JESUS ORTIZ | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor CTS pipe
Southern California Gas Company | N | LOS ANGELES | HUNTINGTON PARK | 2021-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EFI GLOBAL | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | STL Gas Service was struck by a backhoe while digging to install a water line. The service was off by3 4 feet due to locating issues and service having an insulated coupling that could have of played a factor in proper locating of service. The 3rd party company stuck a piece of wood in the other side of insulated coupling and tapped up to stop the leak which was controlled to a certain extent prior to the crews arrival.ï¿½
Southern California Gas Company | N | LOS ANGELES | HUNTINGTON PARK | 2021-04-27 | Third party excavation damage | Riser | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RM INVESTMENT | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service line and fixed it them selves by bending live service and taping it with electrical tape and wasn feett aware of branch service they buried the repair never notified anyone
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HP COMMUNICATIONS | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit service while digging.ï¿½ Service line was not marked correctly due to locating wire not connected correctly.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | TELCOM ENGINEERING GROUP | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 1 inch line with backhoe while digging trench for Edison.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DOMINGUEZ GENERAL ENGENEERING | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor APL was trenching for electric utilities with a backhoe when they damaged the 1 inch plastic main on Corona Way, Laguna Beach. Contractor exposed a conduit that looked similar to our 1 inch Adyl A under slurry and assumed this was natural gas as it was in line with marks. SCG locator marked this area to due measurements in GIS and weak signal that lined up with measurement.ï¿½
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ZEVA AWAD | HAWTHORNE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA needed excavation by damaging party. No one on site upon distributions arrival. Per CS rep, damaging party knew where service was but removed flags prior to excavating.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | R R HAULING CLEANING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching to install a sub pump.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-03-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WACONAH CONSTRUCTION | INGLEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called in by damaging party. Contractor damaged 1 inch plastic service while repairing drain.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MEDINA ZENDEJAS | INGLEWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Mini Excavator damaged 2 inch PE serviceï¿½
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-07-21 | Third party excavation damage | Main | Steel | Directional Drilling | 2 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CROSSTOWN ELECTRICAL | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Directionalï¿½drill Failed to maintain clearance to Gas lineï¿½
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-08-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | GREEN B CONCRETE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | New track home development. No USA. Contractor digging over PE Stub with backhoe and ripped off fused plastic cap.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ALL AMERICAN ASPHALT | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor is replacing handicap ramp and at the curb face on the side walk, they hammered stakes down to secure the forms before pouring concrete. Service was shallow and struck it with wooden stake.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HAMPTON TEDDER ELEC | COMMERCE |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor hand digging water svc. at water meter to fix leak, while using hand pick employee struck 0.5 inch cts svc line. Hole at damage was full of water.ï¿½ Crew dropped back to SMC and capped for crew to complete next day after water was cleared out.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | ALLEN LIGHTING SERVICES INC | COLTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Time metï¿½
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-07-31 | Third party excavation damage | Miscellaneous/Other | Material not known | Not Available | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per incident commander No Gas Co involvement Source of leak was a hit 3 main at 3883 W Century Blvd Damage was done by 3rd party while excavating No meter on site and this meter was the closest to site Incident command transferred to Gas Ops Crew arrived on site and leak repaired at 17 48 No injuries or fatalities
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PRECISION PIPELINE | NORWALK |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | No valid USA
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | wire was found to be 20 from mark
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 1 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SO CAL EDISON | TORRANCE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Edison was performing pole replacement with auger.ï¿½ Snagged steel line.ï¿½ At the time they believed to be abandoned.ï¿½ They proceeded to cut it out of the way and that feets when they realized the line was live.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 7 |  | S B CONSTRUCTION | YORBA LINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging trench to install conduit hit 0.5 inch IPS Standard Service and 2 branch services with backhoe.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-08-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PLATINUM LANDSCAPE | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 16 |  | CABLE TECH CORP | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor stated they were hand digging over gas service line because they ere going to cross our utility. They damaged service with service with a shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALLEN | COLTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor performing pothole over 0.5 inch CTS service struck service causing leak.ï¿½ Used sharp shooter.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GOTHICS | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inchP service while trenching to install electric conduits.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CABLE TECH | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Per LCT Andrew Slykhuis, Third Party Contractor was using boring equipment to install fiber optic lines when the service was hit.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | M TEK COMMUNICATIONS | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging to install communications cable when the hand shovel came in contact with Gas Comp facilities causing a leak.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-10-12 | Third party excavation damage | Main | Polyethylene Pipe | Drain cleaning equipment such as snakes, etc. | 2 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | MATTUCCI PLUMBING | INGLEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Company contractor Mattucci Plumbing was clearing roots from sewer lateral for the SLIP department when he struck a SCG main intrusion with a snake. View of the main was obstructed by the roots.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | S B CONSTRUCTION | YORBA LINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor his 0.5 inch IPS service with backhoe digging trench to install conduit.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GREEN AND SONS PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged a 0.5 inch cts serviceï¿½
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2021-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ALLEN SERVICES INC | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while excavating in street, 3rd party came in contact with abandoned stub.ï¿½
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2021-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VOT DEVELOPMENT GROUP INC | GLENDALE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Mr. Torossian feets worker wasï¿½using a jack hammer to dig in dirty trying to find a sewerï¿½line and hit the IPS service.ï¿½ The service line was exposed and visible when it was hit.ï¿½ There was no USA called in at the time.ï¿½ Customer was informed to call 811 to renew tix.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2021-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | NOREEN MARKEL | LA CANADA FLINTRIDGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Owner John Nelson was installing copper water lines and dug within 24 of USA delineations with excavator Failed to exercise caution and did not hand dig exposing gas lines Severed service in two spots about 20 feet apart
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2021-10-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PAUL ROBERTS | ROSEMEAD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | more info
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LA CANADA FLINTRIDGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowners contractor pulled and stretched 0.5 plastic service with bucket of miniexcavator.ï¿½ Service was dug and exposed by company employee to locate and mark service for Homeowner whom had notified DigAlert.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2021-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | KY KANG | LA CANADA FLINTRIDGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit gas line while digging for fence post. No USA calledï¿½ in
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2021-12-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GAGNIER LANDSCAPING | SIERRA MADRE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA REQUESTED, GARDNER WAS PLACING REBAR IN THE GROUND.ï¿½ Permanent repairs made.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2021-06-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LA CANADA FLINTRIDGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor using backhoe damaged service when they were digging for a new retaining wall.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2021-12-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HAYK YADERYAN | SUN VALLEY |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA ticket available. Third party company trenching on private property and damaged 0.5 inch PLA service.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2021-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARIN BUILDERS CONSTRUCTION | NEWHALL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Marin Builders Construction struck SCG service line with a jackhammer while trenching to install water pipes.ï¿½ No Valid USA
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARTIN GOMEZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging to put in palm trees hit 0.5 inch CTS Service. No USA called in
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ROBERT BRKIC CONSTRUCTION | MONROVIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2021-07-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | ROBERT BRKICH CONSTRUCTION INC | MONROVIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Robert Brkich contractor for LaCr Valley Water was digging with backhoe to install a fire hydrant on public property There were no delineations found for USA Told contractor we do not engineer the entire block for them They are required to delineate area of excavation for locator to identify our gas lines with USA No USA
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2021-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ART KESHISHIAN | SAN FERNANDO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | While digging trench w mini excavator, contractor hit 0.5 inch cts service in cased in 0.75 inch steel. Crew completed service alteration.
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2021-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CUSS CONSTRUCTION INC | LA CRESCENTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Homeowner trying to find sewer hit 1 2 plastic service with shovel Valid USA was called in company crew arrived and made Permanent repairs
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | R RAMIREZ | LA CRESCENTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck CTS w Shovel while digging to install cinderblock wall There was no USA marks or ticket
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JOEL ROCHA | LA CRESCENTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging trench for retaining wall hit branch service.
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2021-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | OFELIA FIALLOS | LA CRESCENTA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in. Contractor was digging to install irrigation line and hit gas service.
Southern California Gas Company | N | LOS ANGELES | LA MIRADA | 2021-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TORRENT RESOURCES | PHOENIX | AZ | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | incorrect facility records map. Unmapped cutback service
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2021-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LA PUENTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The homeowner was digging a trench to install a water line and failed to pothole our service. He proceeded with a backhoe and damaged our 0.5 inch cts service. The service was within 2 feet of marks. Homeowner admitted he failed toï¿½hand dig over our facility.ï¿½
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2021-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DSRM CABLE CONSTRUCTION IC | LA PUENTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Plastic service hit by homeowner trenching for water lines, No USA.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PROLIFIC PLUMBERS AND ROOTER | LA PUENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Navarro was digging to fix sewer and cut our service line
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LARRACHE LAND COMPANY | LA PUENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was installing a new water line with no USA and was trenching with a backhoe and hit our 0.5 inch cts serviceï¿½
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | LINE WORKS | LA VERNE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | The contractor was driving a stake into the ground when they damaged a plastic gas service. The contractor did not notify USA and is fully responsible.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2021-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LINE WORKS CONSTRUCTION INC | CORONA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer digging for new sewer line with no USA.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2021-10-08 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | HENKELS AND MCCOY | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | owner failed to call for USA and struck service.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VINCENT SHUM | LA PUENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching with backhoe to replace sewer lateral and damage our 0.5 inch plastic service.ï¿½ Marks were off and verified signal was very weak.ï¿½ Service was a 10 percenter, itï¿½was the reason why marks were off.ï¿½ Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2021-04-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PARERA CONSTRUCTION | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging with mini backhoe and severed 1 inch plastic service line.
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2021-08-10 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARB INC | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor crew ARB struck gas service while excavating in extremely hard soil with hand tool
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2021-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | OPTIMUM INC | BLOOMINGTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew arrived in a timely fashion
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2021-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | EMPIRE POOL DREAMS | FONTANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor did not call USA prior trenching for pool line
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | SoCalGas facility was mapped incorrectly and mislocated,3rd party contractor severed 1 2 cts service with backhoe
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JDC CONCRETE | UPLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for homeowner hit gas line with excavator. They did not call USA and the lines were not marked.ï¿½
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2021-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DOMINGUEZ GEN ENG INC | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was excavating trench for a water main replacement struck a plastic gas service with a shovel causing an escape of gas.
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Material not known | Backhoe/Trackhoe | 0 | 44 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MONDRAGON GENERAL CONSTRUCTION | GARDEN GROVE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Rooter Solutions claimed to have called 811 at 10 44am but did not speak with anyone and did not receive a ticket .ï¿½
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2021-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DM G | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was repairing water line and was cutting with saw and cut through 1 inch Main. Contractor had called USA ticket in after damage approx an Hr later.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | WALTER MARIN | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Walter Marin hit SCG service line with shovel while digging to repair a water leak.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-08-11 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOUGLAS AVILA | ROSEVILLE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | auguring for electrical pole
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | SO CAL SEWER | SIGNAL HILL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | So Cal Sewer Water hit 1 2 SVC line while digging with mini Excavator to perform work on sewer No USA on site or obtained
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner struck service with a pick axe while digging a footing for a wall
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | OSCAR | LANCASTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was having tree removed. Hit service with backhoe. Service that ended up being hit was at address of 4016 W Avenue L2.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | LANCASTER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Homeowner wasï¿½
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LANDALE MUTUAL WATER CO | LANCASTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit service with a shovel while removing some dirt and concreteï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging post holes for fencing
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home Owner hit Gas service while digging to install water line.ï¿½
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | ROCKSCAPES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 2 service no EFV
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-08-02 | Third party excavation damage | Main | Material not known | Backhoe/Trackhoe | 2 | 60 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RAMIREZ PLUMBING | OXNARD | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Called in,ï¿½ Ramirez Plumbing worker hit 2 inch Gas main while digging trench for sewer line with Backhoe.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 23 |  | SECC COMMUNICATIONS | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SECC contracting for Frontier Communications struck SCG service whileï¿½digging for drop kits.ï¿½ sidewalk parkway
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage by homeowner while digging trench for electrical No USA
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | MONTALBAN PHILIP A INC | LOS ALTOS |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | hit service with shovelï¿½
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-08-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 4 |  | TRENCHER S WEST | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Trenchers West digging outside deliniated USA area Struck 2 Main
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TRENCHERS WEST | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Marco Molina, of Trenchers West, struck SCG service line with shovel while trenching for installation of utilities at new construction.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALBERT HOVAKIMYAM | LANCASTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 1 2 service by homeowner installing sprinklers Had valid USA and was marked correctly
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit service while using a trencher to install sewer line to his workshop.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 230 | 215 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  |  | NA | HAK AWAY TRANSPORT | LANCASTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor for a solar company had done grading and damaged appx. 50 feet of 0.75 inch HPSVC.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GROUND WORKS | SANTA CLARITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was excavating with shovel to expose gas service for SCG Contractor to abandon the service the following day.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2021-07-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALBD ELECTRIC AND CABLE | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Part Contractor hit 1 SVC Stub while trenching for Street light install No USA
Southern California Gas Company | N | LOS ANGELES | LAWNDALE | 2021-07-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | NA | LAWNDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner digging to install drain pipe to make connection with sewer and struck 0.50 inch service line with a shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | LAWNDALE | 2021-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | C P CONSTRUCTION | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator damaged gas service while potholing with shovel. Marks good.ï¿½
Southern California Gas Company | N | LOS ANGELES | LAWNDALE | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | DOMINGUEZ GENERAL ENGINEERING INC | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | There was two gas lines in one hole so when 3rd party contractor exposed 1 gas line they didn t know a 2nd one was below and over 1 ft
Southern California Gas Company | N | LOS ANGELES | LAWNDALE | 2021-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | DOMINGUEZ GENERAL ENGINEERING INC | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor was excavating to install water main hit 1 2 cts service with backhoe usa was notified and the gas line was correctly marked
Southern California Gas Company | N | LOS ANGELES | LAWNDALE | 2021-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | DOMINGUEZ GENERAL ENGINEERING INC | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor did not expose clearly marked gas line by hand digging used back hoe and damaged our line
Southern California Gas Company | N | LOS ANGELES | LITTLEROCK | 2021-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LITTLEROCK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Friend of home owner was excavating tree stump and damaged gas service.
Southern California Gas Company | N | LOS ANGELES | LITTLEROCK | 2021-05-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LITTLEROCK | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner occupant, Roman Cruz, struck SCG service line while trenching to build install privacy wall.
Southern California Gas Company | N | LOS ANGELES | LITTLEROCK | 2021-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JESSE HOOKER | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | excavator hit riser while doing demolition
Southern California Gas Company | N | LOS ANGELES | LOMITA | 2021-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GREG BLOOMSTADT | LOMITA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner hired workers to upgrade sprinkler lines which damaged service. No USA
Southern California Gas Company | N | LOS ANGELES | LOMITA | 2021-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | V IBRAHAM | WOODLAKE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor struck our service while digging for drainage No USA
Southern California Gas Company | N | LOS ANGELES | LOMITA | 2021-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GOOD GUY PLUMBING | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was working on emergency sewer repair. Damaged our service with pick axe.
Southern California Gas Company | N | LOS ANGELES | LOMITA | 2021-05-14 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COMPANY CONTRACTOR TRENCHING | NA |  | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging trench to has Gas Co. moveï¿½ line to different location damaged service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | ANDY S PRECISION SEAL STRIPE APSS | CASTAIC | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor pulled out tree stumps out using backhoe damaging plastic main Contractor was advised to call Underground Service Alert USA at 811 whenever digging even when in private property Contractor had an expired ticket
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | K C LEE | MISSION HILLS |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractors were digging for water line repairs and hit our line.ï¿½ No USA was called.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DARIN MARTEN CONSTRUCTION | PACIFIC PALISADES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service was damaged with a shovel No USA provided
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HOMEOWNER | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Land owner crew were trenching with hand toolsï¿½for a sewer install. While digging,ï¿½ crew struck 1 inch PE gas line in private property. EFV activation shut gas off ï¿½upon my arrival.ï¿½ï¿½Crew has completed ï¿½permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GALAXY PLUMBING HEATING AND AIR CONDITIONING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner Developer didn feett call for a USA ticket and hit own gas service with shovel while digging to repair sewer line. Homeowner was advised by company crew to call Underground Service Alert USA at 811 whenever digging, even when in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DAVID ABRE | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.5 inch CTS service with backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DYNALECTRIC | LOS ALAMITOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per LCT Lupe Castillo, Third Party contractor struck Gas service with Hand shovel while pot holing. Looking for service.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | KIETH FEGLEY | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch PLA service cut into with axe by laborer removing treeï¿½roots
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | DWP LOS ANGELES | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Gas main was hit by LADWP while trenching to install water main.ï¿½ Line was not marked in the area that it was hit.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SPENCE CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ROMANS LANDSCAPING | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trying to replace drain in yard cut into 1 inch plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PLUMBING AND SEWER CARE | NORTH HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while digging to repair sewer line Gas company crew on site informed the contractor to call Underground Service Alert USA at 811 anytime when planning to dig so the utilities can be located
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-07 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DERECK ORNELAS | LOS ALAMITOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 3rd parity Contractor working for DWP was installing underground power for lighting. The contractor Potholed 48 feet feet deep at the Marked location of the Gas Main however, he did not expose it, did not call the Gas Co. to assist in locating it. The contractor did not expose all utilities before starting the boring process and struck our 2 feet feet gas main.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-16 | Operator excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DIGNA MEJIA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JOSE ANGEL LEIVA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Requested Customer Was Laying Bricks.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 33 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | VALVERDE CONSTRUCTION | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor using excavator over gas line has USA but no delineations were marked on ground.ï¿½ Contractor also did not pothole gas line while crossing, only used backhoe to dig.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hired by owner was digging hole to plant tree in front yard and hit steel service line with clayspade. There was no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | JUVENTINO LOPEZ | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator damaged the service as crew was in route to locate and mark the emergency ticket at that location.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LAUSD | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Requested, LAUSD Working Digging To Install A Basketball Pole
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LADWP | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | damage to 0.5 inch ips service. customer failed to use proper precaution while excavating near SCG service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | SMALL CELL SOLUTIONS | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | installing conduit for fiber optics
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-24 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 14 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid USA ticket The Gas marks where within tolerance LADWP was hand digging in order to repair the leak at theï¿½water service ï¿½During excavation the 2 PLA main was damaged SCG crew repaired 2 of 2 PLA main
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-01 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PRECISION PIPELINE | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor damaged an unknown stub while excavating to install water.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PRECISION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with backhoe and was unaware of the location of the main. Did not hand expose Substructure, hit with machinery.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 39 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | R R DEMO AND GRADING CORP | WOODLAND HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not have USA, grader ripped through service while grading.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | P G SHORING DRILLING INC | SAN FERNANDO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 0.75 inch STL stub damaged by auger. No Sign of riser. Was probably not inputted into service history correctly. Had EE update Service history.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer claims they were digging and smelled gas, but it was cut in half when we exposed it.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner Contractor didn feett call for a USA ticket and hit own gas service with shovel while digging to repair sewer line. Homeowner was advised by company crew to call Underground Service Alert USA at 811 whenever digging, even when in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 8 |  | CALIFORNIA PAVING AND GRADING COMPANY | LOS ANGELES | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading the street when they hit service with the grader.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALL IN ONE CONSTRUCTION | LA HABRA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to install a sewer line and struck a plastic service with a shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trying to install post for home owner damaged 0.5 inch CTS service with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DAMIAN MARIN | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA WAS NOT NOTIFIED
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Tenant Jose Guervara said he was digging in yard near MSa and hit 0.50 inch IPS service. ETR spoke with owner of property Ana Rodriguez and she said she did not give tenant permission to dig on property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor for homeowner damaged 0.5 inch adyl a service with shovel while excavating to relocate pole for gate ahead of concrete pour for new driveway.ï¿½ No USA notification for excavation work prior to damage.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AFFORDABLE BUILDING SOLUTIONS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RED LILLY PLUMBING INC | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working to install new retaining wall damaged 0.5 inch PLA service with shovels at two separate points.ï¿½ Contractor did not have a USA ticket.ï¿½ Company crew completed permanent repairs.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Work is being performed for address of 1217 W. 75th St.ï¿½ Workers excavating for footing of block wall and hit 0.5 inch CTS service for address 1223 W. 75th St.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | URBAN BUILDERS COM | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The crew was trenching in private property without callingï¿½for dig alert While excavating the 1 2 cts service was damaged
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BORGESE CONSTRUCTION | SANTA MONICA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service with a Back Hoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damaged gas SL while digging to repair sewer line. No USA at this address
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | YVETTE BARBARENA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner didn t call for a USA ticket and hit own gas service with shovel while digging to repair driveway Homeowner was advised by company crew to call Underground Service Alert USA at 811 whenever digging even when in private property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Sewer replacement being performed by homeowner, no call for USA.ï¿½ Damaged SCG Service line with Shovel and called SCG.ï¿½ SCG arrived on scene and evacuated 4 residents.ï¿½ Repairs were made and evacuation was lifted when levels of gas were deemed safe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-20 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 4 |  | HP COMMINICATIONS | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 2 inch plastic main with shovelï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TAYLOR D PLUMBING INC | NORTHRIDGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party operator was digging trench for new gas main. while trenching for the end of main the crew hit the main with backhoe. no USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RIGHT PRICE ROOTER AND PLUMBING | SUNLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Sewer contractor damaged SL for 1257 while digging to repair sewer for 1255
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RGA CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert USA ticket The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging even when in private property Informed homeowner as well
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ELROY COHEN | WOODLAND HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for home owner to install sewer Lateral was digging in Private Property and struck 0.5 inch plastic service with shovel, company Crew arrived and Made Permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CCMP LLC | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Company Contractor, Teichert, damaged 2 inchPAM while digging to expose 2 inchPAM.ï¿½ Damage was done using hand tools.ï¿½ 2 inchPAM was hit three times causing leaks at each cut.ï¿½ ï¿½Permanent repairs completed by Company Crew.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HOME OWNER | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line by third party contractor . NO USA. Crew arrived and control gas release . Spoke to contractor and explained the importance of 811
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PATHI PLUMBING | SHERMAN OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.5 inch ips service by plumber repairing sewer
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | A D PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber melted plastic service line while brazing copper water line for home
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | THE DRILLER MARTINI DRILLING | GARDEN GROVE | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 feet CTS SL while drilling prior to 48 hour USA start datetime
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DAVID ADILE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | David who was on site claimed they did not hit line but when crew dug up line looked to be a dig in damage from either a shovel or some other digging hand tool
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MEJIA OSMINTS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service line was exposed by contractor in trench for sewer replacement. Contractor cut through service line, casing with CTS inserted, to get the line out of the way. Upon cutting it, they found the line was live and called So Cal Gas.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FMB DEVELOPMENT | BEVERLY HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Upon arrival 1 inch PLA pipe was cut in half with a uni loader, gas was not blowing do to EFV.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WARASIC | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged service that was incorrectly marked. After an investigation of returning to the location with the employee, reviewing GIS it was found that the 810 locator was picking up an abandon service on the same property. There was a previous mark and his read were high over that mark which was directly in line with the MSA. The service to main connection was only found due to the damaged service. Service History and measurements were completely wrong and there was no history of an alteration or abandonment. Also service was inserted on copper line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JAVIER SANTANA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert USA ticket Contractor was not on site Company crew informed the homeowner to always call USA at 811 when any digging will take place
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACHECO BUILT IT | NA |  | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Builders were digging near where they knew the plastic service line was and hit the line with a hand tool.ï¿½ They did not have a valid USA at the time of excavation.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | BERTHA LIDIA CAMPOS | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The customer s nephew was trenching in doing so he damaged the PLA service with a shovel No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WAISMAN CONSTRUCTION | CANOGA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Power pole was installed directly on the PE service, resulting in a damage
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-02 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | L A DW P | LOS ANGELES |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Homeowner was hand digging trench to install a houseline and in the process 0.5 inch CTS service was struck with a shovel. Advised homeowner to contact 811 for all future excavation work
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 0.5 inch Plastic cutback service in casing, damaged cutback service was recorded in service history as abandoned, not present on GIS, and no riser was present to locate. USA valid, and damage occurred within delineation.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SAFE CALI PLUMBING | MISSION HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA contractor hit service multiple times with a jackhammer
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LARSON CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was installing a sewer drain line, without a DIG ALERT ticket, and damaged his 0.5 inchP service with a DITCH WITCH
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LARSON CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor was excavating to install storm drain pipe under 0.5 inch gas service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SE PIPELINE | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third Party Damage, contractor hit service with shovel, outside of delineation.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SABER FOUNDATIONS | SANTA FE SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Hit gas line while digging to put support beam for foundation.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WALKER WORKSHOP | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor ripped up service with backhoe while trenching No USAï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ARK DESIGN CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging with Mini Excavator to install footing for a wall Private Property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | BIG BEN ENGINEERING | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Line was mis marked by 30 putting contractor not at fault and should not be billed
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-27 | Third party excavation damage | Miscellaneous/Other | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | PANORAMA CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading driveway and found 0.75 inch steel line and wanted to verify if it was live or not so they cut into line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BITECH CONSTRUCTION | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator did not hand expose 2 inch plastic main before digging with mini excavator.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per CR20, homeowner was using back hoe to level driveway for new concrete when service was hit.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CITY OF LA BURUE OF STREET LIGHTING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was hand digging to install lights on the customers property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VHL PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert USA ticket. The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging, even when in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LILIPUT | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscapers digging in property to put in plants ended up hitting and damaging 1 inch IPS service with a shovel. No USA was called
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FORD PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 2 CTS Service hit with shovel while performing sewer work No USA called in prior to job start
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SO CAL SEWER INCORP | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damage gas service while digging to uncover sewer No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-06 | Third party excavation damage | Not Available | Copper | Backhoe/Trackhoe | 0 | 60 | 18 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | IRISH CONSTRUCTION | ROSEMEAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Re damaged stub by service abandoned at the SMC.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 30 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ENRIQUE CRUZ | SAN FERNANDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to install block fence damaged 2 PE service No USA ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MAJOR PLUMBING | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Developer was trenching with an excavator for New Business Plumbing installation when they struck our marked service line.ï¿½ Upon notification SCG arrived and secured the area calling for distribution assistance.ï¿½ LCT Luis Ramirez arrived an hour after initial notification and controlled the blowing gas before making repair to the damaged line.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-21 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | SE PIPELINE CO | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged correctly marked gas facility while attempting to hand expose Gas company crew on site informed contractor to use more caution while excavating around underground substructures even if by hand
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JOSHUA GASPELUM | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | work done for home owner. digging out water serviceï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 55 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PWC | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor 3rd party hit plastic gas line with hydralic jack hammer
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GERARDO LIMON | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was trenching along property line with small backhoe when he struck 1 inch Plastic service which was not marked due to NO USAï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 8 |  | MOLT CONSTRUCTION | BEVERLY HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavatingï¿½ trench for sewer with no USA Ticket.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | D CORPORATION | NUEVO |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Home owner hit service with shovel while digging.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | INGOLD CONSTRUCTION | PACOIMA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service with backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SOLEX CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | W A RASIC | LONG BEACH |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | "The contractor damaged a unmarked plastic service within their delineation. The Locater did not have any knowledge of this service due to it not being mapped.ï¿½ The meter itself is far away from the damage location at a club house within a golf course.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 28 |  | JESSIE S CONSTRUCTION | SOUTH BAY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor did not call dig alert. The operator was using a backhoe as he excavated and damaged the 2 feet feet PLA main on private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ANCHOR LOANS | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit 0.5 feet IPS serviceï¿½ while hand digging for a railing.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LAS FLORES CORPPORATION | GLENDALE |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SANTOS VASQUEZ | LANCASTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging for footing and cut the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DYNALECTRIC KDC | LOS ALAMITOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged correctly marked gas facility while drilling with a bore machine. Contractor pothole service 4 feet from were it was damage but never exposed were they will be crossing our gas service. Gas company supervisor on site informed contractor to expose all located gas pipelines by hand. On site supervisor also advised the contractor to expose utilities by hand before using any machinery near our substructures.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LA department of water and power was digging inside property they struck and damaged 1 inch plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CITY OF LOS ANGELES | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | City of LA was removing soil with skip loader cutting into edge of hill to set krails to help protect from landslide and or debris falling down to the street. While doing so they hit a 1 inch plastic gas service that ran up the hill to 2001 N Soto St, LA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ROCKHILL CONSTRUCTION | LOS ANGELES |  | N | Y | Yes | No | No | Yes | No | Yes | No | The contractor was hand digging to perform maintenance on the sewer line when they damaged the plastic gas line.ï¿½ The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CESAR HERNANDEZ | COMPTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew arrived on scene and 0.50 CTS was damaged by mini excavatorï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | KEITH HAMILTON | LOS ANGELES |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch service with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-04 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SE PIPE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit stub service with backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DYNAELECTRIC | LOS ALAMITOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged service that was incorrectly marked. Multiple employees have attended to this USA ticket and have faced the same issues. All plastic services either don feett have locate wire or have bare locate wire which has eroded after time and is giving them an inaccurate signal.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | GOLDEN STATE CONTRACTORS | GARDENA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LCT looked for G feets on curb. LCT used SVC History. LCT told DWP to pothole for service. DWP failed to expose service after request from LCT.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 40 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 1 |  | RM INVESTMENTS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Company performing demolition on vacant lot at 206 E 87th St. hit 0.5? CTS and put electric tape over leak. Contractor claims to have USA ticket
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 1 |  | A1 GOODWILL ASKUS PLUMBING SERVICES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumberï¿½cut into old drain with a sawzall reciprocating saw to install a new drain cleanout.ï¿½When he cut the old drain, he accidentally cut the 0.5 inch cts service. Service ignited at damage point.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KONSTRUCT INC | LA VERNE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA 3rd party Contractor Dig In
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WA RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 1 2 cts plastic service with shovel while excavating for water service replacement USA was called and service was marked correctly within 2 foot tolerance
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | COMET ELECTRIC | CHATSWORTH |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Operator was using a small excavator to attempt to replace the sewer line and hit the 0.75 steel serviceï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-02 | Third party excavation damage | Not Available | Material not known | Backhoe/Trackhoe | 0 | 30 | 23 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DOTY BROS | COMPTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per USA ticket report the USA dig ticket had expired when damaged took place.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-25 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While diggingï¿½to set dirt forï¿½concrete stairs, contractor damaged SL with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | NA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | MCR due to residents evacuated for safety
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PREMIERE CONSTRUCTION | DOWNEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged facilities, Failed to expose crossings in bore path
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PRO AMERICA BUILDERS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut through our service line believing it was an abandoned line. Contractor did not call for an Underground Service Alert USA ticket. The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging, even when in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BERMUDA PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged 0.5 inchts service with shovel exposing sewer line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WPIC CONSTRUCTION | MONROVIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Coms Contractor potholing for substructures in priorï¿½to directional drilling damaged plastic serviceï¿½by hand with a shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RODRIGUEZ LANDSCAPING AND TREE SERVICE | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was hand digging for some irrigation lines and struck and damaged 0.5 inch IPS service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | REANE RICHARDSON | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading when gas service was hit with shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BUREAU OF STREET LIGHTING | LOS ANGELES | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor began work without SCG markingsï¿½on the ground dug before valid start time 48 hour time requirement
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged 0.5 inch IPS service with clay spade by DWPï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RICHARD B CHUTUK SONS INC | LOS ANGELES | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Damaged 1 inch stub service with backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BAY CITY GEOLOGY | WOODLAND HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching for new water line and damage 2 inch gas service for Hotel. Service marked correctly.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | HHS CONSTRUCTION | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator had interference Picked up a good signal over the steel main Contractor fail to hand exposed 4 PE main after finding 4 steel main
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-19 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | LADWP RICARDO ALVERAZ | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP damaged 2 inch plastic main with clayspade. Valid USA. Facilities were marked correctly.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TRINITY RECREATION CENTER | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Line was damaged by who was at one point working on landscaping this was never reported and should be billed Contact with recreation center will be required for billing
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner was digging for sewer line when he struck the 0.5 inch service.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SE PIPELINE | LOS ANGELES | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit plastic service with shovel while hand digging
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew called in possible leak while pot holing, after exposing main it was determined Desert Water Agency damage pipe with a probe while pot holing to expose main.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.5 inch cts service with backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | V10 CONSTRUCTION | LA CRESCENTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1 inch plastic service with backhoe while repairing sewer line. Ripped line apart in two places.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KEVIN CHAVEZ | BURBANK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert USA ticket. The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging, even when in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CHRIS CERVANTES | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | developer struck gas service with mini excavator. line was clearly marked with yellow flags and yellow gas marks on parkway.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EPC | SOUTH EL MONTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert USA ticket The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging The contractor called for USA after the damage
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HERNANDEZ GARDENING | CANYON COUNTRY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert USA ticket The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging The contractor called for USA after the damage
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | V10 CONSTRUCTION | LA CRESCENTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while contractor was trenching for sewer, came in contact with Gas service line.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | MP7 | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Line drawn in GIS shows service going to a manifold however there are two manifolds one which is not drawn.ï¿½ There is an abandoned curb valve in street and house also looks abandoned.ï¿½ Service is cross lotted with no markings for an easement.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SERVITEK ELECTRIC INC | WALNUT |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was digging with backhoe for storm drains when he damaged 2 inch PLA stub. stub was correctly marked by CO. Contractor who installed stub.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 20 | 18 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PORTRAIT CONSTRUCTION | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per Steve Smith, they were digging a trench for electrical and nicked the plastic service.ï¿½ He said they had a spotter and still hit it with a small backhoe.ï¿½ They were not hand digging and did not call dig alert.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged own gas service while digging to plant a tree. Since the homeowner was completely unaware of 811 Underground Service Alert, Gas company crew on site informed the homeowner to call Underground Service Alert USA at 811 anytime when planning to dig so the utilities can be located, even in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DIAMOND WEST CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA contractor hit service line multiple times with skid steer
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | OCEAN VIEW PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | URBAN CONSTRUCTION AND DESIGN SOLUTIONS | LONG BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Damaged SL while grading driveway for property owner. No USA called in
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 6 |  | AMERICAN INTEGRATED SERVICE | WILMINGTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trying to repair a broken water line and hit the gas line with a shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALL TIME PLUMBING EC INC | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was installing irrigationï¿½line for homeownerï¿½when they damaged the gas service line with a shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SINIA CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit plastic service while digging.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MOTA BUILDERS | VAN NUYS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Valid USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging in the yard to repair the water line Contractor damaged 1 2 CTS pipe with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-05 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SE PIPELINE | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company contractor hit plastic service while digging. Contractor was replacing new service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RICARDO HERNANDEZ | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Home owner was excavating for upgrade of all utilities on home. Hit unmarked gas line with shovel. Fire depart on scene and evacuated 3 occupants to neighboring home.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ONEWAY ROOTER SERVICES | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Sewer lateral being replaced for homeowner. Contractor performing work broke gas service with a shovel, No USA was calledï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | ATTIA GROUP | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 inch PE service on 9 30 21.ï¿½ Crew was called on 10 0.51 to make permanent repairs.ï¿½ Per LCT He believes the contractor damaged the service digging to install cinder wall.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 6 |  | EPC | SOUTH EL MONTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit plastic gas service while hand digging USA was current and marks visible
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CLAY REED | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading to widen the road and hit the plastic service with the skip loader. No USA called.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JC RETROFIT | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while trenching to install utilities contractor hit 0.5 inch pla gas svc.ï¿½ No USA called and contractor not willing share any information
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-05 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TEICHERT PIPELINE INC | CHINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While trying to install concrete fence post, homeowner gardener came in contact with gas service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ROOTER GUARD | VAN NUYS | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor performing sewer repair damaged service with hand tool while digging before 48hr USA Notification requirement Service was marked accurately from previous USA for different contractor
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TM REAL ESTATE HOLDINGS | DOWNEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party contractor was digging to install irrigation system when the 0.5 inch plastic CTS service was hit with a hand shovel per LCT Carlos Aguilar.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | tenant said he smelled gas and decided to dig there
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DYNAELECTRIC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew was called out for a code one. In excavating the 1 inch service was discovered to damaged cut in half and then backfilled. Upon repair being complete the service was discovered to be a chocked service, with water and mud.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ROBERTO AVISTA | CHATSWORTH | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 0.75 inch steal service damaged by contractor grading lot.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 3 |  | HEFLIN PLUMBING | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 0.5 inch CTS service while digging trench for sewer line. No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | LADWP | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP exposed two steel lines with vacuum and assumed they were the active gas lines They started digging the trench with the backhoe and struck the live 2 Gas Main The markings on the ground were correct and stated the size and pipe material 2 Plastic Main Mark was within tolerance zone Company crew completed repairs
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | STELEE INDUSTRIES | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner was grading and struck PLA SVC and failed to notify USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MISAEL CEREZO | BREA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was removing railroad track steps and excavating by hand. He damaged the service with a shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ENUZSZON RED LP | CALABASAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor did not have a valid USA and damaged our half inch PLA service while excavating to repair sewer.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | STARLITE | BOSTON |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut into steel service with saw assuming that it was a house line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | STARLITE BUILDING GROUP | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 2 inch PLA service with backhoe digging planter foundations
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-29 | Operator excavation damage | Main | Steel | Miscellaneous/Other | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TEICHERT PIPELINES INC | CHINO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | cts svc was hit with a post hole digger
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ENVIRONMENTAL LANDSCAPE | LA CANADA FLINTRIDGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to install sewer hit 1 inch plastic service w excavator
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Crew was digging to extend a Path way down the side of a home and hit Gas service with a shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-15 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARIZONA PIPELINE | CHATSWORTH | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Arizona Pipeline hit 0.5 inch plastic line which was inserted in 0.75 inch steel.ï¿½ Company crew completed permanent repairs.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While hand digging to repair sewer line in private property, contractor hit a 1 inch PLA service w an EFV installed at SMC.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RAUL MENDOZA VICTORIA S SANGA LANG | LOS ANGELES | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Damaged 1 2 cts service by hand tool while contractor was performing fence work No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MICHAEL DESIGN BUILD | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 inch IPS service while digging.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | TEAM FISHEL | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor hit marked 1 inch plastic service with shovel while potholing.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-17 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 18 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARIZONA PIPELINE | NORTH HILLS | CA | Y | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Company contractor located and marked gas service for themselves While using concrete saw crew cut into 3 4 steel service Service was found in the concrete approximately 4 depth Fire department evacuated 2 residents and closed street in front of address and including in front of 4 neighboring houses
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Found service hit damaged hissing upon arrival.ï¿½ Contractor dug to plant a tree.ï¿½ 811 was not called.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Jose Montano 2132168513 Reported Hit Front Yard Line. Gas Line Hit With A Shovel While Working On The Sewer Line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CALIFORNIAS S | SUN VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing sewer line hit gas line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP was digging and had exposed copper casing, they used a hacksaw to cut into the casing to see if it was an abandon line and cut into 0.5 inch plastic service.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | AMERICAN INTEGRATED SERVICES INC | WILMINGTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was excavating in private property and damaged 1 inch plastic service with excavator. Found abandoned steel service but should have hand dug around our riser. Marks on sidewalk note the service as plastic.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PAEZ CONSTRUCTION | INGLEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ALL USA marks were GOOD, contractor was cutting sewer with a saw and cut through our service without verifying depth of service. This is the second damage to this service with the same contractor. First time NO USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SEWER PIPELINE | LOS ANGELES | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor for homeowner began digging to repair sewer lateral prior to notifying 811 and while excavating, damaged 1 inchIPS gas service with hand digging tools.ï¿½ Contractor called 811 after the damage had occurred and upon arrival, SCG locate and Mark found damaged line and notified supervision.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GWG CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit line with shovel while digging to install drain on side of house.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NS CLEANUP | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hired NS Cleanup to install a new drain line for the garage which will be converted into ADU.ï¿½ NS Cleanup began saw cutting concrete for trench when they cut into 0.5 inch Plastic encased in 0.75 inch steel.ï¿½ Homeowner called in a USA ticket but only as of that morning around 8am.ï¿½ Ticket was not legal until, 5 13 21, approximately 8am.ï¿½ ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor repairing driveway hit service line with shovel while digging.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ERS RESCUE ROOTER | PARAMOUNT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor his PLA line. No USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | WA RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor dug outside of described work area on ticket, locator specified on ticket that work would be performed on south side of street per Rasic. Damageï¿½occurred on north side of street.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP hit an unmarked service line due to a mismark Locator had gone of measurements and did his best with the locator The signal seems to had bled off to a stl line that he picked up while locating The actual service itself snaked around a manhole and was not traceable from the the riser
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-26 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PRME POINT CONTRACTING | CALABASAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor had exposed gas service and damaged the line while grading.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP Water failed to hand exposeï¿½gas service during trenching operations with backhoe. 0.5 inch CTS gas service was cut all the way through by backhoe. Marks by SCG were very accurate and visible.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ROOTER SOLUTIONS | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Arrived on scene and CTS pipe was cut and taped by contractorï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AL TOTAL SERVICES CONTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging with backhoe to repair sewer lateral struck 0.5 inch plastic gas service.ï¿½ No USA ticket was called before digging.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-12 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MORGAN CONSTRUCTION | GLENDORA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR DIGGING FOR FOOTINGS.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MURILLO DEMOLITION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Murillo Demolition damaged the service line with a hand shovel. While trenching for the yard line.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JF DESIGN CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to lower grade for driveway, Contractor damaged SL with rock drill
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner feets contractor began installation of new stairway in backyard.ï¿½While excavatingï¿½ for new supporting retaining walls and stairs the gas service was exposed.ï¿½ Contractor exposed the steel casing of 0.5 plastic service for approximately 5 feet and about 18 inch above ground.ï¿½ Contractor cut a inspection window into casing and then proceeded to cut into plastic using a grinder.ï¿½ Homeowner nor contractor had a USA ticket.ï¿½ï¿½ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | LADWP | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP hit our 2 inch plastic main with backhoe.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | LAWRENCE | KS | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was hand digging for landscaping and knicked and damaged 1 inch service running inside property near riser
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JA SCHOYER SCHROYER | SUNLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert USA ticket. The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging, even when in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 8 |  | WESTSIDE INVESTMENTS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | service was cut with a sawzall
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SUNNY DWELLINGS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was in the process of digging trench for fencing. Broken gas line caused by shovel, Customer did not call for USA priorï¿½to starting workï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Son of homeowner doing repair on sewer line damaged 1 inch pla service with electric jackhammer.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DWP | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew was working on water service while digging with shovel crew damaged line. Serviceï¿½Line was mismarked service was damaged.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITYWIDE CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Devloper was working on property digging trench for irrigation while digging knicked 0.50 inch cts service with shovel. Developer had called in USA prior but never renewed ticket.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LEGASPI CONSTRUCTION SERVICE | WEST COVINA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-05 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JSN GENERAL CONTRACTORS INC | PARAMOUNT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Odor complaint was called into CS 020421 ETR performed leak investigation at 4240 W 62nd St. LA and found that there was a slight smell coming from 4245 W 62nd ST. where the home was demolished but did not detect gas when taking ground samples. Unable to get in through fence. Issued RFA for Distribution to investigate next day. CT Medrano investigated 020521 and found the riser damaged and buried. Contractor damaged the riser with a backhoe when performing the demolition in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | INFINITY PLUMBING INC | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to replace sewer line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit service while digging for fence post No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EXTERIOR LIGHTING LANSCAPES | BEVERLY HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew digging to install drain and cut 0.5 feet cts SL in casing
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ADEL SAWIRIS | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor was removing trees and cut into gas service while cutting into rootsï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | DWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Installation of grounding rods and hit service.ï¿½ USA marked but DWP still struck service within delination.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | J T DEVELOPMENT | LA VERNE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Pipe attached to concrete which leaked when removed.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DMG CONSTRUCTION ENGINEERING SERVICE INCOME | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | developer struck gas service with rebar when setting it for concrete driveway
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LA LOW FLUSH TOILETS INC | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Damaged 1 2 cts service while performing sewer work
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-13 | Third party excavation damage | Valve | Steel | Grader/Scraper | 3 | 30 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | ALL AMERICAN ASPHALT | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor ran over gas valve can with piece of paving equipment and broke 3 inch steel valve inside.ï¿½ Contractor admitted fault.ï¿½ Valve was marked offset from curb accurately.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | UNITED DWELLING | LOS ANGELES | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | "Service line was located using wire at riser which was not connected properly after confirming marks put down by our ETD who located service. We also hooked up at damage point and got the correct location of pipe out towards street.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 inch PLA service damage by trench wench at new development site.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | damaged 0.5 inch cts service by DWP
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CC E COMPANIES INC | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 feet SL while digging to install electric line. No active USA for contractor
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SANTIAGO ESPINOZA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit 0.5 plastic service while hand digging to install fire pit
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CARBAJAL CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with backhoe hit plastic line.ï¿½ EFV tripped upon arrival.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ESTRADA CONSTRUCTION | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA requested, customer was grading
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LUIS GARCIA | EL MONTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was Digging to Repair water service and struck 0.5 inch plastic service with shovel, No USA was called in. company crew arrived and made permanent repairsï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MOON VALLEY NURSERY | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging a hole to plant a tree and struck our service line.ï¿½ There was no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BM GROUP LLC | BEVERLY HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator damaged the 1 inch service with backhoe.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LSI GENERAL ENGINEERING CONSTRUCTION | BURBANK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damagedï¿½ cause by shoring falling and struck gas main
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HERNANDEZ MASTER MASONRY | SYLMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic Service cut with backhoe while trench digging for sewer.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KINCAID | THOUSAND PALMS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cap damaged at stub. Repaired damaged by capping off stub at damage.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | owner was digging in front yard to install new gas houseline.ï¿½ While digging hit our plastic gas service.ï¿½ No USA was called in.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch cts line with hand tool while digging for sewer line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | TUFF PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Cesar Velasquez, of Tuff Plumbing, struck SCG branch service with pneumatic spade while digging to replace sewer laterals for property owner Viller Bates
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 44 |  | JM COMMUNICATIONS | VAN NUYS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1 inch PEï¿½ service damaged. Service was not located, it lead the Dead end main. GIS show service fed off of W 52nd Pl main. MSA not visible from street.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EDWARD CASTANEDA | LA PUENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Edward Castaneda cut SCG service line with clippers while trenching to install irrigation for home owner Trevor Steadman. Castaneda mistakenly identified service line as a root.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DEPARTMENT OF WATER AND POWER | LOS ANGELES | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Service line was damaged by DWP while working on water main project. The ETD did locate the facility as best as possible but due to measurement off and no direct connection was off his mark. This was verified by Gus Carrillo supervisor onsite as well as ETD who marked utility while supervisor onsite.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LUMAR CORP | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert USA ticket The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging even when in private property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HENKELS AND MCCOY | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was hand digging and damaged 0.50 inch plastic gas serviceï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LA DWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch cts service in casing damaged by DWP with backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JOSHUA PELL | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service line hit by contractorï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner claims friend was doing work near meter and cut service line with concrete saw.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SVN LIFE RAMCO ELECT | RESEDA | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Excavation by damaging party with no USA.ï¿½ Contractor cut through line with saw while trying to remove tree root.ï¿½ No USA to extend work into back patio.ï¿½ USA was expired.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BAKER ELECTRIC | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR DIGGING FOR WATER LINE, FAILED TO USE CAUTION WHILE DIGGING
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | ECO HOMEBUILDER | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | coring for a new footing for bleachers in a baseball diamond. Were not able to provide USA ticket number. marks visible on curbï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MANARDO GROUP | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut into gas service with saw No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RESCUE ROOTER | PARAMOUNT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working on house replacing sewer, contractor cut and damaged 0.5 inch CTS service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SPRING GATES GARAGE DOORS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged SL while digging to install gate for homeowner. No USA notified
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RC STEELE LLC | LOS ANGELES | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SYLVIA ORTIZ | LOS ANGELES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | The contractor was probing for the gas line and poked through the 2 inch plastic gas main. The contractor failed to expose by hand and protect the facility.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-08 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP Digging To Repair Water Main, Damaged With Failling Debris From Backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RUFF CONSTRUCTION INC | CARSON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was digging out drive way approach, and struck 0.5 inch Service in casing with backhoe, service was miss marked by company employee and valid USA was called in by contractor.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BUREAU OF STREET SERVICES CITY OF LOS ANGELES | LOS ANGELES |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew replacing pole and guy wire for Edison struck our 2 inch Pla gas main with a shovel and punctured it. Marks good.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | JEREMY MORRIS CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor performing sewer work did not call in Underground Service Alert.ï¿½ Service was unmarked and contractor hit service line with hand tool.ï¿½ Crew arrived onsite and controlled the broken and blowing gas service.ï¿½ Crew made repair and replaced broken section of pipe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | MATTHEW STEWART CO | SIGNAL HILL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit our service and thought unmarked line was abandoned Per locator GIS showed a standard and branch when there were actually two standards Our locator verified in Service History and measurements the hit standard was not documented in GIS
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 4 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RUIZ BROS CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called in for work being performed.ï¿½ Contractor drilled into 1 inch gas service and called gas company.ï¿½ Customer service requested Distribution and crew arrived and controlled gas shortly after arrival and made permanent repair.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damaged by unknown party 6 people evacuated due to migration of gas Crew controlled gas and made permeant repairs
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KC GENERAL BUILDING INC | NA |  | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit a plastic service with a backhoe and per ETR unable to provide a USA ticket.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-10 | Third party excavation damage | Riser | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CALIFORNIA DRILLING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Demo the whole lot
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | GREEN LEAF | HUNTINGTON BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 service damaged by contractor with mini ex when doing demo work for new sidewalk
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MCCAN EXCAVATING AND DRILLING | LONG BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew hit 1 inch PLA service with Backhoe, while trenching.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MECHANIC EXCAVATION AND DRILLING | LONG BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit 1 inch plasticï¿½service with backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NICKY FIERRO | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged plastic service while digging to install electrical conduit. The locater did not mark this due to it not being mapped.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 8 |  | RAIMONDO CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Raimondo Construction Co was excavating with a backhoe and trenched to place an electrical conduit No USA provided They damaged the 1 PLA service along with valve casing the day before
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 36 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NOT APPLICABLE | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Homeowner was digging with a post digger and struck the service line no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | DREAMWORK | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for addition and hit service with shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GREEN DESIGN BUILDERS INC | LOS ANGELES |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS AUGERING FOR A NEW ELECTRIC POLE WHEN THEY HIT THE PLASTIC SERVICE INSERTED THROUGH 1 1 4 inch STEEL CASING. SERVICE WAS UNLOCATABLE.ï¿½ CREW TRIED TO LOCATE THE SERVICE AS WELL WHILE THEY WERE ON SITE AND COULD NOT GET A GOOD SIGNAL.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GABRIEL SAADAT | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was exposing the corner intersection they had just concrete cut. They were using equipment to pull away the concrete. the main was marked by them contractorï¿½ after potholing.ï¿½ line was marked in orange paint due to it being shallow.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | POSADA PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert USA ticket The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging even when in private property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | HHS COMMUNICATIONS | AZUSA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor on site cut through 0.5 inch CTS Service in casing.ï¿½ No pothole was performed.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MIKE PRLICH SONS INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contactor was installing storm drain for city of LA and wile pot holing the gas service they struck it with a shovel Company Crew arrived and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | ALFREDO GOMEZ | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit 2 inch plastic svc with a backhoe. service was marked correctly.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BEVERSON CONSTRUCTION | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew digging over 0.5 inch IPS SL and damaged with shovel. Crew admitted to seeing warning mesh but still hit line. 5th time at this location, for damage andor service alteration for same contractorcompany, for same building and for the same existing SL.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BHP COMMERCIAL SERVICES | REDONDO BEACH |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service was struck with a probe.ï¿½ It is unknown what type of work was being done by home owner.ï¿½ USA was not called.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | CROSSTOWN ELECTRICAL | BALDWIN PARK |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit service line but EFV installed so no major gas flowï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALFRED MANAIAN | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home Owner hired gardener to plant a tree and while digging hole gardener hit service line. No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALFRED MANANIAN | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to maintain markings and struck previously potholed 2 inch PLA Line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TEICHERT PIPELINE | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert USA ticket The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging even when in private property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VCI CONSTRUCTION LLC | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor trenching to install 5G communications when gas line was hit.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VALUE CONSTRUCTION | SHERMAN OAKS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 inch cts PLA service, while trenching to install pool line. Third party did not have USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ROSELYNN JUAN | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in, and contractor hit gas svc with shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | D CORPORATION | NUEVO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Fence Contractor Damaged plastic SL while digging to install fence for Homeowner
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GATOR CONSTRUCTION | SANTA CLARITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit gas line while installing fence.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP was trenching with a backhoe Upon arrival at Vista and Beverly Blvd the 2 plastic main was damaged by LADWP on the north side of Beverly Blvd ï¿½The locator had a meeting with the LADWP Gregory Matchie 818 749 5204 Gregory matchie LADWP com and what was discussed is that the excavation would stop north of Beverly Blvd at the alley on Vista That is where the main ends at Vista north of Beverly Blvd Also the locator mentioned per the conversation meeting with LADWP it was stated that they would not be doing any excavation near Beverly Blvd This meting was conducted verbally The 2 main is located in the sidewalk the HP main is located within ten feet of the delineation No HP standby was requested
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | BRADLEY JAMES BONTEMS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ALL gas lines were marks out correct. Contractor hit service with shovel while trenching.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ARMEN | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was working to replace sewer line when they damaged the 1 2 CTS service The service was damaged on 9 8 2021 the contractor used tape and water clamp in attempt to stop the leak SCG was notified on 9 9 2021 of the damage as gas began to escape
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ROBERT PAGAN CONSTRUCTION CO INC | LOS ANGELES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Customer contractor Robert Pagan hit current SCG service line while trenching in preparation for SCG to install a new service line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | AMERICAN DRAIN LLC | PALM SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber was doing work for homeowner and plumber cut into 0.5 inch cts in 0.75 inch steel casing with Sawzall.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ESSENTIAL LIFE | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 2 Plastic service No call for USA No evacuations Crew arrived and made repairs
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DIRT WORK ENGINEERING | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was working on sewer line when they hit it with a backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | area of work not marked. branch service struck while excavating
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RED LILY PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 2 PE plastic service hit with shovel by Red Lilly Plumbing exposing sewer line to make repairs USA ticket was not legal Started working before the 48 notification legal start time
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARTIN CONSTRUCTION INC | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The Planner is currently investigating this matter.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MANNING TRUST INC | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic service with jackhammer while digging
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ARROW GARDENING | INGLEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Contractor damaged service line while digging to install fence post
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-07-16 | Third party excavation damage | Not Available | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALL ABOUT LANDSCAPING | TARZANA | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | NA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MG INVESTMENT PROPERTIES | VAN NUYS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA landscaper dug through 0.5 inch pla service with a Pick Axe.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-09-11 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SJ CONSTRUCTION TECH EO | LOS ANGELES | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Contractor damaged gas service and did not call for an Underground Service Alert USA ticket The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging even when in private property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-06 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 9 |  | HW POWER INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | H.W. Power damaged 2 inch plastic main while excavating with hand tool. Marks were within tolerance zone.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 8 |  | ARCS PLUMBING SERVICES | PALMDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic service while hand digging for sewer repair.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | J S PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | svc hit with shovel while digging for drainage pipe no USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 30 | 23 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HZS ENGINEERING CONSTRUCTION | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | wrap damaged from 3 4 service with exposing for new drainage installation no blowing gas
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Plastic 1 2 CTS service hit by DWP while replacing water service Claim service was not marked but 3 PE main marks visible Concrete where service marks would be had been removed
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ELIRAZ MALKA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HitLine 3rd party contractor . Valid USA .Crew controlled leaking service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | RENE VASQUEZ | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Dig in on service with sharp shooter shovelï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 21 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | LUIS BAREO | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SAMOUEL SHEMTOV | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner had his workers digging with backhoe in the front yard and pulled the plastic service that was incased in steel 0.75 foot piping. The plastic service was damaged at the SMC.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EXCLUSIVE POOLS INC | GRANADA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew was trenching to install drain system when they hit 0.5 CTS NO USA service with shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | golden state water damaged cutback service when installing new water service.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SHLOMO | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors unhooked three meter manifold from wall to stucco house, while pulling on manifold, riser snapped below service valve at threads.ï¿½ Replaced AL riser.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | G A | VAN NUYS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged correctly marked gas facility while attempting to hand expose. Gas company crew on site informed contractor to use more caution while excavating around underground substructures, even if by hand.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARROW PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner hired contractor to digï¿½ out for new drain. Contractor had no USA.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | JIMMY CENTENO | LOS ANGELES |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CUSTOMER DID NOT REQUEST FOR A USA, CUSTOMER WAS DIGGING TO INSTALL A WALL
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TEICHERT PIPELINE | CHINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Doty Bros came in contact with an abandoned service in private property. line was not active.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-04-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MENUET ADAMS | CARSON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Requested, Digging For Irrigation
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DAN LEWIS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RENU MULTI FAMILY | SCOTTSDALE | AZ | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Locator failed to mark service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor while excavating to install sewer damaged 1 2 ips service with pick axe No USA was called
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | GUS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 2 inch plastic gas main, crew made permanent repairs. Contractor was educated about USA law.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-02-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AR PIPELINE | NEWBURY PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Lupe Castillo, Third Party contractor was digging with hand shovel to install power lines.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2021-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.5 | 43 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BALI CONSTRUCTION | SOUTH EL MONTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Owner wanted to plant a new tree and in the process of removing the old tree, he cut through a root with a saw and came in contact with our service.
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2021-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALAMEDA CONSTRUCTION SERVICES | COMPTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water Company doing water project struck our service with a shovel while exposing. Marks good.ï¿½
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2021-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BOX CONSTUCTION | ROLLING HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Digging foundation for new home to be built.
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 2 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PHIL REZVANI | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged gas service with mini excavator. servive was visiblly marked with marking flags.ï¿½
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2021-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 7 |  | NA | LYNWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch IPS HIT while performing emergency sewer repair
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 6 |  | JOSE AMAYA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged gas service when digging up for new sewer install no usa was called in mcr was created
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2021-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | SULLY MILLER CONTRACTING | BREA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor thought steel line was active gas line.ï¿½ Active gas service was plastic.ï¿½ Marked correctly.ï¿½ Bill Contractor.ï¿½
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2021-06-21 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | SE Pipeline excavating for main job, hit 0.5 inch plastic service with shovelï¿½
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 48 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PETER MCCOY CONSTRUCTION | BEVERLY HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew was digging near service and Knicked 1 inch plastic service with round point shovel ï¿½
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2021-04-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 48 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ROTO ROOTER | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor doing work for sewer, damaged 2 inch adalay main with excavator.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2021-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 48 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ROTO ROOTER | PARAMOUNT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was digging to replace sewer, Contractor stuck and damaged 0.5 inch cts service with backhoe.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JULIONJJJJOTO ROOTER | PARAMOUNT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party contractor was trenching for sewer when service line was hit with a hand shovel.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ESSEX GENERAL BUILDERS | CALABASAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service line while digging out for pool.ï¿½
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2021-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | OCEAN POINT DEVELEPOMENT | MALIBU | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | NA
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | MALIBU | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing stakes for rebuild due to recent fire.ï¿½
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2021-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JB ENGINEERING | MALIBU | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor thought gas was abandoned and damaged 0.5 inch ips adlyA pipe. replaced 1 foot of pipe.ï¿½
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | A1 POOL SPA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching to install PVC Pipe for pond and didn feett know gas line was there.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 48 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GMP SEPTIC AND SEWER | MALIBU | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | directional bore hit steel service to standard and branch when pulling conduit through slot hole
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 48 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KIA CONTRACTORS | SYLMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ï¿½"
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KIA CONTRACTOR | MALIBU | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating for sewer repair and damaged our PE service.ï¿½
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-08-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BENNET LANDSCAPE | HARBOR CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor was hand digging in yard to install conduits and struck our plastic line There was no USA delineation but front of property had No Gas Water and Comms written in front of driveway
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ASPLUNDH CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor installing electrical for the City of Manhattan Beach hit line with shovel.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BARDEN ELECTRIC | MANHATTAN BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor exposed our 1 2 ips line accurately marked and bored a 4 accubore right on top of it and damaged it midway through the property Negligent in protecting our facilities
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-09-21 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SE Pipeline did not accurately locate gas service Gas service was a cross lot and was struck with a shovel 116 4th st was the service that was struck
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOTLINE CONSTRUCTION | MANHATTAN BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hotline construction hit exposed 1 2 cts line with shovel USA was notified and service was marked properly They have hit our lines multiple times this month and are very negligent
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-06-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JMP BUILDERS INC | LONG BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was open trenching parallel next to our line and struck it with a shovel.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-06-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HANOVER BUILDERS INC | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer was welding on steel beams that run on the sides of the home about 50 feet down. The gas service was running along side the steel beam that they were welding on and blew a pin hole in the 1 inch plastic service that was under about 6 inches worth of sand.ï¿½
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HOTLINE CONSTRUCTION | MENIFEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to dig to installation depth. He stopped once he found the oldï¿½gas line. He then broke to newer live one with the excavator..
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-03-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOTLINE CONSTRUCTION | BRENTWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging by hand to expose the plastic gas main and struck it. USA marks were located correctly.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 17 |  | HOTLINE CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Contractor for Edison pulled up on a 3 4 steel line where 1 2 cts was inserted and ripped our line Looks like contractor purposely pulled up on our line to install four 4 conduits where our service line was crossing Damage prevention was on site to investigate the matter
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HOTLINE CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Locate was spot on contractor didn t dig deep enough to expose 1 2 ips plastic Dug past it by a foot and found a 3 4 steel pipe and assumed it was live Used backhoe to excavate the rest of the hole and hit our accurately marked line
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-06-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CITY OF MANHATTAN BEACH | MANHATTAN BEACH | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Customer request positive I.D. of gas line inside of a copper service.ï¿½
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | STREAMLINE LANDSCAPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor cut into svc while installing drain
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-04-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0 | 30 | 26 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | PERFECTION PLUMBING | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor dug by usingï¿½oldï¿½USA marks and pulled plastic 2 inch pe main
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | W E O NEIL CONSTRUCTION CO OF CALIFORNIA | EL SEGUNDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor dug into our plasticï¿½gas service that was not identified in Service History and is not connected to a riser.ï¿½
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | KOLB CONSTRUCTION | REDONDO BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Private contractor was digging access point to homeowners crawl space and struck our 1 2 cts line with a shovel and clamped the service USA was not called Contractor should be billed
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-08-02 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CASNER CONSTRUCTION | REDONDO BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was installing retaining wall for planter and struck 2 PE gas main with shovel possible pick axe USA was good and utilities were properly located
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-07-16 | Operator excavation damage | Miscellaneous/Other | Steel | Backhoe/Trackhoe | 1 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | while grading side of hill after excavating for bore pit backhoe came in contact with drip line that is fed from 6 line henderson clamp was used to control gas
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ADEEDOO PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging in backyard struck 1 2 cts with shovel USA was not called
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-08-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HOTLINE CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck unmarked service with backhoe House was on a corner lot and service was coming off cross street
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOTLINE CONSTRUCTION | MANHATTAN BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was accurately marked with a visible mark less than 2 feet away Service was already exposed 3rd party contractor did not adequately protect our facilities
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HOTLINE CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Hotline Construction was machine excavating trench when they struck a properly marked gas service Customer should be billed
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HOTLINE CONSTRUCTION | BRENTWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Contractor was using a backhoe and damage our gas line. Delineation was mismarked.ï¿½
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FINLEY S TREE LANDSCAPE | TORRANCE | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Service pipe was damaged while excavation tree. 3rd party not able to determine tree root and pipe.ï¿½
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PILLAR HOMES | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not notify USA and damaged 0.5 inch PE service with a uniloaderï¿½while removing a planter.ï¿½
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | MOORE BASEKETBALL INSTALLATION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor grading for basketball pole They did not have USA
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ASOLUNDH CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged line while potholing around tree roots and damaged gas service.ï¿½Failed to maintain distance from gas service
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Electrical contractor doing work for homeowner turn out to be gas houseline leaking shut off and clam shell gas riser issued 1813 tell customer repairs houseline leak.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PREMIER BUILD GAS | LONG BEACH |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Fernando Serna, Third Party Contractor was excavating to install electrical conduit when service line was hit with shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | MAYWOOD | 2021-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SANTIAGO MEJIA | MAYWOOD |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HIT MAIN BY CITY OF REDLANDS CONDUCTING WATER MAIN REPAIRS. NO USA.
Southern California Gas Company | N | LOS ANGELES | MISSION HILLS | 2021-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | D R HORTON INC | CANOGA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging contractor damage out plastic service line while digging to install a new drain Contractor did not call in for a USA ticket
Southern California Gas Company | N | LOS ANGELES | MISSION HILLS | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SUPER DAVE S PLUMBING ROOTER | SUN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, contractor hit service at branch tee
Southern California Gas Company | N | LOS ANGELES | MISSION HILLS | 2021-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | VELASQUEZ IRON WORKS | SAN FERNANDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hired fence contractor to perform fence installation, fence contractor failed to obtain valid Dig Alert Ticket. As of result damaged 0.5 CTS branch service while excavating post holes. 2 Outages
Southern California Gas Company | N | LOS ANGELES | MONROVIA | 2021-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | GROUND BREAKERS | LEBEC | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Two Brothers Septic Tank Services struck SoCalGas service line with backhoe while repairing septic tank for homeowner Pedro Alvarez.ï¿½ The work area was marked with paint and flags.
Southern California Gas Company | N | LOS ANGELES | MONROVIA | 2021-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | EXCEL PAVING CO | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor grading to install new curbgutter. backhoe tried moving large rock and grabbed 0.5 plastic service inserted in steel. Contractor did not pot hole our service.
Southern California Gas Company | N | LOS ANGELES | MONROVIA | 2021-07-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ROGER LI | MONROVIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Ready for Area Manager approval
Southern California Gas Company | N | LOS ANGELES | MONROVIA | 2021-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | WESTERN ROOTER | SANTA CLARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Plumbers damaged gas pipe while installing the sewer lateral.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2021-02-05 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HW POWER | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 2 inch gas plastic main while potholing for a pole replacementï¿½with our main located directly next to power pole. Damage was a minimal but fixed.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MAX OUT INC | LAWNDALE | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | USA marks off by 27 contractor hit service with hand tool
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LUIS REFUGIO | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch cts plastic service with hand tool.ï¿½ No USA notification.ï¿½ 3 residents evacuated from property by fire department.ï¿½ Crew arrived, stoppedï¿½gas flow, and evacuations were lifted.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2021-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew found code 1. Found a clamp on plastic service from unknown damaging party.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2021-12-16 | Third party excavation damage | Not Available | Material not known | Not Available | 0 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic service.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MAX OUT INC | LAWNDALE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 0.50 inch plastic service with hand tool. Valid USA.ï¿½ Marks were removedcovered during excavation with no call for re mark.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2021-11-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 14 |  | BIG BEN ENGINEERING | IRVINE |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | "CONTRACTOR WAS DIGGING TO ECTEND FOOTING WHEN HE HIT THE PLASTIC SERVICE.ï¿½ THE CONTRACTOR KNEW WHERE THE SERVICE WAS DUE TO THE COMPANY CREW BEING ON SITE TO DO AN ALTERATION ON THE SERVICE.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2021-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | BIG BEN CONSTRUCTION | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | 3rd party contractor trenching trench in property hit and damaged 0.5 inch IPS service with electric clayspade jackhammer.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2021-11-23 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BIG BEN ENGINEERING | IRVINE |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Owner of property was trying to fix a water leak and was digging without a USA ticket. While digging with a shovel they damaged the 0.5 pla service.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BIG BEN CONSTRUCTION | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor came in contact with 0.5 inch Line. No USA.ï¿½
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2021-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MSP CONSTRUCTION | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for home owner damaged plastic service with jack hammerï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | MORENO VALLEY | 2021-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JOSUE NAVARRO | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor struck our gas service while digging without a USA ticket.
Southern California Gas Company | N | LOS ANGELES | NEWHALL | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARTIN CONSTRUCTION | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Miss Mark Valid USA Contractor hit 1 IPS Service while trenching to install conduit Had counseling session with Locator
Southern California Gas Company | N | LOS ANGELES | NEWHALL | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | THE PLUMBOLOGIST | NEWHALL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber hit 0.5 CTS Service while digging for emergency waterline repairs
Southern California Gas Company | N | LOS ANGELES | NORTH HILLS | 2021-03-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PLUMBRE MAN PRO | WINNETKA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber was digging to install a clean out on sewer lateral with no USA
Southern California Gas Company | N | LOS ANGELES | NORTH HILLS | 2021-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HI AM INVESTMENTS INC | SAINT LOUIS | MO | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contract trenching without USA to install drainage hit newly installed gas service Crew made repairs in ditch Trench crew assumed pipe was deeper
Southern California Gas Company | N | LOS ANGELES | NORTH HILLS | 2021-12-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | R3 CONTRACTORS | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractorï¿½hit a inchabandoned stub inch that was never abandoned. The stub was not marked as well. The locater did not know this and is not at fault.
Southern California Gas Company | N | LOS ANGELES | NORTH HILLS | 2021-09-30 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 4 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LADWP | VAN NUYS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP crew while attempting to cut and remove pvc riser at existing power pole excavation using reciprocating saw inadvertently cut a small slit on our 4 Gas Main that was directly underneath their conduit Existing marks adequate to show Gas Main located near power poles and marks were within 2 ft rule from damage location 1 nearby building evacuated with 2 evacuees at the time Building evacuated is a small business Liquor Store business interrupted while the repairs took place In addition power was interrupted to small business center for the SCG crew to safely perform their work Repairs made with leak clamp
Southern California Gas Company | N | LOS ANGELES | NORTH HILLS | 2021-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CITY PLUMBING AND ROOTER | WINNETKA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner hired plumber to repair sewer and water line.ï¿½ Plumbers hit our plastic service with electric clay spade.ï¿½ No USA was called.ï¿½ Permanent repairs made by company crews.
Southern California Gas Company | N | LOS ANGELES | NORTH HILLS | 2021-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SALVADOR S PLUMBING | SILMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 inch plastic service while pot holing.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | COLLIN MASONRY | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 inch IPS gas service while excavating for irrigation. No USA
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BUILDER HUB INC | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic service no usa ticket
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ET DEVELOPMENT BUILDER HUB INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer had his laborers digging around the service line and a worker struck the line with a shovel.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SERGIO GUZMAN | NORTH HOLLYWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA ticket Customer removing fence post and caught the service when lifting the post out Service apparently in contact with post
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LUIS GONZALEZ | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1 2 plastic service with trencher No USA
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-10-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | E BRAUH | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged gas service with a back hoe whileï¿½excavating forï¿½building foundation.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 27 |  | LADWP | NORTH HOLLYWOOD |  | N | Y | Yes | Yes | No | Yes | No | Yes | No | Damaged 0.5 service by contractor repairing water service to residence. Crew controlled gas and made permanent repairs.ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-03-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DELTA PIPELINE INCORPORATED | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Facility was marked out correctly with yellow paint.ï¿½ Contractor failed to pothole to verify.ï¿½ Contractor ripped through 1 inch plastic service with backhoe.ï¿½ Was bent back and taped.ï¿½ Valid USA ticket.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PETRELLI ELECTRIC COMPANY | SANTA CLARITA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit 0.5 inch plastic service.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP excavating by hand methods using shovel to expose gas facility unfortunately hit the line 1 Outage Crew made repairs in the same ditch for DWP water main Gas Svc marks north of ditch was more than 2ft off mark however mark just south of ditch was in line with the gas service utility Excavator should have used more precaution especially in easy soil
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LADWP | VAN NUYS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DWP Trenching for watermain install potholed for gas service at this address They exposed a steel service pipe and called in to confirm that was the live utility Locator J Salcido reported to site hooked up to the riser wire and confirmed that was the plastic service encased in steel pipe DWP proceeded to excavate with backhoe and damaged the correct facility which was direct bury service not per service history an encased service in street Crew reported and made necessary repairs in DWP trench
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ONE STOP PROPERTY SOLUTION | MISSION HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor pulled up service with grader while pulling up concrete.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SOUTHWEST DEVELOPMENT INC | VAN NUYS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor digging for pool hit our service with shovel
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-01-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARAMNOND SOROOIAN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JESUS MIRANDA | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors were digging trench to install fencing and hit our plastic service No valid USA Permanent repairs were made
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CONNER CAMPHOUSE | NORTH HOLLYWOOD |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was digging with back hoe and hit our plastic service line.ï¿½ excavator knew out line was there, service was correctly marked out but he carelessly used backhoe over plastic service.ï¿½ Permanent repairs were made same day.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 14 |  | UNDERGROUND SOLUTIONS | SIMI VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was digging with backhoe to install conduit.ï¿½ Contractor failed to hand dig to expose service before digging with backhoe.ï¿½ Contrctor had valid USA ticket and service was marked 28 inches off actual line.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NORTH HOLLYWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging to install a post for a new gate. Thought our service was a root and sawed through it.ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While a contractor was using a backhoe, they hit the gas service.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NORTH HOLLYWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HAMIK AVETISYAS | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Digging on expires USA. Did not use caution digging over gas service where marked.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 16 |  | WA RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor slightly nicked plastic service while auguring.ï¿½They potï¿½holed abandoned steel service thinking it was live and nick the plastic service 2 feet away.ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SIPAN DESIGN AMP DEVELOPMENT LLC | GLENDALE |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Field Planner Jose Martinez drove by job site and noticed that service had a weird clamp on it. Called it in and had a crew dispatched out. 3rd party contractor had damaged the pipe but did not report it. Crew made proper repairs.ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | plastic service in casing was cut and nobody around job site
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | NORTH HOLLYWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging with backhoe to install drains no usa.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OFER | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor dug before USA was good, contractor was using auger and hit service. Contractor was installing septic tank.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2021-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EDWARD HARUTTYUNA | NORTH HOLLYWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Workers for homeowner hit 1 2 plastic service with shovel while trenching to install waterline No USA
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2021-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SALVADOR TORRES | NORTHRIDGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service line while hand digging to relocateï¿½Electrical Panel. No USA ticket although homeowner claimed they did, no one was able to produce copy or at least number.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2021-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 17 |  | GEORGE AYLI | NORTHRIDGE |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with a backhoe and hit the service line. No USA the USA they referenced was from 2019.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2021-07-02 | Third party excavation damage | Meter | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NORTHRIDGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party hit service and damage 1 2 USA was expired
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2021-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NORTHRIDGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor hit 0.5 inch CTS service. No USA called in
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NORTHRIDGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Second Occurrence of damaging the service. No USA
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | NORTHRIDGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner had contractor dig on property to trench and install new sewer line.ï¿½ Contractor damaged our 0.5 inch cts service with shovel.ï¿½ Customer did not have a valid USA ticket number.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2021-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NORTHRIDGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner digging, damage 0.5 inch Service.ï¿½No USA called in
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2021-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | 2H CONSTRUCTION | SIGNAL HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was augering to install a pole forï¿½covered area and hit the service line.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2021-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LADWP | NORTHRIDGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DWP hit 0.5 service. was not marked correctlyï¿½
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2021-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | NORWALK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner was digging to install a drain line in his yard
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2021-12-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | METROPOLITAN STATE HOSPITAL | NORWALK |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party excavator trenching to install first of several laterals on Rayen St damaged 2 inch PE main while digging with backhoe. SCG Main marks were not properly maintained after recent rain storm, contractor believed main turned into the alley and that it didnt connect to Sepulveda Blvd. However no end of main or elbows marked to cause this confusion.ï¿½
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2021-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2021-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | STEPHEN DORECK EQUIPMENT RENTALS | PICO RIVERA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor was digging trench for new water main when they dugin to a 1 inch PE service.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2021-11-29 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | HW POWER | ANAHEIM |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working for homeowner struck our service line while hand digging, No USA ticket.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2021-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | GENERAL CONTRACTORS TENANT IMPROVEMENTS | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck 1 inch plastic 3xs while setting metal supports for concrete forms
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2021-12-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DORECK STEPHEN EQUIPMENT RENTALS INC | PICO RIVERA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party Contractor working on behalf of the homeowner was trenching for sewer and private gas houseline damaged the gas service pipe that feeds this address and the neighbors. No USA was called prior to excavating. Pictures Taken. 2 Outtages one house vacant which was the house work was being conducted. Crew repaired section and reinstated both gas services. Occupant advised to contact dig alert to have utilities marked.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2021-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 4 |  | SUN CAPITAL ENERGY | POMONA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | VCI was boring and hit our line that was not marked.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DANIEL MACIAS | PACIFIC PALISADES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2021-02-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MARKS STEVENS CONSTRUCTION | TARZANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CS spoke to contractor.ï¿½ Contractor was grading with excavator and did not pothole service before using equipment.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2021-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LABOR OF LOVE HOME REPAIR | TOPANGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for home owner excavating for sewer line struck 0.5 inch cts service line in property.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2021-12-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JIP CONSTRUCTION INC | NORTH HOLLYWOOD |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was installing water softning system and thought our line was the water service, he started to saw into it when gas started to escape.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2021-04-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JIMENEZ DEMOLITION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors damaged 1 inch service line while demoing house.ï¿½ Appears to have been hit multiple times.ï¿½ No USA. Abandoned at SMC to prevent further damages.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RH HOME | PACIFIC PALISADES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was excavating with large machinery and gauged our 2 inch main.
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | S PEREZ | PACOIMA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper home owner was pot holing in yard to install pergola Hit plastic service with shovel No valid USA
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2021-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | EASY FLOW PLUMBING INC | RESEDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor, after exposing line, accidently hit service with backhoe.
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2021-05-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PACOIMA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor hit 0.5 inch IPS with pickaxe while digging up wall footing.ï¿½
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2021-12-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | PATRICIA MUNOZ | MISSION HILLS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging a trench the third party contractor severed our 1 inch pla service
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2021-03-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DENALI CONSTRUCTION | SUN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Was digging out sewer line and hit plastic gas service using a shovel.
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2021-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | PACOIMA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner contracted friends of the family to demo and construct a paver driveway, during the course of excavating for subgrade without a valid Dig Alert ticket the crew broke the gas service. SCG crew arrived and identified the pipe as obsolete PVC pipe that cannot be fused on. To mitigate leak emergency USA was called to abandon service at SMC and reinstate at later date. It is recommendation from District that homeowner is only billed for work estimated amount of time to control leak at the source, due to obsolete pipe it took longer to remediate appropriately D. Real
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2021-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CAL EMPIRE | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd Party Contractor hit 1 2 plastic service while directional boring to install electrical conduit USA was current locator did not mark facilities correctly due to signal interference The service shows on other street per GIS and Epoch Records ï¿½
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | H7 | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service by 3rd party contractor w No USA
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2021-12-18 | Third party excavation damage | Miscellaneous/Other | Steel | Augur | 6 | 100 | 95 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ROKSTAD | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck a 6in high pressure supply line with an auger.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SCE | LANCASTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCE hit gas svc line with shovel inside P P No USA on site or called in
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 9 |  | ROTO ROOTER | LANCASTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 service by 3rd party contractor w No USA
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 9 |  | ROTO ROOTER | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 1 plastic service by 3rd party contractor
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2021-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JUAN OSPANA | PALMDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damage 0.5 inch plastic service while installing drain
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2021-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ANTONIO CISNERO | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Antonio Cisnero struck service line with hand tools while trenching to install electrical facilities for homeowner
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2021-02-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GENUINE CONCRETE | LANCASTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors lowering final grade for drain.ï¿½
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2021-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VILLA SCAPE CONTRACTOR | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage by 3rd party contractor No USA on site Hit 1 2 svc line with Backhoe
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2021-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AAA GREEN BUILDERS | MISSION HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer hit gas service while digging for fence
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ED POOL SPA | PALMDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit Service No USA
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2021-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Trenching to install a fence
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2021-11-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GROUNDWORKS ENGINEERING INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. party contractor was digging for for power when they hit Gas service with shovel.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2021-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PALMDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damaged 0.5 in plastic service with an electric jack Hammer while installing Leach Field for Septic System.ï¿½ USA 811 was not called.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2021-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | PALOS VERDES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Jesus Lecona Homeowner Rantin Golchini struck SCG service line with skid loader while grading his yard in preparation to build a retaining wall.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2021-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EAP EXCAVATION | PALOS VERDES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Elio Chitay from EAP excavation called that while digging with a pick hit service line. 310 202 0647
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2021-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20001 |  | 1 |  | CAL CO | LOMITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Grading the land for construction and struck gas service. Did not call USA prior to beginning work.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2021-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WAR CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging a trench alongside our gas line with sharp shooter struck our 1 2 ips line trying to remove roots USA was called and gas lines were accurately marked
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | W A RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit our plastic service with an excavator after being exposed.ï¿½
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2021-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MASTER PLUMBING | LOMITA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA REQUESTED, CONTRACTOR DIGGING FOR A POOL
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2021-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | PALOS VERDES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit 0.75 steel svc with a pick axe no USA called
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GS EQUIPMENT AND RENTAL | REDONDO BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor was using back hoe for grading when service was hit. Paint marks were good, flags seem to be moved for excavation purposes.ï¿½
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WARASK CONSTRUCTION | PALOS VERDES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service damaged by backhoe while trenching Service was not marked USA was current
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2021-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | W A RASIC | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was digging trench for new water main. Contractor states that there was no mark for the steel service that was struck. Locator stated it was marked. He stated he specifically marked that service. Contactor ended pulling service to where it was blowing over the SMC connection across the street.ï¿½
Southern California Gas Company | N | LOS ANGELES | PANORAMA CITY | 2021-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MIRIEM SCHEFER | PANORAMA CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 0.5 inch plastic service while digging
Southern California Gas Company | N | LOS ANGELES | PANORAMA CITY | 2021-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | PANORAMA CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner was digging in yard to remove tree.ï¿½ Hit 0.5 inch plastic branch service to the neighbors house.ï¿½ No USA was called in.ï¿½ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | PANORAMA CITY | 2021-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LA GREEN DEVELOPMENT | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was trenching to install new water sewer pipeline for property.ï¿½ As they were sawzawing to remove tree root, they cut into our 0.75 steel line directly below the root.ï¿½ Permanent repairs were made with 0.75 clamp.ï¿½ No valid USA.
Southern California Gas Company | N | LOS ANGELES | PARAMOUNT | 2021-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MDA BUILDER | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck a 1 inch plastic service with a backhoe digging for a sewer.
Southern California Gas Company | N | LOS ANGELES | PARAMOUNT | 2021-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 0 | 0 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | PARAMOUNT | 2021-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 44 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | W A RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 0.5 inch PLA Service damaged by a hand shovel while potholing for water line installation.ï¿½
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MORLEY BUILDERS | SANTA MONICA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit our plastic service it does not currently serve a building because the construction has not been finished yet. The crew turned off the curb valve, which stopped the gas. Afterwards, the crew performed a service alteration to repair damaged section.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CITY OF PASADENA | PASADENA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Pasadena City water was installing a new pipe and hit our 0.5 cts service cutting it in half.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-06-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | STAN KRUPA | SAN DIMAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging with pick axe for electrical and hit our plastic service
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PASADENA WATER POWER | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Pasadena water and power were using their backhoe and the operator hit and broke our fully exposed and marked out service.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-08-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 37 |  | SOCALGAS | PASADENA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | company crew was potholing for gas line and hit service.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-04-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TD GENERAL COMPANY INC | WALNUT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was using pick ax and hit our 2 inch line.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALL SEASONS | BELLFLOWER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per Abundio the contractor for All Season General Contractor stated that there was a usa for the location, But with more investigation the was no usa for this location. he said there were marks on the concrete , but they removed the concrete.ï¿½
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-05-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NEW GENERATION PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging a trench for electrical and hit our service with his pick axe. 811 was not called.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-01-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PASADENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | owner and contractor were digging with a pick for gardening purposes an hit our service line.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JIM PARTAIN | LA VERNE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor trenching to install block wall damaged 0.5 plastic service with shovel. No USA was called
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GAGNIER LANDSCAPE | SIERRA MADRE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | home owner installing solar panels with company called Cal Solar Group. Homeowner trenching for conduit upgrade to save money. USAï¿½ ticket B213000283 was under Cal Solar Group not homeowner.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-07-22 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NPL | MIRA LOMA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | contractor was digging with shovel sharp shooter
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SALVADOR RUELAS | LOS ANGELES |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While digging trench contractor struck gas line with sharpshooter.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LOS RIOS LANDSCAPING | AZUSA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ALL USA marks were good, contractor hit service to abandon home while grading.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | SOLANO TREE SERVICES | POMONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Tree company hit our line while digging to remove hedges.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GABRIEL ALVAREZ | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit with backhoe while trenching for retaining wall
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARK COYNE | PASADENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service with saw ï¿½ USA was not notified Permanent repairs complete
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | KOKO DRAINS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged cts service repaired Permanent repairs complete
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JJ CONSTRUCTION | BALDWIN PARK | CA | N | N | Yes | Yes | Yes | Yes | No damage to SUOF. | Yes | Yes | Contractor doing work to install drain damaged gas service All repairs made permanent
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PASADENA WATER DEPT | PASADENA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Water Company hit plastic service with back hoe. Failed to pothole service first. to confirm marks were correct. Marks were off by 4 feet no locate wire and company measurement was off by 4 feet.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BEDROCK CONSTRUCTION | BREA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | third party contractorï¿½hit our plastic service with a backhoe. They turned the blowing gas off using our curb valve.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PASADENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner was digging to remove a tree, did not hit line but service line broke when tree was uprooted.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MAXIMUM VARIETY STRUCTURES INC | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging to install an electrical conduit.ï¿½
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-01-06 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | FS CONTRACTOR INC | SYLMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working for the City of Pasadena damaged 2 inch plastic main while digging over it.ï¿½
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GSC IRONWORKS | LA PUENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA ï¿½ Service damaged while installing post for fence Permanent repairs complete
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 39 |  | CAL QUAKE CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors were digging to install supports for building and hit our line with an excavator.ï¿½ 39 outages
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOSE M MEJIA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner was digging in front yard to add sprinklers and plants and hit our plastic service.ï¿½ No usa called.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SUNSATIONAL POOLS AND SPAS | REDLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor was digging up pool equipment and hit our plastic 0.5 inch service
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | VICTOR CERON | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was hand digging with a shovel to put in a cinder block wall when they hit our service.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | INOR ROBINSON JR | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner was putting in a new water line and said that a rock caused the cut in the plastic service.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PASADENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging Holes To Install A Fence
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15001 |  |  | NA | ZICO GLOBAL ELECTRIC | BURBANK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator directed to immediately call for remarks and was informed it is their responsibility to ensure marks are maintained.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MAGISTRALE CONSTRUCTION | SOUTH PASADENA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging outside of delineation and damaged our service with a shovelï¿½
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DAVID MILLER | RESEDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Alameda Construction Services was digging to install bollards next to the gas meter. As they were potholing, the 0.5 inch cts service was hit causing a small leak.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | MCC EQUIPMENT RENTALS | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractors were open trenching for the city of pasadena and they hit our plastic service.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2021-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MCC EQUIPMENT RENTALS INC | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | contractor was digging to find electrical box
Southern California Gas Company | N | LOS ANGELES | PICO RIVERA | 2021-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | AMOUR PLUMBING | RANCHO CUCAMONGA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was trying to find sewerï¿½line and pulled end cap off the stubï¿½
Southern California Gas Company | N | LOS ANGELES | PICO RIVERA | 2021-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FRANK RUBALCAVA | PICO RIVERA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage by landscaper hired by the Irvine company . Wood stake puncture the service . Crew arrived and control release of gas .
Southern California Gas Company | N | LOS ANGELES | PICO RIVERA | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | METRO RF SERVICES INC | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor hit svc, while hand digginf. svc mislocated
Southern California Gas Company | N | LOS ANGELES | PLAYA DEL REY | 2021-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 5 |  | GREEN BUILDING CORPORATION | ALHAMBRA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Mark was 4 feet off when struck supervisor Andres Sandoval and ETD Robert Bernal went out to job same day and located service by hooking up to the wire on the riser and got same exact locate as before when hooking up to wire at riser Where damage occurred there was no wire to be found within hole Crew ended up putting EMS ball to help locate and putting a G on curb
Southern California Gas Company | N | LOS ANGELES | PLAYA DEL REY | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MATHEW AND STEWART COMPANY | SIGNAL HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor working for city of LA was trenching street with backhoe to install new sewer, when trenching piece of asphalt fell in and snapped 0.75 steel service in half.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2021-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALL CITY PLUMBING | RANCHO CUCAMONGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was Called in to Verify locating of gas service
Southern California Gas Company | N | LOS ANGELES | POMONA | 2021-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | CHALMERS CONSTRUCTION SERVICES INC | LA CRESCENTA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | LOS ANGELES | POMONA | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | EDWIN DE LA CRUZ | POMONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Review Complete
Southern California Gas Company | N | LOS ANGELES | POMONA | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | POMONA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner hired his neighbors to help dig his sewer line and hit our service. No USA at the location of damageï¿½
Southern California Gas Company | N | LOS ANGELES | POMONA | 2021-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PRO WEST ENGINEERING | POMONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Requested
Southern California Gas Company | N | LOS ANGELES | POMONA | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GL CONSTRUCTION | DIAMOND BAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor knew that the gas service was in the excavation but dug with a shovel and hit it anyway.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2021-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Drain cleaning equipment such as snakes, etc. | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | POMONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | sent to area manager
Southern California Gas Company | N | LOS ANGELES | POMONA | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CITY OF POMONA | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Reviewed and approved
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2021-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | JUAN SALMERON | PORTER RANCH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hand digging for sewer hit our service No USA called in
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2021-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JUAN GONZALEZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While repairing water houseline leak in yard, gardener hit 0.5 inch CTS service w a shovel. No valid USA
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2021-10-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MAINGREEN SCENE LANDSCAPE DESIGN | CHATSWORTH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Dug after ticket expired. Failed to hand dig before using excavator.
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2021-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SYED A HASAN | PORTER RANCH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 inch PLA service was damage by an auger in the process of excavating for the installation of a light pole.ï¿½
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | RANCHO PALOS VERDES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging on property for a drain pipe. Customer did not call USA and hit service during excavation.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2021-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OWNER | RANCHO PALOS VERDES | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | Damaging party should be billed Had valid USA but expired on 8 19 21
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NEIL PATEL | RANCHO PALOS VERDES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | gas service damaged with shovel when digging out for block wall blowing gas
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2021-12-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ï¿½3rd Party Contractor hit 0.5 inch plastic service while excavating . Marks not visible due to contractor excavation.ï¿½
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2021-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SALS PLUMBING INC | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber damaged plastic service with no USA
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | PACIFIC POOL PLUMBING INC | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Branch service was not properly marked with standard service Branch service was struck with trencher while plumbing company was digging for pool line
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2021-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | RANCHO PALOS VERDES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging to install an irrigation line when they hit the service line. USA had not been notified.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2021-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SEAHILL TOWN HOMES HOA | PALOS VERDES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber was excavating without a usa ticket and damaged plastic service.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2021-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JUNRU PAN PD DEVELPMENT | LOMITA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged Line Or Pipe Riser During Installation Of Storm Drains Digging With Shovel.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOMITA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LCT Huerta Arrived And Didnt Find Blowing Service ,But Was Getting High Reads Decided To Dig Up And Found Servicve Punctured With A Pavers Stake Newly Installed Pavers Were Present On Site, Service Was Being Majority Plugged By Paver Stake And Only Allowing Small Ampiut Of Gas To Escape.ï¿½
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2021-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ROY SEYAMAK | RANCHO PALOS VERDES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor exposed our 3 4 steel service smelled gas and called it in USA was notified Gas leak was due to corrosion
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2021-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 38 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | RANCHO PALOS VERDES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | gas line appeared to be cut with a hand saw.ï¿½
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2021-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | A S READE PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA notification, plumber did hand excavate but had multiple sub structures in his excavation.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2021-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NFQ BUILDERS | NA |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Excavator exposed plastic pipe that was outside of where he was trenching. Damaged ourï¿½pipe in the trench without exposing for clearance.ï¿½
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BUILDER BOY | LONG BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 0.5 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | VNYL CONCEPTS | NEWBURY PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor installing a new drive way fence hit 1 2 cts service with shovel USA was not called
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HYTON CONCRETE | REDONDO BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Hyton Concrete was trenching partially demoing and doing remodeling at 425 N Maria Ave in Redondo Beach when they struck the 1 2 cts PLA service It was branched to 427 N Maria Ave The contractor had no USA ticket and there was no USA marks on the ground
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2021-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EL SEGUNDO PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber was working to fix leaking water line on customer property and hit our line while digging. No USA.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | BERNICE CARDENAS | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor for homeowner was excavating in private property to install a fence He cut 1 2 cts service in casing with a sawzall USA was not notified
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2021-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MIKE POLAND | REDONDO BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit SVC while digging with shovel for planterï¿½
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | COMPLETE PACKAGE DRAFTING | WOODLAND HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging for Irrigation hit 0.5 inch CTS. No USA called in
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2021-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BENECIO ARIAS | RESEDA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor, Jesus Nunez, was working on sewer and cutting pipe when he nicked the buried gas line. New driveway is being installed and grade has been lowered from23 inch to 8 inch. USA ticket. Locate and mark flags were visible.ï¿½
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DEAN SHABBOUEI | ENCINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. party Contractor hit 2 inch service that APL just instilled
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | RESEDA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors were hand digging to install new sewer line Hit our plastic service with a shovel and severed it permanent repairs made with 2 couple and 1 ft of pipe No USA
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2021-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | RESEDA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage service while hand digging No USA
Southern California Gas Company | N | LOS ANGELES | ROLLING HILLS | 2021-03-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  | 6 |  | HSQ PLUMBING | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging for sewer damaged 6 feet main with backhoe in new housing complex.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2021-08-30 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | A C SPRAGGINS ENGINEERING | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 2 inch pla main w a shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2021-01-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CITY OF ROSEMEAD | ROSEMEAD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | City of Rosemead workercontractor while in the process of digging out trench line for water service hit and caused leak on gas company service while working with an expired USA Ticketï¿½
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MASREW CONSTRUCTION | SOUTH EL MONTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was dinning and hit gas service. No USA was called.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2021-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GENERAL BUILDING CONTRACTOR | TEMPLE CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was hand digging trench for drain line and hit 1 inch pe plastic service.
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BNC INDUSTRIES | SANTA MARIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Crew was digging around foundation to pour new foundation and failed to properly hand expose service Not clear if USA was valid but older flags and marks were clearly visible On going construction site with many different contractors working there ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2021-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ROBERT LOPEZ | SAN DIMAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2021-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2021-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ADAM ORTEGA | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per Javier Martinez Backhoe Operator claims they hand dug excavation and thought they were clear of the gas service. Mr. Martinez continued to remove dirt from excavation with Backhoeï¿½ and hit Gas Service.
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | RAMIREZ CONSTRUCTION COMPANY | AZUSA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor should be billed for damage
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | L G CABLE CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3 4 in steel service damaged while direction boring stub service was unknown not in GIS or service history Service stub was abandoned at SMC
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | SAN FERNANDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner Hit gas line digging footing for an add onï¿½
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2021-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SALDIVAR ALFONSO DE HARO | SAN FERNANDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors were digging to install new fencing and damaged our 0.5 cts plastic service with a shovel.ï¿½ No USA.ï¿½ Permanent repairs were made with 2 couplings and 1 foot of new pipe.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2021-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SUPERIOR CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA was not notified
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SAN FERNANDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner excavating trench to install water service and damaged 1 2 plastic service No USA called in and company crew made permanent repairs
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | HHS | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | worker hit 1 inch plastic service with backhoe while digging. permanent repairs were made.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CASTLE BAY CONSTRUCTION | ARCADIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating with out calling in USA to have gas utilities marked , damaged 2 inch pe serviceï¿½
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2021-05-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | CITY OF SAN GABRIEL PUBLIC WORKS | SAN GABRIEL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Public works doing excavation with backhoe struck 2 inch plastic gas main.
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2021-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RIGHT PRICE ROOTER AMP PLUMBING | SUNLAND |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit gas serviceï¿½
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CITY OF SAN GABRIEL | SAN GABRIEL | CA | N | N | Yes | No damage to SUOF. | Yes | Yes | No damage to SUOF. | Yes | Yes | City of San Gabriel crew hit plastic service with shovel while excavating. City crew was working job with an expired ticket. Marks were still visible and correct.
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | CARLOS LILES | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to maintain proper digging practices and failed to use a spotter.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2021-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SAN GABRIEL | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner called landscaper to remove tree stump and they hit our line, then took off before crew arrived.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2021-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  | 1 |  | HARTMAN PLUMMING SERVICES | COVINA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was using a jack hammer and hit our plastic service.
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2021-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to maintain clearance from gas service and was digging with a backhoe.
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DANIEL S DEVELOPMENT GROUP | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no USA requested, digging to install a new drain
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2021-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | AB CONSTRUCTION | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per LCT M. Souquette,ï¿½ AB Construction was pressure washing water main to install fiber optic. Service line was exposed and wasï¿½struck by pressure washerï¿½causing damageï¿½leak.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2021-07-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SULLY MILLER | BREA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractors grading and damaged 2 steel valveï¿½casings and lids.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2021-03-31 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MATUCCI PLUMBING | GARDENA | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber was repairing water service for NPL and hit our new 1 inch pla service.
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2021-06-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SULLY MILLER CONTRACTING CO | BREA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a tunnel bar and hit our plastic service
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2021-06-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SULLY MILLER CONTRACTING COMPANY | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was hand digging with a pick axe to break up the dirt in the street and they hit our plastic service.
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2021-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ENVIRONMENTAL LANDSCAPE DEVELOPMENT INC | ALTADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit our service with a shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2021-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ADEEDO | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on the sewer line hit our plastic service
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2021-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VCI | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor pulling conduit for ATT damaged gas service Permanent repairs complete
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2021-06-29 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BOB MARC PLUMBING | TORRANCE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor Damaged Gas Co. Facilities with backhoe while attempting to install sewer.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2021-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LIBIANO CONSTRUCTION | REDONDO BEACH | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | There are multiple USA for this address specifying different projects. There was no current USA for the work they were doing and where they were doing it where the line was hit. Contractor admitted that marks and flags were put in place and they were removed through out the project.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2021-04-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WATER AND POWER | SAN PEDRO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP was trenching across the street to install a water service. As they were trenching the struck our 2 inch gas mainï¿½with the backhoe. The main was mismarked by 5 feet6 feet from where the damage occurred. Company was notified and crews arrived on site to make repairs.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2021-03-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SAN PEDRO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner doing remodel struck our service with a metal stake when making a form for concrete pouring. There was an EFV so customer didnt realize he hit it till he realize he had no gas and then called it in.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SE PIPELINE | SOUTH EL MONTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | There was a USA and it was marked correctly, contractor failed to use asution while exposing gas line.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2021-10-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | STERLING PLUMBING | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor for So Cal Edison damaged a plastic service with a backhoe while excavating.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2021-12-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TORO ENTERPRISES | OXNARD |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Toro was excavating to install a sewer line struck a gas main stub with their backhoe.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2021-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Copper | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  |  | NA | ENDRIZZI ENTERPRISES INC | ANAHEIM | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor started digging to install fencing prior to 48 hour time frame.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LADWP | SAN PEDRO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | steel service 45s at the parkway crossing lots. SMC is in front of neighbors house. When locating, the locator followed our service up to the park way but kept going straight in line due to a near by waterline. the locator got up to our main and put paint on the ground.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2021-12-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LADWP | SAN PEDRO |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Homeowner stated that he hired laborers from Home Depot to clean out the backyard and they dug a hole and left. Homeowner got upset and threw digging bar. It landed in hole damaging gas service.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2021-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 65 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LADWP | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Allegedly, DWP damaged an unmarked service.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2021-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | LADWP | SAN PEDRO |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP was digging with a small excavator when they struck a gas service. Service had been previously damaged and was marked. LADWP failed to hand dig and exposeï¿½service prior to using excavator.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2021-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RMJ COMMUNICATION | SAN PEDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service damaged by contractor digging for a communication vault in parkway Service marked correctly
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2021-12-22 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | A L COMMUNICATIONS INC | NORTH HILLS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Water company damage gas service in the process of making repairs on water service.ï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2021-10-02 | Third party excavation damage | Riser | Polyethylene Pipe | Not Available | 0.75 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LANDSCAPE DEVELOPMENT INC | SANTA CLARITA | CA | N | Y | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Contractor excavated without a USA. Damaged the 1 inch Gas Stub while attempting to expose it.
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2021-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | STATE GREENS LANDSCAPE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no USA was called. Explained to contractor the importance of calling 811.ï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2021-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BRIAN BEDELL | CHINO |  | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 0.5 inch plasticï¿½serviceï¿½line when installing storm drain for house.ï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA FE SPRINGS | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CHAD DAVIS FIRE PROTECTION | HUNTINGTON BEACH | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Davis Fire Protection hit Gas main. Digging before legal start date on USA ticket
Southern California Gas Company | N | LOS ANGELES | SANTA FE SPRINGS | 2021-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ACCI | COMPTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party Contractor installing a gate and hit our gas line when they were driving the stakes in the ground.
Southern California Gas Company | N | LOS ANGELES | SANTA FE SPRINGS | 2021-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TECHNICO TV INC | BELLFLOWER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Technico construction was boring in a new line for Charter Communications when the bore unit hit a 0.75 steel stub with in the path of the bore.
Southern California Gas Company | N | LOS ANGELES | SANTA FE SPRINGS | 2021-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NORWALK LA MIRADA PLUMBING | NORWALK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber hit service line with shovel, No USA called in.
Southern California Gas Company | N | LOS ANGELES | SANTA FE SPRINGS | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | 2H CONSTRUCTION | SIGNAL HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Developer dug into 2 inch service with backhoe, did not expose correctly by hand. Marked correctly.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-08-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MASTER ROOTER PLUMBING INC | PARAMOUNT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FRED LAERAN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating for demo and damaged gas facility
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | RS ONE PLUMBING AND ROOTER | SANTA MONICA | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | digging to fix sewer
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JOSE MENDEZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to extend house worker hit 0.5 inch cts service with shovel. Gas service was marked correctly but contractors did not call for their own USA ticket
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | FORDS PLUMBING AND HEATING | CULVER CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 5 |  | SPY ROOTER | NEWBURY PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | AVANT ROOTER | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer did not call 811 to locate gas service before installing sewer line
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | THE ERWIN ESSIE APPEL TRUST | SANTA MONICA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On Arrival, crew spoke with contractor John Stakk. he stated that they caused damaged with backhoe while digging. They clamped and tapped service before arrival. He claimed Dig Alert incorrectly marked gas line on ticket A210060453. it was bare tracer wire causing bad connection so Employee created marks off of service history.ï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ROOTER MAN PLUMBING | SYLMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew was digging up to replace sewer for home owner, when crew struck service while hand digging. There was no USA
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-07-08 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COLICH SONS | GARDENA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party contractor was trenching to install new water main while trenching ended up hitting 0.75 inch abandoned 10 stub that wasnt on our maps or GIS records.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | IRISH CONSTRUCTION | ROSEMEAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JIMENEZ DEMOLATION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | K J PARTNERS CONSTRUCTION | CASTAIC | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching to install water line and used saw to cut into gas line thinking it was not a active line.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | K J PARTNERS CONSTRUCTION | CASTAIC | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching hit gas service where existing clamp was on steel service tightened clamp down.ï¿½crew was previously at this address two days prior and installed clamp.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | T T PLUMBING | LA VERNE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was removing underground pipe and thought the gas serviceï¿½was abandon.ï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALFREDO COYOTL | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching and hit plastic service line.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-02-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor came in contact with 3 inch PLA Main. Main was correctly marked within 24 inch, they dug up the steel line and marks on ground clearly stated inchPLA inch.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PROFESSONALS | GARDEN GROVE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer had no USA and should be billed
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JACK HALEY EXTERIOR | SANTA MONICA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR HIT PLASTIC SERVICE WHILE DIGGING WITHOUT USA
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | COLICH SONS | GARDENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | 24 7 EVENTS | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 247 Events was drilling rods into the ground directly over the 2 inch SVC STL without potholing and some drill points were outside of delineated area. Punctured Gas Line in 4 different points.ï¿½ ï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOHN WHITE PLUMBING ROOTER | CULVER CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Workers working to fix sewer line did not notify USA and while hand digging to expose sewer ended up hitting and damaging 0.50 inch ips service with shovel.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-02-18 | Third party excavation damage | Miscellaneous/Other | Steel | Backhoe/Trackhoe | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALEXANDER DEMOLITION | GARDENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor knew where main was and did not hand expose where stub was located.ï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RENUS BUILDERS INC | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was trenching for new utility install while trenching they hit 0.50 CTSï¿½with a clay spadeï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | COLICH AND SONS | GARDENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CHERLY RAISS | SANTA MONICA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While trenching for new sewer line, came in contact with PLA gas Service line.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MIKE PRLICH SONS INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MIKE PRLICH SONS INC | BALDWIN PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2021-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MIKE PRLICH SONS INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ALL USA marks were GOOD. contractor pulled cap off with excavator. Contractor did not hand expose service.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2021-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SHERMAN OAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Order was initially called in for indications by foundation.ï¿½ Upon further investigation and after excavation, found that the service had been damaged and was attempted to be repaired by tape wrap.ï¿½ Customer occupant denies any work was ever done on property.ï¿½ No valid USA or any information was given.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2021-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EMIL GHOOKASSIAN | SHERMAN OAKS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was installing bollards and hit service while hand diggingï¿½
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 11 |  | SINAI CONSTRUCTION | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While working on an earthquake building retrofit, contractor hit 0.5 inch IPS service while hand digging. Valid USA on file with clear correct marking.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2021-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HC BUILDERS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew hit 0.75 inch steel service while excavating without a USA, would not give any info regarding names or phone numbers. Sent out damage prevention Juan Garcia Lopez 818 269 6760
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2021-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SHERMAN OAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was trenching to pour foundation and sliced into out 1 2 plastic service No USA was called in gas was not blowing due to existing EFV Service was repaired with a plastic coupling
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2021-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SHERMAN OAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Initially order was called for gas indication by foundation.ï¿½ Upon arrival and investigation, plastic service was damaged while home owner installed new sewer clean out.ï¿½ Plastic service was clamped by ownercontractor but still leaking.ï¿½No USA ticket.ï¿½ Crews replaced riser and made permanent repairs.ï¿½
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2021-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | GOR MNATSAKANYAN | SHERMAN OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KIMBERLY HICKS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractors were digging to install electric conduit and hit our service No USA and permanent repairs were made
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2021-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GOED COSTRUCTION | SUNLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | While building new house, 3rd party contractor failed to wait for abandonment before excavating. USA ticket expired.
Southern California Gas Company | N | LOS ANGELES | SIERRA MADRE | 2021-05-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BIG BEN CONSTRUCTION | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Serivce was not located and contractor hit the service line with a backhoe.
Southern California Gas Company | N | LOS ANGELES | SIERRA MADRE | 2021-01-13 | Operator excavation damage | Main | Steel | Miscellaneous/Other | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 8 |  | NPL | NA |  | Y | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | NPL contractor for gas company was out doing paving repairs for one of our cuts in the streets. While grinding asphalt to prep the area for paving repair, Grinder struck and pulled off a SVC Tee. Top of the tee was roughly 8 inch deep. extremely shallow main will be put in for replacement.
Southern California Gas Company | N | LOS ANGELES | SIERRA MADRE | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | DOUMIT COMMUNICATIONS INC | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor exposed a pipe and assumed it was our gas line and began the work, then hit our line while boring.
Southern California Gas Company | N | LOS ANGELES | SOUTH EL MONTE | 2021-04-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MAYANS DEVELOPMENT | YORBA LINDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer hit and damaged 1 inch plastic gas service while digging to install drainage line ...No USA called in.
Southern California Gas Company | N | LOS ANGELES | SOUTH EL MONTE | 2021-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ABARCA LANDSCAPING | HEMET | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping company installing Drainageï¿½line had no USA and damaged 1 inch PE gas Service with mini excavator bucket, no pothole
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | HECTOR CONTRERAS | DOWNEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer should be billed for this due to no USA and damaging service with shovel
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2021-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ANTHONY GRECO | SAN MARINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | owner and contractor was using a jack hammer to do work and hit our plastic service.ï¿½
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2021-11-30 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | QUALITY JET ROOTER | WHITTIER |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck gas service with asphalt while widening core hole.ï¿½
Southern California Gas Company | N | LOS ANGELES | SOUTHGATE | 2021-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | NA | SOUTHGATE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | crew did corp cock on 2in steel main. main was marked for large water replacement job. marks at address were faint but other marks down the street were visible and main had been potholed many times along the same block. crew did not properly hand expose before using back hoe.ï¿½
Southern California Gas Company | N | LOS ANGELES | STEVENSON RANCH | 2021-03-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NORRIS CONSTRUCTION | LITTLEROCK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Damaged service from trencher. Did not hand expose facility.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ERIC CASTELBLANCO | STUDIO CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While customer was using a mason drill to install a fence, they hit the gas service.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2021-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CUSTOM BUILT CONSTRUCTION | WEST COVINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was trenching along side our steel 3 4 inche service As the service was being moved around it caused the corroded section of the steel service to corrode Had to alter the service from PL to meter by inserting cts Permanent repairs completed by crew same day
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2021-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BUILT IN 72 INC | CALABASAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service with a Back Hoe.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | AMID KHALIF PLUMBING | STUDIO CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic service with small excavator while digging for sewer
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2021-10-21 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | TROUTWINE PLUMBING | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor struck 2 inch steel main with accupunch while installing new water service.ï¿½
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2021-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | ARG BUILDERS INC | LOS ANGELES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | After an investigation, it has been determined by admittance from the builder Frank Cao, he had his guys abandon our ï¿½? CTS service inserted in 1? steel. He told me over the phone his guys abandoned the service near the property line. There was an old spa sitting over the cut, which the on call crew could not see. After Frank?s workers showed up and moved the spa this morning, we dug it up and found the 1? steel threaded with a cap and taped up. The plastic service inside was blowing through the casing towards the street.ï¿½ SCG cut back the service correctly at PL.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2021-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALBINO CONSTRUCTION | STUDIO CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Fire sprinkler company was at hotel locating their water line and probed through our one inch gas line.ï¿½
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2021-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALBINO CONSTRUCTION | LOS ANGELES |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with a mini excavator and they caught the cap with the bucket and damaged the service.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2021-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT, Raynaldo Rodriguez Homeowner was digging a trench in preparation for SCG to install a new service line.ï¿½ In doing so, the homeowner hit the current SCG service line with hand tools. House is vacant while it is being remodeled with no gas meter.ï¿½ Meter was removed but service was not abandoned.ï¿½
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALL ABOUT LANDSCAPE | TARZANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While grading new property, contractor hit 0.5 inch IPS service. No valid USA
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2021-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MCR CONSTRUCTION | BURBANK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractorï¿½ was fixing the the concrete patio and damaged the service it was in the concreteï¿½
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AMIR COHEN | NA |  | N | Y | Yes | No | No | Yes | No | Yes | Yes | Builder cut into riser causing damage. USA on file is expired. SCG crew cut back service.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2021-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SUN VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA was not notified
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | UNITED ENGENNERING | SUN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | did not notify USA
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SHIRLEY EGYED | SUN VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit 1 2 plastic service with shovel SoCalGas Crew made repairs
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 13 |  | TECHNICO | BELLFLOWER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | A 3rd Party contractor hit a 2 inch plastic service with a backhoe while trenching to install telecommunications. USA ticket was current. The service was not marked.ï¿½
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2021-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PETRELLI ELECTRIC CO | SANTA CLARITA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit plastic service that was not marked out
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2021-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GEVORK KHACHATRYAN | SUNLAND |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit servc. Contractor hand digging hit plastic servc.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CARLOS FERNANDEZ | CANYON COUNTRY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ï¿½
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | REDKORP | CALABASAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging around footing of raised foundation and struck our 0.75 inch steel. There were USA markings but the concrete slab the marks were made on was demolished The contractor clamped the pipe and it was not leaking when I arrived on scene.
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2021-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TARON GHUKASYAN | SUNLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Municipality was not careful while digging with a shovel over plastic gas service.
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2021-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HOME OWNER | SUNLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home Owner Hit Line while hand digging in private property..
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2021-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MM C CONSTRUCTION | SUNLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor homeowner didn t call USA and took a grinder to our plastic gas line that was in casing to cut out of the way of the new footing location
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2021-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ROOTER GUARD PLUMBING SERVICES | VAN NUYS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor hit main w backhoe while excavating the EOM for Company contractor to install new main to new housing development.ï¿½
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2021-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CHRIS MEHRABIAN | SUNLAND |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged PLA service while hand digging.ï¿½
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COMMERCIAL PAVING AND COATING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged riser with paving machinery. No USA ticket.ï¿½
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2021-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ORTIZ BUILDERS INC | BELLFLOWER |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing a fence and while digging pole holes they hit our service.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2021-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 16 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GOLDEN LEGACY CARE CENTER | SYLMAR | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | While hand digging contractor hit plastic service. Per LCT notes no valid USA but visible old marks.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | AMERICAN QUALITY PAVEMENT | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Contractor hit 1 IPS plastic service while excavating for new handicap ramp No Police or Fire dept on scene by the time Gas Ops arrived
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2021-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ANTONIO HERNANDEZ | SYLMAR |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner performing weatherproofing on home with a hired hand, damaged service line while digging around home
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2021-02-17 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KAMS GENERAL CONSTRUCTION INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors were grading in the alley with a bobcat loader and struck the riser and service valve came off. LAFD arrived and controlled gas by plugging with redwood.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2021-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ACE TREE SERVICE | SAN FERNANDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Repair fence and failed to call 811 and hit line with jackhammer digging for a fence post.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SYLMAR | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit plastic 1 2 IPS service while digging with backhoe for retaining wall Customer had invalid USA digging was done prior to 48 HRs ticket
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2021-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DAVID CONTRACTOR | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Damage. Excavation caved in and damaged plastic service.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2021-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DWP | NA |  | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | contractor grading driveway and hit riser
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | TARZANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner was digging with excavator in property to install new water lines.ï¿½ Operator damaged our 0.5 cts platic while digging.ï¿½ No valid USA ticket was called in.ï¿½
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2021-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LIGHTNING CONSTRUCTION DESIGN INC | TARZANA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | "Contractor damaged service
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2021-07-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 30 |  | EDWIN PORTILLO OPERATOR | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging for sewer and they damage 2 main with backhoe No USA called in
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2021-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TURN KEY CONSTRUCTION AND DESIGN INC | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging with a trencher when they hit are 0.5 inch ips service. No USA called in
Southern California Gas Company | N | LOS ANGELES | TEMPLE CITY | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HTX HOMES | TEMPLE CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Large excavator was used toï¿½demo and contractorï¿½hit service. Service was supposed to be abandoned by NPL before demo.
Southern California Gas Company | N | LOS ANGELES | TEMPLE CITY | 2021-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOMINGUEZ GENERAL CONTRACTOR | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Damaged PE service while excavating within 2 of visible marks
Southern California Gas Company | N | LOS ANGELES | TEMPLE CITY | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JAMES THU LIEU | TEMPLE CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner and contractor failed to notify 811 to locate and mark gas line prior to diggingï¿½
Southern California Gas Company | N | LOS ANGELES | TEMPLE CITY | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | TEMPLE CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no USA was requested customer trying to repair a drain
Southern California Gas Company | N | LOS ANGELES | TEMPLE CITY | 2021-11-08 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | FODDRILL CONSTRUCTION CORP | CHINO |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Gothic Landscape Hit Service while installing irrigation. Contractor was working with expired USA.ï¿½
Southern California Gas Company | N | LOS ANGELES | TEMPLE CITY | 2021-01-09 | Third party excavation damage | Riser | Polyethylene Pipe | Not Available | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARPI CONSTRUCTION | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor setting the walls to pour a concrete driveway, they hammered in a stick of rebar and hit our plastic service
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-09-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WILCOX WILCOX | CANOGA PARK | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Wilcox and Wilcox was machine excavating a trench to install conduit for street lighting when they struck our known marked 2 PE gas main USA ticket they provided was expired
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DESIGN MASONARY | CANYON COUNTRY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | USA was called it was a cut back stub with no history SMC had a dresser so there was no way to locate it Main was accurately located along with all other mains going into the property
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | TORRANCE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage by Third Party Contractor.ï¿½ 0.5 inch plastic service was hit with a Commercial grader, while digging trench for a new service.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SPECTRUM INVESTMENT DEVELOPMENT INC | ARCADIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with shovel for new sewer hit the gas service.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LOU BOBCAT WORKS | WOODLAND HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | DWP was working to install new water service after the water main installation when they hit for the second time a 0.5 inch cts service to 112 w 81st street. I arrived on site and spoke with crew due to marks from first incident not updated the DWP crew is claiming mis marks so I had LCT Huerta update the marks as how service should be marked out this service snakes from PL to SMC at an angle.ï¿½
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FINDLEY SOUTH BAY | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No current USA on file. Customer submitted for USA ticket after incident. Customer was removing gravel and adding cement and digging to install ballards. They hit our line when digging for the ballards.ï¿½
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FUJIMOTO LANDSCAPING | HARBOR CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor hit 0.5 inch plastic service while digging to install irrigation.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 0 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | AIRCRUSH | SIGNAL HILL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR HIT GAS SERVICEï¿½
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-06-15 | Third party excavation damage | Main | Steel | Augur | 2 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  | 1 |  | EDISON | TORRANCE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Edison was using an auger to dig down for a power pole in the parkway. There was flags right next to where they were digging and marks on the asphalt about 20 feet away, clearly indicating that our gas line ran right where they were digging. They augered down 4 feet and hit our 2 inch steel gas line.ï¿½
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | JACKBUILT | TORRANCE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Line was located but the USA ticket has been expired since March. Fail to upkeep marks, fail to refresh ticket, also ripped out warning mesh covering our pipe.ï¿½
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SABER | TEMECULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Foundation Restoration company had holes excavated all along the house Did not have a USA ticket Dropped a large L Bracket into one of the holes and hit our plastic line that was slightly beneath the dirt
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MANUEL VAZQUEZ GENERAL PLUMBING | LOS ANGELES | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Developer was trenching with shove across our gas line, severed 0.5 cts line.ï¿½
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-10-27 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | ANDREW PRIZLER | TORRANCE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCG employee damaged a plastic service while running down the pogo to take underground samples.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BOGART CONSTRUCTION | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1 inch service installed in a poor location. Historically the area was a nursery, but was later converted and paved over. Building was moved which caused the poor meter location and service not located for project.ï¿½
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GOLDEN STATE BUILDERS | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors directional boring to install conduit.ï¿½
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2021-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | JSL FIRE SPRINKLER SERVICES | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While 3rd party was excavating to replace fire sprinkler, damaged gas line service
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2021-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ARMAN KHACHATRYAN | TUJUNGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Part Contractor was digging a septic pit with Bobcat when struck our facility.
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2021-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RAYMOND ROJAS | SYLMAR |  | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 2 inch plastic gas main, crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2021-09-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DUTTON PLUMBING | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing contractor hit service with a shovel while hand digging to repair the water line No USA was called in
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2021-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | TUJUNGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit 1 2 plastic service with grader while grading toï¿½ pour concrete for driveway No USA called
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | V10 CONSTRUCTION | LA CRESCENTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Sheared AL riser while using an excavator to demo lot No USA
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2021-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 4 |  | PETRELLI ELECTRIC INC | SANTA CLARITA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Petrelli Electric was working for DWP replacing wood power pole. they had USA but only updated ticketï¿½did not do remarks.
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2021-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | PNR BUILDERS INC | WOODLAND HILLS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor, Teichert, began digging in sidewalk for new service installation to, 719 Isabel St, when they hit 0.5inch Plastic service to, 715 Isabel St.ï¿½ hit service was found cross lotting and marked as such.ï¿½ Teichert crew hit line with shovel while hand digging.ï¿½ Company crew completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2021-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EXCEL PAVING CO | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO USE CAUTION WHILE EXPOSING GAS LINE, CONTRACTOR DIGGING FOR ELECTRICAL WIRING
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2021-07-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | INTERTEX GENERA CONTRACTORS | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to call USA and hit service EFV activated
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2021-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DREAM TEAM CONSTRUCTION | ENCINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party called in gas damage at this address Upon arrival no one on site no heavy machinery onsite but visible track marks Damaged area looked to be partially backfilled according to Crew No visible marks for USA No active USA ticket found Crew exposed leaking PE pipe squeezed It was determined the pipe damaged is an inactive stub standard that also supplies branch service Standard has no riser Crew retested disconnected pipe held up pressure test and made repairs to reinstate Attempts to reach property owner via realty company sign on the property were unsuccessful listing agent refused to release info Reached out to SCG Land Right of Way Dept received property owner info however listed number is for PO Box company Notified planning to plan for Branch Convert to Standard and abandon inactive standard service in empty lot
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2021-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | LADWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DWP damaged a mismarked encased plastic service while trenching for watermain. Mark was off by more than 2 ft. The marked location was on an abandoned steel gas service.ï¿½
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | VALLEY VILLAGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Building a house damaged service with wooden stake will bracing form
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | VALLEY VILLAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner used day laborersï¿½to dig long trench to back of house for sewer work. Workers hit 0.5 inchcts service. No USA on file
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2021-04-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 9 |  | NA | VALLEY VILLAGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While trying to pull out a tree stump w a miniexcavator, homeowner broke 2 inch Aldylay Main, no valid USA
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DWP called in emergency ticket for main replacement and locator made attempt to mark ahead of DWP. Locator placed marks down for 0.5 inch Plastic serviceï¿½ Line, DWP uncovered a Steel line at the marks and assumed the utility was encased in steel. DWP resumed digging and hit the actual line more than 24 inch away from marks. We advised them to contact SCG when there is a discrepancy in material type so we can verify marks.
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GOLDEN STATE BORING PIPE JACKING INC | CHINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Golden State Boring Company, performing direction boring for Advanced Geo Solutions whom was contracted by WA Rasic the general contractor to DWP. Golden State Boring damaged an unmarked, unknown 0.75 steel stub service which is inactive and not in use. Drilling operations seized while crew mitigated the leak confirmed service not in use and performed a cut back alteration. Unable to access main at the time of damage due to K Rails of ongoing project are over the gas main.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARAM AKPPYAN | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was excavating in order to remove a tree stump, without a USA.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | HAYK HAYKYAN | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner Hayk Haykyan struck SCG service line with tunnel bar while digging holes to install fence No USA was called in Permanent repairs made to plastic service
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to fix sprinklers HO hit 0.5 inch CTS service w a shovel
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SOROUSH ARANI | NA |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor drove stack into ground to create barrier to pour concrete for curb and gutter The stake was driven into the 2 inch plastic service No valid usa
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MOHAMED MOSSAMI | VAN NUYS |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party locator struck 0.5 inch svc line while probing for septic tank. No USA called by contractor. SCG crew arrived and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 5 |  | LA DWP | NORTHRIDGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DWP trenching for new Water Main, working from west to east. During the process DWP damaged an existing gas service at this property which is the standard service for several addresses. Gas serviceï¿½ marks for this property was on the east side of the property on the east driveway which coincides with GIS mapping. However actual service runs thru the west driveway of the property.ï¿½
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ROGA PARRA | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor cut through 3 4 steel casing hitting 1 2 CTS Thinking it was copper water line No USA called in
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CALL FOR CONSTRUCTION INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was trenching to install new water line for ADU.ï¿½ Contractor damaged our service while digging damage our plastic service.ï¿½ They had current USA ticket and facilities were correctly located and marked with yellow paint.ï¿½ Contractor failed to excavate with caution damaging our service.ï¿½
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | STEVEN CASTLEBLOCK | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | third party contractor hit gas line while hand digging No USA
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | OSBALDO ROJAS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging in private property to pour foundation.ï¿½ They hit copper casing with a shovel pinching the plastic 0.5 inch service inside.ï¿½ Company crew arrived and made repairs.ï¿½ No USA was called in.ï¿½ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | VAN NUYS | CA | N | N | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Contractor performing site work including house demo struck steel gas service with excavator when attempting to demo a wall Refused to provide information as they are working for the homeowner No USA was called No Marks Present Crew Cold Pinched service to stop flow of gas and eliminated that squeeze via hot squeeze Cutback service due to demo and safety Meter picked up by customer service
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CONTRACTOR | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR HIT SERVICE While excavating. No USA was called.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-02-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | IRISH CONSTRUCTION | ROSEMEAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While digging trench to install telephoneï¿½conduits for ATandT, Irish Construction hit marked 2 inch PA main w backhoe. Contractor had a valid USA but did not potholeexpose our marked facility first.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inch pla service while hand digging a trench during construction of new house.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NATHANIEL SROR | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating, contractor hit gas service line.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SAND LOT HOMESE | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 inch plastic main was hit by DWP.ï¿½ They were excavating with backhoe to repair water main leak.ï¿½ They hit gas main with backhoe.ï¿½ No valid USA ticket was called.ï¿½ only 3 outages.ï¿½ No street closure, no fire or police dpt.ï¿½ Crews made permanent repairs with 2 couplings and a new 4 feet pipe.ï¿½
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | CAL EMPIRE ENGINEERING INC | COVINA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third Party contractor damaged unmarked PA gas service. Service was not marked due to incorrect records and facility maps.ï¿½
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor was digging with no valid USA
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NEXT GENERATION BUILDERS | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was marked correctly, contractor hand dug as required and found a 0.75 inch line on the mark but it wasn feett ours. Our service was approx. 18 inch away which was struck w a mini excavator.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cust was digging in own yard removing tree roots.ï¿½ damaged our 0.75 inch steel service.ï¿½ Repair was made with 0.75 x 6 inch adams clamp.ï¿½ No USA was called
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | H O hit service with shovel while trenching to repair sewer lat No USA ETR evacuated and called LACFD Crew dug control hole and altered service ~K Rodriguez~
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-09-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DELTA FIRE PROTECTION AND EQUIPMENT | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Delta states they had Gas Line Exposed was aware of our utility installed at this location based on existing marks left by installation crew They claim during the process of trenching a piece of concrete fell back into the trench and severed the line No Active USA on file for Delta Fire Protection and Equipment EFV Tripped and minimized gas being released Crew made repairs authorized by Supervision to perform immediate cutback alteration and cap the service There is an issue with Fireline Running line location D Ticket to follow suit for service line extension
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2021-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MANUEL AYALA | PACOIMA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching with backhoe to install new sewer line.ï¿½ Hit 0.5 cts plastic service incased in copper with backhoe.ï¿½ Service was cut and capped at point of damage due to house being remodeled and vacant.ï¿½ No valid USA.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2021-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VALUE CONSTRUCTION ZONE | SHERMAN OAKS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 0.5 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2021-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP Hit Gas Line While Exposing Line, LADWP Was Repairing A Water Leak
Southern California Gas Company | N | LOS ANGELES | VENICE | 2021-05-14 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DWP called in an emergency ticket on 5 14 2021. DWP started probing, prior to the gas main being located and marked, investigating where the water leak was coming. They called approximately 45 minutes later to inform the Gas Company they have hit the gas facility in the street.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | S P BEAGLE | HERMOSA BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor damaged a 0.5 inch ips cutback crew abnd at smc
Southern California Gas Company | N | LOS ANGELES | VENICE | 2021-10-08 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 20 |  | LADWP WESTERN DISTRICT | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor dug on an expired DIG Alerrt and failed to pot hole 1 inchP gas stub before damaging it with a skid steer mounted auger.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2021-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JERSON VELAZQUEZ | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic service while installing a fernce post
Southern California Gas Company | N | LOS ANGELES | VENICE | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TOP YOU LLC | VENICE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating for drain line, Paez Tech came in contact with Service line .
Southern California Gas Company | N | LOS ANGELES | VENICE | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | STEINER CONTRACTORS | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to install fence hit 0.5 inch CTS Rider, pipe. Contractor bent pipe back.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2021-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EXPRESS PLUMBING AND REMODELING | WOODLAND HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for new drainage for home owner, Knicked 0.5 inch cts service with shovel.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2021-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | TOMOVICH AMP ASSOCIATES | PICO RIVERA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The homeowner had her friend helping install an electrical conduit without a USA ticket. during excavation they damaged our 0.5 inch pla service.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2021-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MATTHEW STEWARAT CO | SIGNAL HILL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Crew was working on replacing sewer lines to homes, When contractor struck and damaged 0.5 inch cts service with backhoe. Contractor dug outside delineation area.
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | Y | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | WALNUT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer was digging with a electric clayï¿½spade with no USA, developer said once they damaged our pipe the gas ignited and his employee got burned on his arm. He was transported to the hospital with minor burns.ï¿½
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2021-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JOHN CITI | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service was not located and was damaged by bobcat while grading. Contractor had valid USA.
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | WALNUT | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | lancaping
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2021-08-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | R R PROS | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit unmarked 1 2 plastic service while breaking concrete out around post to remove fence Company crew advised contractor to always call Underground Service Alert 811 before digging even if on private property
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2021-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HHS CONSTRUCTION ANDREW GONZALEZ | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Installing Cable Conduits Spectrum
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2021-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | REHABAND CONSTRUCTION | DOWNEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Crew explain to the contractor that he can not just move our lines it is not safe for him or the public for him to do such thing to our lines
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ROD PAZ BRO INC | WEST COVINA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit service with splitter will pulling pipe to replace water service. 3rd party contractor did not have ticket andï¿½ was working off ticket from suburban water.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2021-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 100001 |  | 1 |  | E R CONSTRUCTION INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor was digging a hole with a backhoe and damaged a 0.75 inch steel gas line.
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2021-09-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 31 |  | E R CONSTRUCTION INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor should be billed for incident
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | JAVIER TORRES | WEST COVINA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contract was demolishing the building on the property before the gas service was abandoned. The service was marked from another USA ticket but they did not have a current USA.ï¿½
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2021-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | WEST COVINA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant of the house was digging to repair the sewer and hit our line
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2021-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MURGUIA CONSTRUCTION INC | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Ready for approval
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2021-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 8 |  | DM G CONSTRUCTION ENGINEERING SERVICES | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was installing guard post for our company
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2021-09-13 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 8 |  | AMS CONSTRUCTION | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Review is complete
Southern California Gas Company | N | LOS ANGELES | WEST HILLS | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AKM FIRE INC | TARZANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | excavator failed to pot hole prior to trenching
Southern California Gas Company | N | LOS ANGELES | WEST HILLS | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | POWER ELECTRIC | LOS ANGELES | CA | N | Y | Yes | No | No | Yes | No | Yes | No | 3rd party damage 1 2 service while hand digging expired USA
Southern California Gas Company | N | LOS ANGELES | WEST HILLS | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NORTHWEST EXCAVATING | NORTHRIDGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While hand digging for Cable TV 3rd party contractor hit 0.5 inch service
Southern California Gas Company | N | LOS ANGELES | WEST HILLS | 2021-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FLAMINGO CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer digging for sewer and no USA was called in.
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2021-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 9 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Unmarked SL damaged by DWP while trenching
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2021-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TOMOVICH ASSOC | PICO RIVERA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was trenching and installing sewer when they damaged mismarkedï¿½0.5 feet feet plastic SL. LCT on scene located two signals from riser. One signal located out to where damage occurred and the other signal located out to where marks were placed on ground by locator
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2021-03-22 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | SOCALGAS | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TOMOVICH ASSOCIATES | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor did not pothole, prior to excavation. Contractor while excavating damaged 0.5 inch CTS service.ï¿½
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MATTHEW AND STEWART CO MASCO | SIGNAL HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator hit line 4 feet feet from marks on ground
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2021-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PRO CRAFT CONSTRUCTION | REDLANDS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 inch pla service with backhoe while installing electrical conduit
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OHS | WEST HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party crew hit 0.5 inch CTS PLA service while trenching crew. Crew did not have USA.
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2021-04-02 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | UNDERGROUND SOLUTIONS | SIMI VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While boring in a 2 feet feet telecommunication line, contractor damaged our 2 feet feet steel main
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DOMAIN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging footing for addition to home and damaged SL. No USA called in for this job
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2021-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HIGHROUND SOLUTIONS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Worker for contractor removing roots cut into 3 4 steal service with sawzall Claims he hit service with shovel No USA called in for this location
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2021-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | DWP | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Area marked correctly, Contractor severed service while digging around marks
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2021-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MARINA LANDSCAPING | WEST HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged SL while digging to install water service. Gas line was marked correctly
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2021-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | KAREN GOLD | WEST HOLLYWOOD |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner damaged 0.5 inch service while digging footing for retaining wallï¿½
Southern California Gas Company | N | LOS ANGELES | WESTLAKE VILLAGE | 2021-09-30 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | M TCK COMMUNICATION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | MTec was preforming work with spectrum when they bored through a SCG 2 inch PLA main. MTEC was working with out a USA ticket.
Southern California Gas Company | N | LOS ANGELES | WESTLAKE VILLAGE | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CONEJO VALLEY PLUMBING | THOUSAND OAKS | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party Contractor was replacing sewer line for home owner. While digging,ï¿½they hit the 0.5 CTS gas service.
Southern California Gas Company | N | LOS ANGELES | WESTLAKE VILLAGE | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CALIFORNIA PROFESSIONAL ENGINEERING | ROWLAND HEIGHTS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | they were hand shoveling to create a trench for a new service and damaged the service to the house next storeï¿½ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | WHITTIER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | plumber digging for sewer, hit gas service. NO USA called in
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | TE ROBERTS INCORPORATED | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working on home for sewer upgrad, hit plastic service with shovel. No USA was called, no location of substructures located.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NO BEST INC | GARDEN GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | grading company hit svc line with backhoe, marks visible, failed to expose by hand.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MR GIUSEPPE | WHITTIER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCG contractor was using post hole digger to excavate for a meter bollard and he clipped a plastic service causing a small leak.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | R J NOBLE | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While grading the street the grader came into contact with our service running long side
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-03-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CAL WEST LANDSCAPING | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While using an excavator to dig for drainage, the operatorï¿½dug intoï¿½our 2 inch PE main. USA was not called and no markings were present at scene of damage.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-07-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SAFEWAY ELECTRIC | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging for Edison a back hoe operator hit a 2 inch PE main
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-08-24 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Grader/Scraper | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | EXPRESS PLUMING CO | WHITTIER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing Co. Hit 2 Inch Pla Main With Mini Excavator. No USA Called In
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-06-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SAFEWAY ELECTRIC | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While the contactor was digging to install anï¿½Edison line, the operator of theï¿½back hoe digging hit our 2inch PE main. No USA was called
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-03-02 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 21 |  | EDISON | SANTA FE SPRINGS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Edison was auguring for a new Edison pole when they came into contact with our 2 inch PE main.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SPIRIT GENERAL CONTRACTING | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Developer hit 2 inch steel service while demolishing building and concrete. Service clearly marked.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PHILLIPE QUIROZ | WHITTIER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner sliced the 1 2 cts service in half with a hand shovel while working on his sewer lateral
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ART MORRENTES | WHITTIER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner damaged plastic service while digging up sewer line, NO usa called in
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | I RAMIREZ | SAN FERNANDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While the contactor was using power tools to dig through hard dirt to install Edison, he severed a 0.5 CTS plastic service stub. Other USA feets present and marks for the gas were visible but the contractor did not hand dig service before using power tools.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CITY OF WHITTIER WATER DEPARTMENT | WHITTIER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors where digging for the water company when they hit our buried gas line that was clearly marked.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NO BEST INC | GARDEN GROVE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor doing work for City, hit 1 inch PLA svc while grading for new curb and gutter. SVC was mis marked.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-02-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BUCCOLA LANDSCAPE SERVICE | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no USA was requested, customer digging for drainage
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-09-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MONTEBELLO SPRINGS LANDSCAPE CONSTRUCTION | JURUPA VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging out the drive way approach for a new tract home project the contractors back hoe hit our 2 PE main No USA was called and main had been exposed with in same excavation as damage Failure to secure in place
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-07-30 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MCKINNEY CONSTRUCTION | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While installing a new water main the operator of the backhoe hit an A B nipple on the 2 main
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CLEAN OUT PLUMBING AND ROOTER | LA HABRA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. party contractor hit gas line while digging for sewer. USA was Valid
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | ROBERT BRKICH | MONROVIA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party damaged , Company crew arrived and controlled the gas leak .No USA
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | K STAR VINYL FENCING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit a 1 2 service while using posthole diggers to install a new fence
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2021-05-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | 2020 CONTRUCTION | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Backhoe Operator Damaged Plastic Main Without USA Ticket.
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2021-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CARLOS GIL | WILMINGTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut the service line and tied it off to perform grading and other work Customer Service received no usage order and when they arrived to the address found the meter and riser cut off House line was relocated as well as if they wanted an alteration With no planning or houseline clearance gave order to cap pipe and informed customer to contact planning services to get alter paid for and scheduled Could not put riser back to where it used to be
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JUAN GARCIA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was excavating for a footing for a room addition when they hit the service with a shovel. USA had not been called.ï¿½
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | WILMINGTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant hit service line with jackhammer
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DYNA ELECTRIC | LOS ALAMITOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | No USA, hit service with jackhammer
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2021-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | OHL NORTH AMERICA | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Water company hit unknown stub while excavating trench. Company crew abandoned service at SMC after verifying that it was not tied to any service. Service was not marked due to being an unknown stub.
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2021-09-26 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 0.75 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | OLSONS ROOTER | BURBANK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor was trenching to install gas water and electric lines As they were cutting into tree roots they cut into our 3 4 steel service Permanent repairs were made by on call crew
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2021-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | WINNETKA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner struck service while digging for water with no USA
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2021-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TRAN VAN TAI | WINNETKA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cust was digging holes to plant trees and hit our service.ï¿½ No USA called.
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2021-12-02 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | REMODELING EMPIRE INC | BELL |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was hand digging to install footing for staircase. They did not call USA.ï¿½
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2021-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL RETROFIT | RESEDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating trenching to install power conduit in the street. He hit our 0.5 ips line with a clayspade.ï¿½
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2021-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | WOODLAND HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging in their yard landscaping and hit our service with shovel to branch service.ï¿½ No USA ticket.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2021-06-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | BOUCHARD COMMUNICATIONS | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor found old steel line but failed to dig the two feet around. Struck 1 inch service with excavator.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | WOODLAND HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner cut thru a 0.75 inch steel line. No USA was called in
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2021-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SHARP LINE PLUMBING CO | WOODLAND HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.75 inch steel service was cut with a saw when 3rd party contractor was cutting sewer lateral for replacement. Contractor stated that gas line was marked in the middle of his excavation on concrete they removed which would have put marks for service at acceptable distance. Distribution crew had to don fresh air equipment to safely control gas at contractors excavation. fire and police department on site, 2 structures evacuated, streets closed for safely.ï¿½
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2021-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HOMEMADE CUSTOM BUILDERS | ENCINO | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. party damage 0.5 feet CTS with backhoe. USA ticket was expired
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2021-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HOMEMADE CUSTOM BUILDERS | ENCINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Second time they Hit SVC with no USA
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2021-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | WOODLAND HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner digging for drain pipes
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2021-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | STEVEN BALDONO | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor digging with No USA and cut thru 0.75 steel line
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 39 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | INFINITY FENCE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor hit 0.5 inch CTS , No USA Called in
Southern California Gas Company | N | ORANGE | ALISO VIEJO | 2021-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PLUMBING BROTHER S AND ROOTER SERVICE | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Occupant hired a third party contractor to install a new sewer lateral for adu to be added at rear of house. No USA called and during hand excavating they damaged the PE gas service. Occupant was unable to provide contractor info and was informed about dig alert. Occupant made aware of being billed for damage if no contractor info provided. Crew altered service for repair.ï¿½
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-03-31 | Third party excavation damage | Main | Steel | Boring Equipment | 3 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | CABLETECH | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to install cable conduit bored through main. line was marked correctly. contractor failed to maintain distance.ï¿½
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HSU MANAGEMENT | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1 2 pla service while hand digging with shovel contractor had USA and location was marked correctly
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-05-18 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TEICHERT PIPELINES | CHINO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck 0.5 plastic service while potholing for electrical line
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-06-28 | Operator excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PUI | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor probed through 2 inch PE Main stub while trying to locate main.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-01-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | ANAHEIM PUBLIC UTILITIES WATER DEPARTMENT | ANAHEIM | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Anaheim public works was excavating to replace their water service.ï¿½ USA ticket was called in, however they started digging prior to the valid start date.ï¿½ The public works department struck the 2 inch PE main with a back hoe.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-08-25 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | MORAS EQUIPMENT AND CONSTRUCTION | PICO RIVERA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator trenching without first fully hand exposing nearby existing main
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-12-19 | Third party excavation damage | Not Available | Material not known | Not Available | 0 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors were instructed to call locator is unable to find service line due to poor connectivity and no ground wire. Locator went off service history footage and marked service line 3 feet off.ï¿½ Line struck by Backhoe bucket.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BLACK BIRD | GARDEN GROVE |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | excavating to install Edison power pole
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RANCHO PACIFIC ELECTRIC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck service while excavating to install telecommunications.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GPI | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 inch Plastic service was hit with the trencher while trenching for lighting.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GENTRY GENERAL ENGINERRING | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hired by the city of anaheim struck 0.5 inch plastic service. Dug directly over marks thinking service line was deeper than expected. Poor excavation practices. Coached contractor on USA law and proper digging techniques to safely dig around all marked substructures.ï¿½
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 3 |  | NA | YORBA LINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Property owner hired contractor to excavate for new sewer installation. Contractor had pipe exposed right in the middle on the trench and struck 0.5 inch ips tr418 pipe with shovel. Spoke with property owner on proper digging techniques and practices. Gas service was marked correctly and exposed prior to striking. Upon speaking to residents Iï¿½come to find out this is the second time this gas service was struck within the same week. Verified with on call supervisor at the time, Patrick Young. Spokeï¿½with property owner on his negligence to prevent gas damage and dig safely.ï¿½Expressed the major consequences of hitting theï¿½gas line again and the little room for error he now has with this being the second damage within the week.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CABLECOM LLC | ANAHEIM |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | none
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARIJET COMMUNICATIONS | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while digging by hand.ï¿½ Marks were correct.ï¿½ï¿½
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-07-01 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NPL CONSTRUCTION | BREA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NPL damaged 1 2 plastic service that was to be abandoned NPL located the service Service was abandoned and replaced that same day
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-01-12 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 30 |  | SNS DIRECTIONAL DRILLING | NORCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | per ticket and 3 locators who were called to site the intersection was not originally requested to be located. No delineation found except for fresh mark right at damage location. Claims will investigate.ï¿½
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-06-07 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NPL CONSTRUCTION | MIRA LOMA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck 0.5 plastic service with shovel.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 46 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | STREAMLINE PLUMBING | GARDEN GROVE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber boring new water service struck 0.5 plastic service under homeowner drivewayï¿½
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LINCOLN CONTRACTORS | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit buried facilities while exposing it by hand digging.ï¿½ Contractor gave supplied USA number A210320447 however, this does not seem to be a valid ticket number.ï¿½ï¿½
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-08-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | OB SEWER AND SEPTIC | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | developer digging without USA ticket struck our gas line with a backhoe
Southern California Gas Company | N | ORANGE | ANAHEIM | 2021-01-05 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 44 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RBT ELECTRIC | PLACENTIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A contractorï¿½relocating aï¿½water line hit our gas line while digging without USA, the EFV lowered the pressure enough for the contractor to put a PVC cap on the damaged pipe then backfilledï¿½ and continued working. They called in the damage on 1521, when onsite i was informed the damage occurred before Christmas 2020. The crew also found the damage was still leaking when they exposed the damage
Southern California Gas Company | N | ORANGE | BREA | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALL CITIES ENGINEERING INC | JURUPA VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service with excavator while trenching for water.ï¿½ no USAï¿½
Southern California Gas Company | N | ORANGE | BREA | 2021-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 0 | 0 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | J J ELECTRIC | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | ORANGE | BREA | 2021-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor hit gas service. Service was marked 5 feet off. Service was marked with measurements, no wire on service and no G on curb.ï¿½ Confirmed no signal when trying to back locate.ï¿½ Contractor din not call after not call after they were not able to locate service off of marks. Marks indicated inchmeasurements only inch.ï¿½ï¿½
Southern California Gas Company | N | ORANGE | BREA | 2021-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | WILLIAMS PIPELINE CONTRACTORS INC | MISSION HILLS |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Plastic service was damaged, while homeowner doing yard work.
Southern California Gas Company | N | ORANGE | BREA | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WILLIAMS PIPELINE CONTRACTORS INC | MISSION HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit service with shovelï¿½
Southern California Gas Company | N | ORANGE | BREA | 2021-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WILLIAM PIPE LINE | MISSION HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor remodeling foundation when service was hit with backhoe. Crew arrived and controlled release of gas
Southern California Gas Company | N | ORANGE | BREA | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | WILLIAMS PIPELINE | MISSION HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit gas line while digging for sewer. No USA
Southern California Gas Company | N | ORANGE | BREA | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | GUARD FIRE PROTECTION | ANAHEIM | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor digging with backhoe hit a correctly marked plastic service ï¿½
Southern California Gas Company | N | ORANGE | BREA | 2021-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | 2 GUY ELECTRIC CORP | HACIENDA HEIGHTS | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Signal Was Pulled To Electric Lines. Area Marked Before Electric Onsite. USA Ticket Had Expired Before Contractor Began Excavating
Southern California Gas Company | N | ORANGE | BREA | 2021-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BIG BEN CONSTRUCTION | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor does not hand excavate by hand prior to using power excavation.ï¿½ Contractor also does not contact utility if they can not fine service in marked out area per dig alert policy.ï¿½ï¿½
Southern California Gas Company | N | ORANGE | BREA | 2021-07-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HENKELS MCCOY | CHINO | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Company contractor performing accu bore struck 1 2 plastic service in private property resulting in 1 residential outage No evacuation customer not home Service restored upon customer return in afternoon Service was properly located Contractor failed to protect in place D Error has been issued
Southern California Gas Company | N | ORANGE | CAPISTRANO BEACH | 2021-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | JOSE GOMEZ | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was making repairs to broken sewer and damaged 0.5 inch IPSï¿½gas pipe with shovel.ï¿½
Southern California Gas Company | N | ORANGE | CAPISTRANO BEACH | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | CAPISTRANO BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in, and contractor hit 0.5 inch IPSï¿½service with Shovel while digging to install drain.
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CREATIVE CONTRUCTION | LAKE FOREST | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit PE gas service while installing sewer.
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2021-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PETE BLACK CONSTRUCTION | NEWPORT BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was hand digging over sewer and damaged marked gas line.
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2021-12-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SADDLEBACK FENCE AND VINYL | COSTA MESA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. party contractor digging for irrigation hit service line. No USA called in
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2021-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | QS LANDSCAPE | CORONA DEL MAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit line digging irrigation trenchï¿½
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2021-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CAMPO LANDSCAPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging doing landscape work and hit the P.E. Service. USA ticket was expired at the time of the damage. Contractor also failed to maintain marks.
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2021-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | CAL BORE | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Valid USA located by co contractor Damaged 2 PLA with Bore Damaged over 2 from marks with underground bore
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2021-08-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WEST END ENGINEERING | ORANGE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Damaged 1 2 plastic service with shovel Marked Correctly USA ticket expired
Southern California Gas Company | N | ORANGE | COSTA MESA | 2021-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | JSQ IMPROVEMENT | HUNTINGTON BEACH |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 2 CTS branch service NO USA
Southern California Gas Company | N | ORANGE | COSTA MESA | 2021-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DM CONCRETE DEVELOPMENT | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Developer damaged exposed gas service while installing a drain.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2021-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VCI CONSTRUCTION LLC | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The gas line was marked out
Southern California Gas Company | N | ORANGE | COSTA MESA | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JA SALAZAR CONSTRUCTION | LA HABRA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was in process of digging upï¿½
Southern California Gas Company | N | ORANGE | COSTA MESA | 2021-08-16 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AMPAM PARK MECHANICAL | CARSON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged Service in Private property NO USA
Southern California Gas Company | N | ORANGE | COSTA MESA | 2021-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 65 |  | MACADEE ELECTRICAL CONSTRUCTION | CHINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA for contractor that damaged 2 inchPLA Service
Southern California Gas Company | N | ORANGE | COSTA MESA | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | GRANKOL ENTERPRISES | IRVINE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor was grading with a bobcat pulled a 3 4 steel service U S A ticket was expiredï¿½
Southern California Gas Company | N | ORANGE | COSTA MESA | 2021-11-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TANNER RJ CONSTRUCTION | COSTA MESA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While using an auger to drill new location forï¿½pole replacement Contractor augered steel service in half.ï¿½
Southern California Gas Company | N | ORANGE | COTO DE CAZA | 2021-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HACIENDA PIPELINE CO | YORBA LINDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor had a valid USA however, they continually renewed the ticket without asking for remarks. They damaged a 1 inch PE service while using a trencher.ï¿½
Southern California Gas Company | N | ORANGE | COTO DE CAZA | 2021-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MAXX AIR HEATING AND PLUMBING | COSTA MESA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in by contractor, contractor hit 0.5 inch service.
Southern California Gas Company | N | ORANGE | CYPRESS | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | DOWDLE CONSTRUCTION | LOS ALAMITOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1 2 pla service with backhoe No USA ticket
Southern California Gas Company | N | ORANGE | CYPRESS | 2021-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | NPL | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractorï¿½damaged 0.5 inch plastic service while digging to find water lines
Southern California Gas Company | N | ORANGE | CYPRESS | 2021-07-30 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NPL CONSTRUCTION | MIRA LOMA | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While prepping SMC for split and pull Contractor struck a marked 1 2 PE service
Southern California Gas Company | N | ORANGE | CYPRESS | 2021-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PRECISION PIPELINE | NORWALK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Garden Grove water Hit a Half inch plastic service with a back hoe while digging up a water leak The service was half plastic and half steel Locater had marks down and the water company failed to expose the service before digging with the back hoe and struck the service at the plastic part of service Pinched service and made repairs
Southern California Gas Company | N | ORANGE | CYPRESS | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HARRISON BUILDING INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 inch pla service while digging
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | S JADE CORPORATION | LAGUNA BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in and contractor hit our gas line.
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-10-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DTM CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator trenching to install sewer connection. Dug to 48 inch within property and unable to find service where marked. Began turning trench to sewer lateral and struck service line 8 foot N mark flags
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARTISTIC BUILDERS | WHITTIER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ALL gasï¿½marks were GOOD and visible Contractor hit 1 2 service with shovel ï¿½
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | THE ARTIST BUILDER | WHITTIER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Locator marked out ALL gas lines gas lines wereï¿½marked and visible for contractor Contractor was grading and hit 1 2 service he said he knew the gas line was there ï¿½
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GRIFF COMM | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. party contractor hit gas line while digging for sprinkler. No USA called in
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SOUTH COAST WATER DISTRICT | LAGUNA BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor had a valid USA. Locator did not locate out service. Supervision pulled in locator and talkï¿½to him about mismark and he will receive a note to file for this incident. This was locators 1st mismark.
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-03-18 | Operator excavation damage | Main | Steel | Miscellaneous/Other | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DC POWER | NA |  | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in and contractor hit 2 inch ST Main with jackhammer.
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-03-29 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NPL | BREA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CUSTOM BUILDERS | HUNTINGTON BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in and contractor hit gas service.
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-08-24 | Third party excavation damage | Meter | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DANA PACIFIC LANDSCAPE | SAN JUAN CAPISTRANO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damaged service with fence post digger No USA
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A code 1 was found while an EE was walking leak survey Upon finding the source of the leak it was determined that our service was damaged when a new fence was installed There was no USA ticket called in for the area
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ZSW INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in and NO ticket on file.
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | URIEL LOPEZ LANDSCAPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in and contractor hit 0.5 inch CTS service with shovel.
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-01-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HAMMER DOWN | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 3 inch main with back hoe clearing for water.
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-03-22 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 3 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LUPE ALVARADO | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | all USA marks were good contractor saw zaw through top of 3 inch stl main, thinking it was an abandon line.
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-04-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 7 |  | NA | DANA POINT | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Owner did not have NO USA, they were digging to plant some tree and hit our 1 inch PLA service with a shovel.
Southern California Gas Company | N | ORANGE | DANA POINT | 2021-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RS MYER | LAGUNA NIGUEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged service while attempting to remove tree out of ground. Contractor stated that the backhoe operator had a look out watching to see service.
Southern California Gas Company | N | ORANGE | FOOTHILL RANCH | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | C T CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in and contractor hit 1 inch IPSï¿½stubï¿½with backhoe while trenching grading area to pour concrete.
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | OC405 PARTNERS | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OC 405 Project . Contractor fail to performer proper excavation practices
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TONG V NGUYEN | FOUNTAIN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage no USA Crew responded and controlled gas leak
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2021-06-28 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NPL CONSTRUCTION | MIRA LOMA | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NPL was paving around valve can and dropped hot asphalt in valve can. Hot asphalt damaged 1 inch poly valve.
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2021-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TIM GREENLEAF ENGINEERING | HUNTINGTON BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Serviceï¿½was marked out from a previous U.S.A. ticket, riser was damaged when it was ran over with a skip loaderï¿½
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HCI INC | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Rock fell on main while excavating causing a leak.
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2021-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VCI CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party damaged .Locator marked service off measurements due to no riser found at location . Crew arrived and control release of gas .
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2021-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HCI | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Contractor excavating through driveway and damaged the gas service.
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2021-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GUERREO LANDSCAPE AND MAINTENANCE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and Landscaper was digging to plant trees when they hit our 1 2 service
Southern California Gas Company | N | ORANGE | FULLERTON | 2021-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | R J NOBLE | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor grading for the city hit our 0.75 inch steel service that was marked correctly.
Southern California Gas Company | N | ORANGE | FULLERTON | 2021-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARIZONA PIPELINE CO | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Arizona pipeline hit our plastic service while hand digging to install conduit.
Southern California Gas Company | N | ORANGE | FULLERTON | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BASE POINT GENERAL ENGINEERING | BREA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no USA digging without potholing. 2nd damage at this location
Southern California Gas Company | N | ORANGE | FULLERTON | 2021-04-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 9 |  | ARKIUS | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, Contractor Digging For Sewer
Southern California Gas Company | N | ORANGE | FULLERTON | 2021-04-07 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 3 |  | FULLERTON WATER DEPT | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Fullerton water department was digging to make repairs to a water service and they struck a 2 inch plastic service. it was a plastic offset on a steel service, the plastic was not in service history and not shown on any map GIS or EPOC.
Southern California Gas Company | N | ORANGE | FULLERTON | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CORBEL COMMUNICATIONS | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor did not pothole before digging
Southern California Gas Company | N | ORANGE | FULLERTON | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor doing work for the home owner damaged our plastic service while trenching to in stall sewer lateral .Sherman Veal located the service hooking up directly to the wire at the riser. after the damage was repaired we used his locator to relocate the service while the hole was open. we got zero signal over the service and a high signal where he previously put his marks down.ï¿½
Southern California Gas Company | N | ORANGE | FULLERTON | 2021-08-26 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | CITY OF FULLERTON WATER | FULLERTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | damaged 1 inch plastic main with probe while investigating water leak
Southern California Gas Company | N | ORANGE | FULLERTON | 2021-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ROBERT HEINZEL | FULLERTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hitï¿½are pipe while doing landscaping. And remolding there home.
Southern California Gas Company | N | ORANGE | FULLERTON | 2021-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | QT GENERAL CONTRACTOR INC | GARDEN GROVE |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While 3rd party performing work for homeowner to repair sewer houseline damaged the gas service with shovelï¿½
Southern California Gas Company | N | ORANGE | FULLERTON | 2021-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GUTIERREZ LAND SCAPING | LYNWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing communication lines
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2021-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VCI CONTRUCTION | UPLAND |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 3 inch main while working on sewer line. Contractor failed to pot hole by hand before using a track hoe damaging the main. The main was properly marked on the street andï¿½after speaking with the homeowner Vicky Height provided a USA ticket number that was called after the damaged happened. I advised the contractor to get his own ticket before continuing with the work.
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2021-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MAZIA LUNA | GARDEN GROVE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner cut into our gas service while excavating to install a gas line for a pool heater
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HIGGINS CONSTRUCTION | MONTCLAIR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Grading contractor damaged 2 service did not pothole USA marks were removed during construction SCG not at fault
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VVD | GARDEN GROVE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 0.5 inch plaï¿½ service while excavating
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | STRONG INC | LOS ALAMITOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 2 inch plastic main with a trackhoe while installing electrical conduit. The contractor failed to hand expose the pipe before using the machine. The pipe was properly mark on the street with yellow paint and flags inside the fence.ï¿½
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2021-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CITY OF GARDEN GROVE | GARDEN GROVE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Did not pothole the plastic service before using a back hoe
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2021-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOEY NGUYEN | GARDEN GROVE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, Home owner stated was digging for a drain line. Service bent back on arrival.ï¿½
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2021-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | KORDICH CONSTRUCTION INC | CYPRESS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Part contractor damage our 0.5 IPS with backhoe.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DON WEILER | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd. party contractor demoing house hit gas line. USA expired
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FRISCH AND SONS HEBER | VILLA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 3 4 stl service with mini excavator while digging to install irrigation No USA
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RAFAEL S FARIAS GENERAL CONTRACTOR | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged plastic service with a backhoe while excavating for sewer Our facility was accurately marked Contractor failed to dig safely
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOME OWNER | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit Service while handing for drainage
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EXCEL PAVING COMPANY | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractors digging trench for sewer line and came across our gas line Exposed it by hand and found out the gas line was leaking so they called it in It was a 3 4 service line and LCT made a permanent repair with a clamp
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-12-22 | Third party excavation damage | Meter | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | BELCO ELECNOR GROUP | HUNTINGTON BEACH |  | N | Y | Yes | Yes | No | Yes | No | No | No | 3rd party contractor hit 0.5 IPS service plastic with bore machine.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GRP CONTRACTORS | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damaged 1 2 plastic service with shovel USA marks where visible and marked correctly
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 8 |  | CREDOS BUILDERS | INGLEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1 inch service while digging to install grease pit.ï¿½
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | NA | NA |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged , no usa . Crew arrived and controlled the unplanned release of natural gas
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | NA | HUNTINGTON BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damaged gas service while digging.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-11-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PHIL ETNYRE | HUNTINGTON BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | "Home owner hired a plumber to replace corroded leaking water line and ended up cutting into our gas line thinking it was the water line he was working on. The old steel gas line had 0.5 inch CTS inserted inside which began to blow once cut.ï¿½
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-12-06 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | B N REMODELING | GARDEN GROVE |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 inch PLA Service with probe while potholing for water line. USA Valid and marked correctly
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ELITE ROOTER | FULLERTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor digging for bore hole and hit our gas service with a shovel.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CRANDALL S PLUMBING | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damaged 1 2 plastic service with backhoe Service marked in yellow paint and flags SCG not at fault
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DELTA FLOOR CARPET ONE | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1 2 pla service while digging in private property No USA
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TRU LANDSCAPE SERVICES | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party damage hit marked stub 0.5 IPS gas line with a mini excavator.ï¿½
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-02-04 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 150 |  | CONNERS SAW CUTTING | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor cut into our 2 inch stl pipe in 4 inch stl casing while saw cutting. Pipe and casing shallow due to being on top of a large channel.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2021-11-06 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SERVICE LINE HIT WITH SHOVEL TO FIX A PLUMBING ISSUE.
Southern California Gas Company | N | ORANGE | IMPERIAL | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DEVELOPER | IMPERIAL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with a trencher to install a drain hit the service line No USA notification
Southern California Gas Company | N | ORANGE | IRVINE | 2021-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | EMPIRE DESIGN LANDSCAPE ASSOCIATES INC | NEWPORT BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No usa called in contractor liable for damages occured
Southern California Gas Company | N | ORANGE | IRVINE | 2021-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CRUZ CAT CONSTRUCTION ENGINEERING | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3dr Party contractor damage 1 PE service with excavator No USA
Southern California Gas Company | N | ORANGE | IRVINE | 2021-07-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | CAL WEST UNDERGROUND | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 2 plastic main with a mini excavator while digging to install street lighting They did not have a USA ticket
Southern California Gas Company | N | ORANGE | IRVINE | 2021-07-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | INFINITY PLUMBING | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plummer was excavating with backhoe damaged 1 2 plastic service with EFV ï¿½No USA ticket
Southern California Gas Company | N | ORANGE | IRVINE | 2021-05-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SILVERWOOD LANDSCAPE CONSTRUCTION | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 inch PE service with backhoe while grading. Contractor did not have a USA ticket.
Southern California Gas Company | N | ORANGE | IRVINE | 2021-06-25 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CMU MASONRY ALEJANDRO CORONA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in and contractor hit 1 inch riser with shovel.
Southern California Gas Company | N | ORANGE | IRVINE | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | REBEL PLUMBING | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Lines marked correctly by a private contractor. No USA .ï¿½ Contractor was installing new cable lines
Southern California Gas Company | N | ORANGE | IRVINE | 2021-07-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PULTE HOMES | MISSION VIEJO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit marked visible gas service Locator marked out ALLï¿½gas main service contractor hit service with backhoe
Southern California Gas Company | N | ORANGE | IRVINE | 2021-05-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | IRVINE COMPANY | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic stub while hand digging to install a drain. USA was not called.ï¿½
Southern California Gas Company | N | ORANGE | IRVINE | 2021-01-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AC SPRAGGINS ENGINEERING UNDERGROUND INC | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA . Crew and Supervisor explain to contractors the importance of 811
Southern California Gas Company | N | ORANGE | IRVINE | 2021-07-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CORNERSTONE CONCRETE INC | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Locator marked our 1 2 service and contractor still hit service ALL marks were GOOD
Southern California Gas Company | N | ORANGE | IRVINE | 2021-12-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BUCCOLA LANDSCAPE SERVICES INC | ANAHEIM |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Faith Electric hit steel service with auger while installing power poll anchor. Standard SVC was located but not branch svc.ï¿½
Southern California Gas Company | N | ORANGE | IRVINE | 2021-02-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BUCCOLA LANDSCAPING | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | ORANGE | IRVINE | 2021-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MOUNTAIN MOVERS ENGINEERING INC | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA , Contractor damaged service while grading . Evacuated the jobsite for safety . Crew arrived and controlled gas leak . Sup and crew advise the contractor of 811
Southern California Gas Company | N | ORANGE | IRVINE | 2021-06-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PAC SHORES | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in and contractor hit 1 inch service with backhoe.
Southern California Gas Company | N | ORANGE | IRVINE | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage discovered on routine leakage survey no one claims responsibility damage not reported by damaging party NO USA
Southern California Gas Company | N | ORANGE | IRVINE | 2021-06-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CORNERSTONE CONCRETE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party damaged . When crew arrived no one was on the scene. Service had EFV . Crew controlled and repaired service line
Southern California Gas Company | N | ORANGE | IRVINE | 2021-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | NA | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was digging to install a drainage line when they damaged a gas service. The Contractor did not have a USA ticket andï¿½is fully responsible. ï¿½
Southern California Gas Company | N | ORANGE | IRVINE | 2021-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ACE LOW VOLTAGE | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit service with excavator.
Southern California Gas Company | N | ORANGE | IRVINE | 2021-11-16 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | CANSCO | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 inch service line while digging for sewer
Southern California Gas Company | N | ORANGE | IRVINE | 2021-07-15 | Third party excavation damage | Riser | Polyethylene Pipe | Miscellaneous/Other | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RICK HAMM CONSTRUCTION | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor used sawzall to cut into live riser thinking that it was the abandoned customer pool line They did not call USA
Southern California Gas Company | N | ORANGE | IRVINE | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | INTERIOR ELECTRIC INC | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 2 inch PLA service while grading . Service was marked crew arrived and controlled release of gas
Southern California Gas Company | N | ORANGE | IRVINE | 2021-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SOCAL EDISON | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractors No USA Crew controlled gas leak and alter service
Southern California Gas Company | N | ORANGE | IRVINE | 2021-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JENNIFER BAJOREK | IRVINE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to add cable for communication. No USA Crew control gas leak and repaired service
Southern California Gas Company | N | ORANGE | IRVINE | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KRONMULLER CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was setting wooden stake in the ground and hit our 1 inch PLA service. All marks were good.
Southern California Gas Company | N | ORANGE | IRVINE | 2021-01-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SHEA HOMES | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaging party should be liable for repairs
Southern California Gas Company | N | ORANGE | IRVINE | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RAM CONSTRUCTION | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All USA marks were on there marks, contractor DIDN feetT HAND expose service. Contractor hit 0.5 inch PE service with backhoe.
Southern California Gas Company | N | ORANGE | IRVINE | 2021-04-08 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CAL BORING | NA |  | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2nd party contractor damaged gas service . They stated that they were not aware of service crossing bore path . Crew and Sup explained to contractor the importance of double checking the records ï¿½. USA ticket was. system not accepting
Southern California Gas Company | N | ORANGE | IRVINE | 2021-03-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | PAULUS ENGINEERING | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did expose both mains, they had orange paint on the ground like with all other utilities they found. contractor hit gas main with excavator. locator did mark out gas line.
Southern California Gas Company | N | ORANGE | IRVINE | 2021-01-26 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL WEST UNDERGROUND | NA |  | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor did not call in for a USA. contractor was digging to extend stub and they hit stub with backhoe.
Southern California Gas Company | N | ORANGE | IRVINE | 2021-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit line atempty construction site. unreported damage on 0.5 ips service updated completed date to coincide with GSO.
Southern California Gas Company | N | ORANGE | IRVINE | 2021-05-24 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARB INC | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DIMP contractor ARB accidentally hit service with shovel ahead of main service replacement
Southern California Gas Company | N | ORANGE | IRVINE | 2021-10-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FYDAQ | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging, with hand tools, to install yard drainage line when he hit the 0.5 inch CTS service. No USA ticket.
Southern California Gas Company | N | ORANGE | LA HABRA | 2021-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | 2022BROTHERS INC | FULLERTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Damage, Contractor Did Not Call USA To Dig To Install Fencing.
Southern California Gas Company | N | ORANGE | LA HABRA | 2021-09-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | AMERICO BUILDERS | FULLERTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Americo Builder did not call USA. Struck 1 inch svc with backhoe
Southern California Gas Company | N | ORANGE | LA HABRA | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOHN GALVIN | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck a plastic gas line while had digging
Southern California Gas Company | N | ORANGE | LA HABRA | 2021-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | LA HABRA WATER | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While probing for the water main, the contractor pierced our 0.5 IPS service line.
Southern California Gas Company | N | ORANGE | LA PALMA | 2021-08-12 | Third party excavation damage | Miscellaneous/Other | Steel | Backhoe/Trackhoe | 0.5 | 465 | 465 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LA CO PUBLIC WORKS | SOUTH GATE | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | NA
Southern California Gas Company | N | ORANGE | LA PALMA | 2021-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LEGACY COMMUNICATIONS | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 0.5 inch plastic gas line with excavator.
Southern California Gas Company | N | ORANGE | LA PALMA | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LEGACY COMMUNICATIONS | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor damaged 0.5 inch plastic service while excavating to install for ATandT.
Southern California Gas Company | N | ORANGE | LA PALMA | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NX UTILITIES | SAN MARCOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged 1 2 plastic service with backhoe ervice was mismarked No locate wire
Southern California Gas Company | N | ORANGE | LA PALMA | 2021-05-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 8 |  | LEGACY COMMUNICATIONS | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged 2 inch plastic main while digging with mini excavator. Contractor failed to expose our pipe correctly
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NPL CONTRCTOR | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2021-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALFREDO GARCIA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging for footing struck our gas serviceï¿½
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2021-07-13 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | AM ORTEGA | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1 PE main while excavating SMC Proper excavating techniques were being performed I believe the hard soil played a big role in this situation
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2021-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RADACH CONSTRUCTION | DANA POINT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck 1 2 plastic service with a post hole digger while working to install a fence post Contractor did not call USA
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2021-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KALKA PLUMBING | IRVINE | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Contractor did not have a USA, he cut he wrong line. contractor knows he feets at fault
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2021-03-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOSHUA DYKES | ALISO VIEJO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in and contractor hit 1 inch PLA service with stake.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2021-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | ADVANCED GEOTECHNIQUES | ROCKLIN | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and contractor hit gas service.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2021-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BROWN BROTHERS CONSTRUCTION AND ASSOCIATES | LAGUNA BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged steel service with an excavator while digging to build new concrete steps Contractor had a valid USA ticket and our marks were accurate Contractor failed to pothole and dig safely
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | API | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Department of water and power was probing to find a water leak and was probing above gas main and probed into gas main.
Southern California Gas Company | N | ORANGE | LAGUNA HILLS | 2021-01-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | LEATHERWOOD CONSTRUCTION INC | FOUNTAIN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All locators marks were good, contractor did not expose 3 inch main was digging with backhoe and hit 3 inch gas main. Contractor knows they are at fault.
Southern California Gas Company | N | ORANGE | LAGUNA HILLS | 2021-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PALMERS LANDSCAPE | LAGUNA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and contractor hit gas service digging out to build wall.
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2021-07-07 | Operator excavation damage | Riser | Steel | Not Available | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOSE ORTEGA | BREA | CA | Y | N | Yes | Yes | No damage to SUOF. | Yes | No damage to SUOF. | Yes | Yes | NPL replacing a standard Branch they failed to properly locate existing services being replaced was in fact 2 standards being replaced cut into liveï¿½service they thought was a branch resulted in blowing gas and damage to Gas co property Valid USAï¿½
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2021-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RANSCAPES | IRVINE | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party contractor pot holed and found a abandon STL line service when theï¿½
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2021-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VEGA LANDSCAPE | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1 2 plastic branch service while digging to install wall Contractor failed to maintain marks
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2021-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ARTISTIC MAINTENANCE INC | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged our service while hand digging to fix a water leak Contractor did not have a USA ticket
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2021-09-23 | Third party excavation damage | Main | Steel | Boring Equipment | 4 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 17729 |  | 11 |  | JFL ELECTRIC INC | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | On 9-23-2021 SoCalGas was notified of a third party damage at 28332 Capistrano in the city of Laguna Niguel. Third party contractor was attempting to bore in new street lighting and struck a 4in steel gas main. SoCalGas crews responded and controlled gas at 15:00. USA ticket A212520515 was issued for this project, however, no delineation was provided. SoCalGas electronic response of no delineation was not responded to by the contractor prior to commencing. There were no injuries or fatalities resulting from this incident. This incident was reported to the CPUC when SoCalGas became aware of major media coverage.
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2021-06-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TOP LLC | WOODLAND HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in and contractor hit was trenching to install in Electric and hit gas service.
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NEWMAN LANDSCAPE INC | LAGUNA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in, and contractor hit 0.5 inch CTS service with Shovel while digging to install drain.
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2021-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew went out to centerfix existing leak and when they finally center leak they dug it up andï¿½found an unapproved clamp on our PLA main that was leaking. This clamp was from anotherï¿½utility company hitting us and fixing it themselves. NO record of SoCal Gas EVER being at this location.ï¿½
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2021-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | LAKE FOREST | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | EIR went through some correction issues with dispatch as far as arrival times go But is now corrected This was not my district to cover for such On Call was just assisting Jacob Lopez the On Call sup for Orange Coast at the time
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2021-07-08 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 0.75 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CARLOS MUNIZ | COVINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Locator marked out Main and service Contractor hit riser with the wheel of a scissor lift
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2021-01-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3749 |  | 0 |  | LEATHERWOOD CONSTRUCTION INC | FOUNTAIN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SoCalGas was notified of a third party damage at 24321 Avenida De La Carlota Laguna Hills, CA. Third party contractor damaged a 3 inch plastic gas main. SoCalGas personnel were sent to the scene and safely controlled the gas. No injuries were reported due to the release of gas. SoCalGas initially reported due to receiving area odor complaints in the general area of 24451 Highpine Rd Lake Forest, CA. Crews were dispatched to investigate. Throughout the investigation, it was later determined that the cause of the area odor was due to the third party damage at 24321 Avenida De La Carlota Laguna Hills, CA. This Incident was reported to the CPUC due to public attention.
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2021-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GJ M LANDSCAPING | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a backhoe to remove copper piping and hit the service line to the adjacent address of 1354.
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2021-03-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SANTANA CONCRETE | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and contractor hit gas line.
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BILL GREELAY | NEWPORT BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and contractor hit gas service.
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2021-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BUCCOLA LANDSCAPING INC | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Ian Burns was incident commander Contractor failed to call USA
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2021-11-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL WEST UNDERGROUND | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was using an auger to install street lighting foundations when he damaged our 2 inch PE main. Contractor did not have a USA ticket.ï¿½
Southern California Gas Company | N | ORANGE | LOS ALAMITOS | 2021-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CTM INC | LOS ALAMITOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor damaged our service line with a shovel while trenching for Drain line.Damage occurred in the backyard.
Southern California Gas Company | N | ORANGE | LOS ALAMITOS | 2021-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 9 |  | DOMINGUEZ GENERAL ENGINEERING | CHINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 inch main Hit by Loader while moving surface sand dirt.
Southern California Gas Company | N | ORANGE | MIDWAY CITY | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AMPCO CONTRACTING | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 0.5 inch service while potholing with shovel for crew to abandon.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GLEN OTTENS | MISSION VIEJO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA . Crew and Supervisor explained to contractor the importance of calling 811
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2021-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GROVER CONSTRUCTION INC | SAN CLEMENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Was Called In And Contractor Hit 0.5 Inch Service With Shovel While Digging To Install Drains.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | YUNA MULLICK | MISSION VIEJO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging to plant palm and struck an unmarked 1 2 IPS PE service
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DEMPSEY CONSTRUCTION | CARLSBAD | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractors claimed locator marked out the service. Crew found paint and flags but they were not SCG. Contractor hit the 1 inch plastic service while removing a pedestal for a light. Contractor dug before USA was valid.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2021-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | IRRISCAPE MARTIN GARCIA | TEMECULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing Irrigation
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2021-12-02 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PREMIER BROADBAND SERVICES INC | CORONA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ï¿½"
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2021-02-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ASPLUNDH | ANAHEIM | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor hit service with back hoe digging with a expired ticket
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2021-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | HOTLINE CONTRACTOR | NEWPORT BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | HCI dug into PE service with shovel while trying to pothole our utility. Locator signal jumped to other utility causing mismark.ï¿½
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2021-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RESIDENTIAL ELECTRIC | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging To Lay Down Electric Conduits. No USA. Crews Responded And Repaired Damaged Service
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2021-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALI ZONOUZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage Owner damage service line with jack hammer crew responde3d and control gas leak
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JACK WANG | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor had the 2 inch gas main exposed and damaged it with a backhoe by working to close to it with heavy machinery.ï¿½ The contractor admitted fault and is fully responsible.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2021-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MATA CONSTRUCTION CO INC | SANTA ANA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party contractor damaged gas service, dug prior to U.S.A. ticket being valid before 48 hrsï¿½
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2021-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | NEWPORT BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no USA requested, customer digging for fence post
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JPT CONSTRUCTION | NEWPORT BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was trenching for electrical in private property and damaged plastic gas service. No USA ticket.ï¿½
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2021-11-29 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CARLOS FABRICIO | NEWPORT BEACH |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line. 0.5 inch cts service. Valid USA. No visible delineation or USA Marks for any utility at time of incident. 6 people evacuated from two residences by fire department. Crew arrived, controlled gas, made permanent repairs, and evacuations were lifted as appropriate.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2021-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PRO DEMO | NEWPORT BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was demolishing structure when they damaged the 0.5 inch Plastic service with a Bobcat. NO U.S.A. ticket.ï¿½
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2021-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MDM | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 2 plastic service by 3rd party contractor while removing roots No U S A ï¿½
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | T E ROBERTS INC | ORANGE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Rafael Lua third party digging with backhoe installing water main.
Southern California Gas Company | N | ORANGE | NEWPORT COAST | 2021-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 2 |  | HYFA INC | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Ready Dig hit service with backhoeï¿½
Southern California Gas Company | N | ORANGE | ORANGE | 2021-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COASTAL | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hitline NO USA , Crew control leak and repaired service
Southern California Gas Company | N | ORANGE | ORANGE | 2021-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | UNITED CONSTRUCTION COMPANY | RANCHO CUCAMONGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Called In. Contractor Building Wall, Hit Service Line.
Southern California Gas Company | N | ORANGE | ORANGE | 2021-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CEBALLOS CONSTRUCTION INC | ARTESIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | While contractor was trenching with a shovel, they hit our gas service.
Southern California Gas Company | N | ORANGE | ORANGE | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HHS CONSTRUCTION | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Customer was digging around property to do foundation work when they hit service line with clay spade. Service was not marked due to USA not being notified. Company crew was able to clamp leak.
Southern California Gas Company | N | ORANGE | ORANGE | 2021-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HHS CONSTRUCTION | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit main while trenching with mini excavatorï¿½
Southern California Gas Company | N | ORANGE | ORANGE | 2021-11-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 9 |  | E DAN CONSTRUCTION INC | ORANGE |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR HIT SERVICE LINE WHILE REMOVING TREEï¿½
Southern California Gas Company | N | ORANGE | ORANGE | 2021-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | EDISON ELECTRIC | SANTA ANA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 inch PE service called in by other contractors. Contractors on site indicated that DTM Construction hit service while trenching with a backhoe for a wall.ï¿½
Southern California Gas Company | N | ORANGE | ORANGE | 2021-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ATLAS INC | STUDIO CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging for sewer repairs damaged our 1 inch plastic gas service with a jackhammer that was being used forï¿½digging.
Southern California Gas Company | N | ORANGE | ORANGE | 2021-07-13 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CITY OF ORANGE WATER DEPT | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas main was hit while probing for water main lateral
Southern California Gas Company | N | ORANGE | ORANGE | 2021-06-25 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit stub while digging to install supply line. Facility was not mapped and no records indicate gas facility at damage location.ï¿½
Southern California Gas Company | N | ORANGE | PLACENTIA | 2021-09-10 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 4 |  | SE PIPELINE CONSTRUCTION | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Company contractor struck 2 plastic gas main with backhoe SCG Gas Ops crew made perm repairs Contractor failed to maintain proper clearance of correctly marked SCG facility Contractor also failed to excavate by hand as per SCG policy when working over plastic main or service D error issued to SE Pipeline to Trujillo Grading
Southern California Gas Company | N | ORANGE | PLACENTIA | 2021-03-23 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 3 |  | SHEA HOMES | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper hit main while planting trees.ï¿½ No USA
Southern California Gas Company | N | ORANGE | PLACENTIA | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CABLE COMMUNICATIONS | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While installing a grounding rob the contactors hit a 1 PE service
Southern California Gas Company | N | ORANGE | PLACENTIA | 2021-12-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | FLAMINGO CONSTRUCTION INC | STUDIO CITY |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor digging with excavator struck a marked gas line while installing conduit.
Southern California Gas Company | N | ORANGE | PLACENTIA | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Arizona pipeline was digging next to our service riser when they struck the plastic service. Marks in the street where visible butï¿½the flags ETD had put theï¿½in the grass and planter where removed. Arizona pipeline said they were gone before they got to the job.
Southern California Gas Company | N | ORANGE | PLACENTIA | 2021-05-24 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | AM ORTEGA | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 0.5 plastic service with shovel.
Southern California Gas Company | N | ORANGE | PLACENTIA | 2021-07-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 5 |  | VALDEZ UNDERGROUND | BLOOMINGTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged our 2 plastic gas main while excavating with a back hoe Gas line was marked correctly ï¿½
Southern California Gas Company | N | ORANGE | PLACENTIA | 2021-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | SERGIO HERNANDEZ POOL PLUMBING | FONTANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party nicked gas line with shovel while digging to install pooline. USA was not called.
Southern California Gas Company | N | ORANGE | PORTOLA HILLS | 2021-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JASPER MASONRY COMPANY | COSTA MESA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to call USA and damaged our service
Southern California Gas Company | N | ORANGE | PORTOLA HILLS | 2021-07-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JASPER MASONRY COMPANY | COSTA MESA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call USA They damaged the plastic service with a backhoe while digging for a wall
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2021-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WEBB CONSTRUCTION DAVID WEBB | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Damage No USA Crew controlled gas release and alter service
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2021-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TABA CONSTRUCTIONS | NA |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor nickedï¿½gas line, while digging it up, USA was good and so was locator feets marks.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | IRVINE FENCE | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Marks were accurate and it was located on time Contractor failed to pothole safely and failed to provide delineation Service was hit within 6 of marks
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2021-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC CONTRACTOR | SAN JUAN CAPISTRANO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call in for a USA Ticket. Contractor was breaking driveway to remove tree branch and they hit service with a pick axe. Contractor knows hes at fault.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2021-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LOS SOLIS LANDSCAPING | TUSTIN | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hand digging for retaining struck and damaged 0.5 inch CTS gas service line. USA was not requested.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2021-04-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CH ANDERSON CONSTRUCTION | SAN CLEMENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in and contractor hit 0.5 inchï¿½gas service with backhoe on accident.ï¿½
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KEVIN SHEEHAN | SAN CLEMENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and contractor hit gas service.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2021-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DON WERT CONSTRUCTION | SAN CLEMENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Was Called In And Contractor Hit 0.5 Inch Plaï¿½Service With Shovel While Digging To Install Irrigation.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | STN BUILDERS INC | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit 1 inch plastic service while boring.ï¿½
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2021-08-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NESTOR JIMENEZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 2 PLA service by contractor while grading NO USA
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2021-02-25 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 42 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CITY SAN JUAN CAPISTRANO WATER DEPARTMENT | SAN JUAN CAPISTRANO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not hand expose service and pulled on service with backhoe.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2021-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | D K PIPELINE | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All marks were down Flags and Paint. contractor hit service with shovel. Contractor at fault.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SAN JUAN CAPISTRANO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2021-05-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ALBD ELECTRIC CABLE | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Contractor dug outside of Delineation and NEVER called in to remarks new area.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | QUEST ENGINEERING INC | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party demo crew damaged 1 PE service Failure to expose prior to performing work
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LNS CONSTRUCTION | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Edison was making a repair on one of there box and hit our line with a shovel.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ORANGE COUNTY PLUMBING | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Half inch plastic service hit with shovel. Service was marked correct.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GJ GENTRY | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was replacing sewer lines and damaged 0.5 inch CTS service. service was marked incorrectly by Gas Co. locator, but damage occurred 6 20.51 and USA ticket expired on 6 15 21.ï¿½ï¿½
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-06-22 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | service was located by SCG contractor SE Pipe. They areï¿½completing aï¿½main service replacement for DIMP, while excavating service the contractor damaged the plastic service with shovel.ï¿½
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TUI UNDERGROUND UTILITY CONTRACTOR | SAN JACINTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The gas line was marked and still damaged our line
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WALSH CONSTR | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Plastic service pulled out of ground when grading.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | CABLE TECH | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | this was a damage to a 0.75 inch steel service with no valid USA.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LUCAS BORDERS INC | LA HABRA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit our properly marked 0.5 inch plasticï¿½service.ï¿½ Marks were very light due to them running a sweeper over the street on a daily basis,
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CONAN BUILDING CO | SAN CLEMENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Damaged 0.5 inch service while digging near riser. NO U.S.A. ticket.ï¿½
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | CITY OF TUSTIN | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor liable for damages
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PARADISE DESIGN | SAN CLEMENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while excavating to install fence
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | LUCAS BUILDERS | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor hit and damaged a 0.5 inch CTS service in copper casing.ï¿½ Facility was in marked.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | LUCAS BUILDERS INC | LA HABRA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Third party contractor installing sewer for the City of Santa Ana hit a 0.5 inch CTS service encased in copper.ï¿½ Facility was marked, however the marks were approxamatly 6 feet off.ï¿½ The contractor pot holed the day before and could not find the facility, therefore they should have called 811 again asking for a verifacation of marks.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-02-22 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | ROTO ROOTER | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Third party contractor hit 2 inch plastic main with a mini excavator.ï¿½ Per the first ticket, it stated they would be working in the driveway of the residence.ï¿½ The second ticket did not specify, however they dug outside of he deliniation of the concrete walkway.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-03-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit us while digging up to replace sewer.ï¿½
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JNA FENCE | NA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | City of Lindsay was repairing a water line and damaged our gas service, they excavated prior to legal start time of their USA ticket.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SANTA ANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and contractor hit gas service.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MUL CONSTRUCTION INC | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ï¿½"
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC HYDRO TECH | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading to install new asphalt damaged 1 2 IPS gas service No valid USAï¿½
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-05-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party damaged . Unknow party that damaged main . Repairs were found on main due to code 1 conditions . Crew altered main .
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JUAN LOZANO | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Contractor was excavating and damaged the plastic Gas Service.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | SRK ENGINEERING | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging a trench
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | VANTAGE UTILITY SERVICES | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damage by contractor . Contractors fail to practices proper excavation procedures . crew repaired damaged service
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-05-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALDRIDGE ELECTRIC PREFORMING WORK FOR WALSH | LIBERTYVILLE | IL | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Aldridge construction excavating for walsh, struck 2 inch PE gas main within properly marked delineation. Failed to pothole prior to excavating.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | JOSE MARTINEZ | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging to plant a tree, and severed plastic service with shovel.ï¿½
Southern California Gas Company | N | ORANGE | SANTA ANA | 2021-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | NA | SANTA ANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was excavating to install a wall.ï¿½ Home owner did not call Dig Alert and did not have a USA ticket.ï¿½ They struck a 0.5 inch plastic service.
Southern California Gas Company | N | ORANGE | SEAL BEACH | 2021-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MICHAEL JURADO JR | STANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damage our line with pick axe Line was marked correctly and gas line was exposed
Southern California Gas Company | N | ORANGE | SEAL BEACH | 2021-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HACIENDA PIPELINE | YORBA LINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas line was hit with mini excavator while performing work to install electrical for Edison.ï¿½
Southern California Gas Company | N | ORANGE | STANTON | 2021-12-17 | Third party excavation damage | Riser | Polyethylene Pipe | Not Available | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | STANTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor hit 0.5 inch plastic service in casing with trencher. USA ticket was expired.ï¿½
Southern California Gas Company | N | ORANGE | STANTON | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALL AROUND UNDERGROUND | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 0.5 inchplastic service while excavating.
Southern California Gas Company | N | ORANGE | STANTON | 2021-07-13 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HIGHRIDGE LANDSCAPE INC | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 2 plastic main in private property with ditch witch NO USA
Southern California Gas Company | N | ORANGE | SURFSIDE | 2021-10-14 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SURFSIDE COLONY | SURFSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Open Trenching for sewer and ripped out our gas line with the backhoe.
Southern California Gas Company | N | ORANGE | SURFSIDE | 2021-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARIZONA PIPELINE CO | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 0.5 inch pla service while digging by hand
Southern California Gas Company | N | ORANGE | TRABUCO CANYON | 2021-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CABALLERO POOLS AND SPA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged our 1 2 plastic service with a shovel while excavating for a new wall and failed to notify USA
Southern California Gas Company | N | ORANGE | TRABUCO CANYON | 2021-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JASPER COMPANY | COSTA MESA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | ORANGE | TUSTIN | 2021-11-15 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | PACIFIC WEST COMMUNICATIONS | SAN DIMAS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor dug up a hole which contained a steel line and a copper line. He was trying to cut off the water and saw zawed through the copper line thinking it was water. He clamped the pipe himself and gas was controlled when we arrived.ï¿½
Southern California Gas Company | N | ORANGE | TUSTIN | 2021-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JC CONSTRUCTION | HAWAIIAN GARDENS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor using a backhoe to dig a wall footing when they bent a steel service. Contractor was not onsite when we arrived and there was no valid USA.ï¿½
Southern California Gas Company | N | ORANGE | TUSTIN | 2021-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | API | CERRITOS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Damagedï¿½1 service by 3rd party contractor backhoe USA ticket expiredï¿½ did not hand expose PLA gas service
Southern California Gas Company | N | ORANGE | TUSTIN | 2021-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CW DRIVER | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaging party should be laibleï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2021-10-20 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARIZONA PIPELINE CO | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Plumber sliced 0.75 steel service with sawzall
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2021-07-19 | Operator excavation damage | Main | Steel | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 21 |  | NPL | BREA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2nd party contractor excavated over marked 1 PE main which resulted in a damage
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2021-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SID WALKMAN | WESTMINSTER |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2021-04-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LANDMARK DESIGN | WESTMINSTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 0.5 inch ips service.
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2021-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | WESTMINSTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 0.5 inch pla service while digging for foundation. No USA
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2021-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | WESTMINSTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged gas line while grading for new paving.ï¿½
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2021-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LSCO | RANCHO CUCAMONGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating without USAï¿½ damaged our plastic serviceï¿½
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2021-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RJ ALLEN | GARDEN GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor trenching for new sewer line damaged service with no USA
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2021-01-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CG LANDSCAPE INC | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscapers installing a tree support drove their steak into our plastic service, USA was not called
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2021-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KEVIN GARCIA | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging to replace a water service
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PACIFIC WEST COMMUNICATION | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | failed to take caution when potholoing
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2021-05-05 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SE PIPELINE CONSTRUCTION | SANTA FE SPRINGS | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Nathan Reddixï¿½SE Pipeline marks their own lines.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2021-03-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MASTER P S POOLS SPAS INC | YORBA LINDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch Plastic service struck by contractor hired by home owner to dig outï¿½pool excavation. No USA.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2021-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RILO PLUMBING | PLACENTIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service while digging without USA ticket.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2021-04-02 | Third party excavation damage | Main | Steel | Grader/Scraper | 3 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | PROGUE GRADING | GARDEN GROVE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Developer was grading when his bulldozer hit our 3 inch steel main and pulled it out of the 4 inch plastic it was tied too.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2021-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | KRISTY KLINE | BANNING | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | Contractor digging for water service replacement and damaged service with no USA
Southern California Gas Company | N | RIVERSIDE | BANNING | 2021-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | JIMMY BATSON | BANNING | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Could not locate valid USA
Southern California Gas Company | N | RIVERSIDE | BANNING | 2021-05-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AC SPRAGEN ENGINEERING | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for Edison in a new Tract development when they damage 2 inch PLA main in dead in street. NO USA
Southern California Gas Company | N | RIVERSIDE | BANNING | 2021-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RGCI GRADING | HUNTINGTON BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging for fence posts, No USA.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2021-07-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | MCC EQUIPMENT INC | YUCAIPA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor found exposed the marked 2 steel main as 2 PLA Contractor did not call SCG to verify and find the 2 PE main they continued to work striking the plastic main
Southern California Gas Company | N | RIVERSIDE | BANNING | 2021-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ROTO ROOTER | DESERT HOT SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Requested, Contractor Working For Customer Digging For Sewer Plumbing
Southern California Gas Company | N | RIVERSIDE | BANNING | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ALL AMERICAN ASPHALT | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG contractor was digging to expose Gas line that they located when they damaged the plastic service with a shovel. The contractor failed to protect the facilities in place and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2021-10-04 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Grader/Scraper | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ALL AMERICAN ASPHALT | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No damage to SUOF. | Yes | Yes | LADWP was excavating to install water line and hit our service.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2021-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.75 inch line was struck. we were called out to indentify it. was not a live line. abandoned.ï¿½
Southern California Gas Company | N | RIVERSIDE | BANNING | 2021-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PARDEE HOMES | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | New constructionhit service wbackhoe.ï¿½ No USA Ticket
Southern California Gas Company | N | RIVERSIDE | BANNING | 2021-10-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GEMP POWER SYSTEMS | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A retaining wall was being installed along the property line near the 2 inch PLA main. During the installation process, 0.5 inch rebar was driven into the ground and struck the SCG main.ï¿½
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2021-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CHERRY VALLEY WATER | BEAUMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | water department was working on a line when they hit our service trying to expose theirs.
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2021-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ORTIZ ENTERPRISES INC | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, contractor damaged 0.5 inch plastic service while digging to start building a wall around yard
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2021-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 19 |  | SECC CABLE COMMUNICATIONS | CHINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor using radial arm saw cutting out a cable box chopped 0.5 feet service in half.ï¿½ No USAï¿½
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2021-12-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC SHORES MASONRY | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Contractor hit 0.5 inch IPS service while jack hamerring hole for new fence posts
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2021-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WESTERN CONSTRUCTION SPECIALISTS | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | renter of the property stated that a few years back the septic tank was replaced by the homeownerï¿½in the excate location of the damage. over the years they had smelled gas but never thought to call it in. after so long the smell started to give them headaches and that is when the call was finally made to use to come check out the oderent complaint. during the investigation we found a prior damage which was repaired by the septic contractor which had failed causing the leak.
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2021-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOSE GONZALEZ | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor decided to cut the service out of his way while grading.
Southern California Gas Company | N | RIVERSIDE | BERMUDA DUNES | 2021-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL PACIFIC ELECTRIC | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor punctured gas line while probing for it. Contractor did not have their own USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | BLYTHE | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | BLYTHE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner was hand digging to install sewer and hit the service line.
Southern California Gas Company | N | RIVERSIDE | BLYTHE | 2021-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LA VERNE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner was hand digging to replace irrigation and water lines and hit the service line with a shovel.
Southern California Gas Company | N | RIVERSIDE | BLYTHE | 2021-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RONALD EDWARDS | BANNING | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to install sewer line hit the service line with a pick axe.
Southern California Gas Company | N | RIVERSIDE | CABAZON | 2021-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ASPHALT | CYPRESS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Confusion by the locator due to many tickets in the area and the easement was not clear.ï¿½
Southern California Gas Company | N | RIVERSIDE | CABAZON | 2021-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | NA | CABAZON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hti service with backhoe fixing water lineï¿½
Southern California Gas Company | N | RIVERSIDE | CALIMESA | 2021-07-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | NA | CALIMESA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner hit service with trencher
Southern California Gas Company | N | RIVERSIDE | CALIMESA | 2021-07-19 | Third party excavation damage | Not Available | Polyethylene Pipe | Hand Tools | 0.5 | 315 | 300 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PRO ENGINEERING SERVICES | NA |  | N | Y | Yes | Yes | No | Yes | Yes | Yes | Yes | HP 10 main was struck due to mis mark Damaged wrap not leaking
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | PALM SPRINGS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner hired a contractor to plant a tree and during this process damaged a plastic gas service. The homeowner did not contact USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HYSELL POOL COMPANY | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The pool contractor damaged the plastic gas line while trenching. The pool contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2021-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TURN AROUND COMMUNICATIONS | WALNUT |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | USA NUMBER NOT PROVIDED, PER LCT USA TICKET WAS EXPIRED, AND OR RENEWED FOR REMARKING. CONTRACTOR DIGGING TO CLEAR PAVEMENT.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CONCRETE SOLUTIONS | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Concrete Solutions struck SCG service line with loader backhoe while grading yard to install pool for homeowner The contractor did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2021-03-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PL MASONRY | SAN CLEMENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service while trenching for a block wall. Contractor did not notify USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EMILIO LANDSCAPING 006116 | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor damaged the plastic service while excavating to remove a stump The contractor did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2021-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | COACHELLA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner failed to contact USA and damaged plastic service while removing a tree.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2021-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PACIFIC UTILITY INSTALLATION INC | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor damaged a plastic gas line while excavating with a mini excavator The contractor did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JACOBSON ENGINEERING CONSTRUCTION | THOUSAND PALMS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was potholing with a back hoe when they damaged a 2 inch plastic service The contractor did not hand expose and is fully responsible
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2021-02-09 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TBU INC | BEAUMONT | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to wait 48 hour time requirement and damaged 2 inch plastic main.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | OPTIMUM INC | BLOOMINGTON | CA | N | Y | Yes | Yes | No damage to SUOF. | Yes | No damage to SUOF. | Yes | No damage to SUOF. | The contractor damaged the plastic gas line while hand digging the SMC up for a gas service upsize. The contractor failed to protect facilities in place andï¿½hit it with a shovel, poking a hole in it. ï¿½
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-05-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AC SPRAGGINS ENGINEERING UNDERGROUND | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor failed to call USA and damaged main with backhoe.ï¿½
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | BIG BEN ENGINEERING | TUSTIN |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The Contractor damaged a plastic service while excavating to install a sewer line. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-06-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JURUPA COMMUNITY SERVICES | MIRA LOMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | contractor damaged unmarked gas facility while trenching to install electric conduit. contractor was excavating outside of deliniated area. contractor was asked to contact dig alert 811 when the scope of the job is changed so utilities can be marked to prevent injury or property damage. BB 6 25 21
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MDM CONSTRUCTION INC | SIMI VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Damage contractor struck 1 plastic stub while excavating for building footing Valid USA marks clear and accurate Contractor failed to pothole stub
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BIG BEAR POOL AND SPA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | damage repaired without incident
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TRINITY CUSTOM POOLS | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged unmarked gas facility while hand trenching to install gas line to backyard for pool. USA was not called. Contractor was asked to always call 811 2 days prior to any excavating to prevent injury and property damage. BB 5 4 21
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | THE AMAZON CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Workers struck the gas service with a pickaxe while trenching from the front house to a newly constructed back house Service was marked and previously exposed by workers ï¿½
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TAPIA S CONCRETE SERVICE | MENIFEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called by contractor. service was damaged by jack hammer being used as clay spade.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WEST END ENVIRONMENTAL SAMPLES | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | No | Valid USA contractor augured through plastic service workingï¿½outside of delineation No delineations were found near damage location work was being performed before legal start time
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DRILL SUB | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Workers struck service with a shovel while digging for irrigation. No USA.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-01-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 50 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 50 |  | SRG CONTRACTORS | NEWPORT BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged unmarked gas facility while excavating to repair driveway at new apartment complex. USA WAS NOT NOTIFIED. Contractor was asked to always notify USA811 2 working days prior to any excavating to prevent injury and property damage. BB 110.51
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-07-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | WILHELM ELECTRIC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | na
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-04-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GREEN BEE CONTRACTORS | NA |  | N | N | Yes | Yes | Yes | Yes | No damage to SUOF. | Yes | Yes | contractor was excavating for sewer with backhoeï¿½and damaged marked stubï¿½
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-05-06 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ETR probed through service during leak investigation.ï¿½
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-12-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VALVERDE CONSTRUCTION INC | SANTA FE SPRINGS |  | N | Y | Yes | Yes | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was trenching when the PLA service was damaged.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-12-10 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 4 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | W C C S INC | RANCHO CUCAMONGA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged unmarked gas facility while drilling to install a new light pole in new development. USA was not called. contractor onsite was asked to always notify USA 2 days prior to any excavating so utilities can be marked to prevent injury or property damage. BB 12 22 21
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-08-11 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PCG PACIFIC CONSTRUCTION GROUP | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party Contractor Damage no USA auger gouged 2 inch plastic service no leakage ï¿½
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TOWO ENTERPRISE INC | FULLERTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor failed to use caution while exposing gas line.ï¿½
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-08-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DING DAN SHAO | CORONA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging for irrigation near meter damaged gas service while cutting away roots with small shovel No USA
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-09-01 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | CITY OF JURUPA WATER CO | MIRA LOMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water company replacing service by splitting theï¿½service damaged the main Valid USA did not pothole
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-06-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ZUNIGA POOLS | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Workers building a pool struck the service with a shovel. No USA.ï¿½
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-08-16 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | JURUPA COMMUNITY SERVICES | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor Damage failed to pothole 2 PLA main valid USA marks clear and accurate ï¿½
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BCC CONTRACTING INC | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged unmarked gas facility while trenching for sewer in new development. USA was not notified. Contractor was asked to always contact 811 USA so utilities can mark facilities to prevent injury and property damage. BB 6 20.51
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | T WALKER | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner was removing tree stump Homeowner called in USA and the service was properly marked with paint and flags It appears the homeowner struck the 1 2 service with a shovel
Southern California Gas Company | N | RIVERSIDE | CORONA | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RANCHERS HOTEL BUILDERS | SPARKS | NV | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to notify USA and struck PLA service stub with backhoe.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2021-08-13 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC WEST UNDERGROUND | YUCAIPA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NPL damaged a cutback service STUB that was located off measurements NPL does their own locating and is fully responsible
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2021-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MARTIN ESPINOZA | DESERT HOT SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | "The contractor damaged a 2 inch plastic main by potholing with a backhoe.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2021-11-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | THOMPSON ELECTRIC | HESPERIA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Area of work not marked within the 30 inch radius of the pole replacement
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2021-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | DESERT HOT SPRINGS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging to install fence post when he hit the plastic gas line. Homeowner did not contact USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2021-07-08 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NPL | MIRA LOMA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | DESERT HOT SPRINGS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor damaged the plastic service while removing a tree. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2021-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | INDIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner was digging to install irrigation when the plastic gas line was damaged. The homeowner did not notify USA dig alert and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2021-12-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALMS UNDERGROUND | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was digging to install a cement slab with the damaged the plastic gas line. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2021-06-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 8 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ECO MASTER CORP | RANCHO MIRAGE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | The contractor wasï¿½grading to close toï¿½the 8 inch plastic main and sheared off a 2 inch high volume punch tee. The contractor was also working on an expired ticket and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 162 | 155 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MISSION SPRINGS WATER DISTRICT | DESERT HOT SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor damaged a high pressure service while excavating for water. The contractor was working on a expired USA ticket and is responsible.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WILSON BACKHOE SERVICE | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in. ESTRELLA CONSTRUCTION HIT SERVICE WITH BACKHOE,951 285 1687ï¿½
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | A F PLUMBING | DESERT HOT SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating to expose drainage pipeline to repair damaged 1 2 CTS service No USA notification
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2021-05-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 75 |  | MISSION SPRINGS WATER DISTRICT | DESERT HOT SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water Company Failed To Use Caution While Exposing Gas Line. Gas Line Marked As Plastic, Excavator Found Steel Line And Failed To Contact SCG For Verification Before Continuing Excavating And Damaged 2 Inch Pa Main
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | M J GRADING SERVICES | INDIO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | The contractor was grading and damaged a plastic gas service The contractor did have a USA but it was not valid and it hadn t been marked yet The contractor is fully responsible
Southern California Gas Company | N | RIVERSIDE | EASTVALE | 2021-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COLONIAL ELECTRIC INC | CHINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to notify USA and struck service.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-01-11 | Operator excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ACCESS GENERAL CONTRACTORS | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage 2party contractor GIPP hit 0.5 inch CTS with shovel. USA was called, markings were clear with yellow paint. Contractor hit within the delineated area.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-11-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 inch service damaged by shovel pick while digging for electrical new propertyï¿½
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JOHNSON JENNINGS | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage No USA
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-05-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AL ABBASI | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was diggingï¿½to repair sewer lateral and hit gas line with back hoe. Gas line was about 4 inch from the Sewer line.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MICHAEL HERBST | HEMET | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service was bent and damage by third party contractor when using backhoe. USA was called. ETD failed to correctly mark the service.ï¿½
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CITY OF HEMET WATER COMPANY | NA |  | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | HEMET | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Requested, Installing Fence Post
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | HEMET | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage Customer fail to call to updated USA ticket was expired Customer damage gas line when digging to install water linesï¿½
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | RCR CONSTRUCTION | JURUPA VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 2 CTS Service was hit by contractor installing fence postï¿½with post hole digger USA was not called
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | HEMET | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 inch gas service while handï¿½trenching to install electrical conduits for property owner. No Valid USA exist for address.ï¿½
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-08-30 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | A M ORTEGA | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | gas co contractor had air jetted into a bore hole and was hand digging with shovel looking for his air jet when he cut into the existing gas service while digging dirt had covered up the existing line and he lost track of where it was in the excavation
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | PACIFIC UTILITY INSTALLATION INC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor claims damage was done and covered up by hired laborer on 8 6 No USA available but correct markings present
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-07-21 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | JOHN GRIFFIN CONSTRUCTION | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was working near our gas line to uncover water sewage lines They were probing into the dirt and punctured 2 PE mainï¿½
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC UTILITY | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 2 CTS stub was damaged by 3rd party contractor while hand digging to expose the gas stub
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | HEMET | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowners uncle was digging to install yard drainage for backyard. Branch was damage by shovel from Homeowners uncle. No USA called.ï¿½
Southern California Gas Company | N | RIVERSIDE | HEMET | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | R B BACKHOE DUMP TRUCK SERVICE | WINCHESTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1 PE service with backhoe while trenching to install 4 conduitï¿½on 8 6 21 He performed his own repair using a Stab fitting ETD discovered damaged while completing a L M ticket on 8 10 21 USA was not called
Southern California Gas Company | N | RIVERSIDE | HOMELAND | 2021-12-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | RIVERSIDE COUNTY TRANSPORTATION | RIVERSIDE |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | worker digging out footing hit svc no USA called inï¿½
Southern California Gas Company | N | RIVERSIDE | HOMELAND | 2021-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Directional Drilling | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 100001 |  | 1 |  | DC DRILLING INC | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damage by 3rd party contractor hit service with bore drill. GIS and Map didï¿½ not indicate their was a service at the 31525.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2021-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DUNNS DESERT LANDSCAPE | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic service while trenching for drainage. Contractor did not notify USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2021-01-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AEE MASONRY | BERMUDA DUNES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was hand exposing gas service to verifyï¿½Depth and damaged service with shovel. Contractor was using another company feets USA and did not have one of their own.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2021-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | IMMACULATE MASONRY | COACHELLA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while excavating the service line was struck and damaged.ï¿½
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TIERRA SITE WORKS | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was grading when they damaged a plastic gas line. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2021-10-14 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JAMES A SHIRLEY CONSTRUCTION | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | "The Contractor damaged a mismarked plastic gas line while trenching to install a electrical conduit.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VAN DYKE | TWENTYNINE PALMS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Customer installing a sewer line.ï¿½No USA was requested
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GRAYCO ELECTRIC | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was digging with a pick axe for electric conduit when they damaged a gas line. The contractor did not have a USA ticket and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2021-12-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RG CONCRETE | PALM DESERT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 0.5 inch service with trencher. USA was not called.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROCIO BERUMEN | INDIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CJW CONTRACTOR | SAN JACINTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Nicked plastic service with a shovel while potholing for it. Facilities were located correctly an Contractor is fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-02-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CJW | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging right next two the 2 inch plastic main with a backhoe when it was struck. Gas facilities were located and marked correctly and contractor is fully responsible. ï¿½
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SCORPION BACKHOE | HEMET | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor dug before their USA 48 hour time requirement and damaged a plastic service The contactor is fully responsible
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BRIAN WESTLAKE LANDSCAPE | LA QUINTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor damaged the plastic gas service while digging for landscaping project. The contractor removed flags and failed to take care ofï¿½thier markings and protect the facilties in place.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HANDEL S POOL SERVICE | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged plastic service while trenching to install a pool gas line The contractor did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-07-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WALTON BROTHERS CJW | SAN JACINTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor damaged a 2 plastic main with a backhoe The contractor failed to protect facilities in place
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-09-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WALTON BROTHERS | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor damaged a 2 inch plastic main while grading The contractor did not notify USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-03-04 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | K HOVNANIAN HOMES | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor suspected to have damaged a gas line and was digging to find it. Contractor failed to contact USA and is fully responsible.ï¿½
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | INDIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging for the sewer line when they hit gas line. Homeowner failed to contact USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-04-26 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | INDIO WATER AUTHORITY | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor damaged the 2 inch plastic main while potholing. The facility was marked correctly and the contractor is fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CJW GENERAL CONTRACTING | SAN JACINTO | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor did not provide delineations and the Locater requested for them. The contractor hit the service for lot 42 while diggingï¿½at lot 43.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-02-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CJW GENERAL CONTRACTOR | SAN JACINTO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor dug before 48 hour time requirement and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ALMS UNDERGROUND CONSTRUCTION | CATHEDRAL CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged plastic service while potholing it, contractor is fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARELLANO LANDSCAPE | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was excavating to remove bushes and damaged a plastic gas line The contractor did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | A N POOLS | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-07-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DANIEL SALAZAR | THOUSAND PALMS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor damaged a plastic service with a shovel while excavating to remove a Palm Tree The excavator did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-09-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KARGENDA BUILDER | INDIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The contractor damaged a plastic gas line while trenching for sewer and admitted to the damage prevention analyst that the marks were removed during excavation The Contractor failed to maintain marks and is fully responsible
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CLASSIC POOL AND SPA | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic gas service with shovel while digging for pool gas line.ï¿½ Contractor failed to contact USA and is fully responsible. ï¿½ ï¿½
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MIGUEL OCON | INDIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner was digging to install a post and hit our plastic service The homeowner did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20001 |  |  | NA | BLACK GOLD BUILDERS GROUP INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service while trenching for sewer. The Contractorï¿½did not contact USA andï¿½is fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | INDIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner was digging up a fiscus tree when they damaged the plastic service The homeowner did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CERDA STEEL | COACHELLA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service while trenching, they did not contact USA andï¿½are fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | H7 CONTRACTING ENGINEERING | MURRIETA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor Hit stub that had already been exposed with aï¿½backhoe. Contractor admitted they knew where stub was at from potholing it. The Locaters marks were off but he didï¿½write inchPothole inch on curb due to no EM ball at end of stub and also marked the inchG inch on the curb.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HIGUERA S POOL | COACHELLA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor damaged the plastic service line while trenching for a pool line.ï¿½ The contractor did not notify USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALEX CARDNEAS CONSTRUCTION | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Recv online A1, Contractor hit service, new address, KB homesï¿½
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-01-12 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TBU INCORPORATED | BEAUMONT | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor damaged plastic main while hand digging. The contractor did not have a current USA and is fully responsible. Previous marks offsets found to have been covered by dirt. Most recent ticket expired 01072021
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JONES BROTHERS CONSTRUCTION | COACHELLA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | "GREG PETERS 3106299170 CALLED TO REPORT DAMAGED LINE WHILE DOING ELECTRICAL WORK WITH BACKHOE.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JONES BROS CONSTRUCTION | COACHELLA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The contractor Damaged a 2 plastic service that was not mapped on GIS and not in Service history
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-07-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JONES BROTHERS | COACHELLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor damaged a 2 plastic main while excavating with a backhoe The contractor failed to hand expose by hand and is fully responsible
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | T BILL | BEAUMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Damaged Plastic gas service while hand exposing it with a shovel. Facilitiesï¿½ were located correctly and contractor is fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HEGGE ELECTRICAL CONTRACTORS | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SOCALGAS Contractor Struck Gas service while potholing riser.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2021-08-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BELCO | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck properly marked 2 PLA main with mini excavator Contractor had said previously potholed and dug too deep
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2021-12-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DOWNEY CONST | REDLANDS |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging for irrigation. Damaged service with no USA
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2021-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | JURUPA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2021-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | JURUPA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage Homeowner was working near the gas line ï¿½with a saw in one hand he slipped causing damage to the service. NO current USA.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2021-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SAHION LORETO | JURUPA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2021-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | MIRA LOMA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging for drain line failed to notify USA and struck facilities.ï¿½
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2021-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HOME OWNER | JURUPA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Contractor performing soil sample testing dug into the service and did not hand expose prior to using hand auger tool.ï¿½
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2021-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BROWN SERVICES | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | .5 inch service was hit with shovel.ï¿½
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2021-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BORDEN EXCAVATING INC | CALIMESA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor broke our 0.5 inch pla service while digging trench for a water line
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2021-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROBERT SANDOVAL | JURUPA VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator failed to notify USA and struck service with backhoe.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2021-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | JURUPA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was trenching to install a sewer line when he struck our service with a shovel Home owner did not notify USA
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | JURUPA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner struck line digging in yard.ï¿½ No USA.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2021-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KARAKI WESTERN ESTATES | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to notify USA and struck end of main with mini excavator
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2021-01-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | D AMIGO MAINT CONST | CARLSBAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging a trench for the new gas station when they struck a 2 inch service.ï¿½
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2021-12-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SOCAL GAS | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber hit gas line with a shovel, performing plubing repairs
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2021-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CAMACHO S GARDENING | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor damaged the plastic gas line while grading The contractor did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2021-09-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | UNITED BROTHERS CONCRETE INC | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor damaged the plastic gas service while trenching with a mini excavator The contractor did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2021-10-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TBU INC | BEAUMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was just located the day prior. Contractor did not use caution while excavating footings.ï¿½
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2021-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CHICAS LANDSCAPING | COACHELLA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractorï¿½damaged plastic service while excavating for a water line. The Contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FELIX PLUMBING | COACHELLA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor is fully responsible."
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC WEST UNDERGROUND INC | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The contractor damaged a plastic stub while excavating for electric conduit. The locater did not mark this stub and was confused on where the excavator was going to dig the trench.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2021-10-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC WEST | YUCAIPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was damaged when contractor was boring . Mis mark by SCG . Spoke to employee.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2021-12-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LA HACIENDA NURSERY LANDSCAPE INC | INDIO |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.5 inch CTS service. Contractor failed to hand expose.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2021-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BOBCAT SERVICES | DESERT HOT SPRINGS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor damaged a plastic stub while excavating for sewer.ï¿½ The contractor did not notify USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LA QUINTA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service while digging to plant a new palm tree. Contractor failed to contact USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | T B U INC | BEAUMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew damage stub service while pot holing.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TBU INC | BEAUMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor David HerreraTBU admitted to removing flags during excavation. The contractor failed to maintain markings and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2021-03-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 100 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While third party contractor was digging to expose service to be abandoned a 4 inch Punch T cap was hit with a track hoe causing rupture and escaping of natural gas.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2021-03-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LAKE ELSINORE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner digging to repair leech line
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2021-12-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TRAVIS WOOLSEY | LAKE ELSINORE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA . Plumber was digging to replace sprinkler line
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2021-08-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LAKE ELSINORE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged by home owner and called in as a leak
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2021-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BROOK REDMOND SOCAL EARTHWORKS | COSTA MESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2021-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALLIED PLUS | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to pothole by hand prior to utilizing mechanical means
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | IOB INTERNATIONAL LINE BUILDERS | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage USA was called Marks were visible and correctly marked Contractor was tunneling into back and hit 1 2 service with the shovel Contractor failed to protected facility
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2021-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JOSE AGUILAR | LAKE ELSINORE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service while trying to repair broken water line.ï¿½
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC UTILITY INSALATION INC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | altered service to repair leakï¿½
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2021-09-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | PACIFIC UTILITY INSTALLATION | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 2 P main with back hoe prior to exposing gas main Dug prior to USA ticket being valid
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HOME OWNER | LAKE ELSINORE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing fence with post hole digger called usa after service was hit
Southern California Gas Company | N | RIVERSIDE | MECCA | 2021-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | MECCA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged plastic service while trenching for sewer.ï¿½The homeownerï¿½did not notify USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JIMMY LOPEZ | MENIFEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner had valid USA with accurate marks and struck service hand digging.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | stub damaged and folded back and taped than found during trench inspection
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | stub was hit and folded over than found during trench inspection
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-12-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC UTILITIES | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival crew found 0.5 inch plastic service had been damage.ï¿½ It appeared to have been pulled and crew found service pinched with vice scrips.ï¿½ No one on scene, but it appeared they working to removeï¿½tree.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-04-26 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COLONIAL ELECTRIC | NA |  | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party damage. 2 inch PE main was hit with trencher. Main was previously marked, contractor was aware of the marks. Failed to pothole.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-05-17 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LYLE PARKS JR CONSTRUCTION | ANAHEIM | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Developer had secured steel plate over SCG facilities with a metal stake. They disregarded the yellow main marks next to stake placement causing damage to leak. Damage occurred on 5 15 but was not reported until 5 17 am.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NORSTAR | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damage 3rd party hit 0.75 steel service with backhoe. USA was called. Epochfield and service history was incorrect causing a mismark.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LC PAVING | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage Third party contractor hit 0.5 inch coupling with shovel.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NONE | MENIFEE |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor working on street improvement. Contractor was grading street and damaged service.ï¿½
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SOCALEDISON | MENIFEE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 0.5 inch cts service was hit with auger. Service not marked. 2 risers at this location, not mapped in GIS. Locator marked 1 of them.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-07-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MURRIETA DEVELOPMENT | TEMECULA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating to install new sewer line when he struck the 4 PE main He said that the main was not in there plans USA was expired
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-07-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PACIFIC WEST UNDERGROUND | YUCAIPA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating to find the end of main and damaged the 2 PE main with backhoe USA was not called They knew where the end of the main was located because they had it staked out with a conduit
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JAMES MCMAN INC | MARCH AIR RESERVE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damage Third party contractor hit the service line contractor indicating he thought the service was abandoned The ETD stated in his remarks that the area of excavation was not delineated ETD tried several time to call the number on the ticket The address given was for another location GIS shows elsewhere with no conflict The facilities not mapped in GIS discrepancies in service history
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-02-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LENNAR HOMES | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damage at an unknown time frame. Unknown if damage was caused after stub install or after stub was extended.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | GJ GENTRY GENERAL | UPLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not have a USA, working on widening the street grading
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CHARLES MERRIAM | UPLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage No USA third party damage was hand digging and hit service with shovel
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-09-27 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | VISTA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 2 P main caused by third party contractor with shovel Contractor did not provide delineation for their work site Started excavating before Dig Alert ticket was valid
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL WEST LANDSCAPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA notification was made.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2021-03-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MERITAGE HOMES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No usa called prior to excavating
Southern California Gas Company | N | RIVERSIDE | MIRA LOMA | 2021-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | LARRY EKROTE | RANCHO CUCAMONGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hitline, no usa . Crew arrived and control release of gas . Explain to contractor the importance of 811
Southern California Gas Company | N | RIVERSIDE | MIRA LOMA | 2021-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | F M POOL CONSTRUCTION INC | JURUPA VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while excavating contractor struck service
Southern California Gas Company | N | RIVERSIDE | MIRA LOMA | 2021-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DAVID RODRIGUEZ | JURUPA VALLEY |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractors excavating footing for wall with no valid USA ticket struck unmarked 1 inch PLA svc with shovel
Southern California Gas Company | N | RIVERSIDE | MIRA LOMA | 2021-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | MIRA LOMA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging without USA ticket struck PLA service.
Southern California Gas Company | N | RIVERSIDE | MIRA LOMA | 2021-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HERMAN WISAKER | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ALL gas lines were marked correctly Contractor was digging to install post and struck houseline ï¿½
Southern California Gas Company | N | RIVERSIDE | MIRA LOMA | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FRIEND OF HOME OWNER | COVINA | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Struck our service while digging a trench for a line in their front yard ï¿½
Southern California Gas Company | N | RIVERSIDE | MIRA LOMA | 2021-09-08 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 30 |  | OPTIMUM INC | BLOOMINGTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not pothole.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOSE CARRERA JR | MORENO VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging up lines for sprinkler system Used saw to cut out tree roots and hit 1 2 pe service
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HYBRID POWER ELECTRIC INC | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 24 |  | GREEN PERSPECTIVE | SAN MARCOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Damaged 1 inch pe service with trencher. Contractor dug out of the delineated area.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JESUS VEGA | MORENO VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner failed to notify USA and struck service with pickaxe while digging for electric line.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | INTERNATIONAL LINE BUILDERS INC | JURUPA VALLEY | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | damage 3rd party was excavating a hole for accubore when they hit our 0.5 cts line with a shovel. valid USA clearly marked out.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OC CONCRETE | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party trenching company was trenching for a dry utility and struck our 0.50 ips gas stub. no usa locates where on site in the work area.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JAVIER TREE SERVICES LANDSCAPING | MORENO VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor replacing water main struck our plastic service line while digging.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-06-07 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | TK CONSTRUCTION | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working for local water company was potholing to install new water main when contractor damaged main with a shovel sharp shooter. Contractor has previously pothole gas main in other locations on the street, USA gas marks were accurate.ï¿½
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TK CONSTRUCTION | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 2 CTS service damaged by 3rd party contractor as he was trenching with backhoe to install water main
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | PRO WATER ENGINEERING | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2 inch PE main was damaged by backhoe. USA ticket was called in and it was marked correctly. Contractor failed to pothole.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-02-08 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SPRINT ELECTRIC INC | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 2 inch PE main by 3rd party contractor. Main was hit with auger. No active USA Ticket.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITY OF MORENO PUBLIC WORKS | MORENO VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Damaged 1 inch pe service by 3rd party contractor when installing a ground stake for hardscaping. USA was expired. Marks had been removed. Failed to pothole.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-09-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PREMIER PLUMBING CO | NA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating to expose sewer lateral when he struck 1 2 IPS service with EFV Damaged occurred on 9 27 21 and was not called in till the next day by the inspector USA was not notified
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AMERICAN WEST RESTORATIONS | MORENO VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party employee of home owners insurance company was digging a new trench for an electric line when he struck our 0.50 ips gas service. no USA was called in.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | MORENO VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Did not notify USA The contractor was grading and hit our service without a USA ticket
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TK CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was trenching to install Storm drain when the trench collapsed damaging 1 2 CTS service
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | LESLIE SMITH | MORENO VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner working in yard struck service with shovel ï¿½ Homeowner was told about 811 to call before you dig
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HYBRID POWER ELECTRIC | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was cleaning out trench when he grazed the 1 2 CTS service damaging it USA was not called
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-08-03 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SOCALGAS | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG employee was preforming a leak investigation for SCG during that investigation he used an impacto bar to place near the main and ended up going through the main
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | COREY DENNY | MORENO VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Valid USA from homeowner and contractor. Contractor damaged 0.5 inch CTS Service while hand excavating to fence pillar.ï¿½
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | MORENO VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging for sewer line install
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2021-02-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | PRO WATER ENGINEERING INC | NUEVO | CA | N | N | Yes | Yes | Yes | Yes | No damage to SUOF. | Yes | Yes | 2 inch PE main was hit by 3rd party contractor with backhoe. Main was marked correctly, marks visible. Contractor failed to hand expose.
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DENISE SOLEK | MURRIETA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home Owner did not call USA
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DAVIS TRENCHING | YUCAIPA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damge thrid party contractor hit serivce with trencher No USA called
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2021-10-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CONSTRUCT AND MAINTAIN CORP | LAGUNA HILLS | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | home owner was digging to run a new line and exposedï¿½ï¿½the serviceï¿½ 3 days ago the occupant refused to give any information
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2021-02-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RESTAD | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | failed to hand expose prior to using mechanical means
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2021-03-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FAIRWAY LANDSCAPING | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA requested, customer digging to install irrigation
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2021-04-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FAIRWAY LANDSCAPING IRRIGATION | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit gas line with backhoe while digging for irrigation
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2021-03-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | INFINITY PLUMBING DESIGNS INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | backhoe operator failed to delineate and pothole by hand prior to using mechanical means and damaged 2 inch pem
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2021-02-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20001 |  | 109 |  | PACIFIC UTILITY INSTALLATION | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | gas line was struck outside of dilineated area
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2021-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ONARCH INC | RIALTO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage Third Party contractor hit 2 inch service with backhoe. USA was cleared marks were visible and clear. Contractor failed to maintain to protected our line
Southern California Gas Company | N | RIVERSIDE | NORCO | 2021-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TRINITY CONSTRUCTION | CEDAR GLEN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service pulled but not broken by water company. During investigation crew found code 3 leak on service and clamped it.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2021-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | FELIPE LEYVA | NORCO |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor installing sewer hit stub with backhoe
Southern California Gas Company | N | RIVERSIDE | NORCO | 2021-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TRINITY | CEDAR GLEN | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor building complex drove wood stake through neighbors service
Southern California Gas Company | N | RIVERSIDE | NORCO | 2021-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PLUMBING PROS | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 Party damage with a excavator service was mark correctlyï¿½ it was poor digging on the contractor.
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2021-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NUEVO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging to repair sewer line with shovel
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2021-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TWO BROTHERS SEPTIC TANK SERVICES | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage occurred on public alley. No delineation mark or USA called in for alley or back of address 10401 Washington Blvd.
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2021-06-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage Homeowner was hand digging to install drainage pipe and hit service. USA was mark correctly and visible. Homeowner failed to maintain clearance and protected gas line when excavating.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | C HUGHES CONSTRUCTION | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was digging for a foundation when they damaged the plastic service line The contractor did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-10-30 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TODD SMITH | PALM DESERT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit 0.5 inch serviceï¿½gas line with a shovel.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-12-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LC PAVING | ESCONDIDO |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor Damaged a incorrectly marked gas line while digging to install a water pipeline.ï¿½ The locater got his best signal indicating it to be a branch, and GIS and Service history also calls it a branch. ï¿½
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SANCHEZ LANDSCAPE CONTRACTORS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor that was digging for irrigation line hit plastic gas service. The contractor failed to notify USA and is fully responsible. ï¿½
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CONSERVE LANDSCAPING | THOUSAND PALMS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor hit the riser with a vehicle while grading a dirt lot. The contractor also did not have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-08-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AC PROFESSIONAL SERVICES | SAN JACINTO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was digging to install electrical conduit when they damaged a plastic gas stub The contractor did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-10-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AC PROFESSIONAL ELECTRIC | SAN JACINTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ï¿½
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COCHRAN COMMUNICATIONS CONSTRUCTION INC | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic service while digging to install a communications box. Contractor failed to contact USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | INDIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging for irrigation and hit the service line.ï¿½ Beto Aranda 7602007727. doing work for homeowner
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GMI LANDSCAPING | THOUSAND PALMS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas Co employeeï¿½skipped this service while locating and markingï¿½out the work area.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-01-18 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | DOWNING CONSTRUCTION | REDLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Valid USA, however marks removed by Contractor via daily street sweeping. Bore overshot proposed location and hit 2 inch main behind water box.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-08-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC WEST UNDERGROUND | YUCAIPA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit 2 plastic main while exposing gas with backhoe No valid USA ticket or delineation was found were the damage occurred
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-10-21 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LIPPERT CONSTRUCTION INC | LA QUINTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service hit by shovel, no USA
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-09-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15001 |  |  | NA | PIERRE LANDSCAPE | BALDWIN PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | This damage was discovered after the fact The contractor was digging with a mini excavator to install irrigation and damaged inactive plastic main and service in multiple spots The contractor did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LIPPERT CONSTRUCTION | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor was grading and failed to hand expose utility beforehand. The contractor damaged the 2 inch plastic main and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | KINDNESS GENERAL CONTRACTORS LLC | CYPRESS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While excavating for water service contractor hit Gas Co service stub.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DESERT WATER AGENCY | PALM SPRINGS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged miss marked gas service. The palm Desert Management Team determined no wire at riser at 1250 Rosaritoï¿½and 1255 Rosarito , ETD hooked up to 1215 Rosarito and picked up signal over water service. ETD was instructed in the future to utilize contractor to pot hole, using measurements, if all else fails utilize Gas Company crew to pot hole.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HERNANDEZ CONSTRUCTION | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA requested contractor was remodeling and damaged the gasline
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DESERT WATER AGENCY | PALM SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor excavating through driveway and damaged the gas service
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-04-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HERMAN WEISSKER | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 2 inch plastic main that was not marked by locater.ï¿½ The Measurements in GIS were incorrect and did not show a plastic main locater could not locate due to this.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-05-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MACIAS EQUIPMENT | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor damaged the plastic service while excavating. The contractor didn feett have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | DESERT PRESTIGE METAL IRON | THOUSAND PALMS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was digging to install a post for a iron rod gate when they damaged the plastic gas line The contractor did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HYDE ELECTRIC | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ï¿½"
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SOS PLUMBING | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was digging to repair gas houseline when they damaged the SCG gas line The contractor did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 8 |  | HERMAN WEISSKER | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The contractor damaged a plastic gas line while digging. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RIGO L LANDSCAPING | DESERT HOT SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service while planting a tree. Contractor failed to contact USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-06-08 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DESERT ELITE ELECTRIC | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor Desert Elite Electric hit a 2 inch IPS main with a shovel hand digging when trying to expose it to trench for a new gas service.ï¿½
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RAPID PLUMBING | CULVER CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor cutï¿½a plastic gas service while cutting a irrigation line out ofï¿½the way. The contractor did not notify USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LEO HERNANDEZ | PALM SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was digging to install a new fence when he damaged a gas line The contractor did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DESERT ELECTRIC ELITE UNDERGROUND | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor failed to pothole plastic service and damaged it with a mini excavator. The contractor also dug before the 48 hour time requirement. ï¿½
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SOUTH WEST PLUMBING | THOUSAND PALMS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The Contractor damaged a 0.5 inch plastic line thinking no gas was within the delineation. A inchNO SCG inch mark was present in the delineation.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-08-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PACIFIC WEST UNDERGROUND | YUCAIPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2 plastic main damage with backhoe by third party contractor when exposing electrical service main gas in a new development site Valid USA ticket marked correctly
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC WORKS UNDERGROUND | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Pacific underground works was digging to install electrical conduit and hit a gas stub Pacific Underground failed to maintain their marks and are fully responsible
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC WEST UNDERGROUND INC | YUCAIPA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was potholing utilities when they damaged the plastic gas service. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | STEEN BOJSEN MOLLEN | PALM SPRINGS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | WHILE EXCAVATING FOR SEWER SLIVE PLA SERVICE WAS STRUCK. EXCAVATOR FAILED TO NOTIFY USA
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JERRY FISHER CEMENT INC | PALM SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor admitted to the Damage prevention Analyst to removing the flags and not putting them back The contractor failed to maintain their marks and is fully responsible
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | BORDEN EXCAVATING INC | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor did not pothole marked service The contractor damaged the plastic service with the backhoe while digging to install a water pipeline
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GILBERTO S MAINTENANCE | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Theï¿½Contractorï¿½damaged a plastic gas line while excavating to remove a tree.ï¿½ The contractor did not notify USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | REDS CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor damaged the plastic gas line while grading the property The contractor did not have a USA and is fully responsible
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GENERAL AC AND PLUMBING | THOUSAND PALMS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. While attempting to cut sewer line to remove clog, gas service was cut by sawzall.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EXCEPTIONAL LANDSCAPING SERVICE | DESERT HOT SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors damaged plastic service while landscaping. The contractor did not contact USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ANGELOS CONCRETE | PALM SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Damaged steel service while grading to install a carport. Contractor failed to call USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FARLEY INTERLOCKING PAVERS | PALM DESERT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Failed To Use Caution While Exposing Gas Line, Demo Driveway
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-12-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CERDA STEEL INC | COACHELLA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-07-17 | Third party excavation damage | Meter | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ALPHLA ELECTRIC | RANCHO MIRAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Alpha Electric failed to call USA damaged service while excavating to install underground electric conduit
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MCGEE CONSTRUCTION INC | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor drove a stake through a 1 inch IPS plastic service. The contractor did not have a USA and is fully responsible. ï¿½
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LAGUNA FALLS POOLS AND SPA | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor damaged the gas service while digging for a pool. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LOCKMILLER VENTURES | MENIFEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging trench for electric with a backhoe and struck our gas 1 2 service no usa markings or flags were noticeable on the jobsite and when asked for a usa ticket no one could provide us with the number
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-02-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SO CAL UNDERGROUND INC | WINCHESTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged service with backhoe. Failed to pothole. marks visible. USA ticket that was given was invalid.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | EMERY PLUMBING | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contactor was digging for sewer lateral using a backhoe when they struck our gas main. no USA ticket was called in.ï¿½
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SOCAL UNDERGROUND | WINCHESTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage No USA . Third party contractors left scene before we arrived
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-02-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC COMMUNITIES | MENIFEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service with excavator. Failed to pothole. Marks visible.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JAMES SAVOY | PERRIS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner struck PE service line while attempting to build fence on propert
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | EDDIE PEREZ | PERRIS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Riser buried by previous land owner Current land was told during sell no utilities on property
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALEXANDER LOPEZ | MENIFEE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with no valid USA ticket struck PLA service with a shovel
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-05-27 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | NA | ROMOLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 2 inch PE main while hand digging. USA was called and marked correctly. He exposed 2 inch PA main that was abandoned and thought that was the main.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-01-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 11 |  | HOME OWNER | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner excavating with Backhoe and did not call USA
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-08-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 8 |  | NA | PERRIS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 PE main damaged by homeowner while trenching to install water service USA not called
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 8 |  | PACIFIC COMMUNITIES | MENIFEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage third party contractor hit service with back hole. Marks were clear 6 inches from the service.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RIVAS PEREZ CLEAN UP | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer damaged a 0.5 inch service with backhoe while trenching to install water.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | INTERNATIONAL LINE BUILDERS ILB | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party was digging trench for edison when they struck our 1 2 gas service After investigation we found our service was mis marked
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | ROSIECROZA GMAIL COM | PERRIS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Pauley Construction crew3rd party contractor called socalgas stating, they smelled gas while backfilling excavation near riser. Contractor crew recently moved communications box in front of the riser where the leak was at.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JULIO MARIN | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage Thirdparty contractor hit service with a backhoe when digging the foundation for a new building. The contractor did not polehole. USA marks were visible.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SO CAL UNDERGROUND | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor struck our gas line with a trencher, NO USA ticket.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOUBLE D PIPELINE | TEMECULA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | water company hit our gas service 14 from our marks gas marks were in line with the meter 10 behind curb service came out from the meter at an angle
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-03-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NP MECHANICAL CO | CORONA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Damge 3rd Party contractor hit service with backhoe. USA was current. Failed to protect faclities
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2021-10-12 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PRECI CRUZ | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping digging trench on the private property near the gas MSAï¿½did not request USA. Joel Fierro says he knows about USA service but saw marking in the street and sidewalk and though they were clear of gas service.ï¿½
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2021-12-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GREENBEE | PERRIS |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR FAILED TO USE CAUTION WHILE EXPOSING THE GAS LINE, DIGGING FOR CABLE LINE
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2021-05-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ECONOMY TREE AND CRANE INC | THOUSAND PALMS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor hit a plastic service while digging with a backhoe to plant a tree. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | RANCHO MIRAGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was digging to fix a sewer line and cut the gas line in half. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2021-02-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | AQUATERRA POOL CONSTRUCITON | RANCHO MIRAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no USA was requested, contractor digging for electrical conduit
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | OLIVER GRADING | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor damaged a plastic gas line while excavating for a drain line. The contractor did not notify USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2021-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | QUALCON | RANCHO MIRAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was digging to install a electrical conduit and damaged a plastic gas line.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | AM ORTEGA | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to find sewage pipe.ï¿½ Contractor said No USA called because emergency repair job.ï¿½ Hit service line with shovel.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2021-10-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JOSE LUIS LUCAS | INDIO | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-08-30 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | BLANCO CONSTRUCTION INC | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Balnco Construction failed to maintain the marks from their USA ticket and struck a 3 main ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CITY OF RIVERSIDE WATER COMPANY | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CITY OF RIVERSIDE | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water Company Pulling Line And Pulled On The Gas Service, Failed To Use Caution While Working Near Gas Line
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-07-08 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 150 |  | CITY OF RIVERSIDE | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | City workers installing guard rail post did not notify USA and damaged 2 PLA Main with an auger ï¿½ Resulting in street closures and outages
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ACCESS GENERAL CONTRACTOR | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOSE ENCISO STEEL PLUMBING | SAN DIMAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with no USA and struck PLA Service
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-01-11 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ICON GENERAL CONTRACTOR | REDLANDS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor digging on expired USA ticket.ï¿½ Contractor cut into live service with hacksaw to get it out of theï¿½way causing damage.ï¿½ Marks still visible for service.ï¿½ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JAMES MOBLEY | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with hand tools
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HECTOR HERNANDEZ | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit 1 2 pla service while digging to install a fence post No USA
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | OPTIMUM INC | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was boring to install a fiber line when they struck a .5 inch stub 5 feet off the main. The stub is not on GIS nor is there service history for it. The stub was abandoned at the SMC.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 90 |  | HCI INC | NORCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor struck a service thatï¿½was not marked due to not mapped and service history shows coming from another street.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | DAVES SONS CONTRACTORS | WILDOMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging on property failed to call USA.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging a fence post when they struck our service USA was not called
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CITY OF RIVERSIDE | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-02-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor struck 2 inch Pla stub while grading.ï¿½ Contractor only notified USA after hitting stub same day.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MURRIETA DEVELOPMENT COMPANY | TEMECULA | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | NA
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RANCHO WEST LANDSCAPE | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service truck with shovel by landscapers
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GREENBEE CONCRETE CONSTRUCTION | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service was struck while excavating for a driveway No USA ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TRI COUNTY DEVELOPMENT | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Inactive service was marked incorrectly.ï¿½ Marks where 4 feet off and EE was counseled to use all available resources.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TRI COUNTY DEVELOPMENT CONSTRUCTION CO | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to expose correctly marked service line and struck with shovel hand digging.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-04-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SALVADORE CANO | DIAMOND BAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to notify USA and struck 2 inch PLA service.ï¿½ Contractor tied service back and was advised to notify USA and to not try and get under control again.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-04-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 7 |  | BURGE CORPORATION | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging To Install Electrical Conduit, Failed To Use Caution While Exposing Gas Line
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITY OF RIVERSIDE | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party damage . Crew arrived and control release of gas .
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JPI | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While hand exposing potholing contractor struck service line with probe ï¿½ Marks were accurate and visible
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | OPTIMUM INC | BLOOMINGTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor was boring, hit a unmarked gas line
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-05-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RL CLOTHEARTHY CONSTRUCTION | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck correctly marked 2 inchPLA main with a mini ex.ï¿½ Contractor also had main exposed approx 20 feet away.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BLUE WAVE POOL | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to notify USA and Struck service with shovel hand digging.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CP CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck service while excavating for sewer.ï¿½ USA valid and marks visible.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-07-15 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CITY OF RIVERSIDE WATER DEPT | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator marked End of main where signal was lost ï¿½ Main was 10 past markings and struck with probe
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JESSE SAAVEDRA | RIVERSIDE |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was digging an electrical line to the side of his house when he struck his gas service with a shovel.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-06-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 5 |  | GJ GENTRY | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor expose abandonedï¿½ line and failed to read marking stating line was PLA and did not pothole over accurate markings.ï¿½ They struck a PLA main with a backhoe.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-08-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 18 |  | RIVERISIDE PUBLIC UTILITIES | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water company said confused about marks and proceeded to dig anyway and struck 2 Pla Main ï¿½ Marks on the ground said to pothole to verify and excavator should have hand exposed to verify and call back for clarifications
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damaged 0.5 inch CTS plastic service with jackhammer digging to install fence post.ï¿½ No notification made to 811 Dig alert.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-02-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ROBERT MENDOZA | RIVERSIDE | CA | N | N | Yes | Yes | Yes | Yes | No damage to SUOF. | Yes | Yes | Contractor hand digging to expose gas line for an alteration struck service with shovel.ï¿½ Marks visible and accurate.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BERKSHIRE HATHAWAY | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavation Damage NO USA
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-04-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hand digging in yard did not notify USA and struck service.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-03-31 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | TRIPPLE J DRILLING INC | PERRIS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Per LCT Brian Allan third party running conduit hit plastic main. USA current.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-11-15 | Third party excavation damage | Riser | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MOHAAMAD SHAATH | RIVERSIDE |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Valid USA, Contractor was digging trench with shovel and hit gas service. Trenching was for a sewer lateral.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | TURNAROUND COMMUNICATION | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for Spectrum hit 1 2 plastic service No valid USA on file ~K Rodriguez~
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-06-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Customer Digging For Water Service And Struck Pla Service.ï¿½ Service Mislocated Due To Insert And Weak Signal.ï¿½ Locator Used All Resources To Locate And Was 6 Feet Off.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-05-11 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CITY OF RIVERSIDE | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While probing to locate the 2 inch plastic gasline, They City of Riverside punctured the main.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CABLE TECH | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Potholing service and struck with shovel hand digging.ï¿½ USA valid and marks accurate.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CABLE TECH | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hand exposing marked PLA service line and struck with shovel.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GRIFFITH COMPANY | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor stated they damaged service while exposing by hand.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2021-02-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 inch stub digging for dry utilities. USA was not called.
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2021-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TBU | BEAUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 inch IPS stub service with the backhoe. USA was not called
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2021-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CORNELAO BUSQUES | MORENO VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew digging to install conduits hit 1 2 cts service w a shovel No valid USA ~K Rodriguez~
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2021-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CORNELIO BOSQUEZ | SAN JACINTO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Workers digging trench to install electrical conduits hit 1 2 service w a shovel No valid USA ~K Rodriguez~
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2021-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | SOBOBA INDIAN TRIBE PUBLIC WORKS | SAN JACINTO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Requested, Contractor Digging For Electric Pole
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2021-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PREMIER PLUMBING COMPANY | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | service was damaged a week ago while digging for sewer. contractor had bent the pipe over and had it held with duct tape. damage was found by KB rep who called it in.
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Material not known | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JEFF RAHMAN | HEMET | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | contractor was digging a excavation for a electric vault outside of our USA marks when he struck our 2 ips service
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2021-03-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC WEST DEVELOPMENT SOCALUNDERGROUND | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Trevor Preston no USA third party digging with backhoe installingï¿½landscape irrigation.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2021-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | KEVIN HARRIS | TEMECULA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working for City of LA to install new sewer lines ended up hitting 0.5 inch IPS service with backhoe. 3rd party contractor did not hand dig line to expose line.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2021-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VALLEY PIPELINE INC | LA QUINTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | third party contractor did not pay attention to the location marks and hit our 2 inch plastic service with a backhoe.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2021-04-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | TEMECULA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Builder homeowner had his son operating a mini backhoe digging a trench for drainage and or electrical conduits when 1 inch PE service was hit. Owner stated he knew it was there and forgot to inform his son of the presence of the line. I told Joe Gramatico to call for USA and he said he knew where everything was and did not need it.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GARRETT CONSTRUCTION | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While diggingï¿½out a previously excavated and exposed service. Contractor damages a 0.5 inch service line. Unsafe digging directly over service line.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2021-09-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | EASTERN MUNICIPAL WATER DISTRICT | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 2 P main hit by third party contractor Did not hand expose Valid USA with visible and accurate gas marks
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MURRIETA DEVELOPMENT | TEMECULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Landscape crew damaged service with shovel.ï¿½ Damageï¿½was tapped upon crew arrival. USA ticket had expiredï¿½
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was installing utility line when gas line was struck with round point shovel, usa marks were visible.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2021-10-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | UNITED BACKHOE SERVICE INC | CLAREMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Mini excavator hit 1 inch service line contractor assumed service line ran in different directionï¿½
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | 3T FENCE | WILDOMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | DamageUSA not notified 3rd party contactor damage service when using posthole digger for a fence.
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2021-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | WILDOMAR | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service hit with shovel no usa
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2021-07-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JMI CONTRACTING | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage third party contractor damage 2 main with a backhoe Main was exposed and USA marks were visible No current USA was called
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2021-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | INTERNATIONAL LINE BUILDERS | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2021-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PRO ENERGY CONTRACTED BY SCE | REDLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damage thirdparty contractor hit 0.5 inch service. The USA was current. ETD failed to mark the service correctly.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2021-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JDS PLUMBING | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch CTS service was damaged by excavator. Service was marked correctly. Contractor failed to hand expose the gas service.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2021-08-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PLATINUM LANDSCAPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage USA not notified Three party contractor hit service with mini excavator
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2021-04-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BEAZER HOMES | WINCHESTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party excavator was digging trench for conduit when they hit our 2 feet feet gas main. crew dug to containment hole to squeeze main and made repairs.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2021-06-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | KANA PIPELINE INC | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 0.5 inch IPS service damaged by 3rd party contractor. Failed to call for USA for that work area.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2021-06-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging trench for new sewer lateral when he struck our 4 feet feet gas main. no usa ticket was called in.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALCORN FENCE COMPANY | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | failure to pothole , contractor was maintaining marks, they also failed to call in for a remark.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2021-07-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | H7 CONTRACT ENGINEERING INC | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage third party contractor hit stub with hand tools No USA
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2021-06-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DSP ELECTRIC | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA 3rd party contractor damage 2 inch PE stub service with trencher to install street light conduct.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2021-07-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  | 0 |  | PAULEY CONSTRUCTION | WINCHESTER | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | On 7-14-2021, a third-party contractor damaged a 2-inch plastic gas service with a mini-excavator between Washington Street and Shrimp Lane in Winchester, CA, when excavating to install communication conduits. Crew responded and controlled the release of gas and made permanent repairs by replacing a section of the main. On 07/12/21 ETD, David Foley indicated on Dig Alert ticket A211930829 ?No scg.? After supervision investigated deeper into the ticket, GIS doesn?t show a main, and there is no current Service History. The investigation of the incident showed there was no valid USA ticket for the contractor. The Dig Alert ticket for the area the damage occurred was not valid until 07/14/21 at 5:01 pm.
Southern California Gas Company | N | SAN BERNARDINO | ARROWBEAR | 2021-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LEE JAMES | RUNNING SPRINGS |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit our 1 inch service line with
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2021-03-25 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CURTIS DRILLING CO | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | There was a current ticket for Baja Construction damaging party was Curtis Drilling Co. they did not have ticket in their name, no valid USA ticket.
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2021-02-03 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NPL | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas svcï¿½struck with pilot bore bit while boring in 2 inch PEM.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2021-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JUAN TORRES | LA PUENTE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MISSION PALLETS | FONTANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while contractor was performing a building demolition they damage our 0.75 inch steel service, no USA called in for the address job site.
Southern California Gas Company | N | SAN BERNARDINO | CEDAR GLEN | 2021-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 0 | 0 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | SAN BERNARDINO | CEDAR GLEN | 2021-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | PAR ELECTRICAL CONTRACTORS | LAKE ARROWHEAD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | There Was A USA, It Was Mismarked. Contractor Digging To Install Anchors For Electrc Telephone Pole.ï¿½ï¿½
Southern California Gas Company | N | SAN BERNARDINO | CEDAR GLEN | 2021-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CAL TRANS | LAKE ARROWHEAD |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, crew was told by their boss that it was ok to dig and that there was no lines in the ground. Damaged 0.5 inch IPS while trenching
Southern California Gas Company | N | SAN BERNARDINO | CEDARPINES PARK | 2021-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GREG GILES | CEDARPINES PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit half inch plastic while digging up sewer. No USA
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-01-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | APJV ELECTRIC | MORENO VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Damage, contractor hit 1 inch plastic service with trencher, valid USA, marks visible and accurate. Contractor failed to hand expose service.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CHINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was excavating septic tank and struck gas service in private property. No USA called
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | CHINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit plastic service with post hole digger, no USA.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FODDRILL CONSTRUCTION CORP | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator struck plastic service. Claims was looking for a steel pipe.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GENTRY BROTHERS INC | AZUSA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gentry Brothers were grading in the alley and hit a abandoned service ,no outages.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CHINO | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | Expired Ticket, Customer Failed To Expose Gasline And Use Caution While Digging, Customer Digging For Sewer
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | CHINO | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | Yes | No | Yes | Yes | Excavator damaged gas service when removing footing for gate. Branch service roped to avoid footing overpour while tracer wire ran in line.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-02-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 65 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BIG BEN CONSTRUCTION | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator struck 2 inch gas service. with backhoe. Marks were 5 feet off. No wire at meter.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HENKELS AND MCCOY INC | BALDWIN PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Developer digging to find and trench for gas service extension.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-02-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 65 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | CJW | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator damaged 2 inch plastic gas main with backhoe. No USA
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-08-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AC SPRAGGINS ENGINEERING | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator damaged gas service with backhoe and tied back pipe Called Gas Co the next day No USA
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-05-24 | Third party excavation damage | Riser | Polyethylene Pipe | Not Available | 0 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LENNAR HOMES OF CALIFORNIA INC | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | It is unknown how riser was damagedï¿½
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | OPTIMUM INC | BLOOMINGTON |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | this was emergency ticket, ETD was on his way to locate and mark but they hit the line before we got there.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA was good Locator marked out standard and branch contractor hit branch service while digging with shovel
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GENERAL ENGINEERING CONTRACTOR | GRAND TERRACE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | All USA marks were visible and USA was up to date Contractor forgot 3 4 STL gas service was there and hit it with a backhoe
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HARDY AND HARPER | LAKE FOREST | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor did not call in for remarks and while theyï¿½wereï¿½grading street they hit 1 2 PLA service
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HARDY AND HARPER INC | LAKE FOREST | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1? plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-08-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BUCCOLA LANDSCAPE | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator trenching for irrigation in parkway area struck gas main with mini x No outages New construction Very old USA on file from a year and a half ago Not updated
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-05-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | INTRAVAIA ROCK SAND INC | MONTCLAIR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator removing a footing for a wall damaged gas main. USA not valid. Old marks faintly visible on curb face as offset.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL WEST UNDERGROUND | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator damaged gas service with mini x. No USA
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SMC CONSTRUCTION | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck service while grading
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2021-11-23 | Third party excavation damage | Not Available | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GUARDIAN PLUMBING | WILDOMAR |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a plastic service with a backhoe while digging for a wall footing.
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2021-10-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ESTRELLA CONSTRUCTION | INDUSTRY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Locator is off work until next year but he marked as No SCG for some reason.
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2021-10-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ESTRELLA CONSTRUCTION | INDUSTRY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was excavating for wall footings and struck the 2 inch PE main. No USA was called for this work.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2021-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ICHIH WANG | SAN BERNARDINO |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. party digging for fence ripped out our gas line. No USA called in
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOHN PHILLIPS CONSTRUCTION | RIVERSIDE | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | excavator struck gas service with shovel while exposing gas line USA expired Marks visible and correct
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2021-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HOME OWNER | COLTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor did not notify USA and is fully responsible.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2021-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CASTRO IRON WORKS INC | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging a post hole to install a side entry gate when he struck the service line
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2021-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | COLTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party Damage, No USA, landscapers grading for homeowner hit plastic service with shovel.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2021-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 27 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer using a post hole digger to put a fence in and hit gas line. Did not call USA
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2021-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HCI CONSTRUCTION | RIVERSIDE |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | USA was not called
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2021-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ROBERTO TOLENTINO | COLTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per comments, homeowner was repairing water line in private property when laborer hit a plastic gas service with a shovel.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SALVADOR ASENSIO | COLTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging for the storm drain
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2021-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | CRESTLINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | service missed marked outside location
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PAR ELECTRIC | REDLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NO USA REQUESTED CONTACTOR AUGERING TO REPLACE BROKEN ELECTIC POLE
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2021-08-11 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ACCESS GENERAL | WESTMINSTER | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 2 PE service hit by so cal gas contractor
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2021-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DRAIN AID PLUMBING | MORENO VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Spoke to foreman of SCE, Hit plastic service while diggingï¿½
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DRAIN AID PLUMBING | CRESTLINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor, Tejon Constructors INC was digging with backhoe to raise an electrical vault for Williams Homes and hit our 4 inch PE main
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | CRESTLINE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service hit by home owner with shovel. No USA.
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | CRESTLINE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this work
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HOME OWNER | CRESTLINE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2021-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CRESTLINE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USAï¿½was called for this work. HO hit the service with a shovel
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2021-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RENE SANCHEZ | CRESTLINE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was landscaping in his property when he struck the 1 2 CTS service
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARS RESCUE ROOTER | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch plastic service was damaged with backhoe while digging for sewer.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-08-28 | Third party excavation damage | Not Available | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | N K DEMO | SAN BERNARDINO | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Property Demo No USA Heavy equipment destroyed riser
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-10-22 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | L R JOHNSON CONSTRUCTION | RIALTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TA RIDARD INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not protect us in place. Damaged plastic service. Damaged with backhoe, should of dug by hand.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 14 |  | MCKINNEY GENERAL ENGINEERING | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | This was a damage to our 0.75 inch service line that was correctly mark under USA ticket, the 3rd party contractor failed to hand expose our service with hand tools.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | N K DEMOLITION | SAN BERNARDINO |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Damaged service tee while grading.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BELCO ELECNON | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while removing fence block wall with backhoe prior to hand exposing.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | FONTANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Jerry Hernandez no usa customer digging with shovel for block wall.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-09-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 42 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HILLCREST CONTRACTING | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called by contractor Failed to pot hole our facilities
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-10-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | T E ROBERTS | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The contractor pothole and verified an incorrect pipe at approximately one foot deep. Damaged within the 24 inch inches.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MCKINNEY GENERAL ENGINEERING | FONTANA | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor damaged service with backhoeï¿½
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | J GINGER MASONRY LP | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA REQUESTED DIGGING FOR SEWER, came in contact with 0.5 inch pla lineï¿½
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-09-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PBU INC | BEAUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | This was an damage to our 1 2 IPS service line with no USA called in
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | GJ GENTRY | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor was digging to install a sewer line when they damaged a 2 inch plastic main. The contractor did not notify USA and is fully responsible.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NPL | EASTVALE |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor working to install water line in trench was digging and hit mis marked 0.5 inch IPS service.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 75001 |  | 1 |  | JAY CHASE | REDONDO BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor using a large excavator to core into the earth broke steel service when pulling coring bit back up. Gas service was extremely corroded and looked to be already leaking. Contractor was installing new septic tanks.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BEHNAM MIRSHAFIEE | FONTANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | This was an damage to a 1 2 CTS service line with no notification to USA
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL WEST UNDERGROUND INC | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | This was a damage to a 1 PLA stub service with no USA
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-12-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BOUDREAU PIPELINE CORPORATION | CORONA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | DIGGING FOR SEWER LINE
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-09-10 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JR CONSTRUCTION CLEAN UP INC | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | this was damage to a 1 al riser by a developer s clean up crew on a new tract site
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-07-24 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MONTE VISTA HOMES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck svc with backhoe while carelessly removing empty electrical conduits Conduits were not going to be used and were considered in the way Spoke with operator and reminded him to hand expose any and all gas pipe prior to using backhoe bucket in excavation Also stood by and watched as he and his crew practiced what we spoke of
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-04-29 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NPL CONSTRUCTION | EASTVALE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while excavating to install new 0.5 IPS service the contractor damage our existing service line with hand tools.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | SENOR SEPTIC CONSTRUCTION AND PUMPING INC | ONTARIO |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit service while doing plumbing workï¿½
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SA GOLDEN INVESTMENTS INC | BLOOMINGTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | this was a damage to a 1 PLA service with no USA called in
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JOSE | FONTANA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic service while digging to remove tree
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-03-03 | Third party excavation damage | Main | Steel | Boring Equipment | 3 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 6 |  | NPL | MIRA LOMA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor boring for main replacement struck and damaged plasticï¿½gas main with pilot bore bit.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2021-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | EDUARDO LEYVA | WEST COVINA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | This was a damage to a 1 2 IPS service with no USA called
Southern California Gas Company | N | SAN BERNARDINO | GRAND TERRACE | 2021-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | GRAND TERRACE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Was Requested, Contractor Digging For A Block Wall
Southern California Gas Company | N | SAN BERNARDINO | GRAND TERRACE | 2021-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EL CO CONTRACTORS | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | this was a damage to our 1 2 IPS service with a valid USA ticket and was marked correctly
Southern California Gas Company | N | SAN BERNARDINO | GRAND TERRACE | 2021-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JNL CONSTRUCTION | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Marks good service damaged while hand digging to make sewer repairs
Southern California Gas Company | N | SAN BERNARDINO | GRAND TERRACE | 2021-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | GRAND TERRACE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Home owner digging to install brick wall at property line hit branch service crossing lot . Had roots wrappedï¿½around line
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CALIBER CONS INC ARROW ELECTRIC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged PE service with a backhoe while trenching for electrical work. USA ticket was valid and contractor agreed to pothole for gas service. Per LCT, flags removed.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2021-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ALL AMERICAN POOL AND SPA | REDLANDS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Anhony Vara no usa. Third party digging to install pool line.ï¿½ CONTRACTORS DAMAGED PLASTIC SERVICE WITH A SHOVEL.ï¿½ï¿½
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2021-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | AYSAR HELO | HIGHLAND |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator dug into facility. Area was marked Correctly.
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MARBEN CUSTOM POOLS | HIGHLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 2 plastic service damage by contractor digging new pool line No USA
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2021-07-23 | Third party excavation damage | Not Available | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HERMAN WEISSKER | DOWNEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damage plastic service with in the 2 of Mark VIA hand digging with shovel ï¿½
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2021-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SLATER INC | FONTANA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Gas main and gas serviceï¿½was locatedï¿½incorrectly by approx. 15 feet. Locator crossed signal with ATT COM line.ï¿½Gas Co. locator referenced maps and service history while delineating area.
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2021-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | HIGHLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner removing treeï¿½
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2021-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MASUDUR CHHOWDHURY | HIGHLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner having sewer work done day labor hit service with shovel and left the sense
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2021-12-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SAN PUOK | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor working for the city of Santa Ana was boring to install underground electrical conduits, they damaged a mis marked 0.5 inch plastic service. the service was supposed to have been fully abandoned according to service history and GIS. the service was only cutback in the street and left as an active stub.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-09-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SCORPION BACKHOE | HEMET | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called for this work
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PAULS ELECTRIC | EL SEGUNDO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ï¿½ Damaged service due to the location pulled away fromï¿½the gas line nearï¿½the point of contact damage. misslocated.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RAUL MACEDO | LAKE ARROWHEAD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner havin work done at house .
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PAR ELECTRICAL CONTRACTORS | RANCHO CUCAMONGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called for this work.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | FAITH ELECTRIC LLC | REDLANDS |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Dug control hole. squeezed plastic service to control flow of gas. made permanent repairs by altering service using 2 feet of cts pipe and 2 cts couplings
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ASPEN CONSTRUCTION | LAKE ARROWHEAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service should have been exposed by hand. Contractor was using power equipment for the excavation and struck the service.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-09-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SCORPION BACKHOE | HEMET | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA stub was marked with a flag from earlier USA
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RODARTE CONSTRUCTION | LAKE ARROWHEAD |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service USA was not called
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-11-05 | Third party excavation damage | Riser | Steel | Augur | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FAITH ELECTRIC | REDLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LACSD WATER COMPANY | BLUE JAY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA was not called for this work.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MTZ CREATIVE CONCRETE INC | SAN BERNARDINO | CA | N | Y | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | ALL USA marks were good and visible. Contractor hit service while trying to expose service with shovel.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FAITH ELECTRIC | REDLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Customer had plumber working to install drain when he hit the gas service and looking at the pipe once exposed noticed he attempted to make repairs but failed and caused service to continue leaking with eventually notifying the gas company.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PRO ENERGY SERVICES GROUP LLC | ESCONDIDO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locate was just outside of the 24 due to the locate wire not being tied to the PE service line
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | POWER ELECTRIC | RANCHO CUCAMONGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Power Electric digging to install an anchor. Previous USA closed for pole replacement. No USA was called for the Anchor work.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BLACK DIAMOND CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per on call LCT Andrew Hernandez contractor hand digging with shovel installing footings for car deck. Had usa but did not provide.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-11-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BLACK DIAMOND | LAKE ARROWHEAD |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | landscaping company was digging to to add a Tree and damaged our service with a gardening pick. No USA was called.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FRED SHEFFRON | LAKE ARROWHEAD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Footing being installed for yard set solar
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PINNACLE PLUMBING | RIM FOREST | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged our gas service while digging up for water.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | IVAN FLORES | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew was digging on a slope with a shovel over mark went service was not potholed crew had a USA ticket
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LAKE ARROWHEAD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 inch service with shovel. No USA
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | SAN BERNARDINO | LOMA LINDA | 2021-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | OMAR TRUJILLO | LOMA LINDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ALL marks were GOOD and VISIBLE. Contractor did not pot hole and verify 2 inch PLA gas svc.
Southern California Gas Company | N | SAN BERNARDINO | LOMA LINDA | 2021-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PROFESSIONAL IRRIGATION SYSTEMS | YUCAIPA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping crew working on water service cut into 0.75 inch steel gas service with saw. USA was not notified.
Southern California Gas Company | N | SAN BERNARDINO | MONTCLAIR | 2021-06-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CABLE BROS | RANCHO CUCAMONGA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Damaged service with shovel digging for cable. No Valid USA found
Southern California Gas Company | N | SAN BERNARDINO | MONTCLAIR | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | J F SHEA CONSTRUCTION INC | WALNUT | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third Party Damage, valid USA, hit steel stub not marked
Southern California Gas Company | N | SAN BERNARDINO | MORONGO VALLEY | 2021-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | BROWNS BACKHOE | WRIGHTWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | worked done by home owner hit by day laborï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-04-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALABBASI CONSTRUCTION AND ENGINEERING | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator doing grade change damaged plastic service that was correctly marked.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | OPTIMUM INC | BLOOMINGTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | No USA Number Provided, Contractor Hit Because There Was A Unmarked Gas Line Not Found In GIS, Contractor Digging To Install Electrical
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-05-05 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MSL ELECTRIC | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged 3 inch main while pulling back Directional Bore. Valid USA
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GH DAIRY | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Farmer attempting to make repairs on a damaged water line hit unmarked gas line
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MSL | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor struckï¿½mismarked gas svc with shovel.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JF SHEA CONSTRUCTION | WALNUT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Failed To Expose Gasline With Caution, Installing Utilities For The City
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VICTOR SALINAS | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | excavator trying to dig up a septic tank damaged the gas service. No USA.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BELCO ELENCOR GROUP | CHINO |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage third party contractor damage service with mini excavator. USA was valid marks were visible. Contractor did not use caution when exposing gas line.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-04-12 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AMPCO CONTRACTING | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator damaged unmarked unknown cut back stub on private property while doing a complete demo.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | ONTARIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator damaged gas line while making repairs to sewer line with shovel standard and branch addresses involved 208 214 E Phillips
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-02-24 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CHRISTIAN SON BROTHERS | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | City the of Ontarioï¿½was hand digging to locate a marked service when they stuck the service they were attempting to find.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-02-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 15 |  | CHRISTIAN BROTHERS | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | excavation was not shored yet and the wall caved in on top of our pipe which was fully exposed
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-11-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC MASONRY WALLS INC | ORANGE |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No usa, hit 0.5 inch CTS gas service while machine digging.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TEICHERT | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was damaged by concrete saw while cutting for concrete repairs. Damage occurred on private property.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TEICHERT | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | No | Comany contractor Teichert located svc incorrectly as short side svc when in fact it was a long side, they proceeded to bore and struck svc
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-08-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CAL WEST UNDERGROUND INC | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was excavating to install telcom Excavator dug past warning mesh and struck 2 PLA main with backhoe
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-02-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LENNAR HOMES | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party Damage, no valid USA, contractor severed main while grading with backhoe.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CP CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged stub service. USA valid, marks not maintained. ticket Audit trail has update only No Marks Required from 10.505 21
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-08-09 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 4 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ULTIMATE INTERNET ACCESS INC | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Mis marked stub struck with bore Locator went off of old marks GIS information incorrect No signal with broken locate wire Contractor potholed stub but did not find pipe Failed to notify Gas Co
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | L S | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Backhoe operator damaged main exposing sewer. No USA
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | NA | ONTARIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was excavating to build a patio and cut the half inch CTSï¿½service.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-12-01 | Third party excavation damage | Main | Steel | Grader/Scraper | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ALL AMERICAN ASPHALT | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | customer was trenching to put waterline and hit gas service with hand tools
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-12-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HORIZON LIGHTING INC | IRVINE |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damage , Active USA , Marked correctly by SCG employee. Contractor failed to expose service line . Crew arrived and controlled release of gas .
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-10-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RYAN | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | plumber thought the gasline was abandoned and drilled into it.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-01-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL WEST UNDERGROUND INC | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service with Backhoe. No Valid USA
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 8 |  | DAGOBERTO ARGUETA | ONTARIO |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner using loader to cut down slope in yard hit 0.5 inch pla service. No valid USA. Crew cut back service for safety precaution.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-11-03 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ULTIMATE INTERNET ACCESS INC | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Irrigation company hit service with trenching equipment.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ULTIMATE INTERNET ACCESS INC | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit while digging trench with shovel
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARIJAET COMMUNICATIONS | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Bored through inactive service. Not marked. Valid USA.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-08-05 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | LANE SECURITY PAVING | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Cored through gas main Marked correctly Contractor was unaware the line was still live
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FYDAQ CO | FULLERTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 0.5 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-03-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 12 |  | SHARPS BACKHOE SERVICE | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging over plastic main and struck main
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-06-11 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CASS ARRIETA | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage to main was caused by a conduit roll that fell into the trench and hitting 2 inch plastic main, causing the damage
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2021-07-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CAL WEST UNDERGROUND | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged by backhoe digging for communications No USA
Southern California Gas Company | N | SAN BERNARDINO | PALMDALE | 2021-04-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | EXECUTIVE PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Giovanny Arzola of Executive Plumbing hit SCG service line with a backhoe while excavating to install sewer laterals.ï¿½ Executive Plumbing was contracting for Pacific Communities Home Builder.
Southern California Gas Company | N | SAN BERNARDINO | PHELAN | 2021-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALPHA OMEGA PLUMBING SEPTIC | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | SAN BERNARDINO | PHELAN | 2021-07-06 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WESTERN CONSTRUCTION SPECIALISTS | NORWALK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Plastic Stub was struck and damage by mini excavator while digging to replace power pole ï¿½
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HERMAN WEISKER | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Unknown stub not mapped damaged with backhoe
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-08-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KITE ELECTRIC | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor dropping in shoring beams struck 4 steel gas main USA valid and marks good Contractor thought gas main was abandoned
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CARLOS CASICLAS | MONTEREY PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service excavating footing for wall with a mini excavator. No USA.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL WEST | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit service with backhoe trenching for conduit. No USA.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-03-31 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 2 |  | CONSTRU ONE INC | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Damage, contractor bored through 2 inch steel main, no pothole. Valid USA, marked correctly.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-10-06 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | NPL | MIRA LOMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Customer hit service while installing a fence. Please do not Bill COVID hardship
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 65 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOME OWNER | RANCHO CUCAMONGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner with no USA damaged gas service while trenching for footing with mini x
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | FONTANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit service with backhoe trenching for wall. No USA
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | R AMP I COMMUNICATIONS | BLOOMINGTON |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Digging for sewer lineï¿½and hit our 0.5 inch IPS ï¿½gas serviceï¿½ï¿½with a shovel. No USA
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | R I COMMUNICATIONS | BLOOMINGTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Company Contractor, ARB, Inc., cut into 0.75 inch steel gas service with concrete saw while saw cutting concrete panel for removal.ï¿½ Gas service was found to only be 3.5 inch in depth at damage location.ï¿½ Company crew arrived and completed permanent repair.ï¿½ï¿½
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | POWERTEC COMPANY | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator damaged gas service while potholing us with shovel Marks good
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | POWERTEC COMPANY | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator damaged gas service with a shovel while exposing us USA marks were good
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-02-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GOTHIC LANDSCAPE | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gothic Landscaping was planting tree, valid USA, crew stated they removed flags over service prior to excavating, failed to maintain or call for marks. Hit service with backhoe, no hand exposure.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CP CONSTRUCTION COMPANY INC | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged stub service with backhoe, Valid USA, Marks 7 feet off
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TROPICAL BREEZE POOLS | MORENO VALLEY | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Per locator delineations in backyard away from meter Marked No SCG for backyard delineation
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RANCHO CUCAMONGA WATER DISTRICT | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | According to the homeowners friend, homeowner hired a handyman to do work around the house. He decide to relocate a palm tree and that is when he damaged the 0.5 inch CTS service on Sunday 12 26 21. The service was taped back with wire and grey tape. The Gas Co. was not notified till the next by the neighbor who called in. No USA Ticket.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PARAMOUNT FENCE BUILDERS INC | JURUPA VALLEY | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | damaged while digging to install fence, USA called in but not valid at the time.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NOR STAR | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Juan Arteaga stated that while trenching the service was struck.ï¿½ They pinch service to control the leak.ï¿½ Damage occurred on 10 6 21 around 3pm and was not reported until 10 7 21.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MORSTAR GENERAL ENGINEERING | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR HIT SERVICE WITH TRENCHERï¿½
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | RANCHO CUCAMONGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit service with backhoe, no USA.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | AJ COMPLETE REMODELING SERVICES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging to install drain, No USA
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2021-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SAFARI LANDSCAPING POOLS | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging without a USA ticket, and assumed that he had found a tree root, when in fact, was our gas service.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2021-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | REDLANDS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2021-05-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | UNLINTIED ENGINERRING CONSTRUCTION | REDLANDS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching when service was hit, No USA.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2021-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HERMAN WEISSKER | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was excavating to repair a water leak when they damaged the 0.5 inch plastic service.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2021-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 2 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | REDLANDS WATER CO | REDLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | water company probe thought main not at fault
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2021-11-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 10 |  | CITY OF REDLANDS | REDLANDS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | H O at 389 E Glen Cir S was hand digging with a shovel to install a fence hit the branch service to 371 E. Glen Circle S Palm Springs no USA.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2021-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | NA | REDLANDS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner was digging a hole in his backyard for a trampoline when he struck our 1 2 gas service no usa was called in before digging
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2021-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TRYCO GERNERAL ENGINEERING | RIM FOREST |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor digging drain damage service while excavating.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | HE HAMMER CONSTRUCTION | YUCAIPA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Should be billed LCT talk to them about calling ing for USA Remarks when removing asphalt
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2021-04-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WARREN MEYER SON S | HESPERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor in construction site damage plastic service with heavy machinery once he already had it expose.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2021-01-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HARDY HOPPER INC | LAKE FOREST | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor struck new 1 inch PE service that was recently installed. There was an asphalt trench that went all the way across the street.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Material not known | Hand Tools | 1 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WEST END PLUMBING | RIVERSIDE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | this was a 1 PLA service damage
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2021-10-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | RESORT STYLES | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Locators marked out all svc and Main. But some other utility used yellow paint to mark out Telephone. This was the reason the contractor did not pot hole our gas svc. This was not a Locator error.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2021-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DEAN COOK | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging over 2 inch PE main with a back hoe.ï¿½ While excavation the hit the cap of a 2x1 pinch tee causing the cap to leak and deforming the top of the punch tee.ï¿½ï¿½
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2021-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BHI | SAN BERNARDINO |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Noï¿½Valid USA USA Was Expired, contractor was excavating trench to install electric conduits and hit the 0.5 inch CTS Gas Service for property 1616 Lamego Dr, GLN. Though USA was expired the old markings were correctly marked for service.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2021-12-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | EBD GENERAL ENGINEERING INC | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was digging to expose the utilities in the area when they damaged aï¿½ 2 inch plastic main.ï¿½ This damage was discovered after the fact, it was not leaking but the 2 inch plastic was kinked. The contractor did not notify USA and is fully responsible. ï¿½
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2021-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SILVAR OUTDOOR LIVING | CORONA | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No USA from contractor
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2021-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HERMAN WEISSKER | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while SCE contractor Herman Weissker was excavating to install Elec lines they damage our 0.5 CTS service.
Southern California Gas Company | N | SAN BERNARDINO | RIMFOREST | 2021-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | RIMFOREST | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called for this work
Southern California Gas Company | N | SAN BERNARDINO | RUNNING SPRINGS | 2021-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BRUCE ORONA | RUNNING SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was digging with shovel when he damage plastic service.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CM PLUMBING | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber cut though svc line
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-02-09 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CAL WEST UNDERGROUND INC | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | trenching to install dry utilities, contractor failed to use caution while exposing gas line
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALL PRO PLUMBING | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbers pulling new sewer lines through old sewer ,hooked gas riser causing it to pull and damage service.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | LIGHT AND POWER | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was damage when pulling old power pole
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor grading to install sidewalk damage 0.5 inch cts service.ï¿½ USA was not notified.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | STEVE S P RADOS INC | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck and damaged 0.5 inch cts marked gas service while digging to install sewer.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-02-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ROOTER HERO | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this work. Service was hit and damaged
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GRIFFITH LANDSCAPE | SANTA FE SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged 1 inch plastic gas service when driving a metal stake into the ground to help support the wooden frame to pour concrete to install sidewalk and gutter
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service was damage with shovel while digging trench for fence. NO USA.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-11-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | INFINITY ENERGY INC | ROCKLIN |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner cut through our service while trenching for electrical conduit. Customer claims he thought our line was a tree root.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | EW HARMON | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damage 1 feet unmarked PLA service.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DAN MOORE ELECTRIC | SAN BERNARDINO | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | hit service not valid USA
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DAN MOORE ELECTRIC | SAN BERNARDINO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor Failed To Use Caution While Exposing Gas Line. Contractor Digging For Communications
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 28 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RAFAEL PONCE | WEST COVINA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Sanchez developer damaged abandoned stubservice line. No gas leak, no leak repair order necessary.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SAN BERNARDINO FIRE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | conty fire cleaning area after fire damaged service
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-01-04 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | STEVE P RADOS INC | SANTA ANA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Unknown stub hit by excavator equipment. ETD did not pick up ant signal or see any history about this stub in GIS.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BHI PLUMBING | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor damaged a 0.5 inch IPS stub that ran cross lot. Crew abandoned the stub at the branch connection.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JESUS MADRIGAL | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-12-06 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VICENTE RODRIGUEZ | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit gas and water service with a backhoe while trenching for landscaping.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was trenching by hand and damage 0.5 inch plastic service.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-07-16 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | J M LEYVA ENGINEERING | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor pot hole for SCG found steel line and proceeded to bore fail to expose 2 all around main and damage live plastic main that was located in the bottom ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | THOMAS DUM LONG AN FARMS | WESTMINSTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service damage by home owner while digging for drain lines JV
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | UC FENCE | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging hole for fence postï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WOOD ASSOCIATES DEVELOPMENT | REDLANDS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service damage with shovel No USA
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1.25 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LYNN LEE | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | plumber was fixing house when he cut thought 1.25 stl svcï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Home owner was removing stump when he damage svc.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | ARIJET COMMUNICATIONS | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2 service damaged while boring , location was marked correctly
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CITY OF SAN BERNARDINO | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | City Inspector smell gas at Water Dept. excavation. Water Dept. claimed inspector was probing near area.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ALL COUNTIES FENCE SUPPLY | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit line with post hole digger in order to install fence.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 4 |  | PROPERTY MANAGEMENT | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | worker was cutting out tree and hit svc with a shovel
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Did Not Have USA. Contractor Was Digging To Install Fence When They Hit The Gas Line.ï¿½ Contractor Backfilled The Posthole They Were Digging And Tried To Say It Wasn Feett Them.ï¿½ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HOMEOWNER | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | utility Contractor damaged 1 inch plastic service while prepping for bore. damaged with a shovel by hand.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service while digging to install sewer.ï¿½ USA was not notified.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TK CONSTRUCTION | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Hit plastic service with backhoe, fail to call for refresh marks.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TK CONSTRUCTION | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2nd plastic service hit same day, fail to call for refresh marks.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-11-23 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Trencher | 0.75 | 27 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RAY JASSO | BLOOMINGTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner removing palm tree damage plastic CTS service. No USA.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TBU INC | BEAUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor TBU was trenching for drainage when they damage 0.5 feet CTS service.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SAN BERNARDINO | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | Yes | No | Yes | Yes | Home owner struck gas service with back hoe digging a trench for retaining wall footing inside property , USA ticket expired , no marks or delineation present,ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LIFETIME SOLUTION | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home Owner damage plastic service by meter, Not valid USAï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2021-03-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | TK CONSTRUCTION | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | replacing water mainï¿½
Southern California Gas Company | N | SAN BERNARDINO | TWENTYNINE PALMS | 2021-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 41 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | A O PRO PLUMBING | TWENTYNINE PALMS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Contractor assumed steel service line was an abandoned water line and cut it to access lids for septic tank
Southern California Gas Company | N | SAN BERNARDINO | TWIN PEAKS | 2021-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1 | 60 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | TWIN PEAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Called. owner was clearing out snow and debris and grading his driveway with a bobcatï¿½
Southern California Gas Company | N | SAN BERNARDINO | TWIN PEAKS | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CREW ELECTRIC | TWIN PEAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | SAN BERNARDINO | TWIN PEAKS | 2021-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | TWIN PEAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this work. HO replacing waterline
Southern California Gas Company | N | SAN BERNARDINO | TWIN PEAKS | 2021-09-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ESTRADA YARD CLEAN UP | LAKE ARROWHEAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITY OF UPLAND | UPLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The occupant of the property was digging to install a fence when they damaged a plastic service.ï¿½ The occupant did not contact USA and is fully responsible.
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2021-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HENKELS AND MCCOY | POMONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged Service, Valid USA
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2021-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 65 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | UPLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner struck branch service with excavator. Service did not leak. Small leak at bushing of branch servcie meter.
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PAYLESS 4 PLUMBING INC | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a backhoe excavating to install an electrical service when he struck a 1 inch PE stub.
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TWIN OAKS LANDSCAPE | WRIGHTWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | New business track homes Irrigation company damaged gas service with mini x No USA
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2021-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | L L BUILDING MATERIALS | BALDWIN PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | excavator using mini X dug into plastic gas service. No USA.
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2021-10-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WILLIAM JOHNSON OPTION ONE PLUMBING | RANCHO CUCAMONGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit 0.5 inch plastic service. no usa
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2021-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | OPTION ONE PLUMBING | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA WAS GOOD, CONTRACTOR FAILED TO USE CAUTION WHILE EXPOSING GAS LINE DIGGING FOR SEWER
Southern California Gas Company | N | SAN BERNARDINO | WRIGHTWOOD | 2021-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ELITE FENCE | PHELAN | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | C M CONSTRUCTION | YUCAIPA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service damage while digging post post Out of USA delineation
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2021-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | YUCAIPA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging to repair water lines.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2021-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | SOUTH MESA WATER CO | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | City workers damage plastic service with backhoe when repairing sewer lines.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HOMEOWNER | YUCAIPA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hitline per 3rd party contractor . No USA . Crew arrived and control release of gas . Sup explained to contractor the importance of 811
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2021-06-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | YUCAIPA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damage plastic service in the process of home addition work. No USA.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2021-03-01 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ACCESS GENERAL CONTRACTING INC | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor installing meter guard hit service with shovel.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2021-01-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KIM MCCULLOUGH | YUCAIPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Developer damage plastic stub with EFV valve while digging for Edison trench.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2021-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BORDEN EXCAVATION | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractors was digging trench line to install water main and hit a sub svc
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MARCO CERVANTES | JOSHUA TREE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. While digging for septic tank lids, Excavator found 0.75 inch gas service and began trenching along side of it. He eventually hooked service causing it to rupture. Water service as also damaged by Contractor
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ACTION PUMPING INC | YUCCA VALLEY | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Excavator started digging before USA ticket was valid
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2021-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GAYLER CONSTRUCTION | THERMAL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Valid USA While excavating for drainage pipe installation 1 2 CTS stub was damaged Stub was located on right side of house Full service installed on left side of garage No SCG documentation for short side stub
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BILL RICHARDS | HEMET | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Previous marks whiskers from USA ticket called in over 1 year ago. Excavator hit service with shovel while digging trench for sewer connection
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2021-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20001 |  |  | NA | ARAUJO CONSTRUCTION | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator trenching for sewer failed to pothole service. Per Locator, excavator was informed that service line crossed proposed trenching area and was told by excavator he would pothole before trenching through
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2021-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WILLIAM SELLERS PLUMBING | YUCCA VALLEY |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew performing leak repair discovered leak was caused by an unreported damage
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2021-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | IAN ZEISING | YUCCA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowener replacing fence and fence posts. No USA called prior to damage. Upon removing fence post, service was damaged in the course of work. Supervisor directed homeowner on how to call USA 811. Damaged area replaced with less than 2 feet of 0.5 inch Cts by crew.
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ACTION PUMPING | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to install sewer line, damaged BRANCH service at home. service was located by SCG locator, but marks flags and whiskers were removed by excavator during excavating
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2021-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | ARROYO GRANDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA not contacted before digging
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | JUSTIN TRAMMELL | SANTA MARIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging for fence no valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2021-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FORM DESIGNS AND BUILD | SAN LUIS OBISPO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | DWP Hit unmarked 0.5 inch plastic service
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2021-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOUSE AND BUILDING MOVERS | ARROYO GRANDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HomeBuilding mover hit service while digging up footing. No Valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2021-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CARLOS ROGOS | NIPOMO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing fence post hit gas service.
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AUBURN OAK BUILDERS | BAKERSFIELD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Damage caused by developer digging up 1 2 plastic service
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SANTA MARGARITA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA ticket. Service was hit while installing a fence
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | R W CONCRETE CONTRACTORS | SAN CARLOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA ticket. Contractor hit service while installing a garden.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-06-24 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | MARK SWITZER EXCAVATING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged 1 PLA main with probe while trying to expose gas facility.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-08-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | ATASCADERO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner digging fence posts with post hole digger damaged 1 2 pla service no USA
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | NIPOMO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Digging hole for satellite dish with post hole digger ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-02-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid USA, Contractor failed to maintain clearance
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROBERT MOORE TRACTOR SERVICE | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was grading when service line was hit with the backhoe.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | ATASCADERO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Struck 0.5 inch IPS service while digging for a fence post. No USA.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner damaged service while digging for a wood retaining wall.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SAGE LANDSCAPES | LOS OSOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-02-02 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | INTEGRITY GENERAL ENGENEERING CONTRACTORS | NA |  | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damaged by second party during work hours. Investigation performed by Shannon Halweg.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-10-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TWISLEMAN | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while digging to install sewer. Service marked correctly with paint and also flags
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-06-21 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 0 | 59 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | ATASCADERO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner knocked off some wrap from STL service. no leak or damage to STL service.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-12-06 | Third party excavation damage | Meter | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ATEAM FENCING | ATASCADERO |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while homeowner was digging for new fence post, service line was struck with shovel causing an uncontrolled release of gas.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2021-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | THOMAS HIMMELRICH | ATASCADERO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner Thomas Himmelrich hit 1 2 inch service with a jackhammer while digging out pole to replace fencing
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2021-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MOLINA BROS | CAMBRIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2021-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MOLINA BROS | CAMBRIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2021-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOHN PARKER | CAMBRIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2021-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CAMBRIA COMMUNITY SERVICES DISTRICT | CAMBRIA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Work being done at home owners property and damaged gas service line. No USAï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2021-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RICK VALENTE CONSTRUCTION | CRESTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | CAYUCOS | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JUSTIN RODRIGUEZ | NIPOMO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging for retaining wallï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | GROVER BEACH | 2021-04-01 | Operator excavation damage | Main | Steel | Miscellaneous/Other | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | INTEGRITY GENERAL CONTRACTORS | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Integrity contractor welder burned through main installing a service tee.
Southern California Gas Company | N | SAN LUIS OBISPO | GROVER BEACH | 2021-01-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | D SNYDER | LOS OSOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA. Contractor hit service with form stake for paver driveway
Southern California Gas Company | N | SAN LUIS OBISPO | GROVER BEACH | 2021-03-17 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | INTEGERITY | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2nd party damage.ï¿½ Contractor Integrity digging to install new service struck 0.5 inch IPS plastic service.ï¿½ USA Ticket good, Marked correctly.
Southern California Gas Company | N | SAN LUIS OBISPO | GROVER BEACH | 2021-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JI FISHER CONSTRUCTION | NIPOMO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes
Southern California Gas Company | N | SAN LUIS OBISPO | GROVER BEACH | 2021-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | NEW ERA LANDSCAPING INC | GROVER BEACH | CA | N | Y | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | homeowner was gigging on his property to have new sewer line installed when he hit our gas service line with a pick axe.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | GROVER BEACH | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | JJ FISHER INC | NIPOMO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid USA excavator failed to verify material pipe location prior to using machine excavator
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2021-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS OSOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator did not use caution while digging hole with post hole digger
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2021-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GREG FRYER | LOS OSOS |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA PROVIDED, UNKNOWN WHAT THEY WERE DIGGING FOR.ï¿½ No one was onsite for information
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2021-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | A1 CONCRETE INC | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor performing concrete work for solar street lightsï¿½ contractor failed to exposed gas line with hand tools before digging with augur.
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2021-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | NA | LOS OSOS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA.
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2021-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JESUS NUNEZ | LOS OSOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | crew was working installing trees on private property for Homeowner and in the process came in contact with with 0.5 inch IPS service line with jack hammer.
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2021-03-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOS OSOS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per Incident Commander Ry Plakias Renter of home, Jessica Wilsonï¿½struck service line while removing tree.ï¿½ Wilson states that a shovel was used.
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2021-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOS OSOS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was replacing a water line when gas service was struck with a digging bar.
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BURCH CONCRETE SOLUTIONS | LOS OSOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor digging with shovel and hit gas line while performing work for homeowners sewerï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | MORRO BAY | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WILLIAMS CONCRETE | MORRO BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes
Southern California Gas Company | N | SAN LUIS OBISPO | MORRO BAY | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ANVIL BUILDERS | MORRO BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was moving dirt from hill side when the hit 0.5 inch CTS Service.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2021-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NIPOMO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner nicked 0.5 inch PLA service while digging a hole for a fence. No USA. Service was not disrupted. Crew was able to tank meter and make repair without dropping customer.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2021-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RICARDO LOPEZ | OCEANO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.ï¿½ 3rd party damage to plastic service
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2021-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for the homeowner struck our gas line while hand digging.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | G DURAN | NIPOMO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer says they were digging trench for fence and hit service with shovel.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2021-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NIPOMO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | struck 0.5 inch cts plastic service with hand tool while excavating.ï¿½ USA Marks accurate.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2021-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RYAN EDWARDS | NIPOMO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, homeowner digging with shovel and hit service.
Southern California Gas Company | N | SAN LUIS OBISPO | OCEANO | 2021-04-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MIKE BOGLE CONSTRUCTION INC | ARROYO GRANDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging utility trench for electric and gas.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NA | PASO ROBLES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Homeowner damaged steel gas service when digging up tree roots.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2021-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PASO ROBLES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA ticket. Service was hit while grading for retaining wall.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2021-07-12 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | 2nd party ARB damage on 1 2 pla service while open trenching new service Contractor failed to expose facilities while digging over marks USA marks were accurate Crew dropped back and capped service to allow ARB finish the replacement
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CAMERON HATKINSON | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | digging for water, drain gas electricï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | PERRIS | 2021-02-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC COMMUNITIES | MENIFEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Operator hit service with excavator. Failed to pothole. Service was marked. Marks were visible.
Southern California Gas Company | N | SAN LUIS OBISPO | PISMO BEACH | 2021-12-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KIRK CONSTRUCTION | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Laborers were trenching to install a water service to the backhouse. Day laborers struck the line with a pick ax while trenching and then clamped it with a 0.5 sleeve, Causing the gas to migrate through the copper casing and next to the foundation. Evacuation was declared and aeration procedures began after gas was under control.
Southern California Gas Company | N | SAN LUIS OBISPO | PISMO BEACH | 2021-11-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RAY ORTIZ | SANTA MARIA |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Damaged 1 inch plastic service, crew made repairs.
Southern California Gas Company | N | SAN LUIS OBISPO | PISMO BEACH | 2021-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC LIMM LANDSCAPE | ATASCADERO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was auguring to place railroad ties upright to prevent erosion on his property. He was auguring within the tolerance zone.
Southern California Gas Company | N | SAN LUIS OBISPO | PISMO BEACH | 2021-11-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PACIFIC RIM LANDSCAPE | ATASCADERO |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in, contractor was digging footing to install wall and hit service with shovel.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | GOOD NEIGHBOR CONSTRUCTION | SAN LUIS OBISPO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA ticket.ï¿½ 3rd Party contractor digging to repair water line.ï¿½ Struck 0.5 inch cts plastic service with shovel.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor was hand digging to expose 0.5 inch pla stub then damaged it.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LENOR FELIX | ARROYO GRANDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor broke service while replacing the sewer line. No USA
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | DAN EDWARDS | SAN LUIS OBISPO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 2 service Customer excavating on Expired USA ticket NO VALID USA
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SEAN BOLDUAN | SAN LUIS OBISPO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service that was incorrectly marked. After an investigation with EE he notified DWP foreman that he did not have acess to locate service he when off by service history measurents., marked plastic service with measurements from service history which was 4 feet off. Employee used all available resources to try to eliminate the possibility of a damage gas line.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-03-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AYALA EARTHWORKS SERVICES | SAN LUIS OBISPO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party damage of 0.5 inch plastic stub in new business tract.ï¿½ No USA ticket.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-09-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FENCE WORKS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Code one indications were found while crew was investigating a no gas at the meter order created by CS While investigating crew found the damaged 1 2 pla service under a brand new post that had been installed Damage from a post hole digger EFV worked and stopped flow of gas but leaked and caused gas at the foundation
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-06-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JOSEPH ENGINEERING | NIPOMO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Valid USA ticket. Facility not located by company locator.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-07-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LANDSCAPE DEVELOPMENT INCORPORATED | SAN LUIS OBISPO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-05-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AMBIENT COMMUNITIES | SAN LUIS OBISPO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | trenching for utilities. No USA ticket
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-05-14 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | INTEGRITY CONTRACTORS | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged service while hand digging
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FERREIRA INC | SAN LUIS OBISPO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Work performed after ticket expired, sawzall used to cut through roots above service. Marks slightly faded, but visible in location of damage.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SAN LUIS OBISPO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT B Mintun, Cust Digging Hole To Install A Fence Post
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | REGINALD B CORELLA | SAN LUIS OBISPO |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this work. Cal Trans was cleaning the roadways for future snow issues and cut the hill damaging the 0.5 inchPE service
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SALVADOR GONZALES | ARROYO GRANDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging with post hole digger with no valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-05-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | ARROYO GRANDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA ticket damaged plastic service hand digging
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HENKELS MCCOY | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged our 1 inch service while excavating to install a retaining wall. The contractor did not have a USA but marks were visible from a previous ticket.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | STARILE BUILDERS | MORRO BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service by accident with shovel while hand exposing
Southern California Gas Company | N | SAN LUIS OBISPO | TEMPLETON | 2021-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | ATASCADERO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged service while excavating with post hole diggers to install fencepost.ï¿½
Southern California Gas Company | N | SANTA BARBARA | BUELLTON | 2021-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | GRANITE CONSTRUCTION CO | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to properly pothole, verify location and protect svc.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2021-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CARPINTERIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner damaged 0.5 inch Plastic service while digging to remove a tree stump.ï¿½
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ZACK MOORE MAC BROWN EXCAVATING | CARPINTERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Mac Brown Excavation removing cement footings for residential site development.ï¿½ Hit 0.5 service line suppling neighbors meter.ï¿½ 625 Sand point was located branch with flags and contractor knew location. 607 Sand Point Standard was in homemade conduit within the cement footings they were removing.ï¿½ USA Ticket numbers provided were for Tierra Contractors for water main replacement on Sand Point Road.ï¿½ No valid USACompany unaware of work being performed.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2021-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JOSE QUINTERO | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customers contractor was removing old fence post and struck gas service.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2021-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WILSON ENVIRONMENTAL CONTRACTING | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged our 0.5 inch service while excavating to run an irrigation line. had active USA and our service was properly marked.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2021-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | GOLETA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Kris Wieland Homeowner Paul Kouns struck SCG service line while digging with hand tools to install a drainage line
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | GOLETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas service damaged while digging with a shovel in the yard.ï¿½
Southern California Gas Company | N | SANTA BARBARA | GUADALUPE | 2021-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PG E | SANTA MARIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | PGandE hit 0.5 feet line while excavating.
Southern California Gas Company | N | SANTA BARBARA | GUADALUPE | 2021-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALEX VILLA | SANTA MARIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Builders were excavating a trench crossing our service line that was marked when installed with flags.ï¿½ï¿½
Southern California Gas Company | N | SANTA BARBARA | GUADALUPE | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | SONS GENERAL ENGINEERING | SANTA MARIA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Land owner Grading at property failed to notify USA and struck service.
Southern California Gas Company | N | SANTA BARBARA | GUADALUPE | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | NIPOMO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Nephew of the home owner was building a fence for his aunt. No USA and hit 0.5 inch pla branch service with post hole digger.ï¿½
Southern California Gas Company | N | SANTA BARBARA | GUADALUPE | 2021-09-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TLC UNDERGROUND INC | NIPOMO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party damage ï¿½ USA Marks accurate ï¿½ Failed to hand dig as required 2 plastic main damaged by backhoe
Southern California Gas Company | N | SANTA BARBARA | GUADALUPE | 2021-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 8 | 60 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  |  | NA | R BAKER | ARROYO GRANDE |  | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 8 inch plastic main gouged by back hoe necessitating main alteration.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2021-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOMPOC | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The home owner was trenching to install a sewer line and struck the gas service line. The customer called the FD. The ETR arrived and secured the area. The Gas Co crew arrived and controlled the leak and made repairs. The service was restored the following morning. There was no street closures, no injuries, no evacuations, and no media.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MIKE MITCHELL CONSTRUCTION | PASO ROBLES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without notifying USA struck an unmarked 1 PE Gas Service
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2021-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LUIS QUEBEDO | GOLETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA ticket. 3rd party contractor was digging for fence post.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2021-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | NA | LOMPOC | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner excavating without USA struck 1 2 PLA SVC Spoke to homeowner about the importance of calling 811
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2021-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOMPOC | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging with a post hole digger to install a fence post.ï¿½
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2021-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JMLCONSTRUCTION | LOMPOC | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging post hole to repair fence did not request USA and damaged 1 2 PE service
Southern California Gas Company | N | SANTA BARBARA | LOS ALAMOS | 2021-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | KENDALL JACKSON WINES | LSAL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Ticket
Southern California Gas Company | N | SANTA BARBARA | LOS OLIVOS | 2021-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | UBC BUILDING CORP | LOS OLIVOS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was building a retaining wall and was digging the footing and came across tree roots and 0.75 inch STL service. Contractor used saw zaw to cut roots and cut STL gas service.ï¿½
Southern California Gas Company | N | SANTA BARBARA | MONTECITO | 2021-12-06 | Third party excavation damage | Not Available | Material not known | Not Available | 0 | 0 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for concrete pad and struck gas 1 inch plastic service with backhoe.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor hit our 0.5 inch service while digging a footing for a wall. the service was very shallow, our planner is aware and working with the contractor to resolve the issue.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service hit with Grader while laying foundation for new driveway.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | EXPRESS ROOTER | CARPINTERIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor boring on expired USA Ticket.ï¿½ Found SCG USA flags removed upon arrival.ï¿½ SCG flags found in trash can near gas meter.ï¿½ Contractor failed to expose service crossing in sidewalkdriveway prior to boring new sewer line in.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PACIFIC MATERIALS LABORATORY OF SANTA BARBARA INC | GOLETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Pacific Materials performing soil testing with auger on property for 1220 Coast Village.ï¿½ Soil testing being performed outside of 1212 Coastï¿½Village delineations and had no USA on file.ï¿½ 1212 Coast Village had USA to remove fencing between 1212 and 1220 Coast Villageï¿½properties.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging hole to bury the family dog. during the excavation process the customer damaged our 0.5 inch service. No USA was called.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CHM LANDSCAPE SERVICES INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching to install new irrigation line hit 0.5 inch plastic service with trenching shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HOT LINE CONSTRUCTION INC | SANTA PAULA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Customer was digging and hit the branch service.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PHILLIP INGRAHAM | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Handyman working for owner hit gas service while posthole digging while landscaping.ï¿½ No USA called.ï¿½ Per owner USA doesn feett mark lines on private property.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JERRY THE PLUMBER | SANTA BARBARA | CA | N | Y | Yes | No | No | Yes | No | Yes | No | Contractor was exposing sewer drain clean out in front yard near building.ï¿½ While hand digging, contractor damaged 0.50 inch plastic service.ï¿½ Previously exposed 1 inch yard line and thought that was gas service.ï¿½ Working being performed was outside of USA descriptionrequest.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SANTA BARBARA | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | PSM Landscaping was clearing slope over existing 0.5 service on an expired USA ticket.ï¿½ Hit service with track hoe.ï¿½ Failed to verify service location prior to using mechanical equipmentï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GOODLAND PLUMBING | GOLETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit plastic service with trenching shovel while trying to excavate sewer line.ï¿½ Had removed SCG Flags in excavation area in yard next to gas meter
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | CESAR FIGUEROA | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Not Gas Co Related 3rd party contractor damaged plastic gas service while performing driveway repair Service was not leaking or blowing Service had to be altered No Emergency services or evacuations
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ACCI ALFARO COMMUNICATIONS | COMPTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor, pot holing to expose our service for directional boring, hit line with shovel while trying to expose crossing.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor exposed 0.75 inch steel service while excavating for new water line. While trenching on other side of service line, backhoe bucket caught steel service and pulled 0.5 inch plastic insert out damaging line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ESAU MORENO | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party was digging trenches for drainage without USA and hit our 0.5 inch pla service with a shovel. crew was able to pinch the line where it was already exposed in another area of the yard. ETR had 1 home evacuated upon supervisor arrival.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | DENNIS NELSON CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor damaged line while trying to pothole electric conduit in very hard soil.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PROGRESSIVE LANDSCAPE | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Progressive Landscaping hit 0.50 inch service line while digging to plant a 5 gallon hedge on Saturday, July 3rd.ï¿½ Contractor had another workerplumbercontractor make repairs with water coupling and buried line for the weekend.ï¿½ On Tuesday, July 6th, Art Gonzalez Primary of Progressive Landscape smelled gas and exposed buried damaged service.ï¿½ He contact SCG at 937 CSO Leak issued.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GEORGE THE ROOTER MAN | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | leak caused by unreported damage to main.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SB TURF LANDSCAPE | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ANTHONY CHAVES | SANTA BARBARA | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | Yes | No | Yes | Yes | Non leak damage Bent service
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LUCIO | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor did not notify USA and damaged our 0.50 inch PLA service while digging a post hole. contractor had left the work area by the time supervision arrived.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SB TURF | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to install a fire pit line.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LOW COST PLUMBING | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator hit PLA service with shovel
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner was digging postï¿½ holes right over our service and hit the 0.50 inch line while digging. he did not have a valid ticket but the service was marked at the curb line about 30 feet away.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TORO ENTERPRISES INC | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No Valid USA, Contractor was digging trench with shovel and hit gas service. Home owner is expanding driveway.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CAL REAL POOLS | SANTA BARBARA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Damaged service Permanent repairs completed
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VENTURA DIRECTIONAL DRILLING INC | SANTA PAULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor tried to bore in line without pot holing our service.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NEWGEN COMMUNICATIONS INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working without a USA ans severed our 1 inch pla service with a shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer of recordï¿½was digging to install a plant next to garage in line with the gas meter and hit the gas service with a shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARNOLD BROS CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with shovel for a retaining wall.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SELF EMPLOYED | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing a fence post over existing gas service.ï¿½ Struck gas service with pry bar.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching to install irrigation line hit 0.5 inch gas service with shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SCHWAN BROS | GOLETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor did not have a valid USA ticket while digging for pool lines and severed our 1 inch pla service while digging.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-08-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BOB S BACKHOE AND TRUCKING | GOLETA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor agreed to pothole service prior to excavating Contractor used backhoe and damaged 1 2 inch service while removing a septic tank
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.5 service by homeowner doing construction. Service was cutback by crew because at the customers request due to continuing construction activity on the property
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Upon arrival the contractor had already left the work site. we found a 0.5 inch pla service severed and folded back.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged our 0.5 inch IPS service while digging. upon the ETRs arrival the he found the service bent back and ziptied. the contractor had already left the worksite.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called in for this job.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-01-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | TIERRA CONTRACTING | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 2 inch plastic main while excavating to install new water main. crew pinched the 2 way fed main and repaired damage using two electrofusion couplings. There were no outages on this damage.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 43 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | THE TOWBES GROUP | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The third party contractor cut our service back himself and used a pvc mechanical coupling to control the service. Once this was identified we sent a crew out to do a proper cutback.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hired a unlicensed contractor to build a fence on her side yard. while the contractor was digging a post hole he hit the neighbors service.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PAUL EGGLI | SANTA BARBARA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut into plastic service with sawsall while trying to remove some roots.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MCALLISTER CONSTRUCTION CORP | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged our 0.5 inch pla service with a shovel while exposing the line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROOTER SOLUTIONS | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor found oldabandonï¿½copper water line approximately 1 foot off our service marking and assumed it was the gas service.ï¿½ Contractorï¿½continued excavation and struck 0.5 plastic service that was in line with our markings.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LOW COST PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party plumbing contractor damaged the 0.5 inch CTS plastic service with a shovel while digging to expose the plumbing.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | TIERRA CONTRACTING INC | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor exposed plastic service and accidently nicked service with shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JV CONCRETE | SANTA BARBARA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor was digging over our 0.5 inch service. the USA ticket they had called in was expired. marks were still visible.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ROOTER SOLUTIONS | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no usa, unaware of who damage are line, LCT found are line damage and clampedï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-10-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JAAX CONCRETE INC | SAN LUIS OBISPO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | service line damaged while digging for sewer lateral
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CEDRO CONSTRUCTION | SANTA PAULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor was digging to expose our service which was properly marked out for ticket. While exposing our line the contractor damaged the 0.5 inch plastic service with a shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GARDEN SMART | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping contractor was hand digging adjacent to the house when they struck 1 2 service line No USA calls were made prior to digging No evacuations were required since no one was home FD assisted with eliminating ignition sources and RFA for Distribution was requested to control and repair the damaged service Non Haz made before IC handed over to Distribution Field Supvr II
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. No one onsite.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MIKE KELLY CONSTUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | rd party contractor contacted SoCal gas asking for a cutback to be done that day. we told them they would have to be scheduled. instead of waiting they rolled back our service but still hit it with a shovel while digging.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CIDRO CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while trenching for a new water main the contractor was trying to move a very large boulder and it rolled and hooked the service and severed our 0.5 inch service.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 10 |  | EASLEY CONCRETE | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor exposed service line in work area and while trenching further the operator hit 0.5 inch service with excavator bucket.ï¿½ Area USA delineations were removed covered during trenching operations.ï¿½ USA Flag was found directly above damaged service upon arrival and pictured for claims.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-12-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2021-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | 101 CONSTRUCTION | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors were diggingï¿½for a foundation and hit our 0.5 inch pla service with a shovel. They did not have a valid USA.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-06-15 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | SNELSON | CERES | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Signal interference from old steel pipe led locator to pick up steel line instead of the wire on the plastic service.ï¿½ The service was marked as plastic, when Snelson dug on mark and found a steel line,ï¿½ they did not stop the job to determine why steel was exposed instead of plastic as marked. Instead they continued to Dig and hit the plastic service 8 feet from the Marked service.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CASSIDY POSTAL FENCING | SANTA MARIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while digging for fence post. No USA.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4057 |  | 8 |  | MGE UNDERGROUND | PASO ROBLES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | A third party contractor damaged a 1/2 inch stub with a backhoe, causing a release of gas. SoCalGas crews responded and controlled the gas. There were no injuries resulting from this incident. The incident was reported to the CPUC when SoCalGas became aware of media coverage. Further investigation found the employee could not locate the stub showing in GIS with their equipment, and there was no service measurement information on the stub in the system. The employee tried to contact the excavator to let them know, but could not leave a message. The stub was abandoned same day and all records updated accordingly.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CCB COASTAL COMMUNITY BUILDER | OCEANO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged stubï¿½as it was being exposed to extend by a backhoe. No USA.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HCI CONSTRUCTION | SANTA MARIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Damage All USA Markings Accurate Contractor Failed To Exercise Caution Around Gas Service
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Trenching to install conduits.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SANTA MARIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit line while grading over service.ï¿½ No USA.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | HUGHESNET DISH | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. 3rd party contractor digging to install satellite pedestal.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | S S DIRECTIONAL DRILLING | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors were potholing to find gas line when gas line was struck with hand tools. All lines were marked correctly.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 5 |  | HQ CONTRACTOR | SANTA MARIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Work For Frontierï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | KIRK CONSTRUCTION | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit black cap off punch tee
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SANTA MARIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowners handy man, was digging a hole to fix fence and damaged gas line with hand tool.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-01-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SANTA MARIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service marked 0.5 inch PLA, homeowner found old 0.75 inch steel and thought that it was the active gas line, began using Mini excavator and dug into 0.5 inch plastic service.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | LNG CABLE | SANTA MARIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SANTA MARIA | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | Contractor with expired USA ticket hit marked 1 2 pla svc
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-08-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | G M ENGINEERING | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit buried facility with back hoe after pipe was hand exposed USA marked correctly
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SANTA MARIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA ticket expired Existing marks were accurate Homeowner hit gas line while potholing by hand
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SANTA MARIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Home owner hit service while excavating USA Valid Marks visible
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FANCO DEVELOPMENT INC | SANTA MARIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor with expired usa hit plastic svc
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-03-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SHEA HOMES | ORCUTT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Was not able to make contact with responsible party. Construction workers called to report smell of gas. Work is being performed for Shea Homes, contractors on site wasï¿½Joseph Engineering. Call site contact to request USA tickets for the project and which company was excavating at the time. Failed to get response.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WILSON EXCAVATION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged the 0.5 inch pla stub while trying to expose to with backhoe. No USA. Contractor was digging trenches for new gas.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RYAN MATHESON | SANTA MARIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | PLUMBER UNKNOWN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Branch service hit with shovel or pick while trenching Contractor pinched line No gas migration Line capped due to raw sewage in trench No road closure no police fire or media
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2021-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HELPING HAND CONSTRUCTION | SANTA MARIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Branch service damaged by contractor digging to install new sewer Service pinched by contractor No gas migration Service capped due to unsanitary working conditions Raw sewage in trench Dispatch notified and memo placed on accounts No injuries no Fire Dept no evacuations
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2021-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SOLVANG | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damage by home owner. No USA.
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2021-09-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | REDFERN GARDENING SERVICE | SANTA YNEZ | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2021-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | J AMP AMP K POOL CONSTRUCTION INC | SANTA YNEZ |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customers claims he did not damage pipe and only smelled gas when he was digging to expose previously repair at Clamp. Evidence of tampering with clamp from gouges in clamp.
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2021-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MCELWAIN CONSTRUCTION COMP | SOLVANG | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Digging to install gas house line to pool heater struck Gas Company service with hand tools. No USA ticket for work.
Southern California Gas Company | N | SANTA BARBARA | SUMMERLAND | 2021-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ALEJANDRO LANDSCAPE | MONTECITO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 2 PLA Service damaged by a shovel during landscaping work
Southern California Gas Company | N | TULARE | DINUBA | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | AGEE | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while grading contractor did not pot hole service which was marked correctly and visible
Southern California Gas Company | N | TULARE | DINUBA | 2021-05-19 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | QUALITY LANDSCAPE CONSTRUCTION | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Landscaper trenching for tree root barriers. USA was called and service was located properly.
Southern California Gas Company | N | TULARE | DINUBA | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | WESTSCAPES | HANFORD |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 1 2 plastic line crew made permanent repairs
Southern California Gas Company | N | TULARE | EARLIMART | 2021-11-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  |  | NA | EXAEL VALDOVINOS | EARLIMART | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 0.5 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | EARLIMART | 2021-06-02 | Third party excavation damage | Main | Steel | Not Available | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 30001 |  |  | NA | NICHOLAS CONSTRUCTION | SHAFTER | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating prior to having a valid usa ticket and broke a 2 inch HP main.
Southern California Gas Company | N | TULARE | EARLIMART | 2021-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARMANDO RUIZ | EARLIMART | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to install a fence
Southern California Gas Company | N | TULARE | EXETER | 2021-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | WABO GENERAL CONTRACTORS | HERCULES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to maintain marks and damaged 0.5 inch service.
Southern California Gas Company | N | TULARE | EXETER | 2021-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LIFE WATER SOLUTIONS | FRESNO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging trench to install new sewer line for adu.ï¿½ Claims the dirt was super soft and sliced into 2 inch plastic main with shovel.ï¿½ No valid USA ticket for job being done at the time.ï¿½ Crews main permanent repairs with new 4 feet section and 2 couplings.ï¿½ï¿½
Southern California Gas Company | N | TULARE | LINDSAY | 2021-02-19 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25001 |  |  | NA | UNRUH ENGINEERING | WOODLAKE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was boring to install electrical conduit, they did not pot hole our marked facilities and damaged 2 inch steel main.
Southern California Gas Company | N | TULARE | LINDSAY | 2021-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | STREAMLINE IRRIGATION | KINGSBURG | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1 stub on 2 steel main with while excavating to install irrigation lines were marked but contractor removed whiskers while grading
Southern California Gas Company | N | TULARE | LINDSAY | 2021-03-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | LINDSAY STATHMORE IRRIGATION DISTRICT | LINDSAY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating to repair water line and damaged 2 inch gas main, contractor did not call in a USA.
Southern California Gas Company | N | TULARE | LINDSAY | 2021-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CITY OF LINDSAY | LINDSAY |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ï¿½
Southern California Gas Company | N | TULARE | LINDSAY | 2021-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | LINDSAY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged a 0.5 inch plastic line, crew made permanent repairs, occupant was educated about USA law.
Southern California Gas Company | N | TULARE | OROSI | 2021-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ACCESS GENERAL CONTRACTOR | CORONA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging up service for abadonment and hit the service while doing so. Failed to Hand expose.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | KEVIN CONKLIN | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Bureau of Engineering while working to remove existing concrete sidewalk pulled 0.5 inch plastic service encased in 0.75 inch steel with backhoe.ï¿½ Although service was marked correctly, it was damaged at 7 0.5 inch depth.ï¿½ Crew working on sidewalk dug down to 9 inch.ï¿½ Company crew completed permanent repair.ï¿½ï¿½
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-11-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | AFV PLUMBING | LINDSAY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was installing new water line for home owner when they damaged gas service line with a shovel.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | NA | PORTERVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 1 2 plastic gas line while digging to install a mailbox crew made permanent repairs
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | PORTERVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch plastic gas line damaged by occupant, crew made permanent repairs.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BOLLMER EXCAVATION | STRATHMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor failed to pothole marked gas service and hit with backhoe.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TEICHERT CONSTRUCTION | FOWLER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged a 1 inch gas stub, crew made permanent repairs.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-06-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15001 |  | 4 |  | TICHER CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 4 inch main while excavating, the line had already been exposed once but operator failed to maintain clearance.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MITCH BROWN | PORTERVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a shovel and no USA.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GERARDO BEDOLLA | PORTERVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service was damaged by hand digging Gas Ops made permanent repairs Customer was advised to call 811 before digging
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | HOTLINE | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1 inch plastic service while digging for fence post.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MASCORRO PLUMBING | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor dug outside of delineated area.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CAL VALLEY CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 0.5 inch service while grading, contractor failed to pot hole service prior.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-12-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | QUALITY LANDSCAPE CONSTRUCTION INC | VISALIA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching to install irrigation with out calling in a USA ticket and damaged 1 inch plastic service.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | PORTERVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was installing a fence when they damaged a 1 2 plastic service no usa was called in
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 35 | 30 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | PORTERVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor pulled on steel gas line, not leaking, referred to planning for service alteration.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RAUL CONTRERAS | PORTERVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 2 plastic gas service crew made permanent repairs homeowner was educated about USA law
Southern California Gas Company | N | TULARE | PORTERVILLE | 2021-02-18 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 4 |  | MODERN PLUMBING | PORTERVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 2 inch pa main while trying to cut out a root with a sawzall, the main was cut in half. the contractor was working without a USA ticket.
Southern California Gas Company | N | TULARE | SPRINGVILLE | 2021-08-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 18 |  | MARTIN CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole 2 gas main prior to excavating with backhoe and damaged it main was located and marked correctly
Southern California Gas Company | N | TULARE | STRATHMORE | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TEIRCHERT CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 1 2 plastic line while potholing it crew made permanent repairs
Southern California Gas Company | N | TULARE | TEVISTON | 2021-02-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HILARIO GONZALEZ | PIXLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for drain damaged 0.5 inch service.ï¿½
Southern California Gas Company | N | TULARE | TIPTON | 2021-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 175 | 160 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 3 |  | MENDEZ PLUMBING | CORCORAN | CA | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Contractor failed to maintain locate marks and damaged 0.75 inch HP service.
Southern California Gas Company | N | TULARE | TIPTON | 2021-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LIVING WATER POOLS | TULARE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 0.5 inch gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2021-09-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | DCM CONSTRUCTION | SELMA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged a 2 plastic gas main crew made permanent repairs Tracer wire gave signal off by about 4ft Trace wire issue corrected by crew
Southern California Gas Company | N | TULARE | TULARE | 2021-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Material not known | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  |  | NA | DAWSON MAULDING | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 2 steel main main was not leaking but badly damaged Contractor went out the following Tuesday with FOSII A Mosleh to alter the main main alter was planned as a rush by tech services
Southern California Gas Company | N | TULARE | TULARE | 2021-09-21 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 125 | 120 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  | 1 |  | RT NELSON CONSTRUCTION | IVANHOE | CA | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Contractor operator was not supposed to be digging at the time of damage he went to back up the excavator and forgot to raise bucket and hit gas service
Southern California Gas Company | N | TULARE | TULARE | 2021-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 125 | 120 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | DCW CONTRACTORS | VISALIA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor excavated prior to legal start time on usa ticket contractor damaged 3 4 hp service
Southern California Gas Company | N | TULARE | TULARE | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DAWSON MAULDIN | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 0.5 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2021-06-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | RT NELSON COMPANY | IVANHOE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 2 inch plastic main while digging with backhoe to move cable tv line, no USA was called in.
Southern California Gas Company | N | TULARE | TULARE | 2021-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | TULARE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Company contractor arrived to install a new gas service and found the 3 inch main damaged by unknown party, main was not leaking. company contractor made permanent repairs on 2252021.
Southern California Gas Company | N | TULARE | TULARE | 2021-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | DAWSON MAULDIN LLC | SELMA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractors damaged 0.5 plastic service, USA ticket is valid but service was not marked.
Southern California Gas Company | N | TULARE | TULARE | 2021-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DAWSON MAULDIN | SELMA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 in service while pot holing it, service was mis marked.
Southern California Gas Company | N | TULARE | TULARE | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | TULARE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged gas service while replacing water line, no usa was called.
Southern California Gas Company | N | TULARE | TULARE | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | DAWSON MAULDIN | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 0.5 inch gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | 99 PIPELINE | PORTERVILLE |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 0.5 inch service while installing water main, ETD was off his mark. Etd used measurements to locate because he could not get a signal. It was a steel std service with a branch that had been inserted.
Southern California Gas Company | N | TULARE | TULARE | 2021-06-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | 99 PIPELINE | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1 inch plastic main while excavating, the main was marked and potholed but contractor failed to maintain the marks.
Southern California Gas Company | N | TULARE | TULARE | 2021-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | COMFORT NOW | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating to install a c drain and damaged 1 2 plastic service USA was not notified
Southern California Gas Company | N | TULARE | TULARE | 2021-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NOEL AVALOS | TULARE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging and getting ready to pour concrete for wheel chair ramp.
Southern California Gas Company | N | TULARE | TULARE | 2021-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DURANONG FENCING INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 0.5 inch gas line with post hole digger, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2021-11-12 | Third party excavation damage | Main | Steel | Grader/Scraper | 0.75 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DAWSON MAULDING | SELMA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging to install new sewer lateral, U.S.A. was not Valid, contractor dug prior to legal start time.ï¿½
Southern California Gas Company | N | TULARE | TULARE | 2021-10-11 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DAWSON MAULDIN LLC | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging around 2 inch steel main and discovered existing leak, called scg and crew went out and clamped leak.
Southern California Gas Company | N | TULARE | TULARE | 2021-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | 99 PIPE LINE | PORTERVILLE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged a 0.5 inch IPS gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2021-07-28 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | NA | TULARE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged 2 pa gas main while digging to install sewer cleanout no usa was called in and company was unaware of the work
Southern California Gas Company | N | TULARE | TULARE | 2021-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DAWSON MAULDIN LLC | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 0.75 inch stl stub while digging open trench with backhoe. Stub not on GIS
Southern California Gas Company | N | TULARE | VISALIA | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FUSION | MANTECA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2021-02-11 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PSC | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company contractor damaged a 0.5 inch plastic service with hand tools while working a main and service replacement, SCG crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2021-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew was scheduled to repair a code 3 leak. While repairing leak, they found the service line was leaking due to a previous damage.
Southern California Gas Company | N | TULARE | VISALIA | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MORRIS LEVIN SONS | TULARE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | 3rd party contractor struck 0.5 plastic service with tool while excavating for new sewer install
Southern California Gas Company | N | TULARE | VISALIA | 2021-01-06 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | ARB | BAKERSFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor broke 2x1 punch tee off 2 inch main while compacting with backhoe and compaction wheel, pipeline was not properly shaded prior 11 inch cover which caused the equipmentï¿½to come in contact with our facilities.
Southern California Gas Company | N | TULARE | VISALIA | 2021-03-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | NA | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner damaged a 0.5 inch gas line while excavating trench for electrical conduit, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2021-12-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | SERGIO AVALOS | DINUBA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | TULARE | VISALIA | 2021-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Unreported 3rd party damage, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2021-02-10 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARB | VISALIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1 inch main while hand digging bell hole.
Southern California Gas Company | N | TULARE | VISALIA | 2021-11-24 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PLANET SOLAR INCORPORATED | CLOVIS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck plastic main with mini excavator
Southern California Gas Company | N | TULARE | VISALIA | 2021-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MARGARITO VIDRIO | VISALIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged a 1 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2021-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | VISALIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damage service while digging up tree roots, no usa was called.
Southern California Gas Company | N | TULARE | VISALIA | 2021-01-13 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | WEST TECH SYSTEMS | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pot hole the 2 inch plastic gas main and damaged it, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2021-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MATT GEIGER | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavated without USA damaged a 1 gas line crew made permanent repairs Contractor was educated about USA law
Southern California Gas Company | N | TULARE | VISALIA | 2021-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | VISALIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged ï¿½? plastic service by occupant crew made permanent repairs and occupant was educated about USA law
Southern California Gas Company | N | TULARE | VISALIA | 2021-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ROMANAZZI GENERAL ENGINEERING | EXETER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 0.5 inch plastic gas line, crew made permanent repairs, contractor was educated about USA law.
Southern California Gas Company | N | TULARE | VISALIA | 2021-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOTLINE CONSTRUCTION | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 0.5 inch gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2021-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While excavating for sewer repairs homeowner damaged a 1 2 plastic gas line crew made permanent repairs
Southern California Gas Company | N | TULARE | VISALIA | 2021-10-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | INDUSTRIAL ELECTRIC | FRESNO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 0.5 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2021-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BROWNING CONTRACTORS INC | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor excavating to replace sewer line in alley hit a marked 0.5 inch CTS plastic service.
Southern California Gas Company | N | TULARE | VISALIA | 2021-09-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 8 |  | MADCO ELECTRIC | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole 2 gas main prior to machine excavating damaging the main which was marked and visible
Southern California Gas Company | N | TULARE | VISALIA | 2021-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | YANEZ CONSTRUCTION | REEDLEY |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 0.5 inch plastic service while digging with shovel
Southern California Gas Company | N | TULARE | VISALIA | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DURANGO FENCING | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 0.5 inch plastic gas line while while pounding metal post to the ground, contractor was educated about USA law.
Southern California Gas Company | N | TULARE | VISALIA | 2021-10-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DCW CONTRACTORS INC | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor D Corp was working on installation of new water main when struck and un marked cut back service and notified socal gas of damage then crew stopped the gas and abandoned the cut back to make permanent repairs.ï¿½
Southern California Gas Company | N | TULARE | VISALIA | 2021-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HUMBERTO FLORES | VISALIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install a drain pipe occupant damaged a 1 2 plastic gas line crew made permanent repairs
Southern California Gas Company | N | TULARE | VISALIA | 2021-02-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOUGLAS HAMILTON GRAY COM | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2021-02-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 1 |  | GM ENGINEERING | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor digging for fire riser tie in, damaged a 2 inch plastic main, contractor failed to pot hole. Crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2021-03-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | VISALIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged line while trying to remove tree stump, 811 was not called
Southern California Gas Company | N | TULARE | VISALIA | 2021-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | VARO REAL INVESTMENT INC | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 inch gas line by 3rd party contractor, crew made permanent repairs, contractor was educated about USA.
Southern California Gas Company | N | TULARE | VISALIA | 2021-07-31 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JACOB MULLANEY | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 plastic gas line crew made permanent repairs
Southern California Gas Company | N | TULARE | VISALIA | 2021-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | C MICHAEL HILL | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 4 inch plastic main while directional drilling, Plastic main was miss marked and contractor did not pothole to confirm marks.
Southern California Gas Company | N | TULARE | VISALIA | 2021-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | DI ELECTRICAL | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2021-07-20 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 3 |  | AJ EXCAVATION | FRESNO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 2 plastic main while excavating for road work contractor did not have a valid usa for the area being worked
Southern California Gas Company | N | TULARE | VISALIA | 2021-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | QUALITY LANDSCAPE CONSTRUCTION | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 2 plastic gas service crew made permanent repairs contractor was educated about USA law
Southern California Gas Company | N | TULARE | VISALIA | 2021-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CABLE COM | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while excavating to alter cable conduit.
Southern California Gas Company | N | TULARE | WOODLAKE | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SPECTRUM | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 0.5 inch service while pot holing, service was marked correctly.ï¿½
Southern California Gas Company | N | TULARE | WOODLAKE | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Farm Equipment | 0.75 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | WOODLAKE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged gas service, crew made permanent repairs.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-06-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CENTRAL COAST ENGINEERING | BEVERLY HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Abandoned 2 inch main was Damaged by Contractor. Confirmed withï¿½Engineering that main was abandoned. Located and marked active end of main at least a 1000 feet away from damaged location. Followed up with Planning if repair was needed. ï¿½
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CAMARILLO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged our 1 inch plastic service while digging a trench for a drain he was installing.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | CAMARILLO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property Owner was digging to install guard post for gas meter when they hit a 0.5 inch Plastic service.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CAMARILLO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was digging for fenceï¿½when they hit a 0.5 inch plastic service with hand tool. No USA
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | EDWIN CRUZ | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The home owner was removing tree roots that were growing in the yard. No Dig Alert was called in.ï¿½
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | JOSE NARANJO | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customers contractor hit and damaged our 0.5 inch service while digging with a post hole digger for a new fence post.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-09-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SHEA HOMES | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Not Gas Co Related 3rd party contractor performing work for the homeowner damaged the plastic gas service No USA no evacuation no injuries and no emergency services
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-04-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PRODUCTION PLUS PLUMBING | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Production Plumbing trenching for sewer line for Shea Home new construction. Struck 0.5 plastic stub out for new residential homes.ï¿½ No USA called.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JAY GARCIA | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor for home owner was digging trench for drainage when they struck a 0.5 inch Plastic gas service with jack hammer.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CAMARILLO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 2 PLA service damage by owner occupant during tree removal
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALEX CUEVAS | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called in for this job
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FENCE FACTORY | VENTURA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Damaged Main Digging for Sewer.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-02-25 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | INTEGRITY | RIALTO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company contractor damaged 0.5 plastic service with shovel.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 2 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | A B CONSTRUCTION | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 PLA service was damaged by a 3rd Party Contractor who incorrectly assumed that the pipe was house line that had been closed at the valve
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | STOCK TRENCHING | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | CAMARILLO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA No leak detected on investigation of this main damage Permanent repairs made to damage section of 2 PLA Main
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-09-14 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | LANDSCAPE DEVELOPEMENT | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 2 main USA marks clearly marked with yellow paint Permanent repairs completed by crew
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-05-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | AFFORDABLE PLUMBING | VENTURA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PLA service was damage by a backhoe that was digging to expose the septic system. USA was notified after the damage occurred.ï¿½
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ADVANCED SANITATION | CAMARILLO |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called in for this job.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | THOUSAND OAKS PLUMBING JOHN BARRON | WESTLAKE VILLAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch PLA branch service was struck with a shovel during excavation to work on drainage system.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2021-04-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SAULET MASONARY | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called in for this job.
Southern California Gas Company | N | VENTURA | FILLMORE | 2021-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | FILLMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA was current and located and marked correctly
Southern California Gas Company | N | VENTURA | FILLMORE | 2021-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CALIFORNIA LAND CARE INC | FILLMORE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hector Quintero, of California Land Care Inc., struck SCG feets service line with a trencher while trenching to install a sprinkler system.
Southern California Gas Company | N | VENTURA | FILLMORE | 2021-07-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HEARTSTONE HOMES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The damage to the 1 2 PLA service was discovered by a field technician after the fact The damage was repaired on the same day but the technician was unable to gather much information on who might have caused it
Southern California Gas Company | N | VENTURA | FILLMORE | 2021-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | M BONILLA | FILLMORE |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit marked service line with Shovel.ï¿½
Southern California Gas Company | N | VENTURA | MOORPARK | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ROOTER HERO PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Rooter Hero plumbing was digging a pot hole when they his a 0.5 inch plastic service. No USA
Southern California Gas Company | N | VENTURA | MOORPARK | 2021-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging becausde hw
Southern California Gas Company | N | VENTURA | MOORPARK | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | MOORPARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home Owner was digging Drainage trench when the struck a 0.5 inchplastic service with hand tools. No USA ticket.
Southern California Gas Company | N | VENTURA | MOORPARK | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CLEARFLO POOLS INCORPORATED | MOORPARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas Serviced damagedï¿½by Pool contractor performing work for home owner. No USA.
Southern California Gas Company | N | VENTURA | MOORPARK | 2021-02-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | C GAILLARD | MOORPARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic service with shovel.
Southern California Gas Company | N | VENTURA | MOORPARK | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | NA | MOORPARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner was grading lot and hit 2 inch gas main that supplied five residential homes. No USA Called.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2021-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | THOUSAND OAKS PLUMBING | WESTLAKE VILLAGE |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage Third party contractor hit 2 inch main with backhoe. USA was call marks were visible. Excavator failed to maintain clearance after verifying marks failed to protected the gas line.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2021-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NEWBURY PARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was grading using back hoe when the struck SCG 0.5 feet Plastic service.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2021-05-03 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit gas service with shovel.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2021-05-06 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARB | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ARB Inc damaged 0.5ï¿½plastic service
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2021-04-20 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | APL | NORTH HILLS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service with hand tool.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2021-04-29 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | APL ARIZONA PIPE LINE | NORTH HILLS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 0.5 inch Plastic service with hand tool while doing service replacement for SCG.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2021-05-13 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARIZONA PIPELINE CO | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Arizona Pipeline St
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2021-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | VINYL CONCEPTS INC | NEWBURY PARK |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd part contractor E.H Butland Corp. hit 1 inch Svc. line with mini ex while trenching on property.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2021-02-23 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | APL | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged plastic service with shovel while exposing line.ï¿½
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2021-03-24 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas Company Contractor hit 0.5 plastic service with hand tool while doing service replacement.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2021-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JANISSE SONS INC CONCRETE CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 0.5 inch plastic service while digging footing for post.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2021-03-31 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas Company Contractor Brokeï¿½0.5 inch Plastic service while digging using hand tools.
Southern California Gas Company | N | VENTURA | OAK PARK | 2021-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALPHA 2 OMEGA COMMUNICATION | SYLMAR |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | county of riverside was cutting back on a hill when they hit our gas service with a tractor. no pothole was done to verify the depth of our facility.
Southern California Gas Company | N | VENTURA | OAK PARK | 2021-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BROOKS LANDSCAPE | OAK PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor preforming work for home owner hit 0.50 inch plastic service. No USA.
Southern California Gas Company | N | VENTURA | OAK PARK | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALPHA 2 OMEGA | SYLMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NO USA was called in, pool contractor was digging to install drain and hit gas service with backhoe.
Southern California Gas Company | N | VENTURA | OAK PARK | 2021-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ROOTER SOLUTIONS PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Not Gas Co related The contractor was performing sewer work for the homeowner 1 2 CTS gas service was damaged with a shovel No USA was called
Southern California Gas Company | N | VENTURA | OAK PARK | 2021-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ORANGE PLUMBING | WOODLAND HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor damaged 0.5 inch plastic service with shovel.
Southern California Gas Company | N | VENTURA | OAK VIEW | 2021-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GALLEGOS PLUMBING | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA WAS CALLED IN, While digging to replace sewer, customers contractor hit our service line with shovel.
Southern California Gas Company | N | VENTURA | OJAI | 2021-06-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LT GENERATORS | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called in for this job.
Southern California Gas Company | N | VENTURA | OJAI | 2021-05-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CASITAS MUNICIPAL WATER DISTRICT | OAK VIEW | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Casitas Municipal Waterï¿½damage the gas service at 409 Park Rd, Ojai with a backhoe. The service was damage 1 foot away from the SMC and the location of the damage was unknown the gas was under control. Upon investigation, it was found to be a service damage, not a main damage.ï¿½
Southern California Gas Company | N | VENTURA | OJAI | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | TORO | OXNARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | SCG facility was approximately 30 inch away from the markings. Damage to plastic service was caused by backhoe during trenching operation to install a water main.ï¿½
Southern California Gas Company | N | VENTURA | OJAI | 2021-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TIERRA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party failed to use caution when digging near the 1 2 plastic service
Southern California Gas Company | N | VENTURA | OJAI | 2021-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | OJAI | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Workers wereï¿½grading for a driveway when they went to pull out a large rock and grazed the pipe causing a leak.
Southern California Gas Company | N | VENTURA | OJAI | 2021-06-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 8 |  | RUBEN NAVARRETE | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2 inch Gas main damage by backhoe during trenching operations for water main installation.ï¿½
Southern California Gas Company | N | VENTURA | OXNARD | 2021-08-07 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 50001 |  |  | NA | TORO ENTERPRISES | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Toro Construction hit 3 inch plastic service while grading.
Southern California Gas Company | N | VENTURA | OXNARD | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NICODEMUS CONSTRUCTION | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA 1 2 PLA Service was damaged by a hand shovel
Southern California Gas Company | N | VENTURA | OXNARD | 2021-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1.25 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DFA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The abandoned plastic was damaged The service was not reinstated since the property was under construction
Southern California Gas Company | N | VENTURA | OXNARD | 2021-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NETHOS FENCE | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 2 PLA service damaged by a hand shovel when digging
Southern California Gas Company | N | VENTURA | OXNARD | 2021-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BOB BAKER | OXNARD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA 1 2 PLA service damaged by hand shovel
Southern California Gas Company | N | VENTURA | OXNARD | 2021-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SUNSTONE CONSTRUCTION | NA |  | N | Y | Yes | No | No | Yes | No | Yes | Yes | Damaged service while installing conduit
Southern California Gas Company | N | VENTURA | OXNARD | 2021-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HOMELAND ELECTRIC | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | VENTURA | OXNARD | 2021-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BENJAMIN GUERRERO | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service with shovel.
Southern California Gas Company | N | VENTURA | OXNARD | 2021-11-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PRECISION CONTRACTORS INC | LANCASTER |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | VENTURA | OXNARD | 2021-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TEICHERT PIPELINE | SACRAMENTO |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor damaged plastic service while crossing to install sewer drain.ï¿½
Southern California Gas Company | N | VENTURA | PIRU | 2021-08-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | FENCEWORKS | SANTA PAULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Valid USA Contractor failed to take adequate precaution to avoid damage to plastic service
Southern California Gas Company | N | VENTURA | PIRU | 2021-12-07 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PRECISION DESIGN AND BUILD | NORTH HOLLYWOOD |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 0.5 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | VENTURA | PIRU | 2021-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | PIRU | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged 0.5 inch pla service while digging around the foundation of the home.
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2021-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 0 | 0 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | SANTA PAULA | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damagedï¿½0.5 inch service in 0.75 inch steel casing. Contractor cut into casing believing line was old and abandoned causing damage to the cts pipe inside casing.
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2021-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HOTLINE | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged half inch plastic service while digging.
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2021-08-31 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RAMIRO RUELAS | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The cause of this damage is unknown The LCT that discovered the damage made an attempt to gather information from the developer that was on site at the time of discovery That companies information has been included in this report
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2021-07-21 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TEICHERT PIPELINE | CHINO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Teichert pipeline was performing a service replacement for So Cal Gas when they damaged the live service while boring
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2021-01-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ARP | SANTA PAULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | rd party contractor dug prior to potholing and damaged a 1 inch pla service.ï¿½
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | DARREN WORLEY ARP | SANTA PAULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch plastic service damaged during tree removal on private property.ï¿½
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2021-02-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SAM HILL SONS | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | This is an ongoing project with SCG facilities marked with paint and the developer is aware of the gas facilities being present. Backhoe operator failed to ensure clearance prior to damaging the line.ï¿½
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2021-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SANTA PAULA WATER | SANTA PAULA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No crews called out. ETD was on site andï¿½verified that the hit line by LADWP was abandoned.
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2021-10-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MOUNTAIN WEST | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The ETD located and marked off plans provided by the planner. Per the planner contractor did an infield change to the plans that he was not aware of.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2021-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | MOORPARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor asked to leave site once information obtained from him Area tapped off with caution tape to keep public away from damage location No road closures or evacuations Riser was excavated by contractoas well as the service near the PL of the property where the damage occurred Contractor attempting to tie in to the gas service to run a new line to newly constructed building Home owner confirmed this when they arrived to the site at approx 7 30pm
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2021-11-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LIGHT AND POWER | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not leave enough separation from live service during boring operation.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2021-10-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HAVACHILI | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inch plastic service while while building fence.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2021-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TROW COMPANY | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for footing for roomï¿½addition when they his a 0.5 inch plastic service. No USA
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2021-09-27 | Operator excavation damage | Not Available | Polyethylene Pipe | Boring Equipment | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | ARIZONA PIPELINE | NORTH HILLS | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Arizona Pipeline hit 1 inch unmarked stub wile poring for new main installï¿½
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SUNSET CONSTRUCTION | THOUSAND OAKS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with mini excavator when hit 0.5 inch plastic Service. Service was correctly marked.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2021-09-02 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ARIZONA PIPELINE | NORTH HILLS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG Contractor hit Service with hand tool while doing service replacement.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2021-03-29 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas Company Contractor hit 0.5 inch plastic service with hand tool while replacing gas service.ï¿½
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2021-10-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | GOTHIC LANDSCAPE | SIMI VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Company contractor was potholing a gas service in rocky soil and damaged our 0.5 pla service while digging with a shovel
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2021-09-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAMARILLO PLUMMING | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Not Gas Related 3rd party contractor performing excavations for water lines in new track damaged 1 inch stub at the end of main EFV tripped stopping the gas flow No outages or EMS
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2021-03-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WESTPOINTE HOMES | CALABASAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer was digging for footings with mini excavator when they hit a PE gas stub.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2021-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Material not known | Backhoe/Trackhoe | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | USA BUILDERS CONSTRUCTION INC | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was braking concrete along side of the residence and hit the 0.75 in steel service creating a small hole crew clamp and repaired the small areaï¿½ï¿½ï¿½
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2021-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | J M COMMUNICATIONS | PANORAMA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damaged service while excavating with backhoe
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2021-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HOTLINE CONSTRUCTION | SANTA PAULA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Edison contractor hit 0.50 inch Plastic service while putting in anchor for power pole.ï¿½
Southern California Gas Company | N | VENTURA | SOMIS | 2021-04-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 24 |  | GPM INC | NEWBURY PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was using a backhoe for grading when gas main was hit. SCG ETD marked 5 feet away from digging location.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-01-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | THOUSAND OAKS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA was called in. Main and services was located and marked correctly.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | THOUSAND OAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damaged by customer digging hole to plant new tree. USA not notified.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | THOUSAND OAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Not Gas Corelated. The home owner was installing an irrigation system when he damaged the gas service line with a backhoe.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CITY OF THOUSAND OAKS | NEWBURY PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | City Of thousand oaks technician installing new water service hit like with back hoe during excavating.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CARSON CONSTRUCTION | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading Driveway when the struck a 0.5 inch plastic SCG service . No USA was called in.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JUAN RODRIGUEZ | THOUSAND OAKS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor struck gas service while trying to expose.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PANCZAK CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with excavator and broke 0.5 inch Plastic service. Could not produce USA number.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | R CARMONA | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damaged plastic service with a shovel while attempting to make repairs to the water drainage system.ï¿½
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | A STRAIGHT LINE CONSTRUCTION | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and contractor was removing concrete and while grading they hit our 2 inch main.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-04-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LOS ANGELES ENGINEERING | COVINA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer workingï¿½for the city of Thousand Oaks hit 1 inch plastic service while digging trench for wall footings.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DRAIN MASTERS | OXNARD | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service line while digging for sewer.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VAZQUEZ POOL SPA SERVICE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCG service line hit by Vazquez Pool and Spa Service while digging with hand tools to upgrade pool equipment
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | THOUSAND OAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property Owner dug into 0.5 inch plastic service with shovel whileï¿½trenching for communication install.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TESLA ENERGY | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Tesla Energy was installing a Solar panel for the homeowner and hit Gas Service with a grounding rod. Customer nor the Contractor called Under Ground Service Alert.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CID BUILDERS AND DEVELOPERS | RESEDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating for BBQ line when they struck a 0.5 inch Plastic service.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RATTNER CONSTRUCTION | NEWBURY PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Not Gas Co related 3rd party contractor installing new irrigation lines for homeowner damaged our 1 2 gas service line No USA
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SUB ZERO EXCAVATING | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Was Digging for communication lines with mini excavator when they his 0.5 Plastic service.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | THOUSAND OAKS |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service line damaged by contractor.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2021-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | G DUB INC | DESERT HOT SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged gas service line while digging for electrical. NO USA was called.
Southern California Gas Company | N | VENTURA | VENTURA | 2021-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HARRIS CONSTRUCTION | VALENCIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The 1 2 PLA service was previously cut back for the construction of the property The service was not reinstated
Southern California Gas Company | N | VENTURA | VENTURA | 2021-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | VENTURA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called in for this job.
Southern California Gas Company | N | VENTURA | VENTURA | 2021-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | VENTURA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party hit plastic service while excavating to set fence posts. USA was not called prior to the work starting.
Southern California Gas Company | N | VENTURA | VENTURA | 2021-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | WALKER ELECTRIC | CAMARILLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged plastic service with shovel.
Southern California Gas Company | N | VENTURA | VENTURA | 2021-04-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DALE S BACK HOE SERVICE | SANTA PAULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called in for this job.
Southern California Gas Company | N | VENTURA | VENTURA | 2021-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ERK LUNQUIST | VENTURA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging in electrical conduit and pulled our pipe, tearing it at a nearby coupling
Southern California Gas Company | N | VENTURA | VENTURA | 2021-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 55 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ALFONS CASTELLON | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damagedsevered branched steel service line by contr grading and tree root removal on property line wBobcat equip RFA Gas Ops standby monitored atmosphere and 2 impacted residences completed form 3141 I remained on site until gas ops completed repairs to restore impacted residences temporary. Per LCT By Pass was temporary fixed will return tomorrow 02162021 to repair.ï¿½
Southern California Gas Company | N | VENTURA | VENTURA | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | NA | VENTURA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | installing a fence
Southern California Gas Company | N | VENTURA | VENTURA | 2021-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOSE LANDSCAPE | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to set fence post, contract hit PLA service.
Southern California Gas Company | N | VENTURA | VENTURA | 2021-02-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CANNON CONSTRUCTORS | ENCINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor removing tree stump damaged 2 inch plastic main with backhoe. No USA called in.
Southern California Gas Company | N | VENTURA | VENTURA | 2021-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARB INC | LAKE FOREST | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Customer was digging to make repairs to the sewer and hit the 0.5 inch CTS service with a shovel.
Southern California Gas Company | N | VENTURA | VENTURA | 2021-03-04 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ARB | LAKE FOREST | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | Damage cause by SCG Contractor ARB.ï¿½
Southern California Gas Company | N | VENTURA | VENTURA | 2021-06-07 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | TEICHERT PIPELINES | CHINO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company contractor damaged 0.5 inch plastic service with shovel.
Southern California Gas Company | N | VENTURA | VENTURA | 2021-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC HYDROTECH CORP | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 2 PLA service damage by shovel
Southern California Gas Company | N | VENTURA | VENTURA | 2021-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOHN KISTLER | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for fence when they hit 1 inch the neighbors 1 inch plastic service.
Southern California Gas Company | N | VENTURA | VENTURA | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 11 |  | HOTLINE | VENTURA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Hotline construction damaged a 0.75 inch steel service with a jackhammer prior to having a valid USA ticket.
Southern California Gas Company | N | VENTURA | VENTURA | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JBI ENGINEERING | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Valid USA Service marked correctly Contractor failed to exercise caution while digging near the marked location
Southern California Gas Company | N | VENTURA | VENTURA | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JBI ENGINEERING | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | JBI Construction failed to exercise caution near plastic service that was located and marked correctly
Southern California Gas Company | N | VENTURA | VENTURA | 2021-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DCD CONSTRUCTION | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The plasticï¿½service was struck by a backhoe excavator during digging operations.ï¿½
Southern California Gas Company | N | VENTURA | VENTURA | 2021-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CANDO SERVS | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | third party contractor damaged our 0.50 inch pla service while trenching for a waterline.ï¿½
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2021-11-08 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | VAHDAT CONSTRUCTION | WESTLAKE VILLAGE | CA | N | Y | Yes | Yes | No | Yes | No | No | No | Landscaper was digging for water line repair in private property. Cut service with sawzall. No USA.ï¿½
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2021-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | MULLHOLLAND SECURITY | CANOGA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was hand digging for a post when the hit a 0.5 plastic service with shovel. No USA.
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2021-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LOS ANGELES ENGINEERING INC | COVINA |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Unknown contractorï¿½was digging over gas service damaging gas service. As the ETR was gettingï¿½ï¿½information for damage the contractor made a comment that he was just passing by and was helping the home owner investigate why there was a smell of gas.ï¿½
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2021-12-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a plastic service withï¿½a back hoe
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2021-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MCMASTER HILL CONSTRUCTION | WESTLAKE VILLAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service while digging.
Southern California Gas Company | Y | LOS ANGELES | DOWNEY | 2021-04-22 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 6 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 41900 |  | 40 |  | SELECT ELECTRIC INC | CERRITOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On 4-22-2021, a third-party contractor damaged a 6-inch plastic gas main at 7810 Stewart and Gray Road Downey, CA while boring to install an electrical conduit for a traffic signal light. SoCalGas crew responded and controlled the release of gas. There were no outages due to the incident. The Fire Department shut off the gas to some of our customers out of an abundance of caution. This incident was reported to the CPUC and DOT when SoCalGas became aware of media coverage and due to gas release exceeding 3,000,000 cubic feet.
Southern California Gas Company | Y | LOS ANGELES | LOS ANGELES | 2021-01-09 | Third party excavation damage | Main | Steel | Augur | 6 | 204 | 196 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 55000 |  | 181 |  | SKANKA TRAILER | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | SoCalGas, which had an employee present as stand-by, was notified of a third party damage at Alameda and Temple St., Los Angeles, CA. The third party contractor damaged a 6 inch high pressure steel gas main with an auger. Gas was controlled at 14:33 on 1-9-21. There were no reported fatalities or injuries due to the gas release. The investigation showed the third party contractor had a valid USA ticket A201560744. The third party contractor did not properly expose the main before using the auger equipment. This incident was reported to the DOT and CPUC due to the release of gas and damages exceeding $50,000.
Southern California Gas Company | Y | LOS ANGELES | SANTA MONICA | 2021-04-29 | Third party excavation damage | Main | Steel | Boring Equipment | 16 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 454358 |  | 57 |  | CROWN CASTLE | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 4-29-2021, a third party contractor damaged a 16-inch steel gas main at 1101 Stanford Street, Santa Monica, CA while boring to install telecommunication conduit. SoCalGas crew responded and controlled the release of gas. There were no injuries or further damage resulting from this incident. Investigation of the incident showed there was a valid USA ticket. However, the contractor''s excavation practices were inadequate as it failed to pot-hole the 16-inch main. This incident was reported to DOT and CPUC due to gas release and estimated property damage of $122,000 or more.
Southern California Gas Company | Y | LOS ANGELES | STUDIO CITY | 2021-03-16 | Third party excavation damage | Main | Steel | Augur | 22 | 204 | 190 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1200000 |  | 0 |  | GANGANJEET SINGH | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SoCalGas was notified of third party damage at 2965 Laurel Canyon Blvd Studio City, CA. The third party damaged a 22-inch gas line with an auger. Gas was controlled at 00:31 on 3/17/21. There were no reported fatalities or injuries due to the gas release. The investigation showed the third party was augering for new driveway foundation on an expired USA Ticket. This incident was reported to the DOT and CPUC due to the release of gas and damages exceeding $50,000.
Southern California Gas Company | Y | LOS ANGELES | WOODLAND HILLS | 2021-02-10 | Third party excavation damage | Main | Steel | Augur | 6 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 53150 |  | 0 |  | CALTRANS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SoCalGas was notified of third party damage at 4700 Topanga Canyon Blvd. Woodland Hills, CA. The third party damaged a 6-inch medium pressure steel gas main with an auger. Gas was controlled at 21:33 on 2-10-21. There were no reported fatalities or injuries due to the gas release. The investigation showed the third party was working to install a new street sign without a USA Ticket. This incident was reported to the DOT and CPUC due to the release of gas and damages exceeding $50,000.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-06-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 192 |  | 1 |  | ARIZONA PIPELINE COMPANY | CARSON CITY | NV | Y | Y | Yes | Yes | Yes | Yes | No | Yes | No | Service line was hit with shovel.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 194 |  | 1 |  | ARIZONA PIPELINE COMPANY | CARSON CITY | NV | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 1/2" AA service with sharp shooter due to a facility documentation discrepancy.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 539 |  | 1 |  | HAEN CONTRACTORS | SOUTH LAKE TAHOE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator hit service line with mini excavator, outside of work area.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | OCCUPANT | MODESTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Excavator hit steel service with backhoe while trenching to install new water service. Ticket was not valid and service was incorrectly located due to documentation discrepancy.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-07-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 221 |  | 1 |  | ARCTIC ELECTRIC | STATELINE | NV | N | Y | No | No | No | No | No | No | Yes | Contractor damaged a 1/2" line with a shovel while trenching.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-09-30 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 43 | 43 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 205 |  | 0 |  | SOUTH TAHOE PUBLIC UTILITIY DISTRICT | SOUTH LAKE TAHOE | CA | N | Y | Yes | No | No | No | No | Yes | Yes | South Tahoe PUD damaged pipe wrap on 2-inch steel main with a shovel while working before ticket was valid.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-10-08 | Third party excavation damage | Riser | Polyethylene Pipe | Miscellaneous/Other | 1 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | Yes | Vehicle vs. MSA
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 119 |  | 1 |  | ARIZONA PIPELINE COMPANY | CARSON CITY | NV | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with shovel while exposing for the replacement of the service.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 648 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | No | Yes | Home owner hit gas service with shovel.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1184 |  | 1 |  | JOSE DE JESUS HERNANDEZ | SOUTH LAKE TAHOE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator hit 3/4-inch steel line with excavator.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 45 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | UNKNOWN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | Yes | A cut and capped undocumented 3/4-inch steel service stub was found with previous excavation damage, unknown damaging party
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-11-30 | Third party excavation damage | Meter | Steel | Miscellaneous/Other | 0.75 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | N | No | No | No | No | No | No | Yes | Vehicle vs. MSA
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-09-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 195 |  | 1 |  | GB ENGINEERING | SOUTH LAKE TAHOE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor potholed the line and found an abandoned 1/2-inch AA line, which he mistaken as the live service, and proceeded to use an excavtor when he hit the PE 8100 service.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-09-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 382 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | No | Yes | Homeowner was digging and hit a 1/2" gas service with a shovel.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 149 |  | 0 |  | ARIZONA PIPELINE COMPANY | CARSON CITY | NV | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 1/2" service with shove while removing roots.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-05-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1692 |  | 0 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner installed paver walkway and inserted a nail into ground which hit the gas service.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2021-05-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | SOUTH TAHOE PUBLIC UTILITIES DEPARTMENT | SOUTH LAKE TAHOE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Incorrectly marked main damaged with backhoe, no release of gas.
Southwest Gas Company | N | EL DORADO | TAHOMA | 2021-09-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 348 |  | 1 |  | THOMPSON BUILDERS | NOVATO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator damaged 1/2" service with an excavator while working under an expired ticket. Additionally, contractor failed to pothole service.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2021-07-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 418 |  | 0 |  | TRUCKEE DONNER RECREATION & PARK DISTRICT (TDPR) | TRUCKEE | CA | N | Y | No | No | No | No | No | No | Yes | 1-inch PE service inside PVC sleeve was hit with backhoe.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 673 |  | 1 |  | TRI WEST HOMES | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 1/2" line with an excavator as they failed to verify location by pothole.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 802 |  | 0 |  | STEELE CONSTRUCTION | TAHOE CITY | CA | N | Y | Yes | No | No | No | No | Yes | Yes | Contractor was digging with a mini excavator and damaged a 1-inch line.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2021-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 241 |  | 0 |  | SN EXCAVATION | TRUCKEE | CA | N | Y | Yes | Yes | No | No | No | No | Yes | Excavator damaged a 1/2" service while digging. Line was not located by locate contractor.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2021-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 317 |  | 0 |  | SN EXCAVATION | TRUCKEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1-inch PE service was hit with excavator.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2021-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 590 |  | 1 |  | HANDCRAFTED STRUCTURES | TRUCKEE | CA | N | Y | No | No | No | No | No | No | Yes | Contractor''s backhoe operator hit 1/2-inch PE line with backhoe and left scence.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2021-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 911 |  | 1 |  | BARRAZA CONST. INC. | TRUCKEE | CA | N | Y | No | No | No | No | No | No | Yes | Contractor was digging with an excavator without a dig ticket and broke a 1-inch gas line.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2021-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 206 |  | 0 |  | GOODRICH EXCAVATION | TAHOE CITY | CA | N | Y | No | No | No | No | No | No | Yes | Contractor damaged service with excavator while digging a trench for conduit.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2021-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 405 |  | 1 |  | HEAVY EQUIP INC | TRUCKEE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was digging outside work area damaged service and sleeving, no release of gas.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2021-07-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1417 |  | 1 |  | OCCUPANT | TRUCKEE | CA | N | Y | No | No | No | No | No | No | Yes | Customer damaged 1/2 inch line with hand tools while installing bear box.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2021-05-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 460 |  | 0 |  | OCCUPANT | TRUCKEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service was damaged while digging for new utility trench.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2021-09-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | HEAVY EQUIP INC | TRUCKEE | CA | N | Y | No | No | Yes | Yes | No | Yes | Yes | Contractor damaged 2-inch PE service while working without a ticket.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2021-11-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 149 |  | 0 |  | RUPPERT INC | TAHOE CITY | CA | N | Y | No | No | No | No | No | No | Yes | The contractor hit a 1-inch line with a mini-excavator while digging for sewer.
Southwest Gas Company | N | PLACER | CARNELIAN BAY | 2021-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 43 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | LIBERTY UTILITIES | TAHOE VISTA | CA | N | N | Yes | Yes | No | Yes | No | Yes | No | Liberty Utilities nicked unmarked service with backhoe.
Southwest Gas Company | N | PLACER | HOMEWOOD | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1105 |  | 0 |  | BLACKTOP PAVING | HOMEWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit unmarked service with mini excavator while removing old pavement.
Southwest Gas Company | N | PLACER | HOMEWOOD | 2021-07-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 43 | 43 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1343 |  | 0 |  | VINCIGUERRA CONSTRUCTION | JACKSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 2-inch PE main, locate marks were 3 feet off.
Southwest Gas Company | N | PLACER | HOMEWOOD | 2021-08-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1211 |  | 2 |  | VINCIGUERRA CONSTRUCTION | JACKSON | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor damaged a 1-inch service line with an excavator due to the locator failed to mark service.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2021-09-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1039 |  | 1 |  | NORTH TAHOE PUBLIC UTILITY DISTRICT | TAHOE VISTA | CA | N | Y | No | No | No | No | No | No | Yes | North Tahoe PUD damaged a 1-inch line with digging bar while working without a valid Ticket.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2021-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 675 |  | 1 |  | LIBERTY UTILITIES | TAHOE VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Liberty Utilities hit marked 1-inch PE service with excavator while digging to install power pole supports. Excavator got water line confused with SWG 1-inch service; water runs parallel above 1-inch gas service.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2021-07-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | JP EXCAVATING AND PAVING | TAHOE VISTA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator damaged line due to incomplete locate.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2021-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 506 |  | 1 |  | RK CONTRACTORS | RENO | NV | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1-inch line with a shovel while digging electric conduit.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2021-07-09 | Third party excavation damage | Riser | Polyethylene Pipe | Not Available | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1629 |  | 1 |  | UNKNOWN | NA |  | N | Y | No | No | No | No | No | No | Yes | Vehicle vs. MSA
Southwest Gas Company | N | PLACER | TAHOE CITY | 2021-09-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 222 |  | 0 |  | JACOB MCCAULEY | PORTOLA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was hand digging for an abandonment and nicked a 1/2" pipe with a shovel,
Southwest Gas Company | N | PLACER | TAHOE CITY | 2021-06-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1400 |  | 1 |  | OCCUPANT | TRUCKEE | CA | N | Y | No | No | No | No | No | No | No | Homeowner damaged service with shovel when digging to replace fence.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2021-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3008 |  | 1 |  | VINCIGUERRA CONSTRUCTION | JACKSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 1-inch PE in sleeving with track hoe.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2021-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | OCCUPANT | TAHOE CITY | CA | N | Y | No | No | No | No | No | No | Yes | Homeowner was grading when he hit 1/2" gas service line with a mini excavator.
Southwest Gas Company | N | PLACER | TAHOE VISTA | 2021-11-17 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 684 |  | 6 |  | TAHOE EDGE LAKE BEACH CLUB | TAHOE VISTA | CA | N | Y | No | No | No | No | No | No | Yes | The contractor damaged 1/2-inch main with a shovel while digging for sewer.
Southwest Gas Company | N | PLACER | TAHOE VISTA | 2021-09-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 425 |  | 1 |  | NORTH TAHOE PUBLIC UTILITY DISTRICT | TAHOE VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While digging North Tahoe PUD knocked off chunk of earth and landed on and twisted tap tee.
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2021-09-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 615 |  | 1 |  | D.R. HORTON | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while replacing damaged temporary power pole for D.R. Horton without USA ticket. Contractor left the scene before SWG arrival.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2021-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 641 |  | 1 |  | OCCUPANT | APPLE VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 1/2" PE service while removing/planting tree.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2021-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 566 |  | 2 |  | B&M PLUMBING | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1/2-inch service line with shovel.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2021-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 375 |  | 1 |  | TOMMYS MASONRY | APPLE VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 1/2-inch PE gas service while trenching due to facility documentation discrepancy.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2021-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 930 |  | 1 |  | MINEO BROTHERS SEPTIC | HESPERIA | CA | N | Y | Yes | Yes | No | Yes | No | No | No | Contracotr damaged unmarked service line with mini-excavator while replacing septic tank.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2021-10-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1774 |  | 4 |  | POWELL CONSTRUCTORS INC | FONTANA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 2-inch PE main while work under a valid ticket from October 2020. Re-marks were requested on January 5, 2021. At time of damage, old markings on jobsite were present, but not where damage occurred.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2021-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 248 |  | 1 |  | HIGH DESERT UNDERGROUND | HESPERIA | CA | N | Y | Yes | Yes | No | Yes | No | No | No | Contractor damaged 1/2-inch service with backhoe while working outside of delienated work area.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2021-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 420 |  | 0 |  | OCCUPANT | BARSTOW | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service line while installing a new fence.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2021-10-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4862 |  | 3 |  | AID BUILDERS, INC | LOS ALAMITOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas main while excavating.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2021-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1101 |  | 4 |  | ARTHUR ROMERO | BARSTOW | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homowners'' grandson damaged a 1-inch service line while operating a skip loader on the property.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2021-07-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 934 |  | 1 |  | DESERT EMPIRE DRILLING | BARSTOW | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck 1-inch PE service while drilling for water well. Line was marked from previous replacement job.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2021-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1584 |  | 1 |  | OCCUPANT | BARSTOW | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged the PE service while digging for a septic tank with a pick axe.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2021-01-18 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 921 |  | 1 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor damaged unmarked gas service while potholing after not waiting for resolution to a trouble locate.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2021-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 436 |  | 2 |  | AR JOENS PLUMBING SERVICES | BIG BEAR CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Contractor damaged 1/2-inch PE service line with an excavator.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2021-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 714 |  | 1 |  | AR JOENS PLUMBING SERVICES | BIG BEAR CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While responding to an odor call, Southwest Gas discovered that contractor had damaged service line and attempted own repairs.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2021-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 299 |  | 1 |  | DONALD HISCOCK | BIG BEAR CITY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | While excavating with a shovel a contractor hit a 1/2" service line.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2021-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 761 |  | 2 |  | AMAZON LANDSCAPE & MAINTAINANCE | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Excavator damaged a 1-inch PE service line.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2021-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 438 |  | 1 |  | OCCUPANT | BIG BEAR CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor for homeowner damaged service line with rebar stake.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2021-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 556 |  | 1 |  | CS CONSTRUCTION | CANYON LAKE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2-inch PE service line with a mini excavator.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2021-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 694 |  | 1 |  | RICE FIRE PROTECTION | MORENO VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While excavating for new water line, contractor hit service line with excavator.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2021-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 249 |  | 2 |  | OCCUPANT | BIG BEAR LAKE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A 1/2-inch service line was damaged while occupant was excavating with hand tool for deck posts.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2021-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 199 |  | 1 |  | CHINA PACIFIC | ALHAMBRA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A 1/2" service line was damaged during excavation work.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2021-07-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1149 |  | 0 |  | BORDEN EXCAVATING INC. | CALIMESA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit a 2-inch undocumented stub while trenching for a water main replacement project.
Southwest Gas Company | N | SAN BERNARDINO | HELENDALE | 2021-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1935 |  | 4 |  | ADVANTAGE DIRECTIONAL DRILLING | VICTORVILLE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged service stub with directional bore.
Southwest Gas Company | N | SAN BERNARDINO | HELENDALE | 2021-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 339 |  | 1 |  | SECC CORPORATION | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1/2-inch PE service while potholing for gas line.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-03-23 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1569 |  | 1 |  | HP COMMUNICATIONS INC. | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas main that was mismarked.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-12-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1034 |  | 2 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged a 1-inch PE service with a shovel while digging out a tree stump.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-10-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 569 |  | 1 |  | JORGE INIGUEZ | HESPERIA | CA | N | Y | Yes | No | No | Yes | No | No | No | Homeowner hit a 1-inch gas service line with a backhoe while working outside delineated area.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-03-08 | Operator excavation damage | A service line with no excess flow valve installed | PVC Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 852 |  | 0 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | While trenching to install new 2'''' PE gas main contractor hit and damaged an undocumented PVC stub
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-12-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 639 |  | 1 |  | ASPLUNDH | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | No | No | No | No | Contractor damaged unmarked gas service.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 258 |  | 1 |  | OASIS CUSTOM POOLS | PHELAN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | Pool contractor damaged riser while excavating to install water and electric line for pool.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-04-14 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 863 |  | 1 |  | HEATH CONSULTANTS INC. | HESPERIA | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Leak survey contractor damaged gas service with punch bar while performing bar hole leak survey.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-10-05 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 752 |  | 2 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-11-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1297 |  | 2 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor damaged 1/2-inch PE service when they failed to confirm all marks were present before digging. The Line Locate Contractor did not have the service located to the address.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 750 |  | 1 |  | DONOVAN HOMES | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2-inch PE service.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1273 |  | 1 |  | POWERTEC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with sharpshooter while potholing.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 274 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service with shovel
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 566 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was installing new sewer line on property when 1/2" service was damaged.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 284 |  | 1 |  | WESTERN CONSTRUCTION | PHELAN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1/2-inch PE service while potholing for gas service.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-04-06 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1297 |  | 1 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavattor failed to verify service line when potholed.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1213 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit gas service with shovel while fixing the sewer
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2021-10-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 40 | 36 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 2044 |  | 0 |  | BELCO ELECNOR GROUP | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failure to pothole and damaged 4-inch PE Main with no release of gas.
Southwest Gas Company | N | SAN BERNARDINO | HINKLEY | 2021-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 611 |  | 1 |  | HAEFELE SEPTIC AND PLUMBING | BARSTOW | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit marked line while grading.
Southwest Gas Company | N | SAN BERNARDINO | LUCERNE VALLEY | 2021-01-08 | Operator excavation damage | A service line with no excess flow valve installed | PVC Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2201 |  | 0 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | No | No | No | Yes | Yes | Undocumented service stub hit with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | OAK HILLS | 2021-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 605 |  | 2 |  | OCCUPANT | OAK HILLS | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit service line while removing tree stump.
Southwest Gas Company | N | SAN BERNARDINO | OAK HILLS | 2021-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1189 |  | 1 |  | ROYAL COMMUNICATIONS GROUP | BUENA PARK | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor damaged gas service that was not located.
Southwest Gas Company | N | SAN BERNARDINO | SUGARLOAF | 2021-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 310 |  | 0 |  | OCCUPANT | SUGARLOAF | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was excavating on his property with a small backhoe and hit a half-inch service line. The homeowner is a propane customer and believed he did not have natural gas service to his address.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-09-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 853 |  | 0 |  | SUPERIOR MASONARY | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A 1-inch PE branch service was damage by contractor.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-07-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1266 |  | 0 |  | 2020 HEATING AND PLUMBING | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck 2-inch PE main with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 478 |  | 0 |  | H7 CONTRACTING AND ENGINEERING | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1-inch PE stub while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-06-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1121 |  | 0 |  | GOTHIC LANDSCAPING INC | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while excavating to install irrigation pipe.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 648 |  | 1 |  | ENCISO''S POOL CONSTRUCTION INC. | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while excavating to run swimming pool electrical.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 862 |  | 1 |  | MARIA DUARTE | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A 1/2-inch service line was damaged by backhoe during a fence installation.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 340 |  | 0 |  | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1-inch PE stub.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 183 |  | 0 |  | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged stub.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1627 |  | 2 |  | FENCE GUYS | HESPERIA | CA | N | Y | Yes | Yes | No | Yes | No | No | No | Contractors damaged service line while digging to install a fence post outside of the requested work area.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-03-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 680 |  | 1 |  | CARLSON MASONRY | APPLE VALLEY | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit the service line while trying to expose the line.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-08-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 955 |  | 1 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner planting a rose bush hit gas line with a pick.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1065 |  | 2 |  | B TOTAL CONSTRUCTION | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-08-11 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 801 |  | 10 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Second party contractor damaged gas service while potholing for a service replacement.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-01-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6966 |  | 3 |  | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damanged main.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1174 |  | 7 |  | DANIEL''S AFFORDABLE LANDSCAPING | HESPERIA | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with shovel.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 773 |  | 2 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit a 1/2-inch service line hit with tractor.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 634 |  | 1 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner''s friend dug up brick wall footing for city inspector and hit gas service.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1221 |  | 2 |  | MICHAEL DAVIS | ORO GRANDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck and broke a 1/2-inch PE service line.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-07-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6654 |  | 0 |  | SULLY MILLER CONTRACTING COMPANY | BREA | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor hit 2-inch PE main with backhoe that was not located. Previous marks were in the area, but were not for this work.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 672 |  | 0 |  | SUPERIOR MASONRY WALLS LTD | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2-inch PE stub.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 521 |  | 0 |  | HEARTLAND GRADING | CARLSBAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged stub while grading.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2021-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 291 |  | 0 |  | TRENCHERS WEST CONSTRUCTION CO | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged PE stub with backhoe while digging trench for joint trench utilities.
Southwest Gas Company | N | SAN BERNARDINO | YERMO | 2021-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 698 |  | 2 |  | OCCUPANT | DAGGET | CA | N | Y | No | No | Yes | No | No | No | No | Occupant was excavating to install new sewer lines and hit 1/2-inch PE service line and then covered the damage with a plastic bag and backfilled the hole, causing significant underground migration causing evacuations. There was current and correct facility markings, in the excavation areas, however, the occupant did not have a valid USA.