## R217666WVC
Utility Name | Notified of Incident | County Name | Incident City | Incident Date | Cause of Incident | Facility Damage | Material Damaged | Damaged Caused By | Pipe Diameter | MAOP of Operator | Operating Pressure | Gas Leak | Operator Caused Fire | Non-Operator Caused Fire | Natural Gas Explosion | Injured Employees | Non-Employees Injured | Non-Employees Injured NA | Employee Fatalities | Non-Employee Fatalities | Non-Employee Fatalities NA | Cost Damage | Cost Damage NA | Customers Effected | Customers Effected NA | Damage Party Name | Damage Party City | Damage Party State | Damage Party Work Operator | Damage Done To SUOF | Underground Service Alert | Valid USA Ticket | Property Mark Facility | Properly Timely Mark Facility | Standby Provided | Delineations Found | Struck Within Delineations | Summary
Alpine Gas | N | CALAVERAS | VALLEY SPRINGS | 2025-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 206 |  | 1 |  | ROBERT FOWLE | SAN JOSE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DP IS CONTRACTOR /HOEMEOWNER HIS EMPLOYEE HIT MARKED LINE WHILE DIGGING WITH SHOVEL. BLOWING GAS X 12 MINUTES.
Alpine Gas | N | CALAVERAS | VALLEY SPRINGS | 2025-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 250 |  | 1 |  | CALIFORNIA FENCE BUILDER | LIVERMORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DP IS CONTRACTOR HIT MARKED LINE WHILE DIGGING WITH POST HOLE DIGGER. BLOWING GAS X 25 MINUTES.
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2025-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3819 |  | 1 |  | HOMEOWNER | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2025-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5738 |  | 1 |  | HOMEOWNER | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3857 |  | 1 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2025-09-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2827 |  | 1 |  | HOMEOWNER | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2025-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 955 |  | 1 |  | SMITH DENISON CONSTRUCTION COMPANY | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1933 |  | 1 |  | ISLAND ELECTRIC | ALAMEDA | CA | N | Y | No | No | No | No | No | No | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2025-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1856 |  | 2 |  | MILLER PIPELINE | ALAMEDA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2025-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2330 |  | 1 |  | HOMEOWNER | ALAMEDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALBANY | 2025-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1764 |  | 1 |  | GROUNDWORKS | FAIRFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALBANY | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3830 |  | 1 |  | HOMEOWNER | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALBANY | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1739 |  | 1 |  | HOMEOWNER | ALBANY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2025-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2394 |  | 1 |  | WHATCHA GROWIN | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2025-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2593 |  | 1 |  | BAY AREA HOME BUILDERS | BELMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2025-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 160 |  | 1 |  | IMPACT SERVICES ENTERPRISES | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILURE TO MAINTAIN MARKS
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2025-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2010 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2025-07-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1917 |  | 1 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2025-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2667 |  | 1 |  | APB GENERAL ENGINEERING | RICHMOND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2025-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1818 |  | 2 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2025-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1659 |  | 1 |  | NORTH BERKELEY DESIGN AND CONSTRUCTION | BERKELEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2025-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4845 |  | 1 |  | JC CONSTRUCTION | VALLEJO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2025-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3942 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2025-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2273 |  | 0 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2025-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1083 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | ALAMEDA | CASTRO VALLEY | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.25 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2304 |  | 1 |  | SPOSETO ENGINEERING | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | CASTRO VALLEY | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2158 |  | 1 |  | LOCAL CONSTRUCTION | PLEASANT HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | CASTRO VALLEY | 2025-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11128 |  | 1 |  | SPOSETO ENGINEERING | LIVERMORE | CA | N | Y | Yes | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | DUBLIN | 2025-07-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7691 |  | 8 |  | ARB INC | PITTSBURG | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | ALAMEDA | EMERYVILLE | 2025-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2542 |  | 1 |  | MONARCH PLUMBING | VAN NUYS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2025-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3256 |  | 1 |  | HOMEOWNER | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2025-07-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3235 |  | 1 |  | OLIVER & SONS CO | FREMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2025-05-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 784 |  | 1 |  | HOMEOWNER | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1105 |  | 1 |  | CASILLAS CONSTRUCTION | NEWARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 386 |  | 1 |  | FIX-IT PLUMBING | MILPITAS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2025-01-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9778 |  | 8 |  | HOMEOWNER | FREMONT | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | LOCATOR ERROR
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10704 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1819 |  | 1 |  | HOMEOWNER | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2025-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10560 |  | 1 |  | PAVEMENT DATA GROUP | SCOTTS VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS / MAPS
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2025-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1107 |  | 1 |  | AHS LANDSCAPING | CLAYTON | CA | N | Y | Yes | Yes | No | No | No | No | No | EXCAVATED PRIOR TO RECEIVING A POSITIVE RESPONSE FROM ALL UTILITIES
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2025-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2094 |  | 1 |  | HOMEOWNER | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2025-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2638 |  | 1 |  | HOMEOWNER | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2025-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2406 |  | 1 |  | CITY OF HAYWARD | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2025-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3167 |  | 1 |  | HOMEOWNER | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2025-02-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8580 |  | 40 |  | WEST VALLEY CONSTRUCTION | CAMPBELL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2025-06-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2171 |  | 2 |  | MEDERIOS CONSTRUCTION | BRENTWOOD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXPIRED USA TICKET; FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2025-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1988 |  | 1 |  | K S CONSTRUCTION AND DEVELOPERS INC | MOUNTAIN HOUSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 546 |  | 2 |  | CAMPBELL SERVICES LLC | STOCKTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | ALAMEDA | NEWARK | 2025-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 925 |  | 0 |  | WEST VALLEY CONSTRUCTION | CAMPBELL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2445 |  | 1 |  | LOCAL GATE COMPANY | VALLEY VILLAGE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11460 |  | 0 |  | EAST BAY MUNICIPAL UTILITY DISTRICT | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2201 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2775 |  | 1 |  | ANDES CONSTRUCTION INC. | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3220 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-05-14 | Third party excavation damage | Main | Polyethylene Pipe | Vacuum Equipment with Agreement | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 13203 |  | 2 |  | MILLER PIPELINE | ALAMEDA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS / MAPS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 4 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2530 |  | 1 |  | CASTILLO FENCING | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 12 | 9 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2480 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3891 |  | 1 |  | HARRY CLARK HEATING AND AIR CONDITIONING INC. | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 12 | 9 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4225 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1741 |  | 1 |  | ALFAROS HAULING | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1230 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3593 |  | 4 |  | UNITED FENCING SERVICES | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5871 |  | 2 |  | PINNACLE POWER SERVICES | VALLEJO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1072 |  | 0 |  | WORLD VTECH CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10680 |  | 2 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2219 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5223 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2671 |  | 1 |  | CHAN DRAINAGE | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 54 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3366 |  | 1 |  | FIOPTIX INC | CONSHOHOCKEN | PA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 47431 |  | 10 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2232 |  | 1 |  | STREAMLINE PLUMBING | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6436 |  | 2 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1906 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3138 |  | 1 |  | ROTO-ROOTER SERVICE COMPANY | CINCINNATI | OH | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER - DAMAGED SERVICE WHILE BACK FILLING
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1951 |  | 1 |  | MONTCLAIR CONSTRUCTION | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 12 | 9 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1084 |  | 1 |  | EF GOMEZ CEMENT CONTRACTOR INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2044 |  | 2 |  | SANCHEZ CONSTRUCTION | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2325 |  | 1 |  | JIMMY ESPARZA''S CONCRETE PUMPING | ROSEVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 12 | 9 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 517 |  | 1 |  | COOPER CONSTRUCTION AND ENGINEERING | NAPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9675 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 54 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2371 |  | 1 |  | PG&E | OAKLAND | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2025-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3821 |  | 1 |  | VILLALOBOS & ASSOCIATES | CAMPBELL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 24282 |  | 1 |  | HOMEOWNER | PIEDMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2025-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2678 |  | 1 |  | AZUL WORKS | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2025-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 886 |  | 1 |  | HOMEOWNER | PIEDMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATED PRIOR TO RECEIVING A POSITIVE RESPONSE FROM ALL UTILITIES
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2025-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 787 |  | 1 |  | KONIG CONSTRUCTION | MOUNTAIN VIEW | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2025-01-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3886 |  | 1 |  | MORENO''S CONSTRUCTION | DIXON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2025-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1128 |  | 0 |  | GP FIRE | PLEASANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2025-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2008 |  | 1 |  | MEDALLION LANDSCAPE MANAGEMENT | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2025-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2466 |  | 1 |  | JMB CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2025-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3924 |  | 1 |  | WILLIAM SU SU CONSTRUCTION STUDIO | CASTRO VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATED PRIOR TO RECEIVING A POSITIVE RESPONSE FROM ALL UTILITIES
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1760 |  | 1 |  | DIABLO GENERAL ENGINEERING | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATED OUTSIDE DELINEATED AREA
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2025-09-24 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 1.25 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2952 |  | 2 |  | STAR ROOTER | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | UNION CITY | 2025-08-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2072 |  | 1 |  | MARQUEZ FENCING | OROVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | UNION CITY | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1794 |  | 1 |  | EXOTIC FLORA LANDSCAPING AND NURSERY | PACIFIC GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | ALAMEDA | UNION CITY | 2025-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1013 |  | 1 |  | HENKEL & MCCOY WEST | STOCKTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | AMADOR | JACKSON | 2025-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2034 |  | 1 |  | BRIGHT OPS SOLAR | WORCESTER | MA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1787 |  | 2 |  | LVS COMMUNICATIONS | COMPTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATION ISSUE
Pacific Gas and Electric | N | BUTTE | CHICO | 2025-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3528 |  | 1 |  | MILESTONE | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | BUTTE | CHICO | 2025-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5888 |  | 0 |  | LVS COMMUNICATIONS | COMPTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | BUTTE | CHICO | 2025-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 318 |  | 1 |  | HOMEOWNER | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2025-04-02 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8338 |  | 10 |  | MORELLO CONSTRUCTION | PLUMAS LAKE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | CHICO | 2025-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1040 |  | 1 |  | M & M FENCING | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2025-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1268 |  | 2 |  | WEST COAST PIPELINE SOLUTI | KLAMATH FALLS | OR | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | CHICO | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4727 |  | 0 |  | SUN COMMUNICATIONS | BAKERSFIELD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | BUTTE | CHICO | 2025-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4069 |  | 1 |  | PAVEMENT RECYCLING SYSTEMS | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | CHICO | 2025-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2691 |  | 3 |  | M J SHELTON GENERAL ENGINEERING | BAKERSFIELD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | BUTTE | GRIDLEY | 2025-08-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7425 |  | 2 |  | STUDEBAKER ELECTRIC | LOOMIS | CA | N | Y | Yes | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2025-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1236 |  | 1 |  | KINSERS CONSTRUCTION | OROVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2025-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2832 |  | 0 |  | PG&E | OAKLAND | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10477 |  | 1 |  | WEST VALLEY CONSTRUCTION | CAMPBELL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2025-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3449 |  | 1 |  | HOMEOWNER | OROVILLE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2025-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6253 |  | 1 |  | HOMEOWNER | OROVILLE | CA | N | Y | Yes | Yes | No | No | No | No | No | EXCAVATED PRIOR TO RECEIVING A POSITIVE RESPONSE FROM ALL UTILITIES
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2025-07-15 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5234 |  | 0 |  | TRIFECTA CONNECTIONS | LA VERN | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2025-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1425 |  | 1 |  | HOMEOWNER | OROVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2025-08-25 | Third party excavation damage | Main | Steel | Grader/Scraper | 2 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 23701 |  | 0 |  | KNIFE RIVER CONSTRUCTION (KRC) | CHICO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | BUTTE | PARADISE | 2025-05-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2176 |  | 2 |  | DESILVA GATES | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2025-01-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3314 |  | 0 |  | RCI GENERAL ENGINEERING | OROVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2025-05-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1990 |  | 0 |  | AMERICAN DREAM CONSTRUCTION | PARADISE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2025-01-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1428 |  | 0 |  | HOMEOWNER | PARADISE | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2025-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1902 |  | 0 |  | ROADSAFE TRAFFIC SYSTEMS | MCCLELLAN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | BUTTE | PARADISE | 2025-09-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2390 |  | 2 |  | HOMEOWNER | PARADISE | CA | N | Y | No | No | No | No | No | No | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2025-06-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2976 |  | 0 |  | WEST COAST PIPELINE SOLUTION INC | MARYSVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2025-02-10 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3181 |  | 0 |  | WEST VALLEY CONSTRUCTION | CHICO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | COLUSA | COLUSA | 2025-05-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  | 1 |  | HOMEOWNER | COLUSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | COLUSA | COLUSA | 2025-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2852 |  | 1 |  | USA DIRECTIONAL BORE | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | COLUSA | COLUSA | 2025-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1891 |  | 2 |  | R&R HORN CONTRACTORS | CHICO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2025-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1937 |  | 1 |  | HOMEOWNER | ALAMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2025-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7645 |  | 0 |  | CA MC KEE CONSTRUCTION GENERAL CONTRACTOR | ALAMO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO EXPOSE FACILITY WITH HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2025-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3425 |  | 2 |  | HUDSON EXCAVATION | BRENTWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 873 |  | 1 |  | HOMEOWNER | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2025-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2260 |  | 0 |  | ALB | PITTSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | BETHEL ISLAND | 2025-09-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2284 |  | 1 |  | DAVIDSON COMMUNITIES | BETHEL ISLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | BRENTWOOD | 2025-08-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1042 |  | 1 |  | GROUNDWORKS | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | BRENTWOOD | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3602 |  | 1 |  | HOMEOWNER | BRENTWOOD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2025-08-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3331 |  | 1 |  | BAY SIDE FENCING | BRENTWOOD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2025-05-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2402 |  | 2 |  | KJ WOODS CONSTRUCTION INC | SOUTH SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXPIRED USA TICKET; FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2025-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2091 |  | 1 |  | HOMEOWNER | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3376 |  | 1 |  | TENNYSON ELECTRIC | LIVERMORE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2025-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1210 |  | 1 |  | TAK COMMUNICATIONS | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2025-07-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3665 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2025-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1572 |  | 1 |  | NEXT LEVEL HOMES INC | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2025-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2532 |  | 1 |  | OLWIN LANDSCAPE DESIGN & CONSTRUCTION INC | PLEASANTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2025-08-20 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 138 |  | 1 |  | UNIQUE POOLS INC | DANVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2025-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3344 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2025-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1402 |  | 1 |  | JUAN RIOS LANDSCAPING | CLAYTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXPIRED USA TICKET; FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10389 |  | 1 |  | GRAND BUILDERS | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2025-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2402 |  | 1 |  | HOMEOWNER | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | EL CERRITO | 2025-09-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1752 |  | 1 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | EL CERRITO | 2025-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1722 |  | 1 |  | HOMEOWNER | EL CERRITO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | EL CERRITO | 2025-06-04 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 19550 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | KENSINGTON | 2025-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10478 |  | 5 |  | HOMEOWNER | KENSINGTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | KENSINGTON | 2025-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1259 |  | 1 |  | LARA''S CONCRETE INC. | MARTINEZ | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FAILED TO MAINTAIN FIELD MARKS
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2025-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1781 |  | 1 |  | UNDERGROUND ELECTRIC CONSTRUCTION CO LLC | BENICIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2858 |  | 1 |  | THE PLUMBING MINISTRY | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2025-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1129 |  | 2 |  | CRATUS | LAFAYETTE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2025-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1870 |  | 1 |  | CRATUS INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS / MAPS
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2025-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2209 |  | 1 |  | FABIAN ELECTRIC | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2025-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1767 |  | 1 |  | HOMEOWNER | LAFAYETTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2025-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3022 |  | 1 |  | HOMEOWNER | LAFAYETTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | OTHER - USA TICKET EXPIRED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2025-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2229 |  | 1 |  | HOMEOWNER | LAFAYETTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2025-09-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1499 |  | 0 |  | HOMEOWNER | LAFAYETTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2025-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2373 |  | 1 |  | HOMEOWNER | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1227 |  | 1 |  | TAK BROADBAND CA LLC | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2025-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1920 |  | 1 |  | HOMEOWNER | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MORAGA | 2025-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Farm Equipment | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2613 |  | 1 |  | ALAMO LANDSCAPE AND MAINTENANCE | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | MORAGA | 2025-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1426 |  | 1 |  | MODERNSCAPES INNOVATIONS | OAKLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO MAINTAIN FIELD MARKS
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2025-02-19 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6461 |  | 0 |  | R & R PACIFIC CONSTRUCTION | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2250 |  | 1 |  | HENNESSEY''S CONSTRUCTION AND FENCE | FAIRFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2025-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2492 |  | 1 |  | HOMEOWNER | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2025-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 968 |  | 2 |  | HOMEOWNER | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2025-03-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6207 |  | 0 |  | MOUNTAIN CASCADE INC | LIVERMORE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  | 2 |  | HOMEOWNER | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2025-08-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1395 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2025-09-19 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4250 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2025-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1653 |  | 1 |  | BROVELLI CONSTRUCTION INC | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2025-02-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2884 |  | 1 |  | HOMEOWNER | ORINDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2025-05-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1742 |  | 1 |  | C & J FENCING | SAN RAMON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1436 |  | 1 |  | SUN RISE CONSTRUCTION | GUSTINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | PINOLE | 2025-07-14 | Third party excavation damage | Main | Steel | Directional Drilling | 6 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 48714 |  | 0 |  | GREGORY DRILLING | NORTH HIGHLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2484 |  | 1 |  | A&J FENCING | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2025-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2828 |  | 1 |  | HOMEOWNER | PITTSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2025-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 17 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3938 |  | 1 |  | HOMEOWNER | PITTSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2025-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7874 |  | 2 |  | ALTA FENCE CO. | MARTINEZ | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2032 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2025-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1120 |  | 1 |  | BAY SIDE FENCING | ANTIOCH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATED OUTSIDE OF DELINEATED AREA
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2025-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 928 |  | 1 |  | GRN ENTERPRISES INC | GRASS VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2025-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2180 |  | 1 |  | HOMEOWNER | PLEASANT HILL | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | DEBRI FELL AND DAMAGED ASSETS
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2025-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2930 |  | 1 |  | HOMEOWNER | PLEASANT HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1555 |  | 1 |  | HOMEOWNER | PLEASANT HILL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2025-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1907 |  | 1 |  | CUSTOM FIRE PROTECTION INC | COARSEGOLD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2025-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1149 |  | 1 |  | THOMPSON BUILDERS CORP. | NOVATO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2025-02-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1608 |  | 1 |  | HOMEOWNER | PLEASANT HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2025-02-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1044 |  | 1 |  | LIVING STONE PAVER SERVICES | PINOLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2025-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8828 |  | 0 |  | RANSOME COMPANY | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2025-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2270 |  | 0 |  | HUDSON EXCAVATION | BRENTWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS / MAPS
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2390 |  | 0 |  | RUBEN BORG FENCE | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2025-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2061 |  | 1 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1501 |  | 1 |  | MILLER PIPELINE | ALAMEDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2025-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10200 |  | 2 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2025-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 12 | 9 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1570 |  | 1 |  | NEMA CONSTRUCTION | ALBANY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | SAN PABLO | 2025-09-06 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7411 |  | 0 |  | HOMEOWNER | SAN PABLO | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | OTHER - LAWN MOVER SHEARED THE RISER VALVE
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1174 |  | 2 |  | BAY DRAINAGE AND LANDSCAPING | SAN RAMON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2025-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4682 |  | 1 |  | HOMEOWNER | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2025-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1633 |  | 1 |  | DELSUR | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2025-05-01 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2277 |  | 0 |  | HUDSON EXCAVATION | BRENTWOOD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1989 |  | 1 |  | FJ&I ENGINEERING INC | SAN PABLO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2025-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1715 |  | 1 |  | JRP CONCRETE CONSTRUCTION | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2025-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1106 |  | 1 |  | ROTO-ROOTER | WALNUT CREEK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2025-09-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1023 |  | 1 |  | C & J FENCING | SAN RAMON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2008 |  | 1 |  | SANTOS SANCHEZ CONTRACTORS | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2025-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1692 |  | 1 |  | HOMEOWNER | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2025-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1581 |  | 1 |  | PANTHEON DESIGN & CONSTRUCTION | STOCKTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2025-05-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1882 |  | 1 |  | SAXELBY PLUMBING | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2025-08-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3598 |  | 1 |  | JUAN EXCAVATION | MOUNTAIN HOUSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2025-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | VULCAN CONSTRUCTION AND MAINTENANCE | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2025-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1393 |  | 1 |  | LASAR UNDERGROUND CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2025-07-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3708 |  | 0 |  | LANDSCAPE CONNECTION | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1924 |  | 2 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2025-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4437 |  | 1 |  | EDDY METAL FABRICATION | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2025-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2922 |  | 2 |  | PG&E M&C ELECTRIC | FRESNO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FIREBAUGH | 2025-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1374 |  | 1 |  | UNITED PAVEMENT MAINTANCE | FIREBAUGH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FOWLER | 2025-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 1.25 | 12 | 8.5 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2371 |  | 0 |  | CITY OF FOWLER | FOWLER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1741 |  | 8 |  | PROSCAPE LANDSCAPE SERVICE | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1373 |  | 0 |  | ROMO PAVING & GRADING INC | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-05-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4252 |  | 0 |  | CITY OF FRESNO | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2048 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1790 |  | 1 |  | ABOVE ALL PLUMBING | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2458 |  | 6 |  | KRC MANAGEMENT | VAN NUYS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2099 |  | 2 |  | VULCAN | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-05-10 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3249 |  | 4 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5147 |  | 0 |  | KATCH ENVIRONMENTAL | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT CORRECTLY MARKED BY PG&E
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2115 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1059 |  | 1 |  | MATTOS UNDERGROUND CONSTRUCTION INC. | LATON | CA | N | Y | Yes | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1557 |  | 4 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-08-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4914 |  | 3 |  | HB COMMUNICATIONS | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1945 |  | 2 |  | BROWNING CONTRACTORS BCI | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12750 |  | 0 |  | SA RECYCLING | FRESNO | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | OTHER - HIT ASSET WHILE REMOVING ASPHALT
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-03-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 608 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3085 |  | 0 |  | ZUMWALT CONSTRUCTION | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1775 |  | 2 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2172 |  | 1 |  | TRI COUNTY EXCAVATION INC | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3080 |  | 1 |  | VALLEY FENCE COMPANY | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1405 |  | 1 |  | TRI COUNTY EXCAVATION | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1107 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 819 |  | 1 |  | VULCAN CONSTRUCTION | SANTA CLARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25 |  | 1 |  | PG&E | OAKLAND | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 536 |  | 2 |  | LASAR UNDERGROUND | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-08-28 | Third party excavation damage | Main | Steel | Trencher | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1893 |  | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 720 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3249 |  | 8 |  | MAPA PLUMBING SERVICES | CHOWCHILLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 589 |  | 0 |  | NA | NA |  | N | Y | No | No | No | No | No | No | No | UNKNOWN,FOUND IN FIELD BY THIRD PARTY CONTRACTOR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5497 |  | 1 |  | KIGGINS CONSTRUCTION | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | KERMAN | 2025-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 53 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1710 |  | 2 |  | RAKKAR DEVELOPMENT & CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | KERMAN | 2025-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 0 |  | HOMEOWNER | KERMAN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | MENDOTA | 2025-02-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6656 |  | 0 |  | AVID WATER | PATTERSON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | FRESNO | MENDOTA | 2025-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2598 |  | 1 |  | EMA CONSTRUCTION INC | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | SELMA | 2025-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2064 |  | 0 |  | EAGLE CONCRETE | SELMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | SELMA | 2025-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4653 |  | 1 |  | HOMEOWNER | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | GLENN | HAMILTON CITY | 2025-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1584 |  | 0 |  | HOMEOWNER | HAMILTON CITY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | GLENN | WILLOWS | 2025-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1188 |  | 2 |  | SITE WORK SOLUTIONS | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | HUMBOLDT | ARCATA | 2025-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14187 |  | 1 |  | HERYFORD ELECTRIC | CARLOTTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO EXPOSE FACILITY WITH HAND TOOLS
Pacific Gas and Electric | N | HUMBOLDT | ARCATA | 2025-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3583 |  | 1 |  | DOBY CLASS | ARCATA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | ARCATA | 2025-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2390 |  | 1 |  | TIM''S PLUMBING | ARCATA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | BAYSIDE | 2025-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1643 |  | 1 |  | HOMEOWNER | BAYSIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2025-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1041 |  | 1 |  | HOMEOWNER | EUREKA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2629 |  | 0 |  | CURB APPEAL CONSTRUCTION | AGOURA HILLS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12758 |  | 0 |  | HOMEOWNER | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1375 |  | 1 |  | BC DRAIN CARE PLUMBING | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2025-06-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3105 |  | 1 |  | HOMEOWNER | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2025-08-29 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8350 |  | 3 |  | HOMEOWNER | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2025-08-27 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 8 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 32 |  | 0 |  | COUNTY OF HUMBOLDT | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2025-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3384 |  | 1 |  | J&G LAWN AND GARDEN | SAN LUIS OBISPO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2112 |  | 1 |  | MICHELS PACIFIC ENERGY | ELK GROVE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | HUMBOLDT | FORTUNA | 2025-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2007 |  | 2 |  | MERCER- FRASER STEVE KOWTKO | EUREKA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | HUMBOLDT | FORTUNA | 2025-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1598 |  | 2 |  | HOMEOWNER | FORTUNA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | MCKINLEYVILLE | 2025-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1352 |  | 1 |  | HOMEOWNER | MCKINLEYVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | MCKINLEYVILLE | 2025-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 300 |  | 1 |  | NORTH COAST FENCING | MCKINLEYVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 992 |  | 3 |  | EQUITY MANAGEMENT INC | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-09-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 765 |  | 0 |  | LANDSCAPE DEVELOPMENT | SEASIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-01-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2469 |  | 1 |  | UNKNOWN | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1284 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3000 |  | 1 |  | SPECTRUM | SANTA ROSA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1615 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2100 |  | 1 |  | CERDA CONCRETE | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1823 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-03-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5682 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1348 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 982 |  | 1 |  | SPECTRUM | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-07-31 | Third party excavation damage | Main | Steel | Grader/Scraper | 2 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 22 |  | 0 |  | STURGEON SERVICES INTERNANTIONAL | BAKERSFEILD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1908 |  | 1 |  | L3 ELECTRIC | LAGUNA | CA | N | Y | No | No | No | No | No | Yes | Yes | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1544 |  | 1 |  | UCI CONSTRUCTION | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 891 |  | 1 |  | CO OPP PLUMBING | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-06-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3142 |  | 10 |  | MASTEC | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-02-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 931 |  | 1 |  | OUTBACK CONTRACTORS, INC | RED BLUFF | CA | Y | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 725 |  | 2 |  | AJ NETCON LLC | CALABAZAS SOUTH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-08-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2166 |  | 6 |  | MASTEC | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2025-05-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 685 |  | 0 |  | LDD CONSTRUCTION | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | RIDGECREST | 2025-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | HOMEOWNER | RIDGECREST | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | RIDGECREST | 2025-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 550 |  | 1 |  | HOMEOWNER | RIDGECREST | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | RIDGECREST | 2025-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 568 |  | 1 |  | IWV WATER COMPANY | RIDGECREST | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | RIDGECREST | 2025-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1115 |  | 1 |  | SIERRA FENCING | RIDGECREST | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | RIDGECREST | 2025-03-17 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2275 |  | 1 |  | FIRST LINE CONSTRUCTION | MORENO VALLEY | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED CORRECTLY
Pacific Gas and Electric | N | KERN | RIDGECREST | 2025-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2318 |  | 2 |  | A&S COMMUNICATION CO | PALMDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | TAFT | 2025-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2442 |  | 1 |  | HPS | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | TAFT | 2025-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 18 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3108 |  | 1 |  | HOMEOWNER | TAFT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | TAFT | 2025-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 18 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2049 |  | 1 |  | SIERRA CONSTRUCTION AND EXCAVATION | MARTINEZ | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | KINGS | AVENAL | 2025-06-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2490 |  | 1 |  | HOMEOWNER | AVENAL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KINGS | KETTLEMAN CITY | 2025-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1879 |  | 3 |  | HOMEOWNER | KETTLEMAN CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 3 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4217 |  | 1 |  | UNITED PAVEMENT MAINTENANCE | HUGHSON | CA | N | Y | Yes | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MADERA | MADERA | 2025-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3586 |  | 1 |  | HOMEOWNER | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3730 |  | 1 |  | PG&E | OAKLAND | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2025-05-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3426 |  | 1 |  | HOMEOWNER | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2025-01-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4780 |  | 0 |  | CVC | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2025-09-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1055 |  | 0 |  | MCCLARD MASONRY CONT. | HANFORD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | MARIN | BELVEDERE | 2025-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2747 |  | 1 |  | HOMEOWNER | BELVEDERE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2025-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1721 |  | 1 |  | BAY PACIFIC PIPELINE | NOVATO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2025-03-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4072 |  | 1 |  | BAY PACIFIC PIPELINE | NOVATO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3492 |  | 1 |  | HOMEOWNER | CORTE MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3839 |  | 1 |  | HOMEOWNER | CORTE MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2025-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 440 |  | 3 |  | ARB | FAIRFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2025-06-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1453 |  | 1 |  | WESTWARD BUILDERS INC | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2025-01-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1584 |  | 1 |  | HOMEOWNER | FAIRFAX | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2025-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Farm Equipment | 0.75 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6661 |  | 1 |  | TREEMASTERS | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2025-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1889 |  | 1 |  | MCARDELL LANDSCAPE INC | PETALUMA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2025-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2371 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2418 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2025-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1245 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2296 |  | 1 |  | BAYSIDE TRENCHLESS | SANTA ROSA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2025-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3475 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS / MAPS
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2025-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1493 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2025-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7352 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2025-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1755 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2025-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 200 |  | 1 |  | SHARK''S PLUMBING | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2781 |  | 1 |  | FERNANDO''S CONSTRUCTION | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2025-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3182 |  | 1 |  | MARIN MUNICIPAL WATER DISTRICT | CORTE MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4726 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2025-09-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2233 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2025-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 667 |  | 1 |  | PG&E | SAN RAMON | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | NOVATO | 2025-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2251 |  | 1 |  | CR CONSTRUCTION-EXCAVATION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | MARIN | NOVATO | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1472 |  | 1 |  | QTC | LINCOLN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATED OUTSIDE OF DELINEATED AREA
Pacific Gas and Electric | N | MARIN | NOVATO | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1831 |  | 1 |  | HOMEOWNER | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2025-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5070 |  | 1 |  | HOMEOWNER | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2025-06-12 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Directional Drilling | 2 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 280 |  | 1 |  | MILLER PIPELINE | ALAMEDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | NOVATO | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3164 |  | 1 |  | NORTH BAY LANDSCAPE MANAGEMENT | SANTA CLARA | CA | N | Y | Yes | Yes | No | No | No | No | No | EXCAVATED PRIOR TO RECEIVING A POSITIVE RESPONSE FROM ALL UTILITIES
Pacific Gas and Electric | N | MARIN | NOVATO | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4176 |  | 1 |  | KATARINA TOTAL YARDSCAPE | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | MARIN | NOVATO | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2508 |  | 1 |  | MARIN POOL SERVICE | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2025-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2367 |  | 2 |  | NEXT LEVEL EXCAVATING | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | NOVATO | 2025-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3467 |  | 1 |  | HOMEOWNER | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | ROSS | 2025-01-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2982 |  | 1 |  | HOMEOWNER | ROSS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | ROSS | 2025-08-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1656 |  | 1 |  | MARTIN TYNAN & SON CONSTRUCTION | BURLINGAME | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | FAILED TO MAINTAIN FIELD MARKS, TICKET EXPIRED
Pacific Gas and Electric | N | MARIN | ROSS | 2025-08-06 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 17918 |  | 0 |  | E K EXCAVATING | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2025-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3548 |  | 2 |  | HOMEOWNER | SAN ANSELMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2025-09-12 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 19247 |  | 23 |  | HOMEOWNER | SAN ANSELMO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2025-05-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 893 |  | 1 |  | HOMEOWNER | SAN ANSELMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2025-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2126 |  | 1 |  | HOMEOWNER | SAN ANSELMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6056 |  | 1 |  | GLOSAGE ENGINEERING | RICHMOND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXPIRED USA TICKET; FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2025-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4073 |  | 1 |  | HOMEOWNER | SAN ANSELMO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2025-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11991 |  | 1 |  | ONGARO & SONS INC | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2025-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1296 |  | 1 |  | HOMEOWNER | SAN RAFAEL | CA | N | N | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2025-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4245 |  | 1 |  | LEO?S TREE SERVICE | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2025-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 872 |  | 1 |  | GREEN THUMB LANDSCAPE | NOVATO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2025-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1144 |  | 1 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2025-07-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8636 |  | 0 |  | GHILOTTI BROTHERS | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2311 |  | 1 |  | KELLY PACIFIC CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1974 |  | 1 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2025-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1746 |  | 1 |  | MAGGIORA & GHILOTTI | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2025-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2464 |  | 1 |  | FJ&I ENGINEERING, INC | SAN PABLO | CA | Y | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY WAS NOT CORRECTLY MARKED
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2598 |  | 0 |  | KENWOOD FENCE COMPANY | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2025-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1974 |  | 8 |  | MAGGIORA & GHILOTTI INC | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | TIBURON | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12767 |  | 1 |  | ULTRA CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | TIBURON | 2025-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1053 |  | 1 |  | HOMEOWNER | TIBURON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | MARIN | TIBURON | 2025-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1832 |  | 1 |  | A-1 GATES & ACCESS | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | TIBURON | 2025-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1598 |  | 1 |  | HOMEOWNER | TIBURON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | TIBURON | 2025-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 858 |  | 1 |  | NERYS ELITE CARPENTRY | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2025-07-11 | Third party excavation damage | Main | Steel | Grader/Scraper | 6 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 56124 |  | 1 |  | GHILOTTI CONSTRUCTION | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1890 |  | 4 |  | ALL GRADE EXCAVATING | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2025-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2130 |  | 1 |  | HOMEOWNER | UKIAH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2025-07-14 | Third party excavation damage | Main | Steel | Grader/Scraper | 6 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 131328 |  | 9 |  | PAVEMENT RECYCLING SYSTEMS | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2121 |  | 1 |  | HOMEOWNER | UKIAH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | ATWATER | 2025-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5568 |  | 2 |  | ADAME COMMUNICATION INC. | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | MERCED | ATWATER | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4660 |  | 2 |  | LVS COMMUNICATIONS | COMPTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | MERCED | ATWATER | 2025-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1386 |  | 2 |  | OMNI UNDERGROUND | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | MERCED | ATWATER | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1480 |  | 2 |  | ADAME COMMUNICATION INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | MERCED | ATWATER | 2025-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4014 |  | 1 |  | ADAME COMMUNICATION INC. | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | MERCED | ATWATER | 2025-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1634 |  | 2 |  | HOMEOWNER | ATWATER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | ATWATER | 2025-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1864 |  | 0 |  | JA HERNANDEZ CONSTRUCTION INC | ATWATER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | ATWATER | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 975 |  | 1 |  | APG SOLAR | ATWATER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | GUSTINE | 2025-06-27 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6287 |  | 0 |  | DANDY CONSTRUCTION INC | FRESNO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXPIRED USA TICKET; FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | MERCED | GUSTINE | 2025-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3100 |  | 2 |  | PRECISION DRILLING | CITRUS HEIGHTS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | MERCED | GUSTINE | 2025-06-18 | Third party excavation damage | Main | Polyethylene Pipe | Vacuum Equipment with Agreement | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6678 |  | 0 |  | DANDY CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | LIVINGSTON | 2025-06-21 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5717 |  | 6 |  | HOMEOWNER | LIVINGSTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | LOS BANOS | 2025-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2984 |  | 1 |  | HOMEOWNER | LOS BANOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | LOS BANOS | 2025-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4203 |  | 1 |  | HOMEOWNER | LOS BANOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | MERCED | 2025-04-02 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2514 |  | 0 |  | JERRYS TRENCHING SERVICE | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | MERCED | 2025-06-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 800 |  | 1 |  | I RAMIREZ CORP | SAN FERNANDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | MERCED | 2025-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1039 |  | 2 |  | ADAME COMMUNICATION INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | MERCED | MERCED | 2025-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8408 |  | 2 |  | ADAME COMMUNICATION INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | MERCED | MERCED | 2025-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 751 |  | 0 |  | RANCHWOOD HOMES | LOS BANOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | MERCED | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 12 | 8.5 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2448 |  | 4 |  | AMERICAN PAVING CO | FRESNO | CA | N | Y | Yes | Yes | No | No | No | No | No | EXCAVATED PRIOR TO RECEIVING A POSITIVE RESPONSE FROM ALL UTILITIES
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2025-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 585 |  | 0 |  | MASTER WORK BUILDERS | CARMEL BY THE SEA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2025-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4582 |  | 1 |  | MARIANO DURANTES CONCRETE AND MASONRY | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20300 |  | 1 |  | REDSTONE CONSTRUCTION INC | ATWATER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS / MAPS
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2025-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1583 |  | 1 |  | COAST ESTATE | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2025-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2654 |  | 1 |  | HOMEOWNER | CARMEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL BY THE SEA | 2025-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 874 |  | 1 |  | HOMEOWNER | CARMEL BY THE SEA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | CARMEL-BY-THE-SEA | 2025-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2040 |  | 2 |  | HOMEOWNER | CARMEL BY THE SEA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL-BY-THE-SEA | 2025-07-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2194 |  | 0 |  | HOULIHAN DEVELOPMENT | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL-BY-THE-SEA | 2025-08-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10886 |  | 26 |  | PACIFIC TRENCHES | LAGUNA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MONTEREY | MARINA | 2025-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2080 |  | 1 |  | SANDALWOOD PROPERTY MAINTENANCE | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MARINA | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2016 |  | 32 |  | HOMEOWNER | MARINA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11053 |  | 1 |  | TREE WORKS | CORONA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2025-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 430 |  | 1 |  | HOMEOWNER | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2025-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3090 |  | 2 |  | BG CONSTRUCTION | MONTEREY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2025-07-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3168 |  | 0 |  | JDS PLUMBING & UNDERGOUND | SEASIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MONTEREY | MOSS LANDING | 2025-09-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1859 |  | 1 |  | ANDERSON PACIFIC | SANTA CLARA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | MONTEREY | PACIFIC GROVE | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1569 |  | 1 |  | HOMEOWNER | PACIFIC GROVE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2025-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 978 |  | 1 |  | DEL MONTE GARDENERS | MONTEREY | CA | N | Y | No | Yes | No | Yes | No | No | Yes | EXCAVATED PRIOR TO MARKS
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2025-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2082 |  | 1 |  | SURRY ELECTRIC | PRUNEDALE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2025-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2335 |  | 1 |  | DYNAMIC LANDSCAPING | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | MONTEREY | PRUNEDALE | 2025-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3394 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | PRUNEDALE | 2025-08-18 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11673 |  | 8 |  | LTZ COMMUNICATIONS | HOUSTON | TX | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO EXPOSE FACILITY WITH HAND TOOLS
Pacific Gas and Electric | N | MONTEREY | PRUNEDALE | 2025-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2310 |  | 1 |  | INNOVATIVE CONSTRUCTION SOLUTIONS | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATED OUTSIDE DELINEATED AREA
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2025-05-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1550 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2025-08-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3355 |  | 1 |  | GILS PLUMBING | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2713 |  | 1 |  | LLANO CONSTRUCTION | HOLLISTER | CA | N | Y | Yes | Yes | Yes | No | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2025-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3636 |  | 2 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2025-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1943 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2025-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 1 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6725 |  | 2 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2025-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1872 |  | 1 |  | GOLZ CONSTRUCTION | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2025-09-17 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7231 |  | 6 |  | CITY OF SALINAS PUBLIC WORKS | SALINAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO EXPOSE FACILITY WITH HAND TOOLS
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2025-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3941 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2025-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3218 |  | 1 |  | ACME PLUMBING | SALINAS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | MONTEREY | SEASIDE | 2025-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2450 |  | 2 |  | HOMEOWNER | SEASIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SEASIDE | 2025-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1406 |  | 0 |  | HOMEOWNER | SEASIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SOLEDAD | 2025-04-28 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20080 |  | 0 |  | ZARA CONSTRUCTION | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | AMERICAN CANYON | 2025-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1834 |  | 1 |  | GHILOTTI CONSTRUCTION | SANTA ROSA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXPIRED USA TICKET; FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | NAPA | AMERICAN CANYON | 2025-08-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1372 |  | 1 |  | KEREX ENGINEERING | MARTINEZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | NAPA | AMERICAN CANYON | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1486 |  | 0 |  | ARB INC | LAKE FOREST | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | NAPA | AMERICAN CANYON | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1929 |  | 1 |  | ADVANCE CONCRETE INC | NOVATO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | NAPA | AMERICAN CANYON | 2025-01-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3292 |  | 7 |  | WEBER GENERAL ENGINEERING | DIXON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | ANGWIN | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 697 |  | 1 |  | HOMEOWNER | ANGWIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | ANGWIN | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4471 |  | 1 |  | VETERAN POWER | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | NAPA | CALISTOGA | 2025-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2068 |  | 1 |  | GHILOTTI CONSTRUCTION | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | NAPA | CALISTOGA | 2025-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1935 |  | 1 |  | LANDMARK | ROCKLIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | CALISTOGA | 2025-06-27 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2146 |  | 0 |  | CALWALLS | BENICIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILURE TO MAINTAIN MARKS
Pacific Gas and Electric | N | NAPA | NAPA | 2025-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1681 |  | 5 |  | MILLER PIPELINE | ALAMEDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | NAPA | 2025-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 54 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7393 |  | 1 |  | HOMEOWNER | NAPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | NAPA | NAPA | 2025-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1.25 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1056 |  | 1 |  | PROPERTY OWNER | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2025-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2552 |  | 1 |  | HOMEOWNER | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2025-09-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 245 |  | 0 |  | RAUL LANDSCAPING | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2025-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2208 |  | 0 |  | PMH CONSTRUCTION | ORANGEVALE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | NAPA | NAPA | 2025-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 54 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3640 |  | 1 |  | HOMEOWNER | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2025-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4720 |  | 1 |  | HOMEOWNER | NAPA | CA | N | N | No | No | No | No | No | No | No | OTHER - METER WAS MOVED BY CONTRACTOR AND CAUSED DAMAGE
Pacific Gas and Electric | N | NAPA | NAPA | 2025-08-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2018 |  | 1 |  | IRONCAT | WINDSOR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2025-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11650 |  | 0 |  | CVE DEMOLITION INC. | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2025-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20626 |  | 0 |  | GHILOTTI BROS | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | NAPA | YOUNTVILLE | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1788 |  | 1 |  | LAPONZA PLUMBING | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | YOUNTVILLE | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1365 |  | 1 |  | AMERICAN LEAK DETECTION | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1298 |  | 1 |  | HOMEOWNER | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2025-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2096 |  | 1 |  | HOMEOWNER | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2185 |  | 1 |  | HOMEOWNER | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2025-04-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 870 |  | 0 |  | BLACKTOP ASPHALT | NEWARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2025-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2680 |  | 1 |  | HOMEOWNER | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2025-05-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1048 |  | 0 |  | PROCIDA LANDSCAPING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | PLACER | AUBURN | 2025-06-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2092 |  | 0 |  | HOMEOWNER | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2025-08-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1569 |  | 0 |  | HOMEOWNER | AUBURN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | PLACER | AUBURN | 2025-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2095 |  | 8 |  | POSITIVE ENERGY | AUBURN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2025-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2659 |  | 1 |  | JEFFERS DOLAN & DOLAN | GRANITE BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2025-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1273 |  | 1 |  | BELL BROTHER''S HEATING & AIR | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2025-07-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2197 |  | 1 |  | HOMEOWNER | GRANITE BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2025-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3914 |  | 1 |  | HOMEOWNER | GRANITE BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | LINCOLN | 2025-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | LAFLEUR CONSTRUCTION | ORANGEVALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | PLACER | LINCOLN | 2025-07-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4543 |  | 1 |  | EXCEL ELECTRIC | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | LINCOLN | 2025-09-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1363 |  | 1 |  | IKES LANDSCAPING | DAVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | LINCOLN | 2025-01-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9714 |  | 0 |  | FLOWLINE CONTRACTOR INC. | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | PLACER | LINCOLN | 2025-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2003 |  | 1 |  | FLOWLINE CONTRACTOR INC. | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | LOOMIS | 2025-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2358 |  | 1 |  | HOMEOWNER | LOOMIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | LOOMIS | 2025-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1616 |  | 1 |  | HOMEOWNER | LOOMIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2025-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2209 |  | 2 |  | RYAN LYNCH CONSTRUCTION | AUBURN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATED PRIOR TO RECEIVING A POSITIVE RESPONSE FROM ALL UTILITIES
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2025-09-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3810 |  | 0 |  | CARDENAS & SON EXCAVATING | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2025-04-18 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4200 |  | 1 |  | MOUNTAIN CASCADE | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2025-08-23 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3238 |  | 4 |  | HOMEOWNER | ROSEVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2025-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1820 |  | 1 |  | TW ENTERPRISES | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2025-09-19 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2865 |  | 0 |  | INFINITY GENERAL ENGR. CONSTRUCTION & DESIGN | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2025-03-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1856 |  | 1 |  | CULTIVATED LANDSCAPE MANAGEMENT | NORTH HIGHLANDS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2025-03-19 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 52 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3696 |  | 1 |  | MOUNTAIN CASCADE INC. | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2025-06-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1259 |  | 1 |  | AMERICAN HOME ENERGY SAVERS | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1680 |  | 4 |  | DIRT MOVERS INC | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2025-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5626 |  | 1 |  | MONTEJANO VENTURES | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2025-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1720 |  | 1 |  | HOMEOWNER | CARMICHAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2025-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3315 |  | 3 |  | HOMEOWNER | CARMICHAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2025-07-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 931 |  | 0 |  | M&H ELECTRIC | FRESNO | CA | N | Y | No | No | No | No | No | No | No | OTHER - SHEERED OFF RISER WITH SKID STEER LOADER WHILE GRADING PROPERTY.
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2025-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3748 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2025-09-23 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1191 |  | 4 |  | LUND CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10650 |  | 2 |  | HOMEOWNER | CITRUS HEIGHTS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2025-04-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Farm Equipment | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2106 |  | 1 |  | HOMEOWNER | CITRUS HEIGHTS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2025-06-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1894 |  | 1 |  | BUTTE COUNTY HOUSING AUTHORITY | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1540 |  | 2 |  | QUEST MEDIA & SUPPLIES | YUBA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2025-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1376 |  | 1 |  | HENRY JOHN WHITNEY | FAIR OAKS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2025-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1634 |  | 2 |  | HOMEOWNER | ELK GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2025-07-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2209 |  | 1 |  | NORTH SKY | MCLELLAN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2025-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2151 |  | 2 |  | NV COMMUNICATIONS | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1264 |  | 1 |  | TOP RAIL FENCE CORP | ELK GROVE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2025-06-13 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5908 |  | 0 |  | JUAN EXCAVATOR SERVICES | OLIVEHURST | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15148 |  | 1 |  | GRANITE CONSTRUCTION CO | WATSONVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER - GAS FACILITY WAS PARTIALLY EMBEDDED IN ASPHALT
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2025-01-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2760 |  | 3 |  | PG&E GAS | OAKLAND | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2025-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1558 |  | 1 |  | HOMEOWNER | FAIR OAKS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2025-02-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5716 |  | 3 |  | 5 STAR RESIDENTIAL AND COMMERCIAL | NORTH HIGHLANDS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2025-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2303 |  | 1 |  | HOMEOWNER | FAIR OAKS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2025-07-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4541 |  | 1 |  | C&R CONCRETE | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2025-05-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1272 |  | 1 |  | NEXT LEVEL HOME PERFORMANCE | DIAMOND SPRINGS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2025-07-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9223 |  | 0 |  | HOMEOWNER | FOLSOM | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2025-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5031 |  | 1 |  | HOMEOWNER | FOLSOM | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | GALT | 2025-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1681 |  | 2 |  | CASTILLO FENCING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SACRAMENTO | GALT | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2192 |  | 0 |  | MAXSIM | GALT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | GALT | 2025-09-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9111 |  | 3 |  | BLACKTOP ASPHALT/ALWAYS PAVING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2025-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2403 |  | 2 |  | HOMEOWNER | NORTH HIGHLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2025-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1469 |  | 1 |  | HOMEOWNER | NORTH HIGHLANDS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2025-05-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1755 |  | 0 |  | COPPER CREEK LANDSCAPING | TULARE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2025-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2779 |  | 1 |  | HOMEOWNER | NORTH HIGHLANDS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2025-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 450 |  | 1 |  | GRANITE CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2025-05-14 | Third party excavation damage | Main | Steel | Grader/Scraper | 2 | 51 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15275 |  | 0 |  | HOMEOWNER | NORTH HIGHLANDS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SACRAMENTO | ORANGEVALE | 2025-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14088 |  | 0 |  | HOMEOWNER | ORANGEVALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | RANCHO CORDOVA | 2025-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20000 |  | 1 |  | ASPIRE COMMUNICATIONS INC | LAKE MARY | FL | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | RIO LINDA | 2025-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2293 |  | 1 |  | ESPINOZA''S CONCRETE | RIO LINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | RIO LINDA | 2025-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7500 |  | 0 |  | MOUNTAIN CASCADE | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXPIRED USA TICKET; FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SACRAMENTO | RIO LINDA | 2025-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2087 |  | 12 |  | HOMEOWNER | RIO LINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-03-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3446 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-03-11 | Third party excavation damage | Meter | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1395 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | CONSTRUCTION DEBRI FELL ON METER
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1823 |  | 1 |  | CAMACHO HOME IMPROVEMENT | WEST SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-07-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3719 |  | 2 |  | GRANDE CONSTRUCTION | BURLINGAME | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2094 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-06-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 330 |  | 1 |  | CENTURY POOL | ORANGEVALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 12 | 8.5 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1252 |  | 1 |  | JW FENCING AND IRON WORKS | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1184 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2757 |  | 1 |  | GROUNDWORKS CA | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-03-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3620 |  | 1 |  | CITY OF SACRAMENTO | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-07-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6309 |  | 0 |  | SANCO PIPEINE | LOS GATOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 423 |  | 1 |  | VULCAN | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1548 |  | 1 |  | ON-SITE ENGINEERING AND PAVING | SEBASTOPOL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3895 |  | 5 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-08-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3024 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-03-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1318 |  | 1 |  | LANDMARK BUILDERS | GRANITE BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-09-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7244 |  | 0 |  | STAR-RAY PIPELINES | EL DORADO HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2070 |  | 1 |  | AERCO PACIFIC CO | RANCHO CORDOVA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1050 |  | 1 |  | CORE | ROSEVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2653 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1174 |  | 2 |  | ST FRANCIS ELECTRIC | SAN LEANDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-04-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1946 |  | 1 |  | FLOREZ PAVING | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATED PRIOR TO RECEIVING A POSITIVE RESPONSE FROM ALL UTILITIES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3800 |  | 1 |  | FLOREZ PAVING | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS / MAPS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-04-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14211 |  | 1 |  | MOUNTAIN CASCADE | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2903 |  | 1 |  | AMERICAN HOME ENERGY SAVERS | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS / MAPS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-08-27 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 21582 |  | 10 |  | SB PLUMBING | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 35083 |  | 2 |  | GRANITE CONSTRUCTION | WATSONVILLE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-09-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4965 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 160 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-07-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3145 |  | 1 |  | VULCAN | FRESNO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-06-26 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 16129 |  | 1 |  | ASTA EXCAVATOR COMPANY | RIO VISTA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2528 |  | 4 |  | CASTILLO FENCING | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1767 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 279 |  | 1 |  | CITY OF SACRAMENTO | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3265 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-08-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5066 |  | 0 |  | FD CONSTRUCTION | PETALUMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-08-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 0 |  | TEICHERT PIPELINES | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1617 |  | 0 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4529 |  | 1 |  | ZEPEDA?S GENERAL CONSTRUCTION | NORTH HIGHLANDS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 803 |  | 0 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2732 |  | 1 |  | NOR CAL FOUNDATION SUPPORT | FAIRFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2535 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2025-08-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9719 |  | 1 |  | SMUD | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN BENITO | HOLLISTER | 2025-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2663 |  | 2 |  | GUTIERREZ CONSTRUCTION | HOLLISTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN BENITO | HOLLISTER | 2025-09-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1240 |  | 0 |  | PREMIER LANDSCAPE | HOLLISTER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN BENITO | HOLLISTER | 2025-07-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1870 |  | 0 |  | PEREZ NURSERY AND LANDSCAPING | BRENTWOOD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 15 | 12 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1911 |  | 1 |  | GHILOTTI CONSTRUCTION | SANTA ROSA | CA | N | Y | Yes | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-02-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1625 |  | 1 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1551 |  | 1 |  | ESQUIVEL GRADING & PAVING INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3211 |  | 1 |  | MICHAEL O''SHAUGHNESSY CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9184 |  | 1 |  | PRECISION ENGINEERING INC | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 9.2 | 7 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3635 |  | 1 |  | SEQUOIA BAY CONSTRUCTION INC | RANCHO CORDOVE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2566 |  | 6 |  | FIDELIS CONSTRUCTION | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-06-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9712 |  | 9 |  | PG&E | OAKLAND | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4028 |  | 1 |  | SMI DEMOLITION CO | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4901 |  | 1 |  | ASSURE MSP INC | PLEASANTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-06-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4345 |  | 2 |  | MICHAEL O''SHAUGHNESSY CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1878 |  | 1 |  | FAST RESPONSE PLUMBLING & ROOTER | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2034 |  | 1 |  | MICHAEL O''SHAUGHNESSY CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-04-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10252 |  | 0 |  | PHOENIX ELECTRIC COMPANY | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1749 |  | 2 |  | MICHAEL HEAVEY CONSTRUCTION INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5821 |  | 1 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | No | Yes | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-04-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3261 |  | 1 |  | SKYTEK GENERAL ENGINEERING | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2163 |  | 1 |  | R & S CONSTRUCTION MANAGEMENT INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-09-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8962 |  | 1 |  | FONTENOY ENGINEERING | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2530 |  | 1 |  | J FLORES CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-02-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15400 |  | 14 |  | SF WATER DEPARTMENT | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-01-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 47687 |  | 1 |  | SAN FRANCISCO WATER DEPARTMENT | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 800 |  | 1 |  | ELITE ENGINEERING CONTRACTORS | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5391 |  | 1 |  | DEL SECCO DIAMOND CORE & SAW | HAYWARD | CA | N | Y | No | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1.25 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2043 |  | 1 |  | MAN-FER-CONSTRUCTION | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 502 |  | 1 |  | LC GENERAL ENGINEERING & CONSTRUCTINON, INC | PLEASANT HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10375 |  | 1 |  | J FLORES CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 12 | 10 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3012 |  | 1 |  | PHASE 3 COMMUNICATIONS INC. | SAN JOSE | CA | N | Y | Yes | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | ESCALON | 2025-05-13 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3440 |  | 4 |  | PG&E | OAKLAND | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | FRENCH CAMP | 2025-04-07 | Third party excavation damage | Riser | Steel | Trencher | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 546 |  | 0 |  | MAYA CONSTRUCTION | FRENCHCAMP | CA | N | N | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LATHROP | 2025-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1378 |  | 1 |  | ROTO ROOTER | ARCATA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LATHROP | 2025-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1317 |  | 1 |  | 805?S FRAMING | MANTECA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | LATHROP | 2025-07-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5215 |  | 0 |  | EVERGREEN LANDSCAPE SOLUTIONS | LODI | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3537 |  | 3 |  | J. RASBERRY GENERAL ENGINEERING | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2025-07-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11356 |  | 0 |  | AV III INC | ANTIOCH | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2025-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1450 |  | 3 |  | CITY OF LODI ELECTRIC DEPT | LODI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2025-08-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1485 |  | 0 |  | HOMEOWNER | LODI | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4666 |  | 1 |  | NACHO?S PLUMBING | LATHROP | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2025-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1529 |  | 1 |  | GATES CONCRETE AND CONSTRUCTION INC. | ACAMPO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2025-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2247 |  | 1 |  | ARTIFICIAL TURF AND LANDSCAPING | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2025-09-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 616 |  | 1 |  | HOMEOWNER | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2025-09-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 597 |  | 0 |  | 3 PHAZE ELECTRIC | MANTECA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2025-07-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2133 |  | 0 |  | TEICHERT UNDERGROUND CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1890 |  | 1 |  | TEICHERT UNDERGROUND | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2025-05-28 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2844 |  | 0 |  | SOUTH IRRIGATION DISTRICT | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2025-07-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2690 |  | 1 |  | INDEPENDENT CONSTRUCTION | CLAYTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2095 |  | 1 |  | COLLINS ELECTRIC | WOODSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2025-04-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1299 |  | 0 |  | EVERGREEN LANDSCAPE | LODI | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | RIPON | 2025-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1846 |  | 2 |  | HOMEOWNER | RIPON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2025-09-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 502 |  | 2 |  | PACIFIC PARKS LANDSCAPING | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2025-06-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1099 |  | 2 |  | TECHCON MONUMENT CONSTRUCTION | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2025-09-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1083 |  | 1 |  | IKE''S LANDSCAPE INC. | DAVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2025-09-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 502 |  | 1 |  | IKE''S LANDSCAPE INC. | DAVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2532 |  | 1 |  | BADILLO CONSTRUCTION & ENGINEERING | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2025-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2240 |  | 4 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2025-08-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7829 |  | 0 |  | DIRT MOVERS | STOCKTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 12 | 8.5 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1382 |  | 1 |  | DISCOUNT PLUMBING ROOTER INC. | DALY CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1005 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1780 |  | 2 |  | HOMEOWNER | STOCKTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2025-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1352 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2025-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1997 |  | 0 |  | AZUL WORKS, INC. | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2025-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2263 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1821 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2025-09-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2695 |  | 1 |  | BAY LANDSCAPE | SAN LORENZO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2025-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1625 |  | 1 |  | HOMEOWNER | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2025-07-02 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15477 |  | 28 |  | DR PIPELINE INC | SAN MATEO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2025-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2185 |  | 1 |  | HOMEOWNER | TRACY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2025-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2427 |  | 0 |  | CALIFORNIA LANDSCAPE SERVICE INC. | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2025-07-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3751 |  | 1 |  | DISCOUNT PLUMBING ROOTER INC. | DALY CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2025-08-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 35056 |  | 3 |  | CITY OF BELMONT PUBLIC WORKS | GRANITE BAY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2025-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6487 |  | 2 |  | FIOPTIX | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2025-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9904 |  | 2 |  | FIOPTIX INC | CONSHOHOCKEN | PA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2025-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5456 |  | 1 |  | NATIONAL PAVER SYSTEMS, INC | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2025-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2192 |  | 2 |  | HOMEOWNER | BELMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2340 |  | 1 |  | HOMEOWNER | BURLINGAME | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2025-06-24 | Third party excavation damage | Main | Steel | Trencher | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2421 |  | 0 |  | J MORAGA CONSTRUCTION | MERCED | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN MATEO | DALY CITY | 2025-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2983 |  | 1 |  | JLG CONCRETE SAW CUTTING | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | DALY CITY | 2025-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 17351 |  | 0 |  | AC EARTHWORKS | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | DALY CITY | 2025-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1598 |  | 2 |  | HOMEOWNER | DALY CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | EAST PALO ALTO | 2025-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6215 |  | 1 |  | WEST BAY SANITARY DISTRICT | MENLO PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | EL GRANADA | 2025-04-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2111 |  | 1 |  | DELANEY CONSTRUCTION | EL GRANADA | CA | N | Y | No | No | No | No | No | No | No | OTHER - SIDEWALK COLLAPSED & DAMAGED LINE
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2025-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2603 |  | 1 |  | NUEVA BUILDERS | FOSTER CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | HALF MOON BAY | 2025-08-22 | Third party excavation damage | Riser | Steel | Trencher | 0.75 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1289 |  | 1 |  | CHRISTIANSEN CONSTRUCTION | CONCORD | CA | N | N | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HALF MOON BAY | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5501 |  | 1 |  | BAY COUNTIES LANDSCAPE & CONSTRUCTION | PLEASANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2025-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2615 |  | 2 |  | UTILITY CONSTRUCTION SERVICES | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2025-07-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3633 |  | 1 |  | ADORNO CONSTRUCTION INC. | CAMPBELL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2025-03-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1269 |  | 1 |  | THE GARDEN ROUTE CO. | SOUTH SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2025-06-02 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11955 |  | 5 |  | HOMEOWNER | HILLSBOROUGH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2025-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1926 |  | 1 |  | BAYVAL ELECTRIC | HILLSBOROUGH | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2025-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4096 |  | 1 |  | MILL-WOOD DESIGNS, LLC | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2025-06-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1015 |  | 1 |  | KAVANAUGH CONSTRUCTION COMPANY | MOUNTAIN VIEW | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2025-08-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1584 |  | 1 |  | SILICON VALLEY ASPHALT | GILROY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2025-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3819 |  | 1 |  | TECHCON MONUMENT CONSTRUCTION | MORGAN HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2025-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2898 |  | 0 |  | MB MILLENNIUM BUILDERS INC | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2025-08-04 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2406 |  | 1 |  | BELL PLUMBING OF SAN MATEO | SANTA CLARA (SAN JOSE DIVISION) | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2025-07-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1711 |  | 1 |  | ADVANCED QUALITY PLUMBING | MORGAN HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SAN MATEO | MILLBRAE | 2025-07-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9872 |  | 4 |  | DISCOUNT PLUMBING ROOTER INC. | DALY CITY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | SAN MATEO | MONTARA | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2969 |  | 1 |  | ROTO-ROOTER SERVICE COMPANY | EAST PALO ALTO | CA | N | Y | Yes | Yes | No | No | No | No | No | EXCAVATED PRIOR TO RECEIVING A POSITIVE RESPONSE FROM ALL UTILITIES
Pacific Gas and Electric | N | SAN MATEO | MONTARA | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1740 |  | 1 |  | DAVID MOSSA EXCAVATION | MONTARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN MATEO | MONTARA | 2025-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3107 |  | 1 |  | SIERRA WEST BUILDERS | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MONTARA | 2025-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2306 |  | 1 |  | VERDURE CONSTRUCTION LLC | HALF MOON BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MOSS BEACH | 2025-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2591 |  | 1 |  | HOMEOWNER | MOSS BEACH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | PACIFICA | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2134 |  | 1 |  | UTILITY CONSTRUCTION SERVICES | SOUTH SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | PACIFICA | 2025-09-23 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12590 |  | 2 |  | ATLAS PLUMBING | SAN BRUNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN MATEO | PORTOLA VALLEY | 2025-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1389 |  | 1 |  | HOMEOWNER | PORTOLA VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | PORTOLA VALLEY | 2025-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9734 |  | 2 |  | MILLENNIAL CONCRETE | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | PORTOLA VALLEY | 2025-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1136 |  | 0 |  | 2911 CONTRACTORS | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | PORTOLA VALLEY | 2025-09-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2464 |  | 1 |  | GO GREEN ENGINEERING | SPRECKLES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2025-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1699 |  | 1 |  | GARY POLLACK CONSTRUCTION AND EXCAVATION | LOS GATOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2025-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4933 |  | 1 |  | SAXELBY PLUMBING | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2219 |  | 1 |  | LAUREL WAY LLC | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2025-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1096 |  | 1 |  | CASEY CONSTRUCTION | REDWOOD CITY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS / MAPS
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2025-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1200 |  | 1 |  | CASEY CONSTRUCTION | REDWOOD CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2025-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6070 |  | 1 |  | BAY AREA PAVING | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2025-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4714 |  | 1 |  | PAVE TECH PAVING | LINCOLN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2025-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8370 |  | 1 |  | DAVID MOSSA EXCAVATION | MONTARA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2236 |  | 1 |  | LAND ESCAPES | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2025-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3273 |  | 1 |  | SIONES CONCRETE CONSTRUCTION | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2025-08-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2452 |  | 2 |  | JMB CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2025-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 105432 |  | 7 |  | MCKIM CORPORATION | GILROY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO MAINTAIN FIELD MARKS
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2025-05-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4300 |  | 1 |  | MAKONI CONSTRUCTION, INC | MENLO PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1138 |  | 1 |  | JMB CONSTRUCTION INC | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2025-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1800 |  | 1 |  | JMB CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2025-06-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2732 |  | 1 |  | JMB CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2025-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2055 |  | 1 |  | MCGUIRE & HESTER | ALAMEDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2025-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1888 |  | 1 |  | HOMEOWNER | SAN CARLOS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2025-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2457 |  | 1 |  | KEREX ENGINNERING INC | PLEASANT HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3205 |  | 2 |  | HOMEOWNER | SAN CARLOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN MATEO | SAN FRANCISCO | 2025-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5628 |  | 0 |  | SILVERADO CONTRACTORS | EMERYVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | OTHER - SIDEWALK COLLAPSE
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2025-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2751 |  | 2 |  | MCKIM CORPORATION | GILROY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2025-04-25 | Third party excavation damage | Not Available | Steel | Miscellaneous/Other | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2631 |  | 1 |  | FELLOWES CONSTRUCTION | SAN CARLOS | CA | N | N | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4037 |  | 1 |  | HOMEOWNER | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2184 |  | 1 |  | ANDERSON?S TREE CARE SPECIALIST, INC. | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2025-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2696 |  | 1 |  | VISION LANDSCAPE & DESIGN INC. | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SOUTH SAN FRANCISCO | 2025-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 16 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3149 |  | 1 |  | UTILITY CONSTRUCTION SERVICES | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | SAN MATEO | SOUTH SAN FRANCISCO | 2025-08-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9548 |  | 1 |  | HOMEOWNER | SOUTH SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | WEST MENLO PARK | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5197 |  | 1 |  | CALIFORNIA UTILITY | LOS GATOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | WOODSIDE | 2025-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5878 |  | 1 |  | SF UNDERGROUND INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN MATEO | WOODSIDE | 2025-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2027 |  | 1 |  | LVI ENGINEERING | SAN RAFAEL | CA | N | Y | Yes | No | No | Yes | No | No | No | EXPIRED USA TICKET
Pacific Gas and Electric | N | SAN MATEO | WOODSIDE | 2025-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3102 |  | 1 |  | UTILITY CONSTRUCTION SERVICES | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2025-03-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5200 |  | 1 |  | HOMEOWNER | CUPERTINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2025-04-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5804 |  | 0 |  | DRYCO | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | GILROY | 2025-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2274 |  | 1 |  | ACE FENCE & GATE | SUNNYVALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SANTA CLARA | GILROY | 2025-06-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1427 |  | 0 |  | APEX DIRECTIONAL DRILLING | SANTA CLARA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SANTA CLARA | GILROY | 2025-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2750 |  | 1 |  | QUALITY FIRST HOME IMPROVEMENT INC | YUBA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | GILROY | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2378 |  | 1 |  | HOMEOWNER | GILROY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS | 2025-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1066 |  | 1 |  | HC CONSTRUCTION LLC / HAI XUCHEN | FREMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS | 2025-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1831 |  | 1 |  | 2911 CONTRACTORS | MADERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2025-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1581 |  | 0 |  | SAND HILL PROPERTY COMPANY | PALO ALTO | CA | N | N | No | No | No | No | No | No | No | OTHER - Sheared off riser with Lawn Mower
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2025-03-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 956 |  | 1 |  | VALCON | CUPERTINO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2025-05-13 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1375 |  | 1 |  | HYLTON PLUMBING INC | SAN JOSE | CA | N | N | No | No | No | No | No | No | No | OTHER - CONTRACTOR ERROR
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2025-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1533 |  | 1 |  | CENTRAL FIRE SERVICES | PLEASANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2025-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4152 |  | 1 |  | HOMEOWNER | MILPITAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2025-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4075 |  | 0 |  | MILLCREEK ELECTRIC INC | CERES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2025-07-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2531 |  | 0 |  | NEWPATH LANDSCAPE SERVICES INC | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2025-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1708 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | No | No | FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2025-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2765 |  | 0 |  | J S MILLER CONSTRUCTION INC. | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 8 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 739 |  | 2 |  | SAN JOSE WATER COMPANY | SAN JOSE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1770 |  | 6 |  | GATOR ROOTING & PLUMBING | FREMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-01-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1353 |  | 1 |  | FINESSE FENCE | LOS BANOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1871 |  | 2 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-07-15 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 30965 |  | 2 |  | PG&E | OAKLAND | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-05-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1639 |  | 1 |  | VILLALOBOS & ASSOCIATES | CAMPBELL | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2085 |  | 1 |  | TOP ROCK CONSTRUCTION | HOLLISTER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-08-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1041 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-02-21 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 16350 |  | 4 |  | LEWIS & TIBBITS | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-07-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1755 |  | 2 |  | FIBERTEL | SAN JOSE | CA | N | Y | Yes | Yes | No | No | No | No | No | EXCAVATED PRIOR TO RECEIVING A POSITIVE RESPONSE FROM ALL UTILITIES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2219 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 3 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9014 |  | 1 |  | TUCKER CONSTRUCTION INC | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2052 |  | 2 |  | R GUZMAN GREENSCAPE INC | LAFAYETTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4823 |  | 1 |  | ASHLAR BUILDING | LATHROP | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 580 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 945 |  | 1 |  | SANCHEZ ELECTRIC | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2826 |  | 1 |  | TUCKER CONSTRUCTION INC | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1813 |  | 2 |  | AJ CONSTRUCTION | FREMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2539 |  | 1 |  | TRUE SOLAR & ELECTRIC INC | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1654 |  | 0 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3406 |  | 1 |  | VITALITY | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10433 |  | 4 |  | CITY OF SAN JOSE | SAN JOSE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2079 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1804 |  | 2 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 833 |  | 2 |  | EAGLE''S PLUMBING | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2602 |  | 2 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 890 |  | 0 |  | HOMEOWNER | SAN JOSE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2025-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4185 |  | 2 |  | MEZA''S FENCE INC | OAKLAND | CA | N | Y | Yes | Yes | No | No | No | No | No | EXCAVATED PRIOR TO RECEIVING A POSITIVE RESPONSE FROM ALL UTILITIES
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2025-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2290 |  | 0 |  | PENINSULA DEMOLITION INCORPORATED | SAN CARLOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2025-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2539 |  | 1 |  | LEWIS & TIBBETTS | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2025-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3441 |  | 0 |  | MK PIPELINES INC | HOLLISTER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2025-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 720 |  | 1 |  | JAZ BUILDERS INC | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2025-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 993 |  | 1 |  | HOMEOWNER | APTOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2025-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 466 |  | 1 |  | MR ROOTER PLUMBING | APTOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SANTA CRUZ | BEN LOMOND | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 955 |  | 1 |  | DAHLEN STRUCTURAL INC. | SCOTTS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | BEN LOMOND | 2025-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 736 |  | 1 |  | ALPHA OMEGA ELECTRIC | SCOTTS VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SANTA CRUZ | BOULDER CREEK | 2025-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1555 |  | 1 |  | TOM''S SEPTIC CONSTRUCTION | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | BOULDER CREEK | 2025-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1040 |  | 0 |  | ANDERSON PACIFIC ENGINEERING | SANTA CLARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SANTA CRUZ | CAPITOLA | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2121 |  | 2 |  | COASTAL EVERGREEN | SCOTTS VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SANTA CRUZ | CAPITOLA | 2025-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1356 |  | 2 |  | TOWER''S ELECTRIC | APTOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | CAPITOLA | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1099 |  | 1 |  | BETZ WORKS | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | SANTA CRUZ | CAPITOLA | 2025-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 818 |  | 1 |  | KRAEMER ENGINEERING | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | FELTON | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 759 |  | 1 |  | HOMEOWNER | FELTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2025-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1403 |  | 1 |  | DOAN CONSTRUCTION | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2025-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WHITLOW CONCRETE | CAPITOLA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2025-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1280 |  | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 915 |  | 1 |  | SHORELINE ELECTRIC | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2025-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2485 |  | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2025-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2262 |  | 0 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2025-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 977 |  | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2025-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1446 |  | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2025-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1119 |  | 1 |  | HOME OWNER | SANTA CRUZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SCOTTS VALLEY | 2025-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2531 |  | 1 |  | HOMEOWNER | SCOTTS VALLEY | CA | N | N | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SCOTTS VALLEY | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2258 |  | 1 |  | BJORN AGAIN RESTORATION | GALT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SOQUEL | 2025-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 944 |  | 1 |  | KJ WOODS | SOUTH SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXPIRED USA TICKET; FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SANTA CRUZ | TWIN LAKES | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2541 |  | 1 |  | BALLESTEROS LANDSCAPE | LINCOLN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE, TICKET EXPIRED
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2025-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1612 |  | 1 |  | MP NEXLEVEL | ROCKLIN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXPIRED USA TICKET; FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2025-03-07 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3877 |  | 3 |  | INTEGRATED HOME SOLUTIONS | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2025-06-12 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6785 |  | 0 |  | MCKIM CORPORATION | GILROY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SHASTA | ANDERSON | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4154 |  | 1 |  | HOMEOWNER | ANDERSON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | ANDERSON | 2025-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2838 |  | 1 |  | HOMEOWNER | ANDERSON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | ANDERSON | 2025-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1390 |  | 2 |  | CAL ELECTRO INC | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2025-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1228 |  | 1 |  | SENTRY PLUMBING & FIRE PROTECTION | REDDING | CA | N | Y | Yes | No | Yes | No | No | No | No | OTHER
Pacific Gas and Electric | N | SHASTA | REDDING | 2025-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2067 |  | 1 |  | EARL?S PERFORMANCE PLUMBING | CHICO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATED OUTSIDE DELINEATED AREA
Pacific Gas and Electric | N | SHASTA | REDDING | 2025-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1379 |  | 1 |  | HOMEOWNER | REDDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SHASTA | REDDING | 2025-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 582 |  | 1 |  | HOMEOWNER | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2025-07-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1406 |  | 1 |  | AXNER EXCAVATING | REDDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SHASTA | REDDING | 2025-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1806 |  | 1 |  | HOMEOWNER | REDDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SHASTA | REDDING | 2025-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5606 |  | 1 |  | CHASE RAY | COTTONWOOD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2025-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 836 |  | 0 |  | EDDIE AXNER CONSTRUCTION | REDDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SOLANO | BENICIA | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1252 |  | 1 |  | G&G DECK AND FENCE | BENICIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SOLANO | BENICIA | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3635 |  | 1 |  | HOMEOWNER | BENICIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | BENICIA | 2025-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9397 |  | 2 |  | HOMEOWNER | BENICIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | BENICIA | 2025-08-14 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8203 |  | 12 |  | DC ELECTRIC MATT SHIPP | PACHECO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SOLANO | BENICIA | 2025-09-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3573 |  | 1 |  | HOMEOWNER | BENICIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2025-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1277 |  | 2 |  | GHILOTTI BROTHERS | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2025-08-18 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9820 |  | 0 |  | DIABLO GENERAL ENGINEERING LLC | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2025-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2666 |  | 1 |  | HM CONCRETE INC | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2025-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2498 |  | 4 |  | FIGUEROA LANDSCAPE COMPANY | WOODLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2025-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2003 |  | 4 |  | SUNRUN | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SOLANO | RIO VISTA | 2025-05-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1608 |  | 1 |  | PACIFIC COAST LANDSCAPE | BYRON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | SUISUN CITY | 2025-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4678 |  | 1 |  | HOMEOWNER | SUISUN CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | SUISUN CITY | 2025-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2244 |  | 1 |  | QUALITY PLUMBING AND ROOTER | ANTIOCH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2025-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2186 |  | 1 |  | SATORI CONSTRUCTION | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2025-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 51 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5707 |  | 1 |  | KOIOS ENGINEERING INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2025-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2359 |  | 1 |  | HOMEOWNER | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2025-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 51 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2992 |  | 1 |  | SCHREDER AND BRANDT MFG | CHICO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2025-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 51 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 47311 |  | 1 |  | HOMEOWNER | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2025-06-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 51 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6402 |  | 2 |  | AMERICAN UNDERGROUND | BYRON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2025-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1767 |  | 2 |  | GHILOTTI CO | SAN RAFAEL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2025-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2300 |  | 1 |  | HOMEOWNER | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2025-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1989 |  | 8 |  | NOR CAL FOUNDATION SUPPORT | FAIRFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2025-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 25 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1429 |  | 1 |  | HOMEOWNER | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2025-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2317 |  | 1 |  | LANDMARK | ROCKLIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2025-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 25 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4117 |  | 1 |  | FOCUS ROOTER PLUMBING | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2025-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1906 |  | 1 |  | HOMEOWNER | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2025-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1118 |  | 1 |  | AHMAD HASSAN LANDSCAPE SERVICES | CAMERON PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1047 |  | 1 |  | HOMEOWNER | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5148 |  | 1 |  | MYERS AND SONS CONSTRUCTION | ORANGE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2025-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 4040 |  | 3 |  | HOMEOWNER | VALLEJO | CA | N | Y | Yes | No | No | No | No | No | No | EXPIRED USA TICKET
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2025-03-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 25 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2677 |  | 0 |  | EVERGREEN LANDSCAPE SOLUTIONS | LODI | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SONOMA | FORESTVILLE | 2025-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8552 |  | 1 |  | HOMEOWNER | FORESTVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3325 |  | 1 |  | HOMEOWNER | HEALDSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2025-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4860 |  | 1 |  | GTZ FENCES | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2025-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11712 |  | 0 |  | NEXT GENERATION OF BUILDERS | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PENNGROVE | 2025-09-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 13109 |  | 1 |  | GHILOTTI BROTHERS | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2025-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4544 |  | 1 |  | EMPIRE LANDSCAPE | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2025-02-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3151 |  | 1 |  | NOR CAL LEAKS | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2025-05-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Farm Equipment | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1433 |  | 0 |  | HOMEOWNER | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2025-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1438 |  | 1 |  | VISTA LANDSCAPE | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2025-09-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5134 |  | 1 |  | HOMEOWNER | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2025-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2568 |  | 0 |  | SERRES CORPORATION | SONOMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILURE TO MAINTAIN MARKS
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2025-06-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1212 |  | 1 |  | HOMEOWNER | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | ROHNERT PARK | 2025-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4368 |  | 1 |  | HOMEOWNER | ROHNERT PARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | ROHNERT PARK | 2025-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2891 |  | 1 |  | HOMEOWNER | ROHNERT PARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-02-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2322 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4050 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3470 |  | 0 |  | HOMEOWNER | SANTA ROSA | CA | N | N | No | No | No | No | No | No | No | WORKER STOOD ON METER SET AND GSL SNAPPED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5078 |  | 1 |  | REDWOOD EMPIRE VINEYARD MANAGEMENT | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4011 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1211 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3115 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-04-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1763 |  | 1 |  | JARCO LAND INC | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 34227 |  | 0 |  | TENNYSON ELECTRIC | LIVERMORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2288 |  | 1 |  | LEDUC AND DEXTER | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO EXPOSE FACILITY WITH HAND TOOLS
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2217 |  | 2 |  | C&C CONTRACTING | COTATI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2765 |  | 1 |  | FLOWRIGHT PLUMBING | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 2 |  | JACKSON''S PAVING & EQUIPMENT RENTAL | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2116 |  | 1 |  | SMI DEMOLITION COMPANY | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2367 |  | 1 |  | REDWOOD RESIDENTIAL FENCE | GRANITE BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2025-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3243 |  | 0 |  | NORTHWEST GENERAL ENGINEERING | SANTA ROSA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS / MAPS
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2025-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2156 |  | 1 |  | MARK CIDDIO WOODWORKS & CONSTRUCTION | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2025-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4431 |  | 1 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2025-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1288 |  | 2 |  | HOMEOWNER | PETALUMA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXPIRED USA TICKET; FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2025-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1948 |  | 1 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2025-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1448 |  | 1 |  | EMPIRE CONSTRUCTION & ENGINEERING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2025-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1087 |  | 1 |  | SCOTT CHARLES POND MCPHERSON | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2025-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7059 |  | 1 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 35527 |  | 1 |  | HOMEOWNER | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2025-06-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6039 |  | 1 |  | HOMEOWNER | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2025-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3820 |  | 1 |  | HENRY GOMEZ CONSTRUCTION | SONOMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATED OUTSIDE DELINEATED AREA
Pacific Gas and Electric | N | SONOMA | SONOMA | 2025-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1765 |  | 0 |  | EK EXCAVATING | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2025-07-16 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8208 |  | 6 |  | OC JONES AND SONS | BERKLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SONOMA | SONOMA | 2025-05-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4023 |  | 0 |  | RDZ CONSTRUCTION | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2025-08-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3141 |  | 1 |  | VISTA LANDSCAPING | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | WINDSOR | 2025-07-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1831 |  | 1 |  | HOMEOWNER | WINDSOR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SONOMA | WINDSOR | 2025-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1533 |  | 1 |  | HOMEOWNER | WINDSOR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2025-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1331 |  | 1 |  | PG&E GAS GC | MODESTO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | STANISLAUS | CERES | 2025-03-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9138 |  | 55 |  | UNITED PAVING | CERES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | STANISLAUS | CERES | 2025-07-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1641 |  | 2 |  | ARAGON INC | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2025-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1495 |  | 2 |  | PG&E GDGC | SAN CARLOS | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | CERES | 2025-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3017 |  | 1 |  | HOMEOWNER | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2025-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 742 |  | 1 |  | JIMENEZ CONCRETE | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2025-09-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5103 |  | 2 |  | PLATINUM GENERAL ENGINEERING | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | STANISLAUS | DENAIR | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3900 |  | 1 |  | HOMEOWNER | DENAIR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | EMPIRE | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1552 |  | 2 |  | HOMEOWNER | EMPIRE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | HUGHSON | 2025-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4132 |  | 1 |  | TURLOCK IRRIGATION DISTRICT | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | HUGHSON | 2025-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3106 |  | 1 |  | HOMEOWNER | HUGHSON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | HUGHSON | 2025-08-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2433 |  | 1 |  | HOMEOWNER | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1839 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-01-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2525 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1279 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1310 |  | 1 |  | B&A CONSTRUCTION | SALIDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2206 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1412 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1098 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1516 |  | 1 |  | AARON RICHARDSON CONSTRUCTION | MODESTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1908 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2168 |  | 1 |  | TITAN FENCE | BENICIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1886 |  | 2 |  | THE ELECTRIC COMPANY | PATTERSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1402 |  | 1 |  | GENJAZZ SOLUTIONS | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3184 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1782 |  | 1 |  | TOSTED ASPHALT INC. | HUGHSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2561 |  | 1 |  | PHOENIX BUILDING | MODESTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXPIRED USA TICKET; FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1317 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATED PRIOR TO RECEIVING A POSITIVE RESPONSE FROM ALL UTILITIES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-01-15 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5505 |  | 0 |  | E. BELTRAN SERVICES INC | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2735 |  | 2 |  | FOWZER ELECTRIC | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3133 |  | 1 |  | MV SOLID FENCING | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2109 |  | 2 |  | THE ELECTRIC COMPANY | PATTERSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1223 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1755 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-08-19 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7391 |  | 0 |  | HENSEL & CASTILLO FENCING | CITRUS HEIGHTS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1335 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-05-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3190 |  | 7 |  | P L CONSTRUCTION | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1393 |  | 1 |  | MID CAL PIPELINE | MERCED | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXPIRED USA TICKET; FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1168 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2009 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-02-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1378 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-07-02 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 126 |  | 0 |  | TURLOCK IRRIGATION DISTRICT | TURLOCK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATED OUTSIDE DELINEATED AREA
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-01-27 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 23397 |  | 0 |  | COMCAST COMMUNICATIONS | PHILADELPHIA | PA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1301 |  | 1 |  | JOHNSON & SONS PLUMBING | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2025-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2878 |  | 0 |  | HOMEOWNER | OAKDALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2025-03-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2532 |  | 3 |  | REDSTONE CONSTRUCTION | ATWATER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2025-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1543 |  | 5 |  | REDSTONE CONSTRUCTION | ATWATER | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2025-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1794 |  | 5 |  | REDSTONE CONSTRUCTION | ATWATER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2025-07-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2078 |  | 1 |  | PLATINUM CONSTRUCTION | CHICO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2025-03-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 570 |  | 1 |  | REDSTONE CONSTRUCTION | ATWATER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2025-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 800 |  | 2 |  | UNITED PAVEMENT MAINTENANCE | HUGHSON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2025-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1783 |  | 1 |  | RP LANDSCAPING | WATERFORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | PATTERSON | 2025-05-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7172 |  | 0 |  | TERRALINK COMMUNICATIONS | FAIR OAKS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXPIRED USA TICKET; FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | STANISLAUS | RIVERBANK | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7477 |  | 2 |  | EFI ENGINEERING INC. | TUSTIN | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | STANISLAUS | RIVERBANK | 2025-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1874 |  | 2 |  | EFI ENGINEERING INC. | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2025-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1339 |  | 1 |  | CONCRETE | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2025-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2213 |  | 8 |  | PG&E | OAKLAND | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1590 |  | 1 |  | SOUTH TREE LANDSCAPE MGMT | DELHI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2025-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 918 |  | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2025-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 798 |  | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2025-08-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2583 |  | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2025-02-15 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 3 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27143 |  | 0 |  | GOOD FELLOW BROS INC | LIVERMORE | CA | N | Y | Yes | Yes | No | Yes | Yes | Yes | Yes | FAILURE TO MAINTAIN MARKS
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1186 |  | 1 |  | MORELLO CONSTRUCTION | TURLOCK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SUTTER | MERIDIAN | 2025-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Farm Equipment | 2 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20730 |  | 1 |  | ALSCO GEYER IRRIGATION | ARBUCKLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3152 |  | 1 |  | BEI CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2025-04-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2920 |  | 2 |  | GIGAWAVE | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2025-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3375 |  | 1 |  | FLETCHERS PLUMBERS | YUBA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2025-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | WHITMER CONSTRUCTION AND PLUMBING2553 BLEVIN ROAD | YUBA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | TUOLUMNE | STRAWBERRY | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2252 |  | 1 |  | SONOMARIN SOLAR | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | YOLO | DAVIS | 2025-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1252 |  | 2 |  | WOODLAND ELECTRICAL INC | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | YOLO | DAVIS | 2025-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3018 |  | 1 |  | HOMEOWNER | DAVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2025-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8363 |  | 5 |  | DELTA CONCRETE | CITRUS HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2025-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 44945 |  | 2 |  | GEORGE REED INC | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | YOLO | WOODLAND | 2025-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3410 |  | 1 |  | HALL?S PLUMBING | ESPARTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | WOODLAND | 2025-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2125 |  | 1 |  | SUPERIOR FENCE & CONSTRUCTION | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | YOLO | WOODLAND | 2025-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1937 |  | 1 |  | MP NEXLEVEL LLP | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | WOODLAND | 2025-05-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2475 |  | 1 |  | CITY OF WOODLAND | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | WOODLAND | 2025-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1647 |  | 1 |  | ARGONAUT CONSTRUCTORS | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES - FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | YUBA | MARYSVILLE | 2025-01-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 53 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3241 |  | 0 |  | GHITA UNDERGROUND ENGINEERING INC. | LINCOLN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YUBA | MARYSVILLE | 2025-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 53 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4013 |  | 1 |  | AERCO PACIFIC CO | RANCHO CORDOVA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YUBA | OLIVEHURST | 2025-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 54 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1814 |  | 1 |  | NEWLAND ENTITIES INC | YUBA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | YUBA | OLIVEHURST | 2025-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 54 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 842 |  | 2 |  | RCI GENERAL ENGINEERING | OROVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | YUBA | WHEATLAND | 2025-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 56 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5389 |  | 1 |  | HOMEOWNER | WHEATLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
San Diego Gas and Electric | N | SAN DIEGO | BONITA | 2025-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | CV ELECTRIC | CHULA VISTA | CA | N | Y | Yes | Yes | Yes | No | No | No | No | Upon arrival, CV Fire Department were on scene while SDG&E Gas Emergency Response Crew (GERC) members were working to control the gas leak. On-site, I spoke with Carlos Vazquez Jr., worker for CV Electric. Carlos stated he was excavating with a shovel when he was attempting to trench for an electric panel upgrade, when the 1/2? plastic gas service was damaged. Carlos provided a valid USA ticket (#CSB253280442) for the trenching work being completed for the electric conduit installation. It was confirmed that the USA ticket was valid and that the SDG&E mark outs were accurate and within the zone of tolerance. The 1/2? plastic gas service was observed to have been damaged with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | BORREGO SPRINGS | 2025-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ARB INC | VISTA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival our SDGE gas crew were getting the damage controlled and repaired. Spoke with Javier Marin with ARB INC who stated on May 13th at 1pm that his crew was digging when they managed to hit the gas. Observation of the damage was a 1/2? plastic gas service hit with a shovel while potholing for the utilities. Valid USA ticket and the mark out is accurate.
San Diego Gas and Electric | N | SAN DIEGO | BORREGO SPRINGS | 2025-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ARB INC | VISTA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | On Wednesday 5/21/25 at approximately 14:00 I met onsite with Javier Marin with ARB. Javier and his crew were performing work for SDG&E to install new gas lines. They were potholing the utilities to confirm the exact location at the time of the damage. A laborer was digging with a shovel to expose a water line when he damaged the 1/2" plastic gas stub. During my investigation, I determined that the location of the damage was approximately 3 feet away from the marking in yellow paint that was placed for this line. The gas was marked per map measurement and the contractor was told to pothole to find the line. They had not yet potholed for the gas. I confirmed that the locator marked the gas stub accurately according to the map measurements. I also confirmed that the line could not be located using electromagnetic locating equipment. The measurements shown on the map did not account for the angle of the pipe (9'' push) which is what led to the mis-mark. CSLB#194079
San Diego Gas and Electric | N | SAN DIEGO | CARDIFF | 2025-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2814 |  | 2 |  | GOOD LIFE DEVELOPERS | CARLSBAD | CA | N | Y | No | No | No | No | No | No | No | Upon arrival our SDGE gas crew had the damage controlled and were in the process of making repairs. Spoke with JIM ACHEY with GOOD LIFE DEVELOPERS who stated that he was using a shovel when he damaged the gas line. Jim and his investors own the property we?re this damage occurred. Observation of the damage was a 3/4? gas service hit with mechanized equipment not a shovel (impossible). Jim was putting in a new storm drain when the damage occurred.
San Diego Gas and Electric | N | SAN DIEGO | CARDIFF-BY-THE-SEA | 2025-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | ARB INC | SPRING VALLEY | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 9/29/25 at approximately 10:10AM I arrived onsite at 945 Woodlake drive in Cardiff-By-The-Sea. I observed contractor ARB INC doing work for SDG&E onsite. The leak was controlled upon my arrival and the gas supervisor showed me the damage location. I observed a cut along the pipe in a hole that was dug near the side of the address. I observed yellow flags on either side of the damage location showing the line was accurately marked. I spoke with Javier Marin onsite. Javier is the superintendent in charge for ARB. He directed me to his foreman Carlos Perez (949-307-9101). Carlos stated that a laborer named Jose Ruben Romero was hand digging with a shovel over the gas. He stated they knew the gas was there but the ground was hard and there were roots. While digging with his shovel parallel with the pipe he accidentally cut into the gas line. They agreed the markings indicating the location of the gas line were accurate.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | TERRAMAR CUS BUILDERS INC | CARLSBAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department was gone. Our SDGE gas crew had the damage controlled. Spoke with Carlos with TERRAMAR CUS BUILDERS INC who stated on September 5th at 3:25 that his crew was trenching when they hit the gas line. Obersvation of the damage was a 1/2? plastic gas service hit with a shovel while trenching for a panel upgrade. The marks are good. The damage happened right next to the gas meter.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | TERRY WEATHERFORD | CARLSBAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On Tuesday 6/17/25 at approximately 1:45PM I arrived at 1751 Tamarack Ave in Carlsbad. Upon arrival I made contact with Terry Weatherford. Terry stated that he was performing excavation work for a sewer line install for an ADU. Terry stated he was doing the work for the homeowner who is a friend. He was performing the work under an owner-builder permit and was not performing the work officially as a contractor. While he was potholing utilities he thought he had found the gas line already but actually had exposed a communication conduit. He proceeded to dig with a Jack hammer and hit the gas line. He agreed the markings onsite were accurate. I explained the importance of understanding the labeling placed by the locator to know what he is looking for when potholing.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1861 |  | 7 |  | TERRY WEATHERFORD | CARLSBAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke with Terry Weatherford who stated the 1/2" poly service line had been damaged while trenching with shovel for the electric panel upgrade. Mr. Weatherford informed me he is helping the homeowner who is his friend completed the work to help save some money. Mr. Weatherford added the gas line had been previously potholed, but the ground is very hard to trench in and his helper accidentally hit the gas line. I advised Mr. Weatherford to re-notify on his ticket (USA A252060207) that his trench was going to be extended, that way the locators could account for the new work area. Once the damaged 1/2" poly service line was controlled by the SDGE GERC crew to was confirmed the line had been damaged with a shovel. Most gas locate marks that had been previously placed by the SDGE locator had been destroyed. However, I could still observe a couple of gas locate flags that aligned with the path of the damaged 1/2" poly service line. I setup my damage kit and took my damage photos. It is clear Terry Weatherford damaged an accurately marked 1/2" poly service line while trenching with shovel for the electric panel upgrade.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ZANA ELECTRIC | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. Spoke with ARMANDO RAMIREZ with ZANA ELECTRIC who stated on September 15th at 11:35am that his crew was trenching near the electric transformer when they hit the gas. Observation of the damage was a 1/2? plastic gas service hit with a shovel while trenching for a panel upgrade.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-06-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | TVD INCORP | CARDIFF BY THE SEA | CA | N | Y | No | No | No | No | No | No | Yes | On 6/13/25 at approximately 16:00 I arrived at 2960 Roosevelt st in Carlsbad where the gas damage occurred. When I arrived the gas leak had been controlled and repairs were made. I met with Rick Cameron who works for TVD INCORP. He stated that the gas has just been installed today and backfilled. He said they had to re-expose the new service because it needed to be lowered. They knew exactly where the gas service was running. While moving the dirt the 1" plastic line was damaged with a shovel. Rick had a dig alert ticket but let it expire on 4/30/25. He said they weren''t planning to do anymore digging which is why he didn''t have a valid ticket. I advised him to always keep his tickets updated until all work is completely done.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | J B HOME IMPROVEMENTS INC | SAN MARCOS | CA | N | Y | No | No | No | No | No | No | No | Hamid Beikzadeh stated that his crew was digging a trench to install a sewer line for an ADU. While digging with a shovel they damaged the 1/2" gas service. The majority of the flags that the gas line was marked with were gone. This led to them losing track of the exact location it was marked. They never potholed the gas line. I explained to Hamid that he needs to keep his ticket valid and call for remarks whenever needed. Also that he needs to expose the pipe by hand to confirm the exact location.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-10-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | DEDMON HOME REPAIR | LAKE ELSINORE | CA | N | Y | No | No | No | No | No | No | No | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with BAHRAMI, MURTAZA who is the property owner who stated on October 10th at 12:30pm that his operator hit the gas line. Spoke with Nathanael Dedmon who is the operator who stated that he was trenching when he hit the gas line. Observation of the damage was a 1? plastic gas service hit with a mini excavator while trenching for electric panel upgrade.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | LG ELECTRIC INC | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department was not on scene. Spoke with Luis Garcia crew who work for LG Electric Inc who stated on March 19th at 5:20pm that they were trenching when they hit the gas. When asked if the flags were moved they stated that Luis Garcia moved the flags over to the side. The crew stated that the marks out was correct. The damage occurred about 2 feet from the gas meter. Observation of the damage was a 1/2? plastic gas service hit with a jackhammer while trenching for a panel upgrade.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-07-14 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 1.5 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1315 |  | 0 |  | DOUGLAS PIPELINE INC | LAKE ELSINORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Upon arrival the SDGE gas crew was RFS the dead end of the gas main. The contractor has a valid USA dig alert ticket. Our SDGE locator marked the dead end of the gas until he lost his signal. The signal he got was about 15 feet short of where the gas dead end ended. This is not the fault of the contractor because they did not know the gas went that far into the work area. We are having our Quality Assurance team take a look at what happened at this job.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ELITE ROOTER | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. Spoke with OMAR HERNANDEZ with ELITE ROOTER who stated on September 15th at 6:55pm that he was digging up the sewer when he hit the gas line. Observation of the damage was a 1/2? plastic gas service hit with a shovel while digging for a sewer line. Omar did not have a USA ticket.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MARK RUBINS | CARLSBAD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | Spoke with Mark Rubins onsite. Mark is the homeowner for the property and was performing work himself. Mark stated that he was digging to replace his sprinkler system. He was digging with a shovel and hit the 1/2" plastic gas service causing the damage. He did not have a USA ticket. He said he knew about 811 but didn''t think of calling. I educated him and he called in a ticket onsite.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MATTHEW SMITH | CARLSBAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival our SDGE gas crew had the damage controlled and repaired. Spoke with H/O SMITH, MATTHEW who stated that he has some guys doing the trench for him for a panel upgrade when they hit the gas. Observation of the damage was a 1/2? plastic gas service hit with a shovel while trenching for a panel upgrade. The SDGE locator was very close to the tolerance given. The maps are wrong and this is a mapping error. The homeowner will not be billed.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | SEMA CONSTRUCTION | CARLSBAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Met with Cody Lindenmayer who is the onsite foreman for SEMA. Cody stated that they were demoing asphalt and concrete when they damaged the gas line. There was 18" of asphalt and concrete that they were saw cutting then breaking and lifting with an excavator. While doing this they clipped the gas service. It was 3" below the bottom layer of concrete. I advised them to make sure to pothole before getting into the dirt with their excavator. CSLB #685954
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | DBK ELECTRIC CONTRACTOR | ENCINITAS | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | On Wednesday 7/23/25 at approximately 3:45PM I arrived at 6511 Onda Pl, Carlsbad. The gas leak had been controlled upon my arrival. I observed a crew of 3 people digging a trench in the front of the address. I stopped them from digging as I did not observe any markings in their work area. They said their boss had left. I called Marc Prosi with DBK electric contractor. Marc stated that he had called dig alert for this job in the beginning of June. He said he was concerned with the lack of marks and recalled the ticket in on 7/2/25. At this time he did delineate the jobsite. Following this he met with an SDG&E trench inspector and observed the jobsite. He said he only saw orange marks at this time. He stated that he expressed this concern with the SDG&E inspector who told him he was cleared to dig. His crew proceeded to dig and damaged the gas line with a shovel. I told Marc he should never proceed to dig without the necessary markings and should always confirm positive responses on his ticket. I verified the documentation and found the original ticket was closed for no delineations on 6/9/25. On 7/2/25 the ticket was resent as no response for SDG&E and stated site is now delineated. SDG&E did not respond to this request because it was overlooked by the locator.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | DBK ELECTRIC | ENCINITAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with Marc Prosi with DBK Electric who stated on March 17th at 2:30pm that his guys were digging when they managed to hit the gas. The USA ticket for this job expired on March 14th. Observation of the damage was a 1/2? plastic service hit with a jackhammer while trenching for an electric panel upgrade.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2025-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  | 0 |  | JOSE ROSALES | SAN MARCOS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled and repaired. Spoke with JOSE ROSALES MARTINEZ who is the contractor doing the work. Jose thought that the gas line would be deeper then 15?. Observation of the damage was a 1/2? plastic gas service hit with a shovel while trenching for new drains. When I asked Jose if he knew what dig alert was he was unaware of this service. I made sure he called in a USA ticket even though he is done digging.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  | 0 |  | FIOPTIX | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Don Bell foreman with Fioptix who stated the gas line had been damaged while excavating to intercept communication conduit with a sharpshooter shovel. Don Bell and his crew were not disputing marks and added they accidentally caught the line while digging thru roots and hard ground. Once the SDGE GERC crew controlled the blowing 1/2" poly service line it was confirmed it had been damaged with hand-tools. Within the location of the damage I could observe SDGE gas locate marks that aligned with the path of the damaged 1/2" poly service line. I set up my damage kit which confirmed the marks were accurate and took my damage photos. It is clear Fioptix damaged an accurately marked 1/2" poly service line excavating with hand tools.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-02-04 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3033 |  |  | NA | EVOLUTION CONCRETE CONSTRUCTION | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke with Brian Redman site superintendent who confirmed Evolution Concrete Construction were drilling with mechanized equipment when they damaged the marked 2" poly gas main. Evolution Concrete Construction were not onsite, but I contacted Raul Hernandez foreman with Evolution Concrete Construction who stated they had not seen the marks for the damaged gas line. I advised Brian R. to make sure his subcontractor request remarks before continuing with drilling so they can have a fresh mark-out and can avoid existing utilities for the the light pole locations. Within the location of the damage I was able to find offsets that placed a mark within the path of the damaged 2" poly gas line. I set up my damage kit, confirmed the yellow offset was accurate and took my damage photos. It is clear Evolution Concrete Construction damaged a marked 2" poly gas line.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3103 |  | 1 |  | CATS EXCAVATING INC | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | Yes | On-site I spoke to Garrett Rash foreman for CATS Excavating Inc. who stated the 2" poly service line had been damaged while grading with mechanized equipment. Garrett Rash informed me the grading was being done for M A Steven''s Construction who were going to install a retaining wall & fencing for the school. Garrett Rash was unable to provide a valid dig alert ticket and assumed since they had seen utility locate marks they were also covered to excavate using the marks on-site. I advised Garrett Rash to request his own dig alert ticket before continuing with any proposed excavation, which he agreed and called one in. Once the damaged gas line was controlled by the SDGE GERC crew we were able to confirm the 2" poly service line had been damaged with mechanized equipment. Within the locations of the damage I could observe gas locate marks which aligned with the path of the damaged gas line. I set up my damage kit which confirmed the marks onsite were accurate and took my damage photos. It is clear CATS Excavating Inc. were grading without a valid dig alert ticket and damaged an accurately marked 2" poly service line which had been marked for another contractor.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-07-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3966 |  | 43 |  | DOMINGUEZ HAULING | CHULA VISTA | CA | N | Y | No | No | No | No | No | No | No | On-site I spoke to Antonio Ramirez with Dominguez Hauling who stated the gas line had been damaged while trenching for pool plumbing with mechanized equipment. Antonio Ramirez was unable to provide a valid dig alert ticket and informed me the work was being completed for homeowner Peggy Marron. I spoke to Peggy Marron who confirmed she had hired Antonio and his crew to trench for the plumbing for a future pool. Peggy Marron also provided USA A251780145, and added the crew was not expecting to come across gas at that location since no gas had been marked at that location for her dig alert ticket. It was unclear to determine if Peggys ticket covered that location since I did not observe delineations at that location at this time. I advised Antonio Ramirez to request their own dig alert ticket since they are the ones actually completing the trenching. Once the damaged 1 1/4" poly main gas line was controlled by the SDGE GERC crew we were able to confirm it had been damaged with mechanized equipment. I did not observe delineations or locate marks other than the ones placed by the locator for the GERC crew within the location of the damage. I placed my damage pylon and took my damage photos. It is clear Dominguez Hauling failed to request a valid dig alert ticket for the trenching taking place at this location.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | SIMPER SOLARIS CONSTRUCTION | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Emilio Correa who stated him and his crew were trenching with hand tools to upgrade electric when they damaged the marked 1/2" poly service line. Emilio informed me they had pot and found the gas line closer to the electric hand hole, but they failed to excavate with caution when crossing the line closer to the riser. Emilio Correa provided USA B250220957, and claimed they were working under Semper Solaris Construction. Within the location of the damage I could observe gas locate marks in form of yellow paint and flags that aligned with the path of the damaged 1/2" poly service line. I set up my damage kit which confirmed they gas locate marks were accurate and took my damage photos. It is clear Emilio Correa damaged an accurately marked 1/2" poly service line while trenching with hand tools to upgrade electric.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-01-11 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8843 |  | 83 |  | VIDEA VOICE DATA | GARDEN GROVE | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | On-site Heath Gurley foreman with Video Voice Data Communications stated the 2" gas main had been damaged while driving a metal beam under sidewalk with a hammer. Heath Gurley and his crew were trying to install electric wiring for a EV Charging station. Heath Gurley provided USA A250080248, which was not valid until Monday 01/ 13/25 at 8:00am. I advised Heath Gurley and his crew to always wait until ticket is valid and all utilities have responded. Upon arrival to the damage site, I could observe the SDGE GERC crew working on control for the damaged 2" gas main. The fore department had road closures within at the entrance of the property. Within the location of the damage I could observe what Heath Gurley had stated which was a metal beam embedded under the sidewalk which crossed the path of the gas line. I did not observe any gas locate marks since VIdeo Voice Data Communications flailed to wait the appropriate time and began working before the legal start date on the ticket.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-10-11 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3033 |  | 0 |  | TVC GROUP | NATIONAL CITY | CA | N | Y | Yes | Yes | No | Yes | No | No | No | On-site I spoke to Sergio Ferrer with TVC Group who stated his crew damaged the 2" poly gas main while boring to install communication conduit. Mr. Ferrer confirmed USA B252650482 and been requested to complete the proposed work. Mr. Ferrer was aware his crew had dug beyond the delineated areas, which had not been covered by any utility. He added they were going off marks a private locator had placed for them along with depth of the existing pipes. I advised Sergio Ferrer and his crew to stop work and call in a ticket to cover the areas where they were currently boring, for which he agreed. The SDGE GERC controlled the blowing gas line, however the damaged pipe was still buried and needed to be uncovered. An additional SDGE crew was requested and once they uncovered the pipe it was confirmed the 2" poly main had been damaged whit a grundomat horizontal boring tool. Within the location of the damage I did not observe any contractor delineations or utility markout. I placed my damage kit and took my damage photos. It is clear TVC Group damaged the 2" poly while boring beyond the delineated area.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ADRIAN ORTIZ | CHULA VISTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | Yes | On-site I spoke to homeowner Adrian Ortiz who stated the 1/2" poly gas line was damaged while excavating to place a tree with hand tools. Adrian Ortiz was unable to provide a valid dig alert for the proposed landscaping. I provided 811 dig alert information and advised Adrian Ortiz to request a valid dig alert before continuing with any excavation. Once the damaged gas line was controlled and exposed by the SDGE GERC crew were able to confirm it had been damaged with hand-tools. Within the location of the damage I did not observe any delineations or mark-out completed for the work taking place. I set up my damage kit and took my damage photos. It is clear Adrian Ortiz damaged a 1/2" poly service line while excavating to place a tree without a valid dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | RICARDO DAVILA | SAN DIEGO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | On-site I spoke to homeowner Ricardo Davila who stated the 1/2" poly service line had been damaged with hand tools while trenching to upgrade electric for an ADU. Ricardo Davila was unable to provide a valid dig alert ticket number. I advised Ricardo Davila to request a valid dig alert ticket and wait the appropriate time before continuing with any excavation. Within the location of the damage, I did not observe any delineations or utility locate marks. I completed a ticket search and was unable to find a valid ticket for the proposed work taking place at the property. It is clear homeowner Ricardo Davila failed to request a valid dig alert ticket before excavating to upgrade the electric.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1315 |  |  | NA | JACQUES PAVING INC | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | On-site I spoke to Guillermo Jacques owner of Jacques Paving Inc. who stated the gas line had been damaged while grading with mechanized equipment. Guillermo was unable to provide a dig alert ticket, he assumed no ticket was needed since they were working on private property. I advised Guillermo to request a valid dig alert ticket before continuing with the grading. Once the SDGE emergency crew was able to control the blowing gas line we were able to confirm it had been pulled and damaged by the grader. Within the location of the damage I did not observe any delineations or locate marks. I placed my damage pylon and took my damage photos. It is clear Jacques Paving Inc. failed to request a USA dig alert ticket. (License #789040).
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2814 |  | 2 |  | CASPER COMPANY | SPRING VALLEY | CA | N | Y | No | No | No | No | No | No | Yes | On-site I spoke to Mathew Schlick foreman with Casper Company who stated the 3/4" steel gas stub had been damaged while excavating to remove old curb and gutter with mechanized equipment. Mathew Schlick informed me the work was being completed for Pacific Building Group, which had informed them there were no underground utilities at that location. Mathew Schlick was unable to provide a valid dig alert ticket. I advised Mathew S. to request a valid dig alert ticket before continuing with the proposed work taking place at the job site. Once the damaged gas line was controlled by the SDGE GERC crew we were able to confirm the 3/4" steel gas stub had been damaged with mechanized equipment. I did not observe any delineations or locate marks placed for Casper Company within the location of the damage. I set up my damage kit and took my damage photos. It is clear Casper Company failed to request a valid dig alert and damaged a 3/4" steel stub while excavating with mechanized equipment.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1651 |  | 4 |  | VICTOR COLORADO | CHULA VISTA | CA | N | Y | No | No | No | No | No | No | No | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled. Spoke with Victor Colorado over the phone and he stated that he was digging for a new fence when he hit the gas. Victor did not know what a USA dig ticket was. Observation of the damage was a 1/2? plastic gas service hit with a shovel while putting in a new fence. I let Victor know that he would need a dig alert ticket to get the area marked out.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | SUNSHINE COMMUNICATIONS INC | EL CAJON | CA | N | Y | No | No | No | No | No | No | No | On-site I met with Scott Ludwig with Sunshine Communications Inc who stated the 1/2" poly service line had been damaged with hand tools while excavating to repair communication conduit. The workers stated they had been coming across a lot of tree roots when next thing they know they had hit the gas line. Scott Ludwig was unable to provide a valid dig alert ticket. I advised Scott and his crew to stop all work and not continue until a valid dig alert ticket has been requested and completed. Once the SDGE GERC crew was able to control the blowing gas line we were able to confirm the damaged 1/2" poly service line was completely wrapped in tree roots. I did not observe any delineations or locate marks placed for Sunshine Communications Inc to complete the proposed work. It is clear Sunshine Communications Inc failed to request a dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ORLANDO CUNANA | CHULA VISTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | Upon arrival, SDG&E Gas Emergency Response Crew (GERC) members had controlled the leak and were making the repair to the damaged gas line. On-site, I spoke with the homeowner, Orlando Cunana, who stated his handyman was not excavating and that the trench was already open from a previous contractor, whose information Orlando did not want to provide. Orlando stated his handyman found the 1/2? plastic gas service damaged already, although they was clearing the trench line for a sewer install with hand tools. Orlando stated he previously had a USA ticket but ?very long ago.? It was confirmed that there was no valid USA ticket within the 2025 year. The 1/2? plastic gas service was observed to have been damaged with a shovel. Orlando was advised to halt all excavation until a valid USA ticket is confirmed.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  | 0 |  | EVERLAST CONSTRUCTION | BONITA | CA | N | Y | No | No | No | No | No | No | No | On-site I spoke to Charli N. worker for Everlast Construction who stated the 3/4" steel service line had been damaged while grading lot with mechanized equipment. Charli added he was in the process of removing some tree roots when he realized the gas line was tangled between the roots and had been yanked along with the roots. Charli was unaware if a dig alert had been requested and provided his boss Bilal Nuhaily number. I contacted Bilal N who stated no dig alert had been requested since Charli was on the lot just to clear some dirt, rubble and roots. I advised Mr. Nuhaily to request a valid dig alert before any work continued at the lot. Once the blowing gas line was controlled by the SDGE GERC crew it was confirmed it had been damaged with mechanized equipment. I placed my damage pylon and took my damage photos.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2025-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | WESTCOAST BUILDING AND DESIGN | SANTEE | CA | N | Y | Yes | No | No | No | No | No | No | On-site I contacted Rene Rivera with West Coast Building & Design who stated his worker Kevin H. accidentally damaged the 1/2" poly service while trying to expose it for the SDGE trench inspector. I also spoke to Kevin Hernandez worker at site who confirmed he was not there to dig, but to just meet with the inspector to have the trench cleared. However , he was asked to remove the sand covering the gas line when he accidentally hit it. Mr. Rivera provided USA A251740746, which expired on 7/21/2025. I advised both Mr. Rivera and Mr. Hernandez to request a valid dig alert ticket before continuing with the project. Once the damaged 1/2" poly service line was controlled by the SDGE GERC crew it was confirmed it had been damaged with hand tools. Within the location of the damage I could observe all trenching had been completed and even some new electric conduit had been placed. I also noticed most if not all SDGE locate gas marks had been destroyed. I set up my damage kit and took my damage photos. It is clear West Coast Building & Design damaged a gas line while trying to expose it with an expired ticket.
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2025-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  | 0 |  | LUSARDI CONSTRUCTION | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | On-site I spoke to Chet Adkins superintendent with LUSARDI Construction who stated the 1" poly gas line had been damaged while trying to fully expose it with mechanized equipment. Mr. Adkins informed me his crew was in process of grading the lot when the 1" poly line was discovered. He added the line had been potholed & found, as well as had portion of it exposed when it was accidentally struck with the backhoe. Mr. Adkins provided USA A253300483, which was requested to install 5 temporary power poles at a different location. Once the SDGE GERC crew fully controlled the damaged 1" poly service line it was confirmed it had been damaged with mechanized equipment. Within the location of the damage I could observe gas locate marks that aligned with the path of the damaged 1" poly gas line. I set up my damage kit, confirmed the locate marks onsite were accurate and took my damage photos. It is clear LUSARDI Construction damaged an accurately marked 1" poly gas stub while trying to expose it with mechanized equipment and was grading without a valid dig alert ticket to cover proposed work area.
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2025-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MEZZ CONSTRUCTION | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke with David M. Mezzacappa with Mezz Construction who stated the gas line had been damaged while trying to pothole the existing utilities with hand tools. David was aware the marks had been destroyed and agreed to request remarks to prevent another damage from occurring. Within the location of the damage I did not observe locate marks since they had been destroyed due to the work taking place. I set up my damage kit and took my damage photos. It is clear Mezz Construction failed to request remarks before excavating in an area where marks had been destroyed.
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2025-06-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | NICHOLLS DESIGN BUILD | CORONADO | CA | N | Y | Yes | Yes | No | No | No | No | Yes | On-site I spoke to Kraig Nicholls and his worker with Nicholls Design Build who both confirmed the 1/2" poly service line had been damaged while excavating to expose it with hand tools. Kraig Nicholls stated they are currently excavating to have meter and gas service line moved to a different location. Kraig Nicholls confirmed USA A251630142 had been requested by him, which after reviewed I determined its legal start date was not until 6/16/25 at 17:01. I advised Kraig and workers to delineated the proposed work area to have the locator complete the ticket before continuing with any excavation. Once the gas line was controlled by the SDGE GERC crew we were able to confirm it had been damaged with hand tools. I did not observe any delineations or gas locate marks within the location of the damage. I set up my damage kit and took my damage photos. It is clear Nicholls Design Build failed to wait the appropriate legal start Date & time and dug early.
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2025-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2281 |  | 13 |  | FALLETA CONSTRUCTION INC | IMPERIAL BEACH | CA | N | Y | No | No | No | No | No | No | Yes | On site I spoke to Tony Falleta with Falleta Construction Inc. who stated the 1/2" poly service line had been damaged while excavating to install a temporary utility pole with post hole digger. Tony Falleta was unable to provide a valid dig alert ticket. However, after completing a ticket search I found USA A251430715 which its job description was also to install a temporary pole. USA A251430715 was requested by National Construction Rentals on 5/23/2025 and its legal start date was for 5/29/2025. National Construction Rentals workers were not on site. I also attempted to contact the caller on the ticket Oscar Lira at 619-667-2600, but he did not answer. I advised Tony Falleta to stop all excavation work and request his own dig alert ticket. Once the damaged 1/2" poly service line was controlled by the SDGE GERC we were able to confirm it had been damaged while digging for a pole with hand tools. Within the location of the damage I could observe some faded, but mostly destroyed gas locate marks that aligned with the path of the damaged gas line. Which had been placed for a previous USA ticket that was no longer active. I set up my damage kit and took my damage photos. It is clear Falleta Construction Inc. failed to request a dig alert ticket to excavate for a temporary utility pole.
San Diego Gas and Electric | N | SAN DIEGO | DEL MAR | 2025-07-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | BRUCON CONSTRUCTION INC | BONSALL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival our SDGE gas crew had the damage controlled and repaired. Called and spoke with JASON DRAPER with BRUCON CONSTRUCTION INC who stated that his crew called him and let him know that they hit the gas while trenching for wet utilities. Observation of the damage was a 1? plastic gas service hit with a shovel while trenching for wet utilities.
San Diego Gas and Electric | N | SAN DIEGO | DEL MAR | 2025-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | JIM VOLLGRAFF | VISTA | CA | N | Y | No | No | No | No | No | No | No | Met with Jim Vollfgraff onsite. Jim stated that he was hired by homeowner Luke Palmo to install an upgraded water system to the house and needed to dig up the drain line. Jim stated they were doing exploratory digging with a shovel to find the drain line when they hit the gas service. Jim stated he knew what dig alert was but failed to use the service for this job. When I asked Jim if he was a licensed contractor he said that he was not. I educated him on the importance of using dig alert and had him call in a ticket onsite.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2025-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SMITH BROTHERS CONSTRUCTION | SOLANA BEACH | CA | N | Y | Yes | Yes | No | No | No | No | No | On-site I spoke to Jay Ferschweiler foreman with Smith Brothers Construction who stated the 1/2" poly service gas line had been damaged with hand tools while trenching to install private gas line. Jay F. claimed the original markout completed on 1/07/2024 by the SDGE locator showed a different path for the 1/2" poly service line and that his crew was not expecting the line to take the path that it did. Jay F. provided USA A250060390, for which he had requested remarks on 1/16/2024 and legal start date is not until 1/17/2024 at 5:01 pm. I informed Jay his ticket had not been remarked yet and that he needed to wait until all utilities responded before he could continue excavating. Within the location of the damage, I could observe most marks had been destroyed due to the work taking place. The closet SDGE gas locate mark was in form of a flag and it was clearly accurate since the SDGE GERC crew had found the line and used it for control utilizing that mark. I set up my damage kit and took my damage photos. It is clear Smith Brothers Construction failed to wait for their remark request and dug in an area where marks had been destroyed.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2025-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | WYYERD FIBER | NATIONAL CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. Spoke with Edward with WYYERD FIBER who stated on October 27th at 8:30pm that his crew was boring when they managed to hit the gas line. Observation of the damage is a 3/4? stl gas service hit while boring to install conduit.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2025-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | PRO ENERGY SERVICES | ESCONDIDO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department had the road secured while our SDGE GERC crew was getting the damage controlled. Spoke with Josh from Pro Energy He was the safety on site I asked him about what had happened, and he stated to me that while his crew was pot holing the marked 1/2" poly gas service at 1145 am they had exposed the service but shortly after they went to lunch and when they got back from lunch the crew started to uncover the gas line again to continue their work they lost track of it and with the shovel they penetrated it at 1: 39 pm. The Excavation was started on July 7th at 1145am but was the official start date was July 7 at 1:10pm. The area had been marked accurately with flags and paint on 6/30/2025 on same ticket. Observation of the damage was a 1/2" plastic gas service hit with a shovel while installing an anchor for SDGE.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | VALS CONSTRUCTION | EL CAJON | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I contacted Nate N. Foreman with Vals Construction who confirmed the gas line had been damaged while excavating for pole anchors with a jack hammer. Initially Vals Construction crew mentioned they were in the process of potholing when the gas line was damaged and that they were not expecting to come across the gas line that deep. However, Nate mentioned he had walked the job prior excavation started and determined they were far away enough from the marks that had been placed for them to safely excavate without coming across the gas line. Once the damaged 3/4" steel service line was controlled we were able to confirmed it had been damaged with the jack hammer and its depth was at approximately. 6'' deep. Within the location of the damage most marks & flags had been destroyed due to work taking place. However, there was still a flag and some paint by the curb which aligned with the path of the damaged 3/4" steel service line. It also appeared that some of the gas locate flags had been moved by someone and placed behind some wooden boards that possibly could have confused the crew that was excavating for the anchors. After reviewing the pre-excavation photos taken on 2/6/20205 for USA B250351144, it is clear the damaged 3/4" steel service line had been accurately marked. Vals Construction failed to pothole to determine the exact location and depth of the marked gas line before excavating to place new pole anchors.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MENDOZA SUPREME LANDSCAPE DESIGN INC | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I met Francisco Mendoza with Mendoza Supreme Landscape Design Inc who stated the gas line had been damaged while excavating to install a retaining wall with mechanized equipment. Francisco added he had been careful while excavating by the marks. However, him and his crew assumed the gas line would be deeper. I advised Francisco to always pothole by hand to determine exact location and depth of all existing marked utilities. Within the location of the damage we could observe most marks had been destroyed, but we could still see some faded yellow paint marks and flags which aligned with the path of the damaged 1/2" poly service line. After reviewing the pre-excavation photos provided by the locator it is clear Mendoza Supreme Landscape Design Inc damaged a marked 1/2" poly service line and failed to pothole.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2025-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | D''S HOME REPAIR & REMODEL AND WEHRLY ELECTRIC | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | On-site I spoke to David Dickey with D''s Home Repair & Remodel who stated the 1/2" poly service line had been damaged while trenching with hand tools to upgrade electric. Mr. Dickey informed me he had been hired by John Wehrly Electric to complete the trenching. However John Wehrly was not on-site and had not been made aware of the incident that had occurred. Mr. Dickey was unable to provide a valid dig alert ticket, he was advised to request his own dig alert ticket before continuing with the proposed trenching. Once the damaged 1/2" poly gas service line was controlled by the SDGE GERC crew it was confirmed it had been damaged with hand tools. Within the location of the damage I could observe gas locate marks in form of paint and flags which aligned with the path of the damaged gas line. The marks had been placed for USA A251840437 on 7/08/2025, which had been requested by John Wehrly. I set up my damage kit, confirmed the gas locate marks were accurate and took my damage photos. It is clear D''s Home Repair & Remodel failed to request their own ticket and damaged an accurately marked 1/2" poly service gas line.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2025-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ROMA ENGINEERING AND CONSTRUCTION | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid usa ticket A250220356. The 1/2? poly service hit with shovel while digging trench to place conduit. Our crews no longer onsite. Most of the marks destroyed but there is one flag about 12? feet behind the damage that shows that the line was most likely marked accurately. Also, the worker with Roma Engineering & Construction who hit it told me there were flags showing the path of the line.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2025-09-29 | Operator excavation damage | Miscellaneous/Other | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  | 0 |  | SAN DIEGO GAS AND ELECTRIC | EL CAJON | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Cody S foreman with SDGE who stated that the crew was excavating to open up a weld hole when they cracked an unmarked 3/4"steel stub with mechanized equipment. The SDGE gas crew had a valid dig alert ticket and were onsite working on a code 2 leak. Cody added the marked 1 1/2" steel gas main had been potholed and found. However, they were not expecting to come across a stub at that location. The stub was approx.1'' long and not on the maps. I set up my damage kit and took my damage photos.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2025-12-23 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  | 0 |  | PROPERTY OWNER KASAY ESHO | EL CAJON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | On-site I spoke to property owner Kasay Esho who stated the gas line had been damaged while grading with mechanized equipment within his property. Mr. Esho and workers were unable to provided a valid dig alert ticket, one was created after the damage occurred. (USA A253570140) I advised Mr. Esho to wait for legal start date and until all utilities have responded before he continues grading. Once the damaged gas line was controlled y the SDGE GERC crew it was confirmed the 1" poly stub had been damaged with mechanized equipment. Within the location of the damage I did not observe any delineations or utility locate marks for the work taking place. I set up my damage kit and took my damages photos. It is clear Mr. Esho and workers damaged a 1" poly gas stub while grading with mechanized equipment without a valid dig alert ticket/ markout.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2025-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | SYNTHETIC LAWN SOLUTIONS | EL CAJON | CA | N | Y | No | No | No | No | No | No | No | On-site I met Robby Brockman with Synthetic Lawn Solutions who stated the 1" poly service line had been punctured while placing steel stakes for a proposed retaining wall. Robby Brockman was unable to provide a valid dig alert ticket and was advised to request one, for which he agreed. USA A252890563 was created after our conversation. Once the damaged 1" poly service line was controlled by the SDGE GERC crew we were able to confirm it had been punctured with a steel stake. Within the location of the damage I did not observe any delineations or mark out completed for the work taking place. I set up my damage kit and took my damage photos. It is clear Synthetic Lawn Solutions was excavating and placing steel stakes without a valid dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2025-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JAV CONSTRUCTION | ESCONDIDO | CA | N | Y | No | No | No | No | No | No | No | On Friday 12/5/2025 at approximately 12:00 PM I arrived onsite at 1089 Rancho Santa Fe Rd, Encinitas. Upon my arrival the SDG&E emergency response crew had just controlled the leak. I made contact with Tony Vega with Jav Constructions. Tony stated that he was the contractor performing the excavation onsite. He had laborers digging a trench to install electrical conduit when they damaged the 1/2" plastic gas line with a shovel. Tony did not have a dig alert ticket for his work at any point in time. I explained to Tony that he must call and receive a ticket for his work and wait the legal amount of time before continuing his work. He agreed and called 811 while onsite.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2025-12-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | DAVID DREWELOW | ENCINITAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | Upon arrival our SDGE gas crew had the damage controlled and were making repairs. Spoke with DAVID DREWELOW who is the property owner who stated on December 2nd at 12:30pm that he was putting in a new post for his fence when he managed to hit the gas line. Observation of the damage was a 1? plastic gas service hit with a post hole digger while putting up a new fence. The property owner was aware of dig alert but decided not to call one in.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2025-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | REMODELING SAN DIEGO | ALPINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On Friday 12/19/2025 at approximately 1:25PM I arrived onsite at 1184 Sidonia St, Encinitas. Upon my arrival I made contact with SDG&E gas supervisor Mike Horowitz. Mike spoke with the contractor Lior Peled while he was onsite and took his statement. He was no longer onsite when I arrived. Per Mike, Lior stated that his crew was digging with a shovel to install electrical conduit for a panel upgrade. While digging with the shovel they hit the 1/2" poly gas service. They knew the gas line was there but accidentally hit it with the shovel. The markings onsite were accurately placed and labeled.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2025-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MARIN SANCHEZ | ENCINITAS | CA | N | Y | No | No | No | No | No | No | No | Upon arrival the crew had the damage controlled and repaired. Spoke with the property owner and he stated on October 31st that he had his landscaper digging to plant some plants when they managed to hit the gas. I called and spoke to Marin Sanchez and advised him to call in a USA dig alert ticket. He has not done that and I?m not sure if he will. Observation of the damage was a 1/2? plastic gas service hit with a sharp shooter while digging for new plants.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2025-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | COASTAL CONCRETE | CARLSBAD | CA | N | Y | No | No | No | No | No | No | No | On Wednesday, 5/7/25 at approximately 4:30 PM I met with Nicholas Luisi onsite at 155 Rosebay Dr in Encinitas. Nicholas stated that his employees were working to remove and replace concrete. After breaking up the concrete they were trying to remove roots that were in their way. While using a digging bar to pry the roots up the damaged the 1" gas service with the digging bar. He stated he did not call dig alert because he was only planning to remove and replace concrete. I advised him to always call in a ticket for his work. He called in a ticket while onsite. CSLB #1106606
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2025-04-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | DRAVES PIPELINE | BONSALL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival both the SDGE crew and Draves crew were gone. The damage gas service was repaired. I called and spoke with Diego Santillan with Draves Pipeline who was the forman onsite who stated on April 30th at 6:39pm that he was digging and knew the gas line was there but still managed to damage it. Observation of the damage was a 1/2? plastic gas service hit with a shovel while doing trenching work to install water, sewer, and electrical.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2025-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | CELESTINE DE LA VICTORIA | ENCINITAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | On Thursday 10/9/2025 at approximately 11:00 AM I arrived onsite at 1605 Caudor st in Encinitas. I made contact with the homeowner Celestine De La Victoria. She stated she had hired laborers to dig out a portion of her hill to install a retaining wall for an area to store her trash cans. While performing this work they hit the gas line with a shove. I informed Celestine that she needed to call in a dig alert ticket and wait until the legal start date and time to continue digging. She agreed and I assisted in delineating her work area with white paint.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2025-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | MEHTA MECHANICAL INC | LA PALMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Met onsite with Manuel Vera (714-363-1396). Manuel was the onsite foreman for Mehta Mechanical Inc. Manuel stated that they were potholing the gas line when one of his guys was probing to try and determine how much deeper the line was. While probing they accidentally punctured the gas service. Manuel stated that they knew the gas was there and the markings were accurate.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2025-01-27 | Third party excavation damage | Main | Steel | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4817 |  | 20 |  | JOES PAVING COMPANY INC | VALLEY CENTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Met onsite with Elias Orozco (760-755-3213). He is the foreman for Joes Paving Company onsite. Elias stated that they were grading with a tractor loader to lower the grade of the road to reconstruct the road. Elias said they had potholed down at the edges of the road where the gas services were but admitted that they did not pothole to verify the depth and location of the gas main before digging. They failed to expose the gas main with hand tools before using mechanized equipment. The marks were destroyed at the time of the damage, but pre excavation photos show the line was marked accurately. Measuring from original grade the gas main was at a depth of approximately 27 inches.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2025-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | GAURDIAN PLUMBERS | TEMECULA | CA | N | Y | No | No | No | No | No | No | No | Met with Anthony Rickard with Gaurdian Plumbers onsite. Anthony stated that they were digging for an emergency sewer repair for a customer when they damaged the 1/2" poly gas service with a shovel. Anthony said he had seen some markings for other utilities and made an assumption that he knew where the gas would be. He was familiar with using dig alert but proceeded to dig anyways without a ticket. The ticket for this property was called in by a different company and not legal until 2/19/25 at 5:01pm. He called in for his own emergency ticket while onsite after the damage.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2025-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | BAAZIZ ACHOUR | ENCINITAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | On Monday 5/19/25 at approximately 16:30, I met onsite with homeowner Baaziz Achour. Baaziz stated that he had somebody working to widen his driveway on his property. He stated that they were using a bobcat and grading a hillside for the widening of the driveway. While grading they damaged the gas service. He said they expected the line would be deeper. I measured the gas line at 27" depth at the location of the damage. Baaziz stated that he would be taking full responsibility for the damage. I discussed dig alert laws and regulations with him and advised he call in a ticket and wait for legal start date before continuing work.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2025-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  | 0 |  | RODRI CONSTRUCTION | SPRING VALLEY | CA | N | Y | No | No | No | No | No | No | No | On Saturday 10/18/2025 at approximately 9:15AM I arrived onsite at 817 Appleridge Dr, Encinitas. Upon arrival I made contact with Adrian Rodriguez who is doing work for Rodri Construction. He stated that they were removing a tree stump to be able to lay pavers. While digging around the stump he stated they hit the gas service with a shovel. Adrian was unaware of the need to call 811 for his work. I educated him on California dig laws and informed him he needs to get a dig alert ticket and wait the legal amount of time before continuing work. Adrian also provided me with contact info for Marcelino Rodriguez who is the owner of Rodri Construction.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2025-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | MOTIVE INFRASTRUCTURE SOLUTIONS | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | On Monday 10/20/2025 at approximately 4:25 PM I arrived onsite at 1343 Gamble st in Escondido. Upon arrival I observed a 1/2" plastic gas line that was damaged in a hole being dug in the front yard of the address. I received the phone number from a motive employee onsite for the foreman. I called and spoke to Josh Perez at +1 (909) 549-1338. Josh was taking his operator for a drug test at this time which is why he was no longer onsite. He stated that his operator was digging with a mini excavator to install a handhole structure. While digging with the mini excavator he damaged the gas line. I observed the delineations saw they had white makes showing that they would be installing a 2X3 foot handhole. I measured from the delineation that the gas line that was damaged was approximately 5 feet away from this delineation. In addition to this, there were markings showing the gas up to the sidewalk near the work area. These marks were within 2 feet tolerance of the path of the damaged line. I made sure Josh and Joel with motive understood not to dig with mechanized equipment near a know gas line. I also made sure they understood they need to be more clear with their delineation and call for additional marks if they are going to expand their work area or dig outside of the original area as planned.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2025-04-15 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3173 |  | 2 |  | BASILE CONSTRUCTION INC | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage contolled. Spoke with Jeff Reese who is the General Superintendent for Basile Construction Inc who stated on April 15th at 3:00pm that his crew was using a digging bar when they managed to hit the gas. Observation of the damage was a 2? plastic main hit with a digging bar while putting cathodic on the water. This USA ticket for this job was last marked out in 2021 and has only been renewed ever since without requesting any remarks.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2025-09-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | GREENVIEW LANDSCAPE MANAGEMENT | RIVERSIDE | CA | N | Y | No | No | No | No | No | No | No | Upon arrival our SDGE gas crew had the damage controlled. Spoke with IGNACIO SALDANA with GREENVIEW LANDSCAPE MANAGEMENT who stated on September 5th at 10:40am that his crew was digging when they managed to hit the gas line. Observation of the damage was a new 1? plastic gas service hit with a mini excavator while trenching for new irrigation. The new gas service had a EFV.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2025-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MARATHON GENERAL INC | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival, SDG&E Gas Emergency Response Crew (GERC) members had controlled the leak and were working on the repair to the damaged gas line. On-site, I spoke with Sergio Nunez, Foreman of Marathon General Inc. Sergio stated was excavating for roadwork with an excavator when the 1/2? plastic gas service was damaged. Sergio stated he and his crew did not know there was a gas service in the work area as all marks has been destroyed since the mark out was completed. Sergio provided a valid USA ticket (#CSA252610475). Sergio called in a re-mark ticket and has halted exaction until the legal start date. It was confirmed that the USA ticket was valid. The 1/2? plastic gas service was observed to have been damaged with an excavator. There was a singular flag near the top of the fence line of the damage, however there was no directional identification as all remaining marks had been destroyed.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2025-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1791 |  | 6 |  | ARB INC | VISTA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On Wednesday 9/10/25 at approximately 12:45PM I arrived onsite at 2528 White Oak Pl, Escondido. While onsite I made contact with Antonio Rodriguez and Javier Marin who both work for ARB. They explained to me that one of their laborers (Eric Robles) was hand digging with a shovel when he struck a fitting on the 1/2" poly gas service causing the B&B. They had exposed the gas main at a depth of approximately 45" but struck the service at approximately 25". The service came off the main then had a rise of approximately 2 feet. They did not expect this change in depth and were not informed of any rise on the service. The 2'' rise is shown on SDG&E maps. They had a valid USA ticket and did not contest the accuracy of the marks. Markings were no longer visible at the scene of the damage.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2025-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ALLEGIANCE GENERAL CONTRACTING & PLUMBING INC | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | Met onsite with Jesus Gonzalez with Allegiance General contracting & plumbing inc (AGP). Jesus stated that he was hand digging with a shovel to expose a sewer lateral when he damaged the 1/2" poly gas service. AGP was digging without a valid USA ticket at the time of the damage. Jesus was educated onsite about using dig alert and agreed to call in a ticket onsite.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2025-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ETZAE ELECTRIC CORPORATION | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 6/13/25 at approx 10:30AM I was onsite for a gas damage at 320 S Orleans Ave in Escondido. I met with Raul Salazar to discuss the events that occurred. Raul is a project manager for Etzae Electric Corporation and is also the homeowner for the property. Raul stated that they had found the gas line that was damaged previously but were unsure what the pipe was. He said that he didn''t think the gas line would be that small. Further into their excavation they lost track of a the pipe and it was struck with a pic axe. I explained to him the importance of understanding the labels from the marks to know what he is looking for. Also to expose the gas with caution as it can be damaged with hand tools. Raul has a valid USA ticket for this job. I advised him to make sure to call for remarks periodically as well as updating his ticket every 28 days.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2025-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ARCH 2 BUILD | ESCONDIDO | CA | N | Y | No | No | No | No | No | No | No | Met onsite with Tuan Nguyen with Arch 2 Build. Tuan stated that they were digging a trench for a sewer line to a room addition in the back of the house. He stated that he damaged the gas line with a shovel. He stated that he was aware that he had to call dig alert, but still failed to do so. He agreed to call a ticket in the following business day and wait until legal start date/time to continue excavation. CSLB # 1064948
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2025-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2852 |  | 18 |  | CASS ARRIETA | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival both the fire department and police had the road secure while our SDGE gas crew get the damage contolled. Spoke with Oscar with CASS ARRIETA who stated on October 3rd at 12pm that his crew had potholed the gas but still managed to hit it. Oscar did not have any issues with the mark out because he did pothole and found the gas before using heavy equipment. Observation of the damage is a 1? plastic gas service hit with a excavator while digging for a new storm drain.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2025-07-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6673 |  | 52 |  | H7 CONTRACTING | MURRIETA | CA | N | Y | Yes | No | No | No | No | No | No | On 7/10/2025 at approximately 11:30AM I arrived onsite at the intersection of Stanley Ave and N Ash St in Escondido. When I arrived onsite the police and fire department had the roads closed. I observed a large excavator and trench at the intersection with the broken and blowing gas main. I made contact with the construction crew onsite who had been performing the excavation. I spoke with Pedro Vilchis who identified himself as the foreman of the crew for H7 Contracting. Pedro stated that they were digging a trench to install a water line for Beazer Homes. He stated that they had potholed at the location that the gas was marked and did not find the gas. After this they proceeded to dig with the excavator and then hit the gas at a different location. During my investigation I observed that the marks placed by the SDG&E locator were approximately 8 feet from the damage location. I informed Pedro that in CA government code 4216.4(b) it states that the if the excavator cannot find the location of the line marked that they shall renotify the operator for additional information. I asked him to provide a ticket number and he provided me with B251910230. This ticket was called in on 7/10/2025 at 8:45AM and was not valid yet. The other ticket I found was A243480181, which is the original ticket they had called in. This ticket expired on 7/8/2025 at 11:59PM. I confirmed with Raymond Torres with H7 Contracting that he had accidentally let the ticket expire and called in the new one this morning. There were no new delineations in white paint onsite, and all gas markings were very faded. Given this information, H7 contracting was digging without a valid ticket and violated CA gov code 4216.4.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2025-04-28 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3733 |  | 10 |  | PROWESS UTILITY GROUP INC | TEMECULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke withJulian Alcaide with Prowess Utility Group Inc who stated on April 28th at 10:30am that his crew was digging to install a ATT ped when they managed to hit the gas line. Observation of the damage was a 2? plastic gas main hit with a sharp shooter while digging to put in a ATT ped.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2025-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1802 |  | 3 |  | JUSTIN W KLOPFENSTEIN | FALLBROOK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. Spoke with property owner JUSTIN W KLOPFENSTEIN who stated that he had a crew grading on his property when they managed to hit the gas and electric. Oberservation of the damage was a 1? plastic service and electric service hit with a Dozer while grading to add a workshop on his property. JUSTIN W KLOPFENSTEIN did not have a USA ticket for this work.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2025-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | AUDIT MASTERS AND COMMUNICATIONS | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department had the road secured while they wait for our Sdge gas crew to get onsite. Spoke with Ignacio Rosa?s with Audit Masters and Communications who stated on January 7th at 1:30pm that he was digging to remove a cable box when he hit the gas. Ignacio Rosa?s stated that he didn?t see any flags. Observation of the damage was a 1/2? plastic service hit with a clay digger while removing an existing cable box. The work area was clearly marked out and several flags have been taken out to do the digging because the gas runs within inches of the cable box that is going to be removed.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2025-07-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | OPTIMUST PRIME TRUCKING INC | SAN LUI REY | CA | N | Y | No | No | No | No | No | No | No | Upon arrival our SDGE gas crew had the damage controlled. Spoke with ADRIAN AGUILAR with OPTIMUST PRIME TRUCKING, INC who stated on July 24th at 8:49am that his crew was grading and hit the gas. Observation of the damage was a 1? plastic gas stub hit with a mini excavator while grading.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2025-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MATT ZBIEC | FALLBROOK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | Upon arrival the SDGE gas crew had the damage controlled and were waiting on a line crew because the electric service was also damaged. Spoke with MATT ZBIEC who happens to be property owner who stated on November 10th at 7pm that his buddy was grading his property when the utilities were hit. Observation of the damage was a 1/2? plastic gas service hit with a s skid steer while grading to put a retaining wall in. In the process of grading they also hit the electric service to this property. The property owner did not have a USA ticket and did not know what that was. I had him call one in before leaving this property.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2025-06-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | GRIFFITH COMPANY | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival our SDGE gas crew had the damage controlled. Spoke with Woody who works for Griffith Company who stated on June 30th at 3:59pm that he potholed the gas and didn?t expect a rise in the gas line were he hit it. Woody also stated that the mark out was correct. Observation of the damage was a 1? plastic gas service hit with an excavator while trenching for water and storm drains.
San Diego Gas and Electric | N | SAN DIEGO | IMPERIAL BEACH | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1721 |  | 5 |  | PROPERTY MANAGER ANNA LIZA YOUNG | IMPERIAL BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | On-site I spoke to Anna Liza Young the property manager who stated she had a worker excavating with hand tools to repair the sewer line when the 1/2" poly service line was damaged. Anna Liza Young and her worker Sadisadiri Gelacio were unable to provide a valid dig alert ticket, both were advised to request a dig alert ticket before continuing with the proposed work. Once the damaged 1/2" poly service line was controlled by the SDGE GERC crew it was confirmed it had been damaged with hand tools. Within the location of the damage I did not observe any delineations or locate marks to work on the sewer line. It is clear Anna Liza Young and her worker failed to request a ticket before excavating.
San Diego Gas and Electric | N | SAN DIEGO | IMPERIAL BEACH | 2025-05-29 | Third party excavation damage | Main | Steel | Boring Equipment | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2575 |  | 18 |  | JESMAR CONSTRUCTION INC | FALLBROOK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On-site I spoke to Jesse Hernandez with Jesmar Construction Inc who confirmed he was operating the bore machine to place conduit when the 1 1/2" steel gas main was damaged. Jesse H. provided USA A251490169, which its legal start date is not until 06/02/2025 @ 17:01 and informed me he was doing the work for Blue Pacific Eng who were also on-site. I met and spoke to Victor Velazquez (442-207-2763) foreman with Blue Pacific Eng who also confirmed the gas line was damaged while pulling out bore for the underground conversion taking place for the City of San DIego. Victor Velazquez confirmed USA A251250430, was requested by his office to complete the work. However, after reviewing the notes and delineations on-site I noticed the location of the damage was not covered by their ticket. The location of the damage is at approx. 20'' outside the delineated area, which only covered from face of curb to face of curb. I advised both Jesmar Construction and Blue Pacific Eng to request new tickets and place new delineations to cover all proposed work areas before any excavation work continued to take place. Within the location of the damage I did not see any delineations or gas locate marks other than the ones placed for the SDGE GERC crew to control the gas and complete repairs. I set up my damage kit and took my damage photos. It is clear Jesmar Construction failed to wait the appropriate time to have the ticket completed and dug early. Blue Pacific Eng also had its subcontractor bore approx. 20'' outside the delineated work area.
San Diego Gas and Electric | N | SAN DIEGO | JAMUL | 2025-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1732 |  | 2 |  | MERAM CONSTRUCTION | EL CAJON | CA | N | Y | No | No | No | No | No | No | No | On-site I spoke to Irvin Meram owner of Meram Construction who stated his crew damaged the 1" poly service line while grading with mechanized equipment. Irvin Meram was under the assumption that he did not need to request a dig alert ticket since they were grading within the homeowners side yard. I advised Irvin Meram to request a valid dig alert ticket before continuing with any grading for which he agreed and requested USA B25034067. Within the location of the damage I did not observe any gas locate marks or delineations. It is clear Meram Construction damaged the 1" poly service line while grading without a valid dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2025-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JTH CONSTRUCTION INC | TEMECULA | CA | N | Y | No | No | No | No | No | No | Yes | I met onsite with Brian Ollier with JTH Construction on 6/10/2025 at approximately 12:30PM. Brian stated that he was hand digging to expose existing footings when he hit the 1/2" gas service with a shovel. He stated that he knew the gas was there and agreed the markings were accurate. He stated that he had thought the gas line would be deeper. I researched his dig alert ticket and found that the ticket was expired. I advised him to call in a new ticket and wait the appropriate amount of time before continuing his excavation.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2025-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  | 0 |  | VSR CONSTRUCTION | CHULA VISTA | CA | N | Y | No | No | No | No | No | No | No | Upon arrival our SDGE gas crew had the damage controlled. Spoke with JUAN VILLASENOR with VSR CONSTRUCTION who stated on November 27th at 12:15pm that he was grading when he managed to hit the gas line. When I asked him about a USA dig ticket he said that the dig alert told him that no mark outs would be on private property. Observation of the damage was a 3/4? steel gas service hit with a bobcat while grading for property upgrades.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2025-06-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | SANZ LANDSCAPE CONSTRUCTION INC | ESCONDIDO | CA | N | Y | No | No | No | No | No | No | Yes | On-site I met and spoke to crew with Sanz Landscape Construction Inc who stated the 1" poly service line had been damaged while excavating for a retaining wall with mechanized equipment. The crew provided Sanz Landscape Construction Inc owner Everardo Sanchez''s phone number who I contacted via telephone. Everardo Sanchez confirmed his crew damaged the gas line while excavating for the retaining wall and added the work was being completed for Redline Custom Contracting. I advised Everardo Sanchez to request a valid dig alert ticket before continuing with the excavation for the retaining wall. I did not observe any delineations or locate marks placed for Sanz Landscape Construction Inc within the location of the damage. I set up my damage kit and took my damage photos. It is clear Sanz Landscape Construction Inc failed to request a dig alert ticket for the excavation taking place at the job site.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2025-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2954 |  | 4 |  | HP COMMUNICATIONS INC | EL CAJON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On-site I spoke to both John W. Carter and Pablo Aguilera with HP Communications Inc who stated the 3/4" steel gas line had been damaged while trenching with rockwheel trencher to install communication conduit. The foreman Pablo Aguilera informed me they had potholed at the location where the service line had been marked and had found a 3/4" steel pipe at that location.However, they were not expecting to come across any other line at the location of the damage since they had not seen any marks at that spot. Pablo Aguilera provided USA A253350959, which is active and added that all marks have been accurate and they have not come across any issues finding the located gas lines. Once the damaged 3/4" steel service line was controlled and exposed it was confirmed to have been damaged with mechanized equipment. I did not observe any gas locate marks that aligned with the path of the damaged 3/4" steel service line. I set up my damage kit and took my damage photos. It is clear HP pipeline damaged a 3/4" steel service line while trenching with rockwheel trencher to install communication conduit. QA and Damage prevention supervisor determined maps are inaccurate and conductivity issues when locating this gas line.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2025-11-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  | 0 |  | STRUCTWELL CONSTRUCTION INC. | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival on 11/24/2025, Jeffrey Dalglish, Foreman of Structwell Construction Inc., was onsite with crews actively excavating for electrical installation. Jeffrey stated that on 11/07/2025, his crew was utilizing the mini-excavator when they hit the 1? plastic gas service. They initially believed they damaged the retired gas line, as only a small amount of gas released and they continued working. Jeffrey stated that upon arrival of the SDG&E Gas Emergency Response Crew (GERC), it was determined that the 1? plastic gas service excess flow valve (EFV) was triggered when the service was hit. Jeffrey stated they had SDG&E utility marks still visible and they were aware of the location of the gas service, but failed to fully pothole the gas service with hand tools. Jeffrey was provided Dig Alert Literature and educated on pot holing and re-mark tickets. Per SDG&E Gas Supervisor, Mike Balsley?s Fast Field Emergency Incident Damage Report completed on 11/07/2025, the 1? gas service was observed to be damaged with a mini excavator. Per photos provided by Mr. Balsley, there appears to be one singular SDG&E utility gas flag mark out that was near the gas meter; the mark out appeared to be within the tolerance zone. It was that the USA ticket was valid at time of the damage.
San Diego Gas and Electric | N | SAN DIEGO | LA MESA | 2025-12-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4223 |  | 17 |  | AJT CONSTRUCTION INC | EL CAJON | CA | N | Y | No | No | No | No | No | No | No | On-site Pablo Ramirez operator for AJT Construction Inc stated the 2" poly gas main had been damaged while excavating to repair private sewer line with mechanized equipment. Pablo Ramirez informed me him and his crew had spotted the gas line, but accidentally got too close with the excavator bucket. Adrian Jay Tapia owner of AJT Construction Inc was also onsite and was unable to provide a dig alert ticket number. Mr. Tapia along his crew were advised to stop all work and not resume until a 811 ticket has been requested and completed. Once the SDGE GERC crew safely controlled the damaged gas line we were able to confirmed it had been damaged with mechanized equipment. Within the location of the damage I did not observe any delineations or gas locate marks. I placed my damage kit and took my damage photos. It is clear AJT Construction Inc damaged the 2" poly gas main while excavating with mechanized equipment to repair sewer line without a valid dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | LA MESA | 2025-12-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  | 0 |  | TRUSTED CONSTRUCTION | RAMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Clint Young with Trusted Construction who stated the 1/2" poly inserted gas line had been damaged while excavating to relocate gas meter with mechanized equipment. Mr. Young added his worked had been instructed not to excavate with mechanized equipment at the location of the damage. However, he unfortunately did and accidentally damaged the gas line. Once the damaged 1/2" poly inserted gas line was fully controlled by the SDGE GERC crew it was confirmed it had been damaged with mechanized equipment. Within the location of the damage, I could observe gas locate marks that aligned with the path of the damage line. I set up my damage kit which confirmed the locate marks were accurate and took my damage photos. It''s is clear Trusted Construction damaged an accurately 1/2" poly service line while excavating with mechanized equipment to relocate the gas meter.
San Diego Gas and Electric | N | SAN DIEGO | LA MESA | 2025-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SMITH ELECTRICAL CONTRACTORS INC | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department was gone. Our SDGE gas crew had the damage controlled. Spoke with RAFAEL ALVARADO with SMITH ELECTRICAL CONTRACTORS, INC who stated on August 7th at 5:00pm that he was trenching for electrical when he hit the gas service near the handhold on the driveway. RAFAEL ALVARADO also stated that he did not have any issues with the mark out. Observation of the damage was a 1/2? plastic service hit with a shovel while trenching for a panel upgrade.
San Diego Gas and Electric | N | SAN DIEGO | LA MESA | 2025-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | SC VALLEY ENGINEERING, INC. | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Dan Beeson who is the job site Superintendent with SC Valley for the sewer project currently taking place. Mr. Beeson stated his crews were in the process of grinding asphalt when the marked 3/4" steel service was damaged. Mr. Beeson added they were not expecting to come across the service line at that depth. I advised Mr. Beeson to lift the asphalt grinder when coming across marked service lines to try to avoid another damage occurring as well as to pothole by hand to determine exact depth & location, for which he agreed. Once the damaged 3/4" steel service line was safely controlled by the SDGE GERC crew it was confirmed it had been damaged with asphalt grinder at approx. 6" deep. Within the location of the damage, I could observe gas locate marks that aligned with the path of the damaged gas line. I placed my damage kit and took my damage photos. It is clear SC Valley damaged an accurately marked 3/4" steel service line while grading asphalt for their sewer project.
San Diego Gas and Electric | N | SAN DIEGO | LA MESA | 2025-05-15 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12230 |  | 7 |  | T.MAUS GRADING & PAVING | SAN JACINTO | CA | N | Y | No | No | No | No | No | No | No | On-site I spoke to Marcel Cruz superintendent with T. Maus Grading & Paving who stated his workers were auguring to install a new shopping cart corral when the 4" poly gas main was damaged. Marcel Cruz provided USA A250970876, which expired on 5/05/2025 and the work description only covered for removal and replacement of asphalt at 18 inch. I advised Marcel C. to stop work and not continue until a new ticket has been requested with the correct job description. Once the damaged 4" poly gas line was controlled by the SDGE GERC crew it was confirmed it had been damaged with the auger at approx. 3'' deep. Within the location of the damage I did not observe any delineations or locate marks, other than the marks placed for the SDGE GERC crew to complete the needed repairs. It is clear T. Maus Grading & Paving failed to request a valid dig alert ticket for the proposed work taking place onsite.
San Diego Gas and Electric | N | SAN DIEGO | LAKESIDE | 2025-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1026 |  | 1 |  | HAWTHORNE CAT | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | On-site I spoke to Jim Mady facilities manager for Hawthorne CAT who stated the 1 1/4" poly service line was damage while excavating with mechanized equipment to repair sewer line. Jim Mady added they did not request a dig alert ticket since they believed they didn''t need one to excavate within private property. I provided dig alert information and advised Jim M. to request a ticket before resuming with excavation. Once the damaged 1 1/4" poly service line was controlled by the SDGE GERC crew it was confirmed it had been damaged with mechanized equipment. Within the location of the damage I did not observe any delineations or locate marks. I placed my damage kit and took my damage photos. It is clear Hawthorne CAT failed to request a valid dig alert ticket to complete the proposed work taking place.
San Diego Gas and Electric | N | SAN DIEGO | NATIONAL CITY | 2025-09-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | BALLOW CONSTRUCTION INC | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I contacted Rob Andrade foreman with Ballow Construction Inc who stated the marked 1" poly service line had been damaged while trying to pothole for it with a digging bar. I reminded Rob Andrade to keep his dig alert ticket active. Once the blowing gas line was controlled by the SDGE GERC crew it was confirmed it had been damaged with hand tools. Within the location I could observe most locate marks had been destroyed. However, I could observe locate marks on the driveway that aligned with the path of the damaged 1" poly service line. I set up my damage kit, which confirmed the locate marks were accurate and took my damage photos.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-12-04 | Third party excavation damage | Miscellaneous/Other | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3024 |  | 5 |  | JON DEL CONSTRUCTION | ALPINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with LAURO DE LA ROSA with JON DEL CONSTRUCTION who stated at 2:40pm that he was digging with the excavator and managed to hit the gas line. Lauro also stated that the gas line was not exposed before using mechanized equipment. Observation of the damage was a 3/4? steel stub that was not mapped or marked by the locator hit with a excavator while trenching for new sewer line. The contractor is at fault for this damage due to the fact that they should not be using mechanized equipment within 2? of a utility. The contractor didn?t not know this.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JOSH BLANC CONCRETE | OCEANSIDE | CA | N | Y | No | No | No | No | No | No | No | Met onsite with Bryce Carrier. Bryce is the neighbor of Rick Pentella who is the homeowner having the work done for his property. Rick is out of town so Bryce was taking over the oversight of this project. Bryce stated that they were having work done by Josh Blanc Concrete. Josh Blanc was not onsite but his crew was. They were excavating to install utilities, specifically sewer at the time of the damage. They damaged the 1/2" plastic service with a shovel while digging to install a new sewer line for an ADU. The gas line was accurately marked. The ticket for this work had expired on 1/1/25. I informed Bryce and Josh Blanc that they need to have a new ticket and stop excavation until the new ticket is valid. Also discussed safe digging practices with Josh Blanc to avoid these damages in the future.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JOSHUA HELMLE | OCEANSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. Spoke with H/O HELMLE, JOSHUA who stated on July 2nd at 4:00pm that he had some guys digging and managed to hit the gas line. Observation of the damage was a 1/2? plastic gas service hit with a sharp shooter while trenching for drain/sewer.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2631 |  | 18 |  | JAZZAR CONSTRUCTION GROUP | IRVINE | CA | N | Y | No | No | No | No | No | No | No | Upon arrival I made contact with the excavating contractor Joe Jazzar. Joe stated that they were digging a trench with a mini excavator to install electrical conduit when they damaged the gas line. Joe stated that the gas line was not marked. He also stated that he had potholed at the location of the marks placed but did not find anything at this location and assumed that it was deeper. Joe provided a dig alert ticket number that had expired on 12/25/24. I had a discussion with Joe about his expired ticket and advised him to call a new one in before continuing excavation. I also discussed with Joe that if they pothole and do not find our utilities as marked, they need to notify us through dig alert to come back out. Observing the scene of the damage I found that the 1/2" plastic service was mis-marked by approximately 15 feet. Yellow markings onsite were placed after the damage occurred. Investigation by SDGE QA was completed onsite. *CSLB License #1043051*
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3934 |  | 18 |  | CALIFORNIA PLUMBING AND SANITATION INC | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | No | Yes | On Wednesday 6/4/25 at approximately 11:30 AM I met with Miguel Broce onsite at 212 S Pacific St in Oceanside. Miguel explained to me that they had exposed the majority of a gas line in the alley behind the address to install a new gas service. He stated that they were digging with a mini excavator and hit the punch tee on the 3/4" steel service. They didn''t expect the there to be a change in the pipe at all at the service connection and assumed exact depth would stay the same. Miguel confirmed that they did not have a dig alert ticket for the gas work being done in the alley. He only had a dig alert ticket for water work in the front of the property. There were old marks onsite from a previous job so he stated he knew where the gas was. I advised him to call in a ticket onsite for the work being done in the alley.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-10-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | GOTHIC LANDSCAPE | SAN MARCOS | CA | N | Y | Yes | Yes | No | No | No | No | Yes | On 10/9/2025 at approximately 10:15AM I arrived onsite at 2308 Loker Way, Oceanside. I made contact with William Sosa with Gothic Landscape. William stated that their crew had started digging that morning to install drains with a mini excavator and dug into the gas service. This same crew had hit a gas service across the street the day before for the same dig alert ticket. Gothic Landscaping proceeding with their excavation even with the knowledge that the gas had not been marked yet. They were informed to resend their ticket to have the gas mark out completed but failed to do so. They also were using mechanized equipment in an area with known gas present. In addition to this, they had ripped out warning mesh above the gas line before hitting it. I advised William to stop all work and wait until all positive response is received and legal start date and time is reached. He agreed.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-10-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | GOTHIC LANDSCAPE | SAN MARCOS | CA | N | Y | Yes | Yes | No | No | No | No | Yes | On 10/8/2025 at approximately 2:15PM I arrived onsite at 2309 Loker Way, Oceanside. Upon arrival I made contact with William Sosa with Gothic Landscape. William stated that they were digging to install a drain with a mini excavator when they hit the gas line. William did call in a dig alert ticket but did not receive positive response. The ticket was closed with EPR code 22 as no delineations requesting to resend ticket. The SDG&E locator also called William twice and sent him a text asking him to clarify the location because he was unable to find the delineations. William did not call or message back and did not check his EPRs. They proceeded to dig with no marks on the side of address with signs of gas in the area as well. I communicated to William to recent the ticket to get SDG&E back onsite to mark the gas.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-08-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3663 |  | 9 |  | COLONIAL ELECTRIC INC | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On Thursday 8/21/25 at approximately 1PM I arrived onsite at 2638 Vista Pacific Dr. I observed a 2" gas main damaged in a trench behind the sidewalk on the north side of the road. I could see visible marks showing the 2" plastic gas main was marked and labeled in yellow paint. The damaged line was marked accurately within the tolerance zone. I made contact with Casey Selby onsite who is the foreman for Coloniel Electric. Casey stated that they were digging a trench to install electrical conduit from the building to an SDGE electrical structure. He stated that they did not pothole the gas main by hand before using mechanized equipment. This is the root cause of the damage. I explained to Casey that they cannot use mechanized equipment within the tolerance zone until they have exposed the marked utilities with hand tools first. He understood and agreed to follow these rules going forward.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | DUANE ROSS | OCEANSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | Upon arrival the fire department was gone. Our SDGE gas crew had the damage controlled and repaired upon my arrival. Spoke with Duane Ross who is the property owner who stated on January 23rd at 7:09pm that he was digging to replace his fence that blew over. Duane did not know what 811 dig alert was. Observation of the damage was a 1/2? plastic gas service hit with a post hole digger while putting in a fence.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | DOHERTY CONCRETE | OCEANSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Met onsite with gas supervisor. He discussed damage with a Chris Doherty. He stated that the 1/2" plastic gas service was damaged with a shovel accidentally while digging a trench for electrical conduit. The marks were accurate and the crew knew it was there. Met with Aaron onsite and he confirmed this information. CSLB #707928
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | RICHARD SHAFFER | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Met with Richard Shaffer onsite. Richard is the home owner who was digging a trench for new electrical conduit. Richard stated he was digging along the top of the pipe to fully expose it in his trench when he accidentally cut into it with his shovel. He had a valid dig alert ticket and the marks were within the tolerance zone. Safe digging practices were discussed with Richard.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | MOHAMMAD OSTADKAR | OCEANSIDE | CA | N | Y | Yes | Yes | No | No | No | No | No | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with property owner MAHSHID OSTADKAR who stated on December 3rd at 12:58pm that she had a helper dig a trench for a panel upgrade when the gas line was hit. Observation of the damage was a 1/2? plastic gas service hit with a shovel while trenching for a panel upgrade. The USA ticket was never marked out due to no delineations. The homeowner was contacted by our locator about the work area not being marked out because of this. The USA ticket expired on 11/26/25 23:59.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4801 |  | 49 |  | EMERGENCY RESPONSE ELECTRIC | LAKESIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 10/1/25 at approximately 12:00 PM I arrived onsite at 3517 Orr st in Oceanside. Upon my arrival I observed a trench being dug on the property. There were visible yellow markings in front of the damage location showing the line accurately marked. I made contact with Ben Dukes (760-419-6547)with Emegency Response Electric. He stated that he was the one performing the digging. He stated he was trying to dig through roots and accidentally hit the gas line with a shovel. He said he knew the line was there and that they had potholed the line further up towards the meter previously. I also called and spoke with Romo Carreno and discussed the damage with him. He is aware of what happened. Onsite I also spoke with Gas Supervisor for SDG&E. He stated they controlled the leak by turning a valve causing 48 outages.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JUAN VITAE | OCEANSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. Spoke with Nicola, Ken who is the property owner who stated on April 3rd at 9:40am that he was digging with the help of his friends when they managed to hit the gas line. Nicola, Ken didn?t know what a USA ticket was. Observation of the damage was a 1/2? plastic gas service hit with a shovel while doing a retaining wall.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-01-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | YNK CONSTRUCTION | ENCINITAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Met onsite with Luis Mungaray with YNK Construction. Luis stated that they were digging a trench to install electric conduit when they accidentally damaged the 1" plastic service with a shovel. Luis stated they knew the gas was close because they had found it further down the driveway and there was yellow caution tape for the gas line. He stated they tried to dig carefully but still damaged the line. There were no visible marks at the damage location but pre excavation photos show the line was accurately marked. I advised Luis to get remarks before continuing work.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-06-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | JOSE LOPEZ | OCEANSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled. Spoke with Jose who is a family member of the owner who stated on June 28th at 11:45AM that he was digging his last section of the trench when he managed to hit the gas. Jose did not dispute the mark out. Oberservation of the damage was a 1? plastic gas service hit with a shovel while trenching for new drains. The 1? plastic gas service had a EFV.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-03-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3033 |  |  | NA | BLUE PACIFIC CONSTRUCTION | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled. Spoke with Tony Harts with Blue Pacific Construction who stated on March 15th at 4:15pm that he was trenching for drains when he managed to hit the gas. Observation of the damage was a 2? plastic gas main hit with an excavator while trenching for drains.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-01-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 56175 |  | 719 |  | UNITED STATES MARINE CORP WATER RESOURCES DIVISION | CAMP PENDELTON | CA | N | Y | No | No | No | No | No | No | No | Met onsite with Darrell Johnson (760-905-6524). Darrell is a crew member of the water resources division for Camp Pendelton. Darrell stated that him and his crew were conducting an emergency excavation with a backhoe to repair a water main leak. He stated that the water leak undermined the asphalt and a piece of the asphalt fell and damaged the 3" gas main. Upon further inspection of the gas main it appears to have been bent upward and broken open from an upward angle. In the professional opinion of the SDG&E gas crew supervisors, the cause of the damage appeared to be from the backhoe pulling up on the pipe while digging, not from something falling onto it. The water resources division did not have a dig alert ticket for the work they were doing. I advised them onsite to call in emergency tickets. Anthony Velletto is the supervisor for the water crew. He called in the emergency ticket and an SDGE locator provided positive response while onsite. Anthony provided me with the new dig alert ticket (A250060999). *After the damage occurred a marine Corp gas crew responded to the damage and shut off gas at a nearby reg station causing an outage to approximately 720 customers*
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2025-06-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | DOHERTY CONCRETE | OCEANSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled. Spoke with Tim Haggerty with Doherty Concrete who stated on June 19th at 10:40am that he found the abandoned gas line and thought it was the energized one and kept on digging and ended up hitting the energized gas service. Observation of the damage was a 1/2? plastic service hit with a mini excavator while trenching to put in a new gas line.
San Diego Gas and Electric | N | SAN DIEGO | OLIVENHAIN | 2025-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2814 |  | 2 |  | SUNNY BUILDERS GROUP | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | Yes | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled. Spoke with Adan Hinojosa on the phone and he stated on June 24th at 4:12pm that he was digging on the side of the property when he managed to hit the gas. Observation of the damage was a 3/4" steel gas service hit with a mini excavator while trenching to put in a retaining wall. Adan Hinojosa did not know what a USA dig alert ticket was.
San Diego Gas and Electric | N | SAN DIEGO | OLIVENHAIN | 2025-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  | 0 |  | CE POOLS | SAN MARCOS | CA | N | Y | No | No | No | No | No | No | No | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. Spoke with the crew with CE POOLS who stated that he was trenching up to the gas meter and electrical when he hit the gas. Observation of the damage was a 1/2? plastic gas service hit with a shovel while trenching in the utilities for a swimming pool. CE POOLS did not have a USA ticket.
San Diego Gas and Electric | N | SAN DIEGO | OLIVENHAIN | 2025-07-31 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3103 |  | 1 |  | AT&T | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | Upon arrival our SDGE gas crew had the damage controlled. Spoke with JOSUE MALDONADO with AT&T who stated that he was digging to put a new pole in. Observation of the damage was a 2? plastic gas main hit with a auger while digging to put a new pole in the same existing area. AT&T did not have a valid USA ticket for this work.
San Diego Gas and Electric | N | SAN DIEGO | OLIVENHAIN | 2025-08-01 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3103 |  | 1 |  | ENDRIZZI ENTERPRISES | ANAHEIM | CA | N | Y | Yes | No | No | No | No | No | No | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. Spoke with REX ENDRIZZI with ENDRIZZI ENTERPRISES who stated on August 1st at 12:35pm that he was grading and thought the gas would be deeper. Observation of the damage was a 2? plastic gas main hit with a bucket loader while grading the street. The USA ticket for this job was expired.
San Diego Gas and Electric | N | SAN DIEGO | OLIVENHAIN | 2025-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | INLAND VALLEY PIPELINE | MENIFEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival our SDGE gas crew had the damage controlled and repaired. Spoke with Hubaldo Hurtado with INLAND VALLEY PIPELINE who stated on October 27th at 9:20am that he had potholed and found the gas in several spots but managed to hit the gas further down. Observation of the damage was a 1/2? plastic gas service hit with a mini excavator while trying to expose the gas line so it can be RFS?d. I let Mr. Hurtado know that he needs to pothole using hand tools not a mini excavator.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2025-08-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3103 |  | 1 |  | DEMCON CONCRETE CONTRACTORS | POWAY | CA | N | Y | No | No | No | No | No | No | No | On 8/18/25 at approximately 11AM I arrived onsite at 13830 Danielson St in Poway. I first made contact with Travis Ross (661-733-5174) who is a Construction Manager for Eolus. Eolus is the company that was in charge of the site where work was being performed. Travis stated that they are using a company called Gridworks to manage all of the sub-contractors performing work at the site. I met with 3 individuals from Gridworks. Jonathan Peralta (949-244-1813), Omar Esieed (415-316-8114), and Kevin Godwin (678-209-4154). Kevin Godwin stated that he was the construction manager in charge. Gridworks hired Demcon Concrete Contractors to excavate to expose a sewer lateral that needed to be cut and capped. Demcon did not have a dig alert ticket for the site and there were no marks present for the gas main that was damaged. Kevin stated that he was unaware that they did not have a dig alert ticket but that he was supposed to confirm that they did before starting excavation. Kevin stated that all claims should go through him for the damage and he will be the main point of contact. He agreed to have a ticket called in for Demcon as soon as possible.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2025-09-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | LV HOLDERBY JR GENERAL ENGINEERING | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department had the road secured while our sdge gas crew get the damage controlled. Spoke with LEN HOLDERBY JR with L V HOLDERBY JR GENERAL ENGINEERING who stated on September 11th at 12:15pm that he was digging to find the gas stub when he managed to hit it. Observation of the damage was a 1? plastic gas service hit with a dig bar while trying to expose the stub. The USA ticket for this job was expired.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2025-09-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3173 |  | 2 |  | LV HOLDERBY JR GENERAL ENGINEERING | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with LEN HOLDERBY with L V HOLDERBY JR GENERAL ENGINEERING who stated that he potholed the gas and knew it was there and still managed to damage it. Len did not have any complaints about the mark out. Observation of the damage was a 2? plastic gas main hit with a excavator while trenching to put utilities in.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2025-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  | 0 |  | IRVING DIAZ | EL CAJON | CA | N | Y | No | No | No | No | No | No | No | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. Spoke with Irving Diaz who was doing some side work for the owner of the property who stated that he was digging for a post when he hit the gas line. Observation of the damage was a 1? plastic gas service hit with a jackhammer while digging to put in a new fence.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2025-03-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | NEED FOR BUILD | POWAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department was gone. The gas had an excess flow valve which stops the gas from blowing. Spoke withRobert Mata with Need For who stated on March 19th at 3:30pm that his crew was trenching for a panel upgrade when they hit the gas. Observation of the damage was a 1? plastic gas service hit with a jackhammer while trenching for a panel upgrade.
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2025-08-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7315 |  | 21 |  | SANTA FE IRRIGATION DISTRICT | RANCHO SANTA FE | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | On 8/11/2025 at approximately 11:40 AM I arrived onsite in front of 15564 Las Planideras in Rancho Santa Fe. Upon my arrival the gas leak had been controlled and I observed a 3" poly gas main damaged in a trench. I made contact with Alfredo Graciano onsite who is a foreman for Santa Fe Irrigation District. Alfredo stated that they were excavating with a back hoe to install a new water service when they hit the gas line. There were no marks for gas in the work area at the time of excavation (photos of gas marks were placed after the damage occurred). I researched the dig alert ticket and found that it was not valid until 8/13/25 at 7:01AM. I explained this to Alfredo and he agreed they had dug before they were supposed to. I showed Alfredo how to navigate the dig alert website to check for individual positive responses and he agreed to use this tool in the future. I also spoke with Santa Fe Irrigation District supervisor Jason Meyer. I explained the issue of not waiting until legal start date/time and he understood and agreed to be more vigilant on positive responses in the future. The dig alert ticket was called in on 8/4/25 which would normally give a start date of 8/6/25 at 5:01PM. Since Jason told dig alert that he was planning to start work on 8/13, they created the ticket with that as the legal start time. I told him to be mindful of this and always check his dig alert ticket and positive response.
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2025-05-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | VAN LYONS COMPANY | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | On Friday, 5/16/25 at approximately 16:30 I met onsite with Francisco Martinez at 17225 Calle Mayor in Rancho Santa Fe. Francisco works for Van Lyons Company. He stated that he and their crew were digging a trench with hand tools when they hit the gas line. He gave me contact info for his boss Edgar Salgado. I called and spoke with Edgar Salgado while onsite. I confirmed the info that Francisco provided me. Edgar stated that they were trenching for the relocation of a gas line. He confirmed that they had not called in a dig alert ticket. He said they had called a while back but not for this job. I educated him on 811 rules and safe digging practices. I advised him and Francisco to cease all excavation until their new dig alert ticket is called in, marked out, and legal. The ticket Edgar referred to having called in previously was for electrical work and called in on 5/13/24 at 13:26 and expired 6/10/24. CSLB # 993981
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | MIKE LLOYD EXCAVATION | RANCHO SANTA FE | CA | N | Y | No | No | No | No | No | No | No | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. Spoke with BRET MINTUN with MIKE LLOYD EXCAVATION who stated on July 2nd at 9:50am that the crew had potholed the gas but still managed to hit it. The area had old mark outs that were accurate. Observation of the damage was a 1? plastic gas service hit with a mini excavator while trenching to put new drains in.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | RAOZ GENERAL | SAN DIEGO | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage contolled. Spoke with Ryan Drosinski who is the Forman onsite for Raoz General Engineering who stated on April 15th at 11:40am that the gas line was exposed partially and his crew assumed that the gas went straight when they managed to hit the gas. Observation of the damage was a 1? plastic gas service hit with a mini excavator while trenching for electrical panel upgrade.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-04-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6055 |  | 3 |  | WA RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site, I contacted Jeffrey McGrand at 915-525-6548, superintendent with WA Rasic Construction, who confirmed the 3" poly gas stub had been damaged while excavating for a new water line with mechanized equipment. Jeffrey stated the crew had seen the marks for the stub, but were not expecting it to be within their work area since the mark out stopped at the fence. I asked Jeffrey the marks placed by the SDGE locator stated to pothole the poly dead end, if they had potholed by hand to determine depth and location for which he stated they had potholed at another location for it. I advised Jeffrey to always pothole by hand when it''s written on the ground by the locator, since most stubs are marked per map measurement and if not found, to re-notify. The damaged gas line was controlled by my arrival. However, it was unsafe to get close since the hole was deep and unstable. Within the location of the damage, I could observe gas locate marks that aligned with the path of the damaged stub as well as an offset near the location of the damaged stub. I set up my damage kit and determined the marks and offset were within tolerance. I reached out to James Foad with WA Rasic Construction, who had requested the dig alert ticket and advised him to request remarks since some marks had been destroyed due to the work taking place. James Foad was not fully aware of what had occurred onsite and was under the impression that shoring or concrete had fallen on the exposed gas stub which had caused it to be damaged. James Foad agreed to request remarks to have fresh marks placed for his crew.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | BURTECH PIPELINE | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke with Juan Vitae foreman for Burtech Pipeline who stated the 1/2" poly service line had been damaged while trenching with mechanized equipment to install new sewer main. Juan V. Added that they planned to pothole and were only removing concrete/asphalt when the shallow line was damaged. I advised Juan V. and his crew to never assume depth on a marked utility and always pothole by hand before using any mechanized equipment above it. Once the gas blowing gas line was controlled by the SDGE GERC crew we were able to confirm the 1/2" poly service line had been damaged with mechanized equipment. Within the location of the damage I could observe faded gas locate marks that aligned with the path of the damaged gas line. I set up my damage kit which confirmed the locate marks onsite were accurate and took my damage photos. I advised Juan to request re-marks since most marks were very faded or had been already destroyed.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | EDUARDO ESTEFAN | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | Yes | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. Spoke with Eduardo Estefan who is doing work for the homeowner. Eduardo Estefan stated on June 24th at 2:40pm that he was trenching for the electric when he hit the gas. Observation of the damage was a 1/2? plastic gas service hit with a pickaxe while trenching for a panel upgrade.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ALBA CONSTRUCTION 3 INC | SAN DIEGO | CA | N | Y | Yes | No | No | No | No | No | No | On-site I spoke to Michael Alba with Alba Construction 3 Inc, who stated the 1/2" poly service line had been damaged while trenching with hand tools to install utilities for an ADU. Michael Alba provided USA B251390300, which had expired on 6/16/2025. No SDGE utilities had been marked out for the expired ticket B251390300, since no delineations had been found at the time the locator responded. I advised Micheal Alba to delineate and call in a new ticket before continuing with the proposed trenching. Once the damaged 1/2" poly service line was fully controlled by the SDGE GERC crew it was confirmed it had been damaged with hand tools. I did not observe any delineations or utility locate marks within the location of the damage. I set up my damage kit and took my damage photos. It is clear Alba Construction 3 Inc damaged a 1/2" poly service line while trenching with hand tools without a valid dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  | 0 |  | RICHARD OLINGER ELECTRIC | VISTA | CA | N | Y | Yes | No | No | No | No | No | No | On Wednesday 9/10/25 at approximately 2:30PM I arrived onsite at 10969 Montongo St, San Diego. I made contact with William Middleton who works for Richard Olinger Electric. William stated that they were digging a trench for electrical conduit and that the ground was very hard and rocky. He was using a rotary hammer with a flat head bit to chip around the rocks. While chipping he hit the gas service. He stated that he knew that gas was there and the marks were accurate. They had a dig alert ticket but it expired yesterday, 9/9/25 at 11:59PM. I advised them to call in a new ticket and they agreed.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | VU CONSTRUCTION | SAN DIEGO | CA | N | Y | Yes | No | No | No | No | No | No | On 9/4/25 at approximately 3:30PM I arrived onsite at 11228 Pegasus Ave, San Diego. I researched ticket information and found that there was a Dig Alert ticket for the work being done. This ticket was called in on 3/26/25 and expired on 4/23/25. The address on the ticket is 11230. The work area is between 11228 and 11230. While onsite I made contact with Thu Vu. He was the one listed as the site contact on the ticket. I communicated with Thu through google translator on my phone as he did not speak English. He only spoke Vietnamese. He stated that while trenching for electrical conduit he hit the gas with a jackhammer. There were minimal markings onsite to show how the gas was running. I asked him if he knew the gas was there. He stated that he thought it was marked incorrectly. I found pre excavation photos showing the line marked in the area of the damage. I communicated to him that his dig alert ticket was expired and that he must call in a new ticket and have everything clearly marked before continuing work.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | PIPERIN CORP | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled. Spoke with Don Gingrich with Piperin Corp. who stated on June 24th at 10:40am that his operator was digging and managed to hit the gas service. Don assumed he knew how all the gas lines were running due to the other services and when they pot holed and didn?t find the gas they assumed it wasn?t in the trench line and kept digging. Observation of the damage is a 1/2? plastic service hit with an excavator while doing sewer work for the city of San Diego.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | AUDIT MASTERS AND COMMUNICATIONS | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with Maurilio Suazo with AUDIT MASTERS & COMMUNICATIONS who stated on September 18th at 9:30am that he was potholing the gas when he managed to hit it. Observation of the damage is a 1/2? plastic gas service hit with a sharp shooter while potholing to expose the gas service. AUDIT MASTERS & COMMUNICATIONS was putting in a communications handhole.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-04-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | JENSEN LANDSCAPE | ENCINITAS | CA | N | Y | No | No | No | No | No | No | No | On Tuesday, 4/22/25 at approximately 3:00 PM I met onsite with Carlos Rodriguez with Jensen Landscape. Carlos stated that he and another employee were operating a mini excavator to dig a trench for installing irrigation. They were performing work for Lennar. There were no signs of any utility markings in the area. I confirmed with Carlos that they did not have a valid USA ticket. He stated that he did not think dig alert was used for private property. I informed him that it is and he always needs to have a valid ticket before excavating. CSLB 881723.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-07-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  | 0 |  | BRIAN LINN | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | No | Yes | On-site I met homeowner Brian Linn who stated the 1" poly service line had been damaged while excavating with mechanized equipment while trying to expose it. Brian Linn informed me they had found a steel pipe within the mark out and assumed that was the gas line they were trying to find not expecting to come across another gas line as they started to open up the hole with a mini excavator. Once the damaged 1" poly service line was fully controlled by the SDGE GERC crew we were able to confirm the gas line had been damaged with mechanized equipment. Within the location of the damage I could observe most gas locate marks had been destroyed. However, I did observe a gas locate mark out on the sidewalk which aligned with the e path of the damaged 1" poly service line. I set up my damage kit which confirmed the gas locate marks was within tolerance and took my damage photos. The SDGE locator also provided a pre-excavation photo taken when he completed the ticket which clearly showed the 1" poly service line had been marked accurately. It is clean homeowner Brian Linn failed to pothole by hand the marked 1" poly service line before excavating with mechanized equipment.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-01-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | TC CONSTRUCTION COMPANY INC | SANTEE | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our Sdge gas crew get the damage controlled. Spoke with Brian Havlu with TC Construction Company Inc. who stated that he was digging when he hit the gas. Brian did not know that the are had gas because this is a completely new development. TC Construction Company Inc has a valid USA ticket and had renewed it only without requesting remarks or mark outs. Observation of the damage was a 1? plastic stub hit with an excavator while trenching for drains. This has been an ongoing project for a new development and the ticket has been renewed several times and at the beginning the gas was not an issue and on December 19th the gas was energized.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | RAMOS POOL AND SAP CONSTRUCTION | LAKESIDE | CA | N | Y | No | No | No | No | No | No | No | Upon arrival our gas crew had the damage controlled. Spoke with FERNANDO RAMOS who is the owner of RAMOS POOL & SPA CONSTRUCTION who stated on July 23rd at 11:55am that his crew was trenching when they hit the gas. Observation of the damage was a 1/2? plastic gas service hit with a shovel while trenching for a new pool.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  | 0 |  | ADVANTAGE TEAM | LA JOLLA | CA | N | Y | No | No | No | No | No | No | No | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. Spoke with Oscar who works for ADVANTAGE TEAM who stated on July 17th at 1:40pm that he was digging to repair a water leak when he hit the gas. Observation of the damage was a 1/2? plastic gas service hit with a shovel while digging to find a water leak at the irrigation valves.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-09-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  | 0 |  | SHASTA LANDSCAPING | SAN MARCOS | CA | N | Y | No | No | No | No | No | No | No | On 9/3/25 at approximately 4:25PM I arrived at 13926 Boyden Way, San Diego. My first observation was that the EIR had the incorrect address. There was no damage at 14099 Angelite Way, San Diego. I observed a 1" plastic gas line with a small gash in the pipe. I initially spoke with Gerc Supervisor Michael Balsley. He provided information for Shasta Landscaping. He was provided this information from the superintendent with Shea Homes. Shasta landscaping was no longer onsite. I made contact with Gibran Alvarez. He is the superintendent for Shea Homes. He confirmed that Shea Homes hired Shasta Landscaping to preform drain work at this location. He also stated that they were digging with a shovel when the damage occurred and that there was no dig alert ticket for the work being done. I informed him to ensure his contractors have tickets before all excavations begin. His contact info is 619-430-0661 Giran.alvarez@sheahomes.com.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | REBECCA BENNETT | SAN DIEGO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | Yes | On-site I spoke to homeowner Rebecca Bennett who stated the 1/2" poly service line was damaged while excavating with hand-tools for a retaining wall. Rebecca Bennett was being helped by a worker when he struck the gas line with a shovel. Rebecca B. was unable to provide a valid dig alert ticket. I advised Rebecca B. to request a valid dig alert ticket before continuing with any excavation. Once the blowing gas line was controlled by the SDGE GERC crew we were able to confirm it had been damaged with hand-tools. Within the location of the damage I did not observe any delineations or marks placed for the work taking place, other than the marks recently placed for the SDGE GERC crew. I placed my damage kit and took my photos. It is clear homeowner Rebecca Bennett failed to request a valid dig alert ticket before excavating for a retaining wall.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | UNKNOWN | SAN DIEGO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | Yes | Contractor who installed fence post hit pipe and buried it with concrete and didn''t notify anybody. Unreported damage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2211 |  | 12 |  | HP COMMUNICATIONS INC | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with JOHN CARTER with HP COMMUNICATIONS INC who stated on October 15th at 12:00pm that his crew was digging when they hit a gas line. Observation of the damage was a 1/2? plastic gas service hit with a shovel while digging to put a hand hole in.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | A.M. ORTEGA | LAKESIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival, SDG&E Gas Emergency Response Crew (GERC) members had controlled the leak and made the repair to the damaged gas line. On-site, I spoke with Mike Miller, AM Ortega Supervisor. Mike stated a crew member was hand digging with a shovel to expose the 1/2? plastic gas service when the damage occurred. Mike stated the gas mark outs were accurate and provided a valid USA ticket (#CSB253040770). Mike stated all work being performed is for a gas main and service renewals for SDG&E. It was confirmed that the USA ticket was valid and the 1/2? plastic gas service was observed, by SDG&E GERC, to have been damaged with a shovel; per GERC, the damage was small enough to cut the line at the damage point and place a coupling to resolve the repair. The gas mark outs were within the zone of tolerance. Mike was highly encouraged to schedule an outreach for re-education on safe digging practices.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-02-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3033 |  |  | NA | HENKELS & MCCOY | SAN DIEGO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Met with Flavio Chavez with Henkels & McCoy onsite. Flavio stated that they were digging a trench for electrical conduit with an excavator when they hit the 2" plastic gas main. Flavio stated that they potholed the marks onsite and exposed a 2" steel gas main. He said they thought that was the gas main due to the location of the marks and that their site plans showed the gas being steel. They proceeded to continue to dig with the excavator and damaged the 2" plastic gas main, which was mis-marked by approximately 4 feet. I informed them that due to the marks being labeled as "PLA" they should have re-notified dig alert that they did not find what was marked onsite. The discrepancy of the material labeled and what was found merited a return trip from SDG&E to verify the location of the line. The contractor is required in CA government code 4216.4 to request the operator to provide additional information when the location of the subsurface installation cannot be determined. In my investigation, I determined that they did not find what was marked while potholing.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | BRIAN KINSEY | SAN DIEGO | CA | N | Y | Yes | No | No | No | No | No | No | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. Spoke with H/O KINSEY, BRIAN on August 19th at 11:30am who stated that he was his guys trenching near the gas meter when they hit the gas line. Observation of the damage was a 1/2? plastic gas service hit with a shovel while doing an electric panel upgrade. This USA ticket was closed originally due to no delineations onsite. The USA ticke was expired since 5/13/25. I advised Brian to call in a new USA ticket if he continues to dig.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-10-08 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | SAN DIEGO GAS AND ELECTRIC | SAN DIEGO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival, SDFire Department were on scene along with SDPD, who had shut of traffic in both directions, while SDG&E Gas Emergency Response Crew (GERC) members were working to control the gas leak. On-site, I spoke with Joe Gonsalves, On-duty supervisor of SDG&E. Joe stated a SDG&E gas crew member was potholing the 3/4? steel gas service with hand tools during a planned gas main extension/ service RFS and relocation job; where potholed, the depth was at approximately 45? deep. To further expose the gas service line within the existing trench, the crew member requested an excavator operator to loosen tough dirt approximately 30? away. While the operator of the excavator loosened the top layer of dirt, the 3/4? gas steel service was damaged at a depth of approximately 25.? It was confirmed that the USA ticket was valid (#CSB252330105) and marked within a timely manner. It was also observed that the mark out for the 3/4? gas steel service was within the zone of tolerance and damaged with an excavator. It was confirmed that the depth change of the 3/4? gas service ranged from 45? to 25? within approximately 30.?
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1581 |  | 3 |  | JOSE ALVAREZ | SAN DIEGO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | On-site I spoke to property owner Jose Alvarez who stated the gas line had been damaged while excavating to install footings for a wall. Jose Alvarez added they had seen the marks, but assumed the gas line would be deeper. Jose Alvarez was unable to provided a valid dig alert ticket, after completed a ticket search I found one for a contractor who was not on-site. I advised Jose Alvarez to stop work and request his own dig alert ticket for the proposed work. After the damaged gas line was controlled by the SDGE GERC crew it was confirmed the 1/2" poly line had been damaged with hand tools. I set up my damage kit and took my damage photos.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | LARS REMODELING AND DESIGN | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | On Thursday, 5/15/25 at approximately 5:45pm, I arrived onsite at 2343 Chicago st, San Diego. Upon my arrival the gas leak had already been controlled. The SDG&E gas crew was the only one onsite. I observed an area in the back yard of the property being demoed with a small portion of a 3/4" steel gas pipe with a hole in it. I used information from the gas supervisors report and some pictures from the locator who responded to the gas leak. I called and spoke with Paul Harte with Lars Remodeling & Design. He stated that they were demoing to pour new foundation when they jackhammered into the gas service. They were using a pointed bit on the jackhammer. He confirmed that they had no dig alert ticket. He agreed to call one in as soon as possible.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-10-18 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  | 0 |  | MARK CATRAMBONE | ESCONDIDO | CA | N | Y | No | No | No | No | No | No | No | On-site I spoke to Real Estate Agent Mark Catrambone who stated the gas stub had been damaged while him along hired workers were excavating with mechanized equipment to repair private sewer line. They are currently in process of renovating the home at the lot and were unable to provide a valid dig alert ticket. Mark Catrambone and his workers were advised to stop work and not continue until a valid dig alert ticket has been requested & completed. Once the damaged stub was controlled by the SDGE GERC crew it was confirmed it had been damaged with mechanized equipment. Within the location of the damage I could observe faded gas locate marks, which had been placed at some point for an expired dig alert ticket. I placed my damage pylon and took my damage photos. It is clear Mark Catrambone and workers were excavating without a valid dig alert ticket for sewer work.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-11-06 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3033 |  | 0 |  | BASILE CONSTRUCTION | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | Upon arrival, SD Fire Department were on scene while SDG&E Gas Emergency Response Crew (GERC) members were working to control the gas leak. On-site, I spoke with Alvaro Betancourt, Foreman of Basile Construction. Alvaro stated his crew was attempting to locate a sewer clean out, when the 1? plastic gas service was damaged with a probe. Alvaro stated he did not have a valid USA ticket and that he normally does not call in a USA for this type of work. It was observed that the 1? plastic gas service was damaged by a probing tool. Alvaro was advised to create a USA ticket, delineate the work area, and ensure to continue excavation after the legal start date.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | MURRAY LAMPERT DESIGN, BUILD & REMODEL COMPANY | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | On-site I spoke to Woodrow Coplin Project Manager with Murray Lampert Design, Build & Remodel Company who stated his workers were in the process of exposing the 1/2" poly service line when it was accidentally hit with hand tools. Mr. Coplin informed me that the gas line was being exposed to have it upgraded to a bigger size. Mr. Coplin was unable to provide a valid dig alert ticket and was advised to request their own ticket. Once the damaged 1/2" poly service line was controlled by the SDGE GERC crew it was confirmed that it had been damaged while pot holing with hand tools. Within the location of the damage I could observe that at some point there had been gas located marks, but they had been destroyed due to the work taking place. I completed a ticket search and found USA B252900207 completed on 10/22/2025. However, USA B252900207 had been completed for CARROLL ENGINEERING AND CONSTRUCTION who were not on-site and were not completing any work when the damage occurred. I set up my damage kit and took my damage photos. It is clear Murray Lampert Design, Build & Remodel company damaged a 1/2" poly service line while pot-holing without a valid dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-08-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10033 |  | 100 |  | S C VALLEY ENGINEERING INC | EL CAJON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with KURT WILLIAMS with S C VALLEY ENGINEERING INC who stated that the line was miss marked and he hit it. Observation of the damage was a 2? plastic main incased in a 4? steel line hit with an excavator while trenching for sewer for the City of San Diego. While observing the scene I came across the potholing done and the line found was a 6? steel line not the 4? steel gas line that was labeled. At this point when potholing for a 4? steel line that?s what needs to be found and this crew found a 6? steel line which they should have renotified. I let KURT WILLIAMS know about this situation which he stated that some other crew did the potholing not his.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | SCM CONSTRUCTION INC | ONTARIO | CA | N | Y | No | No | No | No | No | No | No | On Tuesday, 4/22/25 at approximately 1:30PM I met onsite with Tom Ponder who is a construction manager for Toll Brothers. He explained that he had hired SCM Construction Inc to excavate to install drains at the location of the damage. He provided me contact info for the foreman with SCM Construction Inc. Following this conversation I spoke in person with Ceasar Ortiz with SCM Construction. He was the one excavating at the time of the damage. He stated that they were operating a mini excavator to install drains when they hit the gas line. He confirmed that they did not have the gas lines marked through 811 and had assumed the line would be deeper. I then followed up with their foreman Abraham Lopez. I confirmed this info with him over the phone and discussed dig alert laws with him. I made sure he understood that he needs to have a valid USA ticket before excavating. Abraham Lopez was unable to provide a contractors license number and I was unable to find a valid license number researching online.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | ORION CONSTRUCTION | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Branden Love foreman with Orion Construction who stated the 1/2" poly service line had been damaged while excavating for new storm drain project. Mr. Love was not disputing markout and informed me the 1/2" poly service line had been already exposed when his worker accidentally damaged it. I advised Mr. Love to utilize his dig alert ticket and request for remarks since most marks had been destroyed. Once the blowing gas line was controlled by the SDGE GERC crew, it was confirmed it had been damaged with hand-tools. I did not observe any locate marks within the location of the damage, since they had been destroyed due to the work taking place. I place my damage pylon and took my damage photos. It is clear Orion Construction damaged a previously marked 1/2" poly service line while excavating with hand-tool for storm drain project.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | CITY OF SAN DIEGO | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival, SD Fire Department were on scene while SDG&E Gas Emergency Response Crew (GERC) members were working to control the gas leak. On-site, I spoke with Angelo Williams, Foreman at City of San Diego Water Department. Angelo stated he was excavating with an excavator when he was attempting to move dirt to repair a leaking water service line, when the 1? plastic gas service stub was damaged. Angelo provided a valid USA emergency ticket (#CSA252690132) for the emergency repair work being completed. Angelo stated the gas service line was mis-marked, as he was outside of the tolerance zone when utilizing the excavator. It was confirmed that the USA ticket was valid and marked within a timely manner. It was also observed that the mark out for the 1? gas service stub was labeled ?weak signal, pot & find.? However, it was found the gas mark out to be approximately 10? away from the active gas service stub. The 1? plastic gas service stub was observed to have been damaged with an excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | SE PIPELINE CONSTRUCTION | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | On-site I spoke to Robert Razo foreman with SE Pipeline Construction who stated the 1/2" poly inserted in steel service line had been damaged while trenching with mechanized equipment to install a new gas main. Robert R. informed me they had previously potholed for the line where the marks had been placed, but were not able to find it and assumed the line was deeper than the depth needed. Robert R. and his crew were not expecting to come across it 5'' away from where it was marked. I advised Robert R. to make sure all marked services are previously potholed and if not found to re-notify so we can come out and verify the mark-out. I also provided Robert Razo with my contact information so he can reach out with any issues or concerns. Once the damaged gas line was controlled by the SDGE Gerc crew we were able to confirm the 1/2" poly insert service line had been damaged with mechanized equipment. I set up my damage kit and took my damage photos.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | GEORGE PAZOS | SAN DIEGO | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | On-site I spoke to George Pazos homeowner who stated the 1/2" poly service line was damaged while trying to expose it with hand tools. George provided USA A250990493, which legal start day is not until 04/15/2025. I advised George to stop excavating and not resume until his ticket is valid and all utilities have responded. Once the damaged gas line was controlled by the SDGE GERC crew we were able to confirm it had been damaged with hand tools. Within the location of the damage I did not observe any delineations or completed utility mark out. I set up my damage kit and took my damage photos. It is clear homeowner George Pazos dug prior utility response and valid start date.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | ORTIZ CORPORATION | NATIONAL CITY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Upon arrival I spoke with Claudio Narez with Ortiz Corporation. Claudio stated that they dug into the gas line with an excavator while digging to install a water main. He stated that the gas line was not marked. Upon further inspection of the job site I confirmed the gas line was an unmarked and unmapped 3/4" steel stub. I notified supervision and QA to further investigate.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11182 |  | 137 |  | WEST COAST GENERAL GROUP INC | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department had the road secured while our SGDE gas crew get the damage controlled. Spoke with Casey Sullivan who is the superintendent for West Coast General Group Inc who stated on March 27th at 3:30pm that his crew was supposed to pothole by hand at another location then the one they were at. Observation of the damage was a 1? plastic gas service hit with a excavator while doing wet utilities work. The contractor was diggging within 10ft of a high pressure gas line without a standby.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-02-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | WEST COAST GENERAL GROUP INC | EL CAJON | CA | N | Y | Yes | Yes | No | Yes | No | No | Yes | On-site I spoke to Chris Castorena foreman with West Coast General Group Inc. who confirmed the 1" poly service line had been damaged while trenching with mechanized equipment. Chris C. and his crew were aware the gas line crossed their trench at this location since it had been recently installed to avoid conflict with the work taking place. However, Chris C. and his crew failed to pothole since they were the assumption the gas line had been placed a lot deeper than it actually was. Chris Castorena and his crew were advised to always pothole by hand all known existing utilities and to request remarks since this new 1" poly line had not been marked since it was not here when the last markout was requested. I placed my damage pylon and took my damage photos. It is clear West Coast General Group Inc. failed to request re-marks after knowing new gas lines had been installed and failed to pothole the 1" poly service line to determine its exact depth before crossing it with mechanized equipment.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | FLOW RIGHT | LAKESIDE | CA | N | Y | Yes | No | No | No | No | No | No | On 8/7/25 at approximately 12:45PM I arrived onsite at 3328 Harbor View Drive in San Diego. I initially spoke with Flow Right employee Nick Millan (619-342-6034). Nick stated that they had previously exposed the 1/2" plastic gas service and knew where it ran. They had backfilled and were exposing the line for a second time and accidentally damaged it with a shovel. I also spoke with Kenny Castro onsite who confirmed this information. He stated the marks were accurate and they knew the line was there and accidentally hit it. Kenny understood his ticket was expired as well and called in a new ticket while onsite.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SUFFOLK CONSTRUCTION | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | On-site I spoke to Brendan Mingle with Suffolk Construction who stated the 1/2" poly service line had been punctured by his workers while placing wooden stakes to extend concrete. Brendan Mingle was unable to provide a valid dig alert ticket, but believed one had been called at some point. I completed a ticket search and was only able to find USA A251980485, for Suffolk Construction. However,USA A251980485 is for a different address and the type of work does not match the work that was taking place when the 1/2" poly was punctured. I advised Mr. Mingle to make sure a valid dig alert ticket is requested for the work taking place. Once the damaged gas line was controlled by the SDGE GREC crew it was confirmed it had been punctured with a wooden stakes. I did not observe any gas locate marks other than the ones that had been freshly placed for the SDGE GERC crew. I placed my damage pylon and took my damage photos.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | AO REED & CO | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | On-site I spoke with A.O. Reed & Co workers, one of them named Kevin stated they were excavating with mechanized equipment to move the SDGE gas meter when the already exposed gas line was damaged. The workers claimed they were clearing dirt around the exposed line when the equipment pulled on the 1/2" poly gas line. A.O Reed & Co workers were unable to provide a valid dig alert ticket, they had assumed they didn''t have to since they were within private property. I informed the workers to always request a dig alert ticket even if they believe they are within private property. Within the location of the damage I could observe very faded yellow locate marks however, I was informed a private locate company had been hired to locate all existing utilities. I completed a ticket search and was unable to find a ticket to cover the location of the damage. I set up my damage kit and took my damage photos. It is clear A.O. Reed & Co failed to request a dig alert ticket before excavating to move the SDGE gas meter.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-10-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | NAVIA INC | SAN DIEGO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On-site I spoke to Jesus worker with NAVIA Inc who stated the 1" poly service line had been damaged while trenching for ADU foundation with mechanized equipment. Jesus added no gas locate marks had been placed at this location and they had already potholed and found the gas where the locator had placed marks. Jesus and his crew were not expecting to come across a second gas service line within their proposed work area. Once the SDGE GERC crew controlled the damaged gas line it was confirmed the 1" poly service line had been damaged with mechanized equipment. Within the location of the damage I did not observe any gas locate marks. I did observe gas locate marks 6'' away at another weld hole where a 1/2" poly service line had been pot and found by Jesus and his crew. However, the 1/2" poly was abandoned gas line which had been replaced by the damaged 1" poly service line. I contacted Johnny Pham via telephone and advised him to re-notify to have a SDGE locator revisit the site and mark the full path of the 1" poly service line within his work area. I set up my damage kit and took my damage photos. It is clear NAVIA Inc damaged a mis-marked 1" poly service while trenching with mechanized equipment.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MICHAEL CAIN | SAN DIEGO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | On-site I spoke to Micheal Cain who stated the 1/2" poly service line had been punctured while placing wooden stakes for a proposed retaining wall. Micheal Cain was unable to provide a valid dig alert ticket and was advised to request one, for which he agreed. USA B253050070 was created after our conversation. Once the damaged 1/2" poly service line was controlled by the SDGE GERC crew we were able to confirm it had been punctured with a wooden stake. Within the location of the damage I did not observe any delineations or mark out completed for the work taking place. I set up my damage kit and took my damage photos. It is clear Micheal Cain and workers were excavating and placing wooden stakes without a valid dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  | 0 |  | RIDGELLINE CONSTRUCTION | SANTEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor created a USA ticket to remove tree stump. Did not expose line by hand digging as required.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | GILBERT GUDINA | SAN DIEGO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | Met with Gilbert onsite. He stated he was digging to plant a garden in his front yard. He had potholed the gas in front of the meter and was digging down to expose the pipe again. He was trying to confirm the path of the pipe when he damaged it with a shovel. When I asked him about using dig alert he said he had intended to use the service but didn''t think of it until the day before he started to work and didn''t want to wait. He agreed now to wait until he calls in a ticket and gets positive response before continuing digging.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SPEARHEAD CONSTRUCTION | NATIONAL CITY | CA | N | Y | No | No | No | No | No | No | Yes | On Friday 5/30/25 at approximately 13:15 I met onsite with Octavio Escobar (619-577-9368). Octavio stated that he was using an excavator to dig for footings for a new ADU when he damaged the 1/2" plastic gas service. The gas service was also encased in a 3/4" steel casing. Octavio stated that he was doing the work for Spearhead Construction. He stated that he did know about dig alert but did not call for this job. He agreed onsite to call in a ticket before continuing any excavation. He also provided me with contact info for Marco Guzman who is in charge of this job for Spearhead Construction. CSLB #1099643
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-05-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | TC CONSTRUCTION COMPANY INC | SANTEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Irving Ayala foreman with TC Construction Company, Inc. who stated the marked 1" poly service line was damaged while trying to uncover with a shovel. Irving added the line had been previously potholed. However, his worker accidentally cut into it while trying to uncover the line once again. Once the damaged 1" poly service line was controlled by the SDGE GERC crew it was confirmed it had been damaged with hand tools. Within the location of the damage I could observe SDGE gas locate marks that aligned with the path of the damaged 1" poly service line. I set up my damage kit, confirmed the line was accurately marked and took my damage photos.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-09-16 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10292 |  | 72 |  | TC CONSTRUCTION COMPANY INC | SANTEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke with Jordan Marziale foreman with TC Construction who stated the gas line had been damaged while excavating with mechanized equipment. Mr. Marziale informed me they are currently excavating to complete sewer work and that the damaged gas line had been previously potholed. However, they documented the wrong depth and was not expecting to come across it at the current depth. Once the damaged gas line was controlled by the SDGE GERC crew it was discovered the 2" steel gas main had been hit and an unmapped 3/4" steel stub had been broken off of it as well. Within the location of the damage I could observe gas locate marks that aligned with the path of the damaged 2" steel gas line. I set up my damage kit, confirmed the gas locate marks were accurate and took my damage photos. It is clear TC Construction damaged and broke off a un-mapped stub of an accurately marked 2" steel gas main while excavating with mechanized equipment.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | TC CONSTRUCTION COMPANY INC | SANTEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Jordan Meyer foreman with TC Construction who stated the 3/4" steel service had been damaged while excavating with mechanized equipment for new water lines. Jordan Meyer informed me a different crew had potholed for the utilities and he assumed this line was at a different spot since he had not seen any marks at its location. I advised Jordan Meyer to request re-marks since the last time marks had been requested had been back on 03/24/2025. Once the damaged gas line was controlled by the SDGE GERC crew we were able to confirm the 3/4" steel gas service line had been pulled and cracked by mechanized equipment. Within the location of the damage, I was only able to find a very faded gas locate mark that aligned with the path of the damaged gas line, most marks had been destroyed due to the work taking place on-site. After I reviewed the pre-excavation photos attached by the SDGE locator I was able to confirm the damaged 3/4" steel service line had been accurately marked. I placed my damage kit and took my damage photos. It is clear TC Construction failed to maintain marks and damaged a 3/4" steel service line that had been previously marked accurately.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1581 |  | 3 |  | SC VALLEY ENGINEERING INC | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site Kurt Williams with S C Valley Engineering stated the 1/2" poly service line was damaged while trenching to install a sewer lateral. Kurt Williams added his crew had previously potholed the marked 1/2" poly however, they failed to maintain clearance. Upon arrival to the damage site, I could observe the SDGE GERC crew working on control for the damaged gas line. Once controlled we were able to confirm the 1/2" poly service line had been damaged while trenching with mechanized equipment. Within the location of the damage I could observe gas locate marks which aligned with the path of the damaged line in form of yellow paint and offsets. I set up my damage kit which confirmed the gas line was accurately marked and took my damage photos. It is clear S C Valley Engineering failed to protect and maintain clearance after the marked gas line had been pot and found.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-06-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8843 |  | 83 |  | SUKUT CONSTRUCTION | SANTA ANA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Upon arrival both the fire department and police had the road blocked off while our SDGE gas crew get the damage controlled. Spoke with Noah with Sukut Construction who stated on June 26th at 2:30pm that the gas was marked straight without a turn in direction when he hit it. Observation of the damage is a 2? plastic gas main hit with a excavator while digging for a new sewer line. *I am waiting on a photo of the mark out from our locator who happens to be on vacation.*
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | INTEGRITY CUSTOM CONSTRUCTION | LA MESA | CA | N | Y | No | No | No | No | No | No | No | Met onsite with Alistair and discussed the damage that occurred. He stated that he was digging for new utilities for an ADU and exposing the gas for an RFS. The 1/2" gas service was damaged with a mini excavator. He agreed the marks were accurate and he knew the gas was there. His dig alert ticket was expired and he was advised to call in a new ticket before continuing excavation. Contractor license #842647
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-12-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SUNSET CLIFFS | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | John Heger with Sunset Cliffs Plumbing explained to me that he hit the gas service line with a shovel while digging to cap sewer lines on the property. I asked him if anybody was injured and he said no. I then asked if he happened to have a dig-alert ticket and he said the homeowner had one and the area was marked. I explained to him that dig-alert law requires that each contractor must have their own USA ticket even if another party has one that covers the same work area and work type. He said he didn''t know that and will be sure to call in his own ticket in the future. I then spoke with the homeowners (husband and wife Leighland and Lee). I coached them on the same thing that I explained to Mr. Heger but I also made them aware that the ticket they had was expired and coached them on how to renew tickets in the future. The husband (Leigh) said that there was marks for the gas line but they were destroyed when the concrete was removed. He showed me a yellow dot he placed on a wall (see photo) so that he knew approximately where the gas line was after the marks were destroyed. Additionally, there were still marks visible east of the damage that are accurate and show the path of the line that was hit.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | STANLEY DEAN CONSTRUCTION | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | On-site I spoke to Trevor Martin with Stanley Dean Construction who stated that the 1/2" poly service line had been damaged while trying to expose it with hand tools. Stanley Dean Construction crew added the gas line had been partially exposed and they were not expecting it to be as shallow as it was. Mr. Martin and his workers agreed that at some point in time they had requested a dig alert ticket, but were unable to provide the ticket number. I completed a ticket search and was unable to find Stanley Dean Construction old ticket, I advised Trevor Martin to call in a valid ticket before continuing with the proposed work. Trevor Martin agreed and called one in (USA A2521100626). Once the damaged 1/2" poly service line was controlled by the SDGE emergency response crew it was confirmed it had been damaged with hand tools. Within the location of the damage I did not observe any delineations or gas locate marks. I placed my damage pylon and took my damage photos. It is clear Stanley Dean Construction damaged a 1/2" poly service line while excavating without a valid dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | MG CONSTRUCTION | SAN DIEGO | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | On-site I spoke to Jorge Cardenas and contacted Manuel Gonzalez with MG Construction, both confirmed the 1/2" poly service line had been damaged while grading with mechanized equipment for proposed ADU. Jorge Cardenas added they had come across what they had believed was an abandoned gas pipe and assumed the gas had been relocated. I informed both Jorge C. And Manuel Gonzalez they dug early on their ticket and advised to stop all work until the ticket has been marked/completed. Once the damaged gas line was controlled by the SDGE GERC crew it was confirmed it had been damaged with mechanized equipment. I did not observe any gas locate marks within the location of the damage. I placed my damage pylon and took my damage photos. It is clear MG Construction dug prior valid start date.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | PARDADISE BUILDERS | VISTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | On-site Homeowner Jesse Gaston stated he had Paradise Builders grading with mechanized equipment at his backyard when the gas line was struck. I briefly spoke with Kurt Enyedi with Paradise Builders who stated they were not expecting the gas line to be that shallow and felt like there was no need for a dig alert ticket since no major excavation was taking place at this time. I advised the Jesse and Kurt Enyedi to request a valid dig alert ticket before continuing with any excavation, they will also be contacting the planning department since this gas line is in conflict with the proposed ADU. USA A250290656 was requested after the conversation I had with Kurt Enyedi.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | ADEPT BUILDERS | BONITA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | At approximately 12:45 PM on Saturday 4/26/25, I spoke with Lloyd Dawson with Adept Builders regarding the gas damage that occurred. Lloyd stated that he and his crew were digging with shovels and a pick axe for a trench to install water and sewer. He said there were large rocks in the ground and that they were removing the rocks. While doing this he stated they used a pick axe to pry a rock upward from the ground but didn''t realize the gas line was on top of it. When pulling the rock upward they started to smell gas. This is when they notified SDG&E. Lloyd believes that during the process of prying the rock upward is when the damage to the gas pipe occurred. He said he had no issues with the marks and that they were accurate. He knew the gas was there but didn''t realize it would have been against a rock. Lloyd had a valid ticket for the work he was doing. CSLB #840094
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | J B GENERAL | OCEANSIDE | CA | N | Y | No | No | No | No | No | No | No | On-site I spoke to Jeremy Coyne with J B General who stated the 3/4" steel service line had been damaged while trenching with mechanized equipment for utilities for new construction. Mr. Coyne was unable to provide a valid dig alert ticket, he was advised to request a ticket before continuing with the proposed trenching. Mr. Coyne agreed and requested a ticket while still onsite (USA A252230631). Once the blowing 3/4" joint steel service line was controlled by the SDGE GERC crew, it was confirmed the line had been damaged with mechanized equipment. Within the location of the damage, I could observe some gas locate marks which had been previously placed for another contractor USA. However, most marks had been destroyed due to the work taking place at the site. I placed my damage pylon and took my damage photos. It is clear J B General failed to request a valid dig alert ticket before trenching to install utilities.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | SHIRLY PEREIRA | SAN DIEGO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | On Monday 4/21/25 at approximately 8:00PM I met onsite with homeowner Shirly Pereira. She explained to me that she had hired somebody to install a fence for her. During the excavation for the fence the gas service to her home was damaged. The damaged was caused by a pick axe. I discussed using 811 with Shirly and she had stated that she used 811. I researched and found that she had called dig alert on 7/16/24 for removal of bamboo. Her ticket had expired on 8/13/24. She had no dig alert ticket for the work being done at this time.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-08-22 | Third party excavation damage | Miscellaneous/Other | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  | 0 |  | NATON ENGINEERING INC | RAINBOW | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with Erick Dickens with NATON ENGINEERING INC. who stated that he was removing old soil when he hit a gas line. Observation of the damage was a 3/4? steel gas stub that was not mapped on any program we have. The 3/4? steel gas stub came off a 4? steel gas stub that was also not mapped coming from a valve on the sidewalk going into the parking lot of the building under construction.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | STEL BUILDERS | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled. Spoke with Brian Wood with Stel Builders who stated on March 7th at 12:20pm that his crew was digging for footings when the gas line was hit. Mr. Wood provided me with a USA dig alert ticket that was expired but also not the same address of this damage. I made sure Mr. Wood called in a new USA ticket and explained to him the 4216 dig laws before excavating. Observation of the damage was a 1/2? plastic gas service hit with a mini excavator while digging for footings for a retaining wall. ****Contractor''s License Detail for License # 877267****
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | TC CONSTRUCTION COMPANY INC | SANTEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Irving Ayala foreman for TC Construction Company Inc who stated the marked 1/2" poly service line had been damaged while excavating with mechanized equipment to install a new sewer lateral. Mr. Ayala informed me his guys missed the line and failed to pothole by hand before trenching with the backhoe. Once the SDGE GERC crew controlled the damaged 1/2" poly service line it was confirmed it had been damaged with mechanized equipment. Within the location of the damage I could observe faded locate gas marks that aligned with the path of the damaged 1/2" poly service line. I set up my damage kit, confirmed locate marks were within tolerance and took my damage photos. It is cleat TC Construction Company Inc failed to pothole for the marked 1/2" poly service line.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | 2ND GEN PLUMBING | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | Upon arrival the fire department had the roads secure while SDGE Gerc crew was getting the gas damage controlled. Spoke with Ivan Hernandez owner of 2nd gen plumbing via telephone to discuss what happened and he explained to me the his crew was digging to install sewer pipe and while doing so they hit the gas service for address 4789 Panorama Dr. the contractor did not have a dig alert ticket. The crew had damage a 1/2" poly gas service with a shovel for the neighbors house. I advised the crew to call in a dig alert ticket and they said they were no longer digging.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | MIKE BOLTON | SAN DIEGO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | Upon arrival, SDG&E Gas Emergency Response Crew (GERC) members were working to control the gas leak. On-site, I spoke with the building owner, Mike Bolton, who stated his handyman was excavating and to remove a cactus. Mike stated his handyman hit the 1/2? plastic gas service with a shovel. Mike stated he did not know about Dig Alert law and did not have a valid USA ticket. It was confirmed that there was no valid USA ticket. The 1/2? plastic gas service was observed to have been damaged with a shovel. Mike was advised to halt all excavation until a valid USA ticket is confirmed.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  | 0 |  | A.M. ORTEGA | LAKESIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival, SDG&E Gas Emergency Response Crew (GERC) members had controlled the leak and were working on the repair to the damaged gas line. On-site, I spoke with Mike Miller, AM Ortega Supervisor. Mike stated a crew member was hand digging with a shovel to expose the 1/2? plastic gas service when the damage occurred. Mike stated the gas mark outs were accurate and provided a valid USA ticket (#CSA252610475). Mike stated all work being performed is for a gas main and service renewals for SDG&E. It was confirmed that the USA ticket was valid and the 1/2? plastic gas service was observed to have been damaged with a shovel. The gas mark outs were within the zone of tolerance.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | PEDRO OLIVARES | SAN DIEGO | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | No | Yes | On site I spoke to worker Elias who stated the 1/2" poly service line had been damaged while trenching to upgrade electric. Elias informed me Pedro Olivares had requested a ticket, but had to take off and was currently not on site. I contacted Pedro Olivares who confirmed they had damaged the line while trenching and confirmed ticket number A251060506. Once the blowing gas line was controlled by the SDGE GERC crew we were able to confirm the line had been damaged with hand tools. Within the location of the damage I could observe gas locate marks in form of paint and flags which aligned with the path of the damaged line. I set up my damage kit which confirmed the damage gas line was within tolerance and took my damage photos. It is clear Pedro and Elias failed to pothole and damaged a marked 1/2" poly service line.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-09-15 | Operator excavation damage | Main | Steel | Augur | 8 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 200 |  | 0 |  | SAN DIEGO GAS AND ELECTRIC | ALPINE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew out for pole replacement. Auger bounced and made contact with gas line. Brushed line and made a minor dent. No release of gas. ATF smartsheet entry.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | AXCEL CONSTRUCTION INC | CHULA VISTA | CA | N | Y | No | No | No | No | No | No | No | Onsite I contacted Alex Celia foreman with Axcel Construction, Inc. who stated the 1/2" poly service line had been damaged while trenching to relocate the gas line with hand tools. Alex Celia was unable to provide a valid dig alert ticket. However, he claimed at some point they had requested a ticket, but was unaware they expired. I advised Alex to request a ticket and continue with excavation after it has been completed. After the damaged gas line was controlled by the SDGE GERC crew we could observe that it appeared the gas line had been damaged with mechanized equipment not hand tools. We could also see track marks on the dirt and teeth marks within the trench. I observed some SDGE gas locate flags that had been pulled out and no gas locate marks. I set up my damage kit and took my damage photos. It is clear Axcel Construction, Inc. failed to request a valid dig alert ticket before trenching to relocate the gas service line. (Contractor license number #1039206)
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | BURTECH PIPELINE | VISTA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On-site I spoke to Alberto Uranchez foreman with Burtech Pipeline who stated the 1/2" poly service line had been damaged while excavating with backhoe for sewer replacement. Alberto added they have been potholing all marked gas lines when crossing their proposed trench path. However they were not expecting to come across a gas line at this location since the marks had been placed at approx. 4'' away from their proposed trench. Once the damaged gas line was controlled by the SDGE GERC crew it was confirmed it had been damaged with mechanized equipment. Within the location of the damage I could observe the gas locate marks had been placed at approx.4'' away in a straight line aligning with the gas meter by the side of the home. I placed my damage pylon and took my damage photos.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | BURTECH PIPELINE | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Alberto Uranchez foreman with Burtech Pipeline who stated his crew was saw cutting asphalt when the damage occurred. Mr. Uranchez mentioned the blade on the saw was about 12" and the gas line had not been potholed yet, since they had to remove asphalt first before they pothole by hand. Once the damaged 1/2" poly inserted gas service line was controlled by the SDGE GERC crew it was confirmed it had been damaged with saw while saw cutting asphalt. Within the location of the damage I could observe gas locate marks that aligned with the path of the damaged 1/2" poly inserted gas service line. I set up my damage kit, which confirmed locate marks were accurate and took my damage photos. It is clear Burtech Pipe line damaged a marked 1/2" poly inserted gas service line while saw cutting asphalt for their sewer job.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2884 |  | 3 |  | ROMERO GENERAL CONSTRUCTION | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Aaron Quintero foreman with Romero General Construction who stated the marked 3/4" steel service line had been damaged while excavating with mechanized equipment for road/asphalt work. Aaron Q informed me the damaged gas line had already been found and exposed, but that the operator accidentally yanked it while excavating around it. Aaron Q added they have been potholing all marked gas lines due to that they have been very shallow, specifically between 5" to 10" deep. Once the damaged gas line was controlled by the SDGE GERC crew we were able to confirm it had been damaged with mechanized equipment. Most SDGE gas locate marks had been destroyed within the location of the damage. However, I still could see faded locate marks at each end of the road by the face of curb which aligned with the path of the damaged 3/4" steel service line. I set up my damage kit which determined the locate marks were accurate and took my damage photos. It is clear Romero General Construction damaged a marked 3/4" steel service line after it had been found and exposed with mechanized equipment.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-03-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3103 |  | 1 |  | SOLAR GAIN WEST | TUCSON | AZ | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled. Spoke with Juan Garcia with Solar Gain West who stated on March 14th at 4:20pm that he was trenching for the electrical for the solar when he hit the gas line. Observation of the damage was a 2? plastic gas service hit with a mini excavator while trenching for the electrical for the solar panels.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MULTI-COMM | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled. Spoke with property owner who provided me with GILBERTS information and stated that he hit the gas service with a shovel. Observation of the damage was a 1/2? plastic service hit with a shovel while digging to repaire a cable line. GILBERT who works for MULTI-COMM did not a USA dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3374 |  | 10 |  | BURTECH PIPELINE | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 8/7/25 at approximately 11:45AM I arrived onsite to 60th street in San Diego. The gas leak was located in front of 625 60th street but the damaged service was for address 620 60th street. Onsite I spoke with Burtech Pipeline foreman Alberto Uranchez. Alberto stated that his operator had been trenching with an excavator when he damaged the 3/4" gas service. He stated that they had previously potholed the gas service but the operator overlooked the markings and proceeded to dig with the excavator. There were visible yellow markings for the service in addition to a white G placed by Burtech Pipeline when they potholed the gas service. The marks onsite were accurate and the dig alert ticket was valid.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | BRIAN JENKINS | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled and repaired. Spoke with H/O JENKINS, BRIAN who stated on July 14th that he was digging and hit the gas line. Observation of the damage was a 1/2? plastic gas service hit with a shovel while trenching to move the gas meter.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5151 |  | 54 |  | VCI CONSTRUCTION LLC | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival, SD Fire Department were on scene while SDG&E Gas Emergency Response Crew (GERC) members were working to control the gas leak. On-site, I spoke with Kenneth White, Supervisor at VCI Construction, along with Eric Zinniger, Working Foreman of VCI Construction. Eric stated he was excavating with a mini-excavator when he was attempting to remove the top layer of concrete to expose the dirt, when the 1/2? plastic gas service was damaged. Kenneth provided a valid USA ticket (#CSA25232095) for the trenching work being completed for AT&T conduit installation. It was confirmed that the USA ticket was valid and that the SDG&E mark outs were accurate and within the zone of tolerance. The 1/2? plastic gas service was observed to have been damaged with a mini excavator and was approximately 6? below the top of concrete.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-11-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3033 |  | 0 |  | URBAN WEST CORPORATION | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | Upon arrival, SD Fire Department were on scene while SDG&E Gas Emergency Response Crew (GERC) members had controlled the leak and were working on the repair to the damaged gas line. On-site, I spoke with Scott Hamilton of Urban West Corporation. Scott stated his crew was attempting to excavate for drain pipes when the 2? plastic gas main was damaged with a mini excavator. Scott stated he did not have a valid USA ticket and that he normally does not call in a USA within the ongoing housing development. It was observed that the 2? plastic gas main was damaged by a mini excavator. Scott was educated on Dig Alert law, advised to create a USA ticket, delineate the work area, and ensure to continue excavation after the legal start date.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SC VALLEY ENGINEERING INC | SAN DIEGO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On-site I spoke with Kurt Williams foreman for S C Valley Engineering Inc who stated the 1/2" poly insert gas line had been accidentally damaged after it had been found and exposed by the excavator bucket. Kurt did mention the line had been mis-marked by the SDGE locator, but they had managed to find it without damaging it while trenching to install the new sewer main. I advised Kurt to utilize his active dig alert ticket and re-notify whenever he comes across unmarked utilities to have them identified and determine if they are active or abandoned. Once the line was controlled by the SDGE GERC crew it was clear it had been clearly fully exposed crossing their dug up trench and it had been damaged with mechanized equipment. Within the location of the damage most marks had been completely destroyed, but we were still able to see some faded locate marks that did not align with the path of the damaged gas line. I set up my damage kit and took my damage photos. It is clear S C Valley Engineering Inc failed to re-notify to have the exposed gas line identified once it was found and fully exposed.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-08-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | BURTECH PIPELINE | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Juan Vite foreman for Burtech Pipeline who stated the 1" poly service gas line had been damaged while trenching with mechanized equipment for new sewer lines. Mr. Vite and his crew informed me when they potholed they exposed a 3/4" steel line and assumed that was the marked active gas line. I advised Mr. Vite and his crew to always look for the size and material marked on the ground since, the locator had accurately labeled 1" poly gas for the address. Once the damaged 1" poly service line was fully controlled by the SDGE GERC crew it was confirmed it had been damaged with mechanized equipment. Within the location of the damage I could observe gas locate marks that aligned with the path of the damaged 1" poly gas line. I set up my damage kit and took my damage photos. It is clear Burtech Pipe line damaged an accurately marked 1" poly service line while trenching with mechanized equipment for new sewer lines.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-06-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | BURTECH PIPELINE | VISTA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On-site I spoke to Juan Vite foreman for Burtech Pipeline who stated the 1" poly service line had been damaged while trenching with mechanized equipment for new sewer main. Juan V added his crew have been potholing all marked gas crossings. However, they did not see any marks for this particular 1" poly service line. Once the damaged gas line was fully controlled by the SDGE GERC crew we were able to confirm it had been damaged with mechanized equipment. I did not observe any locate marks within the location of the damage. I placed my damage pylon and took my damage photos. I advised Juan Vite to request remarks since it appears most marks had been destroyed due to the work taking place. It is clear Burtech pipeline damaged a 1" poly service line while trenching with mechanized equipment for a new sewer main.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | STEVEN GIBSON | SAN DIEGO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | On-site I spoke to homeowner Steven Gibson who stated the gas line was damaged while excavating for a retaining wall with hand tools. Mr. Gibson was unable to provide a valid dig alert ticket. However, he requested one once he was advised to call one in before continuing with proposed work (USA A253420242). Once the damaged 1/2" poly service line was controlled by the SDGE GERC crew it was confirmed to have been damaged with hand tools. Within the location I did not observe any delineations or utility locate marks. I placed my damage kit and took my damage photos. It is clear homeowner Steven Gibson damaged the 1/2" poly service line while excavating with hand tools without a valid dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | STEVEN GIBSON | SAN DIEGO | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | Upon arrival, SD Fire Department were on scene while SDG&E Gas Emergency Response & Gas Maintenance Crews members were working to control the gas leak. On-site I spoke to homeowner Steven Gibson who stated he was excavating for a retaining wall with hand tools when the 1/2? plastic gas service was damaged. Steve stated he placed a vise-grip on the line to control the gas line. Steve provided his valid USA ticket (#CSA253420242). It was observed that the USA ticket was valid and the mark outs were accurate and within the zone of tolerance. The gas service was observed to have been damaged with a shovel, however it was cut in order to place a vise-grip for control. This is the second damage from the homeowner; the first occurring on 12/08/2025 (EIR# 120825-082717). Per SDG&E GERC, the homeowner was educated on 12/08/2025 about safety and broken gas lines.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | GOLD STANDARD ELECTRIC | RAMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I met and spoke to Carlos Carvajal project manager with Build Pros Construction who stated the 1/2" poly service line had been damaged by his subcontractor Gold Standard Electric, while trenching to upgrade electric with hand-tools. I contacted Kevin with Gold Standard Electric who confirmed his USA dig alert ticket number (A251690410) and that his crew had been on-site trenching when the damage occurred. Kevin had been told by his crew that they had not seen any gas locate marks at the location of the damage and were not expecting to come across the gas line. Once the damaged 1/2" poly service line had been controlled by the SDGE GERC crew we were able to confirm the line had been damaged with hand-tools. Within the location of the damage, I could observe some yellow gas locate flags which aligned with the path of the damaged line. After reviewing the pre-excavation photos attached to dig alert ticket A251690410 and by observations on-site it was clear the 1/2" poly service line had been accurately marked. I set up my damage kit and took my damage photos. It is clear Gold Standard Electric failed to pothole and damaged an accurately marked 1/2" poly service line with hand-tools.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ARMANDO RAMIREZ | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Armando Ramirez who stated the 1/2" poly service line had been damaged while trenching with hand tools to upgrade electric. Armando confirmed he had requested a dig alert and believed he had been staying clear from the locate marks. However, he assumed he would come across sand or warning mesh before the gas line would appear. I advised Armando to always pothole for any marked utility when coming close to it or its tolerance zone. Once the blowing gas line was controlled it was confirmed the line had been damaged with hand tools while trenching. Within the location of the damage I could observe gas locate marks inform of flags and yellow paint. I placed my damage kit, determined the marks were within tolerance and took my damage photos. It is clear Armando Ramirez failed to pothole the marked gas line to determine its exact depth and location.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | NEW CALIFORNIOA RESTORATION INC | CHULA VISTA | CA | N | Y | No | No | No | No | No | No | No | On-site I contacted Rogelio Diaz who confirmed the 1/2" poly service line had been damaged by his crew while excavating to install a new sewer lateral with mechanized equipment. Rogelio was under the impression that they had a dig alert ticket, but was unable to provide a ticket number. I advised Rogelio Diaz to stop work and not continue until a dig alert ticket was requested and completed. After our conversation Rogelio requested dig alert ticket A250790557. Once the SDGE GERC crew was able to control the blowing gas line we were able to confirm the 1/2" poly service line had been damaged with mechanized equipment. Within the location of the damage I did not observe locate marks or delineations for New California Restoration Inc. I placed my damage pylon and took my damage photos. It is clear New California Restoration failed to request a valid dig alert ticket before excavating to install a new sewer lateral.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-07-24 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3383 |  | 5 |  | VCI CONSTRUCTION LLC | SAN MARCOS | CA | N | Y | No | No | No | No | No | No | No | On July 24, 2025, an SDG&E utility locator discovered a damaged 2-inch poly gas main during a dig alert mark-out. The gas main had been wrapped in black tape and concealed under wooden boards, with no contractors present at the time. Investigation revealed multiple contractors had worked at the site on July 2, 2025, including VCI Construction LLC and AT&T for phone line repairs, as well as Raoz General Engineering for gas utility work. All parties denied responsibility for the damage. Evidence indicated the gas main was properly marked for excavation, and the damage was caused by hand tools. The black tape used to wrap the gas main matched tape on repaired phone lines above the damaged pipe, suggesting a link to prior phone line work. SDG&E GERC crew secured the site, and damage documentation was completed
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3103 |  | 1 |  | ROCK ELECTRIC | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival both the fire department and police had the parking lot secured while our SDGE gas crew get the damage controlled. Spoke with Mike Hammersley who is with Rock Electric who stated on May 8th at 1pm that his crew was digging for electrical when they hit the gas. Mike assumed the gas was out of the way. Observation of the damage was a 2? plastic gas service hit with a excavator while digging for electric. The USA ticket for this job has been expired since 1/08/2025.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-05-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | HORTON ELECTRIC | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | On Tuesday 5/20/25 at approximately 15:30, I met onsite with Tom Horton with Horton Electric LLC. Tom stated that he had laborers digging a trench for electrical conduit. During this excavation they damaged the 1" gas service with a digging bar. He stated that they had known the gas line was there but hit it by accident while continuing their trenching. Tom provided me with a dig alert ticket that expired on 3/19/25. I explained to him that the tickets expire after 28 days and that he needs to call in a new ticket and wait for the legal start time to continue excavation. CSLB#1048842
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-01-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | CACY ELECTRIC | EL CAJON | CA | N | Y | No | No | No | No | No | No | No | Upon arrival, SDG&E gas crew had controlled the gas leak. Met with PCL construction superintendent Ryan Nowierski. Ryan stated that they hired Cacy Electric to trench and install electric conduit. He provided me with contact information for Frank Ramirez with Cacy Electric. I called and spoke with Frank who confirmed that they were digging with a mini excavator to install electric conduit when they damaged the gas service. There was no dig alert ticket for the work being done. I advised Frank to call in a ticket before continuing work and he agreed. His new ticket number is A250131014. *CSLB License #780158*
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-03-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | COAST LANDSCAPING | VISTA | CA | N | Y | Yes | Yes | Yes | No | No | No | Yes | Met onsite with Kiernan Short and Holland Mason with Coast Landscaping. Kiernan stated that his guys were performing landscape work and attempted to pothole the gas line before excavating with mechanized equipment. The line they potholed though was not gas. They exposed a larger pipe at a deeper depth and assumed it was the gas. They then proceeded to dig with a mini excavator and dug into the gas line. I also found that their ticket did not receive positive response for the area they were digging. I advised them to make sure they delineate the work area clearly, receive positive response, and observe marks with size and material to know exactly what they are looking for when potholing.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | CITY OF SAN DIEGO | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled. Spoke with DANIEL DUARTE with the CITY OF SAN DIEGO who stated on July 7th at 11:55am that he knew the gas was there but still managed to hit it. Daniel did not dispute any marks and was aware of the gas. Observation of the damage was 1/2? plastic gas service hit with a digging bar while doing water work.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | CITY OF SAN DIEGO | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival our SDGE gas crew had the damage controlled. Spoke with Daniel Duarte with city of San Diego who stated on April 28th at 12:15pm that his crew was trenching for the new water in the neighborhood when they hit the gas. Observation of the damage was a 1/2? plastic gas service hit with an excavator while trenching for a new water line.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-09-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | BURTECH PIPELINE | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I met and spoke to Alberto Uranchez foreman with Burtech Pipeline who stated the 1" poly gas line had been damaged while trenching with mechanized equipment to install new sewer main. Mr. Uranchez informed me he failed to see the marks for this particular line due to all the equipment and dirt at the job site. I advised Mr. Uranchez to request for remarks to help refresh the marks and make them more visible since most were already very faded. Once the damaged 1" poly was controlled by the SDGE GERC crew it was confirmed it had been damaged with mechanized equipment. Within the location of the damage I could observe faded locate marks that aligned with the path of the damaged 1" poly service line. I set up my damage kit, which confirmed locate marks were accurate and took my damage photos. It is clear Burtech Pipe line failed to pothole an accurately marked SDGE gas line.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-05-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | HENKELS & MCCOY | SAN DIEGO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Onsite Dale Kluge foreman for Henkels & McCoy informed SDGE crews that the 1/2" poly service line had been damaged while trenching with mechanized equipment to install electric. They added they were not aware this line crossed at this locations since they did not see marks for this 1" poly service line. Dale Kluge provided USA A242950198. After the SDGE GERC crew controlled the 1" poly service line we confirmed the line had been damaged with mechanized equipment. Within the location of the damage I did not observer locate marks other than marks for the now abandoned 1/2" poly line that used to service the affected homes. After reviewing USA A242950198, it is clear Henkels & McCoy have been only updating the ticket since the last markout was completed, which was back on 10/26/2024. No request for remarks have been requested since. This new 1" poly service line was just recently placed on March 2025, which explains why it was not marked for Henkels & McCoy.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2025-02-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11083 |  | 115 |  | SCHILLING CORP | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with James Mcdonald with Schilling Corp. who stated that he had the gas line exposed when he was using the excavator next to the gas line while he hit the tap and test stub coming off the 2? plastic main. James also stated that the work area was marked out with whiskers and that they were accurate.The work being done at this work site was installing dry utilities. Observation of the damage was a 2? plastic gas main hit with an excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCO | 2025-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | VARGAS ELECTRIC | ALHAMBRA | CA | N | Y | No | No | No | No | No | No | Yes | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled. Spoke with Hector Ochoa with Vargas Electric who stated on June 25th at 3:30pm that he was trenching and expected the gas to be at the same depth of were he potholed further down and expected to find mesh above the gas line before hitting it. Observation of the damage was a 1? plastic gas service hit with a mini excavator while trenching for new utilities.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2025-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | NATON ENGINEERING INC | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 6/24/25 at approximately 10:40AM I arrived onsite of the gas damage. Shortly after my arrival I made contact with Eric Dickens. Eric is a foreman for Naton Engineering Inc. Eric stated that they were using a skid steer to grade an area of the lot and exposed a portion of the gas pipe. He was unaware that it was a gas pipe and stated they he thought it was just trash. He proceeded to bring over an excavator and dig out the area. When digging with the excavator he pulled out the gas line causing the damage. When I asked him if he knew the gas line was there, he stated that he assumed it was cut and capped at property line. At this time I pointed out that the gas line had been marked with an offset marking that indicated the line ran 27 feet into the lot from the face of curb. The damage occurred at 21 feet from this mark putting it within the distance of the marking. I showed him pre excavation photos as the marks were faded. Naton Engineering had a valid ticket but also failed to pothole and call for remarks once marks were faded. I explained the importance of observing all marks, potholing before digging, and calling in for remarks when marks are faded.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2025-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | SHEDLEY MASONRY | CARLSBAD | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with MAURICIO LOPEZ with SHEDLEY MASONRY who stated on October 23rd at 9:30am that he called in a USA dig alert ticket yesterday October 22nd. I let Mauricio know that his USA ticket is not valid for two business days not including the day he called it in. Observation of the damage was a 1/2? plastic gas service hit with a shovel while trenching for a panel upgrade.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2025-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1651 |  | 4 |  | VCI CONSTRUCTION LLC | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with ROGELIO MONTUFAR with VCI CONSTRUCTION who stated on October 29th at 11:10am that his crew had potholed the gas and it was at 39? top of pipe and managed to hit it still. Observation of the damage is a 1/2? plastic gas service hit at 32? with a rock wheel while trenching for AT&T. VCI did pothole the line and it was at 39? but were they crossed the gas it was a little over 2? from the pothole. The gas came up and they managed to hit it. This is a good example to always pothole the utility at the location you will actually cross it.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2025-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2281 |  | 13 |  | GENERAL 2 CONSTRUCTORS, INC. | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | No | No | No | Yes | Upon arrival both the fire department and police had the shopping center secured while our SDGE gas crew get the damage controlled. Spoke with EDDIE GOMEZ with GENERAL 2 CONSTRUCTORS, INC. who stated on September 24th at 6:20pm that he was digging to put a footing when he hit the gas. EDDIE also stated that he didn?t see any mark outs for gas. Observation of the damage was a 1/2? plastic gas service that was hit with an auger while digging to put footings for a shade post. The USA ticket for this job was expired so I had EDDIE call in a new USA ticket to get mark outs. The USA ticket was closed due to no access. A email was sent to the contractor to get access because it was a daycare. The ticket expired and the area was not marked and the contractor decided to dig anyways.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2025-09-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | DWELL WEST HOMES | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. When I arrived the contractors were gone. I found a phone number for the property owner that happens to be a investment company. Spoke with Deana and she was aware of the damage and made the call when the gas was hit. Observation of the damage was a 1? plastic gas service hit with a shovel while trenching for sewer. They did not have a USA ticket.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | BLUE PALS PLUMBING | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with Francisco Gomez with Blue Pals Plumbing who stated on September 15th at 3:40pm that he was trenching for sewer when he hit the gas line. Observation of the damage was a 1/2? plastic service hit with a mini excavator while trenching for sewer. Blue Pals made the assumption that the gas line would be deeper.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2025-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1651 |  | 4 |  | NORTH COUNTY FENCE AND FABRICATION | FALLBROOK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with Alexis Pineda with NORTH COUNTY FENCE & FABRICATION and he state on October 31 at 2:00pm that he was trenching when he managed to hit the gas line. Observation of the damage was a 1/2? plastic gas service hit with a shovel while trenching for solar.
San Diego Gas and Electric | N | SAN DIEGO | SAN YSIDRO | 2025-02-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3173 |  | 2 |  | MAC GC ELECTRIC INC | SAN DIEGO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | On-site Wade Blackmon with MAC GC-Electric, Inc. confirmed the 2" poly stub had been damaged while excavating with mechanized equipment. Wade Blackmon and crew were unable to provide a valid dig alert ticket. I advised Wade B. And his crew to call in a dig alert ticket before continuing with their excavation. Within the location of the damage I was able to uncover gas locate marks for the damaged 2" poly stub, which had been placed for a different contractor who was not onsite. It is clear MAC GC-Electric failed to request a valid dig alert ticket before excavating with mechanized equipment.
San Diego Gas and Electric | N | SAN DIEGO | SAN YSIDRO | 2025-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JOSEPH CABALLEROS | SAN YSIDRO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | I spoke with both the tenant of the property and the workers whom the property owner hired to perform the drain work for the tenant. The tenant said that property owner (Joseph Caballeros) uses the workers whom hit the gas line for all of his properties. I educated her on 811 and gave her an 811 brochure. I also spoke with one of the workers who explained to me that they hit the gas line with a shovel while digging to do some drain work. I explained to them the importance of 811 and informed them that I had the tenant submit a ticket online their behalf. They''ve worker explained that they are done digging since they have the drain line exposed already.
San Diego Gas and Electric | N | SAN DIEGO | SANTEE | 2025-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JJ PLUMBING | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | On-site Jose with JJ Plumbing confirmed the 1/2" poly service line had been damaged while trenching with hand tools. Jose with JJ Plumbing was unable to provide a valid dig alert ticket, he was asked to stop all excavation and request a valid dig alert before continuing with trenching. Within the location of the damage I did not observe any SDGE gas locate marks or delineations. It is clear JJ Plumbing failed to request a valid dig alert before trenching to install utilities.
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2025-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | BARDIA MOAYEDI | SOLANA BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department and our sdge gas crew were gone. I met with property owner BARDIA MOAYEDI who stated on September 13th at 2:20pm that his crew was trenching for drains/sewer when they managed to hit the gas. Observation of the damage was a 1/2? plastic service hit with a shovel while trenching for drains/sewer. The marks are good and I explained to the homeowner the tolerance zone which he understood.
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2025-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  | 0 |  | J B GENERAL | OCEANSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival our SDGE gas crew had the damage controlled and were making repairs. Spoke with JEREMY COYNE with J B GENERAL who stated on October 15th at 4:30pm that he was removing a tree stump when he hit the gas line. JEREMY also stated that he didn?t expect the gas to be that shallow. Observation of the damage is a 1? plastic gas service hit with a mini excavator while removing a tree stump in the back yard. The gas service was never potholed and the contractor was using mechanized equipment instead of hand tools to expose the gas service. The contractor had no issues with the mark out and assumed the gas would be deeper.
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2025-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | M&S PLUMBING HEATING AND AIR | SAN DIEGO | CA | N | Y | No | No | No | No | No | No | No | Upon arrival the crew had the damage controlled and repaired. Spoke with Tony Martinez who is the owner of M&S PLUMBING HEATING AND AIR who stated that he was putting in thd drains when he managed to hit the gas. Tony said he barely cut the gas. Observation of the damage was a 1/2? plastic gas service hit with a shovel while trenching for new drains. The contractor did not have a USA ticket and the digging was already done when I arrived on scene.
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | TRAVIS JONES | ENCINITAS | CA | N | Y | Yes | No | No | No | No | No | No | On-site I spoke to Travis Jones with Talbot Construction who stated the 1" poly service line had been damaged while trenching with mechanized equipment to install new utilities for the new home. Travis Jones added they had seen the gas locate marks, but were coming across a lot of tree roots and tried removing a few with the excavator when they caught the gas line. Travis Jones confirmed his ticket was USA A251610256, which had expired 07/08/2025. I advised Travis Jones and his crew to request a new valid ticket before continuing with the proposed trenching, which he agreed and did. Once the damaged 1" poly service line was controlled by the SDGE GERC crew we were able to confirm it had been damaged with mechanized equipment. Within the location of the damage I could observe gas locate marks which aligned with the path of the damaged line. I set up my damage kit, confirmed locate marks at site were accurate and took my damage photos. It is clear Talbot Construction failed to keep their ticket active and did not pothole the marked 1" poly service line.
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2025-05-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | ALI JASIM | SPRING VALLEY | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | On-site I spoke to homeowner Ali Jasim who stated the 1" poly service line had been damaged while trenching with mechanized equipment to upgrade his electric. Ali Jasim provided USA A251270611, which legal start date is on 05/09/2025 @ 17:01. I informed Ali Jasim he needed to stop excavating and not resume until all utilities have responded to his ticket. After the SDGE GERC crew controlled the damaged gas line we confirmed the 1" poly service line had been damaged with mechanized equipment. Within the location I did not observe any delineations or locate marks. It is clear Ali Jasim dug prior valid start date/time and damaged a 1" poly service line which had not been marked yet.
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2025-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | VINCE GARCIA | SPRING VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled. Spoke with Vince Garcia who is the property owner who stated on March 22nd at 2:50pm that he was digging to follow his existing electric line to the house to see what the length was for a future panel upgrade. Observation of the damage was a 1/2? plastic gas service that was hit with a shovel while trenching for a panel upgrade.
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2025-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1581 |  | 3 |  | TEAN MERINO LANDSCAPE | ESCONDIDO | CA | N | Y | No | No | No | No | No | No | No | On-site I spoke to Enrique Merino Carrasco with Team Merino Landscape who stated the 1/2" poly had been damaged while excavating to place a retaining wall with mechanized equipment. Enrique and his crew added they were unaware gas crossed the work area. They also informed me they were completing the work under Apelinc Landscape Services who had hired them to work at this location. Enrique agreed to request a dig alert ticket before continuing with the proposed work and requested USA B252960944. Once the damaged gas line was controlled by the SDGE GERC crew it was confirmed it had been damaged with mechanized equipment. I did not observe delineations or a markout completed for Team Merino. It is clear Team Merino damaged the 1/2" poly service line while excavating without a valid dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2025-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | BLUE PACIFIC ENGINEERING | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival to damage location I noticed the fire department was there also I noticed the construction crew as well as our Gerc crew. I found out who the foreman was and i went over to talk to his Miguel and he was the guy on the excavator he also worked for blue Pacific Engineering I asked him what happened. He told me that while they were Potholing the gas service with the excavator he started to smell the gas in the air and he said that was around 1145am. The first notice was until 12:29pm. After the Gerc crew stop the leak the gas supervisor said that it was clearly damaged by the excavation machine.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2025-08-26 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 5845 |  | 0 |  | SELECT ELECTRIC INC | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Select Electric was boring across the street to install a new electric conduit for street lights for the City of Vista Fire Station. When the bore made its way to the end location the crew smelled gas. Therefore a call was made to SDGE that gas odor was in the air. SDGE crew showed up to investigate the leak and started with test holes where the bore machine crossed our 3" gas main. While SDGE was hammering in the pin bar they struck the gas main which then caused the B&B. The gas was controlled by the pin bar in place until our SDGE gas crews can get a bypass set up. When speaking to Jesus Godinez with Select Electric they let me know that they might have struck the gas when they bored across it earlier that day. After the damage was controlled and dug up you can see significant damage that the bore machine did to the 3" gas main. The bore did not cause the leak but it was damaged enough that it needed to be repaired. I educated Select Electric on the importance of potholing exactly where the bore machine will cross our gas for future jobs to make sure they have proper clearance from any utilities and to prevent damages.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2025-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | HECTOR ALVERAZ | VISTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | BNB 1/2 inch poly service hit with shovel.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2025-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3103 |  | 1 |  | JESSIE''S ELECTRIC | OCEANSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival the fire department had the road secured while our SDGE gas crew get the damage controlled. Spoke with JESSE TELLEZ with JESSE''S ELECTRIC who stated on August 6th at 3:20pm that his crew was digging a trench for new electrical. Observation of the damage was a 2? plastic service hit with a shovel while trenching for a electrical panel upgrade. The maps show that its a 1/2? plastic service but its a 2? plastic service.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2025-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | NEXT GENERATION SEPTIC SERVICE INC | SAN MARCOS | CA | N | Y | No | No | No | No | No | No | No | On Monday, 5/12/25 at approximately 9 AM, I met onsite with Dominic Garcia with Next Generation Septic Service. Dominic stated that him and is crew were digging to repair a septic system for the homeowner. Dominic stated that he had done work on this property before and knew where the gas line was. He had potholed and exposed a 1/2" poly gas line in his work area. At this point he continued to dig with a mini excavator and hit the 1" poly gas line. He did not realize that a new gas line had been installed. Dominic did not have a dig alert ticket for the work being done. I advised him to stop all excavation until his dig alert ticket is legal and all member have provided positive response. I also explained that if he had called a ticket, that SDG&E would have marked the active line and placed a marking to notify him that there is abandoned gas in the work area as well. He stated he understood and agreed to call in a ticket. CSLB# 1115212
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2025-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | HIDDEN VALLEY PLUMBING | ESCONDIDO | CA | N | Y | No | No | No | No | No | No | No | Upon arrival the fire department was gone and our SDGE gas crew had the damage controlled and repaired. Spoke with Benito Fuentes with Hidden Valey Plumbing on February 25th at 5:20pm who stated that his crew was using a shovel to dig for a broken water line when he managed to hit the gas. Benito did not have a USA ticket. Observation of the damage was a 1/2? plastic gas service hit with a shovel while doing plumbing work to stop a water leak.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2025-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  | 0 |  | KHOY DO | VISTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | On 9/2/25 at approximately 430PM I arrived onsite at 421 W Bobier Drive, Vista. Upon arrival I made contact with Khoy Do who introduced himself as the owner for the property. He stated that he and the other 2 men onsite were digging to remove roots. Khoy did not have a dig alert ticket. When I asked him if he was familiar with dig alert he stated that he was. He said he had not expected to hit the gas at the depth they were digging. Once the gas leak was controlled I observed the jobsite with the SDGE GERC crew. They were unable to expose the damage due to the gas line being completely onsite of large roots. It appeared the roots had been cut into with a sawzall. Khoy still stated it was a shovel that caused the damage, but our observations indicated it was from the sawzall. I measured the depth of the gas near the damage at 25 inches deep with measuring tape. Khoy confirmed that he would call in a dig alert ticket before continuing any more work.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2025-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | WEST COAST UNDERGROUND | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | David Lorberter with West Coast Underground stated that they were digging to expose gas to have it removed and install a new service. They accidentally hit the service with a shovel and caused the damage. They knew the gas was there and the marks were accurate.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MATT ATTEBERRY | VISTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | No | No | Upon arrival both the fire department and police had the road secured while our SDGE gas crew get the damage controlled. Spoke with H/O ATTEBERRY, MATT who stated on September 8th at 1:00pm that he was removing some roots when he managed to hit the gas. Observation of the damage was a 1/2? plastic gas service hit with a shovel while doing landscaping work. The homeowner did not know the law.
Southern California Gas Company | N | FRESNO | CARUTHERS | 2025-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HARTZELL GENERAL ENGINEERING | CAYUCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to install sewer, hit & damaged a 3/4 steel service with a track hoe. Crew pinned off service tee & replaced the service.
Southern California Gas Company | N | FRESNO | CARUTHERS | 2025-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1.25 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2819 |  |  | NA | ARCHER CIVIL CONSTRUCTION | TULARE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor excavating for new culvert, hit & ruptured a 1 1/4 steel service. Service history & GIS did not have any records of service location.
Southern California Gas Company | N | FRESNO | DEL REY | 2025-08-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25001 |  |  | NA | RISE UTILITY CONSTRUCTION | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating with a backhoe, lost track of company marks & hit a 2 plastic main. Excavator was counselled on the importance of maintaining marks and using hand tools only when within the tolerance zone of marked company facilities.
Southern California Gas Company | N | FRESNO | DEL REY | 2025-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | JESUS ANAYA | DEL REY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant excavating with a posthole digger to install fence post, hit & ruptured a 1/2 plastic service. Occupant was counselled by LCT on importance of calling 811 for free 2 or more days prior to excavating to get utilities marked.
Southern California Gas Company | N | FRESNO | FRESNO | 2025-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 380 | 380 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TED RAVEN | FRESNO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged hp service while digging grave for deceased animal with backhoe. No usa. Pics sent to @claims photos.
Southern California Gas Company | N | FRESNO | KINGSBURG | 2025-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOHN JOBE | KINGSBURG | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged 1/2 plastic service while digging to install deep water stake. Customer was counselled by LCT on importance of calling 811 two or more days prior to excavating.
Southern California Gas Company | N | FRESNO | KINGSBURG | 2025-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | FERNANDO MARROQUIN | KINGSBURG | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating for fence project, occupant Fernando Marroquin damaged a 1/2 plastic service line, SCG crew made permanent repairs. Mr. Marroquin was educated about USA law.
Southern California Gas Company | N | FRESNO | KINGSBURG | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | K&E ELECTRIC | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to install electric conduit, hit & damaged a 1/2 plastic service.
Southern California Gas Company | N | FRESNO | PARLIER | 2025-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1598 |  | 2 |  | CAMARILLO DRILLING | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck a 1/2 inch plastic service while potholing with hydro-vac equipment. Contractor was advised to use caution when working/excavating within the tolerance zone of any marked company facilities.
Southern California Gas Company | N | FRESNO | PARLIER | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | TRIPLE J DRILLING | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to install telecommunications conduit, hit & damaged a 1/2 plastic service. Excavator was reminded to use caution & expose company facilities when crossing.
Southern California Gas Company | N | FRESNO | PARLIER | 2025-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | CROWN COMMUNICATION | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to expose company facilities, hit & ruptured a marked plastic service.
Southern California Gas Company | N | FRESNO | PARLIER | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | FD ELECTRIC | LYNWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor struck an unlocatable, unmarked plastic branch. ETD instructed to submit MUR to accurately reflect location of branch service.
Southern California Gas Company | N | FRESNO | PARLIER | 2025-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Vacuum Equipment with no Agreement | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3550 |  | 4 |  | UNWIRED BROADBAND | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1/2 plastic service while excavating with hydro-vac to locate company facilities.
Southern California Gas Company | N | FRESNO | PARLIER | 2025-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | UNWIRED BROADBAND | WASCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1/2 plastic service while attempting to locate. Contractor was advised to call in damage when it occurs & not to attempt to repair.
Southern California Gas Company | N | FRESNO | REEDLEY | 2025-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DCW CONTRACTORS | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor probing for company facilities, hit & ruptured a 1/2 plastic service. Excavator was advisor to be more cautious when exposing plastic company facilities.
Southern California Gas Company | N | FRESNO | REEDLEY | 2025-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 400 | 160 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2599 |  | 1 |  | GROUND BREAKER CONSTRUCTION | LEBEC | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor did not notify SCG regarding the need for HP standby. 3/4 steel service was hit while excavating to replace sewer main. Contractor was reminded to schedule HP standby prior to excavating with 10'' of marked HP company facilities.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2025-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JESUS VASQUEZ | BRAWLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged a 1/2 inch plastic gas service. They did not notify USA and are fully responsible.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2025-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 41 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 2179 |  | 1 |  | ROVE CONSTRUCTION | EL CENTRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3/4 Steel service damaged by 3rd party contractor while excavating for curb and gutter project in the City of Calexico. Service was yanked and kinked but no leak was found. Replaced service at damage address.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2025-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | MANUEL ALDERETE | CALEXICO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The occupant- HIT LINE WITH SHOVEL WHILE PERFORMING SEWER WORK
Southern California Gas Company | N | IMPERIAL | CALIPATRIA | 2025-08-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ROVE | EL CENTRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor damaged gas facility because they did not maintain the marks.
Southern California Gas Company | N | IMPERIAL | CALIPATRIA | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ALBERTO LOPEZ | CALIPATRIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Gas Company involvement. Homeowner was hand digging a trench for a water line. The homeowner did not have a USA ticket. ETR requested Gas Ops assistance upon arrival and stood by until relieved. ETR hard closed the MSA while Gas Ops repaired the service to purge and was called back the same day for a restore. There were no injuries, evacuations, street closures or media on site.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2025-08-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ELIO | EL CENTRO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | cut service with shovel-1/2 inch CTS. repaired with coupling. damaging party advised 811 call required by law
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2025-11-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3364 |  | 2 |  | GEORGE LISCIANDRELLO | TUCSON | AZ | N | Y | Yes | Yes | No | Yes | No | Yes | No | Third party contractor damaged a 2 plastic main while excavating with a backhoe. The contractor dug outside the delineation and is fully responsible.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2025-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JONATHAN BUENO | EL CENTRO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Jonathan Bueno with bueno homes construction 760-886-2242 reporting hit line with postdigger while replacing post on fence. no usa called
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2025-12-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | HILBERS | YUBA CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Gas Company involvement. Damaged 2? main by 3rd party contractor while excavating. ETR stood by until Gas Ops arrived. Gas Ops control time was 5:28 p.m. Contractor claims they had multiple USA tickets but lines were not visible due to excavation. Fire Dept left the scene once ETR arrived. There were no outages, street closures, evacuations, media, or injuries.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2025-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROVE ENGINEERING | EL CENTRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | HIT WITH EXCAVATOR, COMPANY- ROAD ENGINEERING, CALLER JOSE TRUJILLO 760-925-2085
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2025-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CARLOS CORONADO | EL CENTRO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant of the home was installing a fence post when they damaged the plastic gas line. The occupant did not notify USA and is fully responsible.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | HOME OWNER | EL CENTRO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Gas Company involvement. Homeowner was using hand tools to dig next to the foundation to work on the restroom when they damaged the service. The homeowner did not have a USA ticket. ETR requested Gas Ops assistance upon arrival and stood by until they arrived. ETR stood by to restore service. There were no injuries, evacuations, street closures or media on site.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2025-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1673 |  | 1 |  | HECTOR GUTIERREZ | CALEXICO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer had 3rd party hand digging for footing of an ADU when they struck the service. The homeowner or 3rd party did not have a USA ticket. ETR requested Gas Ops assistance upon arrival and stood by until relieved. ETR bypassed MSA while Gas Ops repaired the service to purge and rebuild MSA to place back into service. There were no injuries, evacuations, street closures or media on site.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2025-01-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | JOEY BOOTS BUILDERS | EL CENTRO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a plastic gas service while excavating for sewer, the contractor did not have a USA.
Southern California Gas Company | N | IMPERIAL | HEBER | 2025-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 42 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | FEDERICO ALATRO | CALEXICO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | repaired broken and blowing service caused by homeowner driving stakes into the ground while forming for new driveway concrete pour. no USA was called in prior to start of work. it was an unreported damage was called in as a odor complaint.
Southern California Gas Company | N | IMPERIAL | HEBER | 2025-01-30 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 42 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | A & R CONSTRUCTION | BRAWLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor damaged 2 inch plastic main while potholing it with a probe, the contractor failed to protect facilities in place.
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2025-07-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  |  | NA | SIERRA GENERAL CONTRACTORS | ENCINITAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged 2 plastic main while excavating with a backhoe. The contractor did not have a USA.
Southern California Gas Company | N | IMPERIAL | WESTMORLAND | 2025-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ROVE ENGINEERING | EL CENTRO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor damaged plastic service, tracer wire issue, no measurements on file, no way to locate service, marked off best judgement and a weak signal.
Southern California Gas Company | N | IMPERIAL | WESTMORLAND | 2025-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JUAN OTERO | WESTMORLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The customer was digging and hit the service line, they did not have a USA.
Southern California Gas Company | N | KERN | ARVIN | 2025-10-23 | Third party excavation damage | Main | Steel | Trencher | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 0 |  | RUBEN S PIPELINE | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 2 steel main stub during backfilling operations. Our crew installed three top halves to control the gas leak, removing the damaged stub, and installing a canopy to complete the repair. The contractor was reminded of the importance of exercising caution when working near our utilities. Due to multiple incidents involving the same contractor in this area, Damage Prevention has been looped in for further follow-up.
Southern California Gas Company | N | KERN | ARVIN | 2025-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RUBEN S PIPELINE | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party contractor damage stl service with Backhoe. Distribution Crew replaced and put in new service due to damage
Southern California Gas Company | N | KERN | ARVIN | 2025-07-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 16 |  | SIERRA CONSTRUCTION & EXCAVATION | BAKERSFIELD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damage 2'''' plastic main while trenching for Arvin water district to install new water main going east of Haven DR. Etd used all available resources to locate 2'''' plastic main but was 6ft off of location of main. ETD received counseling for future locating and on how to use all available resources. Crew Then arrived to make repairs to 2'''' plastic main.
Southern California Gas Company | N | KERN | ARVIN | 2025-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RAFAEL HERNANDEZ | ARVIN | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was replacing fence posts with post hole digger and hit the service. Homeowner was spoken to that USA was needed.
Southern California Gas Company | N | KERN | ARVIN | 2025-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | J. REFUGIO ZUMIEA | ARVIN | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner struck a 1/2 CTS gas service line with a shovel while excavating for sewer repairs near the left front of the residence. No valid USA ticket was found. Crew leader advised the homeowner on the importance of contacting 811 prior to any digging activities.
Southern California Gas Company | N | KERN | ARVIN | 2025-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | BARTOLO CHAVEZ | ARVIN | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damaged 1/2 ips gas service while digging with shovel to remove a tree stump. Did not notify 811 or valid USA ticket. He called 911, FD and PD were on scene but were gone when SCG arrived at the scene. There were no indications at foundation or inside the home but home owners decided to evacuate and stay outside until repairs were completed. LCT educated home owner of the importance of calling 811.
Southern California Gas Company | N | KERN | ARVIN | 2025-09-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 2 |  | SIERRA CONSTRUCTION & EXCAVATION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor damaged 2'''' pla main with backhoe while excavating. Marks were down and visible. Distribution crew made repairs to damage main
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | JOHNNY THOMPSON | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage to plastic service while contractor was excavating to install a water line. Crew arrived and controlled the damage before making permanent repairs with 1, 1'''' coupling. NO USA was called.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | WATTENBARGER MARK CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor damaged 1/2 CTS service while excavating to expose gas houseline. Damaged while digging with a shovel. Gas service was marked, and USA ticket was valid. Contractor failed to use caution while digging around gas service. LCT reminded contractor on the importance of using caution while digging to expose utilities.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | CAMARILLO DRILLING | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1/2 plastic service while digging with backhoe. Contractor failed to exercise adequate caution while exposing pipe, did not hand dig over facilities. LCT reminded contractor on the importance of exposing utilities by hand and not use heavy machinery before exposing utilities within the tolerance zone.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | SANDOVAL CONSTRUCTION & EXCAVATION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Dug in excavation and used shovel to damage 1'''' plastic stub. Distribution repaired 1'''' Plastic stub.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | UNDERGROUND EXPRESS COMPANY | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While tunneling in to connect two bell holes, contractor hit a 1/2 CTS service. Service was accurately marked, and contractor failed to use caution while digging around our gas line. LCT coached contractor and reminded him on the importance of digging with caution around utilities.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor damage 1/2 cts service with shovel trying to set communications box in the guard. Damage was repaired by crew. USA ticket was expired a day before the damage.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-07-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3270 |  | 1 |  | BERRY S CONCRETE | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was using backhoe to dig a 40ft trench to install a communication line. At the end of the trench contractor damaged 2'''' plastic main. Contractor did not call in USA for excavation.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ROSA KAEHLER | BAKERSFIELD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit svc while post hole digging for fence. No USA
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DON MONKS | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged plastic service while repairing pool line. No USA. Crew arrived and controlled leak before making permanent repairs.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JULIO FRANCISCO | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While demoing carport and driveway, the contractor damaged the 1/2'''' plastic service. Crew arrived and controlled damage. After taking underground samples, the crew evacuated 1 customer due to unacceptable levels at foundation. The crew repaired the leak and aerated until code 1 conditions were eliminated and the ambient readings were negative. The LCT counselled the contractor foreman on the importance of USA even if just demoing.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DAN | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit 1/2 CTS service while hand digging to install a fence. USA was not called in. LCT advised and counseled homeowner on the process and importance of calling in USA tickets before digging.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CAL VALLEY CONTRACTORS | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas service was struck by backhoe digging to install new sewer drain. Distribution crew was dispatched to make repairs.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | WESTROCK GENERAL ENGINEERING | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading to lower street and damaged a 1/2 CTS service. Service was marked out by SCG but was part of another company''s ticket. Damaging party did not have a valid USA ticket. Supervisor and LCT spoke with damaging party and reminded them on the importance of calling in a USA, and potholing utilities when any excavation is to be done on top of other utilities.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-10-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | GRIJALVA CONTRACTORS | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged 1 plastic service while digging with a pickaxe. Customer failed to exercise caution while exposing pipe. Crew reminded contractor on the importance of using caution when digging around utilities.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | PACIFIC WEST COMMUNICATIONS | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1/2 cts service while digging with a shovel to expose gas line. LCT reminded contractor of the importance of digging carefully while exposing utilities. Installed a new AL riser due to damage too close to the riser.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2222 |  | 8 |  | CALIFORNIA CLEAN TRANSPORATION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1/2'''' plastic service with shovel while excavating to install electrical conduits. Crew leader spoke with contractor on the importance of using caution while digging around utilities.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ELISHA FRANCISCO | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating to install a block wall, the homeowner failed to notify USA and damaged the 1/2'''' service. The fire department arrived and evacuated 2 people from one building. Crew arrived and controlled the damage before making permanent repairs. The crew then aerated until code 1 conditions were eliminated and evacuations were lifted. I counselled the homeowner to call USA prior any excavation.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2025-04-04 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3270 |  | 1 |  | SOCALGAS | BAKERSFIELD | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating to repair a code 1, the crew damaged the 2'''' plastic main. There was heavy tree roots in the excavation. The crew immediately notified supervision and began altering the main to repair the damage and original code 1.
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2025-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | AMIABLE CONSTRUCTION | CALIFORNIA CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service doing fencing
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2025-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | HHS CONSTRUCTION | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | There was no locate wire on the AL riser. The locator went off measurements. The measurement per Svc History and GIS. Contractor failed to use caution when exposing Gas line. No call was made to tell SCG gas could not be found. Locate wire was installed on service during repair.
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2025-03-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | M M S ELECTRIC INC | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit service by contractor running electrical with backhoe. Failed to exercise caution within delineation. Crew arrived and made repairs.
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2025-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BLAZER SEPTIC SERVICE | TEHACHAPI | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Septic Co. hit service while probing for septic tank. Crew arrived to make repairs.
Southern California Gas Company | N | KERN | DELANO | 2025-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | PACIFIC UTILITY PIPELINE | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While excavating a trench for utilities Pacific Utility Pipeline damaged the 1/2'''' plastic service to 11642 Clinton St. The ticket was closed as No Conflict because service history did not show any service to 11646 Clinton St. The neighbor''s service was under the fence in the wrong property and was damaged. The crew arrived and repaired the damage before verifying that indications had not spread to the foundation.
Southern California Gas Company | N | KERN | DELANO | 2025-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ARTURO PEREZ | DELANO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner contacted plumber to repair waterline. Homeowner did not call in for a USA ticket. While digging, contractor hit the gas line with shovel. Crew went to customer home to make repairs.
Southern California Gas Company | N | KERN | DELANO | 2025-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | HARKER STRIPING | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 cts service while digging with post hole digger. Contractor did not have a valid USA ticket. LCT coached contractor on how to call in a USA dig ticket, and the importance of having all contractors mark out the utilities to avoid damages.
Southern California Gas Company | N | KERN | DELANO | 2025-05-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WISE ELECTRIC AND COMMUNICATION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2'''' plastic main hit by contractor with backhoe while trenching to install electrical conduit.
Southern California Gas Company | N | KERN | DELANO | 2025-05-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WISE ELECTRIC AND COMMUNICATION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Main Was hit from same damage reasons on 5/20/205. Contractor damaged 2?? plastic main while digging to install electrical conduit. Damage was caused by contractor failing to maintain gas marks and not maintaining proper clearance while excavating. Contractor removed whiskers and flags from excavation area prior to digging.
Southern California Gas Company | N | KERN | DELANO | 2025-05-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | REDDIG GENERAL ENGINEERING | KEENE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damage 2'''' plastic main while digging to expose our gas line. Gas line was being exposed by contractor for abandonment and contractor got impatient. Used backhoe to dig and damage line. USA Ticket was good. Flags and whiskers were put in the ground.
Southern California Gas Company | N | KERN | DELANO | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | GUADALUPE ORDAZ | DELANO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer had family member digging to expose pipe to repair. While digging customer used shovel to damage 1/2 cts plastic gas line. Crew was dispatched to repair gas line.
Southern California Gas Company | N | KERN | FRAZIER PARK | 2025-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 58 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ARAVINDU CHITTUMALLA | FRAZIER PARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit service with rebar. No US. No evacuations or agencies on scene. Spoke to customer about call before you dig.
Southern California Gas Company | N | KERN | FRAZIER PARK | 2025-01-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 58 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FRAZIER PARK PUBLIC UTILITY DISTRICT | FRAZIER PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged plastic gas main while excavating. ETD could not get locate signal and exhausted all resources before marking by measurement. Service history and records were inaccurate which led to a damage. After making permanent repairs, LCT installed a locate station to aid with locating facilities in the future. Will also work to send a map update request to update records.
Southern California Gas Company | N | KERN | LANCASTER | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MIGUEL GUTIERREZ | LANCASTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner had a friend removing bushes from yard and hit service while digging. Crew arrived and made repairs.
Southern California Gas Company | N | KERN | LOST HILLS | 2025-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3749 |  |  | NA | PYRAMID HILLS PISTACHIO COMPANY | LOST HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party excavation damage. USA was not called. Excavator was educated by LCT on site regarding legally required USA ticket.
Southern California Gas Company | N | KERN | MC FARLAND | 2025-01-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | LANDSCAPE MANAGMENT | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit main with excavator while digging to install water main. Contractor did not exercise caution while digging to expose gas lines.
Southern California Gas Company | N | KERN | MC FARLAND | 2025-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2047 |  | 1 |  | LUIS CAZARES | MCFARLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to 1 HP Service, home owner damaged while attempting to remove palm tree with tractor. No USA called in. Crew coached home owner on proper 811 excavation process.
Southern California Gas Company | N | KERN | MC FARLAND | 2025-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 1 |  | ALFREDO ABUNES | MC FARLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | EIR created due to Police department and Fire department on scene and evacuations. Fire department evacuated residents due to blowing gas. Home owner damaged 1/2 inch plastic service with sawzall while attempting to remove tree. No USA ticket called in. Crew completed all repairs and counseled home owner about calling in USA tickets any time before digging on their property.
Southern California Gas Company | N | KERN | MCKITTRICK | 2025-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RAMIRO CRUZ | MCKITTIRICK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged 1/2'''' plastic service while excavating to make plumbing repairs. No USA was called. Crew arrived, controlled gas leak, and made permanent repairs. Crew had to aerate due to gas migration under the foundation. Crew aerated until evacuations could be lifted.
Southern California Gas Company | N | KERN | ROSAMOND | 2025-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | COAST CONSTRUCTION GROUP | LANCASTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck 1 service. Barely leaking on arrival.
Southern California Gas Company | N | KERN | ROSAMOND | 2025-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BIANCA GONZALEZ | ROSAMOND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, damaged 1/2 inch plastic pipe
Southern California Gas Company | N | KERN | ROSAMOND | 2025-02-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | POWER PLUS | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit sub with EFV
Southern California Gas Company | N | KERN | SHAFTER | 2025-01-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11740 |  |  | NA | SANDOVAL CONSTRUCTION & EXCAVATION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Sandoval Construction was excavating for water when they damaged the marked 4'''' plastic main. The 4'''' was marked on the street and with flags. Sandoval Construction covered the flags with spoil and the pavement marks with broken asphalt. The crew arrived and controlled the blowing gas in a control hole. The crew repaired the damage by electrofusion. The damage was at EOM so there were no outages.
Southern California Gas Company | N | KERN | SHAFTER | 2025-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HECTOR S PLUMBING | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging trench to install irrigation line and damaged 1/2 cts plastic gas service. Distribution crew made repairs to 1/2 cts plastic gas service.
Southern California Gas Company | N | KERN | TEHACHAPI | 2025-03-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 37 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  | 8 |  | BETOS PLUMBING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 2 service by contractor
Southern California Gas Company | N | KERN | TEHACHAPI | 2025-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | THOMAS ALLAN | TEHACHAPI | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit service with sawzall cutting tree roots
Southern California Gas Company | N | KERN | TEHACHAPI | 2025-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | SHAWN PIMENTEL | TEHACHAPI | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner installing fence struck gas service. no USA
Southern California Gas Company | N | KERN | TEHACHAPI | 2025-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 2 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | WIRING CONNECTION | GARDENA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Fiber crew hit service due to mismarked service. Locate wire was bad and service unlocatable. Crew installed locate station and service is now locatable both directions. ETD shut off the curb valve and crew repaired service
Southern California Gas Company | N | KERN | WASCO | 2025-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CAMARILLO DRILLING | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor exposed abandon 3/4 stl gas line. Contractor thought the abandoned line was live and kept digging a foot away and hit the live 1/2 cts gas line. Crew repaired damaged gas line and informed contractor to be careful when digging to expose gas services.
Southern California Gas Company | N | KERN | WASCO | 2025-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LEGACY LANDSCAPING | WASCO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit 1/2 CTS service while digging to remove footing for wall inside private property. Fire department was on scene. Customer did not call in or have a valid USA ticket. LCT reminded customer on the importance of calling 811 and having utilities marked out and potholed before excavating.
Southern California Gas Company | N | KERN | WASCO | 2025-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | TRIPLE J DRILLING | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While boring to install telecommunications, the contractor damaged the 1/2'''' plastic service. The contractor potholed the service and found steel and assumed the service was inserted. The crew arrived and controlled the damage before making permanent repairs. The LCT counselled the contractor on the importance of verifying marks and underground lines to be certain of the location of the line.
Southern California Gas Company | N | KERN | WASCO | 2025-07-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CAMARILLO DRILLING | CAMARILLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor had Valid USA and was marked correctly. Service was hit while they were using bore machine. No gas was blowing, NO evacuations. Homeowner called after the fact to report damage. Pothole was not done before performing work.
Southern California Gas Company | N | KERN | WASCO | 2025-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | CROWN COMMUNICATION | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor potholed for service and found a steel line. Markings on the ground indicated it was a plastic gas line. Contractor did not continue to dig for plastic gas service and hit 1/2 cts plastic service while performing directional bore.
Southern California Gas Company | N | KERN | WASCO | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | CROWN COMMUNICATION | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor used a backhoe to dig out excavation and struck 1/2 cts gas line. Company crew was dispatched out to make repairs on 1/2 cts service.
Southern California Gas Company | N | KERN | WASCO | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FIBER CO 81 | NUEVO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damage to 1/2'''' plastic stub service. Not marked because it was an undocumented stub service. The crew controlled the damage before abandoning it at the SMC. No way to locate the stub service.
Southern California Gas Company | N | KERN | WASCO | 2025-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CROWN COMMUNICATION | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crown Communications damaged the 1/2'''' plastic service while setting a communications box with a sharp shooter shovel. The crew arrived and controlled the blowing gas before making permanent repairs. The police department evacuated 4 people before leaving when the crew arrived. The fire department also departed when the crew arrived. The crew lifted the evacuations once the gas was under control. The line was correctly marked for the valid USA.
Southern California Gas Company | N | KERN | WASCO | 2025-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | UNITECHZ COMMUNICATIONS | YUMA | AZ | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1/2 ips service while digging with a sharpshooter to expose gas line. Crew completed repairs and reminded the contractor of the importance of using caution while hand-digging to expose gas lines.
Southern California Gas Company | N | KERN | WASCO | 2025-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CROWN COMMUNICATION | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damage 1/2 cts service with sharpshooter. Distribution made repairs to gas service.
Southern California Gas Company | N | KERN | WASCO | 2025-11-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | BURTCH CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While excavating to install water to a new commercial building, Burtch Construction damaged the 4'''' plastic main. Two offset marks in the gutter were found accurately identifying the 4'''' plastic main. After the first ticket in July, the 4 renew tickets did not request marks. The crew failed to pothole prior to excavating with the backhoe. The crew arrived and controlled the damage before making permanent repairs.
Southern California Gas Company | N | KERN | WASCO | 2025-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | DANIEL CORRERO | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor bored through 1/2 cts service. Distribution Crew made repairs to Gas service.
Southern California Gas Company | N | KERN | WASCO | 2025-08-20 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3924 |  | 8 |  | UNITECHZ | YUMA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor installing fiber line by boring. Did not expose 2 plastic main where boring machine crosses over SCG main. Damaged the main while pulling the fiber conduit. LCT counseled the contractor of the importance of exposing all facilities in the work area before boring.
Southern California Gas Company | N | KINGS | CORCORAN | 2025-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | NOLAN S PLUMBING | CORCORAN | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating with a backhoe & no USA, hit & ruptured a 1/2 plastic service. Contractor was counselled by LCT on site about the importance of calling in USA ticket 2 or more business days prior to excavating.
Southern California Gas Company | N | KINGS | CORCORAN | 2025-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 31 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | IGNACIO TORRES | CORCORAN | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged a 1/2 plastic gas line while excavating for fence project. Crew made permanent repairs, damaging party Ignacio Torres was advised to call Dig Alert 811 before excavating, moving forward.
Southern California Gas Company | N | KINGS | HANFORD | 2025-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DURANGO FENCING | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor Durango Fencing Inc damaged a 1/2 plastic gas line while excavating to install a fence, contractor did not have a USA ticket as required, SCG crew made permanent repairs. Jose Landeros from Durango Fencing was advised to have active USA ticket moving forward, when excavating.
Southern California Gas Company | N | KINGS | HANFORD | 2025-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | REIS EXCAVATION | HANFORD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contactor damaged an unmarked, unlocatable 1 plastic stub. Instructed LCT to submit MUR.
Southern California Gas Company | N | KINGS | HANFORD | 2025-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BRANDI KILGORE | HANFORD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant digging to bury dog, damaged a 1/2 plastic service. Occupant was counselled by LCT on importance of contacting 811 two or more days prior to any excavating.
Southern California Gas Company | N | KINGS | HANFORD | 2025-08-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LANDSCAPE DEVELOPMENT | VALENCIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While excavating for drain line, 3rd party contractor Florencio Marion from Landscape Development damaged a 1 plastic gas line, crew made permanent repairs. Contractor was reminded to pothole gas lines with hand tools, moving forward, when excavating.
Southern California Gas Company | N | KINGS | HANFORD | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | IRISH ELECTRIC | TULARE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor excavating with a trencher, hit a miss-marked service. Service was marked approximately 6'' off.
Southern California Gas Company | N | KINGS | HANFORD | 2025-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | SOCAL EDISON | ROSEMEAD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCE working to repair electric lines, hit & ruptured a 1/2 plastic service. USA had not been called. SCE foreman was reminded by LCT to call in USA for any emergency work being done.
Southern California Gas Company | N | KINGS | HANFORD | 2025-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JORGE CERVANTES | HANFORD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer''s contractor hit gas service while attempting to install meter guard.
Southern California Gas Company | N | KINGS | LEMOORE | 2025-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MARTY REEBER | HANFORD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating to repair sewer cleaned out, hit & ruptured a 1/2 plastic service. Contractor was counselled by LCT & FOS on importance of calling USA 2 or more days prior to any excavating.
Southern California Gas Company | N | KINGS | LEMOORE | 2025-07-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 22 |  | GRIZZLY CONSTRUCTION | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was excavating to install water line when they damaged our 2 plastic main, upon arrival main looked to be exposed. It was completely severed in half.
Southern California Gas Company | N | KINGS | LEMOORE | 2025-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DAVID POTTER | LEMOORE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged plastic service while digging for fence. NO USA. Crew replaced 2 ft of pipe to repair damage.
Southern California Gas Company | N | LOS ANGELES | ACTON | 2025-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NATHAN GOODMAN | ACTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit service while trenching for electrical. No USA called
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2025-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CONEJO VALLEY PLUMBING | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1/2 PLA service while excavating for sewer repairs with shovel. Crew made permanent repairs in form of Service Alter. No USA. Contractor called in USA ticket while repairs were being made.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2025-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ESPARZA DESIGN LANDSCAPE INC | OXNARD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1/2IPS service while digging post holes for fencing. No USA called. Permanent repairs made in field by crew. V.S.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2025-06-20 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 6 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 17228 |  |  | NA | FIBERTEL COMMUNICATIONS | SYLMAR | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | A third-party contractor struck our 6 PLA Main during boring operation. Marking Pothole to Verify was indicated adjacent to the 6 PLA Main marking. Contractor performed potholing but did not visually confirm location of 6 PLA Main. Gas Company ETD was not notified when the 6 PLA Main was not identified during the potholing procedure.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | KIM MEJIA | AGOURA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 PLA service hit by contractor working for homeowner. Contractor hit service with post hole digger while digging post holes for fence replacement. NO USA. Contractor was informed of importance of USA. Permanant repairs made in the form of service alter.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2025-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | AVI SHAFRAN | AGOURA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on digging hole to remove roots hit 1/2 plastic service. Service was marked with flags and paint, but was for a different contractor. There was no fire department, police, road closures, evacuations, or news media on scene. Crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | EDWIN SERRANO | AGOURA HILLS | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor hit 1/2 CTS service with hand tools while digging in front yard. GC onsite stated they are adding ADU''s to property. GC stated he had a USA ticket but USA ticket was expired. GC unaware he had to renew ticket after 28 days. No marks visible onsite, entire front yard trenched with mounds of dirt everywhere. SCG service marks visible on sidewalk. Crew pinched service and made repairs via alteration.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2025-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3715 |  | 24 |  | STEPHEN DORECK EQUIPMENT RENTALS | PICO RIVERA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor installing new water main damaged 1 inch service with a backhoe. Incorrect maps and records found which resulted in the damage.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2025-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | TIKAL CONSTRUCTION | ORANGE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | LINE HIT W/PICK. ADDING ADU UNIT. TIKAL CONSTRUCTION LLC . PHD IN ALLEN CABRERA 714-266-9315
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2025-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | AYERS CONSTRUCTION | SAN JACINTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor grading for footing at In n out parking lot struck 1 inch service with bobcat. Service was properly located and marked with paint and flags. Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2025-07-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3364 |  | 2 |  | AT&T | ROSEMEAD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ATT&T crew failed to call in USA prior to using auger machine to displace soil in close proximity to 2pe main.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2025-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 28 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CALIFORNIA HOME BUILDERS AND RESTORATION | GARDEN GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to connect new ADU sewer lateral to existing sewer pipe, found orange colored roots in excavation which caused him to confuse orange 1/2 gas service pipe for a root and attempted to cut through with round shovel. Company crew arrived, controlled escaping gas and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2025-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SON DINH | ALHAMBRA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging trench for sewer hit our 1/2 cts service with a shovel causing broken and blowing. No USA was called in for this job. Pasadena OHS crew arrived, controlled gas and made permanent repairs using 1'' 1/2 of 1/2 cts and two couplings.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2025-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JASP CONSTRUCTION & DESIGN | WALNUT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2inch plastic service hit by contractor that was installing sewer lines to an ADU. No USA was called in.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2025-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ALEJANDRO GARCIA | ALHAMBRA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | FOUND DAMAGED RISER CAUSED BY ALEJANDRO GARCIA/SON IN LAW OF COR DIGGING WITH A SHOVEL WHILE MAKING REPAIRS AT THEIR HOUSE LINE, 811 WAS NOT CALLED
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2025-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DGB CONSTRUCTION | ALHAMBRA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor using trencher for wall installation hit our 1/2 inch plastic service causing broken and blowing. Pasadena OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installing 2'' of 1/2 cts and two couplings. No USA was called in for this job.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2025-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | STEPHEN DORECK EQUIPMENT RENTALS | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck plastic service with sharpshooter while digging.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2025-12-09 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | ACCESS GENERAL CONTRACTING | CORONA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Company contractor struck branch service while digging for bollards.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2025-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 27 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | STEPHEN DORECK EQUIPMENT RENTALS | PICO RIVERA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing sewer used backhoe near SMC and hit unmarked 1/2 service. Appeared service was to a location that was not being used. They did have an active USA. Pasadena OHS crew arrived, controlled gas and made permanent repairs by capping and abandoning the service.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SALCIDO EARTHWORKS | MORENO VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging around tree stump for removal and damaged a 1 plastic service with a shovel. No USA ticket for this incident.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-10-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | VIKING DEMOLITION | GLENDALE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractors struck 1 gas main while digging.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-02-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | INTERNATIONAL LINE BUILDERS INC | ALTADENA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor digging with backhoe when 2 inch plastic gas main was damaged. Valid USA
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | INTERNATIONAL LINE BUILDERS INC | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While excavating to install a conduit, the excavator hooked and pulled the 1/2'' CTS service line. The gas line did not rupture but was stretched close to the breaking point. Crew arrived on site and squeezed 1/2 CTS line and proceeded to make repairs. Crew cut out the damaged section and replaced it using (2) 1/2 CTS couplings and an 18 segment of CTS pipe.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | H & E TREE SERVICE | AZUSA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on tree removal when 1plastic gas service was damage.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | INTERNATIONAL LINE BUILDERS INC | PORTLAND |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor struck gas service with backhoe while digging trench.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | NEW GOOD EARTH | SIERRA MADRE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer had someone working on front yard digging by meter and struck gas service. Customer did not want to divulge information of person performing work.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ANVIL BUILDERS | ALTADENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | During the grading process, the contractor snagged the riser and service. There was a valid USA and the line was marked. The damage happened at the tail end of the job. The contractor just got careless while grading as riser was visible.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-12-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALLEN PIPELINE | MONROVIA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | USA expired, Contractor dug after USA expired and hit 1/2'''' pla service.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 28 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HERNANDEZ LUIS ALFONSO | WEST COVINA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Private contractor hired by business owner for fire debris removal began bundling up debris with mini excavator when stopcock on riser was ripped off steel riser. Crew arrived to control leak and cut back service. Company contractor will abandon service next day.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | TAK CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2plastic service with shovel. no USA.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ANVIL BUILDERS INC | EMERYVILLE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator was removing debris the area. As debris was removed, it struck the 1/2 PE service line. The SCG crew dropped back, squeezed the line and did a cut back tin the yard. The site had a valid USA ticket. The ticket was marked No Gas by the locator. The line was abandoned the next day.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ANVIL BUILDERS | EMERYVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck gas service line during debris removal operations. The gas line was marked and within delineation. Company crew proceeded to abandon the line.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | TIDWELL POWER | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Had valid USA. digging with backhoe next to 2steel gas main when service tee was damaged. contractor failed to expose gas main. locator marks for 2 steel main correctly marked.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DEXTEROUS CREATIVE CONTRACTORS & DESIGN | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging with backhoe 2 steel main was exposed but failed to follow digging procedures. digging with backhoe using 2steel gas main as a guide. damaged abandoned service tee. No USA was called.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ANVIL BUILDERS INC | EMERYVILLE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | During the debris removal process, a riser was struck by an excavator. Crew arrived on site and squeezed the line. Crew went on to make the repair by fusing 1/2CTS cap.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | TIDWELL POWER | RIVERSIDE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3RD party contractor digging with backhoe prior a valid USA. There were old marks from previous USAs in the area.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | TIDWELL POWER | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging with backhoe over 2PLA gas main. Contractor had valid USA.. contractor failed to hand expose 2PLA gas main
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-11-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4110 |  | 10 |  | LEGEND CONSTRUCTION SERVICES | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to remove septic tank with backhoe when 2pla main was damaged. contractor working with expired USA. marks were visible
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NA | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck gas service at the riser. The contractor tied back the line and left the scene. Company crew arrived, squeezed the line and proceed to abandon the service at the smc. The contractor was working without a valid USA ticket.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ANVIL | BURLINGAME | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 1/2 inch plastic service while removing debris with backhoe. valid USA
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HARTFIELD CONSTRUCTION | ARCADIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2 encased plastic service. Contractor did not have a valid USA. Contractor called in USA after the line was hit. Crew squeezed line and fused cap.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  |  | NA | ANVIL BUILDERS INC | EMERYVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavator struck steel service line simultaneously yanking out the branch service as well. Contractor was notified to exercise more caution as the service marked. Company crew went on to abandon the standard service at the smc.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ANVIL BUILDERS INC | EMERYVILLE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with backhoe when gas service was damage.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2025-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LINCOLN AVENUE WATER COMPANY | ALTADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA WAS REQUESTED. Lincoln Avenue Water Company was repairing a broken water main and while excavating, their backhoe damaged / severed a 1/2 plastic gas line.
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2025-02-25 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 50 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GENTRY BROTHERS INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working on replacing curb & gutters digging with backhoe when pulled 2 steel main that was shallow
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2025-06-27 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NPL CONSTRUCTION | EASTVALE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit line during service installation while trying to expose existing service. Incident happen on my DIMP main replacement. Company crew made final repairs.
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2025-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DONALD TANG | ARCADIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on replacing fence. digging with hand tool when 1/2 plastic gas service was damaged. No USA
Southern California Gas Company | N | LOS ANGELES | ARLETA | 2025-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RIGOBERTO ANGUIANO | ARLETA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 1/2 CTS plastic service with hand tools while digging in yard for plants. Homeowner did not have a valid USA. There was no fire department, police, road closures, evacuations, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | ARTESIA | 2025-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 6 |  | PRODIGY PLUMBING | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Broken and blowing 1 plastic service caused by third party damage. Contractor was hand digging for sewer repair when they damaged 1 inch plastic service. No USA.
Southern California Gas Company | N | LOS ANGELES | ARTESIA | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | PRODIGY PLUMBING | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbers damaged 1/2 plastic service with backhoe while digging to replace sewer.
Southern California Gas Company | N | LOS ANGELES | ARTESIA | 2025-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | KMA INSPECTION & CONSTRUCTION SERVICES | TUSTIN | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor did not have valid usa and hit our service with a shovel. 2nd time we have been at this address in a year.
Southern California Gas Company | N | LOS ANGELES | AZUSA | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 57 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2179 |  | 1 |  | PATRICK GALLARDO | AZUSA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner had crew build addition. There was no USA crew cut into steel service thinking it was not active. Crew installed clamp after hot squeeze. service and branch will be replaced on later date,
Southern California Gas Company | N | LOS ANGELES | AZUSA | 2025-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | BURPEE S PLUMBING | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor- plumber was excavating a hole with a mini backhoe on private property and damaged 3/4 steel service line. Damaging party did not have a valid USA ticket for this work.
Southern California Gas Company | N | LOS ANGELES | AZUSA | 2025-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ON POINT PLUMBING | SANTA CLARITA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Broken and Blowing. Damaged 1/2inch plastic service. Hit by backhoe.
Southern California Gas Company | N | LOS ANGELES | AZUSA | 2025-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | T9 ENTERPRISES | LA VERNE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage caused by T-9 Demolition, while performing demo for Graves Construction. According to project sup. Alfredo Garcia, T-9 was overly aggressive and used oversized equipment to perform task outside of instructions and hit 1 svc line as a result
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2025-04-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LONG LUONG | BALDWIN PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Field notes. .SVC was installed 4/17. Contractor hit svc line in provided trench. Svc was covered with warning mesh and shaded with sand. Contractor was installing gas HL and hit the svc with a shovel
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2025-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | JOSE BARAJAS | LAWNDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The customer should be billed for the damage due to not calling in for USA ticket. The customer was trenching to install some sewer pipe and severed a 1/2 inch cts service.
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2025-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1771 |  | 4 |  | JOSE BANUELOS | BALDWIN PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging to remove plants and stated he smelled gas from soil, dug an inch more and found service line leaking.
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2025-04-23 | Operator excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3983 |  |  | NA | NPL CONSTRUCTION | MIRA LOMA | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service tee was hooked and torn off the 2inch steel main by paving contractors. 2nd party NPL was on site to do the paving for the abandonment order at this address.
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2025-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PLATINUM CONSTRUCTION | STANTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LCT notes- arrived onsite broken and blowing my property. fire dept and police contained area. dug control hole and stopped gas flow at 12:25pm . repaired damaged and called for restore
Southern California Gas Company | N | LOS ANGELES | BELL | 2025-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 28 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | CARLOS ALCALA | BELL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit heavily corroded line with shovel.
Southern California Gas Company | N | LOS ANGELES | BELL | 2025-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 4 |  | RICH CHAVARRIA | BELL | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for fence replacement damaged 1 inch plastic service. Contractor did not have a valid USA. Company crew responded and made permanent repairs. There was no fire department, police, road closures, or news media on scene.
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2025-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 5 |  | HOME OWNERS FRIEND | BELL GARDENS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Upon arrival, I saw a bag on the floor for a shark bite fitting meant for house line plastic pipe on the ground. I pointed it out and the person digging, Gustavo Chavaria, and he stated that they hit the line on Saturday, 3/15/2025, and it was blowing hard. They bent the pipe back to stop the leak and installed the fitting. They had no intention of calling in the leak, but on Sunday they heard gas hissing and could smell it and called it in.
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2025-04-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MARIA MORDES | BEL GARDENS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | resident of house was digging trench for sewage and cut through our 1/2 inch IPS service with EFV. Fire Department put a wood plug in to control gas. Downey OHS crew arrived, pinched service and made permanent repairs using 2'' of IPS and two couplings. Occupant had a USA, but it was not renewed.
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2025-11-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | FRANCISCO HERNANDEZ | BELL GARDENS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner was working on property installing new sewer and getting ready to pave for parking lot damaged 1/2 plastic service witch backhoe while digging to install sewer.
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2025-04-16 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 28 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | BIG BEN ENGINEERING | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging up a water valve, contractor pogoed through 2 inch main.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2025-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | JOSE L MARTINEZ | BELLFLOWER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 1/2 plastic service with pick axe while trying to expose sewer line.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ALVALDEZ CONSTRUCTION | CARSON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors relocating fence with no USA trying to remove a fence post they damaged our 1/2 plastic service with a shovel
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2025-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | LUX BUILDERS & REMODELING | MANHATTAN BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contarctor struck 3/4 steel servcie whith Backhoe, No Vaild USA was Called
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2025-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 125 | 125 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ALLO CONSTRUCTION | PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | Yes | Excavator provided no markings for the proposed excavation on site. | No | We arrived to a damaged 3/4 steel service that the owner stuck a branch into to slow down the blow. The fire department called it in and left the scene before we arrived. I called out the oncall High Pressure Construction manager and we were able to safely temporarily repair the service. The Hollywood Base Distribution supervision was notified and has scheduled the service to be altered at the property line. It was night time and we were dealing with some massive roots that hindered us from doing a permanent repair at the time.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2025-06-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HEIDI WETTENHALL | BEVERLY HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner was excavating with an expired USA ticket. The service was damaged with a shovel.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ANDERSEN COMMERCIAL PLUMBING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damage 1/2 plastic while trenching for sewer line No vaild USA ticket
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2025-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | AMERICAN DRAIN WORKS & PLUMBING | CULVER CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on sewer repairs damaged 1/2 CTS service with hand tools. Contractor did not have a valid USA. There was no emergency services, evacuations, road closures, or news media on scene. Company crew capped service and plans were made to complete repair the following day due to the ongoing sewer repair work.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2025-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MOSSER PLUMBING AND HEATING | MARINA DEL REY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaging party Russell Mosser didnt have USA ticket. It was the General contactor didnt have company name on it so ETD sent ticket back has no delineation, but Contractor had gas stub expose an stuck it with the Backhoe.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2025-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | IC PLUMBING & CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party plumber damaged 1/2 IPS service while excavating to repair damaged sewer line during heavy storm.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2025-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FORT MULTIFAMILY | BEVERLY HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor cut 3/4 inch steel service with grinder while doin demo for House No USA
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2025-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DC CONSTRUCTION | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 plastic service with a shovel while digging a trench in private property.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2025-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TH O CONNOR CONSTRUCTION | ENCINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage, contractor hit 1/2 plastic service with mini excavator and was digging without a valid USA. Company crew came on site to control gas and make permanent repairs. Contractor was in the process of cutting back service to property line with Hollywood Field Planner Juan Gonzalez and told planner that he was intentionally going to hit service to speed up the process, I notified damage prevention of issue and unsafe practice. No USA called .
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2025-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WOOD WAYS CONSTRUCTION | WINNETKA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit line while trenching for possible power conduit No Vaild USA
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2025-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | PB CHOICE PROJECT CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Mario Lopez excavator on site hit service with backhoe; he claimed marks were off, but prictures provided by locator shows marks were formerly on patch near their excavation. Marks were no longer visible at time of damage, and excavator trying to deny responsibility claiming mismarked service. ETD verified locate and was able to trace 1 service correctly to damage location. Other marks excavator claim were mismarks are for 3/4 steel svc feeding 630 Williams.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2025-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Upon the crew''s arrival, third party damage was caused while trenching in the backyard. No USA available.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PACIFIC UTILITY INSTALLATION | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit gas service with backhoe failed to ask for remarks
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ARMON SEMERGEN | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for homeowner digging fence post out with mini excavator severed 1/2 plastic in casing feeding neighboring lot. Crew cut back service due to unlivable conditions of vacant house.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | GARY MARKARIAN | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 1/2 plastic service with shovel. No USA called in for this job.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-10-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | M TEK COMMUNICATIONS | BURBANK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party damage 1 plastic service. USA was valid and marks are visible. This is an ongoing work and SCG ask contractor if they need remarks on street and informed him that they don''t need any and that are done working on S Avon.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GARY GEVOJANYAN | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer claims hit service with shovel but backhoe was present. Contractor was trenching from Active car wash towards vacant buildings. Service was found to be an encroachment and customer requested for service to be removed due to none use. Crew dug control hole in sidewalk and cut back service. MTR was removed by customer service.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | SOUREN GRISHIKIAN | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called, hit 1/2 CTS plastic pipe withe shovel
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-04-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | KNA CONSTRUCTION | WALNUT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor remodeling front yard did not have USA damaged 1 inch plastic service with wood stake. Due to grading, service was found shallow by crew. Crew made repairs to leak same day by cutting back service temporarily, then returned the next day after damaging party trenched property line to meter to remediate shallow service conditions that was caused by remodeling activities. Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BRIGHTVIEW LANDSCAPE SERVICES | SAN FERNANDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damaged 1 plastic service with sharp shooter. Found pl to meter exposed for extended period of time and rebar pillar built around 10% portion of riser. Crew replaced PL to MTR.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GEORGE SAPUNJIAN | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit service line with small excavator while doing paving work. Permanent repairs were made by altering service (1'' of 1/2 CTS with 2 couplings). No injuries, no fatalities, no evacuations, no street closures, no police, no media, and no fire department.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | JUSTIN BUTLER | BURBANK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner digging for fence post struct 1/2 cts service. NO usa called.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 5 |  | SEWER & PIPELINE | LOS ANGELES | CA | N | Y | Yes | No | No | Yes | No | Yes | No | 3rd party damage. contractor dug outside of original delineation and after ticket expired. Contractor extended delineation but did not call for a new ticket or amend ticket. Contractor shut down from continued work outside of delineation until new ticket complete and valid. Damage prevention held meeting with contractor. Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GENESIS GROUP BUILDERS | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3 party damage. Contractor was digging with NO USA when 1/2 CTS pipe was damaged. Crew arrived dropped back dug control hole then pinched plastic service. Crew used two 1/2 CTS couplings along with two feet of 1/2 CTS pipe for final repair.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | JOSE GUERRA | BURBANK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CTS service damaged during excavation. Crew made permanent repairs
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-04-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | PULTE HOMES | MISSION VIEJO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged stub service at cap. Crew found end of stub service 1 deep. Stub service was installed by company crew but backfilled by veriforce qualified person by developer. Per veriforce back filler, stub was dug back up by 3rd party and buried again at improper depth. Crew made permanent repairs and relocated 1Plastic service to the proper depth in private property.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2025-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | ANTONIO GONZALES | PORTER RANCH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No ccslb number due to no license. while pulling and digging threw tree roots steel service was struck.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2025-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | QUALITY TECH CONSTRUCTION | SIMI VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage to company property, 3 party damage. 3 party contractor failed to expose service correctly when damaged 1/2 plastic service that was marked out correctly with a valid USA. Crew pinched line used two plastic IPS couplings along with 3 feet of IPS plastic IPS pipe for final repair.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2025-12-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  | 0 |  | HOME OWNER | CALABASAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA WAS REQUESTED contractor was digging trench to install sewer line to new home when they struck plastic service punch tee with excavator
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CALABASAS VILLAGE MOBILE ESTATES | CALABASAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1 gas service while digging with electric jackhammer. No USA, 2 people self-evacuated from mobile home park rec center. Crew arrived and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2025-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BRIAN SWIEDENHESP | CALABASAS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner while digging for fence post struck our service line, NO USA
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2025-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BOOTH GRADING & EXCAVATING | ACTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 2? Plastic cutback service with backhoe while breaking concrete and grading property. Crew pinched 2? plastic main to isolate damage. 2? plastic service was cut and capped at damage location for a removal of an additional 15ft worth of cutback inside property line. No USA called, previous old markings on main street, no delineations found onsite or within property lines. no USA tickets found on Korterra under location address.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2025-10-21 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 0 |  | ARB | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while digging to expose gas service, contractor struck plastic service line with shovel. dirt is hard so shovel bounced off trench and struck the side of the gas service. crew showed up and fixed service. contractor was replacing service already
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2025-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 1 |  | JOSE YUGALDE | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor hit plastic service while digging to expose sewer line
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2025-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | WOLF HAVEN | MURRIETA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck 1/2PLA service while trenching for electrical work. FD evacuated 4 residents from 4 homes and closed street. Permanent repairs made via service alteration. Contractor dug outside described area on ticket, no delineations on-site. Contractor was coached on proper delineation methods and damage prevention knowledge. Evacuations lifted and road re-opened shortly after gas under control by SCG and FD.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2025-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | TRACY BUNETTA | CALABASAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer planting trees. Damaged 1/2 IPS service. No USA called in.
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | FOSTER CONTRUCTION | SANTA CLARITA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while excavating contractor stated he lost sight of service and hit plastic line. Valid USA with paint marks
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2025-08-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | B&W PLUMBING | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was excavating to install new sewer lateral. While digging, contractor hit 1 plastic service. Valid USA. Facility records and maps were incorrect. Crew arrived and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2025-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | FERREIRA COASTAL CONSTRUCTION CO | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Licensed 3rd party contractor had a valid USA for work. While they were excavating to install sewer, they hit mismarked 1 plastic gas line with mini excavator. Service had tracer wire issues and interference with other underground utilities. Crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2025-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | FERREIRA COASTAL CONSTRUCTION CO | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Licensed 3rd party contractor excavating for install of utilities, hit line with backhoe. Line was marked by hooking up to exposed locate wire. Service had 2 different tracer wires and 2 different pipe kinds. Tracer wire caused line to miss marked, locater was led astray. Contractor had valid USA. Reviewed Gas Standard with the employee.
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2025-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SM DEVELOPMENT | SUN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hired by homeowner to upgrade electric conduit. Valid USA. Marks accurate within tolerance zone. Hit with shovel. Crew arrived and replaced damaged section of pipe, completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2025-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While using the auger to install a power pole DWP struck plastic service line. No USA
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2025-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | SCORPION BACKHOE | CANOGA PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging to install sewer lateral contractor struck plastic service line with backhoe. NO USA
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2025-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | BECKS PLUMBING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | plumber was digging to repair sewer line when they struck plastic service with shovel NO USA
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20001 |  |  | NA | CANYON COUNTRY MOBILE HOME ESTATE | CANYON COUNTRY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA contractor was looking for a water leak inside the trailer park damaged the 1/2 line attempted repair found additional EIR created for second damage.
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2025-01-07 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ASPHALT PROFESSIONALS INC | THOUSAND OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor damaged 2-inch plastic main while augering. No USA called for this job.
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2025-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | MIGUEL REYES | CANYON COUNTRY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner stuck pla service repairing sewer leak. No usa called
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2025-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | ONYX PAVING | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CSA251290315D or CSA251290320D, damaged by a paving grinder, failed to use caution while digging
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DRB BUILDERS EXPRESS | NEWBURY PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged service line while removing tree trunk. LCT made permanent repairs by caping at the SMC. Service was previously cut back near MSA for construction. As a preventative measure, FD had evacuated next door neighbor. Supervision along with ETR checked levels near residence and determined that evacuation was not required and was therefore lifted at 9:30am. Underground samples were negative after the repairs and at no time did gas migrate to any structure. No Police, no media, no street closures, no injuries, and no fatalities.
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2025-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | EXPRESS ELECTRIC | GRANADA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA valid & Marks accurate. 3rd Party Contractor was trenching for new electric line when they struck 1/2 PLA Service. Contractor knew where line was marked but assumed service was steel.
Southern California Gas Company | N | LOS ANGELES | CARSON | 2025-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ONYX PAVING CO | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors hit 3/4 steel service with backhoe which cracked service and caused leak, crew clamped leak to make permanent repairs. Contractors had valid USA, and service was correctly marked but they failed to protect our facilities in place by potholing to locate service.
Southern California Gas Company | N | LOS ANGELES | CARSON | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | ONYX PAVING CO | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service with backhoe while replacing curb and gutter. Contractor did have a valid USA but failed to hand expose service. Service was in casing and plastic pipe was pulled significantly. Crew had to go to SMC to make permanent repairs safely. There was no fire department, police, news media, or road closures on scene.
Southern California Gas Company | N | LOS ANGELES | CARSON | 2025-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MARB CONSTRUCTION MANAGEMENT | DOWNEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors damaged 1/2 plastic service while trenching houseline for ADU, no USA called in. Crew altered service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | CARSON | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ANDY BERGLOFF | REDONDO BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 plastic service damaged by contractors digging to install houseline for gas. No USA called in, crew alter service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | CARSON | 2025-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 11 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | RITZ PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing contractor working on sewer repair damaged 1/2 CTS service with hand tools. Contractor did not have a valid USA. There was no emergency services, road closures, evacuations, or news media on scene. Crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2025-03-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GOTHIC LANDSCAPING | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2 inch service on new development while installing drain system in front yard. EFV tripped therefore there was minimal release of gas. Crew made permanent repairs with two couplings and a foot of 1/2 IPS. No injuries, no fatalities, no street closures, no fire department, no police.
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2025-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | WILCOX AND WILCOX | CANOGA PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Contractor hit end of stub while digging trench. Crew replaced cap on stub for perm repair.
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2025-04-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | KENNCO PLUMBING | SANTA CLARITA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on water line in new housing tract hit plastic service. Service did have an EFV. There was no fire department, police, road closures, or news media on scene. Contractor did not have a valid USA. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2025-05-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | WILCOX AND WILCOX | CANOGA PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck 2 pla main having it exposed
Southern California Gas Company | N | LOS ANGELES | CERRITOS | 2025-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BUILDRITE CONSTRUCTION | ARTESIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit our plastic service line while digging for a drainage line.
Southern California Gas Company | N | LOS ANGELES | CERRITOS | 2025-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TRIPLE P PLUMBING & DRAINS | NORWALK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbers installing water service hit 1/2 IPS service with shovel while digging trench.
Southern California Gas Company | N | LOS ANGELES | CERRITOS | 2025-10-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | PAVAH | DOWNEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit line with excavator while digging trench for sewer. No USA.
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FERNANDO BUILDS | VAN NUYS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor struck 1/2 CTS with shovel. Contractor was digging for electrical. Fire departed upon arrival. USA valid and contractor failed to maintain clearance of tolerance zone. Flags removed from excavation area and service area was marked properly with paint.
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2025-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | FERNANDO KEYSSIAN | NORTH HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, hand digging for electrical service and dig in onto our 1/2 plastic service with shovel
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2025-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 45 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MARWAN HALABY | MISSION HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Believe they were making trench deeper and hit our gasline with shovel trying to cut out roots, it was a clean complete cut and pipe has roots around it.
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2025-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | TONY RAUFI | PORTER RANCH | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging hole to expose power when they struck 1 plastic service with excavator. GIS shows no stub was installed and was not located out for that reason
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2025-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | VCI CONSTRUCTION | CHATSWORTH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | while digging with excavator contractor struck steel service. markings where not accurate due to interference with out there utilities, and GIS not correct
Southern California Gas Company | N | LOS ANGELES | CITY OF INDUSTRY | 2025-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DSRM CABLE CONSTRUCTION | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1 PE service with a sharp shooter while potholing to install conduit.
Southern California Gas Company | N | LOS ANGELES | CITY OF INDUSTRY | 2025-09-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | NICOLAS IGNACIO | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor damaged 1 PE service with a shovel while digging a trench to install a casing for the new gas service. No valid USA
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2025-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DOMINGUEZ MASONRY & LANDSCAPING | RANCHO CUCAMONGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2inch service line on private property. No USA was called before digging.
Southern California Gas Company | N | LOS ANGELES | COMMERCE | 2025-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | AMERICAN INTEGRATED SERVICES | WILMINGTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While removing soil with a mini excavator, a 3rd party contractor struck a 1/2 plastic gas service line. The contractor had removed the location flags and covered the paint markings on the sidewalk with a tarp at the time of the incident. The contractor''s USA Ticket was valid and the service line was accurately marked. A distribution crew responded, controlled the gas, and made permanent repairs to the service line.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2025-11-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | ROJAS GENERAL CONSTRUCTION | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1/2 CTS service with hand tools while digging hole for guard post. Contractor did have a valid USA and service was struck within delineation. Service was accurately marked with paint. There was no emergency services, evacuations, road closures, or news media on scene. Crew made permanent repairs to damaged section of pipe and riser.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FRANKS PLUMBING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 CTS service. Fire department was on the scene and evacuated one residence. Company crew made permanent repairs and evacuations were lifted when ambient readings were below the threshold. Company crew made permanent repairs. There was no news media, road closures, or police on scene. There was no valid USA on file.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2025-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | EDESIGN & BUILDING | MONTEBELLO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching to expose gas line when he accidentally damaged 1/2'''' CTS plastic service with shovel. No USA
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2025-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 39 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LESLIE ELECTRIC | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging on private property, with no USA ticket, struck 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2025-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 3 | 59 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | PAVEMENT RECYCLING SYSTEMS | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors damaged 3 steel service while doing paving work. Crew altered service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2025-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SANTANA CONTRACTORS | DOWNEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor had no USA and while digging with a mini excavator while working on the sewer line, damaged a 1/2 CTS plastic service in 1 steel casing. Company crew responded and made permanent repairs by abandoning the service at the SMC.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2025-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TRILOGY CONSTRUCTION SERVICES | BELLFLOWER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1/2 plastic service damaged by contractor crew installing foundation for a wall, contractors had valid USA and cut back service was not marked. ETD checked service history which shows all facilities as abandoned in that area also GIS has no info on cutback service, ETD also ran a block service and none of the measurements, matched the location of the damage. Crew abandoned service at service to main contection.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2025-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CITY LIGHT & POWER | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1/2 plastic service damage by contractors installing anchor for power pole, they had a valid USA ticket, but service wasn''t marked. Crews altered service to make permanent repairs, no emergency services or media were on scene.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2025-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | NICK S PLUMBING | WEST COVINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor should be billed for damage on a 1/2 plastic service due to already being marked out. Shovel was the cause of the damage.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JOHN CIAURI | COVINA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1
Southern California Gas Company | N | LOS ANGELES | COVINA | 2025-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOME OWNER | COVINA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | ARRIVED ON SCENE, SERVICE WAS NOT BLOWING, CONTRACTOR HAD SHARPIE IN SERVICE. NO MARKS FOR SERVICE WAS PRESENT. HOMEOWNER HAS DAMAGED A 1/2 plastic GAS SERVICE BEFORE AT THIS ADDRESS. Customer was grading to pour new concrete for driveway.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2025-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | BERNICA BUILDERS | COVINA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party contractor damaged 1 PE service with a sawzall while cutting out an abandoned steel pipe.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2025-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CONSTRU ONE | COVINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging to expose 1/2inch service and hit the line with the shovel. Slice was large enough that the service needed to be altered.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2025-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | RYAN S PLUMBING | LOMITA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber should be charged for the damage due to not having a USA ticket. Plumber damaged 1/2 CTS PLA service while excavating for sewer lateral repair
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2025-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | REAUME RICHARDSON | PASADENA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party contractor dug into plastic service with backhoe while open trenching during building construction. Contractor had valid USA but did not exercise adequate caution. Service line was marked out properly. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  |  | NA | HBA HANK BLATNIK & ASSOCIATES | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor dug into plastic service while trenching to install conduit. Contractor did have a valid USA. Locate was on mark, contractor simply failed to exercise adequate caution while digging. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HBA HANK BLATNIK & ASSOCIATES | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3RD PARTY DAMAGE , CONTRACTOR HIT 1'''' PLASTIC SERVICE WITH HANDTOOL 3RD PARTY CONTRACTOR FAIL TO EXPOSE GAS LINE
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 59 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | COR DESIGN BUILD | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 plastic riser while grading. Contractor did not have a valid USA. Fire department was on scene but departed upon arrival of ETR. There was no police, road closures, evacuations, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2025-08-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | GREGORY DAVIS & ASSOCIATES | CULVER CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into 1 plastic service with post hole digger while installing beam for new fence. Contractor Did Not have a USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2025-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | ROBERT ALAN CONSTRUCTION | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor digging trench for wall footing damaged 1 plastic service with excavator. Contractor did have a valid USA. Fire department closed off street and evacuated building until gas was under control by company crew. Crew made permanent repairs. There was no news media on scene. ETD was given a note to file by Crenshaw supervision due to mismark.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2025-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | INNOCENTI CONSTRUCTION | CAMARILLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor struck plastic service while open trenching to install water lines. Contractor had a valid USA ,locate was marked out correctly but the contractor failed to exercise adequate caution. Contractor arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2025-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | INNOCENTI CONSTRUCTION INC | CAMARILLO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor dug into 1/2 plastic service. Locator incorrectly marled out the service. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2025-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ANDREW EVERSON CONSTRUCTION | CULVER CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into 1/2 plastic service while remodeling house and digging up foundation of house. Contractor did not have a USA. Crew arrived on scene, performed pressure control and altered service.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2025-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | INNOCENTI CONSTRUCTION INC | CAMARILLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor dug into 1/2 plastic service while trenching to install water. Contractor had valid USA but did not dig with caution. Crew arrived on scene, performed pressure control and altered service.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2025-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1494 |  | 1 |  | INNOCENTI CONSTRUCTION INC | CAMARRILLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor dug into plastic service with excavator. Crew reported to scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2025-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | INNOCENTI CONSTRUCTION | CAMARILLO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd Party contractor failed to pothole SVC hand dig svc. contractor had an expired USA ticket hit 1/2 CTS marked outside of 24 tolerance. sat down with ETD and had a couching conversation and will me on the job with ETD.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2025-05-29 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3644 |  | 5 |  | INNOCENTI CONSTRUCTION | CAMARILLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3RD party contractor failed to pothole 2 main Broken and Blowing : 3rd party Damage. Contractor Bored and hit center of 2'''' Plastic main, contractor claims done by damaged by clay spade.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2025-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JDC SIGLO CONSTRUCTION | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor dug into plastic service with shovel. Crew responded to scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2025-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | OROZCO CONTRUCTION | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging with clay spade to install wall and steps hit our 1/2 plastic cts service causing leak. Contractor then burried the damaged line with dirt causing migrating gas to the foundation of the house. ETR evacuated 4 ppl from 1 house. No USA was called in for this job. ARCOS was answered by Industry LCT Erik Valdez and Alhambra CT Aaron Bennett. Crew dug up the leak, controlled gas and made permanent repairs by cutting out the damaged section and installed 1'' of cts and two couplings. Located out the service before they left and R&R''s were completed by CS.
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2025-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 50 | 47 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  |  | NA | ROBERT ALVAREZ MARCADO | DIAMOND BAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit neighbors branch line attempting to grade property line, bent steel service but no leaks. No USA was requested for this job. Pasadena OHS crew arrived, completed leak investigation and then rewrapped damaged portion of steel. email was sent out to the district to have them do a service replacement.
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2025-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 47 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | HOME OWNER LAWRENCE & STEVE OWNER/BUILDER | DIAMOND BAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit line damage by contractor. SCG marked correctly . Crew arrived and repaired damage service line .
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2025-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RAMON BLANCO | DOWNEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging for water line on Tuesday and hit our gas line with a shovel. He got a clamp and stopped the leak. His wife called the next day as she was not comfortable with the repair. No gas was escaping when we arrived.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2025-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MANHOLE ADJUSTING INC | PICO RIVERA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Manhole adjusting inc., working for onxy paving, was digging to install a sleeve for a valve for a water hydrant as the street has recently been paved. Neither company had USA and they hit our plastic service with a shovel.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2025-07-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JUAN GODINEZ | DOWNEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Mini excavator damaged 1/2 plastic service while digging for sewer. No USA.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2025-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1678 |  | 3 |  | EAGLE PLUMBING | CARSON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit line while digging trench for water
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2025-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | WILLIAMS PIPELINE CONTRACTORS | MISSION HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | broken and blowing service supplying meter 13636917 Arthurs Restaurant
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2025-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 12 | 12 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | GRP CONTRACTORS | BUENA PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party damage. Operator using backhoe pulled out 3/4 steel service while working to replace a sewer section. No injuries, no fatalities, no media, no street closures, no police, no fire dept, no evacuations. Sean O''Connor (damage prevention) arrived and gather all information and pictures regarding the damage.
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2025-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  | 0 |  | RED CONSTRUCTION | FOUNTAIN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while trenching hit 2 in plastic service. No meters installed yet .
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2025-09-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | ROD PAZ BROS | ROSEMEAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor doing work for California American Water to repair a leak on their water main hit our 2 plastic main with a large backhoe. They did have an active USA that they called in as an emergency L&M. The LCT/locator completed locate and told contractors that is was a 2 plastic main within their work area. Later that evening the contractors found 2 steel and assumed that was our main. They did not call or dig more to verify and began to dig with backhoe, hitting our main. Pas OHS crew and Alhambra crew arrived, dug two control holes to pinch on each side of the damage. They made repairs by cutting out the damaged section and installed 1 1/2'' of 2 plastic and two electrofusion couplings.
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2025-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MANUEL NIETO | EL MONTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged 1/2 plastic service while excavating with hand tools. No USA
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2025-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 24 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | 3 SIXTY INNOVATION | SAN DIEGO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INSTALL COMMUNICATION CONDUITS
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TCDC TRI COUNTY DEVELOPMENT AND CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid USA, correctly marked. While digging with backhoe, contractor pulled 1 service. FD first on scene. Due to an overabundance of caution, FD closed Grand Ave from N Sepulveda to Illinois st before crew arrived.
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | HP COMMUNICATIONS | COMMERCE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | while trenching for telecommunications, contractor struck 1/2 PLA service with backhoe. Valid USA, Service was mismarked due to locate signal jumping.
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2025-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 24 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | QUERCUS CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was hand excavating trench with shovel to install water line when they struck our 1/2 PE gas service. No USA, contractor at fault.
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2025-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1766 |  | 1 |  | UNKNOWN | EL SEGUNDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Tenant claims irrigation was worked on recently by owner and had been smelling gas for past 3 days. Per Owners agent, no irrigation work was preformed.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | SHAWN AISHEL | ENCINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA, ETD found damaged 1/2 CTS by backhoe
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | INDEPENDENT CONTRACTOR | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating without a valid USA. The contractor hired an independent operator to excavate to line up new gutter and sidewalk at a new residential construction site. The operator stuck a newly installed 1? plastic service with a backhoe when he failed to follow exaction laws. SoCalGas crew responded, controlled the release, then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | 3Q POOL | WHITTIER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating for installation of pool line, damaged 1/2 gas line with electric jackhammer, No USA for excavation. Crew arrived, controlled gas, and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CARUSO S CONSTRUCTION INC | SHERMAN OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging a trench customer struck plastic service line with backhoe. crew showed up and made permanent repairs NO USA
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | NA | ENCINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging trench to install drain when they struck plastic service line with shovel. NO USA
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | SOUTHBAY INDUSTRIAL SERVICES | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Licensed 3rd party contractor was digging to install new sewer line for ADU, while in the process of digging, he hit the 1/2 plastic gas service with a shovel. No USA for excavation. Company crew arrived and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ADRIAN GAUTHIER | CHATSWORTH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Property owner son and hired hands were working with a valid USA. The property owner son was using a backhoe to excavate for the sewer line. While in the process, the homeowner son struck a 1/2'' plastic service. He then bent it back and taped it up with electrical tape to minimize the release.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 0 |  | YOHAI PINTO | ENCINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was grading on lot to rebuild house when they pull inserted cts service. crew showed up and made repairs. NO USA
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | MLADEN BUNTICH CONSTRUCTIN CO INC | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor crew working for the city of Los Angeles, performing work to locate water leak. While prospecting in private property at 3715 Valley Meadow Rd, contractor crew was using t-handle probing tool to locate underground facility. In the process, crew pierced through 1/2 IPS gas service, causing uncontrolled release of gas. SCG crew arrive on site, controlled gas and made repair via socket fusion repair.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | HOMEOWNER | ENCINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3 party damage. Contractor was digging trench for pool line when damaged half inch service. Contractor was digging with NO USA. LCT dropped back in trench and pinched 1/2 service. Used two couplings along with two feet of half inch plastic pipe for final repair.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-12-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | 4759 FIRMAMENT LLC | ENCINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A ï¿½ plastic service was damaged during sewer lateral excavation by an excavator; no USA markings were present. The building had been demolished, and sewer work was in progress. No personnel were onsite at the time of damage. The issue was reported by Field Planner Charles Shack, who noticed it while in the area. The service was tied back and not blowing. Customer information was retrieved from SAP using a previous contract application.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DAFNA LAHAV DESIGNS | SHERMAN OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating without a valid USA. the contractor was excavating, and they struck a 1/2plastic service with a backhoe while excavating. The contractor was using the backhoe for residential dwelling construction work so they could excavate the location they were wanting to place footing. SoCalGas crew responded and cutback the service to a location that would be away from where the work was being performed. The contractor was informed that they need to contact a planner to get the service line abandoned.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TRIKOLI DEHJANVHI | ENCINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging trench when they struck plastic service line with shovel. No USA
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-02-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LADWP | NORTH HILLS | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | LADWP dig in to service, Valid USA, mismarked by 3''
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | OTONIEL RODRIGUEZ | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was performing trenching operations to tie in new sewer lateral service. Struck 1/2 IPS gas service with shovel, causing uncontrolled release of gas.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2425 |  | 11 |  | ANDERSON PLUMBING | HIGHLANDS RANCH | CO | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber damaged 1/2 IPS service while digging trench for sewer repair. Plumber did not have a valid USA. There was no fire department, police, news media, road closures, or evacuations on scene. Crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 0 |  | DREYFUSS CONSTRUCTION | CULVER CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Dreyfuss Construction performing electrical trenching for new building construction. While excavating with backhoe, Dreyfuss Construction team severed 1 PLA gas service, causing an uncontrolled release of gas. SCG Distribution crew controlled gas and made permanent repair by altering 2'' section of pipe via socket fusion.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | FARAN SUN DESIGN | ENCINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Faranak Bahrami, owner and operator of Faran Sun Design, was performing grading operations for new driveway and parkway restoration. While driving a steel stake into the ground to run a string line, the 3/4 STL gas service was struck, causing an underground release of gas. Workers on site noticed the smell and bubbling of water directly adjacent to the area of intrusion. SCG crew arrived on site, pumped water from excavation site and permanently repaired leak via full encirclement clamp and installed 17# anode.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2025-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | UNLICENSED CONTRACTOR | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Unlicensed 3rd party contractor was digging trench for water. He hit gas line thinking it was a water line. No USA for excavations. SoCalGas crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2025-06-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | UNKWN | GARDENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Customer hit 1 Pla service twice. Both time cust put a clamp on service. Replaced damaged sections.
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CEA ENTERPRISES | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching with mini-excavator to install sewer lateral when they struck our 1/2 plastic gas service. No USA, contractor at fault.
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2025-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | E & M TREE SERVICE | GARDENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit cross-lot branch while installing fence post.
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2025-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1865 |  | 5 |  | JA SALAZAR CONSTRUCTION | LA HABRA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party contractor (Golden State Water Company) was hand excavating hole with shovel to repair leaking water service when they struck our 1/2 PLA gas service. Water company did not wait the required 48hrs prior to excavating. Contractor at fault.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | KARLO AZARYAN | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hired help to excavate a trench for a sewage line. Worker damaged 1/2 plastic CTS with shovel. Fire Dept departed on arrival. No valid USA.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | ARBI | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging for footing pour when they struck plastic service line with shovel NO USA
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | J DE SIGIO CONSTRUCTION | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor for GWP hit our 1/2 plastic service. Valid USA and damage occurred within tolerance zone. USA markings were visible. Contractor struck service while exposing it by hand digging and thought it was a root.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | RAFFI KHAMISIAN | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3 party contractor was digging with EXPIRED USA, when damaged 1/2 plastic service, Crew dropped back dug control hoe used 2 couplings along with 2 feet of 1/2 CTS pipe for final repair.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-12-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DISCOUNT PAVING | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging for sewage line. 1/2 Adyl-A had grown tree root wrapped completely around service line. Contractor cut root and severed service line. Contractor plugged service line with branch. There was no USA
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MANNY | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3 party damage. Contractor was digging trench for unknown utility when damaged half inch service. When arrived service was hissing contractor put clamp on service LCT dropped back and pinched line used new riser and plastic coupling for final repair.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | GNR MEJIA PLUMBING | COMPTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor trenching for drainage struck our 1/2 plastic service with a shovel. Contractor did not call dig alert. Crew was able to make permanent repairs by fusion. Damage resulted in 7 outages. Customer service was onsite to restore units.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | J DE SIGIO CONSTRUCTION | GLENDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged service within tolerance zone, contractor was pot holing by hand and struck the 1/2 cts service in the process. Company crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | J DE SIGIO CONSTRUCTION | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid USA - struck within markings, Contractor failed to hand exposed excavation by hand down to their proposed pipe installation depth. Contractor hand exposed a shallow unknown steel pipe and assumed it was the gas service. This is the 2nd damage within a month, Damage prevention is aware, company crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | INCREDIBLE PLUMBER | RESEDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA, 1/2 CTS gas service was found cut and bent back. How damage happened is unknown, but work was being performed by a hired plumber to who replaced water houseline for property owner. Damage happen inside the plumber''s excavation that took place. Plumber denied damage, property owner was unaware of damage. Company crew made repairs needed.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-04-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | Z AND A PAVING CONTRACTORS | PANORAMA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage to company property, 3 party damage. Contractor was digging trench for power line when damaged 1'' plastic service. Service was marked out contractor failed to expose service. LCT used two couplings along with two feet of PE pipe for final repair.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-09-10 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | TEICHERT | ONTARIO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damage to company property 2nd party damage, Contractor was boring in 2'''' PLA main when 1 plastic service was damaged. Contractor swept the direction of bore and didn''t pick up the crossing service. Crew dropped back dug control hole, pinched service and used 1'' of 1 plastic pipe along with 2 plastic couplings for final repair.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PACIFIC OUTDOOR LIVING | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor struck service line with excavator. NO USA
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | BRIGHTSIDE ELECTRICAL AND PLUMBING | LOS ANGEKES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating without a valid USA. The contractor was excavating install a new drain line for a Whole Foods Market well in the process, of excavating, the contractor struck a 1 inch plastic service with a backhoe.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ALL CLEAR PLUMBING & ROOTER | SYLMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3 party damage. 3 party damage contractor was digging with NO USA when damaged half inch plastic service. Crew dropped back pinched service, used 2 feet of 1/2 plastic IPS pipe along with 1/2 IPS plastic pipe for final repair.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2025-07-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | AEGIS | HUNTINGTON BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on water line had USA for another location at property and decided to dig in an un-delineated location where there were no marks for 2 PLA main. Dug control holes to get gas under control to main repair on main by altering damaged portion.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2025-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 56 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JM CONSTRUCTION | LAKE ELSINOR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service line with clay spade. They did not call dig alert.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2025-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | JM CONSTRUCTION | LAKE ELSINORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor was trenching over plastic gas service to install a brick wall and ended up putting a metal stake through 1/2 plastic gas service. The gas service was already marked out with paint and flags from previous damage a few days before. This was the 2nd damage within days.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2025-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 10 |  | SWE | GLENDORA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit line while digging to install a new sewer line. 1/2inch service was hit with a shovel
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2025-12-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | STAN TEC | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Crew from Stan Tec were performing coring operations and auguring by hand when they hit plastic service line. Crew dropped back and abandoned the line at the smc.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2025-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | RODRIGO TEODOCIO | GLENDORA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2inch plastic service hit while contractor was digging to install gas houseline for ADU.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2025-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | CITY OF GLENDORA WATER DIVISION | GLENDORA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water company hit the service while excavating a water leak. Service was stopped off at the main and replaces once the water was pumped out of the excavation.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2025-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RUSS PERSHING | SAN DIMAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Construction site 1000 N Grand, Digging New Trenches for Electric and Gas using Mini Excavator and shove. Hit 1/2inch service to 920 N Grand.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2025-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 45 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  |  | NA | RODOLFO HERRERA | GRANADA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Upon arrival the technician found that despite the customer''s contractor making contact with our gas service, it did not cause any damage to our facilities. The technician confirmed no damage to the service and no leaks were present. The technician surveyed the area and did not find any indications. Underground samples were negative.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2025-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | FRANK BASILE | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor struck plastic service with a pick when digging near service line NO USA
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2025-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HRATCH ROGER SOUKIAZIAN | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, dig in with pick axe while excavating for sewer.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2025-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOME OWNER | GRANADA HILLS | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | While digging to install drain worker struck plastic service with shovel. marks where visible and contractor had struck line day before also. USA ticket wasn''t valid
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2025-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | US ELECTRICAL | GRANADA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service with shovel while digging up electric conduit. Contractor did have a valid USA and service was marked with flags and paint. There was no emergency services on scene. Crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2025-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | RAZMIK HAKOPIAN | GRANADA HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Mr. Hakopian is performing trenching operations for ADU electrical upgrade. While hand excavating with shovel, he struck the 1/2 IPS gas service, causing an uncontrolled release of gas. Mr Hakopian informed me the marks provided by SCG were not accurate to where the gas line was struck. SCG crew arrived on site to control gas and perform permanent repair via socket fusion alteration of 1'' section of pipe. A jobsite audit revealed there were marks in the paved concrete about 30 from the gas facility damage site. STL riser had no wire to locate PLA service. Riser across the street also had no locating wire. Pipe in ground had no locating wire. There were locating flags in earth area where trench was excavated, but they were no longer standing and had been pulled, tossed to the side. Unable to confirm if those flags accurately marked the gas line.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2025-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | RICARDO LOPEZ | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging trench for ADU. While excavating with pick, crew struck 1/2 CTS gas service causing uncontrolled escape of gas. SCG crew on site to make permanent repairs via socket fusion and replacing riser
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2025-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARMEN GABRIELYAN | GRANADA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor digging a trench with shovel. Contractor working with home owner. No USA.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EDGAR MALCA | SHERMAN OAKS | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | contractor struck plastic service with shovel. no valid USA
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2025-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CAROLINE HACOPIAN | GRANADA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor struck service while doing some land scaping work, crew showed and made repairs NO USA
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2025-01-24 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 4 | 45 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LADWP | NORTHRIDGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP was out replacing a leaking ater main when they pogoed through gas main with pogo. gas pipe was properly marked and with in delineation
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2025-09-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25001 |  |  | NA | GR CONSTRUCTION | GRANADA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging a trench for DWP to install a water line. while trench contractor struck 2 plastic main with excavator. crew showed up and dug control hole and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | H/O TATINTSYAN | GRANADA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while digging to install sprinkler line in yard customer struck plastic service with shovel. had a USA and was marked out in yellow paint
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2025-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MODERN CREATIONS CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA. Contractor damaged 3/4 service with jack hammer while breaking concrete on private property.
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2025-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | L AKMAKJIAN | HACIENDA HEIGHTS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer lied and stated that they smelled gas, but leak investigation showed a hole was dug and dirt replaced at high read spot. shovel marks at damaged area. No USA called for this work. Pasadena OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installed 2'' of cts and two cts couplings.
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2025-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SUPREME REMODELING | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2/IPS service while digging a trench to install a drain. No USA was called.
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2025-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ANDY S POOLS INC | ORANGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 3/4 steel service with bobcat while grading the driveway area, no USA was called in. service was not leaking but was damaged.
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2025-01-13 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 57 | 47 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SOCALGAS | CITY OF INDUSTRY | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | 1st party damage, 3/4 steel service damage by Company crew. Crew was attempting to replace a service, which they had exposed. The service dog legged under the gutter, which was unexpected, this resulted in the crew striking the service damaging serviced tee weld.
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | OHLA USA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damaged 1 1/4 inch steel service with excavator while digging a trench, the service was properly marked and USA was valid.
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2025-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 16 |  | FRANKIE | HAWTHORNE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While trenching for electrical, contractor hit pla line with pick
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2025-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | HONEY CANT DO HOME IMPROVEMENT | LAKEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging for fence post, contractor hit pla line with shovel. No USA
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2025-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GRBCON INC | BALDWIN PARK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractors accidentally damaged 1/2-inch IPS service while excavating to expose service in order make sewer repairs. USA was expired. Service was marked.
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2025-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | HARDY AND HARPER | LAKE FOREST | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While digging up sidewalk, contractor pulled 1/2 CTS line. Valid USA, Service unmarked.
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2025-09-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | RIGHT ANGLE BUILDERS | REDONDO BEACH | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor was hand excavating hole with shovel to install concrete footing when the struck our 1/2 PE gas service. Expired USA, contractor knew our service was there and struck by accident. Contractor at fault
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2025-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was machine excavated trench with backhoe to install water main when they struck our known / marked 1/2 PE gas service. Contractor admitted the spotter / operator forgot the service mark was there and accidently struck service. Contractor at fault. USA was valid.
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor (WAR Construction) was machine excavating trench with backhoe to install water when they struck our known / marked 3/4 steel service. USA valid, foreman admitted they knew marking was there but forgot while excavating. Contractor at fault.
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2025-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | STF CONCRETE | REDONDO BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit pla line with shovel
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2025-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2331 |  | 10 |  | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor (WAR) was machine excavating trench with backhoe to install water main when they struck our unmarked 1/2 PLA gas service. USA valid.
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2025-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | GRB CON | BALDWIN PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Will address with locator in an effort to mitigate miss marks.
Southern California Gas Company | N | LOS ANGELES | HIDDEN HILLS | 2025-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | DAVID MANSOR | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, dig in by 3rd party while digging for sewer
Southern California Gas Company | N | LOS ANGELES | HIDDEN HILLS | 2025-08-07 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 1 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | BLACKBIRD MANAGEMENT | CANOGA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while digging with excavator, contractor struck 1 plastic service. crew showed up and made repairs. flags where visible and somewhere covered up from excavating
Southern California Gas Company | N | LOS ANGELES | HIDDEN HILLS | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BLACKBIRD MANAGEMENT | CANOGA PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was grading with large excavator; while digging, he hit 1 plastic stub. USA was valid. No Tracer wire on plastic stub and did not show up on map. Crew arrived and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | HIDDEN HILLS | 2025-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | MICHAEL LIBRUSH | HIDDEN HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor building new construction, hit gas line with backhoe while digging, causing gas leak. Crew responded and cut back service due to degraded pipe integrity. No USA for work.
Southern California Gas Company | N | LOS ANGELES | HIDDEN HILLS | 2025-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PV ELECTRIC INC | HIDDEN HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor''s employee was digging to install power lines for house generator when he struck plastic line with shovel. crew showed up and made permanent repairs. NO USA
Southern California Gas Company | N | LOS ANGELES | HIDDEN HILLS | 2025-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MEGA CONCRETE | CALABASAS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor, hit line while grading with bobcat NO USA
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | JUDINA AKE | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into 1/2 plastic service with hand tools. Contractor has NO USA. Crew arrived on scene, performed pressure control and altered service.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | JORGE VASQUEZ | INGLEWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant was working on property and stated he was moving some dirt and trash from property in the process of doing this they hit and damaged 1/2 plastic service, Occupant had no USA.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | ESCOBAR CONCRETE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA .....Alter Service Immediate. 3rd Party Damaged , Crew excavating to Abandon water service cut trough 1/2'''' IPS plastic service no EFV. city of Inglewood public works inspector on-site claims contractor is working on a blank permit contractor Escobar Concrete.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | D & A HOME RENOVATIONS | INGLEWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line caused by third party contractor. Crew arrived on scene, performed pressure control and altered service.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-06-10 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor hit 2 plastic gas main with shovel while digging to install conduit. Contractor had a valid USA. Main was marked out properly, contractor did not exercise proper caution while digging over the main. Crew arrived on scene, performed pressure control and altered the main.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | H7 CONTRACTING & ENGINEERING INC | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole gas svc hit 1/2CTS with backhoe locate was on make ,crew arrived and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | NA | INGLEWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA Owner was digging sewer line and mistaken gas line for water line due to PLA service inserted inside copper line
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1848 |  | 4 |  | ARMANDO BORGEZ | INGLEWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner hired plumbing company to repair sewer when the plumber damaged a 1 plastic service while trenching. NO USA was called in by the plumber. Crew arrived and repaired the damaged section and reinstated the service.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | JV LAND CLEARING | SAN DIMAS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Private contractor dug into steel service with backhoe while performing demo and grading work. Contractor had a valid USA, did not use caution while digging. Crew arrived on scene, performed pressure control and cut back service.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | JV LAND CLEARING | AZUSA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party contractor dug into 3/4 stl service while performing building demolition. Contractor was working under an expired USA ticket. Markings were still correct. Crew arrived on scene performed pressure control and abandoned the service at the smc.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | ANTONIO AMBRIZ | INGLEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into service with shovel while trenching on private property to install water line. Contractor did not have a valid USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALLIANCE | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug in 1/2 cts service while doing house demo. Contractor Did Not have a USA. Crew arrived on scene, perfromed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2238 |  | 9 |  | CMJ CONSTRUCTION | INGLEWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit service with electric clay spade while installing house line. NO USA
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | SHINE INVEST DEVELOPMENT | MANHATTAN BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into 1/2 cts service while digging to replace sewer line. Contractor DID NOT have a valid USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1771 |  | 4 |  | WILLIAMS PIPELINE CONTRACTORS INC | MISSION HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor dug into 1/2 inch ips service while trenching to install water lines. Contractor had active USA but did not use adequate caution while digging. Crew responded to scene, performed pressure control and altered service.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WILLIAMS PIPELINE CONTRACTORS INC | MISSION HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor dug into 1/2cts line with backhoe. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WILLIAMS PIPELINE CONTRACTORS INC | MISSION HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor dug into 1/2 plastic service with backhoe. Crew responded to call, arrived on scene, performed pressure control and altered service.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 43 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | TRENCHERS WEST CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 3rd party contractor was working on the street in the process of trenching 3rd party contractor hit an unknown stub, 3rd party contractor was digging outside of delineation
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2025-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  |  | NA | CUTTING EDGE CONCRETE CUTTING | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor cut into 3/4 stl service while saw cutting. Contractor had a valid USA. Service was marked out correct and visible, contractor just failed to exercise adequate caution. Crew arrived on scene, performed pressure control at the SMC and altered the service.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2025-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JG & SON CONSTRUCTION | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Found broken and blowing 1/2 cts service, contractor grading to install driveway hit service in casing and split it in half. No USA called in for this job. PAS OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installed 2'' of cts plastic pipe and two cts couplings.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | JP ELECTRICAL SERVICE | RESEDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3 party damage. Contractor was digging with NO USA when damaged a 1 plastic service. Contractor was digging a trench for power when plastic service was damaged. LCT dropped back pinched line used 3 of 1 plastic pipe along with 2 1 plastic couplings for finale repair.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2025-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JUN HEO | LA CANADA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3rd party damage contractor was digging with no USA while digging trench for water service when damaged half inch plastic service. LCT used two couplings with one foot of half inch plastic pipe for finale repairs.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2025-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ADRIAN GUZMAN | PALMDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA Ticket, 3rd party excavator damaged 1/2 Plastic SVC. Line was hit with a mini excavator while trenching for a foundation re-enforcement. Company crew made repairs needed.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EFRAIN LUNG | ALHAMBRA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber was digging to install a new sewer cleanout. Plumber found steel casing and cut with saw-zaw damaging 1/2 Adyl-A. There was no USA.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2025-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CERVANDO | LA CANADA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was grading and digging with bob cat to install a wall. Contractor hit the 3/4 steel standard and branch also dropped the neighbors service. No USA
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2025-04-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CRESCENTA VALLEY WATER DISTRICT | LA CRESCENTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while backfilling over water main project. company poured sand on top of service line and broke line at coupling from the weight
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CRESCENTA VALLEY WATER DISTRICT | LA CRESCENTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage to company property, water company failed to expose plastic service when digging trench for water main. valid USA marks were visible. Crew arrived dropped back pinched line then used two 1/2 IPS couplings and 2 feet of IPS PLASTIC PIPE for final repair.
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2025-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | ESPINOSA DEMOLITION & HAULING | LA CRESCENTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | company was digging to install conduit for an ADU when they struck plastic line with excavator. there was a USA ticket and the marks where with paint and flags. service was marked out correctly
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CRESCENTA VALLEY WATER DISTRICT | LA CRESCENTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Municipality was trenching to replace water main. An excavation was made to expose the gas service but the incorrect pipe was exposed. Gas service was not daylighted, a backhoe was being utilized within tolerance zone and damaged the gas service. Repairs were made by company crew.
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2025-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | HECTORS TRANSPORT & DEMOLITION | SYLMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging with excavator for sewer line and damaged 1/2 CTS in casing. There was no valid USA. Contractor called USA after permanent repairs were made by SoCal Gas crew.
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2025-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | ARMAND YEGIYANTS | LA CRESCENTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hired contractors to grade and remove debris from front yard. Contractors struck 1/2 service in casing. There was no valid USA.
Southern California Gas Company | N | LOS ANGELES | LA HABRA HEIGHTS | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | J & M LEYVA GENERAL ENGINEERING | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party damage 1/2 cts stub hit with directional bore. Crew had to drop back and pinched stub and capped. No evacuations, no media, no police, no fire dept, no street closures, no injuries, no fatalities. Pictures and information was taken on scene.
Southern California Gas Company | N | LOS ANGELES | LA HABRA HEIGHTS | 2025-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  | 0 |  | FM CONSTRUCTION | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | CONTRACTOR CUT THROUGH LINE WITH SAW THINKING IT W AS ABANDONED.
Southern California Gas Company | N | LOS ANGELES | LA MIRADA | 2025-11-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | WESTERN SUPREME ROOTER | ARCADIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit service while trying to repair the sewer.
Southern California Gas Company | N | LOS ANGELES | LA MIRADA | 2025-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PAREDES CONSTRUCTION | HACIENDA HEIGHTS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Electrical contractor with valid USA trenching damaged with shovel plastic service. Marks bad due to incorrect GIS. very bad signal, no wire, marked measurements. GIS update request
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2025-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | GUSTAVO TORRES | LA PUENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged 1/2 CTS service with mini ex while digging trench for block wall. USA was not valid.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2025-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 2 | 50 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BALFOUR BEATTY | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged/gouged a 2 inch plastic service elbow while using drilling attachment to make a hole for a bollard installation with no USA. Pasadena OHS crew arrived and made repairs by cutting out the damaged section and installed 2'' of 2 inch plastic, 1 2inch elbow and 1 2inch coupling.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2025-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4017 |  | 9 |  | CITY OF INDUSTRY | WEST COVINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water Co. contractor struck 2 plastic main with backhoe.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2025-06-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | NA | LA PUENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call in USA, began excavating for installation of new fence. Ripped branch service in half.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CELESTINO CRUZ | NORWALK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractors trenching for new addition to house undermined retaining wall which fell and snapped service. No USA was called in for this job. Pasadena OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installed 3'' of IPS, two IPS couplings and 1/2 IPS riser.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2025-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NA | LA PUENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner trenching for water line damaged our 1/2 IPS service. No USA was called in for this job. ARCOS called out was made and and crew was sent to eliminate Code 1 and make repairs. Crew arrived, controlled gas and made permanent repairs by cutting out 1'' of IPS and fusing in 1'' of new IPS and two couplings.
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2025-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | JIM HANNAN | LA VERNE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Leak caused by dig-in. Buried facilities hit while exposing it by hand digging by home owner.
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2025-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | MIGUEL GARCIA | LA VERNE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2inch service line on private property. No USA was called before digging.
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2025-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | G LANDSCAPING SERVICES | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 IPS Plastic Service struck by 3rd party contractor with a mini-excavator while digging for retaining wall installation. Excavator struck service while trying to remove tree root.
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2025-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HORIZON UNDERGROUND | NORCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor failed to hand dig near gas line. While the line did 90, the damage occurred right where the marks were painted and within the 2 foot zone. Crew dropped back for safety and found gas line encased in steel, squeezed and did repairs.
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2025-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  |  | NA | FERNANDO FRANCO | LAKEWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner trying to expose sewer to make repairs using a chipping gun damaged our 3/4 service. Crew repaired service with a clamp.
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2025-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 38 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BRIAN | LAKEWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 plastic service hit with backhoe while digging trench to replace sewer.
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2025-08-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CARLOS CERVANTES | REDLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor stuck 1/2 plastic service with shovel No gas was escaping just damage to the pipe
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | GUADALUPE FLORES | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage service by customer NO USA
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HOT LINE CONSTRUCTION | BRENTWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit service while installing conduit. Crew arrived and it appears that damage was caused by faulty locate wire. Verified by crew leader.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | B&L AUTOMATIC FIRE PROTECTION | LANCASTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew did cutback on service/ cust will be calling for alter soon. Service was marked in the correct location
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | ORANGE TRENCHING & PAVING | LAKE ELSINORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while potholing Crew repaired with 2 couplings and a piece of pipe
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-11-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 0 |  | I KHARMA | LANCASTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaging party gave Hotlines ticket number. Crew believes it was not Hotline. Crew said looks like they were doing footing for a wall. All information listed is for the homeowner. Damaging party would not give any information.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOT LINE CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator said no signal, called lct and there was no wire on service.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ALARC CG | ROSAMOND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with excavator to install new sewer line for adu. They hit the service while digging. Contractor had dig ticked from September of last year long expired and no remark was called in. Crew was able to make repairs with couplings and pipe.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JUAN CARLOS ARANA | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party damaged. Homeowner damaged 1/2 plastic service, No USA called in for this job.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-08-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 6 |  | JACOBSSON ENGINEERING CONSTRUCTION | THOUSAND PALMS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit main. No Gas Co marks were in place USA was valid
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | SKJ ENGINEERING | LAKE HUGHES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | CONTRACTOR HIT MARKED SERVICE ON AN EXPIRED TICKET
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | NO LIMIT | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged 1/2 service with shovel while excavating. Crew replaced damaged section of service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  | 2 |  | ALLEN LIGHTING SERVICES | COLTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 IPS service damaged by directional drill valid USA marked accurately Contractor potholed 2'' outside of drill area potholed incorrectly.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 23 |  | LANDSCAPE CONNECTION GROUP | LANCASTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service while doing irrigation repairs. Crew repaired 1 service NO USA
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-12-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 0 |  | INTERTEX GENERAL CONTRACTORS | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR HIT 2 SERVICE WITH EFV NO USA
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DOUBLE G POOLS | LANCASTER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Contractor digging trench for wall footing damaged 1/2 IPS service with excavator. Damage occurred in front of property. Contractor did have a valid USA, but dug outside of delineation. Work area was delineated for backyard pool and spa build. Fire department was on scene but departed when ETR was on scene. There was no road closures, evacuations, police, or news media on scene. Crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | TE NEWTON COMMERCIAL PLUMBING | LANCASTER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit service with mini backhoe. Crew arrived and was able to make repairs.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ALEJANDRO SANCHEZ | LANCASTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged service with jack hammer
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-05-21 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | WOLVERINE GENERAL ENGINEERING | PALMDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR WAS DIGGING W/ SHOVEL, INSTALLING WATER LINES WHEN THEY HIT GAS MAIN. CREW ARRIVED AND MADE REPAIRS.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DESERT PLUMBING | AGUA DULCE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit service while hand exposing
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3983 |  |  | NA | MTZ BUILDING SOLUTIONS | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service with backhoe No USA
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2025-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ERIK VIAMORE | ROSAMOND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service at riser. No USA and no Contractor license found
Southern California Gas Company | N | LOS ANGELES | LAWNDALE | 2025-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | SAUL GONZALEZ | INGLEWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was hand excavating trench with shovel to install sewer lateral when they struck our 1 inch plastic gas service. No USA, contractor at fault.
Southern California Gas Company | N | LOS ANGELES | LAWNDALE | 2025-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2145 |  | 8 |  | KORD FIRE PROTECTION | SHERMAN OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install new sprinkler system, contractor hit PLA line with shovel. No USA
Southern California Gas Company | N | LOS ANGELES | LITTLEROCK | 2025-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | JESUS CORTEZ | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3 party damage. Homeowner had 3 party contractor digging trench for landscaping when half inch plastic CTS service was damaged. Contractor was digging with NO USA. Crew dropped back dug control hoe, used 2 feet of CTS plastic pipe along with 2 CTS 1/2 couplings for final repair.
Southern California Gas Company | N | LOS ANGELES | LOMITA | 2025-08-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GBS GENERAL | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 service damaged by contractor who was exposing service to properly shade with sand instead of dirt, No USA called in. Crew altered service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOMITA | 2025-09-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RAUL FRANCO | LOMITA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged 1/2 IPS service with hand tools while digging for sewer. There was no valid USA. There was no emergency services, road closures, evacuations, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CHRIS & LEO S TREE SERVICES | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party did not have a valid USA. Damaged a plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The service was mismarked due to inaccurate measurements provided by service history. After potholing and failing to find the service, the contractor did not recall the USA ticket for additional SCG markings. Instead, excavation continued approximately ten feet away from the original mark, directly in front of the address. Contractor mentioned that is best practice per his company.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LA DEVELOPING INC | HUNTINGTON PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into 1/2 inch plastic service with excavator while trenching in private property with no USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WARNER TECHNOLOGIES | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging on property to install a new retaining wall in the process of digging 3rd party contractor hit and damaged 1/2 inch plastic line, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 9 |  | FLAMINGO CONSTRUCTION | STUDIO CITY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | EE failed to mark out Long side servcie, cause 3rd party damage,
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LOS ANGELES CITY COUNTY | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LA city was working to install new curb and gutter in the process of digging they scraped a 1inch steel casing that had a 1/2 inch plastic line inside, crew went out and checked line noticed there was no leakage or damage to the line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SHAWN LUONG | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA hit line caused by 3rd party contractor, made permanent repairs
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MOORE FOUNDATIONS | RESEDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Foundation company damaged 1/2 plastic service with shovel while digging for a footing. No USA was called in by the contractor. Crew arrived and replaced the damaged section of pipe and re-instated the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 42 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP failed to pothole service line before excavating with backhoe causing damage to the 1/2 plastic service. crew repaired the damaged section and re-instated the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ALL CLEAR PLUMBING AND ROOTER INC | SYLMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor dug into plastic service while excavating for sewer repair. Crew reported to scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-13 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 3 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3749 |  |  | NA | BAKER ELECTRIC | ESCONDIDO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | ARRIVED AT JOB SITE, 3 PLASTIC MAIN WAS KNICKED WITH A SHOVEL WHILE HAND DIGGING. BAKER ELETRIC WAS EXCAVATING FOR STREET LIGHTING. USA WAS NOT VALID. MARKS WERE VISIBLE AND ACURATE. DAMAGE OCCURED IN FRONT OF ADDRESS IN PARKWAY; 10787 WELLWORTH AVE LOS ANGELES. THE CREW REMOVED AND REPLACED 2FT OF DAMAGE SECTION OF 3 PLASTIC MAIN. ALTERED MAIN ON PARKWAY FRONT OF ADDRESS. EARTH CUT, EXCESSIVE TREE ROOT. DAMAGE PREVENTION WAS NOTIFIED.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LANDMARK CONSTRUCTION | ATHENS |  | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Incident was caused due to the contractor not delignating the area.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 1 |  | LA METRO | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd parity contractor damaged plastic service while excavating. Contractor did not call 811 to request for a remark due to faded locate marks and missing whiskers.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DYNAMIC GENERAL CONTRACTORS | TARZANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into 1 plastic service while digging to repair foundation of complex. Contractor did not have a valid USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  | 0 |  | AMERICAN BUILDERS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property to install new electrical lines in the process of digging 3rd party contractor hit and damaged 1/2 plastic service, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HUGO MAZARIEGO | BALDWIN PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 inch struck by contractor with a shovel. no usa called in.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | RAMZ CONSTRUCTION | HERMOSA BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property digging to install foundation in the process of digging 3rd party contractor hit and damaged 1/2 plastic service, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ACOSTA PIPELINE INC | CORONA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Third party contractor dug into 1 inch plastic service. Contractor was excavating without a current ticket. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 31 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | SHARMA GENERAL ENGINEERING CONTRACTORS | MOORPARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was excavating for new water main when they damaged a 6 PE gas main that was accurately marked and visible. Contractor damaged the line with an excavator. contractor had already exposed the gas main a few feet back and was digging directly over the main when he ripped out 3 punch tees off the top of the main. Crew arrived and dug out control holes, bypassed the gas feed to complete permanent repairs. DPA and supervision was on scene; Contractor did have a valid USA but failed to practice safe excavation methods.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ISMAEL CO | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working to install a new fence in the process of digging for new fence 3rd party contractor hit and damaged 1/2 plastic service, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PEARL FLOW ROOTER AND PLUMBING INC | SYLMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 Plastic service with backhoe while excavating without a valid USA Ticket. On Call Crew responded, controlled gas, and made permanent repairs under workorder 520004158821.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | F AND E CONSTRUCTION | LOS ANGELES | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party Contarctor strukc 1/2 plastic with jack hammer while doing demo work No Vaild USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HARARI CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party company has a valid USA, the marks per damage prevention where marked correctly. Per the LCT, the contractor damaged the plastic service with a jackhammer.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor damaged service line while trenching.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | A PIECE OF WORK CONSTRUCTION | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with trencher causing damage to 1/2 plastic service. No USA called in. Crew altered service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PETER KRASE | VENICE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging on property to install new sprinklers in the process of digging hit and damaged service, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MLB CONSULTING AND ENGINEERING INC | SUNLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Builder''s crew hit the gas line with a skiploader while grading the driveway. The service was previously cutback at property line. Crew was able to mitigate leak by doing full abandonment.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SAUL HUEZO | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property to install new sewer lines in the process of digging trench 3rd party contractor hit and damaged 1/2 plastic service 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | AXIOM GROUP | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The 3rd party contractor did not have a valid USA. The 1 plastic service was damaged while working to install a sign post.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | CSWF CONSTRUCTION | LA PUENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew was called out after hours to a leak investigate, upon arrival the LCT spoke with the property manager and found out the plumbing company had damaged the service line the day prior. the service was found kinked back and tied with tape. the crew performed a cut back at PL. Damage prevention was notified as well as district supervision. Fire department departed upon ETR''s arrival.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 1.25 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3006 |  | 2 |  | SD DANIELS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property doing construction in the process of trying to auger to install new poles, 3rd party contractor hit and damaged 1 inch steel service with Auger 3rd party contractor had no USA they called one in once they damaged the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | G & A UNDERGROUND UTILITIES | VAN NUYS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Uknown stub no records on GIS or Service history, contractor damaged the plastic stub while open trenching, ETD had main located, crew cut back unknown stub to proper stub length.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RIAAN CONSTRUCTION | WEST HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into 1/2 ips with a backhoe while grading for a new build. Contractor did not have a valid USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | SWAZI TAYLOR | WHITTIER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage with no USA, contractor damaged 1/2 cts service while excavating for grade and footing. Crew arrived on site to control gas and make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CLAUDE REDWINE | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner dug into CTS plastic service with a shovel while open trenching to install new houseline to ADU. Homeowner Did Not have a valid USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | PARKIA | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors hit 1 plastic service while digging hole to replace power pole, contractors had valid USA but failed to protect our facilities that were marked correctly and marks visible. Crew altered service to make permanent repairs. No emergency personnel on site.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP damaged 1/2 CTS gas service that was marked correctly, had valid USA, and failed to excavate safely. Crew made repairs of 1/2 CTS gas service by via service alteration.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SOCAL EDISON | COMPTON | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | SCE workers damaged 1/2 plastic service while replacing power pole in alley of address, workers called in USA but dug before legal start date. Crew altered service to make permanent repairs. NO emergency agencies on scene.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 2 | 26 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CESAR | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hand digging and hit plastic 2 service with rebar
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | 4 ECO LIVING | PLAYA DEL REY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY CONTRACTORS DIGGING TRENCH FOR GAS HOUSELINE INSTALLATION WITH MINI EXCAVATOR AND DAMAGED 1/2IPS PLASTIC SERVICE FOR 1331 THAYER. CREW REMOVED AND REPLACED 4FT OF 1/2IPS PLASTIC SERVICE. NO USA WAS CALLED IN BY CONTRACTOR
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Company crew found damage service while working on MSA maintenance order. Crew found damaged and leaking 1/2 Adyl -A with hose clamps and was wrapped in plastic. No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | JAVIER CHAVEZ | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA ..... 3RD PARTY DAMAGE.DAMAGED WHILE DIGGING HOLE FOR A FEANCE ALTER 1'' OF 1/2'''' CTS
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ALICIDES ALEMAN | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging hole in front yard to plant a tree when they struck 1/2 plastic service with a shovel. The homeowner did not have a valid USA. There was no evacuations, emergency services, road closures, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | 25 8 ACQUISITION AND DEVELOPMENT LLC | PORTER RANCH | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into 1/2 cts service with shovel. Contractor did not have USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | RON GONEN | BEVERLY HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was trenching on property with excavator to install a new sewer line in the process of trenching they hit and damaged a 1inch plastic service, 3rd party contractor did not pothole line before digging with excavator.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | RON GONEN | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer was trenching for new conduits and damaged a 1/2 ips service with a shovel. No USA was called in by the developer. Damage prevention was notified.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | QUALITY JET ROOTER INC | WHITTIER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1 inch plastic service while digging for sewer install. Service marks likely removed when contractor saw cut and removed asphalt over service location.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | EC CONSTRUCTION | LAKE ELSINORE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging trench for ADU, contractor hit 1/2 pla service with shovel. No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC STRUCTURE | VENICE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck our 1 inch service by riser while using excavator. no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1501 |  | 1 |  | WA RASIC | BELLFLOWER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor dug into 1/2cts service. Contractor had valid USA, service was mismarked. ETD hooked up to service and felt confident with locate, used GIS and service history as reference. LCT hooked up to service as well and located to same spot ETD did. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | HOME OWNER | NA |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck gas service with shovel while digging for drain line no vaild USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | IAN NOORMANT | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The third-party contractor did not call in for USA, resulting in damage to a plastic service line while digging.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MONTEJO DEMOLITION EXPERT | VAN NUYS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor was digging with a expired USA ticket hit service with backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | PLASCENCIA POOLS & LANDSCAPING | PACOIMA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 CTS service with hand tools during excavation for drain line. Contractor did not have a valid USA. Contractor was attempting to remove buried concrete with hand tools when the damage occurred. There was no emergency services, evacuations, road closures, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOSE ROSAS | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While digging for water main, crew struck service with shovel. USA current and correctly marked.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JONATHAN MARTINEZ | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors damaged 1/2 plastic line while digging trench to install new gas houseline for ADU, no USA called in. Crew altered service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LOS ANGELES HOUSING AUTHORITY | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging for water repair damaged 1 IPS service with backhoe. Contractor did have a valid USA, but failed to pothole gas service. There was no fire department, police, or news media on scene. Crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 plastic service damaged by contractors installing water main. Contractors had valid USA and service was correctly marked but they failed to protect our facilities, Crew altered service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | FIGHTER FIRE PROTECTION | CANOGA PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged plastic service with shovel. No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | REPIPE EXPRESS | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dig in our 1 IPS service with pick axe, crew alter service for repair
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | HOUSING AUTHORITY OF LOS ANGELES | LOS ANGELES | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party contractor caused damage to 1 to gas service with backhoe while digging for water line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HACLA HOUSING AUTHORITY CITY OF LOS ANGELES | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractors damaged 1 plastic service that was mismarked, locator mismarked service due to faulty locating wire signal and no map reference on GIS nor measurements on service history, I had locator came by and hooked up to verify that signal was off also had crew leader hooked up and he also got signal similar to locator around 6'' from location where service got damaged. Crew altered service to make permanent repairs. No emergency services on site.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper damaged a 1/2 plastic service while digging for new irrigation lines. Landscapers had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | CHALLENGE PLUMBING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage by contractor, 1/2 plastic service was hit with a shovel at 1614 S Victoria Ave. Contractor was digging for sewer and was digging without a USA. Company crew came out and controlled gas and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ROTO ROOTER | ALHAMBRA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Roto Rooter plumber excavated prior to valid USA start date and time. Roto Rooter plumber damaged our 1/2 plastic service with shovel while digging to replace sewer line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SERVICE CHAMPIONS | BREA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor Dug Ahead of start time hit 1/2 plastic gas service with shovel marks were visable while doing sewer reapair
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1771 |  | 4 |  | L LEE DEVELOPMENT | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck gas service with shovel while performing sewer work No vaild USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WEBER MADGWICK | CASTAIC | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Riser damaged by contractor while digging with backhoe for a new trench. Contractor provided crew with a USA ticket that was called in right after he damaged the riser. Ticket was not legal yet due to the 48 hr law. Crew replaced the damaged riser with a new riser.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | SAL AMESCUA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer pulled 1 pla service with backhoe. No USA was called.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HI TECH | CALABASAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors working on foundation work and hit 1/2 inch plastic service line in copper casing. Contractor stated they knew where the service was but still damaged our line. There was no valid USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LADWP | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP fail to pot hole for gas service before work start and struck gas service, USA was vaild and gas was mark within delineation
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RAMSEY | PACOIMA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA >>>3rd party contractor hit 1/2 CTS while digging trench for sewer with hand tools
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 44 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JORGE BARREN CONSTRUCTINO | CHATSWORTH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating for new retainer wall damaged a 1 steel service with the breaker attachment on a bobcat, crew arrived dug out a control hole and pinched the steel service. LCT welded new section of pipe. 520004120763
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | UNKNOWN | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor sturck 1/2 plastic line whith shovel while trenching for sewer No Vaild USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | SYCAMORE 2025 | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging trench for wall footing damaged 1/2 CTS plastic service with hand tools. Contractor did not have a valid USA. There was no emergency services, road closures, evacuations, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | IBARRA GENERAL ENGINEERING | LOS ANGELES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | The crew used the 2 Plastic main shut off AT valve located on the Northeast corner of Washington and Norton. - the crew used two electro fused couplings and 3 feet 2 inch plastic pipe for permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 19 |  | SUTTLES PLUMBING & MECHANICAL | SIMI VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party struck 2 inch plastic main with backhoe while trenching for sewer, EE, was off by 3 feet
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GREEN GROUNDS LANDSCAPE SERVICES | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to install a new sewer line struck gas service No USA was called
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 9 |  | IBARRA GENERAL ENGINEERING | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The third-party operator utilized a backhoe to excavate directly above the 2-inch plastic main. By doing so the 2 plastic main was damaged with the backhoe bucket. The locate and marking of the 2-inch main were accurate and consistent from Washington Street to the termination point on Norton Avenue.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FLECHA S CONSTRUCTION | LAKE ELSINORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Due to no access. The service was marked by measurements. Service history indicated that the service is 165 feet from the cross street. The Locator made contact with the contractor and marked the ground for potholing prior to excavation. A mutual agreement to pothole was made, but the pothole was not completed. However, after the damage was repaired. We found after measuring the service was found to be 155 feet from the cross street.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SILVERIO MACIAS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Installing new gas line for ADU, damaged 1/2 service while digging trench. No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TECHNICK CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was working on homeowner''s property in the process of digging to install new concrete 3rd party contractor hit and damaged 1/2 inch plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | ERIC PLUMBING | DOWNEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1'''' plastic service was damaged by backhoe while excavating to install a grease interceptor. No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor has a valid USA. EE looked up service history and epoch and both company tools at the time of the locate and damage, had not been updated.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JOEL CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on sewer lateral connection damaged 1/2 CTS service with excavator. Contractor did have a valid USA but failed to hand expose marked gas service. There was no fire department, police, news media, or road closures on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALLISON MASSEY | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor (Allison Massey LLC) hit 1/2 Plastic Service, No USA. SCG Gas Ops Crew responded, controlled gas, and made permanent repairs to service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ANTONIO CABERARA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property to repair sewer line in the process of digging they hit and damaged a 1/2 plastic service, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | BURPEE S PLUMBING | SIMI VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3 party struck 3 inch Gas Main with Backhoe while trenching for Sewer main USA was Exipred
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MANDOYAN CONSTRUCTION | ENCINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Private contractor dug into 1/2 plastic line while trenching to install sewer drain. Contractor Did Not have a valid USA. Crew reported to scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | A TO Z BUILDERS | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | During trenching to install a sewer line for a new ADU, 3rd party contractor failed to notify 811 Dig Alert, resulting in no USA markings on the project site. According to the contractor on-site, while using a jackhammer to loosen the dirt, they struck a gas service line, causing the gas to ignite. The contractor immediately called the fire department, which responded by extinguishing the flames and wetting the exterior of the home. Additionally, the crew controlled the gas leak and made necessary repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-19 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MATTUCCI PLUMBING | GARDENA | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was called out to fix drain line crew had broken the night before in the process of digging it out 3rd party contractor damaged 3/4 stl line. They had no USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | FORGEN WAY | SAN FERNANDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party company did not have a USA. The contractor damaged the 1/2 plastic service while excavating to install a gate post.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-20 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2798 |  | 15 |  | SOCALGAS | WEST HOLLYWOOD | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Project ticket for another utility company. The service could not be located using the RD8100, and the measurements from service history were inaccurate. Additionally, the Jameson tool was ineffective. A crew was dispatched to pothole for the service, but encountered numerous roots obstructing the process, resulting in damage to the plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | FLAWLESS CONSTRUCTION | TARZANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage, contractor hit a 1/2 ips plastic service with a pickaxe to 2135 Kent St., contractor had no USA and was excavating for new block wall for 2135 Kent St. Company crew came on site to control damage and make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | LUIS GONZALES | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The damage occurred within the delineated area, and the service was properly marked.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JAIME POLO | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor struck 1/2 plastic service while trenching for water line No Vaild USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | ROVELO CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3 party contractor was digging trench for demo of home with NO USA when damaged 3/4 STL service. Crew dropped back dug control hole pinched STL service and used a 3/4 stopcock for final repair.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GENERAL PAVEMENT MANAGEMENT | THOUSAND OAKS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was working on property in the process of digging and grading with backhoe 3rd party contractor hit and damaged 1/2 plastic service, 3rd party contractor had a USA but failed to maintain marks once removing all the concrete.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MR DRAINS ROOT & PLUMBING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PRTY CONTRCTR DAMAGED 1/2 CTS PLA SVC WITH CLAYSPADE, with No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 5 |  | CARMEL CONSTRUCTION | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was working in the alley excavating in the process of excavating 3rd party contractor hit and damaged a 2inch plastic main, 3rd party contractor had a USA but never maintained marks or called in for remarks when removing asphalt.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JMR BUILDING COMPANY | GLENDALE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was working in the street trenching to install new electrical conduits ins the process of trenching they hit and damaged a 1/2 plastic service, 3rd party contractor had a USA, and this service was not on GIS and riser was in bushes ETD located out service that fed building, had crew correct and update service history.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 32 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PROJECT PRE FAB | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with out a usa found Unkown pipe and treid to cut it out of the way with a sawzall resulting in a leak to are facitlity
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | RAMONA | ARCADIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck 1/2 CTS encased service with backhoe in the process of excavating to replace sewer line. full replacement was necessary.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | THE JMR BUILDING COMPANY | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor failed to notify locator he was going to be working near the service that he and the locator mutually agreed needed to get potholed due to no locate wire on plastic service and measurements being way off. contractor damaged service while open trenching. notes documented on ticket.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | OMAR ALVAREZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit Line no USA. 1/2 PLA service. On Call Crew responded, controlled gas, and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | MG ELITE CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging to stall an ADU contractor struck plastic service line with excavator. NO USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | FRACASSO MATTHEW | SAN DIMAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber cut our service line with reciprocating saw while cutting roots for their trench to install sewer line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | PONCE CEMENT | NORTH HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contactor damaged CTS service line in private property while excavating for the installation of a post for a fence.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party damage, 1/2 IPS plastic service hit for 2250 Edendale Pl. Contractor states that they were potholing with hand tools for service but were signs of a backhoe being used and pneumatic tools. Crew came on site to control gas and make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | THE JMR BUILDING COMPANY | GLENDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 1/2 ips service with backhoe. Contractor failed to pothole gas service that was accurately marked and within tolerance. damage prevention was advised, and they met with the contractor the following day.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party company damaged the 1 plastic service, while trying to pot hole and expose service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LUIS MENDEZ | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage, contractor was trenching out for sewer clean out and hit a 1/2 cts plastic service with a shovel in the trenching process in private property. Company crew arrived and made permanent repairs, no USA at job site.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JMR THE BUILDING CO | GLENDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was working in the street trenching to install new electrical lines in the process of trenching they damaged 1 inch plastic service; 3rd party contractor had a USA but marks were faded 3rd party contractor never called in for re marks.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | KARIM | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage, 1/2 plastic service was hit with shovel while trenching for a new sewer clean out pipe for new ADU at rear of property and contractor was digging with no USA. Company crew arrived to control escaping gas and make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | CAA CONSTRUCTION | LANDCASTER |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Workers on site were removing asphalt driveway and hit line by accident, 1 Inch Plastic No USA ticket
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SPENCER WILLIAMS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 plastic line while digging trench to repair sewer, No USA called in. Crew altered service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PROPEERTY CONTROCTOR | VENICE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Private contractor, dig into an unmarked/undocumented CMB abandoned stub.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | EP GARDEN CARE | RESEDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage with a shovel to 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | RACHAEL ALLEN | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor had hired laborers to dig trench and they struck and damaged our 1/2 CTS. There was no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | LADWP | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DWP dug into a 1 plastic service while working on their own facility with a backhoe. Contractor had a valid USA. Service was mismarked by ETD. Locator marked out service and main. ETD stated to have trouble locating service, so he used GIS and service history. I have reached out to op qual for a refresher training with ETD. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | M JIMENEZ | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage with a shovel, no valid USA available. Excavating to move a palm tree from one location to another.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | JULIO GARCIA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage to a 1 plastic service for 264 S Union Ave, contractor was excavating for conduit placement with no USA. Company crew arrived and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | AMERICAN BORING COMPANY | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | No | No | The instructions did not explain for ticket that 2820 Woodstock Rd the plastic service needed to be located and marked. But the after the fact ticket in the instructions it was updated with addresses needing to be located 2805, 2808, & 2820 Woodstock Rd.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | J GRUBB | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3 party damage. Contractor was grading with NO USA when half inch plastic service was damaged. Crew pinched service used 1'' of CTS plastic pipe along with 2 CTS plastic couplings for final repair.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | AURORA LANDSCAPE DESIGN & BUILD | MOORPARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit service with electric clay spade while digging to expose drain. No USA was called in prior to digging.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BEN ANDRES | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per ETD Garcia found damage 1/2 inch plastic service at 304 S Plymouth Blvd, LA. Third party damage with shovel, no meter no gas outages.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3RD PARTY DAMAGED HIT SVC WITH EXAVATOR MARKS WHERE MISSED MARK ... HAD A COUCHING AND COUNSELING WITH ETD ON COMPANY POLICIES.. NOTE TO FILE WAS GIVIN.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | EDUARDO ALFARO | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug int 1/2cts line while trenching during ADU construction. Contractor Did Not have a valid USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | PRIME CONSTRUCTION SERVICE | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was excavating to locate sewer line for sewer lateral replacement. While excavating, laborer hit half-inch CTS service with shovel, causing leak. 3rd party contractor did not have USA. Crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SRC BUILDERS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor chipping concrete near foundation hit 1/2 plastic service with electric jack hammer. Contractor did not have a valid USA. There was no fire department, police, news media, or road closures on scene. Crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck and damaged main with back hoe while excavating for water service at new business.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | GORDON CONSTRUCTION | SANTA MONICA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on demoing the house in the process of demoing the house 3rd party contractor hit and damaged riser with backhoe, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | M CERVANTES | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1inch plastic cts service with shovel by homeowner with no USA , crew arrived to control gas and made permanent repairs to 1inch cts plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-20 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 8 |  | RAD COMMUNICATIONS | PARAMOUNT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Leak investigation uncovered a third party contractor for internet company installed a self drilling steel auger anchor that damaged our 2 plastic main. Damage was within the tolerance zone. There was a valid USA at time of installation. Neighbors verified installation completed couple days prior to USA expiration.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage to company property, 3 party damage. DWP was digging trench when they failed to hand expose 1/2 plastic service. Crew pinched line that was bent back used 2'' of CTS plastic pipe along with 2 CTS couplings for final repair.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | RICARDO GARCIA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install sewer, contractor hit 1/2 inch plastic line with root cutter. No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 0 |  | INTEGRARE GROUP | CULVER CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cutback service was hit while installing pillars, repairs were made by cutting back the service at the parkway.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 IPS service line during excavation with hand tools in the process of making repairs to sewer line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2047 |  | 1 |  | REYNOSO CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 3/4 steel service line with power tool. Contractor did not have a valid USA upon damage. Crew repaired damage to service with leak clamp. No evacuations and fire department was on scene.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MR. WALEED | PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was using an excavator to dig next to retaining wall. Contractor using excavator pulled tree roots that were intertwined on casing and ripped 1/2 plastic service in half. There was no valid USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 12 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP was working on a water leak repair when they hit the 1/2 CTS plastic service with a shovel. LADWP did have a valid USA, marks were accurate and visible. There was no fire department, police, evacuations, road closures, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | LFG ARBOR CARE | CANOGA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | There was an incident where the contractor hit a line with a stump grinder before verifying the location of the service by hand.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-20 | Third party excavation damage | Main | Steel | Hand Tools | 16 | 60 | 50 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contactor failed by exposing main all the way around .No Leak Found. 16''''Main wrap slightly damage Coated crew re-wrapped main .
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors damaged 1/2 plastic service with backhoe while trenching for water main replacement, service was marked correctly but contractors failed to protect service. Crew altered service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BUILD RIGHT LA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA 3rd party contractor damaged out line with a grinder. Crew Alterd service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Employee mismarked the gas service by 14''. and located a water service thinking it was the gas service. The ticket the employee was working is part of a project/water main installation on a residential street.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 21 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HUMBERTO TOSCANO | NORWALK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, home owner was installing a new fence and hit the service with a post hole digger. Company crew responded and controlled the gas and repaired the service per co. standards.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | CREATIVE HOME REMODELING GROUP | STUDIO CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged Service while cleaning area they had exposed to install windows.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OL DEVELOPMENT | SUN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | During trenching operations conducted by a third party contractor for the installation of electrical conduit, a 2 inch plastic gas main was inadvertently struck by a backhoe bucket. The impact resulted in damage to approximately replace three feet of the gas main, which required alteration to restore integrity. Additionally, paint markings were removed during recess grinding in preparation for plating.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | Z AND A PAVING CONTRACTORS INC | PANORAMA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per Edwin Ruiz of Z and Z Paving Contractors Inc, contract crew was hand excavating for foundation footing of new retaining wall. While hand excavating, crew severed 1/2 CTS gas service, causing uncontrolled release of gas. SCG crew arrived to make permanent repair via socket fusion alteration.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | VICTOR ADJEMIAN | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer digging with shovel to plant a potted plant in his yard. He hit the 1/2 plastic service with the shovel. The Fire department responded and called us out. The crew was able to dig a control hole to stop the blow. The crew was able to fuse in a new section of pipe. Once gas under control and acceptable levels were confirmed, the fire department departed.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WEDIW HASAWOVIC | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer digging trench hit 1/2 inch CTS service with pickaxe. Crew got gas under control and used 1 cts coupling for permanent repair. Contractor did not contact dig alert.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | RODRIGO TRIEBEL | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging trench with equipment and broke plastic service line No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | QUALITY JET ROOTER INC | WHITTIER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor damaged 1 inch plastic service with backhoe while excavating for sewer repair with no USA ticket. M&R responded to low pressure alarm and notified distribution of damage. Distribution crew responded, controlled gas, and made permanent repairs to Service under workorder 520004159496.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HANDCRAFTED CONSTRUCTION | CULVER CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into 1/2 plastic service with post hole digger while trying to install beam for fence. Contractor Did Not have a valid USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | DRILL SUB INC | CORONA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party contractor struck 2 inch Gas Main with Backhoe while digging for Condict work, USA ticket was expired
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor struck 2 inch servcie while grading to pour cement with backhoe. Altered 4 ft of damage, No Vaild USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1678 |  | 3 |  | RAMON AVELAR | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | homeowner excavating trench to install sewer, marks were correct, not enough caution while excavating, Company crew pinched the service and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LEGASPI CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into plastic service with pickaxe while building an ADU on property. No valid USA. Crew arrived on scene, performed pressure control and altered service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 2 |  | VELOCITY ROOTER & PLUMBING SERVICES | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage found ATF, home owner hired a plumbing company to replace sewer. Plumbers hit the 1/2 cts gas service while excavating and made their own repairs to the gas service. Per property owner, plumbers did not want to call So Cal Gas to make the repairs when the damaged occurred. The damage was discovered during a site meet with the property owner due to an encroachment. The property owner explained to SCG Field supervision & Planner what had happened and a company crew was immediately dispatched to investigate and make temporary repairs & permanent repairs to follow.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | BEN SHULMAN | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit our1/2 plastic service with a shovel. Contractor had already plugged line when crew arrived and wrapped it with tape. Fire department had already left prior to arrival. There was no valid USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JOSEPH KERKORIAN | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, property owner was excavating to make repairs on their sewer lateral pipe. During hand excavation, the 1/2 plastic service was hit creating a leak. Company crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP damaged a steel service line while trenching with a backhoe. ETD had accurately marked the service, but DWP failed to hand expose the service prior to trenching. Crew arrived and repaired the damage by replacing the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RODRIGO LOPEZ | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor removing concrete, service was in concrete, service pulled during removal, caused the damage.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | MAS CONCRETE | UPLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 1/2 plastic service with a chipping hammer while excavating for a new water line. Crew arrived and completed permanent repairs. Contractor did not have a USA. DPA was notified.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOMEMADE CUSTOM BUILDERS | ENCINO | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | The USA ticket was returned due to no delineations. The contractor had no idea in how to place the delineation with white paint, did not have the ticket re-sent. I explained to him the importance and how to use white for delineation marks. The contractor called in the USA and reported the damage on the same day of the repair.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | AUD CONSTRUCION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor struck 1/2 plastice service with shovel while trenching for sewer repair, No Vaild USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GONZALO SANCHEZ | ROSEMEAD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor pulled steel line out of ground while excavating, cts pipe was inserted into steel. Contractor did not have a USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ROLLAND CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, contractor was excavating trench by hand for drain pipe, in the process they hit and damaged the 1/2 plastic service. Company crew made repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | 8V PLUMBING | VIEW PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property 3 party damage, Contractor was digging trench for sewer installation with NO USA called in when half inch service was damaged. Crew dropped back dug control hole pinched line, used 1'' of 1/2 plastic PE pipe along with two 1/2 plastic PE couplings for final repair.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 26 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SUPREME CONTRACT | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging near 1 service with hand tools and struck service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | ELLIOT WALL DESIGN & BUILD DBA ELLIOT BUILDERS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Elliott Builders construction team was on site performing home renovations. While hand excavating trench, 1/2 IPS plastic gas service was struck multiple times with shovel by construction team. This caused uncontrolled release of gas from multiple points in gas service. SCG Distribution crew controlled gas and made permanent repair by socket fusion and replacing 1'' section of service with two socket fusion couplings.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | IBUILD DEVELOPERS | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging on the property to install new water and sewer lines in the process of digging they hit and damaged a 1/2 plastic service, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | MARTIN | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew repaired damaged 1 steel service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KLEEN CONSTRUCTION | PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating to install a wooden pole struck 1/2 IPS service with pickaxe and did not have a valid USA. Service alteration was done to existing service to repair damage.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | SUNCORE CONSTRUCTION | BEVERLY HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on the property in the process of demoing property 3rd party contractor hit and pulled 3/4 stl service with backhoe, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ASTER CONSTRUCTION SERVICES | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1 Plastic service with Mini Excavator while performing sewer installation with no valid USA Ticket. LCT Gaeta responded, controlled gas, and made permanent repairs to service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | CORDOVA CONSTRUCTION | PACOIMA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Home owner Robert Benvenisti hired third party construction crew, Cordova Construction, to perform sewer lateral installation. While excavating with backhoe, Codova Construction, after failing to confirm location of marked gas line feeding 429 S Citrus Ave, continued excavating with backhoe. Backhoe severed 1/2 CTS plastic service feeding 429 S Citrus Ave, causing an uncontrolled scape of gas. Cordova Construction crew, in an attempt to control the escape of gas, tied back service with wire.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP struck our 1/2 CTS service line in the process of looking for a water leak. LADWP drilled bore hole and using metal probe punctured our service line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JUAN AGUILAR | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors damaged 1/2 plastic CTS service while digging to repair sewer line, No USA called in. Crew altered service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ILB INTERNATIONAL LINE BUILDERS | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor srtuck 3/4 stl service with Bore rod while boring for conduit, didnt allow ETDto remark, USA ticket came in as remark contractor bore adhead of ticket time
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LC CONSTRUCTION | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Builder damaged line in area thought to be clear of our facility. ETD used all resources and line found thought to be ours per indications and using all available resources. Live line was deeper at same location. Performed on site investigation and went over 184.09 with ETD.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | ATS CONSTRUCTION | COMPTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor, Victor Perez, performing excavation operations for construction of new single family dwelling. While excavating with backhoe for foundation footing, Mr Perez struck and severed 1/2 CTS gas service, causing an uncontrolled release of gas. SCG crew arrived on site to control gas and make permanent repair by altering a one foot section of pipe via two (2) socket fusion couplings.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | ATS CONSTRUCTION | GRANADA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging to install support anchors for patio. Struck our 1/2 Adyl-A with a shovel. Contractor had USA expire months ago and did not renew for valid USA. Spoke to foreman who was new and replaced prior foreman.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 1 | 20 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | DHC GENERAL CONTRACTOR | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while tearing down retaining wall for unknown reasons, contractor struck 1 steel line with unknown tool. No USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LUIS ZELAYA | BELL | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating trench for sewer installation damaged 1/2 CTS service with a shovel. Contractor did not have a valid USA. There was no fire department, police, news media, or road closures on scene. Company crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JAVIER MORATHAI | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into plastic service with shovel while working on building for an ADU. Contractor did not have a valid USA. Crew arrived on scene, performed pressure control, and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | VCI CONSTRUCTION LLC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While digging for electrical, contractor hit 1/2 plastic service with shovel. USA current, and was marked correctly.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MARTIN STRAUSS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contactor was excavating for electrical conduit and damaged our 1/2 Adyl-A with a shovel. There was no valid USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HIGH QUALITY REMODEL | WEST HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging to install conduit for electrical contractor hit plastic service line. NO USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | LADWP | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Municipality( Water ) Drilling holes to find water leak punctured our plastic service with a probe. Called Emergency USA but started drilling before locator could arrive at jobsite. Company crew made repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2331 |  | 10 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP struck our service line while looking for water service withing delineation.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | STRONG | LOS ALAMITOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On July 18, 2025, an Underground Service Alert Ticket (CSB251990397D) was closed out as ?Cleared / No Conflict.? Following a contractor request for markings in the delineation, an updated ticket was issued and again closed out as ?Cleared / No Conflict? on August 1, 2025, by the same employee. During excavation within the delineated area, the contractor damaged an unmarked ï¿½? plastic gas service line using an excavator. A Gas Ops crew responded, controlled the gas, and abandoned the service at the SMC per the contractor request. Per Gas Standard 184.00200, the designation ?Clear ? No Conflict? may only be used when the assigned department or district has no Company subsurface installations within the area of delineation and/or the location on the ticket. ? The contractor provided adequate delineation as required by standard. ? No notes were left by the Employee when closing out the ticket. ? The employee did not physically visit the jobsite to verify the absence of subsurface installations within the delineation. The employee was written up for failure to follow policy.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RAMIREZ CONSTRUCTION | SAN FERNANDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor Struck 1 inch plastice service with Backhoe, No Vaild USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | YKS CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging to disconnect the water line in doing so struck the 1/2 inch gas service no USA was expired fail to renew ticket
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DE LA LUZ CONCRETE | AGUA DULCE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, 3rd party dig in with shovel while excavating for water drainage
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | M13 CONSTRUCTION MANAGEMENT | OAK PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor was digging a trench for gas line without a USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SHARP LANDSCAPE DESIGN | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 Plastic service while excavating without a valid USA Ticket. ARCOS Call out provided a gas ops crew. Crew controlled gas and made permanent repairs to service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | GABRIEL GUZMAN | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owners father in law was digging with shovel to replace sewer and damaged 1/2 service. There was no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CARLOS CURIEL | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Damaged by hand tools Crew arrived on jobsite safely Squeezed the service. Made proper repairs
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALEX | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While grading land for foundation contractor struck plastic service line, No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MATTHEW GONZALEZ | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Damaged by jackhammer homeowner was excavated on private property. severed the 1/2 gas line crew arrived on jobsite safely controlled the situation. Made proper repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | MARIA HERNANDEZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA .....3rd Party Contractor damaged gas svc with hand tools digging trenching for sewer crew altered svc
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JALISCO CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor damaged 1 plastic service with backhoe. No USA notified.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  |  | NA | JALISCO CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged this service twice. Once on 1/25/25 and again on 1/26/25. It was damaged by a backhoe both times. two different addresses were used. 5212 S Avalon on 1/25/25 and 5224 S Avalon on 1/26/2025. This is an after the fact EIR.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BALLART S GENERAL CONSTRUCTION COMPANY CORPORATION | TEMPLE CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging for sewage line and struck our 1/2 adyl-a with a shovel. No USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | MONTEJO DEMOLITION EXPERT | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator was demolishing front yard of home and hit our 3/4 steel service. About 8-10 ft of our steel service was ripped out of the ground. 3rd party contractor attempted to stop flow with tree branch and duct tape. No valid USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ALL SHAPES CONSTRUCTION | WEST HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damage, contractor hit 1/2 plastic IPS service with a shovel while excavating. Gas -ops crew arrived to control gas and make permanent repairs. Gas line was marked at property line with yellow paint and flag indicators were placed inside property due to area being in earth.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | SDI | WEST HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA - Damaged 1/2 cts service with shovel. Third party contractor was hand digging a trench for sewer line using a shovel and nicked the CTS gas service creating a leak. Company crew made repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1848 |  | 4 |  | CALIFORNIA PAVING & GRADING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged 1 IPS service while excavating with backhoe to install new sewer line. No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PADILLA POOLS | AGOURA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A third party company damaged a 1/2 CTS service line while performing excavation work. The incident occurred without a valid USA ticket, as no utility locate request had been made prior to digging.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | CALIFORNIA COAST PLUMBING & REPIPING | ANAHEIM | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party contractor bored into plastic service while installing water line. Contractor was working off an expired USA, service was still marked out correctly. Contractor failed to pothole. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CCS PRECISE CONCRETE | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party was doin framing work for Concrete work an doin so drove a wood steak into the ground, hitting our gas service No USA was called
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | MOD RESTORATION & REMODELING | WOODLAND HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA ....1/2 CTS PLASTIC SERVICE WAS DAMAGED WHILE DIGGING WITH HAND TOOLS
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | FRED LEEDS PROPERTIES | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged 1/2 inch plastic service with a shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | LADWP | SAN PEDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor dug into plastic service with hand tools while trenching to install water line. Contractor had a valid USA. Locate markings were good, contractor simply failed to use adequate caution while digging. Crew responded to scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ANDINO BUILDERS | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor did not protect the markings while digging for footings.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | INFINITE IMPACT | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing company was trenching for new drain line when they damaged the plastic service with a shovel. crew arrived and dug out control holes and replaced the damaged section. No USA was called in by the plumbing company.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | UNKNOWN | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3 party damage. Contractor was excavating for removal of tree when half inch plastic service was damaged. NO USA was called in; Crew dropped back dug control hole pinched line and used 2 feet of IPS plastic pipe along with 2 IPS plastic couplings for final repair.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-14 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | ELECNOR BELCO ELECTRIC INC | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor hit 2" plastic main with digging bar while installing conduit. Crew arrived on scene, performed pressure control and altered main.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | LOS ANGELES BUREAU OF STREET LIGHTING | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The marks were incorrectly placed due to plastic service doglegging and the locator frequency detecting an abandoned steel service. 1/2 service was damaged crew on site and made repairs to company facilities. Coaching and counseling and reviewing of policy the conducted with ETD.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | ALONZO CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging trench for sewer repair damaged 1/2 IPS service with mini excavator. Contractor did have a USA and marks were accurate. Contractor claims service is shallow. There was no fire department, police, road closures, evacuations, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-14 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | LIONHORN | CALABASAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged 2 steel main with a back hoe while excavating to build wall. There was no valid USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BENNETT CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into 1/2cts service while open trenching for ADU construction. Contractor did not have a USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-17 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ACCESS GENERAL CONTRACTING | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor removed flag that was in dirt marking where service elbowed over to riser. Contractor hit 1/2 Plastic service vaild USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PLUMBING SOLUTIONS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck our service line with a shovel in the process of repairing sewer line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors damaged 1/2 plastic service with backhoe while digging water trench, contractors have valid USA ticket and service was properly marked but the failed to protect our facilities. Crew altered service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JBIN BUILDER INC | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2 plastic service with shovel while digging for sewer install. No USA was called.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOSE DIAZ | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer damaged plastic gas service while digging for fence posts. failed to call 811.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | EROZ PLUMBING | ROSEMEAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit service line at riser while trenching. Contractor did not have a valid USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | LA SEISMIC CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HIT GAS LINE W/ SHOVEL WHILE INSTALLING NEW WALK WAY RENATO SEBASTANI LA SEISMIC CONSTRUCTION 323-420-4113 NO Vaild USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | QUALITY WOOD FINISHING | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party company had no USA and damaged 1/2 inch plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1/2 plastic service damaged by contractors installing water main, crew altered service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | GOLDEN ESTATE BUILDERS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A third-party company caused damage to a 1/2 plastic service line while trenching for sewer installation.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | AGC BUILDERS | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage with an electrical pneumatic tool. No valid USA available.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DANIEL RUIZ | SANTA MONICA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscape company was auguring for new landscape trees when they damaged a 1 plastic service. The landscaping company did not have a USA. Crew arrived, dug a control hole and replaced the damaged section of pipe. Service was reinstated.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | ROCKSTAR PLUMBING SERVICES | CHATSWORTH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage, contractor hit a 1/2 cts plastic service with a shovel for 658 N Occidental Blvd. Company crew came out to control escaping gas and make permanent repairs, contractor was excavating without a USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | LOS ANGELES BUREAU OF STREET LIGHTING | LOS ANGLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor dug into plastic service while trenching to install conduit. Contractor had a valid USA, locate was marked out correctly. Contractor did not use adequate caution while digging. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 27 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into plastic service with hand tools while doing house demo. Contractor did not have valid USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ROOTER GUARD | SUN VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party damage to a 1 inch plastic service for 7000 W Sunset Blvd, permanent repairs made by company crew.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water company excavating trench for main replacement
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | A&G GARDEN SERVICES | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property digging to fix the sewer and drain lines in the process of digging with backhoe 3rd party contractor hit and damaged 1/2 Plastic service with backhoe, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP Damaged unmarked 1/2 Plastic gas service while excavating for water main install. Service was within delineation and USA Ticket was valid. On Call Crew responded and made permanent repairs to service. Locator was contacted about incident. ETD explained they could not find meter during locate and assumed the service was fed off of the cross street due to the home being a corner lot. Will give documented counseling to ETD covering expectations for Locate and Mark and will review L&M Gas Standard with ETD to ensure all company policies are understood and followed moving forward.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | D CORP | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor pulled 1 service with backhoe. USA valid, service marked but marks not upkept. marks removed with asphalt.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA ... 1/2 CTS PLASTIC SERVICE IN 1/2 COPPER CASING WAS DAMAGE BY THIRD PARTY CUT TROUGH.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RICHARD B CHUTUK & SONS | AGUA DULCE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party damage, contractor hit 3/4 steel service for 729 Robinson St at street while excavating for 726 Robinson St. Contractor had a valid USA with 3/4 steel service marked correctly where service was hit. Company crew came on site and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | During an excavation for water main installation, LADWP damaged a 1/2 plastic gas service with a backhoe. A gas operations crew responded, controlled the gas, and made permanent repairs. LADWP had a valid USA Ticket at the time of the damage. The service was located approximately six feet from the markings provided by SCG. The supervisor on-site notified the technician who initially marked the service. The technician arrived on site and explained that they connected the transmitter to a neighbor''s service due to a locked gate, received a strong signal, and marked the location accordingly. The technician recreated the original location results for the supervisor, which were directly over the incorrect markings. An unknown pipeline was discovered at the site, which likely caused a false signal. DWP hand-dug around this pipeline within two feet before using machine equipment, leading to the damage. In 2019, another 3rd party damage occurred at the exact same location: 520002050565. To prevent future damages at this location, a G was chiseled into the curb directly over the service to assist with future locates.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | FORTY GENERAL BUILDING | BELL GARDENS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors damaged 1/2 plastic service while trenching houseline for ADU, no USA called in. Crew altered service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | PMA RENOVATIONS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing company was excavating with a shovel for a water line repair when they damaged a 1/2 plastic service. Crew arrived on site and dug up control holes and replaced the damaged section. No USA was called in by the plumbing company.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SWIFT PLUMBING | WESTCHESTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SEWER REPAIR BEING PERFORMED FOR 7426 ALVERSTONE, 1/2CTS PLASTIC SERVICE DAMAGED DURING EXCAVATION WITH SHOVEL IN FRONT YARD. CREW REMOVED AND REPLACED 1FOOT OF DAMAGED 1/2CTS PLASTIC SERVICE. NO USA WAS CALLED IN BY THE PLUMERS, DAMAGE PREVENTION WAS NOTIFIED.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 23 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TUNG WING CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging without a USA ticket, thought they were cutting roots and cut a 1/2 CTS service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 23 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | D CORPORATION GENERAL CONTRACTING AND ENGINEERING | NUEVO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | D Corporation hit 1/2inch unmarked plastic service while excavating. Locator error
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JOHANY POLONY | DOWNEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA , USA WAS CALLED IN AFTER THE FACT. 3RD PARTY CONTRACTOR HIT SVC WITH HAND TOOLS
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | STONE YARD LANDSCAPE CENTER | ALTADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party excavation damage to a plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BRANDON PEREZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contactor struck 1` inch plastic service while trenching to waterproof Foundation No Vaild USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MAKI BARA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged accurately marked 1 Service with Backhoe without hand exposing it. ARCOs crew responded, controlled gas, and made permanent repair to service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ARIEL DAVID | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor excavating for Sewer install with no USA damaged a 1/2 CTS Service with Mini Excavator. On Call Crew responded, controlled gas, and made permanent repairs to service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | WAY TO GO BUILDERS | WEST HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging in the property for a fence in the process of digging they hit and damaged 1/2 plastic service, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | A SEWER COMPANY | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1 plastic service in private property with backhoe. No USA was called.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LUIS & ROSE CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | believed service was abandoned and hit with shovel no USA , Cut the service with sawsall,
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DAVID MAGNA JR | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit service with hand tools No USA was called in.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1678 |  | 3 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 inch plastic service damaged by contractors'' potholing with shovel to verify line, crew altered service to make permanent repairs. No emergency service was on-site.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | IDCS CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party company doing demo work. Did not have a valid USA. The contractor mentioned to the customer service tech that he is aware that the service is not abandoned. Still dug over the service and damaged the 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3749 |  |  | NA | PENNINE PLUMBING | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3'''' plastic service damaged by backhoe. No USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JOSE GARCIA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA - WHILE TRYING TO BUILD A FENCE AND DIGGING, CONTRACTOR JOSE GARCIA HIT A SERVICE LINE. CUST DID NOT CALL 811 BEFORE DIGGING
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JUAN GUZMAN | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching to install sewer. Accidently damaged 1/2-inch plastic CTS service with shovel. USA was not called.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ELIZABETH PIOTROWSKI | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd part damage, 1/2 cts plastic service was damaged by shovel while digging in property with no USA. Crew arrived to control gas and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BRANDAN KELCHNER | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party company digging for sewer with No USA. Damaged 1 plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MJ EXCAVATION AND GRADING INC | WEST HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The technician did not connect the RD8100 to locate and mark the service going to the left. Instead, the technician explained to the contractor that one plastic service was marked/flagged at the location. The meter has been removed, but the service is still live. The contractor is aware of the riser, which is marked with a traffic orange cone. Additionally, yellow paint was found at the curb.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | SAMAX PROPERTIES | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service with shovel while trenching.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SWINERTON | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was working on property digging to install new footings and in the process of digging they hit a 1/2 plastic service, 3rd party contractor stated planner told them line was abandoned but ETD went out and located service and informed contractor service is live but contractor went ahead and dug without adequate caution when exposing our line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  | 0 |  | ESCOBAR CONTRACTING | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage originally came in as an odor complaint, upon crew arrival to 9224 new construction there was bridge boards covering a trench in front of property and once uncovered the LCT saw a 2 plastic main pulled and damaged causing it to leak. The trench was provided for a new sewer pipe for property, contractor never informed or called anyone of damage. Valid USA and facility marks were visible and marked correctly, pictures were taken. Company crew stopped and made permanent repairs to damage.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CHRISTINE HOLSCHNRIDER | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hired contractor was doing fence work and damaged customers 1/2 service line while hand digging. Fire department arrived but did not evacuate homeowner. Crew arrived and determined that gas was not near foundation or in danger of anyone. Crew proceeded by repairing 1/2 service damage by replacing damaged section. Customer did not have valid USA prior to excavating.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-14 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor excavating under valid USA Ticket for Water Main installation damaged an accurately marked 2 Plastic Gas Main with sharpshooter shovel while attempting to expose it. SCG Gas Ops crew responded, controlled the gas, and replaced the damaged portion of main.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | STELLAR SIDEWALKS | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA valid, 3rd party contractor was digging up sidewalk, came across our service line tangled with roots, as they went to remove the tree root service was pulled as well
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | BENJAMIN ANGUIANO | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit SVC, no USA. On call Crew responded, controlled gas, and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWDP damaged gas service when digging for new main water line with backhoe. signal interference, gas service in close proximity to water line running parallel and splitting at PL.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DWP Damaged mismarked 1 Gas service while installing new water service. Gas service was 4 feet off mark. USA Ticket was valid. ETD Marked ticket off of measurements due to riser being behind locked gate. Crew responded, controlled gas, and made repairs
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2025-06-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MONTE VISTA HOMES | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was pouring concrete and struck our 1 plastic service with wooden stake. There was no active USA.
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2025-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BERNARDO CAMORLINGA | LYNWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner struck 1/2 inch plastic service with shovel while making repairs to sewer line.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DOMINGUEZ GENERAL ENGINEERING | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Found ETD''s markings correct. When I asked the contractor why he hit our facilities he stated the excavator operator did not see our markings.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VIDMAR | SOUTH EL MONTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was working on property trying to install new drain lines in the process of digging they hit and damaged a 3/4 steel cutback on the property that was not on GIS or epoch, 3rd party contractor had a USA the ETD located the service on the property, Crew that went out abandoned the cut back on WO# 54-681603.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Hand Tools | 0.75 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2179 |  | 1 |  | TETRA TECH CREW | MALIBU | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Army core contractor damaged service tee while not exposing facility that was marked out correctly. Service tee was ripped off causing LCT to repair by installing a double strap tee.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-10-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | LIVE OAK POWER | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | SoCalGas employee mismarked main location causing the 3rd parity contractor to damage the main; However, 3rd party contractor failed to request a relocate due to them not locating the gas main after they hand-dug the area and failed to locate the gas main.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | HOT LINE CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was working on the street trenching to install new conduit lines in the process of digging 3rd party contractor Hit and damaged 1/2 plastic service, 3rd party contractor had a USA but marks weren''t accurate due to locator error supervision coach and counseled ETD and suspended ETD from task 5.1
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PAR ELECTRICAL CONTRACTORS | FONTANA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged plastic service while installing a power pole. ETD had originally marked the service with flags due to a dirt parkway. Contractor did not work this job until a month after calling in the USA. Once the contractor finally worked the job, they renewed the ticket and did not request remarks failing to maintain visible marks. Crew arrived and repaired the damaged section and reinstated the service line.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PAR ELECTRIC | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Third party contractor dug into 1 plastic service with backhoe while open trenching. 2 inch main was marked out, 1 inch plastic service was faded out due to rain. Service had been cut back. Crew arrived on scene, performed pressure control and abandoned service at smc.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | BLOIS CONSTRUCTION | OXNARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was digging to install new water lines in the Palisades area in the process of digging with backhoe they struck and damaged a 1inch plastic stub, 3rd party had a valid USA, When locator went out to locate area there was no riser on property and on GIS and Epoch there was no service showing for that house also ETD checked service history and it stated that service was abandoned at the SMC during the Palisades fire and there was a patch in the street indicating that service was abandoned. This was an unknown stub that no one knew about.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | SEACON CONSTRUCTION | MOORPARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service hit with clay spade by contractor, Builder says marks were visible at one point but after grading the marks were no longer visible. Contractor failed to maintain marks and call in for refresh marks. Crew arrived and repaired the damaged plastic service and reinstated the service.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | SEACON CONSTRUCTION | MOORPARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging on property to fix drain lines in the process of digging they struck and damaged a 1/2 plastic service, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | INTERNATIONAL LINE BUILDERS INC | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Mismark by ETD: An employee volunteered to support the wildfire recovery effort from outside the district. Due to unfamiliarity with the terrain and property lines, local supervision will review the relevant policies with the employee.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LIVE OAK POWER | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor dug into plastic service while installing electrical conduit. Contractor had a valid USA and marking were correct, contractor failed to maintain clearance. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-06-16 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 3 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | INTEGRITY GENERAL ENGINEERING CONTRACTORS | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was working on street digging a trench to install new electrical conduit in the process of trenching 3rd party contractor hit and pulled off a 1 inch service tee off the main, 3rd party contractor failed to hand dig when digging right above our main and hit a stub service.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 0 |  | PCH CONSTRUCTION | WESTLAKE VILLAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit a line while digging for electrical in private, NO USA, CREW WORKERS PINCHED THE LINE WITH METAL WIRES before ETR ARRIVAL, THEN LEFT IMMEDIATELY. SCG crew repaired the 1/2 IPS service line by altering it.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JOES BUILDERS GROUP | MALIBU | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was trenching on property in the process of trenching to install new utility 3rd party contractor hit and damaged 1/2 inch plastic service they had no USA.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2025-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | TIM GREENLEAF ENGINEERING | HUNTINGTON BEACH | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor was grading dirt with backhoe when they struck out known / marked 1 gas service. Contractor knew it was there and struck by accident. USA calid, contractor at fault.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2025-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1766 |  | 2 |  | UNKNOWN | MANHATTAN BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was hand excavating trench with shovel to install fencing when they struck our 1/2 PLA gas service. No USA, contractor at fault.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ROOTER HERO PLUMBING | LA HABRA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor ((Rooter Hero) was hand excavating to install new drain when they sawzall through our 1 PE gas service by accident, while cutting out roots and their existing drain. No USA, contractor at fault.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2025-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | JUAN DE JESUS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. While digging in yard, contractor hit 1/2 PLA line with pickaxe
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2025-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | P & M DRAINOLOGY LLC | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2'''' CTS service. No contractors onsite upon arrival. Service appeared to have been damaged by backhoe. USA was not called.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2025-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BAYVIEW CONSTRUCTION | SANTA MONICA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was hand excavating with shovel to install drainage when they struck our known marked 1/2 inch plastic gas service by accident. USA valid, contractor at fault.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2025-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BEAR VALLEY AND ASSOCIATES | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor accidentally damaged service while excavating to build a retaining wall. USA was not called.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2025-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | KLM ENGINEERING CONTRACTORS | HERMOSA BEACH | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor damaged 1/2-inch CTS service while trenching with backhoe. USA was called but they did not wait the 48 hours. Service hadn''t been marked.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2025-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | AGI GEOTECHNICAL | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor (AGI Geotechnical Inc.) was soil sampling with hand auger when they struck our 1 PE gas service. No USA, contractor at fault.
Southern California Gas Company | N | LOS ANGELES | MAYWOOD | 2025-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MARTIN IMCHAURREGUI | MAYWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damage plastic gas service while excavating a trench for gas houseline from front house to back house.
Southern California Gas Company | N | LOS ANGELES | MISSION HILLS | 2025-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | TROUTWINE PLUMBING | SIMI VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA valid, 3rd party contractor failed to exposed our service line, went ahead and accupunch hit our 1/2 IPS service.
Southern California Gas Company | N | LOS ANGELES | MISSION HILLS | 2025-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MAXIMILIANO SALAS | MISSION HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, 3rd party damaged 1/2 CTS pipe while digging trench for fencing with shovel, crew repair with service alter.
Southern California Gas Company | N | LOS ANGELES | MISSION HILLS | 2025-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | LIZETH CUARA | MISSION HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner Lizeth Cuara hired helpers to perform sewer work on her property at 11042 Burnet Ave, Mission Hills 91345. While helpers were excavating trench with hand tools, they struck and damaged the 1/2 CTS plastic gas service, causing and uncontrolled release of gas. SCG Distribution crew arrived on site to control and make permanent repairs via socket fusion alteration of 1'' section of pipe and two (2) socket fusion couplings.
Southern California Gas Company | N | LOS ANGELES | MISSION HILLS | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 45 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ALTO BUILDER | AGOURA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner had hired third party construction crew to develop ADU on property. While 3rd party construction crew was excavation trench to tie in gas line for ADU, they discovered a 3/4 steel line. 3rd party construction crew attempted to cut out 3/4 steel line to make room in trench. While sawing, 3rd party construction crew discovered gas scaping from pipe. SCG distribution crew arrived on site to confirm damaged 3/4 steel line. Crew installed one 3/4 x 3 Adams clamp to permanently repair and wrapped pipe
Southern California Gas Company | N | LOS ANGELES | MISSION HILLS | 2025-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JUAN TOPETE | MISSION HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property 3 party damage, Contractor was digging with NO USA when half inch service was damaged. Crew dropped back cut casing of service pinched line that was already pinch by contractor. Crew used 2 feet of CTS plastic pipe along with 2 CTS couplings for final repair.
Southern California Gas Company | N | LOS ANGELES | MISSION HILLS | 2025-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | LADWP | GRANADA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP installing trunk water line on Arleta. during excavation of trench with backhoe, excavator operator was extending the arm of backhoe and in the process, struck and damaged 3/4 steel service. this caused a sudden and uncontrolled escape of gas. SCG crew arrived on site and had LADWP crews displace earth and install shoring inside excavation trench to allow SCG crew to enter and make necessary repairs. SCG crew made permanent repair via 3/4 x 3 clamp
Southern California Gas Company | N | LOS ANGELES | MISSION HILLS | 2025-09-30 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 36 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | GTO SERVICES | MISSION HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner of 9947 Norwich Ave was trenching for fence footings. While excavating with backhoe, 3/8 STL branch service was damaged. No release of gas. Crew performed repairs of STL branch service and set riser and MSA in original location.
Southern California Gas Company | N | LOS ANGELES | MONROVIA | 2025-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | HERITAGE DISPOSAL | ALHAMBRA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | GAS LINE DAMAGED BY EXCAVATOR, WHILE FIXING THE PLUMBING.
Southern California Gas Company | N | LOS ANGELES | MONROVIA | 2025-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | TTS ENGINEERING | STANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damage 2 plastic Gas Main. Marked and visible Marks.
Southern California Gas Company | N | LOS ANGELES | MONROVIA | 2025-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WISE CHOISE PLUMBING | GLENDORA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor crew hit 1 plastic service while digging for irrigation line.
Southern California Gas Company | N | LOS ANGELES | MONROVIA | 2025-01-03 | Operator excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3983 |  |  | NA | SOCALGAS | PASADENA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LCT damaged 2 steel gas main. that was just below anther 2 steel main. marks were within 2 feet.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2025-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1678 |  | 3 |  | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ETD responded to Doty Bros water main install project ticket. At this particular address, the ETD could not identify a locate wire at the riser. The technician noticed an insert washer at the riser and hooked up the transmitter to the tang of the riser. The tech followed the signal to the sidewalk, which led to a G chiseled into the curb face. The tech did not receive a signal past the curb face; however, the tech identified existing patches in the concrete that aligned with the G. The ETD then took measurements based on service history and noticed measurements did not align with the G or the patches. The ETD then marked where the G and patches were, as other services were accurately aligned with the G''s on the curb faces throughout the project. The 3rd Party Contractor then proceeded to pothole over the mark and identified a steel pipe. Believing the steel pipe was the casing, the Contractor then began digging with a backhoe, damaging a 1/2 plastic service 8 ft from the mark. SCG company crew responded to the damage, controlled the gas, and made permanent repairs to the service. Once safe, the ETD back traced the locate wire from the damage location, which led to the G. The service deviated from the G to the damage location. Service history measurements were accurate to the point where the damage occurred.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | SAN GABRIEL VALLEY WATER COMPANY | EL MONTE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Water company responding to water leak damaged a 1/2 inch plastic service while excavating on emergency USA Ticket. Crew Responded, controlled gas, and made permanent repairs to service.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2025-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  |  | NA | CITY OF MONTEBELLO | MONTEBELLO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | A third-party contractor damaged a 3/4 steel service line with a backhoe. The contractor exceeded the specified scope of work outlined in their USA Ticket, which indicated a maximum excavation depth of 2 inches. ETD closed the USA Ticket as No Conflict based on the contractor''s specifications. However, the contractor excavated to a depth of 3 feet, resulting in damage to the SCG facility. The Fire Department responded, closed the street to the public, and the SCG crew controlled the gas and made necessary repairs. Upon gas control, the Fire Department departed the worksite and reopened the street.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2025-12-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit accurately marked 1 Plastic service with backhoe while excavating for water main installation. The district crew responded, controlled the gas, and made permanent repairs to the service.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2025-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OAK HILLS IV HOA | MONTEBELLO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging to make houseline leak repairs hit our 2 plastic service with a shovel causing leak. Pasadena OHS crew arrived, pinched service and made permanent repairs by cutting out damaged section and fusing in 3'' of 2 plastic and two 2 couplings. No USA was called in before they hit our service.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2025-12-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | FRANCISCO GUITIEREZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A third-party contractor damaged a 1-inch plastic gas service line with a mini excavator while performing excavation work without a valid USA ticket. The Excess Flow Valve (EFV) activated and successfully shut off the gas prior to company personnel arriving on site. The district crew responded promptly and completed the necessary repairs to restore service.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2025-07-02 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | YOLANDA OSORIO | MONTEBELLO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit 1/2 Plastic service while excavating for ADU build without a Valid USA Ticket. Gas Operations crew responded, controlled gas, and made permanent repairs to service.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2025-08-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | SUP MASONRY | MONTEBELLO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged 1 svc with excavator trenching for retaining wall
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2025-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SAN GABRIEL VALLEY WATER COMPANY | EL MONTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | San Gabriel Water Co. damaged plastic service while digging to repair a water leak. Service was marked out correctly but in the process of finding plastic service they exposed it, then accidently damaged our gas line.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2025-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | OHL USA CONSTRUCTION | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating for street repair dug with an excavator before the legal start date/time listed on the USA Ticket. Contractor struck a 1/2 IPS plastic service with an excavator. The Fire Department responded and temporarily controlled the gas. SCG distribution crew arrived, controlled gas, and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2025-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 5 |  | OHL USA CONSTRUCTION | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was exposing line when struck service with shovel
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2025-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1766 |  | 0 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Unreported damage. Call came in as leak. Was later discovered to be a damaged service by contractors working on house. Contractors has left before crew arrived.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2025-09-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3270 |  | 1 |  | TRE LIGHTING & ELECTRICAL | ANAHEIM | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor hit gas main with mini excavator.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2025-05-03 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 27 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | ESTELLA THAY | MONTEREY PARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hired unlicensed contractor to repair clogged sewer lateral. Contractor did not notify DigAlert and began breaking hard soil with electric jackhammer which despite finding warning mesh, still continued on and hit single feed, 2PLA main. Crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2025-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 27 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SIMON YEE CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging a trench for electrical and water line installation hit our 1/2 IPS service with a jack hammer/clay spade causing broken and blowing. Contractor did have a USA ticket but it had expired back in feb. and the USA ticket noted the delineation and work was to be done in back yard. Pasadena OHS crew arrived, controlled gas with by pinching. Crew made permanent repairs by cutting out the damaged section and installed 2'' of 1/2 IPS and 2 couplings.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GRBCON | BALDWIN PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck plastic service with shovel while digging to expose.
Southern California Gas Company | N | LOS ANGELES | MONTROSE | 2025-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MARIO FUENTES | MONTROSE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, Homeowner was digging with NO USA when damaged half inch CTS service. Crew dropped back pinched service then used 2 Plastic CTS couplings along with 2 of plastic CTS pipe for final repair.
Southern California Gas Company | N | LOS ANGELES | MONTROSE | 2025-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | NOBLE GENERAL CONSTRUCTION | MONTROSE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damaged in a trenched area near the meter set assembly (MSA). Customer stated damage occurred while moving pipe by hand; the damaged section was covered by PVC pipe and tape. Customer/contractor claimed no equipment was in use at the time of damage. No Dig Alert ticket was called by the contractor onsite. Repairs were completed by abandoning the service at the main connection, as the plastic service was obsolete PVC material. The service was already scheduled for abandonment on the next business day by an SCG contractor under work order. Repairs took longer because the obsolete pipe prevented immediate repair at the time of damage. Claims may need to adjust the claim amount accordingly.
Southern California Gas Company | N | LOS ANGELES | NEWHALL | 2025-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LISETTE VALENCIA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 plastic service while digging trench for water line. Contractor did not have a valid USA. There was no emergency services, road closures, evacuations, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | NORTH HILLS | 2025-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | JORGE OJORYAN | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner and his family were excavating without a valid USA. The homeowner''s cousin was using a pickax to assist in the excavation, and he struck a 1/2? plastic service multiple times, causing a release of gas. SoCalGas crew responded, controlled the release, then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | NORTH HILLS | 2025-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | BENLIAN BROS | GRANADA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor was excavating with a valid USA. The third-party contractor was excavating for sewer and accidently struck a 1/2 plastic service with a shovel. The USA marks were visible, and the contractor failed to follow proper excavation procedures
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | JONATHAN | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged service , crew made permanent repair.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 0 |  | SIMCITY CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner Natalie Wong hired contract crew Simcity Construction to excavate trench. While excavating with shovel, 1/2 CTS gas service was struck, causing an uncontrolled release of gas. SCG crew arrive don site to control and make permanent repair via socket fusion alteration of a 1'' section of pipe. Fire Department was not on site upon arrival of IC.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | SHERYL PETWAY REAL ESTATE | WEST HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | New single family home construction on site. Trench had been dug at left side of property, exposing and damaging two sections of 1/2 CTS standard service. Branch feeding 4201 was severed and riser damaged by shovel. Spoke with Sheryl Petway, real estate agent for property. She said the property will not be using natural gas. Informed her the service on property will have to be abandoned. Neighboring branch service at 4201 will need to be replaced.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-05-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | SARAN GROUP DEVELOPMENT | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging on property to install drain line and damaged 1 IPS service with hand tools. Customer did not have a valid USA. There was no fire department, police, street closures, or news media on scene. Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-12-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ROOTER GUARD PLUMBING SERVICES | PACOIMA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging working on drainage system, contractor hit service line with shovel. No USA was called for this job.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-07-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | TM MCKNIGHT CONSTRUCTION ENGINEERING | GARDEN GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party Contractor damaged 1/2-inch service with Grader. USA was valid and all gas facilities was located and marked properly.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | MONARCH CONSTRUCTION | NEWPORT BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party Contractor damaged 1/2-inch plastic service. USA was valid. Locator failed to locate and mark service.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MR DESIGN | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor digging trench for new foundation hit gas service with backhoe. Contractor did have a USA ticket on file, but locator could not gain access to property. Contractor dug without resubmitting ticket. There was no fire department, police, road closures, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-01-16 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | LADWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Gas main was miss marked by company Locator crew made temporary repair due DWP trying to find water leak. capped main on both ends
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DAVID PAVIA | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit plastic service with shovel
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-09-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HASMIK MURADYAN | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged 1 plastic service with an excavator while trenching for a sewer line installation. There was no valid USA on file. There was no emergency services, road closures, evacuations, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | BENTAGA INVESTMENT | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | RFA from customer service then Gas Ops found service damaged at riser and in yard, pinched back and buried at unknown location. Contractor stated they had trenches dug for sewer, forgot gas line was damaged due to debris and trash. Claimed damage happened over a month ago. Claimed homeless people damaged it to steal copper casing. Only 2'' of copper was removed where damaged. AL riser was pulled out of the ground and laying on its side appearing to be an attempt to relocate riser or move for sewer install. Crew cut back service at PL to make safe and allow the customer to arrange riser location (Dticket) with planner. Property owner is proceeding to work with planner on full abandonment.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ALTECE DESIGN | WINNETKA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractors digging for new sewer installment for ADU, hit our 1/2 CTS service with pickaxe
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | EXPRESS CONSTRUCTION GROUP | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY CONTRACTOR DAMAGED 1/2 CTS SERVICE IN COPPER CASING WITH SAWZALL WHILE EXTENDING FOUNDATION. CREW REPLACED DAMAGED SECTION OF SERVICE.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | NA | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner building ADU in rear of property. Homeowner hired third party construction crew to excavate trench for new sewer lateral for ADU. While excavating, third party construction crew struck and damaged 1/2 PLA gas service, causing an uncontrolled release of gas.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | KNOCKOUT ELECTRIC | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing ground rod near electric panel hit 1/2 plastic service. Residence was evacuated by ETR. Company crew responded and made permanent repairs. Evacuations were lifted when gas indications were no longer present at foundation.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | M KESHISHYAN | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party digging for sewer lateral damaged cts service near riser. ETR evacuated 1 resident due to damage location. Crew made permanent repairs and check reads near foundation before lifting evacuations.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2025-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | L&L PLUMBING | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party excavation damaged. No USA called in for this job
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2025-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | CDF CONSTRUCTION | COMPTON | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dug with expired USA. Description of work type on ticket does not match the work type taking place at time of damage or described location of work. While digging for sewer lateral install to ADU, contractor hit plastic branched gas service with shovel. Crew arrived and completed permanent repairs. FD departed prior to supervisor arrival.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2025-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOME OWNER | NORTHRIDGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging/excavating with a shovel and struck our 1/2 plastic service. No USA.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2025-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | VAHE BAGHDASARYAN | PORTER RANCH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3rd party damage. Contractor was digging with NO USA when damaged a half inch service. Crew dropped back and pinched plastic service they used 2 1/2 IPS couplings along with 2'' od 1/2 plastic pipe for final repair.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2025-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | YUI TULUPOV | NORTHRIDGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging trench for irrigation system hit 1/2 inch plastic service with hand tools. Homeowner did not notify USA. There was no fire department, police, road closures, or news media on scene. Crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 6 |  | WIRING CONNECTION | GARDENA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was digging to install electrical conduit when they bored into 1 plastic service. Valid USA. Service was difficult to locate due to locate wire issues. Crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2025-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FELIX MONROY | NORTHRIDGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating without a valid USA. The contractor was using hand tools to excavate and install a new drain line for a residential dwelling. While in the process, the contractor struck a 1/2 inserted plastic branch service.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | NORTHRIDGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP damaged 1/2 CTS gas service with backhoe. Gas service was accurately marked within delineation. Valid USA. Appears LADWP did not pothole before digging with heavy machinery. Crew arrived and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2025-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | LADWP | NORTHRIDGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | dwp was digging to install water valve in street when they struck plastic service line with backhoe. service was marked out with paint. markings where covered with plate and dirt
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2025-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | MARC SEE | NORTHRIDGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating without a valid USA. The homeowner hired a contractor to fix a leaking gas houseline. The contractor was using a backhoe to excavate, and they struck a 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2025-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 45 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | MILLENIAL BUILDERS CALIFORNIA INC | PALMDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was using skids Ter to grade work area and was grading along steel service when they struck service tee with front buck. crew squeezed line and welded on 3/4 tee. contractor was aware that they were knocking off wrap from service pipe
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2025-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DELL LISENBEE | NORTHRIDGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging to a trench to install conduit to back adu when they struck plastic service line with shovel. No USA
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2025-10-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | STEPHEN DORECK EQUIPMENT RENTALS | PICO RIVERA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not have a valid USA ticket. They went off old marks in the street and the service had since been moved, they hit it with an excavator while digging trench for water.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2025-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | HERNANDEZ MASONRY | SHAFTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck 1/2-inch service with shovel during tree removal. Crew squeezed the service, removed tape and found CTS pipe with a slice in it due to a shovel. Crew conducted permanent repairs by fusion. Customer service performed rebuild restore.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2025-01-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DRAIN WITH TRENCHLESS | TORRANCE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating for sewer repair, no valid USA, struck and damaged 1/2 plastic service with shovel. Damage prevention on site spoke with contractor as to the importance of calling 811.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2025-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | CHAMBERLAIN BACKHOE SERVICE | PLACENTIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Backhoe operator damaged 2inch plastic main with bucket, gas no leaking. service will need to be altered to repair damaged service.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | AF CONSTRUCTION | PACIFIC PALISADES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property with an excavator in the process of working on property they hit and damaged 1/2 plastic service, 3rd party contractor had no USA and when etr and crew arrived no one was on site to get any information on the damaging party.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | REPUBLIC FENCE | CHATSWORTH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging on property with postal digger to install gated fence in the process of digging 3rd party contractor hit and damaged 1/2 plastic service they had no USA.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | MOSSER PLUMBING & HEATING | MARINA DEL REY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing company damaged 1 plastic service while digging trench for new sewer and drain lines. Crew arrived and repaired the damaged section of pipe and the service was re-instated. No USA was called in by the plumbing company.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  |  | NA | JENSEN CONSTRUCTION | LA CANADA FLINTRIDGE | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | HITLINE CAUSED EXCAVATION BY JIMENEZ DEMOLITION COMPANY. UPON ARRIVAL FOUND SERVICE COMPLETELY SNAPPED. CREW DUG OUT CONTROL HOLE AND PINCHED THE SERVICE. NO MARKS WERE FOUND DUE TO TICKET BEING SENT BACK BECAUSE EXCAVATOR DID NOT PROVIDE DELINEATION, TICKET WAS ALSO FOUND TO BE EXPIRED.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | CLIFF ROSSIE | PACIFIC PALISADES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit gas service with a back-ho. Contractor/Homer Owner did not have a valid USA.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DJL CONSTRUCTION | SAN DIEGO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | CONTRACTOR FAILED TO MAINTAIN MARKS AND VALID TICKET AT THE MOMENT OF THE DAMAGE TO THE PLASTIC SERVICE. CONTRACTOR DID NOT NOTIFY USA IF THE DIG ALERT TICKET WAS EXPIRED. CONTRACTOR IS RESPONSIBLE FOR NOTIFYING USA FOR REMARKS AND UPDATING THE TICKET.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AMERICAN SAFETY GROUP | TUSTIN | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor dug into 1 plastic service that had been cut back while clearing burned property. Contractor did not have a valid USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AJ ELECTRIC CO | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer was excavating for a retaining wall when they damaged a steel service. Crew dug out the SMC to control the gas and then replaced the damaged section with new pipe. No USA was called in by developer.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MORRONE AND SONS | PACIFIC PALISADES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | BROKEN AND BLOWING WHILE PLUMER TRENCHING FOR NEW WATER SVC LINE NO USA WAS CALLED IN BY PLUMBING COMPANY. CREW ARRIVED AND DUG UP CONTROLL HOLE, PINCHED SERVICE AND REPLACED THE DAMAGED SECTION OF PIPE.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GILAD AVIDOR | SHERMAN OAKS | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was auguring on property to install new posts for addition to house in the process of auguring they hit a 1inch steel line, 3rd party contractor called in a USA but did not provide a delineation so ETD sent ticket back.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | 3 PINOS INC | PACIFIC PALISADES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was driving metal stakes to set forms for concrete pour and damaged 1/2'' CTS service due to no USA being called in. 1'' of 1/2 CTS service was altered for repair.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | GRASS PROPERTIES | WESTLAKE VILLAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property digging for electrical conduit in the process of digging 3rd party contractor hit and damaged 1/2 plastic service with shovel, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-04-28 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | PETRELLI ELECTRIC | VERNON | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | EE did not see the last address on the ticket was on the back street where the main was in the sidewalk. All other poles were inside the property were there was no gas services. EE sent out a clear no conflict response to the ticket. Excavator claimed someone told him the main was abandoned but he did not verify with SoCal gas. gas main was marked next to damage. LADWP augured thru 2 plastic gas main on sidewalk, crew pinched and altered the main installing a new section of pipe to replace the damage.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-03-25 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HERMAN WEISSKER | RIVERSIDE | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2nd party contractor working on Northfield st in the Pacific Palisades checking holes for paving in the process of checking they discovered one hole that wasn?t paved they pulled the plate and discovered the hole was filled with water at that time they decided to check the hole and put the backhoe bucket in the hole to check if it was slurried they noticed it wasn?t and just was full of water they put the bucket back in to get the water out and in the process of bringing the bucket back up they pulled on the abandoned 1 inch service tee off the main
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NATIONAL RENTALS | MONTEBELLO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was working on property auguring in the process of auguring they hit and damaged the 1/2 plastic service that cross lot through the property for the neighboring address, Explained to ETD that on epoch it shows service cross lot through property, and they should have checked and located the neighbors service to verify.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CAS DEVELOPMENT | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property to fix houseline in the process of digging up around houseline 3rd party contractor hit and damaged riser, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-03-03 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LADWP was augering for a new power pole when they damaged a 2 inch plastic main, crew responded and dug up control holes, double pinched and fused a new section of pipe. No USA was called in by LADWP
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | STRAIGHT UP CONSTRUCTION | PLEASANTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor dug into gas service while removing soil from the property. Contractor did not call 811 before doing the work.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GOLDEN STATE EQUIPMENT RENTALS | ENCINO | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 1/2ips service while doing demo work. Contractor did not provide delineation and ticket was sent back as no delineation found by the ETD. Contractor never called back and continued work. crew repaired the damaged section and reinstated the service.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2025-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JILK HEAVY CONSTRUCTION | BREA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was working on installing new guard rails for the city of LA in the process of drilling they hit and damaged a 3/4 steel cutback that was not on epoch or GIS, Crew ended up abandoning stub at the SMC, FOS submitted a MUR request for service history to document the repairs on the appropriate service ID.
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2025-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | J L G LANDSCAPING | CANYON COUNTRY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A third-party contractor struck our gas service line. It has come to our attention that the contractor did not contact 811 to have the underground utilities marked prior to commencing their work
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator misread GIS maps.
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2025-02-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SAM JR CONSTRUCTION | SYLMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party digging to install/replace sewer lateral damaged cts service at pig tail of riser belowground. Crew found pipe clamps and tape installed. Crew replaced riser to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2025-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | JOSE SOLIS | PACOIMA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No usa home owner struck service taking out tree stump
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2025-02-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | WARasik damaged cts service while trenching with excavator. Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PRAMIRA | BREA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew dug control hole to squeeze and stop gas. Repairs made with pipe and couplings.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DANDY CONSTRUCTION INC | FRESNO | CA | N | Y | Yes | No | No | Yes | No | No | No | Crew arrived on site and repaired damaged gas service by pinching and fusing new pipe to alter plastic gas service in damaged area.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | EFRIN MANRIQUEZ | PALMDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party excavation damaged from homeowner. No USA Called in for this job.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-10-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | FIOPTIX | CONSHOHOCKEN |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor putting in Fiber service hit our gas service with shovel causing gas leak. Crew was notified and went out to make repairs.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PRAMIRA INC | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | .75 steel service was struck by a micro trencher. No potholing was done prior. Contractor group was still present at the time of arrival. No fire, police, and or media.. Crew arrived and made perminate repairs.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | PRAMIRA | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor had usa but failed to maintain distance from our gas service and main. struck gas service
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | SAUL GARCIA | PALMDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home ownerr did not call USA
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | MCCLOUD ENTERPRISES | APPLE VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage was reported on 6/9/25 to District planner. Damage looks to be from Backhoe, but contractor claimed shovel. Contractor bent serv back and called next day for repairs. Crew went out and put serv back together. Contractor was advised the importance of calling in damages on time to protect from possible public safety.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | J&A RIVERA COMMUNICATIONS | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Fiber crew potholed in PL rather than in bore path and hit service. Crew dug control hole to squeeze and repair
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | J & A RIVERA COMMUNICATIONS INC | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while potholing
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | L&S CONSTRUCTION | PALMDALE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Damaged caused by contractor potholing and hit our serv. Crew arrived and made repairs.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-04-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | TRIPLE H CONSTRUCTION | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 2 inch with bore. Pipe was exposed via pothole but still hit it
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JOSE REYES | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit service with jack hammer while digging footing for block wall. No USA. Crew made repairs with couplings and pipe.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ADAME COMMUNICATIONS INC | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor boring for fiber install hit service that was not marked correctly. Wire led to where locator marked. Marks were 6ft off. No fault of either party
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-03-26 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 12 |  | ADAME COMMUNICATIONS INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Main hit by contractor while potholing
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | DANDY CONSTRUCTION INC | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Bare locating wire.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | TRIPLE H CONSTRUCTION | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor for fiber hit service while potholing. Crew arrived and made repairs.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | TRIPLE H CONSTRUCTION | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while potholing. Crew repaired with 2 couplings and pipe
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | TRIPLE H CONSTRUCTION | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CREW REPAIRED 1/2IPS SERVICE HIT BY CONTRACTOR POTHOLING
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-02-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ADAME COMMUNICATIONS INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while boring. Crew arrived and made repairs.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2025-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2035 |  | 6 |  | MONSTER ROOTER | ROSAMOND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line by third party contractor attempting to put in sewer line. Line directly under power line, in between mobile home park by laundry room. FD on site, evacuated residence 20 people. Per contractor did not contact dig alert. Crew was able to make repairs with couplings and pipe.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES ESTATES | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2179 |  | 1 |  | 222 BUILDERS | CARSON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was demoing pool with mini-excavator when they struck our 3/4 steel gas service. No USA, contractor at fault.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES ESTATES | 2025-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | 222 BUILDERS | CARSON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor pulled 3/4 steel service with backhoe. USA current. Service marked with flags. Flags were 36 away from service
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES ESTATES | 2025-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PROFESSIONAL DRAINAGE EXPERTS | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging trench damaged 1/2 CTS service with hand tools. Contractor did not have a valid USA. There was no fire department, police, evacuations, road closures, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES ESTATES | 2025-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DANIEL RAMOS | HARBOR CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damaged by fencing contractor with posthole digger. No usa was present.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES ESTATES | 2025-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RIOS MASONRY CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging for landscaping, contractor hit pla line with jackhammer. no USA
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES PENINSULA | 2025-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 2 |  | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged 1'''' plastic service with backhoe while trying to replace damaged water line. SCG employee marked it as a no conflict.
Southern California Gas Company | N | LOS ANGELES | PANORAMA CITY | 2025-05-28 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | CARMELO GOMEZ | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party dig-in damage to 2 aldyl-A plastic gas main. Homeowner (Mkrtchyan) hired 3rd party contractor (Gomez) to clear sewer lateral intrusion caused by roots from sweet gum tree. While clearing roots in the parkway, Gomez used a reciprocating saw to cut what he thought was a tree root and mistakenly cut the 2 aldyl-A plastic gas main. This caused an uncontrolled release of gas. SCG distribution crew made permanent, fittings only repair to 2 aldyl-A plastic gas main via electrofusion coupling. Above ground bypass whip was installed to prevent the dropping of twelve single-family residences.
Southern California Gas Company | N | LOS ANGELES | PANORAMA CITY | 2025-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Construction crew hit cutback service line in trench within the middle of street with a backhoe unmarked, USA valid.
Southern California Gas Company | N | LOS ANGELES | PANORAMA CITY | 2025-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | CITY OF LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on trench for wall footing hit 1/2 CTS service with hand tools. Contractor did not have a valid USA. There was no fire department, police, road closures, news media, or evacuations on scene. Off Hour crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | PARAMOUNT | 2025-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 36 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | TCDC TRI COUNTY DEVELOPMENT & CONSTRUCTION | NA |  | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor boring in fiber optics hit 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | PARAMOUNT | 2025-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1/2 plastic service was marked with yellow paint. Locator couldn''t locate and located off of measurements. Marked just outside 2 ft threshold. Mapping error. Service history being updated. Contractor had valid USA.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | NIKO VAGENAS | PASADENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer putting in a fence post hit a 1/2 cts branch service to 104 parkwood. broken and blowing.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR WAS DIGGING WITH BACKHOE TO INSTALL WATER MAIN. CONTRACTOR FAILE TO PROPERLY EXPOSE 1/2PLA GAS SERVICE. VALID USA.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | CJ CONSTRUCTION | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging to replace sidewalk when service was exposed in steel casing. contractor cut casing with hand saw damaging service.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 28 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MEDRANOS CONSTRUCTION | SYLMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner''s contractor began digging without DigAlert notification to begin driveway widening project. While digging with hand tools, contractor hit 1/2 plastic service approximately 1'' from retaining wall. SCG crew arrived to control the leak then proceeded to complete permanent repairs. Contractor and homeowner were informed of DigAlert and the free of cost process.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-10-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SOUTHWIND LANDSCAPING | FONTANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscapers struck plastic service with shovel while digging.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | PRO VINYL FENCING | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 CTS service was repaired by Debris removal crew. Permanant repairs made.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | MYLES CLARK | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Arrived to find a broken and blowing 1/2 CTS service that was hit with a sharp shooter while excavating for a new power pole.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JOHN LOPES BUILD TO DESIGN | PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing company trenching for water hit our 1/2 inch cts service with a shovel causing broken and blowing. Plumbers pinch the service line back to temporarily control gas. No USA was called in. Pasadena OHS crew arrived, pinched service and made permanent repairs by cutting out the damaged section and replacing it with 2'' of 1/2 inch cts and two cts couplings.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | NATURAL PARADISE LANDSCAPE | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contactor hit a 1/2 CTS service with a shovel while trenching for drainage line. Service casing was also cut with a saw.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GLENN LAUMAN | PASADENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner failed to contact USA prior to digging.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | ENHAUS DESIGN BUILD | ARCADIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with pickaxe / shovel for new waterline when 1/2 Pla. service was damaged. NO USA.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | STEPHEN DORECK EQUIPMENT RENTALS | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging with backhoe without potholing for 1PLA service that was marked. 1PLA was damaged. valid USA.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DE FERMIN PAVERS | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading for pavers.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | POOL AND SPA | SYLMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors hit service. Contractors employees were digging to install new pool line when they cut thru service with shovel. Spoke with contractor and they did not call 811 to mark lines.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ANVIL BUILDERS | EMERYVILLE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | During debris removal operations, excavator stuck 1/2 PE service. Contractor had a valid USA ticket. Locator had marked line as abandoned. GIS has service coming off of New York and when it was coming off Altadena.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | WJ LANDSCAPE | MONROVIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with no USA and hit a 1 inch plastic service.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ESCALANTE OMAR | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged line that had a valid USA and marks were accurate.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RAMIRO CERVANTES | NA |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 1/2 plastic gas service while digging broken post of dogear fence with a post hole digger. Homeowner did not call 811. Company crew arrived to control leak and complete permanent repairs. Home owner was informed of DigAlert for continued work.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2035 |  | 6 |  | STEPHEN DORECK EQUIPMENT RENTALS | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging with backhoe next to 1 PLA gas service when damaged service. service was marked correctly Valid USA. contractor failed to hand expose service prior digging with backhoe.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OB SEWER AND SEPTIC | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while digging with hand tool. Facilities were properly marked. Contractor did have USA ticket.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | CITY OF PASADENA WATER & POWER DEPARTMENT | PASADENA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | CITY OF PASADENA WATER COMPANY WAS DIGGING TO INSTALL NEW SERVICE. VALID USA
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | SUE LEIDNER | LA QUINTA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customers contractor was digging with pole digger to install fence and he hit our 1/2 IPS service causing broken and blowing. Contractor put dirt back over the broken service. No USA was called in for this job. ETR evacuated 6 ppl from 1 building. Pasadena OHS crew arrived, dug control hole, pinched service and made permanent repairs by cutting out the damaged section and installed 2'' of 1/2 IPS and two IPS couplings.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | VASILIS TSINOGOLU | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging without USA.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | PAEZ TREE CARE | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damage 1/2 IPS service with shovel while trenching to replace sewerContractor damage 1/2 IPS service with shovel while trenching to replace sewer
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | CHRISTINA CEPIELCK | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer digging hole for fence post. Struck plastic service with shovel.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MIKE K | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner struck gas service while digging to replace sprinklers.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JIMENEZ CONSTRUCTION | GRANADA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowners contractor mistakenly cut plastic gas service line with a reciprocating saw thinking it was a communication line. No USA ticket for the contractor tasked to reinforce the existing foundation. Company crew arrived to control leak and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | STEPHEN DORECK EQUIPMENT RENTALS | PICO RIVERA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit gas service with sharpshooter while digging.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JT ELECTRIC GATES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging with shovel to install new fence post when 1/2PLA gas service was damaged. NO USA
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALEX PEREZ | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 plastic service while digging to repair sewer. NO USA
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 23 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WEN HAO MU | PASADENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowners'' contractor began digging without USA ticket for concrete footing to support metal staircase in process of being built. While utilizing an electric jackhammer with pointed gad, contractor struck 1 plastic gas service pipe, Company crew arrived and controlled escaping gas then completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOME OWNER | PASADENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for drainage hit our 1/2 plastic service with a shovel causing broken and blowing. No USA was called in for this job. No one in 10 districts answered the ARCOS call out so I used the San Bern On Call crew. They arrived, controlled gas and made permanent repairs by cutting out the damaged section and fusing in 2'' of 1/2 plastic and two couplings.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BRYANT NGUYEN | SAN GABRIEL | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching for developer when plastic service was damaged. No USA
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-03-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CHAMPION WALKER | TOPANGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 inch plastic service while digging with shovel. hit our service in three different locations. No USA
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | VICTORIA FINANCIAL CORP | PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line while installing sprinklers. Crew replaced approx 2 feet of damaged 1 plastic pipe. Installed two 1inch couplins, no additional leakage found. Permanent repairs made.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | OLIVER HOME REMODELS | SOUTH GATE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to install sewer hit 1/2 plastic service with shovel right at meter. Marked correctly with USA and within delineation. PAS OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and replacing it with 1'' of 1/2 cts and two cts couplings.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | BRANDON CONSTRUCTION | LA VERNE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching with shovel. 1/2 CTS service was damaged. NO USA
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | RYAN TAO | SAN DIMAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged service with shovel while trenching for irrigation.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2025-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | CITY OF PASADENA WATER & POWER DEPARTMENT | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 plastic service, Water & Power hit service with shovel while digging hole for electrical pole with no USA .
Southern California Gas Company | N | LOS ANGELES | PICO RIVERA | 2025-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DOTY BROS | NORWALK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | On 11/15/25 while excavating with a backhoe for an emergency WATER MAIN REPAIR, Doty Bros damaged a one half inch plastic gas service in 3/4 casing. The Emergency USA ticket was not yet valid. Gas markings by SoCalGas were accurate. SoCalGas crew arrived on site and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | PICO RIVERA | 2025-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CE CONSTRUCTION | POMONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractors replacing sewer lateral damaged plastic gas service while trying to pothole it. No active USA. Old USA expired for other contractor. Flags and mark visible and correct. SCG on call crew made repairs.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2025-12-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | ABC PARKING LOT MAINTENANCE | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to 1 PLA service in 2 PLA provided conduit. Both Conduit and Service were damaged. Removed section of conduit to expose 1 and replaced damages portion with two 1 PLA Couplings and 3'' of 1 IPS pipe
Southern California Gas Company | N | LOS ANGELES | POMONA | 2025-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 7 |  | RAMON RAMIREZ | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor severed 1 inch plastic service while trenching for drainage.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ECOPRANA INVESTMENTS | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 IPS stub with a mini excavator while digging for sewer. At the time of the damage the contractor did not have a valid USA ticket.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2025-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | STRONG | LOS ALAMITOS | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1 PE service with mini excavator, USA was valid but service was not marked out. ETD was on site 6/3/25 which was prior to the service install, a ticket renewal was sent out on 6/10/25/ and 7/7/25 both were closed out by Business system analyst. ETD never returned to mark the service.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2025-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | AC SPRAGGINS ENGINEERING & UNDERGROUND | ONTARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HIT SERVICE LINE . NOT FOR THE ADDRESS ON ORDER. SERVICE LINE ON 4TH STREET JUST EAST OF PALOMARES. SERVICE LINE DID NOT FEED ANYTHING. POSSIBLY AN OLD CURB BOX. USA CSA250761123D was expired . Crew altered main due to 1 1/4 street tee .
Southern California Gas Company | N | LOS ANGELES | POMONA | 2025-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOME OWNER | POMONA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer using a mini backhoe trying to remove a tree yanked our 3/4 steel service out causing broken and blowing. No USA was requested for this job. Pasadena & Downey OHS crew made permanent repairs by completing a service replacement using 64 ft of cts plastic, 1-1/2 standard riser, and two cts couplings.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CITY OF POMONA WATER DEPARTMENT | POMONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 CTS service with backhoe while installing a water service. The contractor failed to expose the service by hand, the service was marked correctly.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2025-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GENTRY BROTHERS | IRWINDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While excavating to replace water main, 3rd party ripped plastic service with mini excavator
Southern California Gas Company | N | LOS ANGELES | POMONA | 2025-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | DSRM CABLE CONSTRUCTION | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ARRIVED TO BLOWING GAS ABOUT 7 FT FROM BUILDING. DROPPED BACK AND STOPPED OFF SERVICE TO 3 BUSINESSES TO CONTROL GAS.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | GENTRY BROTHERS INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damage SCG service . Facilities was marked correctly . Crew arrived , made safe , and preformed permanent repair .
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2025-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 0 |  | CYRUS ELECTRIC & HVAC | WEST HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cyrus Electric team was digging trench to upgrade electrical line near above ground panel. While excavating with electric clay spade, crew struck and severed 1/2 IPS gas service, causing an uncontrolled release of gas. SCG Distribution crew made permanent repairs by altering via socket fusion repair, one foot section of pipe with two (2) socket fusion couplings.
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2025-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JAN ELECTRIC | NORTH HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party excavated with valid USA. Marks accurate within delineation, excavator failed to practice appropriate excavation methods to expose service. Excavator hit service with shovel while digging. Crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2025-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | ERIC PORTILL | PORTER RANCH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property 3rd party damage. Contractor was digging with NO USA when digging out a trench for retaining wall. 1 service was damaged, LCT dropped back and pinched plastic line. Used 3 of once inch plastic pipe along with two couplings for final repair.
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ORLANDO CONCRETE & PAVERS | RANCHO CASCADES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Homeowner hired 3rd party contractor to build retaining wall, they had a valid USA, hit branch service with mini-excavator. GIS Map did not show service branched off of standard, MSA did not have branch ring, and service did not have locate wire. Tech marked standard off of measurements. Crew arrived and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2025-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | FIBERTEL COMMUNICATIONS | SHERWOOD FOREST | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging without USA. 1/2 plastic service was hit with shovel while digging. Crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2025-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 36 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | PACIFIC CONSTRUCTION AND RESTORATION | WESTLAKE VILLAGE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor working on expired USA ticket. USA ticket expired on 5/7/2025. Damage occurred on 5/12/2025.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | POWER BREAKING & DEMOLITION | ALHAMBRA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor damage 3/4 steel pipe on Saturday, in multiple locations.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | CASNER CONSTRUCTION | MANHATTAN BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor (Casner Construction) was machine excavating trench to install footing when they struck our 1/2 PLA gas service. No USA, contractor at fault.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | JASON NAPIER | REDONDO BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was hand excavating trench with shovel to install water service when he struck our 1/2 PE gas service. No USA, homeowner at fault.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2025-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | GOLDMAN LANDSCAPING | HARBOR CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while landscaping, contractor hit pla service with a shovel
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2025-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GARDEN LEAF DESIGNS | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor caused damage to gas service with shovel when exposing water line. failed to notify 811.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1958 |  | 6 |  | MOTHER EARTH DESIGN | REDONDO BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. While digging to install new drainage, contractor hit pla gas line with shovel.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2025-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MANNY VASQUEZ | REDONDO BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Third Party Contractor was trenching to install a retaining wall along the right side of the property and struck the 1/2 cts service with a shovel. Company crew responded and made permanent repairs by cutting out the damaged section and fusing in approximately 1'' of new 1/2 cts pipe.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | SPACE G PLUMBING | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor caused damage to service while exposing water line. failed to notify 811.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2025-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | AATARI | REDONDO BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging to install electrical conduit, contractor hit service with shovel. No usa.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2025-08-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While trenching for water, contractor struck pla service. Due to EFV controlling flow, contractor unaware of damage. Cust called in as a no gas. Valid USA, struck within delineated area, mismarked line.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2025-03-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LOZA CONCRETE INC | COMPTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call for USA
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2025-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | UNLICENSED CONTRACTOR | NA |  | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Found hit service line with shovel damage, 1/2 plastic service damaged while digging for house & front patio foundation. USA Not valid at time of damage. Crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2025-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BYRON ESTRADA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Unlicensed 3rd party contractor was hired by homeowner to find and fix water leak. He was digging without USA when he hit 1/2 plastic gas service with shovel. Crew arrived and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2025-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | BUILDERS HUB RENOVATION | RESEDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner hired contractor to dig trench to install conduits for an ADU. while digging they struck plastic service line with shovel. NO USA
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2025-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SUNSHINE FOUNDATION REPAIRS | NORTHRIDGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per homeowner, Mr. Gerald Cormier, third party contractor was performing excavating at corner of house in anticipation of home remodeling (extension). While excavating with shovel, contractor struck and damaged 1/2 CTS plastic service, causing an uncontrolled release of natural gas. Crew arrived on site, controlled gas and altered service via socket fusion, making permanent repair
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2025-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | GM CONCRETE | LITTLEROCK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging trench to install drainage when they struck plastic service with shovel. NO USA
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2025-02-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ACCESS GENERAL CONTRACTING | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company contractor was digging to install ballards for meter protection when they struck plastic service line with shovel
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2025-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TRINITY BUILDERS & DESIGN | RESEDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor was digging by the riser to expose service line when they struck plastic service with shovel. did have a usa ticket and flags where placed and located out
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2025-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | APEX CONCRETE | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | company was digging to install conduit for an ADU when they struck plastic line with excavator. there was a USA ticket and the marks where with paint and flags. service was marked out correctly
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2025-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | J DE LEON | RESEDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging without USA, for electric conduit installation. While digging, he hit 1/2 plastic gas service. Crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | ROLLING HILLS | 2025-02-10 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 2 | 59 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SOILS ENGINEERING INC | BAKERSFIELD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor using Auger to drill for soil samples drilled and sliced our 2 inch plastc main. EE closed ticket as no SCG, addressed wrong portion of the polygon. Reviewed gas standards with EE.
Southern California Gas Company | N | LOS ANGELES | ROLLING HILLS ESTATES | 2025-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3RD Party Contractor damaged 1/2 CTS plastic pipe with sharp shooter/shovel.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HAROLD KONG | ROSEMEAD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Code 1 condition found by customer service, customer claimed they were smelling gas at the front yard and him and his friend decided to locate the source of the odor, instead of calling the gas company (because he knew the gas company was too busy assisting with the fires). 2 customers evacuated due to 10% gas at foundation and indications in home. Crew was called out and discovered that the 1/2 service had been cut in half with a reciprocating saw. Crew dropped back squeezed the line and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | D CORP | NUEVO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ETD had difficulty locating service and used service history to mark out location. Employee did express that he had notified contractor to call him back if they did not find service when potholing.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | GOLDEN STATE WATER COMPANY | EL MONTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Water company digging to repair leak and hit plastic service with shovel.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOMETOWN DESIGN | REDLANDS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on house struck plastic service with pick.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The contractor hit an unmarked cutback service that our company''s ETD was unable to locate or identify in the service history, epoch, or GIS.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | D CORP | NUEVO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ETD was in on site in the process of verifying services for the contractor when damage occurred, ETD explained that the contractor was moving to fast and did not allow him to wheel out the service location from the cross street. The mark that he had placed was what GIS showed. Employee has been counselled and was informed to make to stop the job for all future scenarios like this. MUr will be submitted as well as correct service location footage to update GIS.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | CONTRACTOR GROUP ADU | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging for the ADU HIT THE SERVICE LINE ND CUT IT COMPLETELY IN HALF using a shovel. contractor tied the service back. crew answered ARCOS, controlled gas by pinching service and made permanent repairs by cutting out the damaged section and installed 2'' of cts and two cts couplings.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ROBERT BRKICH CONSTRUCTION | MONROVIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck 1/2 service with sharpshooter severing it in half. Crew dropped back controlled gas and repaired the service. Service was struck within delineation.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ROBERT BRKICH CONSTRUCTION | MONROVIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck 1/2 service with shovel while excavating for new water line project. Contractor claimed they excavated a steel pipe and thought it was our service line. The line was clearly marked as PLA in the street.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOV CHAO | ROSEMEAD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner attempting to repair irrigation line struck 1/2-inch service with plastic tubing cutters. Service 2 inches beneath PCV pipe. Homeowner did not contact 811 prior to excavating. Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 27 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DANNY TANG | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to install electrical hit our 1/2 CTS service with a shovel. No USA was called in for this job. PAS OHS crew arrived, controlled gas by pinch and made permanent repairs by cutting out the damaged section and fusing in 2'' of cts plastic pipe and two cts couplings.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-08-22 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 4 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 15 |  | CABLE BROTHERS | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole smc prior to engaging with bore causing damage to 4 PE main and service.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-01-04 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | J A SALAZAR CONSTRUCTION | LA HABRA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging without USA
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  |  | NA | OLEGARIO GARCIA | BALDWIN PARK | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner did not respect the legal start time for USA ticket and started excavating prior to the 48 hour legal start time.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  | 0 |  | FIGURE 8 | SAN GABRIEL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with excavator, hit stubbed service.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TURN AROUND COMMUNICATIONS | COVINA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor boring for fiber optics struck cut back service in street. Crew made permanent repairs by fusion. Cutback service was not marked out due to incorrect service history. All company resources utilized, engineering unable to locate archives.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOME OWNER | ROSEMEAD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor and homeowner both failed to call in USA and also maintain safe excavation practices.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | CPL CONSTRUCTION | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck plastic service with shovel while digging trench.
Southern California Gas Company | N | LOS ANGELES | ROWLAND HEIGHTS | 2025-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 47 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | THE PLUMBOLOGIST | NEWHALL | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Plumbing company damaged SCG service line due to locator unbale to locate service (no wire). Plumbing company failed to pothole . company crew arrived and made safe and permanent repairs complete
Southern California Gas Company | N | LOS ANGELES | ROWLAND HEIGHTS | 2025-09-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ELITE 19 ELECTRICAL | SAN GABRIEL | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck plastic service with shovel while digging trench for electrical conduit.
Southern California Gas Company | N | LOS ANGELES | ROWLAND HEIGHTS | 2025-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 47 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | UNKNOWN | ROWLAND HEIGHTS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Customer cut 1/2 IPS service while excavating to replace sewer.
Southern California Gas Company | N | LOS ANGELES | ROWLAND HEIGHTS | 2025-10-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 47 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RRSW CONSTRUCTION | WEST COVINA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer had no USA, severed plastic branch service while excavating to install retaining wall.
Southern California Gas Company | N | LOS ANGELES | ROWLAND HEIGHTS | 2025-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | COLLECTIVE CONSTRUCTION INC THE | DUARTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor ripped plastic service while excavating for sewer repair.
Southern California Gas Company | N | LOS ANGELES | ROWLAND HEIGHTS | 2025-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | ALEX LEE | DIAMOND BAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing water drain cut into our 1/2 ips service with a sawza causing broken and blowing. Pasadena OHS crew arrived on site, Controlled gas by pinching and made permanent repairs by cutting out the damaged section and installed 2'' of 1/2 ips & two ips couplings. No USA was called in for this contractors job.
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2025-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ADRIAN DE LA TORRES | SAN DIMAS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Homeowner hit service while digging for sewer lateral.
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2025-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DYNAMO PLUMBING & DRAIN CLEANING | WEST COVINA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was trenching in the front yard to repair a section of the customers sewer and ended up nicking a 1/2 cts gas line with a shovel. No USA was called in prior to work being done.
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2025-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | ROBERT BLOUNT | SAN DIMAS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor (home owner) was digging in the yard to install a drainage line and ended up nicking the 1/2 plastic gas line near the riser.
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2025-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOSE ERNESTO | NORTH HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Repairs Complete
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2025-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5022 |  | 38 |  | SILVER STAR CONSTRUCTION ENGINEERING | GLENDALE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1 inch plastic pipe with backhoe. USA valid and was closed out as No delineation provided by Contractor.
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2025-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MATHEW WHITE | SAN FERNANDO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Home owner hit 1/2 plastic line while using mini backhoe during landscaping. Crew performed cutback and made repair with 1/2 socket fusion cap.
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2025-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | KEVIN MOLINA | SAN FERNANDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging for drain install hit service while digging through roots. Crew cut back service night of damage and returned next day to alter and reinstate due to roots in way of making repair. Crew replaced 45'' of cts pipe. No evacuations. No USA.
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2025-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | ERNESTO ROJAS | SAN FERNANDO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA...
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2025-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ULTIMATE GREEN CONSTRUCTION | PACOIMA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged service. Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2025-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VCI CONSTRUCTION LLC | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck 1/2 inch service with a backhoe. Service was struck within delineations. Crew conducted permanent repairs. No street closures, no media, no evacuations.
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2025-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | EDUARDO BARRERA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to install sewer. Sawsalled through our service.
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2025-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOHN FISHER | SAN GABRIEL | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor installing fencing for customer struck 1/2 service with post hole digger/ shovel. No evacuations. Crew made permanent repairs by fusion. No USA
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2025-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 32 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BRIGHTVIEW LANDSCAPE DEVELOPMENT | SAN FERNANDO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damage plastic gas service with a backhoe. The contractor did not have a USA. SoCal Gas not at fault,
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2025-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | DEMO LEADERS | WOODLAND HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck service with back hoe. Old marks from ticket visible and marked accurately. Contractor did not have USA ticket.
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2025-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EFRAIN MONTALVO | PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to plant a new tree hit our 1/2 inch cts service with a shovel causing broken and blowing. No USA was called in for this job. Pasadena OHS crew arrived, pinched to control gas, and made permanent repairs by cutting out the damaged section and installed 2'' of cts pipe and two cts couplings.
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2025-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | WESTERN SUPREME ROOTER | ARCADIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 CTS service line damaged by plumbers doing work on sewer lateral. No USA was called.
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2025-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor damaged 1/2 plastic service while digging with hand tools. No USA
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2025-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KIMBERLY MULLEN | SAN PEDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No USA. Customer was trenching in front yard to perform work on sewer line and damaged the 1/2 plastic service with a backhoe. Company crew responded and made repairs by performing a cutback on the 1/2 plastic service. Service was capped approximately 3'' off of plastic.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2025-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ALEXANDER CONSTRUCTION AND ENGINEERING | GARDENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor working on private property struck 1/2 plastic service with mini-excavator. No USA.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2025-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | ALL AMERICAN PLUMBLING | CITY OF FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber working on drain damaged 1/2 plastic service while excavating with hand tools. Contractor did not have a valid USA. Fire department was on scene, but departed upon ETRs arrival. There was no police, news media, or road closures on scene. Company crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2025-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | KARI KENNEDY | SAN PEDRO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was excavating to plant trees and damaged the yellow wrap on a 3/4 steel service. LCT excavated and re-wrapped pipe on 520004277374
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2025-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | STEPHENS PLUMBING & HEATING | SAN PEDRO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on drain installation cut into 1/2 CTS gas service with saw during excavation. Contractor did not have a valid USA. There was no evacuations, road closures, emergency services, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1771 |  | 4 |  | MIRAMONTES CONSTRUCTION | RIALTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Initial address was 745 W. 32nd St. The actual address is 3202 S. Gaffey. Service was damaged by backhoe.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2025-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | TRUE ROOTER & PLUMBING | WILMINGTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Pl service damaged buy contractor while hand excavting to replace plastic service
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2025-05-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | A CO TEMPORARY POWER | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. 3rd party contractor hit PLA service with auger. crew made perm. repairs
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2025-09-25 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 0.75 | 200 | 165 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 50001 |  |  | NA | LENNAR HOMES | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged and bent over 1'' HP Riser covered with dirt and debris, once it was exposed it was found that 1 service valve was leaking below the threads.
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2025-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOT LINE CONSTRUCTION | BRENTWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Contractor hit 1 PLA Service while trenching across street. USA Valid and Marks valid and directly on top of pipe.
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2025-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | GOTHIC LANDSCAPE | VALENCIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Bad locate wire. No ccslb not a accredited business
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2025-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | BUBALO STEVE CONSTRUCTION | MONROVIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to contact Gas Company upon commencing work, contractor had been advised by ETD to contact us for.
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BUBALO STEVE CONSTRUCTION | MONROVIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor hit service with backhoe. Service was mismarked by 10ft due to tracer wire issues. Service was altered with two couplings and 2ft of 1/2 ips pipe and tracer wire was repaired.
Southern California Gas Company | N | LOS ANGELES | SANTA FE SPRINGS | 2025-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TORO ENTERPRISE | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors doing a water main replacement damaged our plastic service while potholing. They used a sharpened probe to help locate the pipe. Upon further inquiry the job foreman said that tool is not to be used when digging for gas lines and would not be used again. USA was valid and marks were good. The SCG crew made necessary repairs.
Southern California Gas Company | N | LOS ANGELES | SANTA FE SPRINGS | 2025-04-11 | Third party excavation damage | Main | Steel | Probing Device | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3983 |  |  | NA | TORO ENTERPRISES | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Employee from Toro enterprise struck 2 inch steel main that was clearly marked with grounding rod device causing 2 inch steel main to leak
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 32 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | BORGESE CONSTRUCTION | SANTA MONICA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was diggng buy hand to replace gas service and came in conact with exsisting servvice
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | ET DEVELOPMENT | WOODLAND HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was working and getting ready to grade the property, 3rd party contractor was digging up 1/2 plastic service to verify in the process of digging it up they hit and damaged service, 3rd party contractor had a USA and marks were good, 3rd party contractor failed to use adequate caution when exposing our service.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DSM ROOTER AND PLUMBING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging on property to repair sewer lateral in the process of digging 3rd party contractor hit and damaged 1/2 plastic service ,3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-09-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JMA GENERAL CONTRACTOR | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Private contractor dug into 1/2cts line while trenching for an ADU. Contractor did not have a valid USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | ERICK MARTINEZ | SANTA MONICA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging with a pickaxe for a sewer repair when he damaged the plastic service on his property. Crew arrived controlled the gas and made permanent repairs. No USA was called in by the homeowner. DPA was notified.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BRONTE CONSTRUCTION MANAGEMENT | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was trenching to install new electrical conduit in the process of trenching they hit and damaged a 1/2 plastic service, 3rd party contractor called in a USA but never delineated the area, so ticket was sent back.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SHIELDS SEWER CONTRACTING | TORRANCE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was working on address to fix sewer line in the process of digging in parkway to fix the sewer 3rd party contractor hit and damaged 1/2 plastic service, 3rd party contractor had a USA but failed to pothole line before digging.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ADEEDO PLUMBING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property to repair sewer line in the process of digging 3rd party contractor hit and damaged 1/2 plastic service, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | JM COMMUNICATIONS | PANORAMA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was trenching in alley to install new electrical Conduits in the process of trenching with backhoe they hit and damaged 1/2 plastic service, 3rd party contractor had a USA marks were within 2 feet of damage but service was installed backwards during previous gas main replacement I looked up the service sketches and nothing showed gas service running backwards.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BONBON ELECTRIC | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property digging to install electrical lines in the process of digging 3rd party contractor hit and damaged 1/2 plastic service, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MONKEY WRENCH | SANTA MONICA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was repalcing a section of backed up sewer when they dug into 1/2 plastic service with a shovel. No USA. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EMMANUEL GALVAN | LA PUENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Damage. Landscapers Excavating to Plant Tree struck 1/2'''' IPS Service with electric clay spade. No USA called in by landscapers.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | CEDAR CONSTRUCTION | DOWNEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was working on property trying to pull out our pipe in the ground in the process of doing that 3rd party contractor damaged 1 inch steel line, 3rd party contractor stated that someone said line was abandoned.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | DELTA UTILITIES | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was working on property to install new gas house lines in the process of digging they hit and damaged 1 inch plastic service, 3rd party contractor did have a USA ticket, and marks were accurate never potholed line prior to starting work.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2025-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | BUILD METHOD CONSTRUCTION | STUDIO CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on the property they were digging a trench in the process of digging they hit and damaged a 1/2 plastic service, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | DIBARA MASONRY | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per SA40 3rd party contactor , while digging to water proof the side of the house, struck and damaged 1/2inch IPS service, causing an uncontrolled escape fo gas. Crews arrived on site, controlled and made permanent repairs via socket fusion of two (2) 1/2 IPS couplings and a 1 inch section of 1/2 inch IPS pipe.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CB LANDSCAPING | STUDIO CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging to a trench to install conduit to back adu when they struck plastic service line with shovel. NO USA
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 36 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | VALLEY BUILDERS | SHERMAN OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Spoke with Andy, Vartan, and Sarkis Grigoryan on site. Andy informed FOS2 that they were demo''ing property to build new home. Stated plans were in place to abandon gas service but could not wait. SCG crew arrive on site to identify 3/4 STL service (about 50'') section hanging in excavation site and fully exposed, wrap had been disturbed during the excavation process by backhoe. Crew performed cutback inside of private and located SMC in street.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-12-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | LADWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP performing water service tie over. While excavating service to main connection, water worker struck 1 PE gas service, causing an uncontrolled release of gas. SCG crew arrived on site to control and make permanent repair via socket fusion using two (2) 1 IPS socket fusion couplings and a one foot section of 1 IPS PE pipe.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP performing emergency water main repair. After potholing for 1 PLA service, LADWP foreman was unable to successfully confirm locate. Upon findings, ETD on site for HP S/B left job site to make phone call at company vehicle for further direction from local management. During this time, LADWP used back backhoe in an attempt to remove large spoil from inside excavtion site, resulting in severing 1 plastic gas service. ETD left detailed notes on attempt to mark 1 plastic service; sited signal continuity, referencing service history, inductive method. Marks, measurements, and signal continuity were confirmed by FOS2 (JC) on site during field audit with another ETD.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-01-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15001 |  |  | NA | KOBI SERAZI | ENCINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was developing new multi-unit residential building. While excavating with backhoe for sewer tie-in, third party contractor struck and severed 2 plastic main, causing a sudden and uncontrolled escape of gas. SCG crew arrived on site and made permanent repairs via electrofusion.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HOME OWNER | SHERMAN OAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor working for homeowner/real estate agent hit our branched 3/4 Adyl-a with a shovel. There was no USA.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | LADWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Valid USA, DWP struck an unknown stub, that was a cutback. unmarked
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LEILA KARIMPOOR | SHERMAN OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor for homeowner was using a hacksaw and cut 1/2 Adyl -A. Contractor was digging for drainage pipe; no USA.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2179 |  | 1 |  | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor removed planter from property exposing branch service in the process. Contractor cut into service causing leak. Company crew was able to clamp leak and no additional leakage was detected. there was no emergency services, road closures, evacuations, or news media on scene. Information on service was sent to district supervision to address exposed line.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | M TEK COMMUNICATIONS | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Field findings reveal locator incorrectly marked 2 PA main, causing an intrusion damage from directional bore at 4225 Kester Ave. Delineation spans from south PL of 4211 to Sutton St. Locator documented hooking up to 4215 and marking 2 PA main on short side. Locator stated, footage is wrong on epoch...main found it close to the curb in front of address. Locator did not verify GIS footage on site, which was later confirmed by local management. Locator did not reference using service history to verify location of 2 PA main. Locator documented access issue for 4240. Locator did not reach out to local management after discovering what he believed to be inconsistent information with field and GIS and company records.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-05-19 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  | 1 |  | M TEK COMMUNICATIONS | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Field findings reveal locator incorrectly marked 2 PA main, causing an intrusion damage from directional bore at 4225 Kester Ave. Delineation spans from south PL of 4211 to Sutton St. Locator documented hooking up to 4215 and marking 2 PA main on short side. Locator stated, footage is wrong on epoch...main found it close to the curb in front of address. Locator did not verify GIS footage on site, which was later confirmed by local management. Locator did not reference using service history to verify location of 2 PA main. Locator documented access issue for 4240. Locator did not reach out to local management after discovering what he believed to be inconsistent information with field and GIS and company records. Damage at 4211 occurred after initial 2? PA main damage at 4225. Same project and contractor performing work. During repair of 2? PA main damage on 5/20, SCG crew located and marked out entire project scope from 4211 south PL to Sutton St. Technician did not accurately mark service for 4211 which resulted in intrusion damage from directional bore on 5/22.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-09-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | GOLDEN EMPIRE BUILDERS | SHERMAN OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating without a valid USA. The contractor was excavating for new foundation for a new fence/wall that is to be installed for a new residential dwelling. The USA for this property was for a SoCalGas job where SoCalGas installed a new service. SoCalGas crew responded, controlled the release, then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 0 |  | CHAROLETTA J RANSOM | CHINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contract crew was performing demolition work for property owners. While excavating in private property with jackhammer, square spade severed 1 PLA gas service, causing an uncontrolled release of gas. SCG crew arrived on site to control and cut back service at PL, leaving a 1'' section inside of private property.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-02-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | MONTEJO DEMOLITION EXPERTS | VAN NUYS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While demolishing existing single family dwelling, Montejo Demolition Experts exposed 3/4 STL casing with live 1/2 CTS service. Crew on site displaced gas line to the south side of the lot line and continued to excavate. On 2/28, gas leak / damage was called and SCG distribution crew arrived on site to discover exposed 3/4 STL casing, riser and regulator exposed and on south side of lot. Crew performed cutback of approximately 10'' and capped 1/2 CTS service.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-09-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | GARCIAS LANDSCAPING | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Garcia''s Landscaping and Tree Service excavating trench at front side of property for fence installation. While excavating with backhoe, 1 PLA service was struck and severed. EFV activated and working properly upon arrival of SCG team. SCG Distribution crew arrived on site to perform control and permanent repair of damaged section of pipe via socket fusion of two (2) 1 couplings and a 2'' section of 1 IPS pipe.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | LIFELINE FENCE | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contract crew was on site 5016 Nagle Ave, Sherman Oaks, excavating footing for fence installation. While excavating with shovel, contract crew struck and damaged 1/2 CTS service feeding 5024 Nagle Ave, Sherman Oaks, causing an uncontrolled release of gas. SCG Distribution crew arrived on site to control and permanently repair damage via fittings only repair with 1/2 CTS socket fusion coupling.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | JMS ENCINO | SHERMAN OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCG Distribution crew arrived on site to find PLA encased service exposed, bent back and leaking at MSA area. Workers on site are building new single family dwelling. Workers onsite gave SA28 contact of Yuda Banos who reported this is an owner/operator build. SCG Distribution crew excavating to cut back 1/2 PLA service at property line for safety
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2025-01-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JMR THE BUILDING CO | NORCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor was excavating with a valid USA. The contractor was excavating with a backhoe for a new sewer line that is to go to a new multifamily residential dwelling, and they struck a 1 inch plastic service. USA marks were accurate, and the contractor failed to maintain clearance after identifying the marked-out gas line.
Southern California Gas Company | N | LOS ANGELES | SHERWOOD FOREST | 2025-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  |  | NA | FATUMA NASANGA | SHERWOOD FOREST | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was grading lot when they struck steel service with equipment. NO USA
Southern California Gas Company | N | LOS ANGELES | SIERRA MADRE | 2025-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  |  | NA | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to expose service prior digging with mini excavator. marks were visible.
Southern California Gas Company | N | LOS ANGELES | SIERRA MADRE | 2025-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PLUMBING COMPANY | SIERRA MADRE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging without USA. Contractor damaged PLA. gas service while digging to repair sewer.
Southern California Gas Company | N | LOS ANGELES | SIERRA MADRE | 2025-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ERIKA ERICKSON | SIERRA MADRE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Found broken and blowing 1/2 inch cts service, homeowner hit with shovel while trenching for irrigation with no USA. Altered service to eliminate hazardous conditions
Southern California Gas Company | N | LOS ANGELES | SIERRA MADRE | 2025-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SCP CONCRETE CONSTRUCTION | CHINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating for new ADU struck 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | SOUTH EL MONTE | 2025-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | CEG CONSTRUCTION | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor steel service with excavator, and pulled it off the main.
Southern California Gas Company | N | LOS ANGELES | SOUTH EL MONTE | 2025-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | J DE SIGIO CONSTRUCTION | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working on behalf of the City of South El Monte, and in the process of potholing for the accurately marked service damaged 1/2 PE plastic gas service with shovel.
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | JORGE VARGAS | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors damaged 1/2 plastic service while digging trench for sewer line. Service was marked properly but contractors failed to protect facilities already in place. Crew altered service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2025-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor claims no marks, but marks were visible from excavation in the fast lane. Marks were also visible right next to trench but covered by the pile of dirt. Pulled service up with backhoe.
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2025-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MICHAEL WALSH | S. PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called prior to excavation which led to damaged line.
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2025-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 24 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALFONSO VARGAS | POMONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONSTRUCTION PERSONNEL HIT SERVICE WHILE DIGGING UP SEWER. NO USA.
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2025-01-15 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 4 |  | NPL CONSTRUCTION | BREA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NPL 2nd party contractor struck 1/2 service with shovel while trying to locate service for replacement/alteration for gas company work (encroachment).
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2025-10-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | GENTRY BROTHERS | BALDWIN PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 1PLA gas service with backhoe. Marks were off. appears that locator marked old service not new service. contractor had a valid ticket. will follow up with ETD by counselling. will also reach out to OP-Qual dept.
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2025-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CLIFFORD DOUGLAS MASONRY | SOUTH PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY CONTRACTOR DIGGING WITOUT USA. CONTRACTOR DIGGING TO INSTALL WATER SERVICE
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2025-10-29 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3737 |  | 6 |  | GENTRY BROTHERS | IRWINDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with backhoe to install new water line when 2pla gas main was damaged. marks were accurate and visible. Valid ticket.
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2025-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GENTRY BROTHERS | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor found steel pipe they thought was the service. The continued to dig and struck plastic service.
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2025-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MR ORTEGA PLUMBING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging without a USA. contractor damage 1/2PLA gas service while digging to install new water service.
Southern California Gas Company | N | LOS ANGELES | STEVENSON RANCH | 2025-09-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | TEJON CONSTRUCTION | PALMDALE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor hit 4 stub while trenching with backhoe. Contractor told Locator on new ticket that marks were not needed from Gas becuase marks from old ticket were still visible. Additionally the concrete driveway panel was replaced after the Locator confirmed the marks for the stub.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | HM ELECTRIC | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HARUT MIRZAKHAMIAM from HM Electric was hand excavating with pick for electrical trench. 1 PLA gas service was struck with pick and caused an uncontrolled escape of gas. SCG distribution crew made permanent repair via alteration of 1'' section of 1 PLA gas service with socket fusion couplings (2).
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2025-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 0 |  | SO CAL DIRT ENGINEERING | SIMI VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | SO CAL DIRT ENGINEERING, INC. was on site to perform grading for new construction of home. While excavating with backhoe, 2 STL pipe casing was pulled, snapping 1/2 IPS gas service, causing and uncontrolled release of gas. SCG crew arrived on site and controlled gas. Cutback was performed outside of construction area. Remaining footage from main to cutback is 42'' After investigation from local management, it was discovered this line was previously cutback inside of private property, as previous attempts to locate this service were unsuccessful. Service History revealed inaccurate information, documenting inactive service inside of private property.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2025-12-04 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 0 |  | ALL PLUMBING SOLUTIONS & ROOTER | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber for homeowner was trenching to replace sewer line under tree in parkway. Plumber was digging with shovel and struck our 2 plastic main. No valid USA.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | CALIFORNIA BUILDERS | STUDIO CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Was notified on 5/21 by FPA (C.Hernandez) about difficulty locating a branch PLA service on private property. FPA stated developer (Amir Cohen) had confirmed burying the riser and could be located on property. FPA confirmed with local Saticoy management team scheduled date to pothole riser. On 6/12, FPA confirmed on site, damage to 1/2 CTS branch service. Service had been severed, folded back and tied with wire. SCG distribution crew arrived on site make permanent repair via abandonment at branch to standard connection.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 40001 |  | 30 |  | NORTHSTAR CONTRACTING GROUP INC | NEDERLAND | TX | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 2 inch plastic service removing palm tree for parking lot remodel, did not have valid USA. Upon first on scene arrival, ETR found service broken but not blowing. Universal employees escorted ETR to a SCG owned fire control valve Universal studio employees used to shut the gas off. Per Universal Studios employees on-site, Fire Department advised them to shut off fire control valve resulting in approx. 4500'' of 4 inch main to be de-energized and approx. 30 outages between Universal City Walk and 3/4 of Universal theme park. Crews replaced damaged section of 2 inch plastic service to make permanent repairs and purged at 3 end of main locations to 100% gas to re-energize the facilities. See personnel tab attachments for total list of represented responders to the incident.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2025-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | SMART GARDENS | WINNETKA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Smart Gardens digging trench to lay new sprinkler line. While cutting out old drain line, contract crew cut through 3/4 STL casing with 1/2 CTS plastic gas service encased. SCG arrived on site to control gas via upstream control hole. Permanent repair was made with socket fusion of 1'' section of 1/2 CTS pipe and two (2) 1/2 CTS socket fusion couplings
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2025-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1766 |  | 1 |  | UNKNOWN | SUN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | H/O Contractor workers damaged 1/2 plastic service. USA ticket is valid, and all gas facilities are located and marked in a timely manner.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2025-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SHEILA MCCLURE | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged 1/2 plastic service while grading. No USA called in for this job.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2025-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  |  | NA | PACIFIC OUTDOOR LIVING | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line by construction company. Service was bent and tied prior to arrival. Distribution crew made permanent repairs by altering service with two 1/2 IPS couplings and a foot of 1/2 IPS coiled pipe.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2025-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | HAKOP AGAZARYAN | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner damaged 1/2 plastic service with shovel. Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2025-05-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ARTHUR BAGOUMIAN | SUN VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rdc party contractor damaged 1/2 plastic line in casing. No USA was called, and H/O will not give information on Contractor.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2025-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 22 |  | FRANCISCO QUINTERO | UPLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. 3rd Party contractor/ landscaper hit 1/2 PLA Service while digging to plant tree in apartment complex courtyard. CSF declared evacuations for 2 units. LAFD shut down all manifolds is complex. Crew arrived and preformed perm repairs and lifted evacs once safe.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2025-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BRYAN ADONEY MONTES | ARLETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging on the side of home for planter and hit 1/2 gas service with chipping gun/ clay spade type of tool. Contractor did not have a valid USA. There was no valid USA. There was no fire department, police, road closures, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2025-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  | 0 |  | TOP ROOTER | SOUTH GATE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Code one gas at foundation, evacuated 4 units 22 people effected, claims was notified. After crew investigated leak, they determined it was a damage after further investigation a 3-party contractor damaged 3/4 service. Crew used clamp for final repair
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LADWP | VAN NUYS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP crew pulled 3/4 steel service from gas main
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2025-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | STEVE TRUJLLO | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant hit 1/2 CTS service while digging trench in yard. There was no valid USA. There was no fire department, police, evacuations, road closures, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2025-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 0 |  | TOMER MELZERIAN | SUN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner dug and struck 1 steel service while digging did not have a usa.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2025-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ELECTRICAL MANAGEMENT SYSTEMS | PLACENTIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party hit 1/2 inch ips service and pinch service back. FD not on scene upon company arrival. Service was accurately marked by locator prior to damage. Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2025-04-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | SILVER STAR CONSTRUCTION | GLENDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Silver star construction damaged 1 inch plastic service with backhoe. USA marks were accurate. Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2025-01-20 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ASHOT MAKARYAN | SUNLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 steel main damaged by pick axe. Crew installed clamp. No USA
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | EASY PLUMBING | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor doing water pipe work accidentally hit gas line. Contacted dispatch and got crew out. LCT Gonzalez came and repaired the gas line. Fire department evacuated 5 buildings and 30 people in total
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ORZHEN RUSHANYAN | SUNLAN | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner performing construction work to backhouse damaged our service with backhoe. LCT completed permanent repairs. The homeowner called in USA after hitting our service. ETD went out to locate the next business day. No injuries, no fatalities, no street closures. Gas did not migrate to structure.
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2025-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CHRIS HOVAKIMYAN | SUNLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor damaged 1/2 plastic service. NO USA Called in for this job.
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2025-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | UNLICENSED LABORER | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging around tree root
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2025-05-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MAX PAJANI | SUNLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner removing tree at lot line hit service feeding 9711 wheatland. Found service pinched back. Crew replaced damaged portion of service. Delivered dig alert information packet to occupant and advised to call for valid USA.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HERCON CONSTRUCTION | BALDWIN PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor Damaged 1/2-inch plastic service. No USA called in for this job.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2025-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KARA E HILLIARD | SYLMAR | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service was pulled by backhoe no leakage
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2025-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | A ESQUIVEL | SYLMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Unlicensed contractors working for home owner damaged service in two locations, the first location was completely severed and the second location had a 1/4 cut.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2025-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3270 |  | 1 |  | CG CALIFORNIA GATE & ENTRY SYSTEMS | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third-party contractor boring to install electrical conduit damaged our 2? service. Contractor potholed but not deep enough to expose our line. Permanent repairs were made by altering service. No injuries, no fatalities, no street closures. Gas did not migrate to any building. No evacuations. Pictures taken by supervisor on site.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2025-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SARA TOREL | SYLMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. 3rd party contractor hit 1/2 CTS riser while excavating with backhoe. FD gone upon arrival. No Evacs. No pictures taken.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2025-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HECTOR RAMIREZ | SYLMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging trench for electrical conduit damaged 1/2 plastic service. Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2025-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1558 |  | 2 |  | ROOTER HERO PLUMBING | MISSION HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Roto Hero damaged 1/2 inch plastic service digging to repair sewer with hand tools. Crew replaced damage section of service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2025-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | UBALDO MUNOZ | SYLMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor performing electrical work damaged 1/2 inch service with a shovel. Permanent repairs were completed by performing a service alter. No injuries, no fatalities, no street closures, no police, no fire department.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2025-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LUIS ARROYO | SYLMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party Contractor damaged 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2025-01-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LAWDP hit service line while trenching for water. Permanent repairs completed by altering service. No injuries or fatalities. No street closures. No FD, no police, no media.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2025-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | ELECT BUILDERS | GRANADA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No usa struck gas line.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2025-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LADWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | LADWP was digging with valid USA ticket and hit our service. Markings were inaccurate. I spoke to ETD, he lost signal after a small brick wall. ETD located to the best of his ability but was off by about 10ft. A counseling session was held with ETD to use all his resources prior to marking. Permanent repairs were completed by altering service. No evacuations, no injuries, no fatalities, no street closures, no police, no media, no fire department.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2025-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | DSO | RESEDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. 3rd Party Plumber hit 1/2 CTS PLA service while digging for water line repair. No FD on site when crew arrived
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2025-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | MEJIA S LANDSCAPING AND TREE SERVICE | POMONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3 party damage. Contractor damaged 1 service when grading with NO USA contractor was setting wooden stakes for planter when damage was done. Service not blowing service had an EFV LCT pinched service and used 2 couplings plastic along with two feet of one inch plastic pipe for final repair.
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2025-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | AMIN FARAPOUR | TARZANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging to install conduit in trench. contractor struck service line
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2025-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DAY LABORERS | TARZANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging with no USA. Hit 1/2 plastic gas line with pickaxe while digging for ADU foundations. Crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2025-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | HOME IMPROVEMENT SERVICES | TARZANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hired by developer to install water line. Contractor damaged 1/2 plastic gas line while excavating with shovel. No USA for excavation. Crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ROBIN DANNY | TARZANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging trench damaged 1/2 CTS service with hand tools. There was no fire department, police, evacuations, or news media on scene. All roads remained open. No comment was given on the type of work being performed. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2025-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | SAKO HALEBYAN | TARZANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged 1/2 CTS pipe. No USA called in for this job.
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2025-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  |  | NA | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ATF EIR. Contractor ripped out steel service with backhoe. Crew arrived, stopped gas leak, and threaded new riser and installed 3/4 service valve. No witnesses onsite, No USA for excavation.
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2025-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | JM COMMUNICATIONS | TARZANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging with equipment contractor struck plastic service line NO USA
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2025-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | INNOVA CREATIVE SOLUTIONS | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Construction of new property. While excavating new home, construction crew on site relocated gas riser and plastic branch service to left front of property, directly adjacent to neighboring lot line. After having moved gas service, construction crew was excavating for new trench of gas and water. During trench excavating, construction crew severed gas line. Construction crew tied back line in an attempt to control uncontrolled escape of gas. SCG crew arrived on site to make alteration via socket fusion cap repair inside of private property. EMS marker left at cutback site.
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2025-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | TARZANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging around foundation contractor struck plastic service NO USA
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2025-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | FRANCISCO DELGADO | TARZANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3 party contractor damaged 1/2 CTS plastic service. Homeowner hired contractor to dig trench with NO USA to repair sprinkler system when damaged plastic service. Crew dropped back pinched line used 2 CTS plastic couplings along with 2 feet of CTS pipe for final repair.
Southern California Gas Company | N | LOS ANGELES | TEMPLE CITY | 2025-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MILESTONE CONSTRUCTION | ROWLAND HEIGHTS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor failed to maintain safe digging practice over Gas service.
Southern California Gas Company | N | LOS ANGELES | TEMPLE CITY | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | AMERICAN WATER | ROSEMEAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck 1/2 plastic service with backhoe, crew squeezed and conducted permanent repairs. Area was properly delineated and was struck within 24 inches of our marks.
Southern California Gas Company | N | LOS ANGELES | TOLUCA LAKE | 2025-09-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | D&D CONSTRUCTION SPECIALTIES | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor damaged plastic service. No USA called in for this job.
Southern California Gas Company | N | LOS ANGELES | TOLUCA LAKE | 2025-05-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | VICTORIO AND SONS | TOLUCA LAKE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged on a 1-inch plastic service. No USA Called in.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2025-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ANN BIRBECK | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowners were hand excavating trench to install retaining wall when they struck our 1/2 PE gas service. No USA, homeowner at fault.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2273 |  | 2 |  | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor (Doty Bros) was machine excavating trench with backhoe to install water main when they struck our known / marked 3/4 steel gas service. USA valid, contractor at fault. Foreman mentioned he knew the accurate marking was there and instructed his operator to excavate with backhoe assuming our service was deeper. No hand excavation performed.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2025-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LEGACY SEWER & DRAIN | SIGNAL HILL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor accidentally damaged plastic service while trenching to install water line. USA was not called.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2025-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | SOLEX CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors damaged 1 plastic service line while grading and digging to install fencing, no USA called in. Crew altered service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2025-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | STEPHENS COMPANY | FOUNTAIN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor came in contact with are gas service while excavating for water and sewer upgrades NO USA
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2025-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BRIONES COMMUNICATIONS | SYLMAR | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | contractor hit service with a shovel. USA vas valid, but contractor dug outside delineated area. service was unmarked.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2025-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MR DRAINS | WILMINGTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber working on sewer repair damaged 1/2 CTS plastic service with a rotary hammer during excavation. Plumber did not have a valid USA. There was no fire department, police, news media, evacuations, or road closures on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2025-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CITY OF TORRANCE PUBLIC WORKS | TORRANCE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | City of Torrance Water Department was excavating in to repair a water leak when they damaged a 1/2-inch CTS service. Service was marked incorrectly due to bad signal from locate wire since service was incased along with incorrect measurements from service history.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2025-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | GREG FRAME CONSTRUCTION | LA CANADA FLINTRIDGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for new footing when they damaged 1/2 plastic service with hand tools. Contractor did not have a valid USA. There was no emergency services, road closures, evacuations, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2025-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | EDWART SINANI | TUJUNGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner/contractor damaged branch service trenching for utilities for ADU addition. No Valid USA. Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VAHE ISAGHULYAN | TUJUNGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2-inch plastic service. No USA called in for this job.
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2025-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | CRYSTAL FLORES | TUJUNGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No usa called
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2025-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DRAIN KING | CHATSWORTH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Drain King company performing landscaping work for homeowner hit our service line with a shovel. Permanent repairs were completed via service alter. No evacuations, no injuries, no fatalities, no police, no media, no fire department and no street closures.
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2025-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | JACK YAACOUBIAN | TUJUNGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner caused damaged by not calling 811
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2025-07-12 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 40001 |  | 107 |  | CEM CONSTRUCTION | MONTEBELLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage to company property, 3 party damage. Contractor failed to hand expose 2 plastic main while excavating to install new water main. Crew dropped back dug control hole, pinched plastic main used 4 plastic elbows along with 8'' of 2 plastic pipe for final repairs. Pictures were sent in to claims CS took over after main was reinstated to restore the homes that were affected.
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2025-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | JOSH HALL | VALENCIA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit 1/2 service line while performing landscaping work outside. Homeowner was digging before area was delineated. At the time of arrival, crews found service bent and tied, not blowing gas. Permanent repairs were made utilizing 2 1/2 CTS couplings and 1'' of 1/2 CTS pipe. Gas did not migrate to structure.
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2025-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SPECTRUM | PALMDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1 inch service while performing boring operations. Service was located and marked.
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2025-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | CALEX ENGINEERING | NEWHALL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging up buried brick wall to waterproof it when they hit our service line. Contractor tied our service back. Permanent repairs were made by altering service.
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2025-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | CT ELECTRIC | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party struck gas service.
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2025-02-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JAG UTILITY CONSTRUCTION INC | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Contractor hit plastic main while trenching for drainage. Crew performed main alt. for permanent repairs
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2025-04-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 32 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | POWER PLUS | SUN VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | No | No | New development with no houses built yet. Active ticket was called but this specific service was completely buried and not marked. ETD made verbal contact with PowerPlus foreman to inform them of buried lines. Foreman assured ETD that the temporary power poles would be located along the fence away from the area where damage occurred. Permanent repair was made by raising the service above ground and capping the end.
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2025-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | SPECTRUM | PALMDALE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party Contractor damaged unknown 2 inch stub. USA current, stub not located due to no information on company resources.
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2025-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LG BUILDERS | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging in yard when they struck plastic cts service with shovel. NO USA
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2025-05-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 30001 |  | 51 |  | MONTEJO DEMOLITION EXPERT | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Montejo Demolition Experts on site to perform demolition of lot for upcoming new home construction. While excavating with backhoe, Montejo Demolition Experts struct and damaged 2 PLA main inside of construction area. Active USA, but excavator worked outside of delineated and proposed area. SCG crew on site controlled gas via pinch, resulting in approximately 50 outages.
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | RICHARD LAGUNAS | VALLEY VILLAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging to install new fence contractor struck steel service with equipment. NO USA
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2025-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NA | VALLEY VILLAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while tearing down a building contractor broke service valve with backhoe. NO USA
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 16 |  | HR PLUMBING | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on sewer repair damaged 1/2 CTS service with hand tools. Contractor did not have a valid USA. There was no emergency services, evacuations, road closures, or news media on scene. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2025-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | FENCY BUILDERS | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Fency Builders hired by property owner to builder electric fence inside of private property. While excavating for fence footing, Fency Builders team struck 1/2 CTS gas service with shovel, causing an uncontrolled release of gas. SCG Distribution team arrived on site to control and make permanent repair via socket fusion coupling, altering 1'' of damaged pipe with two (2) 1/2 CTS socket fusion couplings.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 3 |  | SHARMA GENERAL ENGINEERING CONSTRUCTION | MOORPARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While excavating for new construction, Pinner Construction crew was operating auger. While augering, crew struck 2inch plastic service inside of private property.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | LADWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP performing new water main installation. While excavating with backhoe in trench, LADWP operator pulled on 3/4 STL service. The force of the pull caused the steel to plastic transition to snap at the 1/2 CTS, causing an uncontrolled release of gas underground. SCG crew arrived on site to control gas and make permanent repair via socket fusion repair and alteration of 15'' section of service.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | LADWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP was excavating with a valid USA. LADWP was excavating to install a new water main. While excavating with a shovel, they accidentally struck an unmarked 1/2? plastic service. The service for this address is not showing in EPOC or GIS. SoCalGas crew responded, controlled the release, then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GREGG DRILLING LLC | SIGNAL HILL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Gregg Drilling LLC crew was on site to perform drilling for soil testing. While performing operation with 8 auger, crew struck 1 inxh plastic gas service underground. SCG crew arrived on site and made repair via cutback of 1 PLA service, removing 30'' of 1 inch plastic service.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NATHAN | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | FOUND DAMAGED 1/2 CTS SVC DIG IN BY HOMEOWNERS WORKER WITH SHOVEL
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JE&R CONSTRUCTION | OXNARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | JE&R Construction was excavating trench on south gutter line to install power conduit upgrade for new building construction at 14810 Delano St, Van Nuys. While excavating with backhoe, JE&R crew struck and severed a 1/2 PLA service that was cutback inside public property. SCG Distribution crew arrived on site to control and cap cutback 1/2 PLA service inside of trench. Remediation work will be scheduled for abandoning the cutback at SMC.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | COBLENTZ PLUMBING AND SEWER CONTRACTORS | BURBANK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Coblentz Plumbing & Sewer Contractors was excavating in the street for new sewer lateral installation of 15009 Wyandotte St. While excavating, Coblentz exposed 1/2 CTS service in casing feeding 15012 Wyandotte St. No release of gas or damage. SCG crew identified tension on 15012 Wyandotte St service caused by casing. Per local management request, SCG crew removed 6'' section of 3/4 STL casing to alleviate stress in 1/2 PLA service. SCG crew reinstated service and altered via 1'' section and two 1/2 CTS socket couplings.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-09-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | AMBY GRIGROYEN | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property 3 party damage, 3 party contractor was digging trench for sewer with NO USA when 3 plastic main was damaged. Crew dropped back dug control holes, pinched main used 4 of 3 plastic pipe along with two 3 electro couplings for final repair.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MARIA MATINEZ | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged to company property 3 party damage, Contractor was digging with No USA when damaged half inch service that was branched off and stubbed. LCT dropped back and pinched line used 1/2 IPS plastic cap for finale repair.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP was performing excavation activities with a valid USA. LADWP was installing a new water service, and they struck a1/2 plastic service with the backhoe while excavating
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 0 |  | CASA VICTORY | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was demolishing multi-unit property with backhoe. PL cutback was performed on 11/21/25 for 15831 Victory Blvd and operator mistakenly thought gas service to 15833 Victory Blvd had been abandoned. Consequently, operator thought the gas riser at 15833 Victory Blvd was not live and struck it with the backhoe bucket. This caused a full severance and an uncontrolled release of gas. SCG crew arrived on site to perform service cutback at property line of 15833 Victory Blvd.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 5 |  | RAPID PLUMBING | INGLEWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner of multi-unit complex hired 3rd party plumbing crew from Rapid Plumbing to install new water line. While excavating trench, plumbing crew struck 1/2 IPS gas service with shovel, causing an uncontrolled release of gas. Damage resulted in 8 dropped meters, including branch neighbor at 16044. SCG distribution crew made permanent repair via fittings only repair of one 1/2 IPS coupling
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BHL INDUSTRIES INC | LYNWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party contractor was excavating with a valid USA. The contractor struck a marked 1/2 plastic service with a backhoe while excavating. The excavator thought the service was abandoned because the gas meter was removed. The service was marked out correctly.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | ROCIO FUERTE | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, homeowner was digging trench for retaining wall with an expired USA. Homeowner damaged 1/2 CTS service. LCT dropped back and dug control hole, used two 1/2 CTS couplings along with 2 of 1/2 CTS pipe for final repair
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-03-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 10 |  | HRD REALTY INC | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Saticoy CSF received call from occupants at 14909 Hatteras St, Van Nuys, claiming of ''no gas.'' CSF confirmed no gas at MSA and stated neighboring property at 5809 Hazeltine Ave, Van Nuys, was demolished and riser had no gas. SCG crew arrived on site to confirm no gas at riser and recent excavation at property line to tie in new sewer lateral. SCG confirmed 3/4 STL casing within excavation for sewer lateral install. SCG crew found severed 1/2 CTS service, bent back and tied off.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | LADWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP was excavating for a new water main, and they had a valid USA. DWP was using hand tools to excavate, and they accidently struck a 1 plastic service with a shovel. DWP stated the dirt was hard and they thought they were further awa from the gas line than they actually were.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2025-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | BRUCE COY | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA on file, home owner was installing new sewer line for his ADU and while excavating damaged our 2 adyl-A main with pick axe.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NEW ELEVATION CONSTRUCTION | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was in the process of grading the property and in the process they hit and damaged a 1/2 plastic service, 3rd party contractor had no USA
Southern California Gas Company | N | LOS ANGELES | VENICE | 2025-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | ORO COAST BUILDERS | WEST HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property to install a new sewer line in the process of digging they hit a 1/2 plastic service, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2025-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  |  | NA | BEAVER DEVELOPING AND REMODELING INC | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer contractor was grading land with a back-ho and damaged the buried gas service. Contractor did not call-in damage. Customer called it in as gas smell. Locate & Mark was correct.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2025-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CHRIS MULHERN DBA MONTANO S LANDSCAPING | VENICE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property in the process of working they claim tree company damaged service but after investigating incident someone was digging over service and damaged service, when showing up on scene no one was there looked up address no USA could be found.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2025-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CHRIS MULHERN DBA MONTANO S LANDSCAPING | VENICE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on Property digging to fix water line in the process of digging 3rd party contractor hit and damaged 1/2 plastic service with shovel, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2025-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NEW FLOW PLUMBING | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging on property to install new sewer line in the process of digging 3rd party contractor hit and damaged 1/2 plastic service, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2025-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ADEEDO PLUMBING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property digging to install new sewer line in the process of digging they hit a 1/2 inch plastic service, They had no USA.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2025-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | PLUMBING AND HEATING | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging on property to install new sewer in the process of digging they hit and damaged a 1/2 plastic service, they had no USA.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2025-09-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 10 |  | CARLOS ESCOBAR CONTRACTING | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was working on property to install new sewer lines in the process of trenching they hit and damaged 2inch plastic main, 3rd party contractor had a valid USA locator''s marks were 3 feet off locator hooked up to two different address and got the same locate off both of the properties, Coach and counseled ETD and told him to use all adequate resources when locating also had crew put ETS station to help with locating and submitted a GIS MUR request for main location.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2025-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TIMOTHY LEFEVRE GENERAL CONTRACTOR | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working and digging on property to work on sewer lines in the process of digging 3rd party contractor hit and damaged 1/2 inch plastic line, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2025-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HANDYMAN | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Handy man damaged service while installing new fence. No Usa was called in by the handyman. Crew repaired the damaged section and re-instated the service.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | REGERAL RETROFITTING | VENICE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Building owner''s contractor damaged the gas service with a hand tool while digging. Property owner did not request a USA before starting the work.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2025-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 41 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | JC CONSTRUCTION ENTERPRISE | VENICE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hired a contractor to do a sewer repair, and a plastic service was damaged with a shovel while digging. The contractor failed to call in a USA. DPA was contacted.
Southern California Gas Company | N | LOS ANGELES | VERNON | 2025-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MEH CONTRACTING | COSTA MESA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Backhoe operator struck SoCalGas 1 Plastic Service while digging a trench at 2550 E. 28th St. The damage service was for the adjacent property 2600 E. 28th ST. No USA ticket.
Southern California Gas Company | N | LOS ANGELES | VERNON | 2025-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | PACIFIC WEST COMMUNICATIONS | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While potholing to verify gas marks, contractor hit pla line with shovel. Valid USA, Line correctly marked.
Southern California Gas Company | N | LOS ANGELES | VIEW PARK | 2025-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TURN AROUND COMMUNICATIONS | WALNUT | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor bored into 1/2 inch plastic service inside steel casing. ETD failed to correctly mark out service line resulting in the hit line. Crew responded to scene, performed pressure control and altered the service. As a result, ETD will receive coaching & counseling and a refresher on policy.
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2025-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CUSTOM ADU BUILDER | FULLERTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line.
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2025-02-26 | Third party excavation damage | Main | Steel | Hand Tools | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | DOTY BROS | NORWALK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party damaged 1 1/4 steel main with a sawzall while trying to remove a water valve. there was a valid USA but the main was not exposed
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2025-12-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | KEVIN VILLAFUERTE | WEST COVINA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck service with excavator while grading yard.
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2025-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | GNB CONSTRUCTION | WEST COVINA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA , hit service line . crew arrived and dug a control hole to stop release of natural gas . Crew repaired damaged plastic service
Southern California Gas Company | N | LOS ANGELES | WEST HILLS | 2025-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LIFE STYLE LANDSCAPES | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor had a valid USA, and service was marked with flags and paint. Service was hit with backhoe while digging hole for tree installation. Service was previously altered and locate wire did not locate well over alteration. Crew arrived and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | WEST HILLS | 2025-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RODRIGUEZ CONTRACTING | CANYON COUNTRY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging for electrical conduit replacement, damaged 1/2-inch plastic service with electric jackhammer. No USA for excavation. Crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | WEST HILLS | 2025-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging a trench to install conduits when they struck plastic service with shovel NO USA
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2025-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TAMA 38 DEVELOPMENT | WEST HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2 inch plastic service while doing demolition No valid USA ticket was expired
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2025-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TWINS TRUCKING | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damage 1 inch plastic service with Bobcat while doing demo work no Vaild USA
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ADBSCAPE | WEST HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party had a valid USA, while excavating asphalt fell on the plastic service prior to exposure. The service was located correctly.
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2025-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DIBARA MASONRY | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On October 2, 2025, supervision was notified about an excavation damage at 1279 Ozeta Ter in West Hollywood. GasOps supervision had their Mid-Cities meeting and were unavailable. I responded to the excavation damage. It was determined that a third-party contractor struck a 1/2-inch plastic pipe while performing construction work. No Valid USA was called in. The fire department was on scene and left once ETR arrived. The crew was able to control the gas at 11:50 am. Permanent repairs were completed by the crew. Damage prevention was notified.
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2025-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1865 |  | 5 |  | NICHES PLUMBING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged service while excavating with no valid USA. Crew responded, controlled gas, and made permanent repairs under workorder 54-672439
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2025-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | UNITED EL SEGUNDO INC | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A third-party company with no valid USA caused damage to a 1/2 plastic service line while removing a pony wall.
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2025-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TEAM ROOTER PLUMBING | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3Rd Party plumbing company attempting to get to their line and struck gas line with shovel in the process, No USA struck 1/2 Plastic
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PROACTIVE CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While removing roots, the contractor inadvertently damaged the plastic service line. There was no utility service alert (USA) available prior to the damage occurring.
Southern California Gas Company | N | LOS ANGELES | WESTLAKE VILLAGE | 2025-10-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | H&R PLUMBING | SLYMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While excavating for a sewer repair, 3rd party contractor hit a 2PLA main with an excavator. Crew dug control hole and squeezed main, permanent repairs made in form of main alteration. Approx 6 units lost service due to main being squeezed. 2 evacuations ordered at time. Contractor onsite stated they did not have knowledge of main crossing their run-path. Contractor onsite stated they did see marks outside of run-path, pictures included.
Southern California Gas Company | N | LOS ANGELES | WESTLAKE VILLAGE | 2025-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | CAL EMPIRE ENGINEERING | COVINA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit SCG Service Line. There were new USA marks and fresh SCG marks in the area. The service that was hit did not have any fresh marks. Old marks were outside of the 2'' range
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PMK DEVELOPMENT | ALTADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | altered 2'' of 1/2cts for 3rd party damage.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ADOLPHO OROZCO | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors digging trench to replace sewer line, had all lines exposed including gas service. They hit the cts gas service when removing dirt next to the sewer with shovel. No USA called for this job. Downey OHS crew arrived, controlled gas and made permanent repairs by installing one 1/2 cts coupling right where the damage in the pipe was made.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | CHAVEZ FENCING | AMITY | OR | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Fencing contractor hit plastic gas service with auger. No USA. Co crew made repairs.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-08-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOT LINE CONSTRUCTION | BRENTWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor from hotline construction hit 1/2 ips service with shovel while digging to install grounding rod for edison. at power pole. Crew installed 1-1/2 ips plastic coupling to repair. No media, no fatalities, no injuries. no street closures, no evacuations. All information was given to damage prevention.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-11-12 | Operator excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3364 |  | 2 |  | SOCALGAS | WHITTIER | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Altered 2 plastic main due to leakage. Tech damaged main while investigating the leak.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  | 0 |  | MANASES CUESSY | WHITTIER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage. Owner was digging to install sewer and in the process of digging, he damaged our 3/4 steel service with a sharp shovel. No media, no police, no fire department, no street closures, no injuries, no fatalities. Crew was able to control gas and make permanent repairs. Sean O''Connor was on site and gather all information from the damaging party.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HAPPY CAMPER HEATING & PLUMBING | WHITTIER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor damaged 1/2 IPS pipe while digging to install a clean out. There was no USA . LCT Quirarte squeezed the 1/2 service and proceeded to make the final repairs using (2) 1/2IPS couplings and (1) 1/2 of IPS pipe. Pipe section was about 12 in length
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PATRICIA ANAYA | WHITTIER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Code 1. Homeowner stuck 1/2 plastic service line with a round point shovel when attempting to work on their water line. Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RAYMOND GUZMAN | WHITTIER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor doing grading for a new wall damaged our 1/2 cts service causing a leak. They taped it with black electrical tape and called in the leak. No USA was called in for this job. Downey OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installed 1 cts coupling.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | AG BUILDERS | WHITTIER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating to replace sewer lateral, contractor damaged a one half inch plastic gas service. SoCalGas crew arrived on site and made permanent repairs. The contractor did not notify USA and did not have a valid USA ticket.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  | 1 |  | CALIFORNIA PAVING & GRADING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Altered 2 steel service due to damage occurring on 10-4-25. had to alter smc and damaged section in private property. Replaced 2 service valve and bypass on riser. Tested 2 service with crystal Gauge and passed. Per engineering meter needs 2 service. Per management ok to alter and reinstate 2 steel service.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | ALL CITY BUILDERS AND DESIGN | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 service with shovel while digging for water line work. No USA was called in for this job. Downey OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installing 1'' of cts pipe and two couplings.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 8 |  | JBR REMODELING | LA PUENTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damage. Contractor hit service while excavating to repair sewer line. No police, no fire, no media, no street closures, no injuries, no fatalities. Sean O''Connor was on site to take pictures and gather all of the damaging party information.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-02-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JUAN GALLARDO | WHITTIER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage. Customer working with landscaping hit a 1/2 IPS service with a shovel. Gas was not blowing due to EFV. Customer was working in their front yard to install sprinklers. No evacuations, no injuries, no fatalities, no media, no police/fire dept, no street closures.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CHARLIE LIU | WHITTIER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit line 1/2 ips service damaged by contractors service exposed upon arrival.repaired leak using 2 1/2'''' ips coupling and 6'''' 1/2'''' ips pipe
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2025-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | LADWP | SAN PEDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP damaged a 1/2 IPS service which was located and marked. Damage was within the 24 of the mark on the asphalt.
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | EVERGREEN ENVIRONMENT | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 Plastic gas service was damaged by a 3rd party contractor. The plastic gas service was not located and marked.
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2025-04-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | SALAZAR LANDSCAPING | LYNWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor working at school, hit 2inch plastic main trenching with a mini-excavator. No USA.
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | STEPHENS PLUMBING & HEATING | SAN PEDRO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging to repair leaking water service, struck 1/2 plastic service with shovel, No USA.
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2025-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | NO LIMIT CONSTRUCTION CORP | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install sewer drain. contractor struck plastic service line shovel. No USA
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2025-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | GEDIKIAN CONSTRUCTION | WINNETKA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging to install sewer lateral. contractor struck service line with pick and clamped leak and called next day. No USA
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2025-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | ISAAC REYES | LANCASTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hired unlicensed contractor to build ADU. While excavating with mini excavator, he damaged a 1/2 plastic gas line. No USA for excavation. Crew responded and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2025-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | OSP CONSTRUCTION | WINNETKA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 3rd party contactor trenching for telecom line struck our 1/2 plastic service. Struck service line appeared to be mismarked and outside of tolerance zone. Crew leader indicated measurements were used per locator.
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2025-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | LINDY CONSTRUCTION | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Without USA, 3rd party contractor excavated to replace sewer. While excavating, they hit 1/2 plastic gas service with shovel. Crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2025-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DIVINE PRO CONSTRUCTION | SOUTH GATE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hired by owner/builder to install sewer lateral. While excavating, contractor damaged 1/2 plastic gas service with shovel. No USA for excavation. Crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2025-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | DIVINE PRO CONSTRUCTION | SOUTH GATE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was hired be developer to install sewer lateral. Valid USA for work. While excavating, contractor damaged marked 1/2 plastic gas service. Service was accurately marked within tolerance zone. Crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2025-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MELVIN CRUZ | WINNETKA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging hole to install sewer clean out. Homeowner was using hand tools. There was no emergency services, evacuations, road closures, or news media on scene. Homeowner did not have a valid USA. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 3 |  | POINT A VISTA FENCING | SAN FERNANDO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hired third party contractor to install fence along property line adjacent to 19801. While hand excavating with post digger, third party contractor struck and damaged 1/2 CTS service, causing an uncontrolled release of gas. SCG crew arrived to make permanent fusion repair, altering 1'' section via two 1/2 CTS socket couplings and new 1'' section of 1/2 CTS pipe
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ROCKSTAR PLUMBING SERVICE | CHATSWORTH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavated to repair water line for homeowner, no USA for excavation. 3rd party contractor hit 1/2 plastic service with shovel.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KAMRAN MASJEDI | WOODLAND HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging to remove dirt for a block wall or fence contractor cut into steel line trying to remove it. crew showed up and clamped line NO USA
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-03-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | NA | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property 3 party damage, contractor was digging with No USA when damaged half inch CTS service. Contractor was jackhammering concrete when damaged service. LCT pinched line with approved pinchers used two feet of 1/2 CTS pip along with 2 couplings to make final repair.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LADWP | NORTHRIDGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP was cutting root with sawzall, while cutting root the operator cut through an unexposed 3/4 steel gas service. Gas service was accurately marked within tolerance zone. DWP had Valid USA for their work. SoCalGas crew arrived and eliminated hazardous conditions.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1678 |  | 3 |  | CSS BUILDERS | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging a trench for foundation pour when they hit plastic service line with shove
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | KING PLUMBING AND CONSTRUCTION LIC 835715 | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install drain contractor struck plastic service line crew made repairs. No USA
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TD CONSTRUCTION SERVICES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dug without USA. While digging, they hit plastic service with clay spade. Crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | NORTHRIDGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Valid USA, Older Ticket. LADWP Damaged 1/2 IPS Service that was not properly marked by SCG. CP 10 Service with no tracer wire. Mismarked by 10ft. LADWP dug at mark, did not find our service and kept digging, failed to call for verification of marks. Partial Fault. 1 Outtage, Service repaired with 1/2 IPS pipe and couplings.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | LOYOLA DEMOLITION | JURUPA VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Loyola Demolition construction team was excavating footing for wall construction. While excavating with backhoe, construction team struck and severed 1/2 IPS gas service, causing uncontrolled release of gas. SCG Distribution crew arrived on site to control gas and make permanent repair via socket fusion alteration of 6'' section of pipe with two (2) socket fusion couplings.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | CARLOS DIAZ | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hired by owner-builder to grade for new construction. While grading with bulldozer, 3rd party contractor damaged 3/4 steel service. No USA for excavation. Crew arrived and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | KAYUMBA | WOODLAND HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while digging to install conduits in trench, contractor struck plastic line with excavator. marks from company where accurate. there was a USA ticket
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | NA | NA |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Homeowner hired unlicensed contractor to dig for irrigation install. Homeowner called in a USA ticket but was expired at time of damage. Service was accurately marked by SoCalGas with visible yellow flags on private property. Service was hit with shovel while digging. SoCalGas crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11833 |  | 1 |  | LADWP | NORTHRIDGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP was probing to check the depth of there water main with probe when they probed through the 4plastic main. Job was USAd and marks where within 24 DWP failed to pothole before probing
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-10-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | RIAAN CONSTRUCTION | CANOGA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavated without valid USA. Contractor contacted dig alert for emergency drain install and reported damaged gas line at the same time. Contractor dug before receiving locate marks from SCG. 1 inch plastic gas service was hit with electric jackhammer. Crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | ABE GUYUMBZHYAN | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged 1 inch plastic pipe. No USA called in for this job.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SAL YUDA | WOODLAND HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor struck plastic service with shovel when working on the side of the house
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2025-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALMOG EXODOS | WOODLAND HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install conduit for electrical line contractor struck plastic service with shovel. crew showed up and made repairs
Southern California Gas Company | N | ORANGE | ALISO VIEJO | 2025-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | IMPROVED PLUMBING | LAKE ELSINORE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line. Contractor struck a service while hand-digging for trenching. MV17 monitored area until gas ops arrived and repaired. No evacuations. No injuries, no media. FD on scene. One outage is the affected facility. Claims was notified.
Southern California Gas Company | N | ORANGE | ALISO VIEJO | 2025-06-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOHN CHRISTOPHER CONSTRUCTION | ALISO VIEJO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew spoke with contractor about digging
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | HOT LINE CONSTRUCTION | CORONA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor hit a 3/4-inch copper stub. The contractors USA was expired. And didn''t maintain their marks.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2179 |  | 1 |  | ALL CITIES ENGINEERING INC | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA was called and the marks were on. Contractor did not pothole before digging.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-10-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 10 |  | DICE IT UP CONCRETE CUTTING & DEMOLITION | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging a trench with an excavator to install electrical for a Wing Stop, contractor was digging over the gas service to pothole it when they damaged a 2 inch gas service feeding local businesses. The contractor said that they knew the service was there but thought it was deeper and they were using the excavator because the road base beneath the pavement was hard. Contractor had an expired USA ticket. The previous location marks on the pavement for the ticket before it had expired were accurate. Gas company crew arrived on site and made permanent repairs.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LINCOLN CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While the 1/2 plastic service was correctly marked and visible, there is an abandoned service that was not marked. The 3rd party crew found the abandoned service and started digging with a backhoe when they damaged the active service.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SEMA | CENTENNIAL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | City of Anaheim contractor relocating service and main pulled on our service slightly damaging wrap on steel service. Crew confirmed that there was no leaks. and repaired wrap on pipe.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-03-25 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 4 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CROSSTOWN ELECTRICAL AND DATA INC | BALDWIN PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor doing work for the GC hit our 4 inch plastic main with his excavator bucket causing broken and blowing. They did not have a USA for this work. Downey OHS crew arrived, dug two control holes, installed punch t''s. two other crews arrived to assist install more punch t''s and help with the squeeze. Gas was controlled and permanent repairs were made by cutting out the damaged section and fused in 3'' of 4 inch IPS plastic and two 4 electrofusion couplings.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MSL ELECTRIC | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor bored through 1 inch plastic gas service with boring machine. Gas service was installed with no tracer wire. Service was marked out by measurements.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 8 |  | LINCOLN CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party crew was hand digging looking for the plastic service, they damaged the service with a shovel. Service was marked correctly.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ANGELS RESIDENTIAL | HEMET | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Construction crew was digging with auger when they damaged unmarked gas service. No USA.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MOHANAD ALKHREISHA | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | found .5 ips service hit with shovel and tapped s hut. SA crew responded.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ASPLUNDH CONSTRUCTION LLC | CYPRESS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 3/4 steel stub / cut back with a backhoe while installing power conduits. Our gas line was not marked due to it not being in our system (GIS) and having no records of the stub / cut back.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WAYNE KING SHEPARD | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit an 1/2-inch plastic service with a shovel. There was no USA called in for this address.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | ASPLUNDH CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working for the city of Anaheim installing electrical conduit hit our gas line with a backhoe but claimed it was a shovel. marks were accurate and visible.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LINCOLN CONSTRUCTION | ANAHEIM |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit our plastic gas service while digging with hand tools
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LUIS CONTRERAS | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 plastic service was damaged by excavator digging for drainage work. No USA. Gas was controlled at 1237 and permanent repairs completed by 1415. Homeowner accepts responsibility for damage
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OUTSOURCE UTILITY CONTRACTOR | ARTESIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The gas service was marked and clearly visible. While hand digging the third party crew damaged the gas service. Although the crew was aware of the service location they thought they had moved to a safe distance when they damaged the service.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-06-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LINCOLN CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor digging struck our plastic main beyond the End Of Main marking. EOM was marked by measurements due to loss of signal on the locating wire.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | ASPLUNDH CONSTRUCTION | PLACENTIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 IPS SVC hit with sharp shooter while exposing for communications trench.520004371280
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NUYANA MALHUTRA | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging in front yard probably working on sewer line. They were not at damage by the time we arrived. No USA. Plastic service was damaged with shovel
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-08-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | UNLICENSED CONTRACTOR HIT OUR 1 SERVICE LINE WITH A MINI EXCAVATOR WHILE DIGGING FOR A DRAIN PIPE. NO USA WAS CALLED IN FOR THIS JOB. ARCOS CALL OUT WAS MADE AND CREW SHOWED UP, DUG CONTROLL HOLE, PINCHED THE SERVICE AND MADE PERMANENT REPAIRS BY CUTTING OUT THE DAMAGED SECTION, ABANDONED THE OLD SERVICE 1'' FROM SMC. NEW TEE, 2'' OF 1 PLASTIC, ONE 1 ELECTROFUSION COUPLING.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JP OPTIMAL CONSTRUCTION | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 plastic service damaged with excavator. No USA.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-10-20 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 4 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 0 |  | FULLMER CONSTRUCTION | ONTARIO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor digging for electrical hit our gas line with a backhoe.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | TE ROBERTS | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party crew failed to maintain Gas Co. marks. Crew was hand digging for their water line when they damaged the 1/2 plastic service.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | KALATU CONSTRUCTION | BELLFLOWER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 1/15/24 while excavating by hand with a pick for a room addition footing, a third party, Kalatu Construction, struck and damaged a 1/2 plastic gas service. Kalatu Construction did not have a valid USA. Gas operations crew arrived on site and made permanent repairs.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LINCOLN CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged plastic service while looking for it.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1598 |  | 1 |  | WEST COAST ARBORISTS | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch plastic service hit with backhoe while digging to plant palm tree. No USA
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROBERT CHIANG | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY DAMAGE ON 1/2 CTS SERVICE PL-MTR, UPON ARRIVAL FOUND TAPPED OFF AND COVERED WITH DIRT. OWNER HIRED UNLICENSED CONTRACTORS TO TRENCH FOR SEWER, 1/2 CTS PLA SERVICE WAS HIT WITH SHOVEL WHICH TRENCHING. NO USA CALLED. SERVICE WAS FOUND TAPED UPON ARRIVAL. SQUEEZED SERVICE, CUT OUT DAMAGE, REPLACED APROX 1'' OF 1/2 CTS SERVICE , TYING IN WITH 2 COUPLINGS, PIPE WAS SHADED AND MESH PLACED OVER TOP .
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOT LINE CONSTRUCTION INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor installing electric conduit hit 1 pla svc with sharpshooter while trying to get through palm tree roots. Markings were accurate
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ASPLUNDH CONSTRUCTION | BALDWIN PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator had nearby utilities interference and did not get a good signal. He wrote to had dig on his mark. 3rd party crew pothole and called EE when they did not find the service. EE arrived and told them he was getting help with the locate. 3rd party crew asked if they could keep working. EE said yes, but away from the missing service. 3rd party crew damaged the unmarked service.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-12-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | MOUTAZ ALSAYED | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA ticket. 1 inch PLA service damaged by backhoe. Provided Damage Prevention pictures.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | OUTSOURCE UTILITY CONTRACTOR | ARTESIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew damaged service while looking for it with a shovel. Gas mark was withing tolerance.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-09-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ASPLUNDH CONSTRUCTION | PLACENTIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party crew was installing electrical conduit. Main was marked and visible. 3rd party crew claims that they used their backhoe to remove concrete or a rock from the trench when they damaged the 2 plastic main.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TED & BROS PLUMBING | ANAHEIM | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party plumber was digging for water line. Contractor did not wait for any utility to mark. Contractor damaged gas service with his shovel.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALL CITIES ENGINEERING | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor digging with backhoe to repair water main hit our 1/2 inch service. USA was valid, but our service was not marked correctly ( 12ft off). Downey OHS crew arrived, pinched and controlled gas. and made permanent repairs by cutting out the damaged sections and installed 2'' of cts pipe and two couplings. OHS crew also located and repainted the service and main.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2025-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOT LINE CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1 Gas Service with shovel trying to expose gas service.
Southern California Gas Company | N | ORANGE | BREA | 2025-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CALIFORNIA BORING INC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging with a backhoe hit our exposed gas line
Southern California Gas Company | N | ORANGE | BREA | 2025-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HBA HANK BLATNIK & ASSOCIATES | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3 different ETD''s were unable to locate 2 plastic service (that''s how it shows in GIS). The service was marked with yellow feathers. Electric Co. was supposed to hand dig and they did not. The feathers were 7'' away from the gas service.
Southern California Gas Company | N | ORANGE | BREA | 2025-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 3 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | J AND A FENCING | HACIENDA HEIGHTS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Added materials used. Fencing co. was augering when they damaged 3 plastic service. No USA.
Southern California Gas Company | N | ORANGE | BUENA PARK | 2025-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | GT | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called. 1 inch service was hit with backhoe. Fixing a retaining wall.
Southern California Gas Company | N | ORANGE | BUENA PARK | 2025-06-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MICHAEL BOGDANO | BUENA PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit are main while using a chipper to go thru roots. No USA was called in.
Southern California Gas Company | N | ORANGE | BUENA PARK | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | contractors working a water job hit our gas line while digging outside of the delineated area
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party was trenching for new underground Edison lines when they damaged unmarked stub service
Southern California Gas Company | N | ORANGE | COSTA MESA | 2025-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | ROGELIO JUARERZ | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractors damage gas service with shovel.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2025-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JOSE DE JESUS MARTINEZ | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit shallow service with shovel while planting. Crew dug control hole, service was not in it. Took a sharp turn not in GIS. 2nd hole needed to be excavated.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2025-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | OMNIBUILD SOLUTIONS | NORWALK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor (Omnibuild Solutions) installing Sewer line Via Open Trench method, while Hand digging hit/ damaged the 1/2IPS Gas Service. No Records of USA upon arrival.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2025-11-18 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | NPL CONSTRUCTION | COSTA MESA | CA | Y | Y | No | No | No | No | No | Yes | Yes | 2nd party NPL hit gas service while trenching to replace gas service.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GRP CONTRACTORS | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Installing power conduit failed to expose 1/2 IPS Gas service and damaged it via open trench method. Valid USA / Gas Was clearly marked correctly.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1865 |  | 5 |  | GARRETT SMAWLEY | COSTA MESA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging for irrigation hit our 1/2 IPS plastic service causing broken and blowing. No USA called in for this job. Police and fire department on scene. 1 person evacuated from building. Downey OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installing 1'' of IPS and two IPS couplings.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2025-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BRIGHTVIEW LANDSCAPE SERVICES | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | City of Costa Mesa Hired contractor to install irrigation system who hired a private locator to locate all substructures. City/ Contractor failed to Notify USA and get subs properly marked out, resulting in damaged 1/2 IPS service line broken and blowing. 3RD PARTY CONTRACTOR BRIGHTVIEW DAMAGED 1/2 IPS SERVICE WITH SHOVEL. WORK BEING DONE FOR CITY OF COSTA MESA IN THE FIRE DEPARTMENT).
Southern California Gas Company | N | ORANGE | COSTA MESA | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | FRISCH & SONS CONSTRUCTION | QUEEN CREEK | AZ | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit service. Started digging before USA was valid.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2025-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | RODOLFO VARGAS | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2IPS At 2801 Habor Blvd at 3:15pm. We arrived there at 4:00pm and was told that the contractor hit our 1/2 IPS service with a jackhammer. Plenty of marks on the ground to indicate where our service runs, control time was at 4:30pm. Pictures were taken on scene. Damage occurred in private property, PL to riser. No MSA. Permanent repairs were made from the hours of 4:15 to 6:30pm.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BLANCO CONSTRUCTION | BUENA PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged 1/2 PLA service by 3rd party contractor, Valid USA incorrectly marked. Contractor potholed service a week prior, did not find service and failed to communicate that with locator when they spoke day prior to damage. conversation documented in KorTerra ticket notes. Locating wire also did not provide signal sufficient to locate gas facilities.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 2 |  | TRE D | COSTA MESA | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Installing Power Conduit for homeowner damaged service line feeding 324 Costa Mesa St. Costa Mesa with Mini-Excavator via Open Trench Method.
Southern California Gas Company | N | ORANGE | CYPRESS | 2025-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EZ FLOW ROOTER & PLUMBING | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Called in
Southern California Gas Company | N | ORANGE | DANA POINT | 2025-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BEST BORING AND BURSTING | COSTA MESA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit service line while digging trench hole
Southern California Gas Company | N | ORANGE | DANA POINT | 2025-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BEST BORING AND BURSTING | COSTA MESA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CARLOS GUTIERREZ (714)699-6781 REPORTING THAT BEST BORING AND BURSTING CREW HIT GAS LINE WITH HAMMER WHILE DIGGING ON PROPERTY.
Southern California Gas Company | N | ORANGE | DANA POINT | 2025-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALAIR ENCINITAS | ENCINITAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 inch plastic service with hand tools while digging to expose gas service. No USA
Southern California Gas Company | N | ORANGE | DANA POINT | 2025-04-22 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 4 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 17138 |  | 45 |  | PRUTER CONSTRUCTION | YORBA LINDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 4 inch plastic main.
Southern California Gas Company | N | ORANGE | DANA POINT | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SOUTH COAST WATER DISTRICT | ESCONDIDO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SVC LINE HIT BY CONTRACTORS WORKING ON WATER LINES IN STREET
Southern California Gas Company | N | ORANGE | DANA POINT | 2025-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NICK HEINRICH | DANA POINT | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Usa was called in. Contractor hit a 1/2-inch service with a shovel.
Southern California Gas Company | N | ORANGE | DANA POINT | 2025-12-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | O DUFFY CONSTRUCTION | ROMOLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | USA ticket was expired and marks were visible.
Southern California Gas Company | N | ORANGE | DANA POINT | 2025-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MEDLIN LANDSCAPE SERVICES | SAN CLEMENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | New home construction-plastic service runs on right side of home from street- nicked with shovel leaking
Southern California Gas Company | N | ORANGE | DANA POINT | 2025-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | GENOVA CONSTRUCTION | LADERA RANCH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | DEVELOPER HIT SERVICE, NO USA
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2025-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged gas service. Contractor failed to hand expose gas service by hand.
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2135 |  | 2 |  | SAM CONSTRUCTION & BUILDER | FOUNTAIN VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Half in PE pipe damaged with shovel while digging trench. Line was mismarked.
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2025-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ULTIMATE KONSTRUCTION | FOUNTAIN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor trenching for sewer hit our 1/2 IPS service with mini backhoe. valid USA on file, but contractor did not verify gas line location. Downey OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installed 2'' of IPS and two couplings.
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2025-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | CITY OF FOUNTAIN VALLEY WATER DISTRIBUTION | FOUNTAIN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water company probed through 1/2 PLA service while digging for water service re-locate. Valid USA, correctly marked with paint.
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2025-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MASTER CONSTRUCTION | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew told contractor to be more careful and call for USA
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2025-10-09 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | NPL CONSTRUCTION | BREA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG Contractor digging to replace service damaged 1/2'''' IPS service with shovel while hand exposing
Southern California Gas Company | N | ORANGE | FULLERTON | 2025-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | PRAMIRA | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor trenching for fiberoptics failed to pothole our pipe and struck it with a ditch witch.
Southern California Gas Company | N | ORANGE | FULLERTON | 2025-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LENNAR HOMES | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to repair a sewer line hit our plastic gas line with a backhoe.
Southern California Gas Company | N | ORANGE | FULLERTON | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WILLIAMS PIPELINE CONTRACTORS | MISSION HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor crew was digging for new water main. The gas service was marked. Crew parked their dump truck over the gas marks and forgot the gas service was there. They damaged gas service while digging.
Southern California Gas Company | N | ORANGE | FULLERTON | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FG REAL ESTATE DEVELOPMENT | GARDEN GROVE | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Downey OHS crew found our ï¿½ IPS service wrapped in water clamps where it was hit, in a trench, just downstream of the branch service. appears to have been hit by a shovel. Nobody on sight, from homeowner to contractor, nobody there. The ETR mentioned he had seen a truck on sight and left as soon as he pulled up. He got a license plate (6763BP2). There was an active USA on file. The crew pinched the service, and made final repairs by cutting out the damaged section and fused in 1'' of IPS and two couplings.
Southern California Gas Company | N | ORANGE | FULLERTON | 2025-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | ACE ALL CITIES ENGINEERING | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service was mismarked by 6''. Locator wrote to pothole. 3rd party crew potholed on locators mark but did not call when they didn''t find the service like they are supposed to.
Southern California Gas Company | N | ORANGE | FULLERTON | 2025-04-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 6 |  | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | VCI was installing new conduit for AT&T. They called for remarks at the intersection of Buena Vista and Wesley. ETD had previously marked and VCI did not find the gas main. I was doing a Field Observation when this ticket came in. ETD was unable to locate and he marked main by using service history, GIS and Epoch. He told the foreman to hand dig and they agreed. They damaged our gas main with an excavator.
Southern California Gas Company | N | ORANGE | FULLERTON | 2025-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ACE ALL CITIES ENGINEERING | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was marked correctly; it was damaged while the 3rd party contractor was potholing.
Southern California Gas Company | N | ORANGE | FULLERTON | 2025-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NOBEST | GARDEN GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit our gas line while grading for new curb and gutter.
Southern California Gas Company | N | ORANGE | FULLERTON | 2025-01-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | S & S DIRECTIONAL DRILLING INC | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | S&S doing contracting work for CableComm. Hit line with a shovel. Everyone still on site. S&S took responsibility for hitting it. Service was marked, contractor took marks off and forgot where the service was located.
Southern California Gas Company | N | ORANGE | FULLERTON | 2025-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | KEITH BERGEN | FULLERTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner struck our gas line while digging to make repairs to his water line.
Southern California Gas Company | N | ORANGE | FULLERTON | 2025-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 55 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BROOKE WIMBERLY | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner struck 1/2 CTS service with auger in private property. No USA. Altered service to make permanent repairs.
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2025-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | 2R DRILLING | CHINO | CA | N | Y | Yes | Yes | No | Yes | No | No | No | 3rd party contractor damaged 1 gas service. USA valid. Gas Service hit outside of delineation.
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2025-09-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | VALLEE ELECTRICAL SERVICES | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor damaged 2 Plastic Gas Main with Backhoe. 3rd party contractor failed to expose gas main by hand.
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2025-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | CITY OF GARDEN GROVE PUBLIC WORKS | GARDEN GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2 inch main was struck with a probe. While the city of Garden Grove was looking for there main. To do a water leak. USA was good and marks were on.
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2025-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | ULTIMATE KONSTRUCTION | GARDEN GROVE | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Plumer dug without a USA
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2025-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PHUC KIN TRAM | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner sawed through steel service while attempting to install for fence. No usa ticket on file.
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2025-02-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | THANH TRAN | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in. Contractor hit a plastic service with a shovel installing conduit.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2025-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ELEVATE METAL | TUSTIN | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging without a USA damaged 1/2'''' plastic service with shovel while installing footing for gate/fence
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2025-07-08 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | CITY OF HUNTINGTON BEACH | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Employee didn''t locate the service which caused the contractor to pull the service. The service wasn''t leaking but we had to replace the service. Employe has been suspended form locating and is being op qual. Also, I have placed a note to file.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2025-08-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DON HANSON | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors were trenching to add in cement footing cut through our ï¿½ IPS service. Clearly marked out with yellow paint. No EFV. Downey OHS crew arrived, found exposed damaged service cut in half, they controlled gas and made permanent repairs by installing one 1/2 IPS coupling.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2025-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MCGREGOR ENTERPRISES | MIDWAY CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 1/2 plastic service. They did not have a digalert ticket.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2025-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | VERNE S PLUMBING INC | BUENA PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA at the time of damage called in after damage occurred. Contractor hit Half inch plastic service with shovel. While doing a sewer repair.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | CITY OF HUNTINGTON BEACH | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit 1 inch service while digging up water leak. USA was called in. Talked to employee and had him review policy and placed a note to file.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2025-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | IMPERIUM | HUNTINGTON BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2-inch plastic service hit with shovel installing fencing. No USA was called in.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2025-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CDE | YORBA LINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged ï¿½ inch ips adyl-a svc caused by shovel, replaced 1'' section of damaged pipe. Service was marked correctly.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2025-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | BURK NIGEL | LOS ALAMITOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 IPS Gas service with shovel. No USA.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2025-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | TKR CONSTRUCTION | LOS ALAMITOS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit branch service while digging for remodel. No USA.
Southern California Gas Company | N | ORANGE | IRVINE | 2025-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | 24 HRC | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage 1 pla service w/ backhoe. No USA. Referred DPA for 2nd damage by same contractor at this location.
Southern California Gas Company | N | ORANGE | IRVINE | 2025-07-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | PME PORTERMATT ELECTRIC | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Job Was Originally a New Business 2? Svc Install Per 540000680863, upon arrival crew noticed 2? PE Main was badly damaged with Deep gauges and cuts, Conducted Main Alteration to ensure integrity of Pipeline.
Southern California Gas Company | N | ORANGE | IRVINE | 2025-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | R DEUTSCHMAN & ASSOCIATES | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 2 PLA service with backhoe, Valid USA correctly marked with paint.
Southern California Gas Company | N | ORANGE | IRVINE | 2025-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MATTHEW AVILA PLATINUM CONSTRUCTION | HESPERIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor excavating a trench to install a sewer line for an ADU, hit the 1/2 IPS service with a shovel. No USA
Southern California Gas Company | N | ORANGE | IRVINE | 2025-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NEWPORT HORIZONS COMMERCIAL | COSTA MESA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging a trench nicked our ï¿½ IPS service with a shovel. No USA was called on their trench work. Downey OHS crew arrived, controlled gas and made permanent repairs using only one 1/2 IPS coupling.
Southern California Gas Company | N | ORANGE | IRVINE | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NEWPORT HORIZONS COMMERCIAL | COSTA MESA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor remodeling home at 19471 Sierra Raton Rd, Irvine, CA, 92603 failed to call in a valid USA ticket while open trenching to install gutter drainage. Damaged 1/2 IPS service line from shovel or hand tool. (Contractor denied digging or exposing the service line and stated the fusion or repair failed from 2 days ago, a previous damage on same service line) NO USA From Developer.
Southern California Gas Company | N | ORANGE | IRVINE | 2025-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PREMIUM BUILDERS | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working at home address of 21 Fuertes Damaged 1/2CTS service line with Shovel, Contractor used SharkBite fittings to repair (NO USA Onsite / They Never called 811), SCG Crew Squeezed line, made permanent repairs.
Southern California Gas Company | N | ORANGE | IRVINE | 2025-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SEA BREEZE LANDSCAPING | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was open trenching for homeowner and cut through the 1/2 plastic service with shovel. No USA.
Southern California Gas Company | N | ORANGE | IRVINE | 2025-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  |  | NA | MACADEE ELECTRIC CONTRUCTION | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor digging to expose our service, hit our service causing broken and blowing. Valid USA with correct & visible marks on the ground. Downey OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installing 3'' of IPS and two couplings
Southern California Gas Company | N | ORANGE | IRVINE | 2025-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LMX BUILDERS | IRVINE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor failed to pothole gas service. USA marks correct.
Southern California Gas Company | N | ORANGE | IRVINE | 2025-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ORANGE COAST PLUMBING | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor replacing irrigation water service, hit service line with shovel. NO USA
Southern California Gas Company | N | ORANGE | IRVINE | 2025-09-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | BUCCOLA LANDSCAPE SERVICES | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | New Business Stub damaged by Contractor hired by developer installing Reclaimed water lines via open trench method and damaged 1IPS long side stub.
Southern California Gas Company | N | ORANGE | IRVINE | 2025-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | MRC MIKE ROVNER CONSTRUCTION | MOORPARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas line with auger while installing fence posts.
Southern California Gas Company | N | ORANGE | LA HABRA | 2025-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOME OWNER | LA HABRA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was planting tree in front yard. No USA. He damaged plastic service with shovel.
Southern California Gas Company | N | ORANGE | LA PALMA | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | GOLDEN PACIFIC BUILDERS | BUENA PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service with backhoe while removing tree. No USA called in
Southern California Gas Company | N | ORANGE | LADERA RANCH | 2025-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ROCKY S CONCRETE REMOVAL INC | NEWPORT BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor using a backhoe doing concrete work hit our 1 inch service causing broken and blowing. They did have a valid USA ticket but removed the visible marks that were on the concrete and did not pot hole for verification. service fed a vacant property. Aliso crew went out, controlled gas and made repairs by abandoning service at the SMC.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ROBERT FERGUSON COMPANY | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with hand tools to locate the gas line because they needed to demo a concrete wall. The gas line was hiding directly below the footing of the concrete wall and they accidentally hit the service with power hand tools. No USA was called in for this job. Two Aliso techs arrived, controlled gas and made permanent repairs by cutting out the damaged section and replacing it with 2'' of 1/2 plastic and two couplings.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FERREIRA COASTAL CONSTRUCTION CO | RANCHO CUCOMUNGA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DAMAGED SERVICE BY CONTRACTOR USING EXCAVATOR.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOT LINE CONSTRUCTION INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2 plastic service.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | TRIVEST BUILDERS | NEWPORT BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew spoke with contractors about needing a USA to dig.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HOT LINE CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while excavating.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOT LINE CONSTRUCTION | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | HIT LINE BY CONTRACTOR. CONTRACTOR HIT LINE TOWARDS THE CUSTOMER HOME
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-08-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | HOT LINE CONSTRUCTION | BRENTWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Utility company was installing cableHot main with mini excavator
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-02-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3924 |  | 8 |  | HOT LINE CONSTRUCTION INC | BRENTWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit 2'''' plastic main
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CALAMERICA CONSTRUCTION INC | COTO DE CAZA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 plastic service with a shovel. No USA ticket.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | CALAMERICA CONSTRUCTION | LAGUNA BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged (branch) gas service while exposing it to install new service.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HOT LINE CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | PER USA DAMAGED LINE 1/2 GAS SERV HIT W/SHOVEL.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-05-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | HOT LINE CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service with a (pointed) probe while looking for the gas service.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CARLOS CAAL | LAGUNA BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA REQUESTED, CUSTOMER INSTALLING PAVERS
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | KISLING CONSTRUCTION | SAN JUAN CAPISTRANO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor trenching for sewer hit our 1/2 service. They had a valid USA but did not properly maintain distance from correctly marked service. Aliso Viejo crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installed 1 1/2'' of 1/2 plastic cts and two couplings.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-02-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor installing a wooden pole for fencing hit our 1 inch ips plastic service causing a leak. contractor left the scene and many hours later his wife called the fire department and reported the leak. she did not give her info. No USA was called in for this job. Downey OHS crew arrived, completed the leak investigation and made permanent repairs by cutting out the damaged section and installing 2'' of new 1 ips and two couplings.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-05-27 | Third party excavation damage | Main | Steel | Grader/Scraper | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4636 |  | 7 |  | JD DEMOLITION AND GRADING | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | HIT LINE PER KAREN ROSALES 714-379-1800 UNSURE OF DAMAGING EQUIPMENT
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-10-17 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 44 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | CARNEY ENGINEERING CONSTRUCTION | ARTESIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hooked 2 steel main resulting in bending/denting the main.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | KUNZIK & SARA CONSTRUCTION | SAN MARCOS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor replacing meter guards, jackhammered through a 1/2 plastic service.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RLB RANCHO LAGUNA BUILDERS | LAGUNA BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging up water service hit our 1/2 cts service causing broken and blowing. No USA was called in for this job. Fires department originally called to scene, but departed before crew arrived. Downey OHS crew arrived, controlled gas and made permanent repairs by installing one 1/2 cts riser and one 1/2 cts coupling.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2025-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | PHILLIPE HORVATH | LAGUNA BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavation Damage to 1/2 plastic service by contractor remodeling home.
Southern California Gas Company | N | ORANGE | LAGUNA HILLS | 2025-10-15 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 3 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | PRAMIRA | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 3 plastic main with an air knife while air jetting to install new fiber lines. Contractor did not pothole the 3 plastic main prior to air jetting. 3 plastic main is 40 deep.
Southern California Gas Company | N | ORANGE | LAGUNA HILLS | 2025-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GERHARD ELECTRIC | LAGUNA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to install conduit electrical hit our 1/2 inch service with a shovel causing broken and blowing. No USA was called in for this job. La Jolla On Call crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installing 2'' of CTS plastic and two couplings.
Southern California Gas Company | N | ORANGE | LAGUNA HILLS | 2025-12-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 7 |  | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | VCI dug before USA was valid
Southern California Gas Company | N | ORANGE | LAGUNA HILLS | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DAVION MAYS | LAGUNA HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Owner trenching for installation of new electrical power panel hit our 1/2 plastic service with a shovel causing broken and blowing. They did have an active USA, but the service was mismarked. Wire did not provide good locating and GIS was wrong about standard and branch. ARCOS call went out with two Aliso techs responding. Fire Department was on scene and evacuated one house/4 ppl. Crew dug down in multiple areas and finally found the service to main connection. They controlled gas by pinching, evacs lifted, crew made repairs by cutting out the damaged section and installed 2 ft of 1/2 cts and two couplings.
Southern California Gas Company | N | ORANGE | LAGUNA HILLS | 2025-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DREAM ESTATE GENERAL CONTRACTING | TUSTIN | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to expose sprinkler system and ended up hitting service line with shovel.
Southern California Gas Company | N | ORANGE | LAGUNA HILLS | 2025-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DREAM ESTATE GENERAL CONTRACTING | TUSTIN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor damaged plastic service with shovel while trenching to install electric conduit.
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2025-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | EXCEL MASONRY | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call 811 when putting in drains for new pool and hit our service with an excavator. Fire dept on scene, no road closures, customer not home when incident occurred so no evacuations.
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2025-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SWIFT WATER HEATER | MISSION VIEJO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while digging to repair broken water line, they didn''t see the service due to water in the hole.
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2025-09-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | KUSTOM WORX CONSTRUCTION | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | HIT SERVICE. UPON ARRIVAL SPOKE TO WORKER RONALD, HE HIT SERVICE WITH SHOVEL AND WRAPPED DAMAGED AREA WITH DUCT TAPE. Locator noted on ticket, no delineation found. Marked service with flags. Flags removed by 3rd party contractor while digging trench.
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2025-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | CONSTRUCTION DEVELOPMENT MANAGEMENT DBA CDM BUILDS | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with mini excavator. Contractor failed to pothole.
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2025-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | AV LANDSCAPING | MISSION VIEJO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Worker hit gas service with shovel while digging hole for fence post
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2025-03-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PATRIOT PIPELINE INC | WILDOMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while clearing out around stub and hit service with shovel.
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2025-04-15 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | PREMIER BROADBAND SERVICES | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1 inch plastic main with a shovel while digging to install Telecommunication box.
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2025-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | AMG CONSTRUCTION | LAKE FOREST | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SERVICE LINE-DIGGING FOR SPRINKLER AND POOL EQUIPMENT ALLEN GREEN-CNTRCTR 949-307-9098 HIT W JACK HAMMER
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2025-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | DO BUILDER & DESIGN | HUNTINGTON BEACH | CA | N | Y | Yes | No | No | Yes | No | No | No | Customer''s initial ticket in October stated work would only be done behind property. Since then, ticket has expired and not been renewed and their scope of work has changed as they hit our service in the front yard.
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2025-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 1 inch plastic service with backhoe. Service was not marked.
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2025-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | NA | LAKE FOREST | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner replacing fence post
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2025-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | U S A DEMOLITION COMPANY INC | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew spoke with contractor about the importance of properly hand digging while around our lines.
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2025-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COLE WILLIAMS | LAKE FOREST | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew spoke to foreman and told him he needs to call for USA to avoid this from happening.
Southern California Gas Company | N | ORANGE | LOS ALAMITOS | 2025-01-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SERVICE 1ST PLUMBING | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1/2 inch plastic line while installing a service. No USA called in.
Southern California Gas Company | N | ORANGE | MIDWAY CITY | 2025-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | CHASE PLUMBING & DRAINS | LAKEWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor Damaged 1/2 IPS Gas service with shovel. USA expired and not renewed for remarking.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2025-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | NF PLUMBING | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HIT 1 PLASTIC LINE BY BACKHOE, CONTRACTORS USED VICE GRIPS TO PINCH LINE, IN FRONT OF GREEN CHILE CANTINA,
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CAL POWER LIGHTING | SAN JUAN CAPISTRANO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor trenching for electrical hit our 1/2 cts service causing broken and blowing. No USA was called in for this job until after they hit our service. Downey OHS crew arrived, controlled gas and made repairs by cutting out the damaged section and installing 2'' of cts and two cts couplings.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2025-02-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CITY SIDE FIBER | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 1/2 service with a shovel. Gas service was not located for this address.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2025-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | FORTIFY FENCE | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was putting in a new post for a gate and hit the service
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2025-11-13 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NPL CONSTRUCTION | BREA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | 2nd party contractor damaged 1/2'' plastic gas service while digging to install new gas service.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2025-03-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GUSTAVO TREE REMOVAL | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1'''' plastic service with hand tools while planting tree. No USA was called in until after the damage occurred.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2025-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PEDRO MORENO | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged service with shovel removing shrubs
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2025-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | PACIFIC STONE CONSTRUCTION | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 plastic service damage by 3rd party contractor. No USA called.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | PACIFIC STONE CONSTRUCTION | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | PACIFIC STONE CONSTRUCTION HIT SVC LINE WAS HIT WITH A CHIPPING HAMMER WHILE DIGGING OUT A TRENCH. NO USA
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2025-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | PACIFIC STONE CONSTRUCTION | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party hit service while trenching. NO USA
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2025-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ASPLUNDH CONSTRUCTION | PLACENTIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor working for the city of Newport Beach damaged 1/2 PLA service with hand tools, Valid USA correctly marked. Contractor thought old abandoned 3/4 steel service was active service & struck active service with shovel.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2025-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BJ SCOTT AND ASSOCIATES | YORBA LINDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 IPS Service by Shovel/ Hand Tool due to Building Contractor framing Home at 22 Royal Saint George, Newport Beach. Contractor was asked for USA Ticket and did not have one nor did they attempt to give any information regarding one.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2025-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5540 |  | 37 |  | TIGHT QUARTERS | SANTA ANA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor dug before start time on USA ticket was valid; no delineations as well for ticket. Third party contactor hit service with Backhoe.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2025-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | VARKEL | LAGUNA HILLS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor Damaged 1/2 CTS Plastic Service via Pothole using improper digging techniques. USA Provided by Developer was Expired, NO VALID USA.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | PRIME HOME CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 service with shovel while digging for area drains/sprinklers. No USA
Southern California Gas Company | N | ORANGE | NEWPORT COAST | 2025-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SUBLIME SETUP | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Ran ARCOs through SEVEN districts.. No takers, OC oncall crew was tied, had to utilize Inland South oncall crew. 3rd party contractor digging to plant a tree hit 1/2'''' CTS service with shovel. Damaging party had no valid USA, they were attempting to use Moon Valley Nursery''s USA ticket. Marks for service were visible and accurate
Southern California Gas Company | N | ORANGE | NEWPORT COAST | 2025-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party landscaper was digging up a drain with a shovel and damaged a 1/2 PLA service No USA
Southern California Gas Company | N | ORANGE | ORANGE | 2025-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was trenching for sewer installation and ripped through our unmarked 3/4 steel service. No records of the service whatsoever in our system.
Southern California Gas Company | N | ORANGE | ORANGE | 2025-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 10 |  | DONCO & SONS | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | 3rd Party company augured through 2 plastic main while drilling for a sign install. Drilling outside of their delineation and service was struck within the 2'' tolerance zone of ETD''s 2 PE Service paint mark.
Southern California Gas Company | N | ORANGE | ORANGE | 2025-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | HIGH SPEED ROOTER & PLUMBING | EL MONTE | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor installing water service hit our 1/2 inch IPS service with an accu-bore causing broken and blowing. No valid USA during time of damage. Ticket was called in after the job. Downey OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and fusing in 1'' of IPS plastic and two IPS couplings.
Southern California Gas Company | N | ORANGE | ORANGE | 2025-03-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HUDSON PARTNER | ORANGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Private contractor ripped through the gas service while trenching to install electrical conduit. Contractor had no USA.
Southern California Gas Company | N | ORANGE | ORANGE | 2025-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RAMONA INC | ARCADIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor ripped through 1/2 CTS service with backhoe while trenching for sewer main installation. Gas service was marked out correctly.
Southern California Gas Company | N | ORANGE | ORANGE | 2025-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOEL ZUNIGA RODRIGUEZ | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching footing for new wall damaged plastic gas service and tied it back. Expired USA. Notes on expired ticket explaining cust req no paint marks only flags. No flags visible at time of damage.
Southern California Gas Company | N | ORANGE | ORANGE | 2025-12-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LAND MECHANICS | ORANGE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3RD PARTY CONTRACTOR PERFORMING LANDSCAPE CONSTRUCTION SEVERED 1 PLA SVC WITH SKID STEER LOADER.
Southern California Gas Company | N | ORANGE | ORANGE | 2025-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | ESTELIOS | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage to 1 inch plastic service. Service was bent back with PVC cap glued onto the end. No USA. Private contractor on site only provided first name and phone number of the individual who damaged the service. Private contractor did not give any other information and claimed that the service was damaged months ago.
Southern California Gas Company | N | ORANGE | ORANGE | 2025-10-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | UNITED PAVING | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor punctured 2 plastic main with excavator while trenching for Edison. Dropped back to squeeze from a safe distance, main was 7'' 3 deep where we dug. Got shoring to safely squeeze. Used 2 electro couplings and 18 of 2 PE pipe to repair. Soaped all fusions and squeeze, no leaks. ETR had meters shut down, restores called in by me in the morning.
Southern California Gas Company | N | ORANGE | PLACENTIA | 2025-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | WILLIAMS CONSTRUCTION SERVICES | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On 10/30/25, while excavating with hand tools to perform landscaping and concrete work, the contractor damaged a one half inch plastic gas service. The concrete in the area had been removed and the USA marks provided by SoCalGas had not been maintained. At the time of the damage the USA was not valid as not all members on the ticket had responded by marking or sending the EPR code. SoCalGas crew arrived on site and made permanent repairs.
Southern California Gas Company | N | ORANGE | PLACENTIA | 2025-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HIGH SPEED ROOTER & PLUMBING | LA HABRA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Upon arrival found 1/2inch service damaged by plumber and crimped. Service was marked and visible within the delineation. Plumber dug outside of delineation.
Southern California Gas Company | N | ORANGE | PLACENTIA | 2025-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  | 0 |  | BARRY RAE | PLACENTIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging with a pick when he damaged our steel service. No USA.
Southern California Gas Company | N | ORANGE | PLACENTIA | 2025-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BACCARO CONSTRUCTION | FULLERTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party crew was digging for Gas Co. service. The gas service was marked and visible. While looking for the gas service they damaged it with a shovel.
Southern California Gas Company | N | ORANGE | PLACENTIA | 2025-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | JAG UTILITY CONSTRUCTION | FOOTHILL RANCH | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party crew call for USA but the ETD that responded on 9/26/25 close the ticket for not having delineation. He tried calling the phone number in the USA ticket to no avail. 3rd Party crew dug without gas marks because the excavator thought he knew where the gas was. 3rd Party crew damaged the 2 plastic cap at the end of the main.
Southern California Gas Company | N | ORANGE | PLACENTIA | 2025-04-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC EXCAVATION | RANCHO SANTA MARGARITA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1 PE service while digging to install drains. Per site conditions no visible USA markings or flags present.
Southern California Gas Company | N | ORANGE | RANCHO MISSION VIEJO | 2025-10-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | FIRST GENERATION | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while exposing it for extend stub work.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | GREENSCAPES LANDSCAPE | SAN CLEMENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | MR MICHAEL HOUSE PH#949-436-1133 REPORTED A HIT LINE CAUSED BY SHOVEL WHILE REPLACING DRAIN LINES.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2025-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC WEST COMMUNICATIONS | SAN DIMAS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | PER JUAN LEYVA W/PACIFIC WEST COMM 951-990-7253 HIT LINE W/EXCAVATOR, POSSIBLY 1/2 PLASTIC SVC
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2025-12-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | ALDERETE CONSTRUCTION POOLS & SOLAR PLUMBING | SAN CLEMENTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit PLA service crew made repairs
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2025-06-18 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 1.25 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITY OF SAN CLEMENTE WATER UTILITIES | SAN CLEMENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | water company bent 1 1/4 stl main at eom
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2025-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CASAS F PRO LANDSCAPE | ORANGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ARRIVED AT LOCATION SPOKE TO CONTRACTOR FERNANDO. HE IS RUNNING A NEW SEWER LINE. THEY HIT SERVICE WHILE TRENCHING. NO USA
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2025-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SOUTHCAL LANDSCAPE | COSTA MESA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Championed the contractor of the importance of calling 811 prior to starting work and the importance of digging with caution around utilities.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GREENSCAPES | LAGUNA HILLS | CA | N | Y | Yes | No | No | Yes | No | No | No | Landscapers digging a trench for drainage from front yard to back yard they hit our 1/2 cts service with a shovel. No USA was called in for this job. Downey OHS crew arrived, controlled gas and they made permanent repairs by cutting out the damaged section and fusing in 1 ft of 1/2 cts plastic and two cts couplings.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | A OMEGA TERMITE & CONSTRUCTION | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged service with shovel while excavating for retaining wall. No USA was called in. Gas Ops Crew from Aliso arrived, controlled gas and made permanent repairs by cutting out the damaged section and installing 2'' of 1/2 IPS and 2 couplings.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2025-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | FH PLUMBING | MISSION VIEJO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 IPS gas service with backhoe. No USA.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2025-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LANDMARK CUSTOM LANDSCAPE | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 plastic service while working on yard drain line.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DONNIE LANCASTER | SAN CLEMENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | TRENCHING FOR NEW CONSTRUCTION
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2025-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ROJELIO LOPEZ | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit service line with shovel, repaired 1ft section of 1/2 cts pla service
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2025-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | GABRIEL RODRIGUEZ | SAN CLEMENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 IPS gas service with shovel. Hand digging.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2025-01-07 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 1 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 8 |  | SANTA MARGARITA WATER DISTRICT | RANCHO SANTA MARGARITA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Water company did not have a valis USA
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2025-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | SOCAL UNLIMITED HAULING | ORANGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors trenching to install irrigation lines,hit the 1/2 plastic service with an excavator.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EM LANDSCAPE POOLS & SPAS | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service with a shovel while performing landscaping.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2025-02-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MIK CONSTRUCTION | ARTESIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit stub service that was used to jump main for abandonment.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2025-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | 24/7 HAULING & DEMO | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA marks were dug out and some were covered by the excavation spoil. Service was bent back when crew arrived at location.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2025-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DELTA PIPELINE | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTORS HIT SERV LINE WHILE TRENCHING TO MOVE WATER STATION AND HYDRANT.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2025-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OMEGA PAVING | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1 inch plastic service line while digging footings. 1 inchplastic was not leaking, the gauge was deep enough to require a repair.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 36 | 34 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FERREIRA COASTAL CONSTRUCTION CO | RANCHO CUCAMONGA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | No damage to company facilities. No escaping gas. 3/4 steel casing had small slice in wrap from shovel.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-06-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1755 |  | 3 |  | BERGMAN KPRS | BREA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1? IPS PLA Service, Hit with Mini Excavator w/ Auger Attachment, No Valid USA, No Locates Marks on arrival. Crew Completed Permanent Repair.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-06-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LOS ANGELES ENGINEERING | COVINA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit service. broken and blowing. was able to expose damage and repair leak. no other issues found or detected.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-05-27 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SOCALGAS | ANAHEIM | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LCT was using improper potholing techniques, hit 2 gas main with backhoe
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-06-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LOS ANGELES ENGINEERING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY CONTRACTOR HIT 1/2 IPS PLASTIC LINE WITH EFV WITH EXCAVATOR. GAVE USA TICKET NUMBER , NO MARKS ANYWHERE ON FLOOR, STATED DID NOT HAVE GPS TOOL ON HAND, GAS WAS NOT BLOWING DUE TO EFV, STOPPED, PUT DAMAGE TO RISER ON STAND UP AND BARRED TO SMC, NO LEAKS FOUND OTHER THAN DAMAGE.REPLACED APROX 3'' SECTION AND TIED IN WITH 2 COUPLINGS.CALLED IN FOR RESTORE , LEFT METER OFF
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PRIMEBORE DIRECTIONAL BORING | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was trenching for communications lines and damaged 1/2 plastic service. USA was valid, service was incorrectly marked. locating wire damaged & service located by footage. footage correct for SMC, but service was roped around trees in front yard.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-08-05 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | PAR ELECTRICAL CONTRACTORS | ORANGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Edison hit our 2 plastic main while augering to replace an electric pole causing broken and blowing. They had a valid USA, but the main was mismarked. Multiple crews from Santa Ana base worked this job and made repairs by stopping the main, and replacing 11'' of old main.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CRAFTSMAN SEWERS | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor with Valid USA digging to install Sewer Main accidentally damaged 1/2 Plastic service by removing buckets of dirt with backhoe. Valid Marks and very Visible, Contractor failed to ensure proper tolerances.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SOLEX CONTRACTING | TEMECULA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged ?? IPS Service Hit with Shovel by contractor working to install fiber and power boxes, USA Valid A251530311, Locates Off 21? due to ETD getting bad signal with power and communication substructures interfering with Locate Signal. ETD use Measurement Only due to signal strength and informed Contractor to call if not found.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JAVIER AYON | AZUSA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, contractor was trenching for homeowner on private property. Contractor sliced through gas service with shovel.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  | 0 |  | DAN S TRACTOR SERVICE | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | old main and service on property not marked. GIS unclear. The meter and service to the property were marked properly. Property over 8 Acres.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | KHIEM CAI | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Work on property evidently done by contractor. 100'' trench squared off and appeared to be done by excavator. Homeowner claims no contractor, just friend helping him out and digging by hand. Also stated they exposed the leak, did not cause it. Evidence shows steel casing pulled back and caused leak in plastic. LCT Lamas cut out section of casing and used 2 couplings and 2'' of pipe to make repair.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WONG QUNG JUNG | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging with shovel for new sewer line to ADU hit our 1/2 IPS service. No USA was called in for this job. Downey OHS crew arrived, pinched service and made permanent repairs by cutting out the damaged section and installed 2'' of 1/2 IPS and two IPS couplings.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-11-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3270 |  | 1 |  | WA RASIC | BELL GARDENS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Dig in. 2 PE SVC damaged with backhoe while digging trench for water hydrant. Construction site for new apartment structure. All earth. Old marks present but no recent valid USA provided. Improper potholing, our service was not exposed prior to excavating with backhoe. 1 customer affected. Unopened restaurant.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DANIEL SEMA | SANTA ANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging for ADU water line hit our 1/2 plastic cts with a shovel causing broken and blowing. No valid USA ticket was on file. Contractor was going off old marks that were put down in 2022. contractor called in USA ticket right after they damaged our line. Downey OHS crew arrived, controlled gas and made permanent repairs by cutting out damaged section and installed 3'' of 1/2 cts and two couplings.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ELT PLUMBING | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber installing drainage damaged our 1/2 IPS service line with a shovel. No USA called in for this job. Downey OHS crew arrived, completed leak investigation and found leaking service due to contractor cutting the service with shovel. Crew made permanent repairs by cutting out the damaged section and installed 2'' of IPS pipe and two IPS couplings.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-09-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | COVA | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor with NO USA on New Business and Development work damaged 2 PLA Service which was installed days prior. Contractor Augured into the 2 PLA Svc while installing Steel Fence posts.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Arizona Pipeline Installing conduit via open trench method damaged 1/2 IPS PLA service line due to service line snaked from SMC location. Contractor had Valid USA.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PAR ELECTRICAL CONTRACTORS | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors for Edison putting in grounding rods were pot holing over our gas service in the parkway next to their pole. While using the shovel at the bank of their hole, the contractor cut through ï¿½ IPS pipe. USA was good and markings were spot on. Downey OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installed 2'' of IPS and two IPS couplings.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY CONTRACTORS DIGGING WITH HANDTOOLS AND NO USA SEVERED 1/2 CTS PLA SERVICE WITH SHOVEL. SERVICE TIED UPON ARRIVAL.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2025-08-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging a trench for a new wall hit our 2 main with a large excavator in an undeveloped new track. The developer had an expired USA, and the contractor knew where the main was, but said he assumed it was deeper. Downey OHS crew arrived, controlled gas by pinching and made permanent repairs by cutting out the damaged section and replacing it with 3'' of 2 plastic, two 2 electrofusions and 2 tee''s for testing.
Southern California Gas Company | N | ORANGE | SEAL BEACH | 2025-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | WELL DONE BUILDING & DESIGN | COSTA MESA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor installing drain & water for house remodel damaged 1/2'''' CTS service with shovel. Invalid USA, marks had been removed, and ticket was expired.
Southern California Gas Company | N | ORANGE | STANTON | 2025-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | GRP CONTRACTORS | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor trenching for sewer line hit 1/2 svc with shovel. Gas marks were spot on.
Southern California Gas Company | N | ORANGE | STANTON | 2025-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3983 |  |  | NA | PAR WEST | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | A contractor hit a 2-inch steel main while replacing a telephone pole. USA was valid and marks were on.
Southern California Gas Company | N | ORANGE | STANTON | 2025-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | THANH TRUNG CONSTRUCTION | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging a trench for construction cut through our 1/2 branch service causing broken and blowing. no USA was requested for this job. Downey OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installed 2'' of 1/2 cts and two couplings.
Southern California Gas Company | N | ORANGE | TRABUCO CANYON | 2025-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HORIZON CONSTRUCTION AND REMODELING | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew made repairs to pla service
Southern California Gas Company | N | ORANGE | TRABUCO CANYON | 2025-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BLACKBIRD ELECTRIC | GLENDORA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew made repairs to pla service
Southern California Gas Company | N | ORANGE | TRABUCO CANYON | 2025-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RESCOM LANDSCAPING | COSTA MESA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HIT GAS LINE WITH PICKS/SHOVELS TO LOCATE THE GAS LINE FOR GRADING TIM O''SULLIVAN W/RESCOM 714-574-5490
Southern California Gas Company | N | ORANGE | TUSTIN | 2025-10-20 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 3 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7769 |  | 0 |  | SECURITY PAVING COMPANY | WESTLAKE VILLAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Security Paving Co. Damaged a 3 Steel Gas Main along with a 11/4 Steel Direct Tie by heavy equipment 950 Loader grading Earth.
Southern California Gas Company | N | ORANGE | TUSTIN | 2025-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VVD VIDEO VOICE DATA COMMUNICATIONS | GARDEN GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | A Communication company was potholing locating their line. While doing so they hit our ï¿½ IPS service in PL just upstream from sidewalk with a shovel. Valid active USA. Downey OHS crew arrived, dug control hole and pinched service to contain gas leak. Crew made repairs by cutting out the damaged section and installing 1'' of ips and two couplings.
Southern California Gas Company | N | ORANGE | TUSTIN | 2025-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CABLECOM LLC | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Found damaged 1/2 inch cts service that was previously cut back cut back service due to damage. USA Valid, Gas line marked incorrectly Service history footage off by 10''
Southern California Gas Company | N | ORANGE | TUSTIN | 2025-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | HP COMMUNICATIONS | LANCASTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor installing fiber hit service will trenching.
Southern California Gas Company | N | ORANGE | TUSTIN | 2025-01-06 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 12 | 188 | 180 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  |  | NA | FERREIRA COASTAL CONSTRUCTION CO | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Damaged 12 H.P. main, sidewall of main was dented while excavating with backhoe. H.P. standby was on site when damage occurred. Valid USA
Southern California Gas Company | N | ORANGE | TUSTIN | 2025-03-20 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 4 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | DASH CONSTRUCTION | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was augering for fenceposts in private property when they struck a 4 inch plastic gas stub. Stub was marked correctly, Valid USA, contractor failed to had dig over gas facilities
Southern California Gas Company | N | ORANGE | VILLA PARK | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TROPICAL PLAZA NURSERY | ORANGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Contractor hit gas service with jack hammer.
Southern California Gas Company | N | ORANGE | VILLA PARK | 2025-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KARL FRANCIS | VILLA PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 3/01/25 while hand digging to remove a stump, a non-licensed landscaper damaged a 1/2 IPS plastic gas service. Gas Operations crew arrived on site and made permanent repairs.
Southern California Gas Company | N | ORANGE | VILLA PARK | 2025-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PLATINUM BUILDERS | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with no USA, hit 1 plastic gas service with shovel.
Southern California Gas Company | N | ORANGE | VILLA PARK | 2025-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1766 |  | 1 |  | DWA PLUMBING | LOS ALAMITOS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Fused 1'' new section of 1/2 IPS plastic pipe to service. soap tested fusions. no leaks. purged at riser. customer service onsite to build meter. work complete. b. brown 1/30/2025
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2025-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TU GENERAL CONSTRUCTION | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching out a drainage pipe hit our 1/2 IPS service with a mini excavator. No USA was called in for this job. Downey OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installing 2'' of 1/2 IPS and two couplings.
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2025-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NTK CONSTRUCTION | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor using a mini excavator to do water line work hit our 1/2 inch plastic service causing broken and blowing. Downey OHS crew arrived, pinched service to control gas and made permanent repairs by cutting out the damaged section and installing 2'' of IPS and two couplings. No USA was called in for this job
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2025-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DIEU NGUYEN | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 IPS Gas Service with shovel. No USA.
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2025-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | OC STAR CONSTRUCTION | WESTMINSTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FOUND DAMAGED 1/2 IPS BRANCH SERVICE. SERVICE WAS DAMAGED BY CONTRACTORS. No USA Called
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2025-09-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NEXT CONSTRUCTION | HUNTINGTON BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for new sewer install for ADU and hit our 1/2 IPS service with a shovel causing broken and blowing. No USA was called in for this job. Downey OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installed 1 ft of 1/2 IPS and two couplings.
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2025-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | QUANG NGUYEN | GARDEN GROVE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2'' service with a mini excavator while installing a sewer line to the back of the property (Future ADU). No USA.
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2025-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | STAR CONSTRUCTION SERVICES | WESTMINSTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Usa was called in. Service was marked correctly. Contractor struck service with shovel.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2025-01-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | BIG BEN ENGINEERING INC | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 inch Plastic service damaged by Big Ben Construction excavator. Broken and blowing. Notified 12:10pm. Valid USA. Contractor did not expose gas line prior to using excavator.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2025-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LEGACY IRON WORKS FENCE & GATES | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging with postal digger for fence. No USA.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2025-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BIG BEN ENGINEERING INC | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor hit our gas line while digging
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2025-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ELIAS ENGINEERING CONSTRUCTION | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew did not pothole service. GIS and service history are wrong, they both say that the service is 3/4 steel but it''s actually 1/2 IPS. Added material used.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2025-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | URBAN LANDSCAPE | NEWPORT BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was hangdogging for new drain line. No USA.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2025-07-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 11 | 11 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 16 |  | MORONGO BAND OF MISSION INDIANS | BANNING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor had valid USA, exposed pipe and still truck gas main.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2025-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DIAMOND W EXCAVATING | WILDOMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor potholing for service and struck service. USA valid and marked with flags.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MURRIETA DEVELOPMENT INC | TEMECULA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1 inch steel service was not marked in the path of work. resulted in a damage.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2025-04-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1865 |  | 5 |  | ORTIZ FENCING | SAN JACINTO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging with postal shovel, struck service, no valid USA.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2025-01-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | MCC PIPELINE | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor potholed service before conducting their work, later hit service when trenching. located out correctly. valid usa.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2025-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MCC PIPELINES | YUCAIPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor valid USA, service marked out correctly (at moment), contractor struct service when excavating. rehooked up to service to relocate out service and did not match. hooked up to riser and also didn?t match.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MCC PIPELINE | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor found unknown/unlocatable steel service with backhoe
Southern California Gas Company | N | RIVERSIDE | BANNING | 2025-05-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC WEST UNDERGROUND | YUCAIPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor struck service while working.
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2025-07-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TBU | BEAUMONT | CA | N | Y | Yes | No | No | Yes | No | Yes | No | No valid USA, contractor digging for irrigation crossing, hit 2 plastic main with backhoe.
Southern California Gas Company | N | RIVERSIDE | BERMUDA DUNES | 2025-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | CHRISTOPHER BAYRON | DESERT HOT SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 cts service damaged by landscaper while attempting to remove a tree from property. Crew was able to make permanent repairs.
Southern California Gas Company | N | RIVERSIDE | BLYTHE | 2025-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | WILL WHITE | BLYTHE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no USA, occupant hit service with posthole digger.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2025-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1766 |  | 1 |  | EDGAR PEA | DESERT HOT SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1/2 CTS service while trying to remove a tree stump. The contractor failed to notify USA/Dig alert before digging.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2025-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RAYUEL ALBARDIN | CATHEDRAL CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 CTS service while excavating with a shovel to plant a palm tree. No USA ticket.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2025-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DESERT ELITE ELECTRIC & CONSTRUCTION | INDIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor hit service while digging for electrical conduit. Unmapped stub at location. Unable to locate. MUR submitted to update GIS
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2025-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DESERT ELITE ELECTRIC & CONSTRUCTION | INDIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator trenching to install electrical conduit damaged undocumented stub across from lot lines of 32205 & 32225 Cathedral Canyon.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2025-12-19 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4390 |  | 13 |  | SOCAL EDISON | CATHEDRAL CITY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ETD mis-marked a 2 PLA main and it was damaged while auguring by SCE.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2025-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ROBERT QUIROZ | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner ruptured a 1/2 cts service with backhoe attempting to remove a Palm Tree. Dig alert not called in.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2025-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | VALLEY PLUMBING | BERMUDA DUNES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third-party contractor hit a 1/2 CTS service line with a shovel while making repair to a water leak. The contractor failed to notify the USA/Dig Alert.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PEREZ LANDSCAPING | CATHEDRAL CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. 1/2 service damaged with shovel by landscaper.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2025-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TBU | BEAUMONT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third-party contractor hit a 1/2 CTS service with a backhoe while installing electrical conduits for Edison. The contractor failed to notify 811/Dig Alert before digging. LCT made permanent repairs with 3'' of 1/2 CTS pipe & (3) 1/2 CTS Fusion Couplings.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CHRIS | CATHEDRAL CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner hit a 1/2 CTS service with a shovel while digging for Lanscaping. Fire department evacuated two persons from Unit # 4. Service was properly marked with flags, but homeowner was not careful when digging around our service.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2025-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DESERT ELITE ELECTRIC & CONSTRUCTION | PALM DESERT | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third-party contractor hit a 1/2 IPS service with a backhoe while trenching to install an electrical conduit. The USA ticket was expired (B252190719) and not renewed for remarking.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2025-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | CM CORP | LAGUNA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third-party contractor hit a 1 plastic service while installing a light pedestal. Contractor failed to notify USA/Dig Alert before digging. Crew made permanent repairs altering 2'' of 1 plastic coil pipe & (2) 1 socket fusion couplings.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2025-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | MAINTENANCE FOR APT BLDG | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 service damaged by maintenance worker excavating for water service repair. No USA.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2025-09-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NUVIEW ELECTRIC | THOUSAND PALMS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party contractor hit a 2 plastic main with an excavator while trenching to install electrical conduits. The contractor did not provided a valid USA ticket. The ticket provided A251400623 was expired on 6/17/25.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2025-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1678 |  | 3 |  | REYES RUDY G | COACHELLA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 plastic branch service hit by company owner rudy reyes with shovel. Digging for irrigation purposes. Rudy Reyes owner of company and land where incident happened. Third party contractor failed to notify USA/Dig Alert. LCT made permanent repair altering 1'' of 1/2 CTS coiled pipe & (2) CTS socket couplings.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2025-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1755 |  | 3 |  | DCR COMMUNICATION | COACHELLA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Third contractor hit a 1 plastic service while boring a communication line (fiber) in. The contractor was boring outside of the delineation.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2025-09-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JONATHAN SEGOBIANO | COACHELLA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HOMEOWNER HIT SERVICE. 1/2 PLASTIC.WHILE REMOVING TREE STUMP. HIT WITH PIC AXE.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2025-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | VAN DYKE | TWENTYNINE PALMS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | A third-party contractor hit an unmarked 3/4 inch steel service with a backhoe while working on a sewer line. The service is not recorded on GIS or service history.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2025-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DESERT WEST CONSTRUCTION | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The pool contractor was digging without a USA ticket and damaged a 1/2 CTS service with a pickaxe. SCG crew made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2025-07-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | PLATINUM LANDSCAPE | PALM DESERT | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 2 plastic main with a trencher while installing a sewer line.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2025-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MONTE VISTA HOMES | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 CTS stub while digging for electric conduit.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KL VENTURES | ALTA LOMA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1/2 plastic stub with an excavator/backhoe while installing electrical conduits. The contractor failed to notify USA/Dig Alert. LCT made permanent repairs with a 1/2 CTS Cap.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2025-02-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | S K L CONSTRUCTION | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A third-party contractor hit a 2 plastic main with a backhoe/track hoe while installing electrical lights. The contractor failed to notify USA/ Dig alert.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2025-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TOM RICHINS | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors doing work for home owner drilled into 1 1/4 inch steel casing with 1/2 IPS service inside, to verify if line was live or dead.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2025-10-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | PLATINUM LANDSCAPE | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor ripped service out of the ground with backhoe
Southern California Gas Company | N | RIVERSIDE | CORONA | 2025-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PG CONTRACTORS | POMONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging for electrical conduit hit service with a shovel
Southern California Gas Company | N | RIVERSIDE | CORONA | 2025-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ALFREDO HERNANDEZ | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service line while trenching to install new leach line for septic system. Homeowner failed to call USA.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2025-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | MEMO VAZQUEZ | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2IPS svc struck & damaged while grading for block wall installation.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2025-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MEMO VAZQUEZ | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck 1/2 IPS service while digging for block wall. No USA, second damage at location by same contractor. Homeowner provided personal info for damaging party info.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2025-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | GILBERT MARTINEZ | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service digging to repair septic system. No USA
Southern California Gas Company | N | RIVERSIDE | CORONA | 2025-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RICHARD RESENDEZ | LAKEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged service with post hole digger. no USA
Southern California Gas Company | N | RIVERSIDE | CORONA | 2025-04-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | CENTURY WEST CONCRETE | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Concrete contractor drove grading stake into earth, NO USA. Contractor reported gas odor 4/25/25, asked for SCG inspection. Crew found damaged stub service.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2025-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | VALVERDE CONSTRUCTION INC | CITY OF SANTA FE SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Construction crew had previously exposed gas line and had forgotten about it when continuing to excavate
Southern California Gas Company | N | RIVERSIDE | CORONA | 2025-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | JOSE GOMEZ | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck and pulled line while digging with excavator.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TAMER EZZAT | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 inch CTS , Third-party damage, crew made permanent repair.NO USA.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2025-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VANNESSA TORRES | CORONA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit gas line trenching to move existing gas line. (future D-ticket)
Southern California Gas Company | N | RIVERSIDE | CORONA | 2025-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MIKE ULIBARRI | CORONA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | THIRD PARTY DAMAGED LINE, DID NOT HAVE USA. CREW MADE PERMANENT REPAIRS.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2025-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LANDMARK ASSOCIATION | VALLEY VILLAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While attempting to remove footing for light pole at new park, excavator damaged 1 PE service. No valid USA. Excavator requested service be cutback per no gas facilities to be installed. Crew also discovered 1 riser in field damaged previously.
Southern California Gas Company | N | RIVERSIDE | EASTVALE | 2025-07-31 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 4 |  | JURUPA COMMUNITY SERVICES DISTRICT | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | JURUPA WATER PERFORMING SPLIT AND PULL FOR WTR SERVICE AND DAMAGED 2 PLASTIC MAIN. Damage prevention was onsite reminding water company that they need to expose SCG marks before any split/pull method. SCG crew made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | EASTVALE | 2025-12-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DOWNING CONSTRUCTION | REDLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor struck 4 Plastic main with backhoe while trenching for water line install. Valid and accurately marked USA, marks visible, contractor failed to hand expose within tolerance zone. One commercial outage.
Southern California Gas Company | N | RIVERSIDE | EASTVALE | 2025-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CAL WEST UNDERGROUND INC | EASTVALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3 PE main damaged by 3rd party contractor with backhoe. No USA Ticket
Southern California Gas Company | N | RIVERSIDE | EASTVALE | 2025-06-24 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JURUPA COMMUNITY SERVICES DISTRICT | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | water company hit marked gas main installing new water service.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2025-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | JORGE VASQUEZ | HEMET | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Approved. No Active USA, current on was expired. FOUND SERVICE LEAKING IN EXCAVATION DUE TO DIG IN. ABAND STUB TO REPAIR LEAK. PERMINENT REPAIRS COMPLETE LEFT CONDTIONS SATISFACTORY. JMF 520004346417
Southern California Gas Company | N | RIVERSIDE | HEMET | 2025-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ROSALIO SERNA | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 1/2IPS service with clay spade. No dig alert.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BORDEN EXCAVATING | CALIMESA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Approved. They did have an active USA; this was a 1/2 stub off the main that was hit and was not mapped. Crew ended up ABD 1/2 IPS Stub @ SMC.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2025-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MICHEAL COMPTON | HEMET | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was digging to install a new septic tank with mini excavator when he stuck 1/2 service to his house. no USA was called in, crew came out and dug a control hole to stop gas flow and made repairs to service.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2025-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BELLA CLEANING MAINTENANCE | HEMET | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged ?? IPS service by 3rd party contractor while installing a fence. NO USA ticket.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2025-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | JESS STONE ELECTRICAL | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA Was Called in.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2025-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NETWORK CONNECTIONS | SIMI VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while boring interdict for frontier communication.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MANUEL GUERRERO | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA
Southern California Gas Company | N | RIVERSIDE | HOMELAND | 2025-11-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | JOAQUIN GONZALEZ | HOMELAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew was called out here for odor complaint. They Exposed unreported damage caused by homeowner while trenching for sewer.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2025-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | DUNN S DESERT LANDSCAPE SERVICE | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 CTS service with a shovel. Crew was able to safely make permanent repairs.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2025-09-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DESERT INNOVATIONS LANDSCAPE | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third-party contractor claims he damaged the service while pulling out a green irrigation box with his hands, but pictures show indications of being hit with a shovel. The contractor failed to notify USA/Dig alert before digging. LCT made permanent repairs with (1) 1/2 CTS socket coupling.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2025-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | STOKER POOLS | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third-Party contractor hit a 1/2 cts service with a shovel while digging or a pool. The contractor failed to notify USA/Dig Alert before digging. LCT made permanent repairs altering 2'' of CTS service with (2) CTS Couplings & Pipe.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2025-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | COMMON GROUND POOL & CONCRETE | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third-party contractor hit a 1/2 cts service while digging to plant a tree. The contractor failed to notify USA/Dig Alert.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | EDILBERTO AGUILAR | CATHEDRAL CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1/2 CTS service with a shovel while removing a tree for the homeowner. The contractor failed to notify USA/Dig Alert before digging.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | H2O LANDSCAPE & MAINTENANCE | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY CONTRACTOR DAMAGED A 1 PE SERVICE WITH A SHOVEL. CREW MADE PERMANENT REPAIRS.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | WALTON BROS ENTERPRISES DBA CJW GEN CONTRACTING | MURRIETA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third-party contractor hit an unmarked 1/2 plastic service with an excavator with trenching to install electrical conduits for IID.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DCR COMMUNICATION | COACHELLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | THIRD PARTY CONTRACTOR HIT A 1/2 CTS SERVICE WITH A SHOVEL WHILE INSTALLING FIBER CONDUIT FOR FRONTIER. CONTRACTOR FAILED TO BE CAREFUL WHILE DIGGING AROUND SERVICE. ACCORDING TO LABORER, HE CONFUSED THE SERVICE WITH A TREE ROOT.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALEJANDRO | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A third-party contractor damaged a CTS service with a shovel. Crew made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GARDENER | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Landscapers excavating to remove tree, damaged service with shovel.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-01-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LA HACIENDA NURSERY AND LANDSCAPE INC | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third-party contractor hit a 1/2 IPS service with a backhoe/mini-excavator while working in a drainage line. The contractor failed to notify the 811/USA Dig Alert.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-08-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TBU | BEAUMONT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 main damage by the contractor while backfilling a trench.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MICHAEL FLORES - SPACE 278 | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit service while installing fence. Crew squeezed and made repairs to 1/in plastic service using one foot of pipe and two fusion couplings. No Injuries, Evacuations, Emergency Services, Media or Road Closures.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | HEATHER LOPEZ | INDIO | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1/2 CTS service while working on sewer. The contractor did not have a valid USA ticket at the moment of the damage. The original ticket was closed as not delineated by ETD.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-08-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | INDIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating to repair sewer drainage at home, 1/2 PLA service damaged
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | CHRIS SCOTT | PALM DESERT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid USA, excavator (Occupant) damaged service with shovel while excavating. Service marked with whiskers in earth over pipeline. Damage caused outage to 3 units.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | COBANO LANDSCAPE & IRRIGATION | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The service that was affected was marked properly, and the contractor did not perform potholing correctly. The contractor did have a valid USA ticket.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALBERT CAMARENA | INDIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged 1/2in plastic service while working on water lines. No Emergency Services, Injuries, Evacuations, Media or Road Closures. Crew made repairs with 1/2in coupling.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | MASTEC COMMUNICATIONS GROUP | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Previous damage by Mastec Communications Group, boring for fiber optic. Original call for no gas at 6 apartments. Mastec excavated (potholed) service in earth, but not where boring. Found disturbed soil in parkway to confirm. 1/2 service in 3/4 casing damaged resulting in 6 outages at apartment complex. Marks found over service and crossing Sonora Ave to be accurate.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | GILBERTO RAMOS | LA QUINTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1/2 CTS service with a shovel while digging to install a brick foundation. The contractor failed to call his own USA ticket. The homeowner called his own ticket. LCT made permanent repairs with (2) 1/2 CTS couplings & 2'' of 1/2 CTS pipe.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GRANITE CONSTRUCTION COMPANY | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Granite Const. was grading the side of the road and removed the current marks and did not pothole to verify depth beforehand.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-04-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GRANITE CONSTRUCTION COMPANY | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor hit a 1/2 IPS service while grading to install curve & gutter. Contractor failed to pot hole by hand to expose the service before using the grader. LCT made permanent repairs altering the service with 2'' of 1/2 IPS pipe & (2) 1/2 IPS Fusion couplings.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2025-07-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | PACIFIC UTILITY INSTALLATION | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A third-party contractor damaged the 2 plastic main with a backhoe. This is the same contractor who is backfilling for our NB install?no USA.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2025-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | INNOVATION BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 1/2 CTS damaged by 3rd party contractor while excavating with a shovel. Service was not marked. Contractor dug prior to ticket being Valid.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2025-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MTC CONTRACTORS | EASTVALE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | customer installing a drain from backyard to the front yard. While customer private contractor trenching for drain they struct our marked 1/2 plastic gas service. Crew got gas under control and made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2025-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DAVID SANTANA | JURUPA VALLEY | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | HOMEOWNER DIGGING TRENCH FOR CONDUIT AND KNICKED 1/2 BRANCH SERVICE GOING TO 5075 TRAIL CANYON DR. ABLE TO PINCH SERVICE AND REPAIR. BRANCH SERVICE WAS NOT MARKED WHERE HIT. CUSTOMER HAD AN EXPIRED USA.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2025-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | LUIS MENDOZA | JURUPA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner hired day laborers to remove old bush stumps. While excavating stump workers knicked 1/2 ips service line.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2025-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BC CONSTRUCTION | JURUPA VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 IPS service was damaged by 3rd party contractor while hand excavating. USA ticket was expired. Marks were visible and accurate.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2025-10-08 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | LEVI LANDSCAPE | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 2 PE main was damaged by 3rd party contractor. NO DELINEATION for USA Ticket. Contractor dug without any marks present.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2025-09-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | WILHELM ELECTRIC CO | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 PLASTIC MAIN HIT BY ELECTRICAL SUB-CONTRACTOR W/ BACKHOE. NO USA TICKET.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2025-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MATHEW CASTANEDA | JURUPA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Worker hit 1/2 plastic service while grading. No valid USA ticket number found for this project.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2025-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | ALL CITIES ENGINEERING | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | third-party contractor failed to maintain proper utility markings and struck a ? steel (STL) gas service line with a backhoe. Southern California Gas (SCG) crew responded to the site and replaced the damaged service line to complete permanent repairs.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2025-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CARL PROCIDA CONSTRUCTION | WHITTIER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 PE service damaged by 3rd party contractor while hand excavating. No USA Ticket.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2025-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | TAREQ YOUNIS | CORONA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party damage, contractor damaged 1/2 PE service within the delineations, marks were accurate. Ticket was expired. SCG crew made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2025-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CJW | MURRIETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor failed to notify USA/Dig Alert before digging damaging a 1 plastic stub with an excavator.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2025-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COBANO LANDSCAPE | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third-party contractor hit a 1/2 CTS service with a backhoe while digging for irrigation. The contractor failed to expose the pipe by hand as required.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2025-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BLAKE KHACHATOORIN | LA QUINTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Service damaged while homeowner planting tree.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | PERFECT POOLS | MENIFEE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged the 1/2 CTS service while working to install pool lines. Contractor had NO USA on file, crew made repairs.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2025-05-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | LAWSON CONCRETE | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY SUB CONTRACTOR HIT GAS LINE WITH SHOVEL WHILE EXCAVATING. CREW MADE PERMANENT REPAIRS NO USA CALLED
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2025-08-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WALTON BROS ENTERPRISES DBA CJW GEN CONTRACTING | MURRIETA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 2 PE main that was mismarked by the ETD and off by 3''.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2025-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | H2O LANDSCAPE AND MAINTENANCE | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third-party contractor hit a 1 plastic stub with a shovel while planting a Palm Tree. The contractor failed to notify 811 before digging.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2025-09-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TBU | BEAUMONT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third-party contractor hit a 2 plastic main backhoe while digging to install an electrical pipe. The contractor failed to notify USA/Dig Alert before digging.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2025-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BARILLAS LANDSCAPE & GARDENING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 IPS service was damaged by a landscape contractor while excavating with a shovel. Upon ETR arrival, FD had 4 people evacuated from 2 structures and the street closed. Time of gas control was 18:30, evacuations and road closure both lifted at that time. No USA ticket.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ENGSTROM CONSTRUCTION INC | INDIAN WELLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third-party contractor hit an non-exposed 1/2 inch cts service line with a saw saw while cutting a pvc drain line. The contractor failed to notify USA Dig Alert.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2025-01-09 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | D T STELLAR GENERAL ENGINEERING | WINCHESTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Claims Investigation Updated.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2025-05-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WALTON BROS ENTERPRISES | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3RD PARTY CONTRACTOR CREW HIT 2 MAIN LINE WITH EXCAVATOR WHILE DIGGING DURING WATER INSTALL PROJECT. CONTRACTOR FAILED TO MAINTAIN FLAGS IN PLACE.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2025-08-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WALTON BROS ENTERPRISES DBA CJW GEN CONTRACTING | SAN JACINTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor digging to install SCE conduit damaged a 2 PE main with an excavator. Contractor did have a current USA but failed to properly expose the gas main.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2025-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RAYMOND KUO | LAKE ELSINORE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA at the time of incident and no one onsite at the home or contractors to be located. Damage Prevention to follow up and get information on who the damaging party was.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2025-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ALFRED MACEDO | LAKE ELSINORE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage occurred to a ï¿½ branch service. Upon arrival, the service had been temporarily tied back. The SCG crew responded and completed permanent repairs, including alterations to the service.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2025-04-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DOUBLE D PIPELINE | TEMECULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA was valid and SCG marks were within the tolerance zone at the time of damage. Contractor failed to maintain clearance after exposing the main.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2025-07-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | MAIL CREEK CONSTRUCTION | CERES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA at the time of incident. 3rd party contractor struck and damaged a 1 plastic service with a backhoe while digging for electrical. Crew responded and made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2025-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LAKE ELSINORE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Damage to 1/2 PLA service while digging out for water line in private property. No USA was called in and no homeowner was available to give out contact information
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2025-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RAQUEL ALEJO | LAKE ELSINORE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 plastic service while trenching for drain. No USA at the time of incident.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2025-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SUPERIOR FENCE & RAIL OF RIVERSIDE & ORANGE CO | MURRIETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA at the time of incident. Contractor damaged a 1/2 IPS service digging for a fence post.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GARNEY CONSTRUCTION | TEMECULA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | USA valid, unmapped cutback was hit by contractor
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 55 | 52 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | G & D DEMOLITION INC | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor demolished a home and pulled a 3/4 steel service out of the ground and left it exposed not leaking. No USA and crew abandoned at the service to main conection for safety.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2025-03-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GARNEY CONSTRUCTION | TEMECULA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Valid usa. damaged inserted plastic service marked by measurement.
Southern California Gas Company | N | RIVERSIDE | MECCA | 2025-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BLANCO CONSTRUCTION | BUENA PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | A third-party contractor damaged a 1/2 CTS service while boring in irrigation lines. ETD failed to locate and mark the damaged service.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2025-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LUIS SANCHEZ | VICTORVILLE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 service No USA
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2025-04-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | PLATINUM LANDSCAPE | PALM DESERT | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service was damaged by 3rd party landscaping company. Service was not marked due to NO Delineation.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ASCEND REAL ESTATE | SAN JUAN CAPISTRANO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. NO USA called in
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2025-05-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GREENBEE | PERRIS | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a service with a backhoe digging for sewer. 3rd party contractor dug prior to ticket being valid.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2025-07-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | AMERICAN LANDSCAPE & MAINTENANCE | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1 plastic service with a backhoe will digging for irrigation. There was no USA at the time of the incident.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2025-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | HOMESITE SERVICES | LIVERMORE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | THIRD PARTY CONTRACTOR DAMAGED 1PLA stub with an excavator. NO DIG ALERT ticket.
Southern California Gas Company | N | RIVERSIDE | MIRA LOMA | 2025-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BC CONSTRUCTION | JURUPA VALLEY | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 pe service by 3rd party contractor while hand excavating. Contractor knew the location of the service. C/S was doing the restore when they hit the service for the 2nd damage of the day.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2025-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DANIEL HERNANDEZ | MORENO VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | struck service while digging to install new fence, no USA called in.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2025-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 53 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JC BUILDING SYSTEMS | MORENO VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. Crew did not hand expose and hit line
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 52 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ML HOME SERVICES | MORENO VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA called in
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2025-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JARED MEDING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged ï¿½ inch cts branch service with pick. No dig alert was requested.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2025-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 49 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  | 0 |  | TOP TIER LANDSCAPE CONSTRUCTTION | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. Did not Notify USA and ended up hitting 2main feeding condo''s
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2025-06-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BOX SPRINGS MUTUAL WATER | MORENO VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. Expired USA Ticket
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SUMMIT ELECTRIC INC | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA Called in
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2025-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | UNLIMITED ENGINEERING | REDLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew was called to a hit 1 plastic service line. When we arrived on scene we found a damaged PLA service folded back and taped. The 3rd party contractor hit the line with a backhoe. There was a mark on the asphalt about 5'' from the trench that was off of measurements of an abandoned line in Service History. The mark has abandoned on it. It did not line up with the trench that they were digging. All facilities to the lot showed to be fully abandoned so this seems like a case of company records not being up to date. Crew will have to have service ID created, so we can create an order to abandon the service.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2025-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LAKEVIEW PLUMBING | HIGHLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer''s plumber removed a palm tree and was digging to repair the sewer lateral due to root damage. Plumber was using a jackhammer to break up the dirt and severed our 1/2 plastic service line. Plumber failed to call for USA. Crew was able to locate the line and safely excavate to control gas and alter service.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2025-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ELMER GUTIERREZ | MORENO VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner Elmer Gutierrez was working on his drain system and hit the gas service while digging. No valid USA.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2025-02-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ROSAURA MARTINEZ | MORENO VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | According to the customer service technician, the homeowner declined to provide information about the party responsible for damaging the gas facility. The technician discovered that a 1/2 CTS plastic service line was damaged due to the installation of a wooden fence post. Upon my arrival homeowner was not on scene. SCG crew made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2025-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | FERREIRA COASTAL CONSTRUCTION CO | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party Contractor DAMAGED 1/2CTS service with shovel. VALID USA. Gas marks were visible and correct.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2025-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ANTHONY CAMPBELL | MORENO VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was removing a tree stump when he accidently sawzalled through the 1/2CTS PLA BRANCH service. NO DIG ALERT.
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2025-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SBLA CONSTRUCTION REMODEL | ENCINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 CTS service damaged by 3rd party contractor while excavating with a post hole digger. No USA Ticket
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2025-07-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | JURUPA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer digging footing hit 1 IPS stub, No USA
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2025-02-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | D R HORTON | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 inch plastic service while digging for a drain. No USA at the time of incident.
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2025-11-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  | 0 |  | BLACK HAWK ELECTRIC | ESCONDIDO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | DAMAGED 2 INCH PLASTIC MAIN WITH BACKHOE. NO USA CALLED UNTIL DAMAGE OCCURED. NOT MARKED. PERMANENT REPAIRS COMPLETED BY CREW. CREW TIMES ESTIMATED ORDER WAS NOT ABLE TO BE COMPLETED TIL THE FOLLOWING DAY
Southern California Gas Company | N | RIVERSIDE | NORCO | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | VVD VIDEO VOICE DATA COMMUNICATIONS | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors replacing Homeowners communication line, hit 1/2 IPS plastic service with a shovel while excavating. No USA was called in for this job. Chino OHS crew arrived on site, controlled gas and made permanent repairs by cutting out the damaged section and installed 2'' of 1/2 IPS and two IPS couplings.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2025-05-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | ASPHALT PROFESSIONALS | NEWBURY PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | asphalt company hit PE service with no USA
Southern California Gas Company | N | RIVERSIDE | NORCO | 2025-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ABARCA LANDSCAPE | HEMET | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | stub was hit during new construction project.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2025-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 59 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | EMPIRE EQUIPMENT SERVICE | JURUPA VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third-party using backhoe damaged the 3/4'''' steel gas service, they did not verify the service location before the use of Heavy machinery. USA ticket was expired.REPLACED SERVICE TO MAKE PERMANENT REPAIRS.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | VISEUR LARRY DEAN | NORCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | service was damaged with a shovel
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | FERREIRA COASTAL CONSTRUCTION CO | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor damaged 1/2 CTS service while potholing to install electrical. Had a valid USA but wasn''t careful when potholing.
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2025-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JONATHAN PLANCARTE | NUEVO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner doing water service repair cut through our 1/2 plastic svc thinking it was a tree root, causing broken and blowing. Chino OHS crew arrived, controlled gas and made permanent repairs by replacing the riser with a new cts riser and 1 coupling. No USA was called in for this job.
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2025-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 49 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | FERREIRA COASTAL CONSTRUCTION | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved, Contractor was digging to pothole gas service when they struck PLA service with shovel. Per contractor, there were roots surrounding area and while digging around roots they hit the service.
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NETWORK CONNECTIONS | SIMI VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1/2 IPS cut back service was damaged by 3rd party contractor while Boring. Active USA ticket. Service was not marked due to no records of it on Service History or GIS.
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2025-01-08 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3830 |  | 7 |  | NETWORK CONNECTIONS | POMONA | CA | N | Y | Yes | Yes | No | Yes | No | No | No | Third party contractor changed scope of work and damaged 2inc plastic main.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-02-04 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OPTION ONE PLUMBING | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing contractor damaged 2 inch steel main with a Sawzall while cutting tree roots. Crew installed an Adams clamp over the leak.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DUNN POOL CO | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating without a USA damaged a 1/2 CTS service.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ANDRES HERNANDEZ | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for irrigation damaged a 1/2 CTS service with a shovel. Crew made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | TORRES ELECTRIC | COACHELLA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third-party contractor hit a 1/2 plastic service with a shovel while installing electrical conduit. The contractor failed to notify 811 before digging.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MONTEREY COUNTRY CLUB ASSOCIATION | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HIT LINE WITH A BACKHOE DIGGING TO REPAIR LEAK ON IRRIGATION SYSTEM NEAR COMMUNITY POOL JEFF OWENS-442-227-6862. USA WAS NOT CALLED.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-03-26 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 4 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SALEM ENGINEERING GROUP INC | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A third party contractor hit a 2 inch plastic main with a probe while taking soil sample for a compaction test. The contractor failed to notify USA Dig Alert.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-06-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | INLAND EMPIRE ELECTRIC | LOMA LINDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | An electrical contractor installing conduit damaged a 2 PE main with a mini excavator. No USA called
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2506 |  |  | NA | SILVERADO WINDOWS | BOISE | ID | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Excavator hit service late afternoon 6/30/25 and didn''t report it until 07/01/25. Service damaged by backhoe while excavating for footing for pillar.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MR ROOTER PLUMBING | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The 3rd party contractor installing a water line proceeded to cut out tree roots and sever a 1/2 CTS service in the process. Crew made permanent repairs
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BRIAN LISTOE | PALM DESERT | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner installing poles for fencing damaged a 1/2 IPS service with a shovel. Crew fixed damage.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | SOUTHWEST PLUMBING | THOUSAND PALMS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing contractor damaged 1 inch plastic service with a shovel, and it ignited, no injuries. Crew replaced 8'' of pipe.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Edison contractor damaged a 1/2 CTS service with a backhoe, service was mismarked due to ethe ETD having connectivity issues.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-02-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COCHRAN COMMUNICATION CONSTRUCTION INC | THOUSAND PALMS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party communication contractor digging around pull box damaged 1 inch plastic stub.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-10-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | JASPER COMPANY | COSTA MESA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third-party contractor hit a 1 plastic stub with an excavator while digging to for a brick wall foundation. The contractor failed to notify USA/Dig Alert before digging.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2025-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11740 |  | 0 |  | TBU | BEAUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 4 plastic main while probing to locate a streetlight. No USA ticket was called or provided by the contractor.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | POST TENSION REPAIRS | LAKE ELSINORE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging with hand shovel looking for utilities. No valid USA. Used 3rd party contractor to locate gas service. Previously damaged riser found at site and service potholed in another location east of damage.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-04-11 | Third party excavation damage | Main | Steel | Not Available | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3983 |  |  | NA | CALPROMAX ENGINEERING | PLACENTIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor hit 2 inch steel main with an Auger while installing street lights for the city of Palm Springs.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | LEGACY EXCAVATION INC | YUCAIPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 IPS SERVICE HIT LINE WITH BACKHOE WHILE TRENCHING FOR UTILITES. THE 3RD PARTY CONTRACTOR FAILED TO EXPOSE SERVICE BY HAND DIGGING.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ASPLUNDH CONSTRUCTION | CYPRESS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HIT LINE WITH SHOVEL BY ASPLUNDH CO. 714-330-5667 WHILE DIGGING TO CHANGE POWER POLE. CALLED BY FOREMAN OF ASPLUNDH CO./LOGAN JARED 808-346-8294. NO USA CALLED.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PLUMBERS | PALM SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party plumbing contractor damaged 1/2 CTS service with shovel. Crew made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | URSA CONSTRUCTION | COACHELLA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A third-party contractor hit a 1/2 plastic service with a shovel while installing an irrigation water line. The contractor failed to notify USA/Dig alert.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | SALAZAR DRYWALL | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY CONTRACTOR DAMAGED A 1/2 CTS SERVICE WITH A EXCAVATOR. CREW MADE PERMANENT REPAIRS. NO USA
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | MR ADRIAN FIGS | CALIMESA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third-party contractor hit an unmarked 1 plastic service with a backhoe while trenching for the installation of a new water line.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | M AND J GRADING SERVICE | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third-party contractor hit an 1/2 CTS pipe with a trencher while doing some landscaping project. The contractor failed to notify USA/Dig Alert before digging.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-05-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GILBERTO GARCIA | DESERT HOT SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit service with shovel digging to remove tree. No USA ticket. No Road closures, no media, no evacuations. Crew repaired with IPS 1 Coupling. ETR restored service. No injuries, no outages.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-03-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BORDEN EXCAVATING INC | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | A third-party contractor replacing water lines damaged a marked 2 inch plastic main with an excavator. Crew made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | J&J LANDSCAPE CONCEPTS | INDIO HILLS | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | The third-party contractor hit a 1/2 CTS service with shovel while digging under concrete wall for irrigation. the USA Ticket provided by the contractor was expired and not renewed for remarking. Also, the ticket was for building a brick wall, not for working on irrigation or landscaping.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BERG ELECTRIC | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third-party contractor hit a 1 inch plastic with a backup while installing an electrical conduit for Edison. The third-party contractor did not expose the pipe by hand digging only.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | DANTOR MARTINEZ CONSTRUCTION | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Labor from Dantor construction was in progress of excavating and landscaping. Was not aware of service line and punctured with shovel. No valid USA. Crew excavating for landscaping and damaged 1 PE service. Claiming that shovel damaged it, but small backhoe on site.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BELLA BLUE WATER | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1/2 CTS service with a shovel while excavating to install a drain. The contractor failed to notify USA/Dig Alert.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JH THOMPSON & SONS | BERMUDA DUNES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor hit a 1/2 IPS stub with an excavator while working on electric.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-05-28 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 10 |  | J AND M LEYVA GENERAL ENGINEERING | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved. Hit 2 Main while directional drilling. Marks Accurate
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | SUN BEES GROUPS DBA TRUE POWER SOLAR | POMONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. Had an Expired USA Ticket, Marks were hardly visible but located accurately. True power solar hand digging with shovel trench to install irrigation/electrical and hit plastic service. trench being dug for new ADU/back house.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | DTS ENGINEERING CONTRACTORS | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 1 pe svc with EFV by 3rd party contractor with backhoe. Failed to hand expose. They did pothole the service but not in their trench line.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | QUADE | CHINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Ticket was completed as clear- no conflict. dig alert: B250350944/ B250350939.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | JV GENERAL CONTRACTOR | CATHEDRAL CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY CONTRACTOR HIT OUR 1 PLASTIC SERVICE LINE BY EXCAVATOR, TRENCHING FOR FRENCH DRAIN. THERE WAS A VALID USA AND MARKS WERE CORRECT, BUT NOT PROPERLY MAINTANED BY THE CONTRACTOR. SAN BERN OHS CREW ARRIVED, CONTROLLED GAS AND MADE PERMANENT REPAIRS BY CUTTING OUT THE DAMAGED SECITON AND INSTALLED 2'' OF 1 PLASTIC PE & 2 1 COUPLINGS.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | SEMA CONSTRUCTION | ENGLEWOOD | CO | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Crew arrived to a hit plastic service line to a riser that was not being used. The 3rd party contractor that hit the service bent the pipe back and tied it to control the flow. We arrived and the crew formally controlled the gas. Contractor was digging with a USA ticket that had not been refreshed in about 5 months, and they hit the plastic 1/2 gas line with a backhoe. The crew abandoned the unused gas line at the SMC. The service was installed at the end of main and led the main about 20'' and then crossed towards the property.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BIG BEAR POOLS & SPAS | PATTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved. Did not pothole line. it was accurately marked.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ARB | LAKE FOREST | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. Expired USA Ticket
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 51 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2047 |  | 1 |  | ARB | LAKE FOREST | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved. Contractor hit 1/2 CTS service while digging with excavator. crew did not pothole. Marks were accurate.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-09-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | SEMA CONSTRUCTION | CARLSBAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SEMA CONST DIG IN 1/2 IPS PLA SRV W/ SHOVEL WHILE EXCAVATING FOR WATER SERVICE. REPLACED APROX 2FT OF 0.5 IPS PE SERVICE WITH 2 IPS COUPLINGS.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | EMWD EASTERN MUNICIPAL WATER DISTRICT | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 CTS damaged by 3rd party contractor while hand exposing.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | PETER GONZALEZ | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging under fence to put concrete and hit service with shovel. No USA Ticket.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | RUBEN RUVALCABA | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner using a mini excavator doing work on his own gas line hit our 1/2 cts service causing broken and blowing. No USA was called in for this job. San Bernardino OHS crew arrived, controlled gas by pinching and made final repairs by cutting out the damaged section and installed 2'' of cts and two couplings.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LC PAVING | ESCONDIDO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Approved. Struck Outside delineated Area
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-02-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SEMA CONSTRUCTIONS | CENTENNIAL |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Approved. Employee had access issues and was documented on ticket that he had to backtrace line, service was to a church.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | JOHN GRIFFIN CONSTRUCTION | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor crew was hand digging to replace communications box for spectrum when they damaged our gas service with shovel. Severed in half, gas line was folded back and zip-tied when I arrived (tied back by contractor)
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TRUE POWER SOLAR | POMONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No usa, damaged cts service
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2025-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2599 |  | 1 |  | SEMA CONSTRUCTION | CARLSBAD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Approved. This Facility was not Mapped on GIS, EE Submitted for MUR and Crew will be submitting for Service Replacement to planning
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2025-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOT PURPLE ENERGY | PALM SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1/2 CTS service with a shovel while working on a solar installation. The contractor failed to notify 811/USA Dig Alert. Distribution crew made permanent repairs altering 2'' of 1/2 CTS pipe with (2) socket fusion couplings.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | WOO ELECTRIC | DESERT HOT SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ALEX WOO WAS POTHOLING TO FIND ELECTRICAL CONDUET FOR HOMEOWNER WHEN HE HIT GAS SERVICE LNE ALOT OF TREE ROOTS DUE TO PALM TREE. ALEX WOO HAD NO USA TICKET
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | INTEGRITY GOLF | FALLBROOK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HIT LINE WITH MINI EXCAVTOR WHILE DIGGING TO FIX WATER LINE. HIT BY INTEGRETY GOLF. No valid USA at time of damage, called in as emergency 9/3. Description in ticket does not match location of damage.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MOHR ELECTRIC | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party electrical contractor damaged a 1/2 CTS gas service line while digging to install conduits. SCG crew was able to make repairs.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2025-03-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | MIGUEL VALIDIVA | COACHELLA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper company digging to install drainage lines damaged 1 inch IPS service with a backhoe. Crew was able to make permanent repairs.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2025-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor hit an unmarked 1/2 IPS Stub with a backhoe while trenching to install a new electrical conduit for EDISON. The Stub was not recorder on GIS or Service History.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2025-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TEAMS SON CONSTRUCTION | RANCHO MIRAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd third-party contractor damaged a 1/2 inch CTS service with a shovel. Crew made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2025-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | RANCHO VERDE LANDSCAPING | REDLANDS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A Third-party contractor hit a 2 plastic main with a backhoe while installing an irrigation pipe. The contractor failed to notify USA/ Dig Alert.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LINCOLN CONSTRUCTION CORPORATION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 PE service damaged by 3rd party contractor with backhoe. USA ticket was valid and service was marked correctly, marks visible. Contractor failed to hand expose.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-11-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | POWER PLUS | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | An unknown contractor struck a ï¿½ IPS stub service with an auger. When SCG arrived on site, no personnel were present to provide information, and the developer was unable to identify who had been working in the area. SCG crew completed permanent repairs to the damaged service.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-11-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | CASS ARRIETA CONSTRUCTION | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | New Business development. Excavator hit line on a stub service. No USA on NB orders with open trenching.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 53 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ALX BUILD AND DESIGN INC | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved. Lines were accurate and they did not pothole gas line, hit with backhoe
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PACIFIC WEST UNDERGROUND | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Marked inaccurately due to Tracer wire issue. Locator did not have access to the meter. He tried back tracing the service. He painted on the ground POTHOLE to VERIFY. Third-party contractor potholed the service location, a week before, did not find the gas and continued to trench, they did not stop the work and they did not notify 811 before resuming the excavation.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | CANDIDO LORENZO | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1PE service damaged by 3rd party contractor while trenching to install drain lines. No USA Ticket
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-03-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | EJ MEYER COMPANY | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | A third-party contractor damaged a 1/2 inch plastic service that was incorrectly mapped on the GIS. Despite a mark on the center median, the USA ticket has been active as an update only since August 2, 2024. The SCG crew has since made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-08-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 20 |  | WEKA | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor digging to relocate water main struck 2 PA Main. Marks and whiskers were not maintained due to dirt road. They did not pothole.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | DAVID DIAZ | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged CTS service no USA called
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  |  | NA | EJ MEYER | YUCAIPA | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3/4 steel service damaged by 3rd party contractor with a backhoe. USA ticket was expired. Cutback service was marked correctly. They had previously crossed that service.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 2 |  | PACIFIC WEST UNDERGROUND | YUCAIPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor punctured 1 pl svc with metal bar probe while probing for the service. Active USA ticket. Service was marked correctly. Marks visible.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | WEKA | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor admitted forgetting about buried service and ripped through it with a backhoe. They had a valid USA, but did not keep clearance. Contractor folded the service back and tapped it to stop the blowing. San Bern OHS crew arrived, pinched service and made permanent repairs using 6'' of 1 plastic and two 1 couplings.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | UNDERGROUND SPECIALIST | MORENO VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was potholing for gas service using hand tools when struck service due to earth being very hard. Marks were visible and accurate. SCG made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 53 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CITY OF RIVERSIDE | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HERMAN WEISSKER | JURUPA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage, contractor hit 1/2 IPS service with Mini excavator, No usa was called in. SCG crew made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party failed to expose marks before digging. Per crew on site marks were within the 24 of mark/flags. Also, no pothole to verify was used by contractor to expose gas facility. SCG crew made permanent repairs to 1/2 service.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-06-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JEREMY STARKE | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant Jeremy Starke struck SCG service line with shovel while hand digging to install meter guard. No USA was called in for this job. San Bern OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installed 1'' of IPS plastic and two IPS couplings.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | OASIS TURF AND HARDSCAPE | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 CTS plastic service by 3rd party contractor while trenching to install drain line. No USA ticket
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | MURRAY COMPANY | COMPTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | A third-party contractor damaged a 3/4 steel service line. The contractor failed to stop the job to verify markings and did not call in for a remark. As a result, the contractor excavated ahead and damaged the steel service. The SCG crew had to install two 4 top halves to control the damage. Crew rewelded the 3/4 steel service line,
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | POWER OF TWO | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Damage to 1/2 CTS service, no USA was called. SCG crew made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RIVERSIDE WATER | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damage- City of Riverside water damaged 1 inch plastic service in public property 3rd party company did not pothole service. SCG crew made permanent repairs by altering 6'' Of 1/2 CTS.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-04-21 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MURRAY COMPANY | RANCHO DOMINGUEZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Damage- old abandoned tee ripped off 4 steel main with excavator in prep for paving. main has been visually seen throughout project but paving was still above 4 steel main and excavator was digging directly on top of main. SCG crews made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-10-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3737 |  | 6 |  | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 2 PE main damaged by 3rd party contractor with backhoe. Mains and services were previously marked. Contractor failed to maintain Marks and/or call for remarks.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ARMANDO CHAVEZ | RIVERSIDE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor Armando Chavez was grading hillside for new residential build before USA being Valid. He struck 1/2 ips svc. Multiple feet of hill side have been removed and exposed cutback approx 20'' w/w pl where dmg occurred. SCG made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 53 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CC RENTAL PROPERTIES | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. Contractor hit line while installing ADU.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CESAR CARRILLO CONSTRUCTION SERVICES | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | UTILITY TRENCH FOR NEW ADU WAS BEING DUG BY CUSTOMER WHEN HE HIT 1/2 CTS SERVICE WITH A SHOVEL. The customer was trying to expose service line in hard earth. SCG crew made permanent repairs, altered service.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | SAFEWAY ELECTRIC | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Damaged STL service, Contractor did not have a valid USA, there was previous marks on curb from previous USA tickets at this location. SCG Crew made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-12-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3270 |  | 1 |  | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 2 pe main damaged by 3rd party contractor with a backhoe. Marks were off due to signal interference. Contractor failed to pothole/verify main location prior to continuing work. Coached and counseled EE.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RICARDO BRITO | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hand digging to install a fence post without a Dig Alert ticket. Residence is unoccupied.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 59 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractors boring to install telecommunications conduit hit our 1/2 plastic service causing broken and blowing. Contractors had current USA, but did not maintain clearance or pot holed to locate service before boring. Chino OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installed 2'' of cts and two couplings.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2408 |  | 10 |  | SOUTHWEST LANDSCAPE & MAINTENANCE | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LANDSCAPE COMPANY WAS USING SAW TO CUT THROUGH TREE ROOTS TO MAKE REPAIR ON IRRIGATION LINE AND CUT 1'''' PLA SERVICE, No USA and SCG made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-01-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DEOK KIM | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant at home damaged a service while digging to plant a tree in the yard. No USA at the time of incident.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3270 |  | 1 |  | OPTIMUM | BLOOMINGTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Direction Drilling Co hit 2" PE service with bore
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | OPTIMUM | BLOOMINGTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor doing directional boring in an empty lot for optical fiber hit an underground unknown 1 IPS stub of ours causing broken and blowing. They had an active USA, but our service was not marked because it was unknown with no Svc ID. San Bern OHS crew arrived, controlled gas and made permanent repairs by cutting back the service and capping it.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RIVERSIDE PUBLIC UTILITIES | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party damage to 1/2 PLA service at 6311 Vonnie Ct. This service was not mapped in GIS and it had no SID record. EE was coached to document on USA tickets when access to a home is not possible. SID has been submitted to be created. SCG crew altered service and permanent repairs were completed.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOMEOWNER | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | H/O hit 0.50 IPS svc w/ shovel while trenching. No USA
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-05-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | DONALD BRIDGEWATER | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Performing sewer work and with shovel damaged service line.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | CDL LANDSCAPE | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party dmg, Contractor did not maintain clearance after verifying marks. SCG Crew made permanent repairs. Dmg prevention was onsite and took pictures of dmg.
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | STEWART ELECTRIC | TEMECULA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA Ticket
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2025-02-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GEOVANNI LEON | SAN JACINTO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner, Gionanni DeLeon, was removing trees from front yard using a back-hoe without a Dig Alert ticket.
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2025-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RODOLFO PADILLA | SAN JACINTO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. this is an after the fact EIR. was originally a Leak and when crew got out there and uncovered it, it was an unreported damage.
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2025-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | VICENTE SANTOYO | SAN JACINTO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third-party damage to 1/2 inch plastic service. Removal of tree stump cause of damage. No USA called in. Fire department and police were on site. Crew controlled damage and made repairs.
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2025-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | JOSE AVILA | SAN JACINTO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA. Damaged 1/2 CTS service stub. Needed to pinch 2 PLA main to be able to make repairs.
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2025-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MARIA ALVAREZ | SAN JACINTO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor installing pool line for home owner damaged ï¿½?? plastic service with shovel while digging without a USA ticket. Customer tried saying they ?found a leak while digging? but the ï¿½?? plastic service was gouged with a shovel and found to be taped up by the responding crew. Damage resulted in 1 outage to 566 Wamblee.
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2025-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RUBEN COLIN | SAN JACINTO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA called in
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2025-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RADFALL COMPANY | SANTA CLARITA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved. Crew found abandoned 1 inch PLA stub that was stubbed out in middle of parking lot. Instructed crew to abandoned stub at SMC so no future damages occur. Service was Accurately located , the contractor did not pot hole prior to digging.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2025-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | FERREIRA COASTAL CONSTRUCTION CO | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party electrical contractor damaged a 1/2 plastic service while working on electrical at the location. USA was valid, marks were visible, and marks were within the 24 tolerance zone.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2025-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EPX GROUP | TEMECULA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, 3rd party contractor damaged a plastic service while digging for a backup generator.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2025-09-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GOTHIC LANDSCAPE | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 plastic service with a backhoe while digging for a drain. USA was called in but SCG locator sent it back due no delineations.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EDIK M ESMAILIAN | TEMECULA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | DAMAGED 1 INCH SERVICE. USA CALLED AND SERVICE MARKED CORRECTLY WITH FLAGS IN FRONT YARD AREA. EXCAVATOR FOUND AT TOP OF EXCAVATION AND THOUGHT IT WAS GOING STRAIGHT BUT IT MOVED OVER A FEW INCHES AND WAS HIT WITH SHOVEL.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2025-04-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | JOSE FARIAS GARDENING | TEMECULA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party landscaping company damaged a 1 inch plastic service while digging for drainage install in homeowner''s property. No USA at the time of incident.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2025-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3270 |  | 1 |  | 24 HOUR EXPRESS SERVICES | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor DAMAGED 2PLA service with mini- excavator. USA marks not properly maintained.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2025-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | ROMERO DAVID PEREZ | MISSION VIEJO | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2 PE service with shovel, while trenching for gas house line for a pool. Company crew reported on scene and made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2025-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FERNANDO SOLIS | TEMECULA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner damaged 1/2cts service with pick. there are gas marks at the address but, home owner was not able to produce a dig alert ticket, so job shut down until a valid ticket has been created.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | FERNANDO SOLIS | TEMECULA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner hit 1/2 inch service with shovel, expired USA, clearly marked out. homeowner has struck this same service twice now.
Southern California Gas Company | N | RIVERSIDE | THOUSAND PALMS | 2025-03-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JAIME ESPINOZA CONSTRUCTION | THOUSAND PALMS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1/2 inch CTS service with a shovel while trenching to install a new sewer line. The contractor failed to notify USA Dig Alert.
Southern California Gas Company | N | RIVERSIDE | THOUSAND PALMS | 2025-03-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GREGORIO ROMO | THOUSAND PALMS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to Company Property, Excavation Damage, a homeowner was digging to plant a palm tree and damaged a 2 inch plastic main. Riverside County Fire Department evacuated 5 adults form one home and California Highway Patrol closed La Canada Way between Robert Rd and Christy Way. There was no media on scene, and there were no injuries or fatalities. Crew responded and repaired main leaving 1 outage. Gas controlled at 3:15 PM- Evacuations and road closures lifted at 3:20 PM. No Dig Ticket.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2025-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | HUMBERTO PEREZ | NORCO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA Called in. Hit with Backhoe while excavating. Replaced 2 ft of 1/2 IPS pe pipe along with (2) 1/2 IPS pe couplings to make permanent repairs. Damage Prevention Notified.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2025-05-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | FAIRWAY LANDSCAPE AND IRRIGATION | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, contractor was digging with mini excavator to install irrigation. Contractor crew left before crew arrived.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2025-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3270 |  | 1 |  | CMD ELECTRIC | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party electrical contractor damaged a 2" plastic service with a digging bar while excavating for an electrical conduit. USA ticket was valid, marks were visible, and marks were within the 24" tolerance zone.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2025-01-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | WAGNOR VASQUEZ | LAKE ELSINORE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 pipe on pigtail of riser caused by powered spade. No USA Ticket
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2025-09-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | FAIRWAY LANDSCAPE & IRRIGATION | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a plastic service while digging for irrigation. Ticket had a USA ticket that was not marked by any utility due to no delineation. Contractor worked anyway.
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2025-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARIO BETANCOURT | BLOOMINGTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service with hand tools, No USA
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2025-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1678 |  | 3 |  | BREMCO CONSTRUCTION INC | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service while demoing home
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2025-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BOUDREAU PIPELINE | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service while installing storm drain
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2025-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | APC damaged steel service while digging trench
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BOUDREAU PIPELINE | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service while installing storm drain
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2025-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 32 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BOUDREAU PIPELINE | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party digging to extend services to new construction.
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2025-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NEEMA GENERAL CONTRACTING | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 plastic service while digging trench line
Southern California Gas Company | N | SAN BERNARDINO | BLUE JAY | 2025-04-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JOSEPH SHUEY | BLUE JAY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner grading driveway and did not call for USA for this work.
Southern California Gas Company | N | SAN BERNARDINO | BLUE JAY | 2025-09-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MOISES NUNFIO | BLUE JAY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating for a wall hit the PE service. No USA was called for this work
Southern California Gas Company | N | SAN BERNARDINO | CEDAR GLEN | 2025-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | JAVIER HERRERA | BIG BEAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating for waterline hit the PE service. No USA was called for this work
Southern California Gas Company | N | SAN BERNARDINO | CEDAR GLEN | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | 24/7 CONSTRUCTION WORKS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this work. Service hit by hand tools (PE)
Southern California Gas Company | N | SAN BERNARDINO | CEDARPINES PARK | 2025-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MICK HILL ENTERPRISES | CRESTLINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while excavating for Septic / sewer lines the gas service was struck. No USA was called for this work
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2025-01-08 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 3 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 4 |  | F E ZIMMER INC | TEMECULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 3 Steel main while grading past 12 depth failing to confirm main location and marks. Contractor did not reach out to USA for any re-marks prior to digging
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2025-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | ELITE EARTHWORKS | MURRIETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call in for USA and hit service.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2025-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | KIRTON LANDSCAPE | CHINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged line with markings on ground and did not maintain proper clearance. Landscaping company was working off other contractor USA ticket. Damage prevention onsite to access damage details
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2025-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | L&S CONSTRUCTION | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor failed to maintain clearance from 2 PLA service while trenching causing broken blowing then bending back service prior to crew arrival to stop blowing gas. Crew arrived along with supervision to access damage and make repairs.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2025-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | GILES ENGINEERING | LAKE ELSINORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ALL USA marks were good, contractor hit gas line with shovel while trying to expose it.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2025-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | MOTIVE ENERGY TELECOMMUNICATIONS GROUP | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor digging for utilities with mini ex damaged unknown abandoned stub not reflected on GIS or Epoch. Stub that was originally abandoned had abandonment cap damaged and was re- abandoned at SMC with new cap installed.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2025-12-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | LA STRADA PIPELINE | LAKE FOREST | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damage new service stub due to not properly maintaining clearance and not notifying USA prior to excavating.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2025-06-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DL LONG LANDSCAPING | CHINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged gas service by landscaping company installing drainage system. No USA notified prior to work.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2025-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | AAA PAVING | RIALTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged service line while grading street. Service was marked and contractor failed to verify location damaging service.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2025-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | VICTOR LOPEZ | CHINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was trenching and damage service with shovel. No USA
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2025-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | YIN PING LIU | DIAMOND BAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged service line while excavating to upgrade electrical panel for home and nicked our service properly marked within delineation and valid USA for this location.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2025-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RENOVATION & CONSTRUCTION SERVICES | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Work being done to install a fence on property line of customer home damaged service line while digging fence post.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2025-05-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARCO GOBIN | CHINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged plastic service with shovel while trenching to install water line. No USA Called in for this location.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2025-05-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | BONANZA PLUMBING | LOMA LINDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Bonanaza Plumbing damage while excavting for sewer and wateral laterals for new housing track. No USA
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2025-05-21 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 88 |  | TE ROBERTS | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damages a 2 gas main while trenching to install a storm drain for the city of Chino Hills 3rd party failed to confirm location of damaged gas main and ensure proper material was identified due to them finding a 1 STL line at location potholed.
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2025-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ARI JET COMMUNICATIONS | POMONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor started work without any marks from any utilities and damaged 1/2 plastic service
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2025-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | SCHUEBEL FAMILY PLUMBING | FONTANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service by homeowner due to no USA. Damage prevention was onsite to discuss issue with customer. Service repaired by crew.
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2025-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | FANTASTIC VINYL FENCE INC | BALDWIN PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not have a USA, they hit the service with a shovel.
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2025-05-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TRENCHERS WEST | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 2 PE newly installed main while trenching failed to maintain proper distance and no USA
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2025-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HANDY HAND | BLOOMINGTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for sewer hit plastic branch service with no USA
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2025-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GARDNER | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gardner hit service while digging for sprinklers
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 32 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | L & G CABLE CONSTRUCTION COMPANY INC | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While boring, contractor hit a 3/4 steel service that was not on GIS.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2025-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | VICTOR ARIAS | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with no USA severed 1/2 plastic service
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PALM MARKET COM | BLOOMINGTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party crew was digging out palm tree and cut through plastic service with shovel.
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2025-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MANUEL MARTINEZ | CRESTLINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | H/O installing irrigation for his yard. Did not call USA for this work.
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2025-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BRANDON ALVARADO | CEDARPINES PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 plastic service hit during excavation of post hole. No USA called for this work
Southern California Gas Company | N | SAN BERNARDINO | EASTVALE | 2025-06-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PARCO STRUCTURES | UPLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging for sewer with backhoe hit our 4 main causing broken and blowing. They did not call USA for this job. Chino OHS crew and crew on extended day showed up to make repairs. Crews dug control holes approximately 20 ft on each side of damage. crews pinched main then made permanent repairs by cutting out the damaged section of main and installed 2'' of 4 plastic and two 4 electrfusion couplings.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2025-11-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | WARD CORPORATION | SANTA PAULA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor stuck 2 plastic stub while digging to install conduit
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2025-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MCKINNEY | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working for city of Fontana hit plastic service in steel casing
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2025-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | THREE SISTERS | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for owner augered through 1 plastic service while working with no USA
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2025-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 32 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GUTIERREZ CONCRETE & MASONRY | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to service while extending driveway. NO USA Dig-in filled in
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 32 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HSQ PLUMBING | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service was damaged to a new construction while digging to install landscaping.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2025-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ADU UTILITIES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service with a shovel. No USA
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2025-01-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PACIFIC WEST UNDERGROUND INC | YUCAIPA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2025-10-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 32 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | HIGHLAND HOSPITALITY | FONTANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to install and irrigation system when they hit a 1 service line. NO USA
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NA | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner digging trench with excavator for brick wall installation hit our 1/2 cts service. No USA at time of damage. person doing work folded back the broken blowing service and duck tapped it. Chino OHS crew arrived, pinched service and made permanent repairs by cutting out the damaged section and installing 2'' of cts and two cts couplings.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2025-04-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TOROS CLEAN UP | BALDWIN PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged occurred after the hours 4/29 contractor hit plastic riser
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2025-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | TERESA FRAIRE | FONTANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer hit service while trenching for fence
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2025-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GEJMAN GARCIA | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was attempted to remove a tree, he dug down to the tree roots and when he was attempting to cut what he thought was tree roots with a electric sawzall he cut through the 3/4 casing and cut into our 1/2 plastic cts service.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2025-04-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8031 |  | 52 |  | DOWNING CONSTRUCTION | REDLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 2 inch plastic main with large backhoe while digging for storm drain
Southern California Gas Company | N | SAN BERNARDINO | GRAND TERRACE | 2025-08-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 54 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RIVERSIDE HIGHLAND WATER | GRAND TERRACE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved
Southern California Gas Company | N | SAN BERNARDINO | GRAND TERRACE | 2025-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | SHIRLEY LEE | GRAND TERRACE | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Hit service due to grading. expired usa
Southern California Gas Company | N | SAN BERNARDINO | GRAND TERRACE | 2025-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | JOHNSON MERLIN CONSTRUCTION | MENTONE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit plastic service with backhoe while installing water main
Southern California Gas Company | N | SAN BERNARDINO | GREEN VALLEY LAKE | 2025-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | NAVARRO CONSTRUCTION | HACIENDA HEIGHTS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this work. service hit by shovel. (PE)
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2025-05-13 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 6 |  | RICHARD NASON | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service was hit with no USA
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2025-07-01 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 3 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3749 |  |  | NA | ROOTER HERO PLUMBING | LA HABRA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Sawzall into Steel main
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2025-01-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FINELINE ELECTRIC | JURUPA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 2'''' plastic stub.
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2025-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARIA RIVERA | HIGHLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating for new sewer line service (PE) was struck. No USA was called for this work.
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2025-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | CHRISTOPHER DURO | HIGHLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner and cousin doing grading for installation of retention wall struck our 1/2 ips service causing broken and blowing. No USA was called in for this job. San Bern OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installed 1'' of ips service, one 1/2 ips elbow, and one 1/2 ips coupling. Restores were completed.
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2025-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | LIVE OAK POWER | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit plastic service while installing power conduit.
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LEOTA CONTREE | BANNING | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA 1 pla service hit
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2025-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | BCA DESIGN & CONSTRUCTION | REDLANDS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit 1 pla svc stub with shovel cut cap off of Stub and reinstalled 1 cap
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2025-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KELCIA TOLAN | HIGHLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant of the residence was doing landscaping work, using a pick and shovel and hit our 1/2 inch plastic cts service causing broken and blowing. No USA was called in for this job. San Bern Crew showed up, controlled gas and made permanent repairs using 2'' of cts plastic and two cts couplings.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2025-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MICHAEL HORAN | CEDAR GLEN | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SHOVEL CAUSED DAMAGE BY PUTTING FOOTING IN FOR DECK BEING INSTALLED, NO USA
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2025-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | TONY S CONSTRUCTION | RUNNING SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA was called for this work. Marks were accurate and correct. Contractor did not use caution during excavating.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2025-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 11 | 11 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | JOHN RADLEIGH | LAKE ARROWHEAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner struck service no USA
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2025-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | OPTIMUM | BLOOMINGTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating for Anchor hit the pe service. No USA called for this work
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2025-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RODRIGUEZ YARD AND TREES | TWIN PEAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | landscaper struck gas service when installing irrigation.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2025-06-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | COR | LAKE ARROWHEAD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. Party Contractor working on waterline hit PE service not marked. No USA was called for this work.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2025-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JOSHUA SYLER | LAKE ARROWHEAD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating for footings, the service was struck and damaged. No USA was called for this work
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2025-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NPC CONSTRUCTION | FALLBROOK | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor excavated before the valid USA ticket due time. Resulting in a 1 PE service being hit by a shovel.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | YOUNGREN CONSTRUCTION | FALLBROOK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor did not use caution around our facility. line was marked and exposed but was still struck.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2025-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ANGEL | LAKE ARROWHEAD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating without a USA for the work being done. excavating for footings
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2025-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | PINNACLE PLUMBING | RIMFOREST | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Usa was called for this work. service hit by shovel. (PE)
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2025-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | S & S DIRECTIONAL DRILLING INC | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 2 inch plastic service not marked and hit during excavations. Contractor dug on a rejected ticket and did not call for new or updated marks. area was not marked by other utilities as well.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2025-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JUAN RIOS | BLUE JAY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating for footings hit the PE service. No USA was called for this work.
Southern California Gas Company | N | SAN BERNARDINO | LOMA LINDA | 2025-06-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LAZER BACKHOE SERVICE | GRAND TERRACE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit service stub with backhoe while digging for new water and sewer.
Southern California Gas Company | N | SAN BERNARDINO | LOMA LINDA | 2025-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MJ JURADO GENERAL ENGINEERING CONTRACTOR | STANTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit 1/2'''' pla service, no usa.
Southern California Gas Company | N | SAN BERNARDINO | LOMA LINDA | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BERG ELECTRIC | AGOURA HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service was hit well potholing with mini EX
Southern California Gas Company | N | SAN BERNARDINO | LOMA LINDA | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service was hit potholing by hand. multiple service with no wire ETD tried to back locate
Southern California Gas Company | N | SAN BERNARDINO | MENTONE | 2025-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2599 |  | 1 |  | FERNANDO Z, DANIEL BURROLA | MENTONE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit steel service while moving some dirt. Crew made permeant repairs. Crew also replaced non-state of the art steel service due to it being shallow.
Southern California Gas Company | N | SAN BERNARDINO | MENTONE | 2025-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | RD PLUMBING & ROOTER | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR HIT SERVICE WITH ELECTRIC CHIPPING HAMMER CAUSING BROKEN/BLOWING
Southern California Gas Company | N | SAN BERNARDINO | MONTCLAIR | 2025-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and contractor hit service with mini-X
Southern California Gas Company | N | SAN BERNARDINO | MONTCLAIR | 2025-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MONTE VISTA WATER DISTRICT | MONTCLAIR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Unknown cause of damage. ALL USA marks are good. Contractor smelled gas.
Southern California Gas Company | N | SAN BERNARDINO | MORONGO VALLEY | 2025-04-21 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CODY BISCO | MORONGO VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Customer damaged 2 inch plastic main with Sawzall while trying to cut tree roots during the excavation process of removing the tree stump. Valid USA and marks were present and correct.
Southern California Gas Company | N | SAN BERNARDINO | MORONGO VALLEY | 2025-06-12 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | VAN DYKE | 29 PALMS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 2 steel main damaged by 3rd party contractor while excavating with backhoe. USA ticket was expired but old marks were still visible from original mark out. Contractor was excavating to install septic leach line.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-12-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ELECNOR BELCO ELECTRIC | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1 gas service while trenching and failed to verify location and maintain proper distance for identified utility by gas company locator.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AYALA CONSTRUCTION | LA PUENTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged un-identified service by 3rd party contractor with mini excavator. Per LCT no USA markings identified while onsite.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-06-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GRIFFITH COMPANY | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1 PE service line while potholing by hand with a shovel. Line properly marked by locator, but contractor still hit by accident.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | NORCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ALL USA marks were good, contractor hit gas service and did not verify before digging.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 235 | 230 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NORSTAR PLUMBING AND ENGINEERING | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor working on curb and gutter storm drain project damaged 3/4 HP service while grading dirt roadway. Contractor failed to maintain visible markings prior to performing this work. Also failed to request a high pressure standby while working near our facilities with heavy equipment.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | WILLIAM RAMOS | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor/Plumber installing drainage, damaged our 1/2 cts service using a shovel. No USA was called in for this job. Chino OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installed 1'' of cts and two cts couplings.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | MSI STRUCTURAL | SOUTH GATE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged Svc digging footing. No USA
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-04-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 59 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CP CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor working on water main installation work damage our 3 inch plastic gas main with backhoe while trenching. Contractor failed to maintain gas marks and did not call in to verify gas location prior to continuing work with poor visibility of gas marking which had been marked months prior to this work taking place.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-10-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 20 |  | MAMCO DBA ALABBASI CONSTRUCTION | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ALL USA marks were GOOD, contractor did not hand expose before digging with excavator.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | ROY CONTRERAS | WEST COVINA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service line while attempting to make repairs to water line and mistakenly cut into casing containing PE line inside. No USA was called in for this area being worked.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-10-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | AMERICANO ELECTRICAL SOLUTIONS | LANCASTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ATF damage by 3rd party contractor. C/S RFA and crew investigation determined damage causing service issue and repairs required to correct this concern. Damage prevention notified and will address this location.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-10-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  | 0 |  | UNIVERSAL PIPELINE | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party trenching contractor damaged 2 poly main due to not properly exposing and maintaining clearance of the pipe prior to digging for utility work.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-09-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PROCRETE CONCRETE | MONTCLAIR | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Damaged service due to homeowner digging around gas service to install sewer pipe. Homeowner failed to maintain proper clearance.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JESSE MOLINA | ONTARIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer doing fencing work installed a metal stake to hold up the fence and hit our 1/2 cts service causing a leak. No USA was called in for this job. Chino OHS crew arrived controlled gas by pinching service. They made permanent repairs by cutting out the damaged section and installed 2'' of cts pipe and two cts couplings.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LA STRADA PIPELINE | LAKE FOREST | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damage gas line while trenching. No history or information on unknown service stub damaged. Locate completed for work area but no way to identify this stub due to no available records.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-07-22 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ELECNOR BELCO ELECTRIC | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All USA marks were GOOD, PLASTIC MAIN DAMAGED BY 3RD PARTY VIA BORING WITHOUT GAS LINE EXPOSED. Contractor was at fault.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | T E ROBERTS INC | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged un-known stub by 3rd party contractor while excavating. Stub was not on GIS and could not be marked out by our ETD due to no record of this stub. Damage prevention was onsite for this dig in.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LA STRADA PIPELINE | LAKE FOREST | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contactor damage unknown service stub while trenching on new tract location.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | GRANITE CONSTRUCTION COMPANY | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged unknown service stub. No record on GIS or any service history information. 3rd party hit stub while trenching to install re-claimed water line for city of Ontario.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-01-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | OLTMAN | WHITTIER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All USA marks are good. Contractor failed to pot hole 4 inch plastic main.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | OAKRIDGE LANDSCAPE | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damage PE service while excavating. Repairs complete.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-07-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OAKRIDGE LANDSCAPE | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 INCH PL LINE DAMAGED BY3rd PARTY DIG IN . PERMANENT REPAIRS COMPLETE . VERIFIED NO MEDIA ON SITE.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-03-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CASS ARRIETA | EL CAJON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging with backhoe hit our 2 inch main causing broken and blowing. USA ticket was expired. 2 inch main was newly installed in a new development and was not serving a single house. Chino OHS crew arrived, controlled gas by pinching the main. Permanent repairs were made by cutting out the damaged section and installing 5'' of 2 plastic stick and two electrofusion couplings.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CASS ARRIETA | EL CAJON | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damage gas service stub while trenching to install conduits and no valid markings in the area. Also, Contractor pinched back stub prior to crew arrival. Damage prevention was onsite.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-10-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | GOTHIC LANDSCAPE | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service line by 3rd party contractor due to not having USA and hitting service line while trenching for development work.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | 2020 PLUMBING & HEATING | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber installing gas houseline used rebar to hold up houseline, stuck the rebar through our service causing broken and blowing. No USA was called in for this job. Chino OHS crew arrived, dug control hole and controlled gas made permanent repairs by capping the 1 plastic stub.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ALABBASI | PERRIS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor digging to install storm drain damaged un-marked 1/2 inch plastic service. Due to the heavy construction taking place with phases being worked on. Our ETD un-intentionally missed the service that was damaged while making out this other phase to be worked.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-08-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PACIFIC UTILITY INSTALLATION | CORONA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service stub by 3rd party contractor while trenching with no proper delineation provided.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-06-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | PACIFIC UTILITY INSTALLATION | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and CONTRACTOR DIGGING FOR COMMUNICATIONS DAMAGED PLASTIC SERVICE.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 8 |  | MAMCO DBA ALABBASI CONSTRUCTION | SAN JACINTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to install storm drain damage 3/4 stl service while marked and exposed. Contractor failed to maintain proper clearance while digging.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-01-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WARREN M MEYER & SONS CONSTRUCTION CO INC | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged main. USA valid and marked correctly
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RS CONSTRUCTION | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit our 1/2 plastic service line while digging to install drain line. No USA was called in for this job. Chino OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installing 1'' of 1/2 plastic cts and two cts couplings.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ARMANDO MEDINA | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service by property owner doing sewer work due to no dig alert called in prior to excavating.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-08-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALL AMERICAN ASPHALT | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor doing road rehabilitation damaged plastic gas service which had been previously identified while potholing with a shovel. Per contractor they knew the service location and accidentally damaged it.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GRIFFITH COMPANY | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NO USA was called in, contractor hit our gas service.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-08-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GRIFFITH COMPANY | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor working for the city of Ontario damaged a 1/2 PE service while probing not properly following steps to ensure line did not get damaged.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2025-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | BREA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and contractor hit service while grading.
Southern California Gas Company | N | SAN BERNARDINO | POMONA | 2025-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All USA marks were good. Contractor did not hand expose 3/4 service.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARCOS LOPEZ | MONTCLAIR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging to replace sewer lateral when they struck our 1/2 CTS gas service with a mini excavator. Customer bent back the plastic service and secured with wire so there was no gas blowing upon arrival. Crew squeezed service properly and replaced small section of service.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-10-01 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ARIJET | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All USA marks were GOOD, contractor did NOT hand expose 3 PA main before boring.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KIRK GRAFTEN | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in, SERVICE WAS HIT TO A EMPTY LOT. NO ADDRESS ON FILE. LINE WAS HIT WITH A BACK HOE
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-04-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | THE RESORT | RANCHO CUCAMONGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ATF un-reported damage to 1 inch plastic service from landscaping company for property being addressed. Code 1 conditions found by ETR and upon crew investigation found un-reported damaged service which was brought to property management team. Damage report submitted and responsible party information was obtained.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | OPTIMUM | BLOOMINGTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor boring for cable tv conduit install bored into a large rock that got pushed into our service causing broken and blowing. company had a valid USA and marks were good. Fire dept evacuated 2 people from 2 houses. Chino OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installing 2'' of CTS plastic and two couplings.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OPTIMA | IRVINE | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor working on building remodel damaged service prior to USA legal start date and no markings to identify service. Mini ex used and damage occurred. Damage prevention team onsite to access damage.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DOCTOR ROOTER | WEST COVINA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party contractor damaged service line while excavating to do sewer work. Contractor failed to follow USA guidelines and excavated utilizing marks on street from previous locate done in this area. Ticket for this work was not valid to dig at time of damage. ETD was onsite to confirm and damage prevention was onsite to access damage with contractor.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-04-23 | Operator excavation damage | Main | Steel | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3346 |  | 9 |  | SOCALGAS | RANCHO CUCAMONGA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LCT was open trenching for new main when big rock pushed up on 1 main.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DRILL SUB | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor working on solar installation hit gas service while trenching to install electrical conduit without a proper valid USA. Damage prevention was onsite and stopped all work until valid USA markings and updated ticket was submitted by contractor doing this work.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BLANCO CONSTRUCTION | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2 PE service while boring in fiber conduit and failed to properly identify gas service location.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | MICHAEL TOLLIVER | RANCHO CUCAMONGA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Homeowner hit 1/2 Service while installing drainage pipe. USA was expired.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ROY ESPINOZA | RANCHO CUCAMONGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged branch svc with shovel. No USA
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ELITE PLUMBING AND DRAINS | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber damaged riser plastic portion of service while digging causing a fizzer leak on service line at riser connection point. No emergency services onsite and crew responded to make repairs.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CONSTRU ONE | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged marked PLA Service while potholing to prepare for bore shot. Contractor failed to maintain proper distance while exposing line.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SELF EXCAVATION | RANCHO CUCAMONGA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damage by homeowner due to digging with expired USA ticket.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | ACC CONTRACTORS | AZUSA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged branch 3/4 service while excavating for utilities with not valid USA ticket on hand. Crew controlled gas and cut back branch service to avoid future damage due to building not occupied or requiring gas at this time per developer.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2025-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | WALTON BROS ENTERPRISES DBA CJW GEN CONTRACTING | MURRIETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and contractor hit 2 PLA main.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MCC EQUIPMENT RENTALS | YUCAIPA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew was potholing with hand tools
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | A1 GENERAL | JURUPA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic service. No USA.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | CAL HOMES GROUP | RANCHO CUCAMONGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HIT LINE WITH MINI EXCAVATOR WHILE DOING CONSTRUCTION TO BUILD A HOUSE. HIT BY COMPANY CAL HOMES GROUP EDDIE SALINAS 909-831-7838
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ILB INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Contractor hit plastic service while installing conduit for Edison, Contractor dug outside there USA.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NELIA CAAN | REDLANDS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this work. while excavating for footings the service was struck.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | arizona pipling hit line while hand exposing
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ALL CITIES ENGINEERING INC | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service hit with backhoe
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | ZAVALAS GARDENING | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor grinding tree stumb hit pla service. No USA was called in.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PRECISION LANDSCAPE SOLUTIONS | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit 1/2'''' pla service while fixing irrigation line, no usa was called.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | PRECISE UNDERGROUND WORKS | HEMET | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor trenching for electric conduits. hit stub svc. No records of stub svc on maps or print
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DSU UTILITY TRENCHING | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | GIS shows Service comes off the front of the house on Morning Dove Ln. But the Service comes from the street below on Sam Timoteo Cyn.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GODDARDS SEWER SERVICES | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service line damaged while third party sewer contractor was excavating.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | AMERICAN SEPTIC | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit our service while digging to remove tree roots for sewer pipe. No USA. San Bernardino OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and installing 1 1/2'' of 1/2 plastic.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MCC EQUIPMENT RENTALS | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | svc was hit
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ALOHA PLUMBING | CALIMESA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing contractor hit 1/2'''' pla cts. with a shovel. Plumber did not call in for USA ticket.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | ALL AMERICAN BUILDING SERVICES | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was hit with mini EX. All marks removed/ all pavement removed.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2025-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RANJO CONTRACTORS | REDLANDS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HIT LINE WHILE DIGGING WITH PICK TO INSTALL WATER LINE. PHND BY ZAUL AGUILAR 951-667-9761.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2025-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FELIPE PINEDO | COLTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck properly marked 1/2 service while excavating with a mini excavator for a block wall. USA was valid and flags and markings were in place and accurate.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | D VEGA BUILDERS INC | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic branch service while digging for sewer
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2025-07-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC UTILITY INSTALLATION | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3RD PARTY B-HOE HIT END OF 1/2 IPS STUB CAP NEW TRACK HOMES
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2025-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | GABRIEL ORTEGA | RIALTO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner trenching for drainage hit our 1/2 plastic cts service with hand tools. No USA was called in for this job. San Bern OHS crew arrived, controlled gas by pinching the service and cutting out the damaged section and replacing it with 1 ft of cts pipe and two couplings. Restores were made.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2025-02-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CJ CONSTRUCTION | SANTA FE SPRINGS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party dug with an expired ticket and not potholing services. No valid USA
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2025-02-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CJ CONTRUCTION | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing curb and gutter hit service
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2025-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | HOME OWNER | RIALTO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging with NO USA and while digging trench to upgrade electrical panel homeowner hit gas service.
Southern California Gas Company | N | SAN BERNARDINO | RUNNING SPRINGS | 2025-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CESAR TORRES | RUNNING SPRINGS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this work. service line struck while excavating.
Southern California Gas Company | N | SAN BERNARDINO | RUNNING SPRINGS | 2025-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LOUS SAENZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service was hit with shovel
Southern California Gas Company | N | SAN BERNARDINO | RUNNING SPRINGS | 2025-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | HILLSIDE PLUMBING SERVICES | HIGHLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit the PE service while excavating for a new waterline. No USA was called for this work.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LUIS LUA | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged ?? IPS Hit with Shovel, NO USA, Homeowners Brother Digging/ Open Trenching for Sewer Lateral Install, No Machines All Hand dig with No USA Marking. Informed Individuals to Call 811 before digging to prevent such events and avoid Safety Hazards.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-03-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | 3D REMODELING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor removing old pipes to install new electrical/sewer mistakenly attempted to remove gas service assuming it was old piping and tried to cut it out with grinder until odor and hissing was noticed and gas then gas company was notified. No USA was called in for this job. San Bernardino OHS crew arrived, controlled gas and made permanent repairs by cutting out the damaged section and slightly corroded riser and replaced it with 2'' of 1/2 CTS, 1 CTS riser and 2 1/2 cts couplings.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-05-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FRANK WANG | HACIENDA HEIGHTS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit pla service, no usa was called.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MIGUEL MARTINEZ | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1/2'''' pla service while repairing sewer line, no USA was called in
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LANG CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service hit with no USA
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LIVE OAK POWER | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | No wire on service. Service history was wrong will have WOC update
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | WESTERN CONSTRUCTION SPECIALISTS | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LCT fixed tracer wire. Hard to locate.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 32 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LANDSCAPE SUPPORT SERVICES | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor doing demolition hit our unmarked marked plastic service. Service was not mapped or in service history. Contractor had a valid USA. San Bernardino OHS crew arrived, controlled gas and made repairs by doing a cut back to fence line. returned on 4/29/25 to make permanent abandonment at SMC.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-04-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ELCO CONTRACTORS | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service hit with hand tools
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BORDEN EXCAVATING INC | CALIMESA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1/2'''' plastic service.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | HOME OWNER | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit 1/2'''' pla service with excavator, No USA was called.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 0 |  | GUILLERMO VEGA | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Usa was called. Customer was moving vegetation and hit our 1/2'''' pla service.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | TADEO GENERAL CONTRACTOR | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was grading day after ticket was called in, before 48 hr response. Ticket had not been marked out. Empty lot, riser was buried, not exposed
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | SAS CONSTRUCTION | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Hit 1/2'''' pla service with Backhoe, while digging for a retaining wall. No USA called.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | JUAN HERNANDEZ | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | service hit with shovel
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-10-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | HAVASU SAND BAR POOLS | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for a pool in rear of property and hit 5501 pla service.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-12-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | OMEGA TRADING GROUP | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit line with shovel
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | MIKE PRLICH & SONS INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service hit
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BRANDON GUERRERO | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor for homeowner excavating for a fence post hit service line to home.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | VALLEY PIPELINE | PALM DESERT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit end of PLA stub.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | HOMEOWNER HERNAN AGUILAR | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit 1/2'''' pla service. no USA was called in. customer called usa after the fact.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-11-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | O DUFFY CONSTRUCTION | MENIFEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | service was hit potholing
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2025-06-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 8 |  | CITY OF SAN BERNARDINO MUNICIPAL WATER DEPARTMENT | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Main was marked within 2''. Water company didn''t pothole before digging
Southern California Gas Company | N | SAN BERNARDINO | TWIN PEAKS | 2025-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SOCAL EDISON | RIMFOREST | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Location marks were in line with the curved angled street. A call should have been made for the locator to return if they were unsure. also, the fact that the contractor augured in front of the pole instead of to the side put this more at risk. too close.
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2025-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 1 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NOVI ENVIRONMENTAL | LAKE ELSINORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit unknown stub that wasn''t in GIS. Locator used ALL resources even called Anaheim to get to pull records and stub was not in system.
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2025-03-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CARLOS POOLS | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Branch plastic service damaged by 3rd party contractor while digging with mini excavator.
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2025-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 8 |  | JOHN ERICA S FENCING CO | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NOoUSA was called in and contractor hit service.
Southern California Gas Company | N | SAN BERNARDINO | WRIGHTWOOD | 2025-09-30 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 2 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ULTIMATE INTERNET ACCESS | WRIGHTWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not properly maintain or pothole our 2'''' Pla gas main. Contractor Directional Drilled right over the top of where the locator marked our 2'''' pla gas main. They were drilling Parallel to our main.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HENKELS & MCCOY | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was hand potholing our gas facilities and damaged 1/2'''' pla service due to hard soil.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2025-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | PINNACLE CONSTRUCTION | CHERRY VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Riser was hit
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2025-02-10 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | WEKA INC | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew was instilling sewer and 2in steel main
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2025-01-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | VICTOR | YUCAIPA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer failed to call 811 to get the existing gas main and services located on their property. They were trenching and hit a 1/2 IPS service line with a backhoe.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2025-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VICTOR LABASTIDA | YUCAIPA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer knew gas line was in the vicinity, but failed to call 811 even though there was a previous hit line here 2 days prior. The customer was hand digging with shovel and nicked the plastic pipe. There was no gas leakage, but the crew needed to replace the section of pipe. There were very harsh non-stop winds that night, so the crew needed to return the next day to do fusions due to all of the dirt and dust flying all around in the excavation.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2025-10-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4110 |  | 10 |  | YUCAIPA VALLEY WATER DISTRICT | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Main replacement took place in area. ETD said GIS wasn?t up to date. Spoke to ETD to use all tool available.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2025-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | CRUZ CONSTRUCTION | BEUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit svc with trencher. svc altr
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2025-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CREATIVE CONCEPT CONSTRUCTION | APPLE VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per incident commander on site, Nestor Araujo Torres, hit line for service to home from contractor looking for sewer. Technician stood by and sent RFA for Distribution. Waited for gas ops took underground samples got 0 indications of gas monitored situation ambient readings 0. Distribution crew arrived and commenced repairs. Technician remained on site to conduct service restore upon repairs completion, per gas ops request. Claims notified. No evacuations, no injuries, no fatalities, no media, no ambulance, no fire department, 1 residence outage, restored immediately after repairs concluded.
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2025-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | HELP PLUMBING | JOSHUA TREE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 damaged IPS service by 3rd party contractor while excavating with a backhoe.
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2025-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | SUKUT CONSTRUCTION | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 3/4 steel service while excavating for ongoing sewer project in the Town of Yucca Valley. Pipe was bent and kinked. Repaired by service replacement, replaced with 1 IPS service.
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2025-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SUKUT CONSTRUCTION | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid USA. Contractor pulverizing street and to prepare for sewer installation and damaged 1/2 plastic service. Service was installed shallow by Company.
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2025-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | SUKUT CONSTRUCTION | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 Service was damaged by contractor while excavating with a backhoe, installing sewer system for Hi Desert Water Agency.
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2025-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SUKUT CONSTRUCTION | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Tore 1/2 plastic service in half with pulverizor straight across from mark on curb.
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2025-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | SUKUT CONSTRUCTION | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor Sukut Const. damage a 1/2 CTS service while excavating for sewer project in Yucca Valley.
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2025-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BILL MORGAN | ARROYO GRANDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner did not notify USA.
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2025-06-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | ERIC ROBINSON | ARROYO GRANDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit 1/2 plastic service with post hole digger. EFV installed on the service. Crew responded and made permanent repairs. Two restores completed. USA was not called.
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2025-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | 1 CENTRAL COAST LANDSCAPE | ARROYO GRANDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with mini x for retaining wall with no USA. The hit our service with the excavator.
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2025-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MARK MORENO | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without a USA hit gas service.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2025-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1755 |  | 3 |  | CENTRAL PLUMBING | GROVER BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party excavation damage by a shovel. 811 was not notified. 3 residential outages. Crew made permanent repairs with an immediate service alter. Permanent repairs complete. No further leakage.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2025-10-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | CASTLEROCK DEVELOPMENT | SAN LUIS OBISPO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party excavation damage. Contractors were digging on an expired 811 ticket when they damaged a 1 plastic stub with an excavator. Crews made permanent repairs with an immediate service alter. Photos emailed to claims photos. Sketch attached.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2025-03-18 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | SOCALGAS | TEMPLETON | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | First-party damage occurred on the 2 inch plastic main due to backhoe excavation. The crew initially exposed the 2 inch plastic main by hand. However, while expanding the hole, the gas facility became covered with dirt. Without verifying the facility''s location, the spotter and operator incorrectly assumed the gas main was not where the backhoe bucket was excavating.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2025-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SNYDER AND SONS | LOS OSOS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party excavation damage broken and blowing 1/2 plastic. service. Contractors digging with expired USA ticket severed service in half with mini excavator. Marks visible and accurate on both sides of the street where the asphalt is still in place. Crew dropped back and dug control hole at SMC to control gas. Repaired damage with immediate service alter. One restaurant outage. Repairs complete. No further leakage.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2025-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | POP S PLUMBING | SANTA MARIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor trenching hit service. Contractor did not have a USA ticket. Crew responded and made repairs. Restore was completed after repairs were made. No fire department on site. 911 was notified of damage.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2025-09-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ATASCADERO MUTUAL WATER | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA markings were current and accurate. During trenching operations, the water company was using a backhoe when the main became obscured by dirt, causing them to lose visual contact. The crew responded quickly by dropping back and controlling the situation through squeezing the main. As a result, service to one house was interrupted due to the squeeze, and another was affected by the damage?totaling two impacted residences. A new section of 2 pipe was installed, and the damaged portion was successfully replaced.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2025-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1766 |  | 0 |  | REDS ON TIME PLUMBING | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party excavation damage. Contractors failed to exercise adequate caution while exposing facility by hand. Damaged 1/2 plastic service with a shovel. Current 811 ticket. Marks visible and accurate. Crew performed immediate service alter to make permanent repairs. No further leakage. Photos emailed to claims photos. Sketch attached.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2025-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1766 |  | 4 |  | RESIDENT | ATASCADERO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party excavation damage. 811 was not notified. Contractors installing fencing damaged 1/2 plastic service. 4 residential outages. Crew performed immediate service alter to make permanent repairs. Tested service, no further leakage. Sketch attached and photos emailed to claims photos.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2025-10-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | SOUZA CONSTRUCTION | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party excavation damage. 2 plastic main severed in half by a backhoe. Souza Construction had a valid 811 ticket but had not requested remarks before paving. Facility had been previously marked but Souza failed to maintain marks as they paved over the marks. No marks visible at time of damage. Crew performed immediate main alter to make permanent repairs. FD on scene. Santa Luica Road closed at Cascabel during emergency. No outages. No evacuations.
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2025-05-07 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HENKELS AND MCCOY | BLUE BELL | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | H&M damaged service with shovel. while trying to cut root with shovel they cut our service. Our line was under the root. (Damaging Party tab updated)
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2025-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | NATALIE RABINER | CAMBRIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The gas service line was struck by a post hole digger hand tool. The occupant was doing landscaping work in the front left yard when the gas service that served the main house and the branch service was struck. The Occupant called the fire department, and the fire department called the Gas Company. The ETR secured the area, continuously monitored above ground, underground, and inside the home for gas migration. The Fire department had evacuated the occupant before the ETR''s arrival. The fire department remained on site and departed after the gas was controlled. There were no injuries, no road closures, no media, no PD. After the Gas Ops crew made permanent repairs, the ETR cleared the house and lifted the evacuation order. The service was restored later that night. The branch service meter was left off and secured due to the customer not home.
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2025-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ROCKY BUTTE MASONRY | CAMBRIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was putting in a new fence without calling in a USA. While digging with posthole digger contractor hit our gas line.
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2025-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CORBET CONSTRUCTION | CAMBRIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not notify 811 and damaged 1/2 plastic service. Based on the contractor''s attitude and actions it''s apparent he is negligent, uneducated and dangerous.
Southern California Gas Company | N | SAN LUIS OBISPO | CAYUCOS | 2025-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HAYDEN CAMERON | LOS OSOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Handy man hit 1/2 plastic service while digging for drain install.
Southern California Gas Company | N | SAN LUIS OBISPO | CAYUCOS | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | KNOWLES N BRENT CONSTRUCTION | CAYUCOS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor was digging on expired ticket and hit gas line with shovel.
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JEFFREY MOORE | LOS OSOS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.
Southern California Gas Company | N | SAN LUIS OBISPO | MORRO BAY | 2025-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | TYSON ARMSTRONG | CAYUCOS | CA | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3rd party contractor was grading to redo the driveway. Contractor failed to pothole the marked gas service and accidently exposed an abandoned steel service. Contractor assumed that the abandoned line was the marked gas service and proceeded to remove soil, damaging the plastic service.
Southern California Gas Company | N | SAN LUIS OBISPO | MORRO BAY | 2025-05-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HARTZELL HORIZONTAL DRILLING | CRESTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Dig in damage on 1/2 service with mini-excavator. Damage was outside of delineation marks. Crew responded and made permanent repairs. Restore of service was completed.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2025-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MACIAS CONSTRUCTION | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating without a USA hit gas service.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2025-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | V LOPEZ | SANTA MARIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor excavating with valid USA hit marked 1/2 service. Contractors potholed steel service, then proceeded to excavate damaging the plastic service in the process. GIS shows steel service and will be updated with service replacement sketch.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2025-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MAXWELL HOUSE CONSTRUCTION | SANTA MARIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd Party contractor was excavating prior to the legal start date and hit marked 1/2 gas service. Contractor was attempting to expose the gas service when it was hit.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2025-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BRIAN BALL | NIPOMO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating without a USA hit gas service.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2025-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JOHNNY RODRIGUEZ | NIPOMO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Homeowner was doing landscaping and digging with a shovel and damaged a 1/2 PLA service. Crew was able to control the gas and make permanent repairs.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JULIO ALBERTO SALVIDAR | NIPOMO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavation damage by 3rd party. Cal Fire responded. Incident number CA-SLU-014412. Hit with fence hole digger. No evacuations, injuries or road closures. Crew responded and made permanent repairs. Two outages which were restored by 11:00pm.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | FIVE STAR FENCING | GROVER BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without a USA ticket hit a gas service.
Southern California Gas Company | N | SAN LUIS OBISPO | OCEANO | 2025-12-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | LSG CONSTRUCTION | MENIFEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service during boring activities.
Southern California Gas Company | N | SAN LUIS OBISPO | OCEANO | 2025-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | LSG CONSTRUCTION | SUN CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 plastic service hit by 3rd party contractor installing coms conduit with shovel.
Southern California Gas Company | N | SAN LUIS OBISPO | OCEANO | 2025-05-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 2 |  | BEACH FRONT BUILDERS | OCEANO | CA | N | Y | Yes | Yes | No | Yes | No | No | No | Made corrections to EIR. 3rd party damage. Contractor dug at back of property hitting 2 plastic main. ETD notes and USA ticket stated work was intended to be at front of property.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2025-09-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | GOTHIC LANDSCAPE | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party excavation damage. 811 was not notified. Contractors damaged 1/2 plastic service with mini-excavator while digging for irrigation/water lines. Crew performed immediate service alter to make permanent repairs. Photos emailed to claims photos. Sketch attached in comments section.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2025-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ROBERT VAZ | PASO ROBLES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party excavation damage. 811 was not notified. Customer damaged 1/2 plastic service with skid steer. Crew made permanent repairs with an immediate service alter. One outage. No further leakage. Photos emailed to claims photos. Sketch attached.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2025-05-20 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavation damage by 2nd party contractor ARB. 1/2 plastic service struck with shovel while attempting to expose it in very hard soil. 811 was notified and active ticket on file. Facility was accurately marked and marks visible. Crew performed service alter to make permanent repairs.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2025-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | H AND H PLUMBING | PASO ROBLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service line was cut with saw by 3rd party contractor while replacing line. Dig alert ticket was current. Crew responded and made permanent repairs. No evacuations or first responders present. Meter was left off and secured. Home under remodel.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2025-08-12 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | JW ENTERPRISES | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Broken and blowing 3rd party excavation damage. 811 was not notified. J.W. Enterprises damaged 2 plastic main with a truck mounter auger. Crews dropped back, dug control holes, and isolated damaged section of main. Permanent repairs were made with an immediate main alter. No outages.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2025-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | SWIFT TECTONICS | SAN ARDO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party excavation damage to UNMARKED 1 plastic stub. Valid 811 ticket. Facility was not posted on GIS but is listed in service history records as Lot 6 and has an EM. No whip at end of service location. Contractors digging for electric hit service at end of stub and took the cap off. Crew fused on new cap, installed new whip with tracer wire. Facility was unmarked due to ETD not checking service history and sweeping with EM locator. Supervisor Allen Johnson met with ETD Justin Kinney at damage location for a coach and counseling session which will be documented on an interim.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2025-03-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SUNDERLAND CHRIS ENGINEERING COMPANY | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage by third party contractor trenching for Power conduit. The contractor dug into 1 inch plastic stub that was just installed earlier that month. The contractor was the one who dug and backfilled the trench. The contractor then dug up our stub coiled it up and buried it so that they could trench past it in the future. Then the contractor still hit the stub because they thought they were clear of the stub.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | ARMANDOS ELITE CONCRETE CONSTRUCTION | PASO ROBLES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party excavation damage. 811 was not notified. Contractors were using mini excavator to dig footings for new building when they struck 1 plastic stub. Crew dropped back, dug control hole, and performed service alter to make permanent repairs. Permanent repairs complete. No further leakage. Photos emailed to claims photos.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2025-03-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | 805 REMODEL | PASO ROBLES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Broken and blowing main caused by 3rd party dig in. FD on scene. No USA called in. No outages, no injuries, no ignition, no road closures. Permanent repairs completed. Photos sent to claims.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2025-07-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | SPURR CO | PASO ROBLES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Spurr was digging trench with backhoe and had no USA for the area they were excavating. While digging trench they hit our 1 pla stub (purge point).
Southern California Gas Company | N | SAN LUIS OBISPO | PISMO BEACH | 2025-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RCH CONSTRUCTION | PASO ROBLES | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging in street with an expired USA. Contractor was digging with a mini x for sewer for a new home when he hit our 1/2 pla svc.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2025-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | TURN AROUND COMMUNICATIONS | WEST COVINA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party excavation damage. Contractors digging for telecom struck a marked 1/2 plastic service. 811 was notified but ticket had expired and was not renewed for remarks. Paint marks on service were visible but were very faded. Contractors were unaware of service being in their excavation as the marks were barely visible. Crew dropped back, squeezed service and made permanent repairs by service alteration.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2025-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 2 |  | SOUZA CONSTRUCTION | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Souza is replacing the sewer main on Mill. The are digging the trench with excavator. They have a valid USA and marks were visible. They potholed found steel service and assumed it was our service, but our actual service was a foot away and they hit it with the backhoe.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2025-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | WAYNE PERRY CONSTRUCTION | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors installing light poles hit service. Marks were not maintained. Fire Department on site, incident number is 25-044207. Crew responded and made repairs. Restore was completed.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2025-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CENTRAL COAST CONCRETE | ARROYO GRANDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ETD Showed up for a regular ticket and found our plastic service broken and folded back. The contractor stated they found it the previous day and accidently broke it and folded it back to stop the flow of gas. They then placed it under sandbags to hold down. After Investigation the contractor assumed it was something they could fix on their own.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2025-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | OUTSOURCE UTILITY | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid USA. Contractor failed to use caution when hand exposing gas service. Contractor hit gas service with sharpshooter.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2025-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | SUNDERLAND CHRIS ENGINEERING | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor had valid USA and it was marked accurately and marks were visible. Contractor was digging over our marks with a shovel when they hit the gas line causing a damage.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2025-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RCH CONSTRUCTION | PASO ROBLES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Valid USA. Unmarked 3/4 steel service hit. Crew hot squeezed service and cut back out of the work area and aerated to eliminate code 1 conditions.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PACIFIC DEVELOPMENT | SANTA MARIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging to do sewer work while digging with Hilti contractor hit gas line. Contractor had a valid USA and there were accurate marks. Contractor failed to pothole gas service.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2025-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | COASTAL CONSTRUCTION | SAN LUIS OBISPO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ATF Damage found during investigation for shallow service.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2025-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TODD MARSHALL | SAN LUIS OBISPO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 1/2 plastic service while digging whole for fence post. No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2025-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | AVG PLUMBING | PISMO BEACH | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party excavation damage. Contractor had an 811 ticket and gas facility was marked accurately and timely however the contractor dug prior to ticket''s legal start time. Contractor was cutting tree roots with a reciprocating saw next to unexposed 1/2 plastic gas service. Upon cutting tree root contractor also cut clean through gas service. Service was not exposed yet. Crew performed immediate service alter to make permanent repairs. Permanent repairs complete no further leakage.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | GOODWIN CONSTRUCTION GROUP | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damage. Contractor hit branch connection while grading driveway. Valid USA, Contractor failed to pothole.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2025-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TRICAMO CONSTRUCTION | SAN LUIS OBISPO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call in a USA. contractor was digging a hole with a post hole digger for a fence. While digging contractor hit our service line.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2025-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ESPINOZA CONSTRUCTION | ARROYO GRANDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | There was no leak found, the service was kinked. The LCT was coached for future situations, this would be No Leak Found in the Leak Investigation and a SCG Non-New business service alteration order would be created. I worked with the leakage department to unlink the alteration order and change the repairs to No Gas.
Southern California Gas Company | N | SAN LUIS OBISPO | TEMPLETON | 2025-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 6 |  | BARRY POOLE | PASO ROBLES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Mini Excavator struck a 1? main line inside the parking lot area of a large commercial property. The buildings on the property had one meter that served several units for each building. The fire department was on site and had turned off the service valves to all the meters. There were no injuries. The 3rd party contractor was using a mini trencher to dig to access a drainpipe when he struck the gas line. PD was on scene then departed, no media, no street closures. approximately 26 people were evacuated by the fire department. Gas-ops dug up a control hole and pinched the gas line. They made permanent repairs and two ETRs restored gas service to the buildings.
Southern California Gas Company | N | SAN LUIS OBISPO | TEMPLETON | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | KEN CHATHAN | TEMPLETON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Corrections Completed
Southern California Gas Company | N | SAN LUIS OBISPO | TEMPLETON | 2025-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | NATHAN GOOSSEN | TEMPLETON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Dig-in damage. Homeowner using excavator to trench for moving the service. USA ticket had expired. Service still had whiskers present. Hit within the delineation area. Crew responded and made permanent repairs. Restore was completed.
Southern California Gas Company | N | SAN LUIS OBISPO | TEMPLETON | 2025-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ARMET S LANDSCAPE | TEMPLETON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party excavation damage. 811 was not notified. 1/2 plastic service damaged installing fence posts. One outage. Crew performed service alter to make permanent repairs.
Southern California Gas Company | N | SANTA BARBARA | BUELLTON | 2025-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | JOSE PLACENCIA | BUELLTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged plastic service with shovel while digging with no USA for drainage work.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2025-12-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GOTHIC LANDSCAPE | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LANDSCAPER HAMMERING METAL STAVES FOR PATHWAY RAILS STRUCK SCG SERVICE LINE CAUSING DAMAGE TO 1 LINE. NO USA #
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2025-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DOUG MCGINNIS | CARPINTERIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was pulling out fence post as he was pulling it out he struck the line.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2025-06-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TAYLOR JANE CONSTRUCTION | NIPOMO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor damaged a 4 plastic main with a mini excavator while installing drainage. Contractor failed to maintain the USA markings that accurately marked.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2025-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 45 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | FENCEWORKS | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1 service line and did not break line so leaks on the service. put a large gouge in the pipe.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2025-02-25 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 4 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ADVANCE ELECTRIC | GOLETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor augered into a 4 inch plastic main with no USA ticket.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2025-03-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | GOTHIC LANDSCAPING | VALENCIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was digging with pick axe and did not maintain clearance from marked out line. Flags were in place and mark was on curb
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2025-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ROTO ROOTER | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY (ROTO ROOTER) STRUCK GAS SERVICE LINE WHILE DIGGING FOR SEWER LINE.NO USA
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2025-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 8 |  | HOT LINE CONSTRUCTION | SANTA PAULA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Edison damaged 2 service while excavating to repair bad run. Edison started excavating before the etd could close out the ticket and created a 2 crack in the service with the shovel.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2025-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | TRIPLE J DRILLING | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party struck SCG service line while boring for cable company. USA LINES WERE VISIBLE WHEN STRUCK BY 3RD PARTIES BORING TOOL.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2025-06-05 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | FIRST LINE CONSTRUCTION | MORENO VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd Party contractor hit 2 main while directional drilling. Like was marked incorrectly records were wrong and Locator make sure to put pothole over their marks. because of the bad signal and bad records.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2025-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MOUNTAIN CONSTRUCTION | EL CAJON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor did not have USA and were digging over a 1/2 service. the service was damaged and repaired by scg crew.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | YANEZ ELECTRIC | LOMPOC | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party struck service line with shovel while digging in marked area cause damage to SCG line.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2025-07-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | GAMBLE CONSTRUCTION | GOLETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck 1 main/service. they did not maintain their marks and lost sight of line.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2025-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | 805 FENCING | SIMI VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3RD PARTY STRUCK GAS SERVICE LINE FOR THE 5TH TIME WITH JACKHAMMER SPADE. AREA MARKED WITH PAINT AND FLAGS. YES, THERE WAS A USA TICKET.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2025-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | TOWBES CONTRACTOR | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3RD PARTY STRUCK SCG SERVICE LINE WHILE DIGGING WITH A BACKHOE.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GAMBLE CONSTRUCTION | GOLETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not use caution when performing work.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2025-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GAMBLE CONSTRUCTION | GOLETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator removed marks left by locator.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DRD BUILDERS | NEWBURY PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Corrections Completed
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2025-07-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | KIRK CONSTRUCTION | ATASCADERO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 3rd party contractor hit gas service while excavation to install a water line. USA ticket is being renewed, however it is for original work to install utilities. Spoke to Mike Devan about calling new USA tickets for different work performed.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SUMMERLAND SPIRITUALIST ASSOCIATION | SANTA MARIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3RD PARTY STRUCK SCG SERVICE LINE WITH BACKHOE WHILE TRENCHING FOR EDISON. LINES WERE CLEARLY MARKED.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | CLEAR SOURCE COMMUNICATIONS | GARDENA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor struck 1/2 Service line while boring
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MUNOZ PLUMBING REPAIR | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service line hit by 3rd party with shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GRANITE CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd contractor while excavating damaged 3/4 service line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LASH CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck 1/2 line with shovel while digging through hard dirt.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CLEAR SOURCE COMMUNICATIONS INC | LAWNDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while potholing.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | DRAIN MASTERS | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd PARTY STRUCK SCG SERVICE LINE WHILE DIGGING TRENCH FOR SEWER. NO USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2782 |  | 14 |  | EMPRESA REAL ALTA CALIFORNIA | PACIFIC PALISADES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY STRUCK SCG SERVICE LIINE WHILE EXCAVATING TRENCH WITH BACKHOE FOR ELECTRICAL LINE.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | TIDWELL EXCAVATING | VENTURA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor hit service stub that had no info on it.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | HARMON CONSTRUCTION | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY STRUCK SCG SERVICE LINE WITH DIGGING PICK, WHILE TRYING TO DETERMINE THE DEPTH OF GAS LINE FOR ADU. NOT CURRENT USA TICKET NUMBER
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SO CAL DIRT ENGINEERING | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party struck SCG service line while digging with shovel and pick. 3rd party trying to locate line for future ADU being built. No USA #
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HARMAN KENYON CONSTRUCTION | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party struck SCG service line with PICK SHOVEL while digging trench for gas new gas service lines. NO USA info was provided by 3rd party.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SILVANO GONSALEZ | CARPINTERIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gardener damaged 1/2 service while excavating without a USA ticket.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | SERGIO VERDUSCO | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party struck service line with shovel while digging for sewer line causing damage to SCG line. NO USA TICKET.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BOMO DESIGN | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Current USA. Failed to maintain flagged service. Requested cut back.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NICOLE NATCHELDER | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged service line with backhoe while trenching for sewer line. NO USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HATCHER LANDSCAPING & CONSTRUCTION | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor dug without USA ticket and struck 1/2 Service.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | GABRIEL ALVAREZ | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damaged SCG service line and riser while digging sewer drain with shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-04-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JF WILL COMPANY | SANTA MARIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor did not pothole service and hit line with an excavator.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-10-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RICARDO QUINTERO | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY SEVERED SCG SERVICE LINE WHILE DIGGING TRENCH WITH SHOVEL. NO USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | LOW COST PLUMBING | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3RD PARTY STRUCK SCG SERVICE LINE WITH JACK-HAMMER WHILE DIGGING FOR SEWER LINE.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-07-23 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LASH CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While exposing our facilities the contactor nicked the plastic main with a shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LASH CONSTRUCTION | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party (Lash) contractor struck 1/2inch service line with backhoe. Job was marked.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | VERNON CONSTRUCTION | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Part hit SCG service line while trenching for sewer line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | LASH CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party excavating trench for water line for the city of Santa Barbara struck SCG service line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RALPH THLICK | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Upon arrival at the scene, Gas Company Crew found that the contractors had already departed. The homeowners were not present, and neighbors informed the crew that the residence is primarily used as a vacation home. The homeowner is not currently residing at the property.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-10-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LASH CONSTRUCTION | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party struck SCG service line with backhoe will digging water line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LASH CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party Contractor Stuck unmarked service stub. Stub was not in archives GIS or Service history.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-04-13 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JAMES HAROLD RICHARDSON | SANTA BARBARA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | previously active gas lamp line service was hit by 3rd party. LCT made repairs and will discuss with Santa Barbara Supervision for further actions for old gas lamp line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-04-11 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  |  | NA | SOCALGAS | SANTA BARBARA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Employee was performing a leak investigation and while they were doing barholes the employee struck the main with pogo.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DAVID SELLENS | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor dug with no USA and struck line
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | 101 PLUMBING | SANTA BARBARA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Corrected.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DRAIN MASTERS | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on sewer line struck service line. NO USA was called out prior to digging.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BEVY HOUSE CONSTRUCTION | SANTA PAULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor Struck line with shovel
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GEORGE THE ROOTERMAN | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck 1/2 inch CTS service line with shovel. Failed to maintain clearance from marks.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-05-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | TIDWELL EXCAVATING | SATICOY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd Party Contractor struck 1/2 Service stub. line was not marked due to no info on stub.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-06-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | MGS GENERAL ENGINEERING | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR STRUCK SCG SERVICE LINE WHILE DIGGING WITH SHOVEL
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ELITE ROOTER | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY CONTRACTOR STRUCK 1/2 SERVICE LINE WITH BACKHOE. JOB WAS NOT MARKED.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | CLEARVIEW LANDSCAPING | GOLETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | DAMAGED WITH BACKHOE.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | BOB S BACKHOE & TRUCKING | GOLETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party struck SCG service line while digging with shovel. There was a USA ticket and service line were identified with yellow paint and flags.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | CHASE DUDDY | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors excavating trenches around property, struck service line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ZACK GONES | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor was digging and struck 1/2 service line. Crew responded and repaired service to home,
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | STEVE HANSON LANDSCAPING | SANTA BARBARA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locate marks were off due to poor signal from bare wire and unknown property lines.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-03-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | VICTOR CRUZ | CARPINTERIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor placing large rocks for landscaping over gas service severed line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CLEARVIEW LANDSCAPE | GOLETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dug without USA ticket and struck 1/2 Service line
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RIVALDO SIERRA | GOLETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 1/2 service. No USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-06-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NICK MASON CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage. Expired USA, marks removed.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-07-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ERIC BALDERAS | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator removed flags for the service.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RAFA VELASQUEZ | CARPINTERIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd Party contractor struck 1/2 Service line
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JOSE SANCHEZ | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY STRUCK GAS SERVICE LINE WHILE DIGGING WITH SHOVEL TO REPAIR WATER LINE LEAK. NO USA.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | JC BUILDERS | NEWBURY PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd PARTY STRUCK SCG SERVICE LINE WHILE DIGGING TRENCH FOR ELECTRICAL WIRE WITH BACKHOE
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 0 |  | KEN FAULK | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was building fence on his property and damaged the 1/d service with a shovel. Homeowner was reminded of calling 811.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3198 |  |  | NA | LOUIS HERNANDEZ | OXNARD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for drainage had no USA and damaged a service.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | KOVACS BUILDERS | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 IPS service was struck by hand tool while digging to install electrical conduit. No USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-11-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | RAFAEL GUTIERREZ | CARPINTERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party struck SCG service line with shovel while trying to remove large rock from sewer line trench. 2nd damage @ this account. NO USA #
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-12-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | ASHLEY FARRELL LANDSCAPE DESIGN | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY STRUCK SCG SERVICE LINE WITH SHOVEL WHILE DIGGING FOR LANDSCAPING. NO USA TICKET
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | SOUTHERN CALIFORNIA ELECTRICAL FIRM | TORRANCE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit marked cutback with backhoe.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | THANE CONSTRUCTION | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party digging out for driveway caused damage. No 811 called
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SANTA BARBARA WATER DEPARTMENT | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | City of Santa Barbara called in USA ticket for emergency Water main leak on sunday 5/11. Upon excavation City of Santa Barbara hit 1/2 CTS service with backhoe (In the evening of 5/11). USA marks present and visible upon arrival.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2179 |  | 1 |  | SYSTEM PAVERS | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was Saw cutting the driveway so they could place pavers. As they were saw cutting they struck the line due to the 3/4 Steel service line being 5 ''Deep.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2025-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LOU WALTHERS | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contactor was digging up pool with backhoe and struck 1/2 IPS service.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ALBERT JAQUEZ | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating without a USA hit gas service.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-09-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | BUTCH POPE ENGINEERING | NIPOMO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating with valid USA hit marked gas service with excavator. Contractor attempted to perform permanent repairs and allowed debris to enter the service damaging the EFV as well. Crew altered service and replaced EFV. Damaging party should be billed for orders attached to this EIR from the damage and orders 520004310123 and 540000692299.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-10-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JARED BIELY | SANTA MARIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without USA hit gas service.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | NICOLAS PEREZ | SANTA MARIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating with an expired USA ticket hit accurately marked 1/2 plastic service. Customer service evacuated 6 residents, crew responded and once gas was under control indications fell to acceptable levels. Evacuations lifted.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | CITY OF SANTA MARIA | SANTA MARIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | City of Santa Maria was excavating with a valid USA. They began digging outside of their delineation and struck an unmarked 1/2 gas service. Service was well outside of delineated area.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MONTE J FARM | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Farm owner plowing irrigation rows with tractor. Hit service in field. No 811 was called. Persons marked out damage with pink flags and continued to plow avoiding damage area. ETR arrived onsite and was escorted by employee to damage area. Tech was unsure if damage was HL or Service. Unable to locate meter and/or riser. Tech called On Call supervisor who determined damage was service. Tech RFA''d for Gas Ops, Standing by. Relieved by Gas Ops at 1458. Gas Ops, Repair detail states service was abandoned at SMC due to no meter and/or service at site since approx. 2015.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-02-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MELENDEZ CONSTRUCTION | SANTA MARIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor excavating with a valid USA hit marked gas service. Spoke to contractor about exercising caution when exposing underground facilities.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SANCHEZ CONCRETE | SANTA MARIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Branch service was located, but no marks were placed over signal locator had on standard service due to signal being outside of delineated area. Actual standard location was inside delineated area and is incorrect on GIS and service history. MUR and service history corrections will be submitted.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | FLORA | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per ETR onsite customer claims she was removing roots with pickaxe to plant new tree and sliced through service. ETR secured meter and took samples at foundation. Samples negative. RFA''d for Gas Ops and stood by. Monitored levels till gas ops arrived. ETR Relieved at 4:45pm. Gas controlled at 5pm. ETR left site while gas ops worked on repairs.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MG ANDALUZ CONSTRUCTION | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating without a USA hit a gas service.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | OMAR CORDOVA | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without a USA hit gas service.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | COASTAL DESIGN BUILD GROUP | AGOURA HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 3rd party contractor with valid USA hit unmarked stub while direction drilling outside of the delineated area. Spoke to tech about using every resource available to mark out the mapped stub if its close to the end of their delineations.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CITY OF SANTA MARIA | SANTA MARIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | City of Santa Maria hit marked gas service with a pogo while excavating to expose a leaking water main.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3270 |  | 1 |  | RODRIGO MARTINEZ | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating without a USA hit 1/2 plastic service.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ANGEL CORTEZ | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party excavation damage broken and blowing. 811 was not notified but marks were visible from a previous locate from an unrelated project in the parkway. Liable person who damaged the service did not even notice the old marks and had no idea what they meant or that natural gas lines are marked in yellow paint.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2025-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MICHAEL USEVISH | SANTA MARIA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party contactor excavating with expired USA ticket hit gas service.
Southern California Gas Company | N | SANTA BARBARA | SANTA YNEZ | 2025-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WILMER MANZIA | SANTA YNEZ | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without a USA hit gas service with posthole digger.
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2025-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JON STEPHEN | BUELLTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor excavating with a valid usa hit a mismarked 1/2 plastic service.
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2025-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CODY DELUNAS | SOLVANG | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, Third Party contractor digging trench for drainage around the house and hit the branch service feeding the neighbors house. Contractor was using a mini excavator. Crew made repairs and ETR was onsite to restore the two impacted houses.
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ABEL FUENTES | LOMPOC | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating without a USA hit gas service.
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2025-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | JOSE MARTINEZ | SOLVANG | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was removing tree stump and damaged service in the process.
Southern California Gas Company | N | SANTA BARBARA | SUMMERLAND | 2025-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | FREELANCE | CARPINTERIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gardener struck 1/2 IPS service while digging to install drainage. Crew replaced 1/2 Riser.
Southern California Gas Company | N | TULARE | DINUBA | 2025-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOMENIC FINO | DINUBA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant excavating to install fence post, hit & damaged a 1/2 plastic service. Occupant was counselled by LCT regarding 811 notification process to have underground utilities located & marked prior to excavating.
Southern California Gas Company | N | TULARE | DINUBA | 2025-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ELKHORN DAIRY | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Farming crew damaged 1 plastic service while installing irrigation lines. No USA notification. SoCalGas crew made permanent repairs and took photos.
Southern California Gas Company | N | TULARE | DINUBA | 2025-03-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HORACIO VIZCARRA | DINUBA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating with shovel to plant a tree, occupant damaged a 1/2 plastic gas line, crew made permanent repairs. Occupant Horacio Vizcarra was advised to contact 811, moving forward, when excavating, he stated that he understood, photos of damage sent to Claims via email by LCT Gilbertson.
Southern California Gas Company | N | TULARE | DINUBA | 2025-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DANIEL BARAJAS | DINUBA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCG crew responded to RFA for damaged gas line, upon arrival, crew found that while working to install a fence post, occupant Daniel Barajas accidentally damaged a 1/2 plastic gas line with a hand operated auger, crew made permanent repairs. Mr. Daniel Barajas was advised to call USA before excavating, moving forward.
Southern California Gas Company | N | TULARE | DINUBA | 2025-01-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITY OF DINUBA | DINUBA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged a non-energized pipe, not connected to company facilities.
Southern California Gas Company | N | TULARE | EARLIMART | 2025-08-25 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SOCALGAS | VISALIA | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | First party damage, ETR damaged plastic service while taking underground samples due to structure fire. Permanent repairs made by crew.
Southern California Gas Company | N | TULARE | EXETER | 2025-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | VINCE FLORES | EXETER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating to repair a water line in private property, occupant Vincent Flores damaged a 1/2'' plastic gas service, SCG crew made permanent repairs. USA was not notified as required, Mr. Vincent Flores was educated about USA law.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BILL NELSON GENERAL ENGINEERING CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit a service while using a hydro-vac to expose prior to boring. Road closure & 8 homes evacuated by local FD necessitating MCR. Contractor was counselled on using caution while working around plastic company facilities.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2025-07-07 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 1 |  | SOCALGAS | VISALIA | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service hit by ETR while using pogo to take underground samples.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2025-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JOSE PAREDES | FARMERSVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating for fence post, occupant Jose Paredes damaged a 1/2 inch IPS gas line, crew made permanent repairs. Damaging party Jose Paredes was advised to contact 811, moving forward, when excavating, he stated that he understood.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2025-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | OWNER | FARMERSVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged plastic service while digging with pik, assumably for fence post. No USA, permanent repairs made by crew.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | BILL NELSON GENERAL ENGINEERING CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contactor grading street for road reconstruction, hit a 1/2 plastic service. Excavator was counselled on using hand tools only when within the tolerance zone of marked company facilities.
Southern California Gas Company | N | TULARE | KINGSBURG | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RAYMOND ANDRATTE | KINGSBURG | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating with hand tools to repair a water line, occupant damaged a 1/2 plastic gas line, crew made permanent repairs. Damaging party Mr. Castro was advised to call 811, moving forward, when excavating, he stated that he understood.
Southern California Gas Company | N | TULARE | PIXLEY | 2025-12-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | WIRING CONNECTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor excavating to expose company facilities, damaged a 1/2 plastic service. Contractor was reminded by LCT to use caution while attempting to expose company facilities.
Southern California Gas Company | N | TULARE | PIXLEY | 2025-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to locate company facilities, damaged 1/2 plastic service. LCT counselled excavator on importance of using caution when excavating around marked company facilities.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | OMAR MARIN | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Occupant excavating with a posthole digger, hit & ruptured a plastic service prior to exposing.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | SOCAL EDISON | TULARE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCE excavating for emergency electrical vault repair. Foreman counselled on importance of waiting for positive response prior to excavating.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-06-04 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | MARTINS CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating with a directional drill, hit & ruptured a 2 plastic main after losing track of depth. Excavator did not have company facilities exposed at the time of damage but had verified depth & location.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | HECTOR GARCIA | POPLAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer augured into plastic service while digging for fence post. No USA
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | BLACK ROCK DRILLING GROUP | ALTA LOMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While digging to install a new telecommunications line, 3rd party contractor International Construction Builder accidentally damaged a 1/2 plastic gas line, SCG crew made permanent repairs. Contractor was reminded to exercise caution, moving forward, when excavating near gas lines.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-12-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | IRISH ELECTRIC | TULARE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator installing electrical conduit damaged a 1/2 plastic service. Contractor was counselled on the importance of using caution when excavating around marked company facilities.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ON DEMAND CONTRACTORS | LA PALMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to locate company facilities, hit & damaged a 1/2 plastic service. Contractor was advised to use caution when excavating plastic company facilities.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-09-23 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3270 |  | 1 |  | RACE COMMUNICATIONS | BURLINGAME | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating with an auger, hit & damaged a 2 plastic main. Excavator did not verify type of material prior to excavating.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SHIRLEY CRAWFORD | PORTERVILLE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer struck plastic service while digging for animal grave, No USA, photos sent to @claims by Supervisor Mejorado
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ON DEMAND | WHITTIER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to expose company facilities, hit a plastic service. Excavator was reminded to use caution when potholing company facilities.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SAMUEL BURGARA | PORTERVILE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged 1/2 plastic service while digging with shovel to repair water line. Occupant was counselled by LCT on importance of calling 811 two or more days prior to any excavating to get utilities located.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | UNDERGROUND SOLUTIONS ENGINEERING | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to locate marked company facilities, hit a 1/2 plastic service. Excavator was reminded to exercise caution while attempting to expose company facilities.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | 99 PIPELINE | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor grade for road reconstruction, lost track of marked company facilities, resulting in a service damage.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | IRISH ELECTRIC | TULARE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor Irish Electric damaged a 1/2 plastic service while working on electric project, SCG crew made permanent repairs. Erick Moran from Irish Electric was reminded to exercise caution when working near gas lines, moving forward, he stated that he understood.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2025-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | RACE COMMUNICATIONS | BURLINGAME | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1/2 plastic service while attempting to pothole. excavator was counselled by LCT on importance of using caution when excavating over marked company facilities.
Southern California Gas Company | N | TULARE | RICHGROVE | 2025-12-31 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 6 |  | TURN AROUND CONSTRUCTION | CITY OF INDUSTRY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor Turn Around Communications damaged a 2 plastic main with sharpshooter type shovel while working to install a new telecommunications line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | STRATHMORE | 2025-03-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | STRATHMORE MOBILE HOME PARK | PORTERVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Code 1 caused by customer installing fence post resulting in an excavation damage. LCT counselled the damaging party on the importance of utilizing free USA service by calling 811 two or more working days prior to any excavation activity.
Southern California Gas Company | N | TULARE | STRATHMORE | 2025-05-16 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3550 |  | 4 |  | JT UTILITIES SERVICES GROUP | WINTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor excavating with directional drill, hit & ruptured a 2 plastic main that had not been marked by ETD. ETD did not utilize all available resources to locate & mark company facilities.
Southern California Gas Company | N | TULARE | TERRA BELLA | 2025-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | MCKUIN PIPELINE | HOLLISTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to locate marked company facilities, hit & ruptured a 1/2 plastic service with a shovel.
Southern California Gas Company | N | TULARE | TIPTON | 2025-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to install a telecommunications conduit, hit & damaged a 1/2 plastic service.
Southern California Gas Company | N | TULARE | TIPTON | 2025-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | TURN AROUND COMMUNICATIONS | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to locate company facilities, hit & damaged a 1/2 plastic service. LCT counselled excavator on using causing when exposing plastic company facilities.
Southern California Gas Company | N | TULARE | TRAVER | 2025-11-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | CITY BORE COMMUNICATION | RIALTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged a 2 plastic main with a mini excavator. Locate wire was damaged & company facilities records were inaccurate.
Southern California Gas Company | N | TULARE | TULARE | 2025-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DAWSON MAULDIN | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to locate company facilities, hit a 1/2 plastic service. Excavator was reminded to use caution when excavating around marked company facilities.
Southern California Gas Company | N | TULARE | TULARE | 2025-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | STIMPLE CONSTRUCTION | TULARE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage, damaging crew was not on site when crew arrived for repairs, appeared to be electric project, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LVS COMMUNICATIONS | GARDEN GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to install telecommunications conduit, hit & damaged a marked service. Excavator was reminded to use caution when excavating within 24 of marked company facilities.
Southern California Gas Company | N | TULARE | TULARE | 2025-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | HOME OWNER | TULARE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer excavating to install electrical conduit for solar, hit & ruptured a 1/2 plastic service. Did not have USA. LCT counselled customer on the importance of having valid USA prior to excavating.
Southern California Gas Company | N | TULARE | TULARE | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  |  | NA | WEST VALLEY CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor backfilling a trench, failed to protect exposed company facilities & severed service with a backhoe bucket. Contractor was counselled on exercising caution while using large excavation equipment around company facilities & never within 2'' of marked or exposed company facilities.
Southern California Gas Company | N | TULARE | TULARE | 2025-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DAWSON MAULDIN | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor did not maintain marks & hit a plastic service. Contractor was reminded by LCT to responsibly maintain marks or call in for remark of job site.
Southern California Gas Company | N | TULARE | TULARE | 2025-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RT NELSON CONSTRUCTION | IVANHOE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to locate company facilities, damaged a 2 plastic service. Excavator was counselled on the importance of using caution when working around marked company facilities.
Southern California Gas Company | N | TULARE | TULARE | 2025-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | GUYLLERMO CASTILLO | TULARE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged plastic service while removing fence post. Customer was counselled on the importance of contacting 811 two or more days prior to any excavation work.
Southern California Gas Company | N | TULARE | TULARE | 2025-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | CITY BORE COMMUNICATION | RIALTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor City Bore Communication damaged a 1/2 plastic gas line while excavating for telecommunications project, SCG made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2025-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DAWSON MAULDIN | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to locate company facilities, hit a 1/2 plastic service. Excavator was urged to use caution while excavating around plastic company facilities.
Southern California Gas Company | N | TULARE | TULARE | 2025-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DAWSON MAULDIN LLC | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit & ruptured a plastic service while grading for paving restoration.
Southern California Gas Company | N | TULARE | TULARE | 2025-04-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | SECURITY PAVING COMPANY | WESTLAKE VILLAGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator hit 1 inch plastic service with backhoe while digging to install sewer line. Excavator was informed they must use hand tools only when within the tolerance zone of any marked company facilities.
Southern California Gas Company | N | TULARE | TULARE | 2025-04-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | SECURITY PAVING COMPANY | WESTLAKE VILLAGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavation damage cause by backhoe. Trench wall failure while excavating. Contractor damaged the same service the prior day.
Southern California Gas Company | N | TULARE | TULARE | 2025-09-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SECURITY PAVING COMPANY | WESTLAKE VILLAGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Road grading was being performed for new road and over pass. Service was hit by graders'' blade. Excavator was counselled by LCT to only use approved excavation methods when within tolerance zone of any marked company facilities.
Southern California Gas Company | N | TULARE | TULARE | 2025-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | THE LANDSCAPE COMPANY | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 3rd party excavator dug outside of delineated area & struck an unmarked service. Excavator was counselled by LCT on importance of working within delineated area/described work area.
Southern California Gas Company | N | TULARE | TULARE | 2025-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | HAIME VALDEZ | TULARE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Unlicensed contractor installing fence post, hit & damaged a 1/2 plastic service. Excavator was counselled on importance of calling 811 two or more days prior to excavating.
Southern California Gas Company | N | TULARE | TULARE | 2025-10-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 17321 |  | 0 |  | USA DIRECTIONAL BORE | BAKERSFIELD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | MCR due to main size & street closure. 3rd party contractor excavating to install a telecommunications conduit, hit & damaged a 6 plastic main.
Southern California Gas Company | N | TULARE | VISALIA | 2025-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALL FLOW PLUMBING | EXETER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating without USA ticket, hit & damaged a 1/2 plastic service. Excavator was counselled by LCT regarding importance of obtaining USA 2 or more days prior to excavating.
Southern California Gas Company | N | TULARE | VISALIA | 2025-07-29 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 1 |  | SOCALGAS | VISALIA | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1st party damage caused by ETR checking for underground samples with pogo.
Southern California Gas Company | N | TULARE | VISALIA | 2025-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AMERICAN | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to expose electrical conduit, hit & ruptured a marked 1 plastic service with a probe.
Southern California Gas Company | N | TULARE | VISALIA | 2025-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FELIPE VASQUEZ | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer excavating to remove tree, hit & damaged a 1/2 plastic service. Customer was counselled on importance of calling 811 prior to excavating to get underground utilities located & marked.
Southern California Gas Company | N | TULARE | VISALIA | 2025-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | M. MADRIGAL | VISALIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged plastic service while digging to remove tree. No USA, Crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2025-09-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LEWIS SHANNON ELECTRIC | HANFORD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit a 2 plastic main while excavating to install electrical conduit. LCT counselled excavator on importance of calling 811 two or more days prior to excavating.
Southern California Gas Company | N | TULARE | VISALIA | 2025-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | STEVE MANOCCHIO | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer excavating to install fence posts, hit a gas service with a posthole digger. Customer was counselled by LCT & FOS regarding the importance of utilizing free 811 service two or more days prior to any excavation activity.
Southern California Gas Company | N | TULARE | VISALIA | 2025-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | HIGHLIGHT ELECTRIC | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor Highlight Electric damaged a 1/2 plastic gas line while excavating to install a telecommunications line, SCG crew made permanent repairs. 3rd party contractor Highlight Electric was digging on expired USA ticket.
Southern California Gas Company | N | TULARE | VISALIA | 2025-05-28 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11740 |  |  | NA | TRAFFIC LOOPS CRACKFILLING | ANAHEIM | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating with auger attachment on a track-hoe, hit & ruptured a 4 plastic main. Excavator used improper equipment within the tolerance zone & was excavating prior to legal start date/time.
Southern California Gas Company | N | TULARE | VISALIA | 2025-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SALVADOS CUEVAS | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install a fence post, occupant Salvador Cuevas damaged a 1/2 plastic gas line, crew made permanent repairs. Mr. Salvador Cuevas was advised to call 811 before excavating, moving forward, he stated that he understood, pictures of damage sent to claims via email by IC Jose Curiel.
Southern California Gas Company | N | TULARE | VISALIA | 2025-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ROBERT S PLUMBING | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating to replace sewer lateral, hit & ruptured a 1/2 plastic service. Contractor was counselled by LCT on importance of calling USA 2 or more days prior to excavating.
Southern California Gas Company | N | TULARE | VISALIA | 2025-09-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LEO TIDWELL EXCAVATING | PASO ROBLES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged a 4 plastic main with backhoe while excavating to install a new Telecommunications line, SCG crew made permanent repairs. Damaged pipe was not leaking but required repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2025-02-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 54 |  | HERBERT KINSER | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit & ruptured a 2 inch plastic main while excavating to replace sewer lateral with a backhoe. Customer did not have USA & was counselled by FOS & LCT onsite regarding the importance of having valid USA prior to excavating.
Southern California Gas Company | N | TULARE | VISALIA | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HERNANDEZ FENCE | HANFORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor installing fence post, hit a marked plastic service with a motorized auger. LCT counselled excavator on importance of using hand tools only to excavate when within the tolerance zone of any marked company facilities.
Southern California Gas Company | N | TULARE | VISALIA | 2025-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MARQUEZ - HANDY MAN | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Handy man excavating with post hole digger struck a 1/2 plastic service. Excavator had left prior to SCG arrival.
Southern California Gas Company | N | TULARE | VISALIA | 2025-03-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DCW CONTRACTORS | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit and ruptured a 1/2 inch plastic service while excavating to repair electrical conduit. There was no USA ticket for the area of excavation. LCT counseled contractor on the importance of excavating with a valid USA.
Southern California Gas Company | N | TULARE | VISALIA | 2025-05-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ANTHONY ALVARADO | VISALIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Customer excavating to locate electrical lines, hit & ruptured a plastic gas service. Customer had previously called in a USA ticket that expired & failed to use caution while excavating over previously marked company facilities.
Southern California Gas Company | N | TULARE | VISALIA | 2025-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AVISON CONSTRUCTION | MADERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to expose company facilities, damaged a 1/2 plastic service. Excavator was counselled on importance of using caution while excavating over plastic company facilities.
Southern California Gas Company | N | TULARE | VISALIA | 2025-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JESSIE MORALES | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Unlicensed 3rd party contractor excavating on private property, damaged a 1/2 plastic service. Excavator was counselled by LCT on importance of calling 811 prior to excavating.
Southern California Gas Company | N | TULARE | VISALIA | 2025-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JM LANDSCAPES | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor J M Landscapes was digging without a valid USA ticket to remove a palm tree and damaged a 1/2 plastic gas line, crew made permanent repairs, damaging party was advised to have a valid USA ticket, moving forward when excavating.
Southern California Gas Company | N | TULARE | VISALIA | 2025-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JAQUE POWELL | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor (handyman) excavating to repair sprinkler line, hit & ruptured a 1/2'' plastic service with a shovel. Excavator was counselled by LCT & FOS on importance of calling USA 2 or more days prior to any excavating.
Southern California Gas Company | N | TULARE | VISALIA | 2025-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | ANTHONY CASIANO | VISALIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer excavating to remove tree stump, hit & ruptured a CTS service. LCT counselled customer on importance of utilizing free 811 service 2 or more days prior to excavating.
Southern California Gas Company | N | TULARE | VISALIA | 2025-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JOHN JIMENEZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant excavating to install water line, hit a 1/2 plastic service. Occupant was counselled by LCT on importance of calling 811 two or more days prior to excavating.
Southern California Gas Company | N | TULARE | VISALIA | 2025-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DURANGO FENCING | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating without USA, hit & ruptured a 1/2 plastic service. Contractor is well aware they should not be engaged in any excavation activities without valid USA.
Southern California Gas Company | N | TULARE | WOODLAKE | 2025-10-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | CITY OF WOODLAKE | WOODLAKE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | City of Woodlake excavating to replace water facilities, damaged a 1/2 plastic service. Foreman was counselled by LCT to keep USA ticket current & maintain marks.
Southern California Gas Company | N | TULARE | WOODLAKE | 2025-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JOSE TADEO | WOODLAKE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer damaged service while digging to replace light post. No USA, crew made permanent repairs.
Southern California Gas Company | N | VENTURA | BELL CANYON | 2025-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | HOT LINE CONSTRUCTION | SANTA PAULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was digging with valid USA. While excavating with shovel, contractor hit properly marked 1/2-inch plastic gas line. SoCalGas crew arrived and completed permanent repairs.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2025-01-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ANNA MARIE SANDOVAL | CAMARILLO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ETR responded to an emergency order placed by a contractor for a hit service line at a residential structure. The service was struck by a contractor while digging a trench for an irrigation system. Upon arrival of the ETR, an RFA For Gas-ops was placed and 3 residents were evacuated from their home due to the hit service and having 8% volume gas at the foundation. Once the repairs were completed and the evacuation was lifted, ETR restored service to the properties, service and safety checked all gas appliances. On-Call claims was notified. There were No injures/fatalities. No Street Closures. No Media No First Responders.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2025-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SELF EMPLOYED | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck 1/2 service line with hand tools
Southern California Gas Company | N | VENTURA | CAMARILLO | 2025-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ALL CLEAR PLUMBING AND ROOTER INC | SYLMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line with chipping hammer while excavating. Work Being Performed- Sewer Work, Damaged with electric clay spade 520004131713
Southern California Gas Company | N | VENTURA | CAMARILLO | 2025-12-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | CHARLIE RUTLEDGE | CAMARILLO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor damaged 1 service while excavating. USA ticket was expired. Crew made permanent repairs.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2025-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | CUSTOM CONTOR CONSTRUCTION | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged stub while digging to install grading stake
Southern California Gas Company | N | VENTURA | CAMARILLO | 2025-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | CSI CONSTRUCTION | FOOTHILL RANCH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CSI damaged 1 PLA service with backhoe while trenching for electruical
Southern California Gas Company | N | VENTURA | CAMARILLO | 2025-06-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | AMBURGEY CARICH CONSTRUCTION | COSTA MESA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged the service, there was NO valid USA.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2025-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | CUSICK ELECTRIC | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew altered service to make permanent repairs
Southern California Gas Company | N | VENTURA | CAMARILLO | 2025-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | IMAGINE DESIGN | CAMARILLO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor dug without a USA ticket and damaged 1/2 PLA service.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | MENDOZA POOL AND PLASTER | SYLMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 plastic service while excavating with hand tools. There was no valid USA
Southern California Gas Company | N | VENTURA | CAMARILLO | 2025-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | FLAMINGO CONSTRUCTION | STUDIO CITY | CA | N | Y | Yes | No | No | Yes | No | Yes | No | Contractor damaged a 1'' plastic service with a backhoe, The contractor called in the USA AFTER the service was damaged and no delineation was given.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2025-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | VINYL CONCEPTS | NEWBURY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 1/2 plastic service while post hole digging for a new fence. There was a valid USA and the marks were accurate.
Southern California Gas Company | N | VENTURA | CARPINTERIA | 2025-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SCOTT TETER | CARPINTERIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging for fence post with no USA.
Southern California Gas Company | N | VENTURA | FILLMORE | 2025-04-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | CIENFUEGOS CONSULTING | THOUSAND OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor severed 1/2 inch service with Ditch witch.
Southern California Gas Company | N | VENTURA | FILLMORE | 2025-07-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | CIENFUEGOS CONSULTING | THOUSAND OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with Mini X while excavating to install waterline. Contractor did not have a USA ticket.
Southern California Gas Company | N | VENTURA | LAKE SHERWOOD | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NA | THOUSAND OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic branch service hit by contractors. Damage was taped off when crew arrived on site. Plastic service was under sewer line that was being installed on private property.
Southern California Gas Company | N | VENTURA | LAKE SHERWOOD | 2025-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | CEJ DESIGN & CONSTRUCTION | WESTLAKE VILLAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | MSA Found off. 3rd party contractor digging with chip hammer to create hole for bollard in front of electric meter. Repairs completed and no restore required due to MSA off.
Southern California Gas Company | N | VENTURA | MOORPARK | 2025-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1771 |  | 4 |  | LOYALTY COUNTS CONSTRUCTION | OXNARD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 IPS service was damage by contractor. Failed to call in USA
Southern California Gas Company | N | VENTURA | MOORPARK | 2025-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | BENJAMIN VENTURA INC | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged PE Line
Southern California Gas Company | N | VENTURA | MOORPARK | 2025-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | CLEARFLO POOLS CONSTRUCTION | AGOURA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while excavating without a valid USA ticket. Crew leader instructed contractor to call 811.
Southern California Gas Company | N | VENTURA | MOORPARK | 2025-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 30 | 30 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COLLIER CONSTRUCTION | MOORPARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | After the fact damage found by Locator in field. Homeowner pulled up steel service and was told that they will be charge for a full service. Order has been created 54/653746
Southern California Gas Company | N | VENTURA | MOORPARK | 2025-01-28 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | CO GTO LAB | WESTLAKE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 inch plastic main damaged by contractor with auger for soil samples. no USA called. 2 inch plastic main abandoned by company crew onsite due to main not supplying and structures, approval from AM and planning. Planning currently working on abandonment order/paperwork.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2025-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | AR PIPELINE | NEWBURY PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 3rd party contractor damage our service line with shovel while digging to instill new water line. Damage occurred outside of their delineation.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2025-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NATURESCAPE | CALABASAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging out a clogged drain without a USA ticket and damaged 1/2 service with shovel
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2025-02-26 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NATURE SCAPE MID VALLEY | THOUSAND OAKS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party damaged pipe on private property when digging for drain line.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2025-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ARL GENERAL ENGINEERING | SIMI VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1/2 PLA service while excavating for water. ticket was active and service marks were visible. contractor struck service with shovel, hard soil. Permanent repairs made via alteration.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2025-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | KIRSCH ELECTRIC | NEWBURY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCG service hit from 3rd party installing a grounding rod. There were no evacuations. No Fire Department. No street closures. 2 homes were restored after the service repair
Southern California Gas Company | N | VENTURA | OAK PARK | 2025-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | PREFERRED REMODELING | ENCINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was adding ADU to home. 3rd party contractors were digging for foundation and struck gas service in the process.
Southern California Gas Company | N | VENTURA | OJAI | 2025-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | CARPER BUILDERS | OJAI | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor Severed 1/2 Service line while excavation with mini excavator.
Southern California Gas Company | N | VENTURA | OJAI | 2025-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MCCLOUD ENTERPRISES | OJAI | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 plastic service with hand tools while trenching for utilities for new above ground parking garage. There was no USA called.
Southern California Gas Company | N | VENTURA | OJAI | 2025-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | PIERCE JAMES CONSTRUCTION | ACTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged 1/2 service while installing sewer line. Contractor failed to expose gas service before excavating with backhoe. No pictures were taken.
Southern California Gas Company | N | VENTURA | OJAI | 2025-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JAMES PIERCE CONSTRUCTION | ACTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | customer damaged service two days in a row.
Southern California Gas Company | N | VENTURA | OJAI | 2025-02-04 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SOCALGAS | OXNARD | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew damaged 1/2 service with backhoe. Maps were not updated to show plastic facilities and they were digging over old steel facilities. Had to locate off measurements.
Southern California Gas Company | N | VENTURA | OXNARD | 2025-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | NA | OXNARD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A 3rd party plumber hired by Mr. Juarez damaged the branch service line to 1731 Valencia Pl, Oxnard while trenching for utilities. There was NO USA and the plumber installed a temporary fitting on the branch gas service line. Damage was found by a locator working on a ticket unassociated with the address. Damage prevention has been notified.
Southern California Gas Company | N | VENTURA | OXNARD | 2025-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | MELESIO JUAREZ DBA MODERNA CONSTRUCTION | OXNARD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Homeowner was trenching for Edison when gas service was hit. Dig alert ticket was expired at the time of the incident.
Southern California Gas Company | N | VENTURA | OXNARD | 2025-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | MELESIO JUAREZ DBA MODERNA CONSTRUCTION | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowners contractor damaged a 1/2 plastic service with hand tools while trenching for utilities. There was a USA but contractor failed to maintain marks
Southern California Gas Company | N | VENTURA | OXNARD | 2025-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | TORO ENTERPRISES INC | OXNARD | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Toro enterprises damaged a 2 inch plastic main with a backhoe. Toro and ETD had a field site meeting and agreed to mark all services between Rose Ave. and Balboa St. Toro did not delineate scope of work and the locater still located the services. The scope of work crossed a 2 main that was not located.
Southern California Gas Company | N | VENTURA | OXNARD | 2025-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CAMARILLO DRILLING INC | NUEVO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service by contractor while putting in telecommunication lines.
Southern California Gas Company | N | VENTURA | OXNARD | 2025-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | GILBERT VASQUEZ | MOORPARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A third party contractor damaged a 1 Plastic service with hand tools while excavating for electric lines. There was no valid USA called.
Southern California Gas Company | N | VENTURA | OXNARD | 2025-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 3 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3749 |  |  | NA | SALAS & SONS | MOOPARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a new 3 inch service at a new apartment complex while excavating. crew was able to utilize a curb valve to control the gas.
Southern California Gas Company | N | VENTURA | OXNARD | 2025-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1678 |  | 3 |  | CHUY S PLUMBING | OXNARD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor dug without USA ticket and struck service line.
Southern California Gas Company | N | VENTURA | OXNARD | 2025-10-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | TRAVIS AGRICULTURAL CONSTRUCTION | VENTURA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 1/2 PLA service while trenching. Locator mismarked. Locate wire was bare wire and severely corroded and signal was choppy. No pictures
Southern California Gas Company | N | VENTURA | OXNARD | 2025-06-04 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  |  | NA | SOCALGAS | OXNARD | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ETD damaged 1 plastic service with a pogo while attempting to get a good ground for his locator to complete a USA ticket.
Southern California Gas Company | N | VENTURA | OXNARD | 2025-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | STEPHEN G MCNAUGHTEN | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 plastic service while excavating for a sewer lateral for an ADU. There was NO Valid USA
Southern California Gas Company | N | VENTURA | OXNARD | 2025-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LEONARDO AMBRIZ | OXNARD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Workers hired by the home owner damaged a 1/2 plastic service while trenching for electrical utilities. There was No USA. 1 evacuation and 1 outage.
Southern California Gas Company | N | VENTURA | OXNARD | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LINE WORKS CONSTRUCTION | CORONA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd Party Contractor was digging and struck 1/2 service line with sharp shooter. They were digging on an expired USA ticket. New ticket did not get called in until they damaged service line. New ticket number A251570241
Southern California Gas Company | N | VENTURA | OXNARD | 2025-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | LINE WORKS CONSTRUCTION | LA VERNE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor potholing for boring operations damaged the 1/2 plastic service while potholing of the gas service. Service was damaged within the 2'' tolerance of the delineated service.
Southern California Gas Company | N | VENTURA | OXNARD | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | CITY OF OXNARD WATER | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water company damaged 1/2 service while working on water line
Southern California Gas Company | N | VENTURA | OXNARD | 2025-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | CARLOS MARTIN | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3RD PARTY CONTRACTOR HIT 1/2 CTS SERVICE WITH SHOVEL SEVERED IN HALF WHILE EXCAVATING TO INSTALL ELECTICAL CONDUIT 2 HOUSE AFFECTED 900 & 840 STERN LN. THERE WAS NO VALID USA
Southern California Gas Company | N | VENTURA | PORT HUENEME | 2025-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | SUNSTONE CONSTRUCTION | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1 service with backhoe while excavating without a USA ticket.
Southern California Gas Company | N | VENTURA | PORT HUENEME | 2025-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1475 |  | 0 |  | SUN STATE CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor ripped 1 Pla service out while trenching. contractor folded over 20'' of 1 service. 520004371301
Southern California Gas Company | N | VENTURA | PORT HUENEME | 2025-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3364 |  | 2 |  | PORT HUENEME WATER COMPANY | PORT HUENEME | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Port Hueneme water damaged 2 main while excavating to repair water line 520004322879
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2025-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1954 |  |  | NA | STANDARD CIVIL | CYPRESS | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | third-party excavator struck a ? steel (STL) gas line located in the street, resulting in damage to the riser inside the curb meter box (CMB). The Fire Department and Police responded to the scene. The Fire Department evacuated 20 units and closed the street to ensure public safety. The USA ticket associated with the excavation was expired. Notes on the ticket indicate that no delineation was provided.
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2025-10-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11740 |  | 0 |  | WILCOX & WILCOX | CANOGA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged 4 Pla newly installed main. damage occurred while rcc crew was working at the other end of the main job. no customers were affected as the main was not feeding any customers yet. 520004324005
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2025-12-12 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  | 0 |  | LENNAR HOMES | SANTA PAULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer was backfilling and grading over newly installed main and damaged 2 line with the loader bucket. 520004369812
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2025-10-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | ACCESS GENERAL CONTRACTING | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | A company contractor installing guard rails damaged a 1/2 plastic service with hand tools. There was a valid and accurate USA.
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2025-01-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | TORO ENTERPRISES INC | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Toro hit service line while pot holing.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2025-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NICHOLAS MICHAEL CAIRNS | SIMI VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 1/2 plastic service with hand tools while trenching for irrigation. There was no USA called
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2025-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | ROK POWER | POMONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Rok power struck 1/2 PLA service while used auger to replace power pole anchor. USA ticket states pole replacement for specific pole number. Pole number matched in field. no mention of anchor replacement or work on USA ticket. SCG closed EPR as no conflict. No delineations provided onsite, Rok power confirmed onsite they did not delineate ticket. PLA service that was hit was to Standard and branch. Hard to locate. Permanent repairs made in form of Service alter.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2025-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | ALEXANDER SUKOPCAK | SIMI VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor hit PLA service with backhoe while excavating for sewer for construction of new property. Contractor did have a USA but his ticket was not valid until 5pm on 6/12. Ticket was marked and located earlier in the day before contractor damaged.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2025-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JA SALAZAR CONSTRUCTION | LA HABRA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 3rd. party contractor struck our gas line with backhoe after failing to pothole. ETD instructed contractor on site that he was getting a faulty signal after using Line tracer. Contractor failed to do so. USA was valid
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2025-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | ECO LANDSCAPING | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The damage occurred at a business. No tab for business. Homeowner would not be the correct selection.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2025-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PERMA GREEN | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit PLA service while excavating for fence posts for homeowner. No USA called. SCG crew called out via Arcos, on-call supervisor onsite. Repairs made via alteration.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2025-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WEST COAST FENCE PROS | OXNARD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Corrected damage opening size and MAOP and operating pressure. Fencing contractor damaged 3/4STL service with posthole digger while digging for fence post for homeowner. Permanant repairs made in form of clamp on STL Service.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2025-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WENC RAMIREZ | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party hit SCG service while hand digging to replace fence post.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2025-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | AARON SOUTHARD | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit CTS service while hand digging.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2025-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | RICARDO PIZANO | SIMI VALLEY | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor and home owner damaged a 1/2 plastic service with hand tools while excavating for a driveway gate installation. There was a USA called in, however there was no USA delineation provided and no USA marks.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2025-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | JUAN ZAPIEN | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging near riser, damage 1/2 CTS service. No USA called in
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2025-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CHERYL STANSBERRY | SIMI VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Howe owners contractor damaged a 1/2 plastic service with hand tools while trying to cut out a tree root.
Southern California Gas Company | N | VENTURA | SOMIS | 2025-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1766 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service line with pick axe while digging for electric. Contractor declined to give his name or company name. Homeowner stated work being done was to install a Tesla battery and that the men digging there were digging for Tesla.520004335838
Southern California Gas Company | N | VENTURA | SOMIS | 2025-01-19 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 3 | 45 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5616 |  | 20 |  | RICK SHACKELFORD | SOMIS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged a 3inch plastic main in public property with a augur machine. Home owner was attempting to replace fencing that was damaged during the Mountain fire. Fire department had partial road closures on Solano Verde Dr. There was No USA.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2025-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2179 |  | 1 |  | CONEJO VALLEY HOME SERVICES | NEWBURY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged steel service on Bart Circle. There was no valid USA Ticket. Conejo Valley Heating & Air were the contractors that caused the damage. CSLB#536456
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2025-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2047 |  | 1 |  | HOT LINE CONSTRUCTION | SANTA PAULA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Hotline hit 3/4STL service while excavating with backhoe, performing work for SCE. Hit line was within hotline''s delineated area. No SCG markings for service were found onsite. District supervision to follow up with employee. Crew responded and made permanent repairs via STL service alteration of approx 2''.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2025-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew made permanent repairs on CTS service using coiled pipe and 2 couplings.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2025-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | DEVEN PATEL | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractors hit service when digging on private property. No USA ticket.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2025-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | EARTH AND OAK ENGINEERING | NEWBURY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit service while hand digging. Contractor did not have USA Ticket.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2025-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | OSCAR MONTOYA | THOUSAND OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic service while digging a wall footing.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2025-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | GT MURPHY CONSTRUCTION | SIMI VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | HIT WITH- SHOVEL OR PICK AXE OR EXCAVATOR UNSURE CONTRACTOR- STARCON GENERAL CONTRACTORS RT SIDE OF HOUSE
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2025-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | ALTO BUILDING | AGOURA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A third party contractor damaged a 1/2 Plastic service with hand tools while excavating for a new sewer lateral. No USA was called in
Southern California Gas Company | N | VENTURA | VENTURA | 2025-09-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3550 |  | 4 |  | CITY SERVICE PAVING | PLACENTIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating without a USA ticket and damaged the 2 main with a backhoe.520004304833
Southern California Gas Company | N | VENTURA | VENTURA | 2025-08-28 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | VENTURA WATER | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Ventura Water Company damaged a 2 plastic main with a steel prob while attempting to verify depth of water service. There was a Valid USA and Markings were correct.
Southern California Gas Company | N | VENTURA | VENTURA | 2025-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 30 | 30 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | MATRIX | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ETD found non-company approved fitting on exposed PLA service while responding to a routine USA ticket. ETD found no leak indications onsite. ETD started damage report and relayed information to G/O FOS. Crew was called to come and remove non-approved fitting and installed an approved company coupling. Permanent repairs made in form of service alteration.
Southern California Gas Company | N | VENTURA | VENTURA | 2025-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JULIANS TREE CARE | OXNARD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Victor Rodriguez calling to report hit service line when digging to remove tree. called from 805-253-5850, hit with pickaxe, Contractor let the USA ticket expire, Also the contractors delineation did not match the excavation area.
Southern California Gas Company | N | VENTURA | VENTURA | 2025-01-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | WEST COAST PIPELINE | PLACENTIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damaged service while excavating near the newly installed service to a mobil home park. no meters were affected as the service was not tied over yet
Southern California Gas Company | N | VENTURA | VENTURA | 2025-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | HALTER ENCINAS ENTERPRISES | VENTURA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | A 3rd party damage occurred at 4055 Pomona St. Contractor did delineate the area with white paint, however he failed to use the words USA and have proper brackets. ETD wrote in notes no delineation but failed to contact the customer or attempt to. Contractor continued to excavate even though he admitted to not checking the EPA codes/notes online.
Southern California Gas Company | N | VENTURA | VENTURA | 2025-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3983 |  |  | NA | DAVIS FIRE PROTECTION | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew used control holes to contain the damage. Crew bored in 15'' of 2 inch to avoid breaking large section of gutter.
Southern California Gas Company | N | VENTURA | VENTURA | 2025-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | STACY STERLING | VENTURA | CA | N | Y | No | No | No | No | No | No | No | Homeowner was excavating to repair sewer and damaged a 1/2 pla service while excavating,
Southern California Gas Company | N | VENTURA | VENTURA | 2025-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | DAVID THOMAS | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 IPS service while excavating. There was no USA
Southern California Gas Company | N | VENTURA | VENTURA | 2025-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1848 |  | 4 |  | HOT LINE CONSTRUCTION | SANTA PAULA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor damaged a 1 service while trenching with backhoe. Service was not marked due to locator error,
Southern California Gas Company | N | VENTURA | VENTURA | 2025-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 50 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2086 |  | 0 |  | SUNSTONE CONSTRUCTION | NEWBURY PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.
Southern California Gas Company | N | VENTURA | VENTURA | 2025-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | SPENCER CONSTRUCTION | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged 1/2 pla service with tunnel par while excavating. Contractor tied back service 520004335536
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2025-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | H&R PLUMBING | SYLMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing contractor hit 1/2PLA service while excavating for sewer repair with shovel. Plumbing contractor stated he had USA, but he did not have USA number. No markings onsite. Plumbing contractor did not have a USA, plumbing contractor called in a rush USA ticket after damage already occurred. Permanent repairs made by crew in form of Service Alter.
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2025-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MO AKHAVAN | WESTLAKE VILLAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 plastic damage by contracting crew grading for home. No USA.
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2025-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 0 |  | COURTNEY KENDALL | WESTLAKE VILLAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home Owner hit gas company line when digging a trench on property. No valid USA. Pictures added to comments.
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2025-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MCMASTER & HILL | WESTLAKE VILLAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors installing fence post damage our 1/2 service. No valid USA Ticket called in
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2025-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  |  | NA | THOUSAND OAKS PLUMBING | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 IPS service hit by plumbing company while excavating for sewer repair. NO USA onsite. Repairs made in form of service alteration.
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2025-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1491 |  | 1 |  | LYNCH PLUMBING | CHATSWORTH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A 3rd party plumber damaged a 1/2 plastic service while excavating with hand tools to repair a sewer lateral. There was NO VALID USA called in.
Southern California Gas Company | Y | RIVERSIDE | SAN JACINTO | 2025-03-20 | Operator excavation damage | Main | Steel | Backhoe/Trackhoe | 1 | 400 | 385 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 150001 |  | 11 |  | TEICHERT | SACRAMENTO | CA | Y | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Teichert is working on an ongoing SCG project in intersection of State St & Esplanade Ave in San Jacinto. While potholing/trenching to set shore boxes, the crew encountered 2-sack slurry over SCG facilities. The crew broke up slurry with a jackhammer & began removing it w/ a backhoe. During the process, the backhoe struck an unexposed 1 inch AB nipple on top of the 6 inch HP main due to a breakdown in crew communication. Although the foreman had informed the backhoe spotter of an existing offset, the information was not retained, leading to the damage. The incident is currently under investigation.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 782 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | N | No | No | No | No | No | No | Yes | HOMEOWNER DAMAGED SEWER LINE WHILE DIGGING TO FIX SPRINKLER SYSTEM. THEY DID NOT HAVE A DIG TICKET.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 479 |  | 1 |  | VINCIGUERRA CONSTRUCTION | JACKSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with shovel.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 366 |  | 0 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner damaged service with shovel.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 808 |  | 1 |  | TAHOE SIERRA BUILDERS | STATELINE | NV | N | N | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR DAMAGED WITH SHOVEL WHILE POTHOLING FOR TREE REMOVAL. DIG TICKET STATED THEY WERE DIGGING ON RIGHT SIDE OF DRIVEWAY BUT CONTRACTORS ENDED UP DIGGING ON LEFT SIDE. THEY HAD A VALID DIG TICKET AND MARKS WERE ACCURATE
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-06-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 641 |  | 2 |  | BLUE DESERT DESIGN | REN | NV | N | N | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | Yes | THE CONTRACTOR WAS CUTTING A ROOT OUT AND DAMAGED SERVICE LINE WITH A SAWZALL.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-10-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 903 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | No | No | The homeownerdamaged a service while grading driveway without a valid dig ticket.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-11-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 428 |  | 0 |  | EL DORADO COUNTY | SOUTH LAKE TAHOE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while digging to remove old storm drain.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-03-11 | Third party excavation damage | Meter | Steel | Miscellaneous/Other | 0.75 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | N | No | No | No | No | No | No | Yes | Vehicle vs. MSA
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-09-29 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 340 |  | 0 |  | MEARS | CARSON CITY | NV | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with shovel.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 507 |  | 1 |  | SAM MARTIN LLC | EL DORADO HILLS | CA | N | Y | No | No | Yes | No | No | No | No | Contractor damaged service line while digging a foundation for a steel building.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 486 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | N | No | No | Yes | Yes | No | Yes | Yes | CONTRACTOR WAS DIGGING UNDER HOMEOWNERS DIG TICKET AND DAMAGED SERVICE LINE WITH AN EXCAVATOR. THE CONTRACTOR DID NOT POTHOLE SERVICE PRIOR TO USING EQUIPMENT.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 554 |  | 1 |  | BARACK PLUMBING | SOUTH LAKE TAHOE | CA | N | N | No | No | No | No | No | No | Yes | CONTRACTOR DAMAGED SERVICE LINE HIT WITH SHOVEL WHILE EXCAVATING FOR WATER SERVICE REPAIR. THEY DID NOT HAVE A VALID DIG TICKET.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 344 |  | 0 |  | SOUTH SHORE CUSTOM BUILDERS | SOUTH LAKE TAHOE | CA | N | N | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR DAMAGED A SERVICE LINE WITH A SHOVEL WHILE EXPOSING IT. THE CONTRACTOR HAD A VALID DIG TICKET.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 526 |  | 1 |  | CHAVEZ PLUMBING | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | No | No | The contractor damaged service with a shovel.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-08-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 486 |  | 1 |  | ACRON LANDSCAPING ENTERPRISES | SOUTH LAKE TAHOE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with stake.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 486 |  | 1 |  | BLAIS BUILDERS | SOUTH LAKE TAHOE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged service with excavator.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-08-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 113 |  | 0 |  | SOUTH LAKE TAHOE PUBLIC UTILITIES | SO LAKE TAHOE | CA | N | Y | Yes | Yes | Yes | No | No | No | No | Contractor damaged service with backhoe.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-10-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 883 |  | 1 |  | LEWIS FENCE CO | COLFAX | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged line with a digging bar.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2025-05-22 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 35 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 680 |  | 0 |  | MEARS | CARSON CITY | NV | N | N | Yes | Yes | Yes | Yes | Yes | Yes | Yes | CONTRACTOR DAMAGED FACILITY DURING BORING ACTIVITIES. THE BORE SHAFT HAD BOWED UP INTO THE EXISTING FACAILITIES. THE CONTRACTOR HIT HARDER GROUND COMPRISED OF A HARD CLAY MATERIAL THE SECOND DAY OF THE BORING PROCESS. THE GROUND CONDITION PRIOR TO THAT WAS COMPOSED MOSTLY OF A SANDY LIKE MATERIAL AND GROUND WATER. WHEN THE BORE BIT HIT THE HARDER GROUND, THE SANDY CONDITIONS DID NOT PROVIDE ENOUGH RESISTANCE TO KEEP THE BORE ROD IN PLACE AND THAT IS WHEN THE BORE ROD FLEXED.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 592 |  | 0 |  | RUPPERT INC | TAHOE CITY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged service with pickaxe.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2025-09-22 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 113 |  | 0 |  | MEARS | CARSON CITY | NV | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with shovel.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2025-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1505 |  | 2 |  | MULHOUSE TRACTOR | GRASS VALLEY | CA | N | N | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR DAMAGED AN UNDOCUMENTED SERVICE LINE WITH AN EXCAVATOR WHILE DIGGING FOR A SEWER LINE. THERE WAS A MAPPING DISCREPANCY. THEY HAD A VALID DIG TICKET
Southwest Gas Company | N | NEVADA | TRUCKEE | 2025-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 43 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 976 |  | 0 |  | MEARS | CARSON CITY | NV | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged service with excavator.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2025-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1435 |  | 1 |  | RK CONTRACTORS | RENO | NV | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service was damaged with an excavator.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2025-01-05 | Third party excavation damage | Regulator | Miscellaneous/Other | Miscellaneous/Other | 0 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | UNKNOWN | NA |  | N | N | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Meter damaged due to snow and ice caved in around meter shelter and put force on the regulator.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2025-02-11 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Miscellaneous/Other | 1 | 43 | 43 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | TENRIK BUILDERS | TRUCKEE | CA | N | N | No | No | No | No | No | No | Yes | Contractor damaged riser while digging.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2025-05-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1270 |  | 1 |  | SER CONSTRUCTION | MEADOW VISTA | CA | N | Y | No | No | No | No | No | No | Yes | CONTRACTOR DAMAGED FACILITY WITH MINI EX WHILE INSTALLING DRAIN PIPE. THEY DID NOT HAVE A VALID DIG TICKET AND THERE WERE NO PREVIOUS MARKS ON THE GROUND.
Southwest Gas Company | N | PLACER | CARNELIAN BAY | 2025-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1334 |  | 1 |  | OCCUPANT | WADSWORTH | NV | N | Y | No | No | No | No | No | No | No | Contractor damaged service with digging bar.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2025-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 216 |  | 0 |  | JP EXCAVATING AND PAVING | TAHOE VISTA | CA | N | N | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged service with hand tools
Southwest Gas Company | N | PLACER | KINGS BEACH | 2025-10-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1132 |  | 1 |  | WASATCH ELECTRIC | SALT LAKE CITY | UT | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor damaged service with a pneumatic digging bar.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2025-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1868 |  | 3 |  | OCCUPANT | KINGS BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Occupant damaged service line with a shovel.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2025-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 505 |  | 1 |  | VINCIGUERRA CONSTRUCTION | JACKSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with digging bar.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2025-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 759 |  | 1 |  | OCCUPANT | KINGS BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner damaged service with shovel.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2025-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1277 |  | 1 |  | TD CONSTRUCTION | RENO | NV | N | N | No | No | No | No | No | No | Yes | THE CONTRACTOR DAMAGED SERVICE WITH A PICK AXE WHILE DIGGING FOR NEW WATER LINE. THEY DID NOT HAVE A VALID DIG TICKET FOR THE ADDRESS. THE CONTRACTOR ASSUMED HIS TICKET FROM LAST YEAR WAS STILL VALID.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2025-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1053 |  | 1 |  | VINCIGUERRA CONSTRUCTION | JACKSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with digging bar.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2285 |  | 1 |  | VINCIGUERRA CONSTRUCTION | JACKSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with excavator.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2025-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2713 |  | 3 |  | LAZZARESCHI CONSTRUCTION | KINGS BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor did not pothole prior to digging with his excavator.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2025-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 639 |  | 1 |  | OCCUPANT | KINGS BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | The contractor had a valid dig ticket but dug outside of USA.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2025-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 972 |  | 1 |  | ALEX PRZYBYSLAWSKI | TAHOE VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to maintain marks.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2025-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1012 |  | 1 |  | BLUE CEDAR RENOVATIONS | TAHOE CITY | CA | N | Y | No | No | No | No | No | No | No | The contractor damaged service while digging with a pick axe.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2025-07-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2345 |  | 0 |  | GENSBURG & SONS | TAHOE CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged main with shovel.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2025-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 973 |  | 1 |  | OCCUPANT | TAHOE CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service line with shovel.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2025-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 986 |  | 1 |  | BASILE MANAGEMENT PRACTICE | TAHOE CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service line with a sharp shooter.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2025-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 600 |  | 2 |  | CE COX ENGINEERING INC | ORGANGEVALLE 1 | CA | N | N | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR DAMAGED FACILITY WITH A MINI EX. THE LOCATE MARKS WERE OFF DUE TO DOCUMENTATION DISCREPANCY.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2025-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 879 |  | 1 |  | OCCUPANT | TAHOE CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner damaged service with shovel.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2025-05-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 366 |  | 0 |  | JUNIOR WILSON | OLYMPIC VALLEY | CA | N | Y | No | No | No | No | No | No | Yes | THE CONTRACTOR WAS DIGGING A WATERLINE WITH A MINI EXCAVATOR AND DAMAGED SERVICE LINE. HE DID NOT HAVE A DIG TICKET.
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2025-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 525 |  | 2 |  | OCCUPANT | ADELANTO | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service line with shovel.
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2025-12-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 495 |  | 1 |  | KEVIN BUSH | SAN BERNARDINO | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service line while excavating.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2025-01-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 873 |  | 1 |  | USA SEPTIC SERVICE | LUCERNE VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | No | No | Contractor hit service line with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2025-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 760 |  | 0 |  | COLONIAL ELECTRIC INC. | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2025-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 805 |  | 2 |  | ALL PRO PLUMBING | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with excavator.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2025-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 960 |  | 2 |  | LICEA ELECTRIC | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with trencher.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2025-06-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6062 |  | 1 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR DAMAGED A MAIN WITH BACKHOE WHILE INSTALLING ELECTRIC CONDUIT. USA VALID.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2025-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 33 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 622 |  | 1 |  | OCCUPANT | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | HOMEOWNER''S SON DAMAGED A SERVICE LINE WITH A SHOVEL. VALID USA TICKET.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2025-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1335 |  | 4 |  | OPTIMUM INC | BLOOMINGTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | PE SERVICE DAMAGED WITH SHARP SHOOTER WHILE CONTRACTOR WAS POTHOLLING.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2025-04-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 272 |  | 0 |  | MORTIMORE CONSTRUCTION | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SERVICE STUB DAMAGED BY SHOVEL DIGGING FOR POWER UTILITY INSTALL INSIDE MOBILE HOME PARK.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2025-04-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 735 |  | 1 |  | GENARO ZAPATA | APPLE VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR DAMAGED A SERVICE LINE WITH A SHOVEL. NO USA TICKET.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 935 |  | 1 |  | BRIGHT PLANET SOLAR INC | WORCESTER | MA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with trencher.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2025-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3049 |  | 2 |  | SULLY MILLER CONTRACTING COMPANY | BREA | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | SERVICE DAMAGED BY EXCAVATOR WHILE DIGGING FOR ROAD IMPROVEMENT. USA TICKET VALID.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 635 |  | 1 |  | DAVID NUNO | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with shovel.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2025-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 531 |  | 2 |  | CARLOS GUERRERO | FONTANA | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service line with a shovel.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2025-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 664 |  | 2 |  | OCCUPANT | BIG BEAR CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service line hit with a shovel.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2025-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 479 |  | 0 |  | NATIVESCAPES INC | BIG BEAR CITY | CA | N | Y | Yes | Yes | No | Yes | No | No | No | Contractor damaged service with auger.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2025-10-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1385 |  | 2 |  | SHAWN MCDONALD EQUIPMENT INC | BIG BEAR LAKE | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Contractor damaged main with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2025-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 601 |  | 2 |  | A R JOENS PLUMBING | BIG BEAR CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with mini excavator.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2025-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 305 |  | 1 |  | S PORTER INC | BIG BEAR LAKE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR DAMAGED GAS SERVICE LINE MARKED CORRECTLY. CONTRACTOR DAMAGED SERVICE LINE WHILE DIGGING WITH AN EXCAVATOR. USA VALID.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2025-08-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 302 |  | 1 |  | NATIVESCAPES INC | BIG BEAR CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with pickaxe.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2025-08-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 645 |  | 2 |  | GORDON EQUIPMENT SERVICES | BIG BEAR CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with mini excavator.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2025-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 441 |  | 2 |  | J O''S PLUMBING | BIG BEAR LAKE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with shovel.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2025-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 731 |  | 0 |  | BEAVER CONSTRUCTION | BIG BEAR LAKE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR DAMAGED SERVICE LINE. PINHOLE LEAK AT BOTTOM OF PIPE DAMAGED WHILE EXCAVATING WITH A SHOVEL AND REPAIRING WATER LINE.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2025-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 569 |  | 2 |  | GILLIGAN CONSTRUCTION COMPANY | BIG BEAR LAKE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | Contractor damaged service while digging
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2025-06-23 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 674 |  | 1 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR DAMAGED GAS SERVICE LINE MARKED CORRECTLY. CONTRACTOR DAMAGED SERVICE LINE WHILE DIGGING WITH A SHOVEL. USA DIG TICKET IS VALID.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2025-04-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 199 |  | 1 |  | GMG INDUSTRIES LLC | BIG BEAR CITY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | SERVICE LINE HIT WITH AN EXCAVATOR.
Southwest Gas Company | N | SAN BERNARDINO | FAWNSKIN | 2025-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 418 |  | 2 |  | SOWRY CONSTRUCTION | BIG BEAR CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR DAMAGED SERVICE LINE WHILE DIGGING WITH A MINI-X.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 630 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CUSTOMER DAMAGED SERVICE WITH JACK HAMMER WHILE TRENCHING FOR IRRIGATION. NO USA.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 510 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1614 |  | 1 |  | SBLA CONSTRUCTION & REMODELING INC | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR DAMAGES A SERVICE WITH AUGER. NO USA TICKET.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 647 |  | 1 |  | JOSE LENA | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | UNLICENSED CONTRACTORS HIRED BY OWER OF PROPERTY DAMAGED A SERVICE LINE HIT WITH POST HOLE DIGGER WHILE INSTALLING A FENCE. NO USA.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1220 |  | 4 |  | ABSOLUTE PUMPING | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service line with shovel.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 464 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 470 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | Yes | No | Yes | Yes | No | No | No | Homeowner damaged service line with shovel.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1559 |  | 1 |  | RED OAK ROOTER | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service line with shovel.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-11-24 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 1 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2783 |  | 16 |  | DCR COMMUINICATIONS | COACHELLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged main with bore machine.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 899 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SERVICE WAS HIT WITH SHOVEL BY HOME OWNER WITH NO USA.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 413 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | HOME OWNER DAMAGED A GAS SERVICE WITH A SHOVLE WHILE INSTALLING ELEC CONDUIT. EXPIRED USA.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 463 |  | 1 |  | RAPID PLUMBING | INGLEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with mini excavator.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 559 |  | 1 |  | RAPID PLUMBING | INGLEWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with excavator.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-04-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1790 |  | 0 |  | RM BACKHOE | ORANGE | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | A CONTRACTOR DAMAGED A MAIN WITH AN MINI EXCAVATOR. NO USA.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 528 |  | 1 |  | GREEN VALLEY LANDSCAPE DEVELOPMENT INC. | HESPERIA | CA | N | Y | Yes | No | Yes | Yes | No | No | No | Contractor damaged service with shovel
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 665 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service with shovel.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-09-11 | Third party excavation damage | Main | Steel | Hand Tools | 4 | 250 | 240 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | CEM CORPORATION | MONTEBELLO | CA | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Contractor damaged main with shovel.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1090 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line with dig bar.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2025-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1129 |  | 0 |  | TBU INC. | BEAUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit main while digging with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | LUCERNE VALLEY | 2025-09-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1231 |  | 1 |  | OCCUPANT | LUCERNE VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged service with pickaxe.
Southwest Gas Company | N | SAN BERNARDINO | OAK HILLS | 2025-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 754 |  | 1 |  | OCCUPANT | OAK HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner damaged service with trencher.
Southwest Gas Company | N | SAN BERNARDINO | OAK HILLS | 2025-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1036 |  | 1 |  | OCCUPANT | OAK HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service line with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2025-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 507 |  | 2 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged service line with post hole digger.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2025-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 828 |  | 2 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service line with post hole digger.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2025-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1503 |  | 2 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service with digging bar
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2025-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 651 |  | 1 |  | REY ESPARZA | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with digging bar.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2025-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 841 |  | 1 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service line.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2025-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 740 |  | 2 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HOMEOWNER DAMAGED SERVICE LINE WHILE USING AUGER WITH NO VALID DIG TICKET.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2025-12-03 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 470 |  | 0 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Stub damaged with compaction equipment.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2025-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 703 |  | 3 |  | DM CONTRACTING INC. | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while removing roots with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2025-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 617 |  | 0 |  | DM CONTRACTING INC. | COLTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with backhoe.