## 2023 Data Set
Index | Utility Name | Fire Start |  | Location |  |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations
|  | Date | Time | Latitude | Longitude | Material at Origin | Material at Origin - Comments | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Notes
20230010N | PG&E | 2023-01-01 | 5:44 | 37.9553 | -122.5357 | Building | N/A | Urban | Structure Only | Fire Agency | Kentfield FD | 107769507 | No | 750 | Splice/Clamp/Connector | Overhead | Yes | 2023-01-01 | 5:33 | Equipment/Facility Failure | Splice/Clamp/Connector | N/A | N/A | N/A
20230009 | PG&E | 2023-01-04 | 18:17 | 37.9187 | -122.6943 | Building | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Bolinas FD | 102248332 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-01-04 | 16:55 | Other | N/A | N/A | N/A | N/A
20230011 | PG&E | 2023-01-05 | 19:42 | 37.8164 | -120.6987 | Vegetation | N/A | Hardwood Forest | Less Than .25 Acres | Fire Agency | Satinslaus Consolidated FD | 102333795 | No | 750 | Service Drop | Overhead | Yes | 2023-01-05 | 19:25 | Contact From Object | N/A | Vegetation | Service Drop | Outside Force
20230015 | PG&E | 2023-01-07 | 23:31 | 37.682 | -122.1121 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Self Extinguished | N/A | 100910264 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-01-07 | 23:09 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230016 | PG&E | 2023-01-08 | 3:45 | 38.3591 | -121.9143 | Vegetation | N/A | Agriculture | Less than three {3} meters of linear travel | Fire Agency | Solano County FD | 103801970 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-01-07 | 23:58 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230019 | PG&E | 2023-01-08 | 20:19 | 37.9286 | -121.2153 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | STOCKTON FD | 102130206 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-01-07 | 23:40 | Wire-Wire Contact | N/A | N/A | N/A | Weather
20230030 | PG&E | 2023-01-10 | 17:00 | 37.5858 | -122.3864 | Building | N/A | Urban | Structure Only | Fire Agency | Burlingame FD | 100258393 | No | 750 | Unknown | Overhead | No | N/A | N/A | Unknown | N/A | N/A | N/A | N/A
20230072 | PG&E | 2023-01-29 | 15:55 | 39.906 | -122.151 | Vegetation | N/A | Agriculture | Less than three {3} meters of linear travel | Fire Agency | CAL FIRE | 101499081 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-01-29 | 15:26 | Vandalism/Theft | N/A | N/A | N/A | N/A
20230090 | PG&E | 2023-02-08 | 12:32 | 39.3623 | -121.8109 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | CAL FIRE | 100377987 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-02-08 | 12:00 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230095 | PG&E | 2023-02-11 | 13:31 | 38.9983 | -121.8247 | Vegetation | N/A | Water | Less Than .25 Acres | Fire Agency | GRIMES FD | 101647984 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-02-11 | 13:28 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230100 | PG&E | 2023-02-13 | 10:53 | 38.1184 | -122.6463 | Vegetation | N/A | Herbaceous | Less than three {3} meters of linear travel | Fire Agency | Novato FD | 102222744 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-02-13 | 10:44 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230108 | PG&E | 2023-02-15 | 18:18 | 37.9216 | -122.0327 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Contra Costa County FD | 103885751 | Yes | 750 | Transformer | Overhead | Yes | 2023-02-15 | 18:14 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20230113 | PG&E | 2023-02-17 | 12:48 | 37.1574 | -122.1332 | Vegetation | N/A | Hardwood Woodland | Less than three {3} meters of linear travel | Fire Agency | CAL FIRE | 101672598 | Yes | 750 | Conductor - Insulated Secondary | Overhead | Yes | 2023-02-17 | 12:46 | Equipment/Facility Failure | Conductor - Insulated Secondary | N/A | N/A | N/A
20230127 | PG&E | 2023-02-21 | 14:25 | 37.5094 | -122.4036 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 103982239 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-02-21 | 13:33 | Contact From Object | N/A | Other | Conductor - Primary | Weather
20230138 | PG&E | 2023-02-21 | 19:17 | 36.5573 | -119.4872 | Building | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Fresno FD | 100890774 | Yes | 12000 | Transformer | Overhead | Yes | 2023-02-21 | 18:11 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20230128 | PG&E | 2023-02-21 | 14:28 | 37.3925 | -122.0249 | Other | Crossarm | Urban | Less than three {3} meters of linear travel | Fire Agency | Sunnyvale FD | 100515055 | Yes | 750 | Crossarm | Overhead | Yes | 2023-02-21 | 14:19 | Equipment/Facility Failure | Crossarm | N/A | N/A | N/A
20230129 | PG&E | 2023-02-21 | 12:08 | 37.6095 | -122.4568 | Vegetation | N/A | Shrub | .26 - 9.99 Acres | Fire Agency | San Bruno FD,CALFire | 100283380 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-02-21 | 11:50 | Other | N/A | N/A | N/A | N/A
20230132 | PG&E | 2023-02-21 | 15:45 | 37.2018 | -120.8439 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 101233140 | Yes | 12000 | Pole | Overhead | Yes | 2023-02-21 | 15:13 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20230135 | PG&E | 2023-02-21 | 11:33 | 39.3139 | -123.7433 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 102188209 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-02-21 | 11:30 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230140 | PG&E | 2023-02-21 | 13:21 | 38.4829 | -123.0009 | Vegetation | N/A | Conifer Forest | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101975840 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-02-21 | 13:12 | Contact From Object | N/A | Other | Conductor - Primary | Weather
20230126 | PG&E | 2023-02-21 | 14:56 | 39.2087 | -121.0609 | Other | Com line | Urban | Less Than .25 Acres | Customer | N/A | 103774732 | Yes | 750 | Conductor - Secondary | Overhead | Yes | 2023-02-21 | 14:52 | Other | N/A | N/A | N/A | N/A
20230148 | PG&E | 2023-02-21 | 14:03 | 38.5296 | -123.204 | Vegetation | N/A | Hardwood Woodland | .26 - 9.99 Acres | Fire Agency | North Bay FD,CAL FIRE | 102022139 | No | 12000 | Jumper | Overhead | Yes | 2023-02-21 | 13:25 | Equipment/Facility Failure | Jumper | N/A | N/A | N/A
20230155 | PG&E | 2023-02-23 | 17:07 | 39.4438 | -122.1897 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | Fed fire service. Wildlife refuge | 100332814 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-02-23 | 17:02 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230154 | PG&E | 2023-02-23 | 11:44 | 40.4985 | -122.3191 | Vegetation | N/A | Agriculture | Less than three {3} meters of linear travel | Self Extinguished | N/A | 101494143, 101494163, 101494139 | Yes | 12000 | Pole | Overhead | Yes | 2023-02-23 | 12:01 | Contact From Object | N/A | Vehicle | Pole | Human Error
20230177N | PG&E | 2023-02-27 | 22:42 | 37.6512 | -122.4563 | Other | Switch , Transformer | Urban | Less than three {3} meters of linear travel | Fire Agency | South San Francisco FD | 107385796 | No | 12000 | Transformer | Subsurface | Yes | 2023-02-27 | 22:39 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20230173 | PG&E | 2023-03-01 | 4:22 | 35.3711 | -118.9608 | Other | Service Drop | Urban | Less Than .25 Acres | Fire Agency | Kern County FD | 100216340 | Yes | 750 | Service Drop | Overhead | No | N/A | N/A | Contact From Object | N/A | Other | Service Drop | Weather
20230175 | PG&E | 2023-03-01 | 14:05 | 38.5214 | -122.548 | Vegetation | N/A | Hardwood Forest | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102269979 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2023-03-01 | 13:44 | Other | N/A | N/A | N/A | N/A
20230191 | PG&E | 2023-03-09 | 10:57 | 38.0038 | -121.8139 | Other | Conductor | Urban | Less than three {3} meters of linear travel | Fire Agency | Contra Costa County FD | 107922053 | No | 750 | Conductor - Insulated Secondary | Subsurface | Yes | 2023-03-09 | 11:19 | Equipment/Facility Failure | Conductor - Insulated Secondary | N/A | N/A | N/A
20230231N | PG&E | 2023-03-25 | 15:51 | 38.5937 | -123.3444 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 102037920 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-03-25 | 15:48 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230255 | PG&E | 2023-04-03 | 16:51 | 35.5029 | -119.287 | Building | N/A | Urban | Structure Only | Fire Agency | Kern County FD | 100209786 | No | 750 | Service Drop | Overhead | Yes | 2023-04-03 | 16:49 | Contact From Object | N/A | Other | Service Drop | Other
20230257 | PG&E | 2023-04-04 | 13:13 | 36.5694 | -121.9311 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | Cypress FD | 101776506 | No | 21000 | Grounding Wire | Overhead | Yes | 2023-04-04 | 13:11 | Contact From Object | N/A | Vegetation | Grounding Wire | Outside Force
20230259 | PG&E | 2023-04-06 | 11:35 | 35.4619 | -120.7872 | Building | N/A | Hardwood Woodland | Less Than .25 Acres | Customer | N/A | 101882614 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-04-06 | 11:33 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230260 | PG&E | 2023-04-06 | 18:56 | 38.1611 | -121.9727 | Other | Bird | Wetland | Less Than .25 Acres | Fire Agency | Suisun FPD | 101560186 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-04-06 | 18:51 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230267 | PG&E | 2023-04-09 | 17:50 | 38.3701 | -121.9934 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Vacaville | 101597556 | Yes | 12000 | Splice/Clamp/Connector | Overhead | Yes | 2023-04-09 | 17:35 | Contact From Object | N/A | Vegetation | Splice/Clamp/Connector | Outside Force
20230272N | PG&E | 2023-04-11 | 10:12 | 38.5061 | -122.3546 | Vegetation | N/A | Hardwood Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 103955988, 103854026 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2023-04-11 | 9:56 | Contact From Object | N/A | Other | Conductor - Primary | Human Error
20230317N | PG&E | 2023-04-12 | 17:08 | 40.7995 | -124.1969 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Samoa FD | 100968938 | No | 12000 | Switch | Overhead | Yes | 2023-04-12 | 17:01 | Equipment/Facility Failure | Switch | N/A | N/A | N/A
20230279 | PG&E | 2023-04-16 | 17:18 | 38.3896 | -123.0837 | Other | Transformer Fault Tamer | Herbaceous | Less Than .25 Acres | Fire Agency | Sonoma Co Fire | 101974232 | Yes | 12000 | Fault Tamer | Overhead | Yes | 2023-04-16 | 17:10 | Equipment/Facility Failure | Fault Tamer | N/A | N/A | N/A
20230282 | PG&E | 2023-04-17 | 17:53 | 38.5502 | -122.5239 | Other | Conductor | Conifer Forest | Less than three {3} meters of linear travel | Fire Agency | Cal fire | 103900419 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-04-17 | 17:46 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230293 | PG&E | 2023-04-20 | 12:02 | 38.6316 | -122.8925 | Other | Conductor | Conifer Forest | Less Than .25 Acres | Fire Agency | HEALDSBURG FIRE DEPT. | 101971228 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-04-20 | 19:40 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230308 | PG&E | 2023-04-24 | 20:54 | 39.1794 | -122.1229 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Williams fd | 101644417; 101626141; 101644415; 101626143 | No | 12000 | Pole | Overhead | Yes | 2023-04-24 | 20:43 | Contact From Object | N/A | Vehicle | Pole | Human Error
20230311 | PG&E | 2023-04-24 | 10:56 | 37.7255 | -120.9482 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Modesto Fire | 102327251 | Yes | 17000 | Conductor - Primary | Overhead | Yes | 2023-04-24 | 10:24 | Contact From Object | N/A | Vegetation | Conductor - Primary | Human Error
20230313 | PG&E | 2023-04-25 | 23:05 | 37.6486 | -122.138 | Other | Pole | Urban | Less Than .25 Acres | Fire Agency | Hayward FD | 102345543 | Yes | 12000 | Pothead | Overhead | Yes | 2023-04-25 | 22:46 | Equipment/Facility Failure | Pothead | N/A | N/A | N/A
20230324 | PG&E | 2023-04-26 | 16:48 | 35.4908 | -119.1539 | Other | Pole | Urban | .26 - 9.99 Acres | Fire Agency | KCFD | 103883757, 103138933 | No | 12000 | Pole | Overhead | Yes | 2023-04-26 | 16:29 | Contact From Object | N/A | Vehicle | Pole | Human Error
20230330 | PG&E | 2023-04-28 | 11:04 | 39.0295 | -122.6715 | Vegetation | N/A | Barren/Other | Less Than .25 Acres | Fire Agency | CAL FIRE | 40861866 | No | 115000 | Conductor - Transmission | Overhead | No | N/A | N/A | Contact From Object | N/A | Animal | Conductor - Transmission | Outside Force
20230331 | PG&E | 2023-04-29 | 9:55 | 37.7573 | -122.4751 | Other | Fence | Urban | Less than three {3} meters of linear travel | Customer | N/A | 101807983 | Yes | 4160 | Connector | Overhead | Yes | 2023-04-29 | 9:52 | Equipment/Facility Failure | Connector | N/A | N/A | N/A
20230333 | PG&E | 2023-04-30 | 13:22 | 38.5182 | -121.742 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | UC Davis FD | 101650681 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-04-30 | 13:14 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230335 | PG&E | 2023-04-30 | 13:18 | 35.3474 | -119.0117 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Bakersfield Fire Dept Station 6 | 100154918; 100244320 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2023-04-30 | 13:10 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20230341 | PG&E | 2023-05-01 | 15:15 | 35.5177 | -119.7903 | Vegetation | N/A | Herbaceous | 10 - 99 Acres | Fire Agency | Kern County Fire Station 26 | 100236631 | No | 12000 | Insulator | Overhead | Yes | 2023-05-01 | 15:13 | Equipment/Facility Failure | Insulator | N/A | N/A | N/A
20230371 | PG&E | 2023-05-09 | 12:22 | 36.8208 | -120.7286 | Other | Pole | Agriculture | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101170969 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-05-09 | 10:26 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230386 | PG&E | 2023-05-13 | 12:27 | 36.6055 | -119.7166 | Other | Transformer | Agriculture | Less Than .25 Acres | Utility | N/A | 100801039 | Yes | 12000 | Transformer | Overhead | Yes | 2023-05-13 | 12:20 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20230388 | PG&E | 2023-05-13 | 9:43 | 34.8901 | -120.3192 | Other | Transformer | Herbaceous | Less than three {3} meters of linear travel | Self Extinguished | N/A | 101861998 | No | 12000 | Transformer | Overhead | Yes | 2023-05-13 | 9:40 | Contact From Object | N/A | Animal | Transformer | Outside Force
20230390 | PG&E | 2023-05-14 | 8:57 | 38.0107 | -122.5364 | Other | Transformer | Urban | Less Than .25 Acres | Fire Agency | San Rafael FD | 102247918 | Yes | 12000 | Transformer Bushing | Overhead | Yes | 2023-05-14 | 8:49 | Contact From Object | N/A | Animal | Transformer Bushing | Outside Force
20230394 | PG&E | 2023-05-14 | 8:54 | 35.6007 | -119.6842 | Other | Jumper | Herbaceous | .26 - 9.99 Acres | Fire Agency | Kern County FD | 103916793 | No | 21000 | Jumper | Overhead | No | N/A | N/A | Contact From Object | N/A | Animal | Jumper | Outside Force
20230396N | PG&E | 2023-05-16 | 14:27 | 36.6045 | -119.642 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Customer | N/A | 100826090 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-05-16 | 14:13 | Contact From Object | N/A | Other | Conductor - Primary | Other
20230399 | PG&E | 2023-05-17 | 15:09 | 36.454 | -121.7151 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 101694770; 101775267 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-05-17 | 15:06 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230401 | PG&E | 2023-05-17 | 15:13 | 38.2234 | -122.2229 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Napa County | 102278134 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-05-17 | 15:10 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20230410N | PG&E | 2023-05-18 | 16:21 | 38.3687 | -121.9778 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Unknown FD | 101663597 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-05-18 | 16:14 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20230409 | PG&E | 2023-05-19 | 3:40 | 36.6708 | -119.7334 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 100793168 | No | 12000 | Transformer | Overhead | Yes | 2023-05-19 | 4:23 | Contact From Object | N/A | Vehicle | Transformer | Human Error
20230412 | PG&E | 2023-05-19 | 13:47 | 38.2601 | -122.0924 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Self Extinguished | N/A | 104026966 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-05-19 | 13:58 | Wire-Wire Contact | N/A | N/A | N/A | Weather
20230417 | PG&E | 2023-05-20 | 16:05 | 35.5982 | -120.8084 | Vegetation | N/A | Herbaceous | Less than three {3} meters of linear travel | Fire Agency | CAL FIRE | 101859931 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-05-20 | 16:04 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230415 | PG&E | 2023-05-20 | 16:27 | 37.7795 | -120.8523 | Vegetation | N/A | Agriculture | .26 - 9.99 Acres | Fire Agency | City of Modesto FD | 102337942 | No | 17000 | Conductor - Primary | Overhead | Yes | 2023-05-20 | 16:17 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230424 | PG&E | 2023-05-23 | 20:21 | 37.4339 | -120.0973 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | CAL FIRE | 101069706 | No | 240 | Compression Connector | Overhead | Yes | 2023-05-23 | 20:17 | Equipment/Facility Failure | Compression Connector | N/A | N/A | N/A
20230427 | PG&E | 2023-05-23 | 13:54 | 36.6188 | -119.6493 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Unknown | N/A | 100841894 | No | 12000 | Transformer Bushing | Overhead | Yes | 2023-05-23 | 13:53 | Equipment/Facility Failure | Transformer Bushing | N/A | N/A | N/A
20230430 | PG&E | 2023-05-25 | 18:03 | 37.3171 | -121.1648 | Vegetation | N/A | Herbaceous | 10 - 99 Acres | Fire Agency | NEWMAN CAL FIRE | 40856800 | No | 115000 | Guy/Span Wire | Overhead | Yes | 2023-05-25 | 18:03 | Contact From Object | N/A | Animal | Guy/Span Wire | Outside Force
20230440 | PG&E | 2023-05-28 | 9:04 | 37.8519 | -120.1648 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | Cal fire | 103354813 | Yes | 17000 | Fuse | Overhead | Yes | 2023-05-28 | 8:58 | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20230480N | PG&E | 2023-05-28 | 13:29 | 38.5405 | -122.7896 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Unknown FD | 101962255 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-05-28 | 9:13 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230439 | PG&E | 2023-05-28 | 10:31 | 34.62 | -120.2113 | Vegetation | N/A | Herbaceous | Less than three {3} meters of linear travel | Fire Agency | SANTA BARBARA COUNTY FIRE | 101876039 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-05-28 | 10:25 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230447N | PG&E | 2023-05-28 | 13:28 | 35.8718 | -119.9155 | Other | Bird | Herbaceous | .26 - 9.99 Acres | Unknown | N/A | 40662545 | No | 70000 | Insulator | Overhead | Yes | 2023-05-28 | 13:28 | Contact From Object | N/A | Animal | Insulator | Outside Force
20230448N | PG&E | 2023-05-28 | 8:54 | 35.1236 | -119.1096 | Vegetation | N/A | Urban | Less Than .25 Acres | Unknown | N/A | 40832212 | No | 70000 | Conductor - Transmission | Overhead | No | N/A | N/A | Equipment/Facility Failure | Conductor - Transmission | N/A | N/A | N/A
20230443 | PG&E | 2023-05-29 | 15:10 | 37.0242 | -120.0796 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101110934 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-05-29 | 15:09 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230453 | PG&E | 2023-05-31 | 17:05 | 36.8044 | -119.5195 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Fresno County FD | 100727902 | Yes | 240 | Service Drop | Overhead | Yes | 2023-05-31 | 17:03 | Contact From Object | N/A | Vehicle | Service Drop | Human Error
20230474N | PG&E | 2023-06-02 | 9:31 | 37.9979 | -121.89 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Unknown FD | 100451928 | Yes | 21000 | Transformer | Overhead | Yes | 2023-06-02 | 9:28 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20230465 | PG&E | 2023-06-04 | 14:35 | 38.1601 | -122.2183 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | American Canyon fire dept/Vallejo FD | 102260391 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-04 | 14:31 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230468N | PG&E | 2023-06-04 | 16:40 | 36.4745 | -121.3318 | Vegetation | N/A | Herbaceous | 10 - 99 Acres | Fire Agency | CAL FIRE | 40658922, 40752793, 40752796 | No | 115000 | Insulator | Overhead | No | N/A | N/A | Contact From Object | N/A | Other | Insulator | Other
20230472N | PG&E | 2023-06-04 | 8:03 | 36.4553 | -121.3318 | Other | Balloon | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 103006689 | Yes | 21000 | Unknown | Overhead | No | N/A | N/A | Contact From Object | N/A | Balloon | Unknown | Outside Force
20230470 | PG&E | 2023-06-05 | 17:41 | 35.0258 | -119.3485 | Vegetation | N/A | Desert Shrub | 10 - 99 Acres | Fire Agency | Kern county fire dept | 1.0019e+17 | No | 12000 | Insulator | Overhead | Yes | 2023-06-05 | 17:37 | Equipment/Facility Failure | Insulator | N/A | N/A | N/A
20230476 | PG&E | 2023-06-06 | 19:06 | 35.2062 | -119.7062 | Other | Pole | Shrub | Less Than .25 Acres | Utility | N/A | 100166370 | No | 21000 | Pole | Overhead | Yes | 2023-06-06 | 12:29 | Other | N/A | N/A | N/A | N/A
20230482 | PG&E | 2023-06-07 | 16:12 | 35.9503 | -120.098 | Vegetation | N/A | Agriculture | .26 - 9.99 Acres | Fire Agency | Kings county | 104154186 | No | 21000 | Lightning Arrestor | Overhead | Yes | 2023-06-07 | 15:50 | Contamination | N/A | N/A | N/A | N/A
20230487N | PG&E | 2023-06-08 | 14:19 | 39.1422 | -121.3226 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 40824541 | No | 60000 | Conductor - Transmission | Overhead | Yes | 2023-06-08 | 14:19 | Equipment/Facility Failure | Conductor - Transmission | N/A | N/A | N/A
20230492 | PG&E | 2023-06-09 | 20:18 | 37.9037 | -121.6973 | Other | Bird | Urban | .26 - 9.99 Acres | Fire Agency | Cc Fire | 44190941, 100485260 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2023-06-09 | 20:10 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230495 | PG&E | 2023-06-10 | 13:54 | 38.9707 | -121.4498 | Vegetation | N/A | Agriculture | .26 - 9.99 Acres | Fire Agency | Wheatland FD | 104186876 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-10 | 14:34 | Contact From Object | N/A | Vegetation | Conductor - Primary | Human Error
20230496 | PG&E | 2023-06-11 | 2:31 | 35.3624 | -119.682 | Vegetation | N/A | Desert Shrub | Less Than .25 Acres | Utility | N/A | 100232474 | Yes | 12000 | Automatic Wire Splice | Overhead | Yes | 2023-06-11 | 2:21 | Equipment/Facility Failure | Automatic Wire Splice | N/A | N/A | N/A
20230501 | PG&E | 2023-06-11 | 16:54 | 36.7481 | -119.6103 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Fresno County FD | 100739067 | No | 750 | Conductor - Primary | Overhead | No | N/A | N/A | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230504N | PG&E | 2023-06-11 | 15:10 | 37.0999 | -120.8783 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Los Banos FD | 101181113 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-11 | 15:09 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20230500 | PG&E | 2023-06-11 | 20:37 | 37.4247 | -121.9217 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | San Jose FD | 100560625 | Yes | 21000 | Switch | Overhead | Yes | 2023-06-11 | 20:06 | Contact From Object | N/A | Animal | Switch | Outside Force
20230502 | PG&E | 2023-06-11 | 20:25 | 37.4218 | -121.9339 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | San Jose FD | 103449887 | No | 21000 | Switch | Overhead | Yes | 2023-06-11 | 20:06 | Equipment/Facility Failure | Switch | N/A | N/A | N/A
20230503N | PG&E | 2023-06-11 | 13:54 | 37.8711 | -122.0822 | Vegetation | N/A | Hardwood Woodland | .26 - 9.99 Acres | Fire Agency | Contra Costa County FD | 100491910 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-11 | 14:30 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230507 | PG&E | 2023-06-12 | 15:58 | 38.8675 | -121.3008 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | LINCOLN FD | 103685765 | No | 21000 | Switch | Overhead | Yes | 2023-06-12 | 15:54 | Contact From Object | N/A | Animal | Switch | Outside Force
20230671N | PG&E | 2023-06-14 | 18:02 | 37.4899 | -122.2144 | Vegetation | N/A | Urban | Less Than .25 Acres | Utility | N/A | 104176068 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-14 | 18:06 | Other | N/A | N/A | N/A | N/A
20230525 | PG&E | 2023-06-15 | 12:30 | 36.141 | -119.5648 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Kings County FD | 103938525 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-15 | 13:36 | Contact From Object | N/A | Other | Conductor - Primary | Other
20230524 | PG&E | 2023-06-15 | 14:33 | 35.6593 | -120.6521 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | CAL FIRE & CITY PASO ROBLES | 101867432 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-15 | 14:38 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230523 | PG&E | 2023-06-16 | 1:27 | 39.9415 | -122.0415 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | CAL FIRE | 101498581 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-16 | 1:10 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230530 | PG&E | 2023-06-16 | 2:10 | 37.8708 | -121.7408 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Contra Costa County FD | 104051753 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2023-06-16 | 1:46 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20230532 | PG&E | 2023-06-16 | 18:20 | 36.7213 | -119.7545 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Fresno FD | 103299980 | No | 12000 | Transformer | Overhead | Yes | 2023-06-16 | 18:18 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20230535 | PG&E | 2023-06-17 | 10:26 | 37.1054 | -120.2248 | Vegetation | N/A | Agriculture | Less than three {3} meters of linear travel | Fire Agency | Chow fire | 101129264 | No | 12000 | Pole | Overhead | Yes | 2023-06-17 | 10:15 | Contact From Object | N/A | Vehicle | Pole | Human Error
20230538 | PG&E | 2023-06-17 | 18:05 | 36.981 | -119.8929 | Vegetation | N/A | Herbaceous | Less than three {3} meters of linear travel | Fire Agency | CAL FIRE | 101214803 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-17 | 18:04 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230551N | PG&E | 2023-06-17 | 15:17 | 37.3778 | -121.8057 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Unknown FD | 100564319 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2023-06-17 | 15:12 | Equipment/Facility Failure | Conductor - Open Wire Secondary | N/A | N/A | N/A
20230541 | PG&E | 2023-06-18 | 16:18 | 36.2375 | -120.3158 | Vegetation | N/A | Desert Shrub | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100743546 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-18 | 15:58 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230545 | PG&E | 2023-06-18 | 13:20 | 36.9226 | -119.8721 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Madera County FD | 101124706 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-18 | 13:11 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230542 | PG&E | 2023-06-18 | 14:37 | 38.5643 | -121.6416 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | DAVIS FIRE DEPARTMENT | 103695376 | No | 12000 | Automatic Wire Splice | Overhead | Yes | 2023-06-18 | 14:21 | Equipment/Facility Failure | Automatic Wire Splice | N/A | N/A | N/A
20230544 | PG&E | 2023-06-18 | 22:05 | 38.8354 | -121.1824 | Vegetation | N/A | Urban | .26 - 9.99 Acres | Fire Agency | Placer county fire dept | 100052373 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-18 | 21:58 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230546 | PG&E | 2023-06-18 | 14:25 | 38.4638 | -122.814 | Vegetation | N/A | Urban | .26 - 9.99 Acres | Fire Agency | Santa Rosa fire | 102017957 | Yes | 750 | Conductor - Racked Secondary | Overhead | Yes | 2023-06-18 | 14:23 | Contact From Object | N/A | Other | Conductor - Racked Secondary | Weather
20230547 | PG&E | 2023-06-19 | 11:44 | 39.3436 | -121.73 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Self Extinguished | N/A | 100411087 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-19 | 11:38 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230554 | PG&E | 2023-06-20 | 20:50 | 38.6796 | -122.9488 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | CAL FIRE | 102033013 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-20 | 20:38 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230553 | PG&E | 2023-06-20 | 8:27 | 37.285 | -120.316 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101140137 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-20 | 8:25 | Contact From Object | N/A | Other | Conductor - Primary | Other
20230555 | PG&E | 2023-06-21 | 3:27 | 36.9839 | -121.4992 | Other | Conductor | Agriculture | Less Than .25 Acres | Fire Agency | CAL FIRE | 100614558 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-06-21 | 3:20 | Contact From Object | N/A | Other | Conductor - Primary | Other
20230560 | PG&E | 2023-06-21 | 15:05 | 39.3517 | -123.8123 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 102180950 | Yes | 12000 | Capacitor Bank | Overhead | Yes | 2023-06-21 | 15:39 | Equipment/Facility Failure | Capacitor Bank | N/A | N/A | N/A
20230570N | PG&E | 2023-06-21 | 12:48 | 37.9566 | -121.696 | Vegetation | N/A | Herbaceous | Less than three {3} meters of linear travel | Unknown | N/A | 100471541 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2023-06-21 | 12:44 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20230565 | PG&E | 2023-06-22 | 16:22 | 37.9876 | -121.0523 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Fire department | 102120282 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-22 | 15:53 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230562 | PG&E | 2023-06-22 | 10:57 | 37.2025 | -120.4716 | Other | Conductor | Agriculture | .26 - 9.99 Acres | Utility | N/A | 101155176 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-22 | 10:52 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20230574 | PG&E | 2023-06-23 | 15:03 | 38.2044 | -122.5543 | Other | Conductor | Agriculture | Less Than .25 Acres | Fire Agency | CAL FIRE | 102006354 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-23 | 14:15 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20230577 | PG&E | 2023-06-24 | 15:27 | 37.958 | -121.9491 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Contra Costa County | 103886020 | No | 21000 | Switch | Overhead | Yes | 2023-06-24 | 15:22 | Contact From Object | N/A | Balloon | Switch | Outside Force
20230595 | PG&E | 2023-06-26 | 12:23 | 38.0821 | -122.6855 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Marin county fire | 103056030, 102229118 | No | 12000 | Transformer | Overhead | Yes | 2023-06-26 | 12:06 | Contact From Object | N/A | Animal | Transformer | Outside Force
20231294N | PG&E | 2023-06-26 | 12:23 | 38.0816 | -122.7016 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | Marin County FD | 102229118 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-11-26 | 12:06 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230590 | PG&E | 2023-06-26 | 8:42 | 39.3207 | -121.5742 | Other | Bird Possibly - Not found | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 100425524 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-26 | 8:35 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230591 | PG&E | 2023-06-26 | 10:47 | 37.1063 | -120.239 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Chowchilla | 101129576 | No | 12000 | Lightning Arrestor | Overhead | Yes | 2023-06-26 | 10:42 | Contact From Object | N/A | Animal | Lightning Arrestor | Outside Force
20230599 | PG&E | 2023-06-27 | 13:42 | 40.123 | -123.9695 | Vegetation | N/A | Hardwood Forest | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103319288 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-27 | 13:35 | Contact From Object | N/A | Vegetation | Conductor - Primary | Human Error
20230601 | PG&E | 2023-06-27 | 12:16 | 35.3197 | -119.0095 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Bakersfield FD | 100254869 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-06-27 | 12:12 | Contact From Object | N/A | Other | Conductor - Primary | Other
20230605N | PG&E | 2023-06-27 | 16:48 | 37.7557 | -122.4872 | Building | N/A | Urban | Less Than .25 Acres | Fire Agency | San Francisco FD | 101808077 | Yes | 750 | Conductor - Secondary | Overhead | Yes | 2023-06-27 | 16:30 | Equipment/Facility Failure | Conductor - Secondary | N/A | N/A | N/A
20230608 | PG&E | 2023-06-29 | 15:30 | 37.9447 | -120.8435 | Vegetation | N/A | Herbaceous | 10 - 99 Acres | Fire Agency | CAL FIRE | 104057219 | No | 17000 | Conductor - Primary | Overhead | Yes | 2023-06-29 | 16:00 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20230611N | PG&E | 2023-06-29 | 20:00 | 39.0256 | -122.9209 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Lakeport FD | 102165984 | No | 750 | Service Drop | Overhead | Yes | 2023-07-29 | 17:59 | Contact From Object | N/A | Vegetation | Service Drop | Outside Force
20230606 | PG&E | 2023-06-29 | 16:01 | 37.9922 | -121.1871 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Unknown FD | 103196196 | Yes | 12000 | Transformer | Overhead | Yes | 2023-06-29 | 15:58 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20230609 | PG&E | 2023-06-29 | 15:56 | 38.438 | -121.7472 | Other | Pole | Agriculture | Less than three {3} meters of linear travel | Fire Agency | dixon fire co | 101576900 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-06-29 | 15:49 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230613 | PG&E | 2023-06-30 | 14:42 | 37.9946 | -121.8992 | Other | Transformer | Urban | Less than three {3} meters of linear travel | Fire Agency | Contra Costa Fire dept | 107914951 | No | 12000 | Transformer | Subsurface | Yes | 2023-06-30 | 14:45 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20230614 | PG&E | 2023-06-30 | 19:45 | 38.9118 | -121.217 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Placer County FD | 100047712 | Yes | 240 | Service Drop | Overhead | Yes | 2023-06-30 | 19:30 | Contact From Object | N/A | Vegetation | Service Drop | Outside Force
20230622 | PG&E | 2023-07-01 | 20:22 | 37.7993 | -121.9249 | Other | Switch/J-box | Urban | Less Than .25 Acres | Fire Agency | San Ramon Fire | 42684821 | No | 21000 | Switch | Subsurface | Yes | 2023-07-01 | 19:57 | Equipment/Facility Failure | Switch | N/A | N/A | N/A
20230623N | PG&E | 2023-07-01 | 14:37 | 36.5597 | -119.48 | Other | Pole | Agriculture | Less Than .25 Acres | Fire Agency | Unknown FD | 100891034 | No | 12000 | Transformer | Overhead | Yes | 2023-07-01 | 14:37 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20230625 | PG&E | 2023-07-02 | 13:49 | 35.3675 | -118.9835 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Customer | N/A | 100245670 | No | 750 | Service Drop | Overhead | Yes | 2023-07-02 | 13:48 | Contact From Object | N/A | Vegetation | Service Drop | Outside Force
20230627 | PG&E | 2023-07-02 | 22:12 | 37.9753 | -120.3564 | Vegetation | N/A | Urban | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101044976 , 101044971 | No | 12000 | Automatic Wire Splice | Overhead | Yes | 2023-07-02 | 18:22 | Equipment/Facility Failure | Automatic Wire Splice | N/A | N/A | N/A
20230651N | PG&E | 2023-07-03 | 16:16 | 39.234 | -121.5811 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 101289441 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-03 | 16:07 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230636 | PG&E | 2023-07-04 | 4:40 | 37.9526 | -122.1037 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 103770053 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-07-04 | 3:38 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230632 | PG&E | 2023-07-04 | 10:51 | 36.9222 | -121.674 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Customer | N/A | 101789252 | Yes | 750 | Connector | Overhead | Yes | 2023-07-04 | 10:50 | Equipment/Facility Failure | Connector | N/A | N/A | N/A
20230642 | PG&E | 2023-07-05 | 6:05 | 37.7225 | -120.69 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102336929 | No | 17000 | Conductor - Primary | Overhead | Yes | 2023-07-05 | 5:44 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230647 | PG&E | 2023-07-05 | 15:58 | 38.7446 | -121.439 | Vegetation | N/A | Agriculture | Less than three {3} meters of linear travel | Fire Agency | Placer County FD | 100063446 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-05 | 15:55 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230652 | PG&E | 2023-07-07 | 7:38 | 38.0911 | -121.8754 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | MONTEZUMA FIRE | 101582875 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-07 | 7:30 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230771N | PG&E | 2023-07-07 | 17:47 | 37.6935 | -122.4228 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | North County Fire Authority | 100294944 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-07 | 17:45 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230659 | PG&E | 2023-07-07 | 20:26 | 38.2098 | -120.7691 | Vegetation | N/A | Herbaceous | 10 - 99 Acres | Fire Agency | CAL FIRE | 40904186 | No | 60000 | Pole | Overhead | Yes | 2023-07-07 | 20:26 | Contact From Object | N/A | Vehicle | Pole | Human Error
20230663 | PG&E | 2023-07-08 | 17:27 | 37.8305 | -120.9978 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | ESCALON FIRE DIST | 103170193 | Yes | 17000 | Transformer | Overhead | No | N/A | N/A | Contact From Object | N/A | Animal | Transformer | Outside Force
20230662 | PG&E | 2023-07-08 | 14:44 | 38.7488 | -121.3295 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | CAL FIRE | 100063572 | Yes | 12000 | Riser | Overhead | Yes | 2023-07-08 | 14:29 | Contact From Object | N/A | Balloon | Riser | Outside Force
20230664 | PG&E | 2023-07-08 | 16:09 | 37.3325 | -122.0193 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Santa Clara City FD | 100534805 | Yes | 240 | Conductor - Open Wire Secondary | Overhead | Yes | 2023-07-08 | 16:08 | Contact From Object | N/A | Other | Conductor - Open Wire Secondary | Weather
20230669 | PG&E | 2023-07-09 | 18:21 | 38.3722 | -121.6849 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | Dixon and Davis FD | 101570563 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-09 | 18:07 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230676 | PG&E | 2023-07-10 | 21:27 | 35.8292 | -120.8448 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Utility | N/A | 101942412 | No | 21000 | Transformer | Overhead | Yes | 2023-07-10 | 21:13 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20230673 | PG&E | 2023-07-10 | 11:42 | 38.3467 | -122.4989 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101986773 | Yes | 12000 | Voltage Regulator | Overhead | Yes | 2023-07-10 | 11:34 | Equipment/Facility Failure | Voltage Regulator | N/A | N/A | N/A
20230680 | PG&E | 2023-07-11 | 10:53 | 38.8061 | -121.4513 | Vegetation | N/A | Agriculture | .26 - 9.99 Acres | Fire Agency | Placer County FD | 100059325 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-11 | 10:51 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20230678 | PG&E | 2023-07-11 | 11:20 | 38.8617 | -121.8065 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | KNIGHTS LANDING FD | 101592356 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-11 | 10:50 | Contact From Object | N/A | Other | Conductor - Primary | Human Error
20230683 | PG&E | 2023-07-12 | 9:54 | 35.3671 | -119.4336 | Other | Lightning arrestor | Agriculture | Less than three {3} meters of linear travel | Self Extinguished | N/A | 100116773 | No | 12000 | Lightning Arrestor | Overhead | Yes | 2023-07-12 | 9:33 | Contact From Object | N/A | Animal | Lightning Arrestor | Outside Force
20230685 | PG&E | 2023-07-13 | 6:53 | 38.0672 | -121.0782 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | Linden FD | 103203506 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-07-13 | 6:47 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230691 | PG&E | 2023-07-13 | 19:15 | 36.7922 | -119.6964 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CFD | 103361396 | No | 750 | Connector | Overhead | Yes | 2023-07-13 | 19:13 | Equipment/Facility Failure | Connector | N/A | N/A | N/A
20230694 | PG&E | 2023-07-14 | 12:58 | 36.9566 | -120.0478 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Unknown | N/A | 42150893 | No | 750 | Transformer | Overhead | Yes | 2023-07-14 | 13:55 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20230692 | PG&E | 2023-07-14 | 4:40 | 39.9482 | -123.774 | Vegetation | N/A | Conifer Forest | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100990776 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-14 | 4:30 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230695 | PG&E | 2023-07-14 | 12:22 | 35.3414 | -118.9875 | Vegetation | N/A | Urban | .26 - 9.99 Acres | Fire Agency | Bakersfield FD | 100135512 | Yes | 240 | Conductor - Open Wire Secondary | Overhead | Yes | 2023-07-14 | 12:20 | Contact From Object | N/A | Vegetation | Conductor - Open Wire Secondary | Outside Force
20230693 | PG&E | 2023-07-14 | 10:36 | 38.9312 | -123.6897 | Vegetation | N/A | Herbaceous | Less than three {3} meters of linear travel | Fire Agency | CAL FIRE | 102186685 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-14 | 10:23 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230700 | PG&E | 2023-07-15 | 11:17 | 39.0572 | -120.98 | Vegetation | N/A | Herbaceous | Less than three {3} meters of linear travel | Fire Agency | Placer Hills FD | 100020421 | Yes | 120 | Conductor - Insulated Secondary | Overhead | Yes | 2023-07-15 | 11:15 | Equipment/Facility Failure | Conductor - Insulated Secondary | N/A | N/A | N/A
20230701 | PG&E | 2023-07-15 | 16:47 | 38.3645 | -122.6857 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Rohnert Park FD | 45245228 | Yes | 21000 | Crossarm | Overhead | Yes | 2023-07-15 | 16:40 | Wire-Wire Contact | N/A | N/A | N/A | Weather
20230697 | PG&E | 2023-07-15 | 7:34 | 35.3351 | -118.8965 | Vegetation | N/A | Agriculture | Less than three {3} meters of linear travel | Utility | N/A | 100169338 | Yes | 12000 | Transformer | Overhead | Yes | 2023-07-15 | 7:26 | Contact From Object | N/A | Animal | Transformer | Outside Force
20230699 | PG&E | 2023-07-15 | 18:05 | 35.6213 | -120.6605 | Other | Connector | Urban | Less than three {3} meters of linear travel | Fire Agency | Paso Robles FD | 101912287 | No | 750 | Connector | Overhead | Yes | 2023-07-15 | 18:03 | Equipment/Facility Failure | Connector | N/A | N/A | N/A
20230707N | PG&E | 2023-07-15 | 13:57 | 39.4754 | -121.2432 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 100417355 | No | 12000 | Automatic Wire Splice | Overhead | Yes | 2023-07-15 | 13:53 | Equipment/Facility Failure | Automatic Wire Splice | N/A | N/A | N/A
20230717N | PG&E | 2023-07-15 | 18:49 | 40.0279 | -122.1716 | Vegetation | N/A | Urban | Less Than .25 Acres | Unknown | N/A | 101530319 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-15 | 18:42 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20230714 | PG&E | 2023-07-16 | 14:50 | 37.9729 | -121.323 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Stockton FD | 102057481 | Yes | 240 | Conductor - Insulated Secondary | Overhead | Yes | 2023-07-16 | 14:45 | Contact From Object | N/A | Vegetation | Conductor - Insulated Secondary | Outside Force
20230715 | PG&E | 2023-07-16 | 21:02 | 35.357 | -119.0412 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Bakersfield FD | 100232501 | Yes | 750 | Service Drop | Overhead | Yes | 2023-07-16 | 20:59 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20230709 | PG&E | 2023-07-16 | 10:03 | 35.3646 | -119.0922 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | KCFD | 100201397 | Yes | 21000 | Riser | Overhead | Yes | 2023-07-16 | 9:45 | Equipment/Facility Failure | Riser | N/A | N/A | N/A
20230716 | PG&E | 2023-07-16 | 20:21 | 40.3887 | -122.413 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 101482195 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-16 | 20:19 | Vandalism/Theft | N/A | N/A | N/A | N/A
20230723 | PG&E | 2023-07-17 | 8:50 | 36.044 | -119.4838 | Vegetation | N/A | Agriculture | Less than three {3} meters of linear travel | Unknown | N/A | 100661519 | Yes | 750 | Connector | Overhead | Yes | 2023-07-17 | 12:39 | Equipment/Facility Failure | Connector | N/A | N/A | N/A
20230731 | PG&E | 2023-07-19 | 21:14 | 37.4921 | -120.524 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101196713 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2023-07-19 | 20:46 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230732 | PG&E | 2023-07-19 | 13:42 | 37.28 | -121.9747 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Santa Clara County FD | 100540824 | Yes | 240 | Conductor - Open Wire Secondary | Overhead | Yes | 2023-07-19 | 13:34 | Contact From Object | N/A | Vegetation | Conductor - Open Wire Secondary | Outside Force
20230726 | PG&E | 2023-07-19 | 7:45 | 37.9458 | -122.1057 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 100460095 | No | 240 | Conductor - Racked Secondary | Overhead | Yes | 2023-07-19 | 7:42 | Contact From Object | N/A | Vegetation | Conductor - Racked Secondary | Outside Force
20230737 | PG&E | 2023-07-20 | 18:41 | 38.3151 | -121.8408 | Other | Bird | Agriculture | Less Than .25 Acres | Fire Agency | DIXON F.D. | 101568308 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-20 | 18:38 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230741 | PG&E | 2023-07-21 | 14:46 | 39.3199 | -121.5054 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | Bangor | 100412119 | Yes | 12000 | Other | Overhead | Yes | 2023-07-21 | 14:44 | Contact From Object | N/A | Other | Other | Human Error
20230738 | PG&E | 2023-07-21 | 0:07 | 36.7441 | -119.8102 | Other | Switch | Urban | Less than three {3} meters of linear travel | Self Extinguished | N/A | 100896125 | No | 12000 | Switch | Overhead | Yes | 2023-07-21 | 0:02 | Vandalism/Theft | N/A | N/A | N/A | N/A
20230776N | PG&E | 2023-07-21 | 0:48 | 38.9706 | -121.6722 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Unknown FD | 101326779 | No | 12000 | Pole | Overhead | Yes | 2023-07-21 | 0:40 | Contact From Object | N/A | Vehicle | Pole | Human Error
20230745 | PG&E | 2023-07-22 | 4:49 | 38.026 | -121.3149 | Other | Fence | Urban | Less than three {3} meters of linear travel | Fire Agency | STOCKTON FD | 102139726 | Yes | 12000 | Parallel Groove Clamp | Overhead | Yes | 2023-07-22 | 4:47 | Equipment/Facility Failure | Parallel Groove Clamp | N/A | N/A | N/A
20230752 | PG&E | 2023-07-22 | 15:19 | 40.386 | -122.3145 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101506014 | No | 750 | Tap Clamp | Overhead | Yes | 2023-07-22 | 16:11 | Equipment/Facility Failure | Tap Clamp | N/A | N/A | N/A
20230748 | PG&E | 2023-07-22 | 12:06 | 38.5042 | -122.7599 | Other | Conductor | Urban | Less than three {3} meters of linear travel | Fire Agency | Wikiup | 102027564 | No | 750 | Conductor - Primary | Overhead | Yes | 2023-07-22 | 12:05 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230751 | PG&E | 2023-07-22 | 12:12 | 35.2171 | -119.3884 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 100228394 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-22 | 12:09 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230758 | PG&E | 2023-07-23 | 15:51 | 35.3673 | -118.9637 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Bakersfield FD | 100216012 | Yes | 240 | Conductor - Open Wire Secondary | Overhead | Yes | 2023-07-23 | 16:34 | Equipment/Facility Failure | Conductor - Open Wire Secondary | N/A | N/A | N/A
20230755 | PG&E | 2023-07-23 | 10:36 | 37.1685 | -121.6512 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103096187 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2023-07-23 | 10:26 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230757 | PG&E | 2023-07-23 | 13:52 | 36.9831 | -120.6203 | Building | N/A | Urban | .26 - 9.99 Acres | Fire Agency | Merced county (dos Palos) inc # 16260 | 101173092 | No | 750 | Unknown | Overhead | Yes | 2023-07-23 | 20:10 | Unknown | N/A | N/A | N/A | N/A
20230763 | PG&E | 2023-07-24 | 1:39 | 36.7272 | -121.6438 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | Salinas fire dept | 101712043 | No | 12000 | Pole | Overhead | Yes | 2023-07-24 | 1:25 | Contact From Object | N/A | Vehicle | Pole | Human Error
20230768 | PG&E | 2023-07-24 | 15:23 | 35.7895 | -119.4356 | Vegetation | N/A | Agriculture | .26 - 9.99 Acres | Fire Agency | Kern County FD | 100173645 | No | 12000 | Pole | Overhead | Yes | 2023-07-24 | 15:20 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20230769 | PG&E | 2023-07-25 | 5:54 | 35.3142 | -118.8965 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Unknown | N/A | 100160511 | No | 12000 | Parallel Groove Clamp | Overhead | Yes | 2023-07-25 | 5:34 | Equipment/Facility Failure | Parallel Groove Clamp | N/A | N/A | N/A
20230772 | PG&E | 2023-07-25 | 19:50 | 36.7855 | -119.7738 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Fresno fire dept | 100870157 | No | 12000 | Connector | Overhead | Yes | 2023-07-25 | 19:49 | Equipment/Facility Failure | Connector | N/A | N/A | N/A
20230773 | PG&E | 2023-07-25 | 16:55 | 36.485 | -121.7421 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | Monterey FD | 101776186 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-25 | 17:01 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230779 | PG&E | 2023-07-26 | 18:29 | 35.3978 | -119.0045 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Bfd | 40367177 | No | 12000 | Transformer | Subsurface | Yes | 2023-07-26 | 18:27 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20230778 | PG&E | 2023-07-26 | 15:48 | 36.3767 | -119.8787 | Vegetation | N/A | Agriculture | .26 - 9.99 Acres | Fire Agency | Kings County FD | 100817518 | No | 240 | Conductor - Open Wire Secondary | Overhead | Yes | 2023-07-26 | 15:46 | Contact From Object | N/A | Vegetation | Conductor - Open Wire Secondary | Outside Force
20230776 | PG&E | 2023-07-26 | 14:30 | 36.6092 | -119.5469 | Vegetation | N/A | Urban | Less Than .25 Acres | Self Extinguished | N/A | 100886311 | Yes | 750 | Crossarm | Overhead | Yes | 2023-07-26 | 14:27 | Equipment/Facility Failure | Crossarm | N/A | N/A | N/A
20230782N | PG&E | 2023-07-26 | 14:13 | 37.0406 | -121.9356 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | Unknown FD | 101688110 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2023-07-26 | 14:00 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230775 | PG&E | 2023-07-26 | 2:21 | 37.9473 | -122.0033 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Concord fire department | 100466225 | No | 750 | Transformer | Overhead | Yes | 2023-07-26 | 2:20 | Contact From Object | N/A | Animal | Transformer | Outside Force
20230782 | PG&E | 2023-07-26 | 20:05 | 36.8013 | -121.7683 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 40644898 | No | 115000 | Conductor - Transmission | Overhead | Yes | 2023-07-26 | 20:20 | Contact From Object | N/A | Animal | Conductor - Transmission | Outside Force
20230784 | PG&E | 2023-07-27 | 10:43 | 38.4381 | -122.5796 | Vegetation | N/A | Urban | .26 - 9.99 Acres | Fire Agency | Santa Rosa FD,Kenwood FD | 41217779 | Yes | 12000 | Capacitor Bank | Overhead | Yes | 2023-07-27 | 10:37 | Equipment/Facility Failure | Capacitor Bank | N/A | N/A | N/A
20230787 | PG&E | 2023-07-27 | 16:27 | 36.2846 | -119.7447 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Kings county | 100832806 | No | 12000 | Pole | Overhead | Yes | 2023-07-27 | 16:19 | Contact From Object | N/A | Vehicle | Pole | Human Error
20230783 | PG&E | 2023-07-27 | 9:45 | 38.1559 | -122.4963 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Customer | N/A | 102225781 | Yes | 12000 | Pole | Overhead | Yes | 2023-07-27 | 9:34 | Contact From Object | N/A | Vehicle | Pole | Human Error
20230788N | PG&E | 2023-07-27 | 12:32 | 37.9071 | -120.6264 | Vegetation | N/A | Herbaceous | 10 - 99 Acres | Fire Agency | CAL FIRE | 101283585 | Yes | 480 | Connector | Overhead | Yes | 2023-07-27 | 12:31 | Equipment/Facility Failure | Connector | N/A | N/A | N/A
20230792 | PG&E | 2023-07-28 | 16:00 | 37.0616 | -121.9787 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | Branciforte FD / CAL Fire | 101799631 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2023-07-28 | 16:32 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230799 | PG&E | 2023-07-29 | 15:41 | 35.6863 | -120.3358 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 101869196 | No | 21000 | Pole | Overhead | Yes | 2023-07-29 | 15:39 | Contact From Object | N/A | Animal | Pole | Outside Force
20230803 | PG&E | 2023-07-29 | 16:15 | 39.1052 | -121.6738 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Yuba City FD | 101331870 | No | 12000 | Pole | Overhead | Yes | 2023-07-29 | 16:12 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20230823N | PG&E | 2023-07-29 | 12:10 | 37.1412 | -120.0654 | Vegetation | N/A | Agriculture | 10 - 99 Acres | Fire Agency | CAL FIRE | 101063650 | No | 12000 | Pole | Overhead | Yes | 2023-07-29 | 12:09 | Contact From Object | N/A | Animal | Pole | Outside Force
20230810 | PG&E | 2023-07-31 | 9:53 | 36.1073 | -119.559 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 103247759 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-31 | 9:36 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230818 | PG&E | 2023-07-31 | 15:22 | 38.2114 | -122.1293 | Vegetation | N/A | Urban | Less Than .25 Acres | Unknown | N/A | 101563108 | No | 12000 | Pole | Overhead | Yes | 2023-07-31 | 15:27 | Contact From Object | N/A | Vehicle | Pole | Human Error
20230831N | PG&E | 2023-07-31 | 4:24 | 39.0514 | -121.4053 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Wheatland Fire Authority | 101303671 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-07-31 | 4:06 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230811 | PG&E | 2023-07-31 | 12:36 | 35.4634 | -119.1847 | Other | Bird | Agriculture | Less Than .25 Acres | Self Extinguished | N/A | 100115938 | No | 12000 | Transformer Bushing | Overhead | Yes | 2023-07-31 | 12:34 | Contact From Object | N/A | Animal | Transformer Bushing | Outside Force
20230823 | PG&E | 2023-08-01 | 18:52 | 35.61 | -121.0855 | Vegetation | N/A | Hardwood Woodland | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101942875 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-01 | 18:33 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230825 | PG&E | 2023-08-01 | 14:57 | 35.3781 | -118.9458 | Other | Connector | Urban | Less than three {3} meters of linear travel | Fire Agency | KCFD | 100249643 | Yes | 750 | Parallel Groove Clamp | Overhead | Yes | 2023-08-01 | 14:49 | Equipment/Facility Failure | Parallel Groove Clamp | N/A | N/A | N/A
20230826 | PG&E | 2023-08-01 | 19:46 | 39.5475 | -121.7078 | Other | Pole | Agriculture | Less Than .25 Acres | Fire Agency | CAL FIRE | 100434557 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-01 | 19:29 | Other | N/A | N/A | N/A | N/A
20230831 | PG&E | 2023-08-02 | 16:53 | 36.4777 | -120.0852 | Other | Pole | Agriculture | Less Than .25 Acres | Fire Agency | CAL FIRE | 100715725 | No | 12000 | Pole | Overhead | Yes | 2023-08-02 | 16:41 | Contact From Object | N/A | Vehicle | Pole | Human Error
20230833 | PG&E | 2023-08-03 | 11:29 | 36.9693 | -121.7654 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | CAL FIRE | 101687876 | Yes | 4160 | Pole | Overhead | Yes | 2023-08-03 | 11:26 | Contact From Object | N/A | Vehicle | Pole | Human Error
20230837 | PG&E | 2023-08-04 | 21:47 | 38.0335 | -122.0731 | Other | Bird | Wetland | Less than three {3} meters of linear travel | Fire Agency | CAL FIRE | 100443754 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-08-04 | 21:42 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230842 | PG&E | 2023-08-06 | 10:58 | 35.1419 | -120.5463 | Other | Balloon | Herbaceous | Less than three {3} meters of linear travel | Fire Agency | CAL FIRE | 101844877 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-06 | 10:40 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20230844 | PG&E | 2023-08-06 | 16:23 | 38.1542 | -121.8705 | Vegetation | N/A | Agriculture | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103376261 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-06 | 16:18 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20230846 | PG&E | 2023-08-06 | 15:28 | 38.0991 | -122.2086 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | VALLEJO FIRE DEPT | 102218555 | Yes | 750 | Connector | Overhead | Yes | 2023-08-06 | 15:26 | Equipment/Facility Failure | Connector | N/A | N/A | N/A
20230847 | PG&E | 2023-08-06 | 15:56 | 38.137 | -121.6844 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | RIO VISTA FD | 101665840 | Yes | 240 | Service Drop | Overhead | Yes | 2023-08-06 | 15:55 | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20230856N | PG&E | 2023-08-07 | 8:21 | 36.0125 | -120.0928 | Vegetation | N/A | Herbaceous | 100 - 299 Acres | Fire Agency | Kings County FD | 40871892 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-08-07 | 8:21 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230854 | PG&E | 2023-08-07 | 0:29 | 37.7476 | -121.921 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | San Ramon FD | 103783551 | Yes | 21000 | Switch | Overhead | Yes | 2023-08-07 | 0:29 | Contact From Object | N/A | Animal | Switch | Outside Force
20230855 | PG&E | 2023-08-07 | 6:13 | 37.8692 | -122.0805 | Vegetation | N/A | Hardwood Woodland | .26 - 9.99 Acres | Fire Agency | Contra Costa County FD | 104055422 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-07 | 6:02 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230858 | PG&E | 2023-08-07 | 13:07 | 36.9374 | -121.7268 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101791697 | Yes | 21000 | Fuse | Overhead | Yes | 2023-08-07 | 13:03 | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20230862 | PG&E | 2023-08-08 | 12:53 | 37.9197 | -122.285 | Vegetation | N/A | Urban | .26 - 9.99 Acres | Fire Agency | Ecfd | 103050215 | No | 12000 | Splice Box | Subsurface | Yes | 2023-08-08 | 12:51 | Equipment/Facility Failure | Splice Box | N/A | N/A | N/A
20230864 | PG&E | 2023-08-09 | 9:31 | 39.304 | -121.5463 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Customer | N/A | 101290144 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-09 | 9:26 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230866 | PG&E | 2023-08-09 | 14:45 | 35.1116 | -118.9149 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Arvin FD | 100169788 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-09 | 14:24 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230868 | PG&E | 2023-08-09 | 16:07 | 38.7128 | -120.946 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Rescue FD | 101412619 | Yes | 750 | Service Drop | Overhead | Yes | 2023-08-09 | 16:06 | Contact From Object | N/A | Vegetation | Service Drop | Outside Force
20230874 | PG&E | 2023-08-10 | 14:58 | 37.1806 | -119.827 | Vegetation | N/A | Hardwood Woodland | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101108312 | Yes | 240 | Service Drop | Overhead | Yes | 2023-08-10 | 14:56 | Contact From Object | N/A | Vegetation | Service Drop | Outside Force
20230872 | PG&E | 2023-08-10 | 4:22 | 37.5876 | -122.3768 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | San Mateo | 100260857 | Yes | 21000 | Transformer | Overhead | Yes | 2023-08-10 | 4:01 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20230873 | PG&E | 2023-08-10 | 0:55 | 35.717 | -119.5526 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Self Extinguished | N/A | 100171613 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-10 | 0:45 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230879 | PG&E | 2023-08-11 | 23:59 | 35.1456 | -119.4933 | Vegetation | N/A | Desert Shrub | Less Than .25 Acres | Fire Agency | Kern County Fire dept | 100241807 | No | 21000 | Lightning Arrestor | Overhead | Yes | 2023-08-11 | 23:24 | Contact From Object | N/A | Animal | Lightning Arrestor | Outside Force
20230875 | PG&E | 2023-08-11 | 14:19 | 40.8704 | -123.5212 | Vegetation | N/A | Conifer Forest | Less than three {3} meters of linear travel | Fire Agency | Forest Service | 104112480 | No | 12000 | Fuse | Overhead | Yes | 2023-08-11 | 14:29 | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20230882 | PG&E | 2023-08-12 | 10:49 | 36.4997 | -119.9532 | Vegetation | N/A | Agriculture | 10 - 99 Acres | Fire Agency | Kings county | 100692644 | No | 12000 | Unknown | Overhead | No | N/A | N/A | Contact From Object | N/A | Animal | Unknown | Outside Force
20230883 | PG&E | 2023-08-12 | 17:50 | 39.8098 | -121.9775 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | CAL FIRE | 100432268 | No | 12000 | Jumper | Overhead | Yes | 2023-08-12 | 17:36 | Contact From Object | N/A | Animal | Jumper | Outside Force
20230884 | PG&E | 2023-08-13 | 14:39 | 37.2497 | -121.9616 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Santa Clara County Fire Dept | 100548377 | Yes | 750 | Conductor - Secondary | Overhead | Yes | 2023-08-13 | 14:38 | Contact From Object | N/A | Vegetation | Conductor - Secondary | Outside Force
20230885 | PG&E | 2023-08-14 | 16:37 | 37.9793 | -121.3162 | Other | Pole | Urban | Less than three {3} meters of linear travel | Fire Agency | Stockton FD | 103820168, 102058478 | No | 750 | Conductor - Secondary | Overhead | Yes | 2023-08-14 | 17:04 | Equipment/Facility Failure | Conductor - Secondary | N/A | N/A | N/A
20230888 | PG&E | 2023-08-15 | 14:11 | 38.4847 | -122.8949 | Vegetation | N/A | Hardwood Forest | Less than three {3} meters of linear travel | Customer | N/A | 102025441 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2023-08-15 | 14:44 | Contact From Object | N/A | Vegetation | Conductor - Open Wire Secondary | Outside Force
20230890 | PG&E | 2023-08-15 | 21:35 | 40.1693 | -123.7073 | Vegetation | N/A | Herbaceous | 10 - 99 Acres | Unknown | N/A | 45033614 | No | 60000 | Conductor - Transmission | Overhead | Yes | 2023-08-15 | 21:35 | Equipment/Facility Failure | Conductor - Transmission | N/A | N/A | N/A
20230895N | PG&E | 2023-08-16 | 17:51 | 37.9561 | -121.2665 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Stockton FD | 102096779 | Yes | 12000 | Guy/Span Wire | Overhead | Yes | 2023-08-16 | 17:46 | Contact From Object | N/A | Vehicle | Guy/Span Wire | Human Error
20230895 | PG&E | 2023-08-16 | 17:38 | 37.6572 | -120.3214 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Customer | N/A | 101189842 | No | 750 | Guy/Span Wire | Overhead | Yes | 2023-08-16 | 17:34 | Other | N/A | N/A | N/A | N/A
20230897 | PG&E | 2023-08-17 | 16:56 | 37.4859 | -119.9695 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 103924940 | No | 12000 | Jumper | Overhead | Yes | 2023-08-17 | 16:47 | Other | N/A | N/A | N/A | N/A
20230899 | PG&E | 2023-08-17 | 19:37 | 39.1878 | -123.219 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Ukiah Valley Fire Authority | 102172647 | No | 12000 | Crossarm | Overhead | Yes | 2023-08-17 | 19:29 | Contact From Object | N/A | Vegetation | Crossarm | Outside Force
20230903 | PG&E | 2023-08-18 | 14:21 | 39.0039 | -121.034 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Placer Hills Fire Department | 100094673 | No | 240 | Pole | Overhead | Yes | 2023-08-18 | 14:11 | Contact From Object | N/A | Vegetation | Pole | Outside Force
20230906 | PG&E | 2023-08-19 | 17:12 | 35.4912 | -119.1529 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | KCFD | 100121511 | No | 12000 | Guy/Span Wire | Overhead | Yes | 2023-08-19 | 15:44 | Equipment/Facility Failure | Guy/Span Wire | N/A | N/A | N/A
20230909 | PG&E | 2023-08-19 | 17:55 | 38.351 | -121.7855 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | DIXON | 101567554 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-19 | 17:54 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230904 | PG&E | 2023-08-19 | 15:49 | 36.6413 | -119.4129 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | CAL FIRE | 100846765 | Yes | 12000 | Pole | Overhead | Yes | 2023-08-19 | 15:48 | Contact From Object | N/A | Vegetation | Pole | Outside Force
20230912 | PG&E | 2023-08-19 | 16:19 | 40.1709 | -123.6093 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 100995833 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-19 | 15:32 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230917 | PG&E | 2023-08-20 | 15:43 | 37.2957 | -122.0233 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | San Jose FD | 100540432 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2023-08-20 | 17:24 | Equipment/Facility Failure | Conductor - Open Wire Secondary | N/A | N/A | N/A
20230929 | PG&E | 2023-08-20 | 0:07 | 39.1428 | -121.9029 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Meridian FD | 101633749 | No | 12000 | Recloser | Overhead | Yes | 2023-08-20 | 0:00 | Contact From Object | N/A | Animal | Recloser | Outside Force
20230932 | PG&E | 2023-08-21 | 15:43 | 36.7493 | -120.6573 | Vegetation | N/A | Agriculture | .26 - 9.99 Acres | Fire Agency | Firebaugh FD | 101175446 | No | 12000 | Connector | Overhead | Yes | 2023-08-21 | 13:32 | Other | N/A | N/A | N/A | N/A
20230930 | PG&E | 2023-08-21 | 15:52 | 38.2481 | -122.7057 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | CAL FIRE | 102019710 | No | 750 | Conductor - Secondary | Overhead | Yes | 2023-08-21 | 13:56 | Contact From Object | N/A | Vegetation | Conductor - Secondary | Outside Force
20230934 | PG&E | 2023-08-21 | 22:57 | 38.167 | -122.508 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102225954 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-21 | 22:44 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20230942N | PG&E | 2023-08-23 | 16:26 | 36.8108 | -119.7783 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Fresno FD | 100852797 | Yes | 12000 | Crossarm | Overhead | Yes | 2023-08-23 | 16:23 | Equipment/Facility Failure | Crossarm | N/A | N/A | N/A
20230944 | PG&E | 2023-08-24 | 13:56 | 37.2695 | -121.8677 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | San Jose FD | 40970544 | Yes | 12000 | Capacitor Bank | Overhead | Yes | 2023-08-24 | 13:53 | Equipment/Facility Failure | Capacitor Bank | N/A | N/A | N/A
20230954 | PG&E | 2023-08-24 | 19:21 | 37.9785 | -121.2732 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Stockton FD | 102061013 | No | 750 | Service Drop | Overhead | Yes | 2023-08-24 | 19:19 | Contact From Object | N/A | Vegetation | Service Drop | Outside Force
20230943 | PG&E | 2023-08-24 | 13:17 | 38.0073 | -121.7934 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Contra Costa County FD | 100454932 | No | 21000 | Crossarm | Overhead | Yes | 2023-08-24 | 12:09 | Equipment/Facility Failure | Crossarm | N/A | N/A | N/A
20230953 | PG&E | 2023-08-25 | 3:28 | 35.2283 | -120.6722 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Utility | N/A | 101849171 | No | 12000 | Riser | Overhead | Yes | 2023-08-25 | 1:38 | Other | N/A | N/A | N/A | N/A
20230955 | PG&E | 2023-08-25 | 10:58 | 36.1694 | -119.5293 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | Tulare County FD | 100766572 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-25 | 10:52 | Vandalism/Theft | N/A | N/A | N/A | N/A
20230959 | PG&E | 2023-08-26 | 19:54 | 37.8054 | -121.4497 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Tracy FD | 103818052 | No | 12000 | Pole | Overhead | Yes | 2023-08-26 | 19:51 | Contact From Object | N/A | Vehicle | Pole | Human Error
20230964 | PG&E | 2023-08-27 | 23:07 | 37.8892 | -121.2867 | Vegetation | N/A | Agriculture | Less than three {3} meters of linear travel | Unknown | N/A | 102068063 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-27 | 22:52 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20230961 | PG&E | 2023-08-27 | 9:29 | 36.3879 | -119.9278 | Vegetation | N/A | Agriculture | Less than three {3} meters of linear travel | Self Extinguished | N/A | 100817759 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-27 | 8:56 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230966 | PG&E | 2023-08-28 | 5:12 | 38.4217 | -122.9565 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 103985976 | No | 750 | Compression Connector | Overhead | Yes | 2023-08-28 | 5:11 | Other | N/A | N/A | N/A | N/A
20230971 | PG&E | 2023-08-29 | 15:37 | 36.725 | -119.7718 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Fresno FD | 100857458, 100857451 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-29 | 14:13 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20230975 | PG&E | 2023-08-29 | 16:55 | 36.75 | -119.7556 | Other | Squirrel | Urban | Less than three {3} meters of linear travel | Fire Agency | Fresno FD | 100860688 | Yes | 750 | Conductor - Secondary | Overhead | Yes | 2023-08-29 | 14:35 | Contact From Object | N/A | Animal | Conductor - Secondary | Outside Force
20230973 | PG&E | 2023-08-29 | 16:55 | 40.0621 | -123.7345 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100988548 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-08-29 | 11:12 | Contact From Object | N/A | Vegetation | Conductor - Primary | Human Error
20230976N | PG&E | 2023-08-29 | 14:59 | 39.11 | -122.3153 | Vegetation | N/A | Hardwood Woodland | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 40813108 | No | 115000 | Conductor - Transmission | Overhead | Yes | 2023-08-29 | 14:59 | Contact From Object | N/A | Animal | Conductor - Transmission | Outside Force
20230981 | PG&E | 2023-08-30 | 17:20 | 36.8827 | -121.6361 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101698883 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2023-08-30 | 16:10 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20230978 | PG&E | 2023-08-30 | 14:11 | 40.4444 | -122.4087 | Vegetation | N/A | Urban | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101490816 | Yes | 120 | Connector | Overhead | Yes | 2023-08-30 | 11:35 | Other | N/A | N/A | N/A | N/A
20230982 | PG&E | 2023-08-31 | 12:40 | 37.0545 | -121.5857 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Morgan Hill FD | 100608723 | Yes | 750 | Connector | Overhead | Yes | 2023-08-31 | 12:39 | Contact From Object | N/A | Other | Connector | Human Error
20230995 | PG&E | 2023-09-03 | 9:48 | 36.1356 | -119.5497 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Unknown | N/A | 100747111 | No | 240 | Conductor - Secondary | Overhead | Yes | 2023-09-03 | 9:43 | Vandalism/Theft | N/A | N/A | N/A | N/A
20230998 | PG&E | 2023-09-04 | 11:22 | 35.3854 | -119.181 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Kern County FD | 100237031 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-09-04 | 9:03 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20231001 | PG&E | 2023-09-04 | 22:12 | 35.4115 | -119.0556 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Kern County FD | 100202801 | Yes | 12000 | Transformer | Overhead | Yes | 2023-09-04 | 20:39 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20230999 | PG&E | 2023-09-04 | 12:06 | 39.9551 | -122.165 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 101503383 | No | 12000 | Pole | Overhead | Yes | 2023-09-04 | 12:02 | Contact From Object | N/A | Vehicle | Pole | Human Error
20231002 | PG&E | 2023-09-05 | 11:51 | 38.1908 | -121.1392 | Vegetation | N/A | Agriculture | Less than three {3} meters of linear travel | Fire Agency | Clements FD | 102075888 | Yes | 12000 | Connector | Overhead | Yes | 2023-09-05 | 11:51 | Equipment/Facility Failure | Connector | N/A | N/A | N/A
20231006 | PG&E | 2023-09-05 | 16:33 | 38.6392 | -120.9105 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | CAL FIRE | 103933231 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-09-05 | 16:27 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20231004 | PG&E | 2023-09-05 | 16:40 | 35.6377 | -120.8547 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | CAL FIRE | 1003394658 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-09-05 | 16:29 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20231007 | PG&E | 2023-09-06 | 12:44 | 35.4976 | -119.2866 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Kern County FD | 100141733 | Yes | 240 | Service Drop | Overhead | Yes | 2023-09-06 | 12:42 | Contact From Object | N/A | Other | Service Drop | Other
20231046 | PG&E | 2023-09-07 | 13:46 | 37.9911 | -121.3498 | Other | Recloser | Urban | .26 - 9.99 Acres | Fire Agency | stockton FD | 102109078 | No | 12000 | Recloser | Overhead | Yes | 2023-09-07 | 13:46 | Equipment/Facility Failure | Recloser | N/A | N/A | N/A
20231009 | PG&E | 2023-09-07 | 11:03 | 38.8839 | -121.3029 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Lincoln FD | 103783448 | No | 12000 | Lightning Arrestor | Overhead | No | N/A | N/A | Contact From Object | N/A | Animal | Lightning Arrestor | Outside Force
20231016 | PG&E | 2023-09-08 | 22:39 | 38.3017 | -122.7429 | Vegetation | N/A | Herbaceous | Less than three {3} meters of linear travel | Fire Agency | Ranch fire department | 103140921 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-09-08 | 22:29 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20231017 | PG&E | 2023-09-08 | 21:12 | 35.6584 | -120.0606 | Vegetation | N/A | Agriculture | 10 - 99 Acres | Fire Agency | Kern City FD | 100176626, 100176632 | No | 12000 | Unknown | Overhead | Yes | 2023-09-08 | 18:38 | Unknown | N/A | N/A | N/A | N/A
20231014N | PG&E | 2023-09-08 | 8:29 | 36.4666 | -121.3896 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Gonzales | 40697724 | No | 60000 | Connector | Overhead | Yes | 2023-09-08 | 8:29 | Wire-Wire Contact | N/A | N/A | N/A | Weather
20231015N | PG&E | 2023-09-08 | 11:18 | 36.2831 | -120.9608 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101728929 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-09-08 | 11:18 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20231019 | PG&E | 2023-09-09 | 5:33 | 35.3647 | -119.0923 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Bakersfield FD | 100201397 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-09-09 | 5:19 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20231020 | PG&E | 2023-09-09 | 7:34 | 37.9999 | -122.3209 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | San Pablo FD | 103914776 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-09-09 | 1:38 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20231022 | PG&E | 2023-09-09 | 21:18 | 38.3449 | -121.9732 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Utility | N/A | 107999934 | No | 120 | Transformer | Subsurface | Yes | 2023-09-09 | 15:14 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20231023 | PG&E | 2023-09-09 | 17:47 | 37.7935 | -120.8698 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Unknown | N/A | 103318128 | Yes | 17000 | Capacitor Bank | Overhead | Yes | 2023-09-09 | 16:28 | Other | N/A | N/A | N/A | N/A
20231145N | PG&E | 2023-09-09 | 19:34 | 37.4212 | -121.1477 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Self Extinguished | N/A | 40643451 | No | 60000 | Insulator | Overhead | Yes | 2023-09-09 | 19:34 | Other | N/A | N/A | N/A | N/A
20231027 | PG&E | 2023-09-10 | 5:48 | 36.8955 | -119.6928 | Vegetation | N/A | Herbaceous | Less than three {3} meters of linear travel | Self Extinguished | N/A | 100729117 ,103997236 | No | 115000 | Transformer | Overhead | Yes | 2023-09-10 | 0:30 | Contact From Object | N/A | Vehicle | Transformer | Human Error
20231029 | PG&E | 2023-09-10 | 11:37 | 36.8945 | -120.7368 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Utility | N/A | 103332036 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-09-10 | 8:58 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20231038 | PG&E | 2023-09-11 | 14:29 | 35.4177 | -119.0398 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Kern County FD | 100241990 | No | 12000 | Transformer | Overhead | Yes | 2023-09-11 | 12:20 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20231039 | PG&E | 2023-09-12 | 20:44 | 38.2038 | -121.2651 | Other | Connector | Urban | Less Than .25 Acres | Fire Agency | Woodbridge FD | 107058966 | No | 12000 | Connector | Overhead | Yes | 2023-09-12 | 20:41 | Equipment/Facility Failure | Connector | N/A | N/A | N/A
20231045 | PG&E | 2023-09-13 | 19:34 | 38.0345 | -122.1847 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101424299 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-09-13 | 19:28 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20231044 | PG&E | 2023-09-13 | 20:05 | 36.8051 | -121.2642 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101774521 | No | 12000 | Automatic Wire Splice | Overhead | Yes | 2023-09-13 | 19:55 | Equipment/Facility Failure | Automatic Wire Splice | N/A | N/A | N/A
20231047 | PG&E | 2023-09-14 | 21:21 | 37.9681 | -122.3559 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Unknown | N/A | 101432055 | Yes | 750 | Conductor - Insulated Secondary | Overhead | Yes | 2023-09-14 | 21:21 | Contact From Object | N/A | Vegetation | Conductor - Insulated Secondary | Outside Force
20231050 | PG&E | 2023-09-14 | 17:11 | 35.2746 | -118.8727 | Other | Pole | Agriculture | Less than three {3} meters of linear travel | Fire Agency | Kern County FD | 100206182 | No | 12000 | Pole | Overhead | Yes | 2023-09-14 | 17:10 | Contact From Object | N/A | Vehicle | Pole | Human Error
20231051N | PG&E | 2023-09-14 | 15:48 | 39.9172 | -122.3112 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101521812 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-09-14 | 15:44 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20231055 | PG&E | 2023-09-15 | 11:21 | 38.1451 | -121.1597 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Lockeford FD | 103129438, 103855450, 102078003 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-09-14 | 11:54 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20231063N | PG&E | 2023-09-15 | 22:32 | 37.0873 | -121.6116 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Unknown | N/A | 100601861 | No | 21000 | Pole | Overhead | Yes | 2023-09-15 | 22:28 | Contact From Object | N/A | Vehicle | Pole | Human Error
20231053 | PG&E | 2023-09-15 | 23:58 | 39.4465 | -121.4572 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 40822470 | No | 60000 | Conductor - Transmission | Overhead | Yes | 2023-09-15 | 23:35 | Contact From Object | N/A | Other | Conductor - Transmission | Other
20231057N | PG&E | 2023-09-15 | 23:48 | 39.4465 | -121.4598 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 42564764 | No | 60000 | Pole | Overhead | No | N/A | N/A | Contact From Object | N/A | Other | Pole | Other
20231059 | PG&E | 2023-09-16 | 9:15 | 39.8356 | -122.0017 | Vegetation | N/A | Agriculture | 10 - 99 Acres | Fire Agency | CAL FIRE | 100432837 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-09-16 | 9:09 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20231062N | PG&E | 2023-09-17 | 6:35 | 39.074 | -121.5388 | Vegetation | N/A | Urban | Less Than .25 Acres | Unknown | N/A | 101314020 | No | 750 | Service Drop | Overhead | Yes | 2023-09-17 | 6:17 | Contact From Object | N/A | Vegetation | Service Drop | Outside Force
20231071 | PG&E | 2023-09-20 | 17:04 | 36.8299 | -119.3287 | Vegetation | N/A | Hardwood Woodland | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100725195 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-09-20 | 17:00 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20231070 | PG&E | 2023-09-20 | 18:08 | 35.2934 | -119.2821 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Self Extinguished | N/A | 100197400 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-09-20 | 18:01 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20231072 | PG&E | 2023-09-21 | 9:34 | 37.9678 | -122.337 | Building | N/A | Urban | Less Than .25 Acres | Fire Agency | Contra Costa County FD | 101435157 | Yes | 240 | Transformer | Overhead | Yes | 2023-09-21 | 9:32 | Contact From Object | N/A | Vehicle | Transformer | Human Error
20231073 | PG&E | 2023-09-22 | 7:07 | 38.641 | -120.8898 | Vegetation | N/A | Hardwood Woodland | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101385520 | No | 12000 | Insulator | Overhead | Yes | 2023-09-22 | 7:35 | Equipment/Facility Failure | Insulator | N/A | N/A | N/A
20231074 | PG&E | 2023-09-22 | 8:00 | 38.3533 | -122.127 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 102289772 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-09-22 | 7:56 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20231078 | PG&E | 2023-09-23 | 21:49 | 37.8437 | -122.286 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Oakland FD | 102297487 | Yes | 240 | Service Drop | Overhead | No | N/A | N/A | Equipment/Facility Failure | Service Drop | N/A | N/A | N/A
20231079 | PG&E | 2023-09-24 | 11:35 | 37.975 | -122.2903 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Utility | N/A | 101428946 | Yes | 750 | Guy/Span Wire | Overhead | No | N/A | N/A | Wire-Wire Contact | N/A | N/A | N/A | Weather
20231083 | PG&E | 2023-09-25 | 14:38 | 39.082 | -123.4957 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102216135 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-09-25 | 14:34 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20231094 | PG&E | 2023-09-27 | 19:26 | 36.2257 | -119.8869 | Vegetation | N/A | Agriculture | .26 - 9.99 Acres | Self Extinguished | N/A | 100685131 | No | 750 | Fuse | Overhead | No | N/A | N/A | Vandalism/Theft | N/A | N/A | N/A | N/A
20231096 | PG&E | 2023-09-27 | 20:09 | 38.6674 | -120.9933 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Cameron park fire department | 101410355 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-09-27 | 20:07 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20231097 | PG&E | 2023-09-28 | 12:36 | 38.2148 | -121.9704 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | Suisun FPD | 103927775 | No | 21000 | Pothead | Overhead | Yes | 2023-09-28 | 12:31 | Contact From Object | N/A | Animal | Pothead | Outside Force
20231115N | PG&E | 2023-09-28 | 11:31 | 38.1585 | -121.6972 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Unknown FD | 101667208 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2023-09-28 | 11:26 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20231101 | PG&E | 2023-09-29 | 10:59 | 37.1717 | -121.6935 | Other | Bushing | Agriculture | Less Than .25 Acres | Fire Agency | Unknown FD | 100602526 | Yes | 21000 | Switch | Overhead | Yes | 2023-09-29 | 10:57 | Contact From Object | N/A | Animal | Switch | Outside Force
20231117 | PG&E | 2023-10-02 | 12:26 | 39.6095 | -121.8985 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Utility | N/A | 100438202 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-10-02 | 12:20 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20231118 | PG&E | 2023-10-03 | 14:08 | 36.1379 | -119.5479 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Kings county | 100747160 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-10-03 | 13:49 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20231119 | PG&E | 2023-10-04 | 11:57 | 38.1511 | -121.615 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Isleton FD | 104052495 | No | 21000 | Potential Transformer | Overhead | Yes | 2023-10-04 | 12:58 | Equipment/Facility Failure | Potential Transformer | N/A | N/A | N/A
20231144N | PG&E | 2023-10-04 | 18:52 | 36.7214 | -121.6581 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Unknown FD | 101783084 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-10-04 | 18:46 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20231125 | PG&E | 2023-10-05 | 16:52 | 39.7392 | -122.0169 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Hamilton City FPD | 100362975 | Yes | 240 | Conductor - Secondary | Overhead | Yes | 2023-10-05 | 16:51 | Wire-Wire Contact | N/A | N/A | N/A | Weather
20231132 | PG&E | 2023-10-06 | 12:42 | 35.5374 | -120.9787 | Vegetation | N/A | Herbaceous | 100 - 299 Acres | Fire Agency | CAL FIRE | 101940548 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-10-06 | 12:36 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20231134 | PG&E | 2023-10-06 | 15:57 | 38.2181 | -122.1118 | Vegetation | N/A | Urban | .26 - 9.99 Acres | Fire Agency | FAIRFIELD FIRE DEPARTMENT | 103696188 | No | 12000 | Unknown | Overhead | Yes | 2023-10-06 | 15:56 | Unknown | N/A | N/A | N/A | N/A
20231129 | PG&E | 2023-10-06 | 10:27 | 36.3774 | -121.3408 | Vegetation | N/A | Agriculture | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101757175 | Yes | 12000 | Automatic Wire Splice | Overhead | Yes | 2023-10-06 | 10:16 | Equipment/Facility Failure | Automatic Wire Splice | N/A | N/A | N/A
20231133 | PG&E | 2023-10-06 | 15:54 | 36.7706 | -121.7649 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | North County FPD | 103954619 | Yes | 12000 | Jumper | Overhead | No | N/A | N/A | Equipment/Facility Failure | Jumper | N/A | N/A | N/A
20231136 | PG&E | 2023-10-07 | 1:55 | 36.0196 | -121.1679 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Customer | N/A | 101728548 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-10-07 | 1:51 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20231147 | PG&E | 2023-10-09 | 22:18 | 37.6305 | -122.1073 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Hayward FD | 100952364 | No | 12000 | Capacitor Bank | Overhead | Yes | 2023-10-09 | 22:15 | Equipment/Facility Failure | Capacitor Bank | N/A | N/A | N/A
20231142 | PG&E | 2023-10-09 | 1:22 | 36.6826 | -119.5652 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | CAL FIRE | 100763816 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-10-09 | 1:20 | Vandalism/Theft | N/A | N/A | N/A | N/A
20231154 | PG&E | 2023-10-12 | 2:31 | 38.6558 | -121.7688 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Woodland FD | 101606130 | Yes | 240 | Conductor - Open Wire Secondary | Overhead | No | N/A | N/A | Contact From Object | N/A | Other | Conductor - Open Wire Secondary | Weather
20231164N | PG&E | 2023-10-15 | 22:37 | 37.908 | -122.4777 | Vegetation | N/A | Hardwood Woodland | Less than three {3} meters of linear travel | Fire Agency | Tiburon FD | 104011208 | Yes | 12000 | Pole | Overhead | Yes | 2023-10-15 | 22:30 | Contact From Object | N/A | Vehicle | Pole | Human Error
20231163N | PG&E | 2023-10-15 | 12:57 | 38.2597 | -121.9661 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Unknown | 101666261 | No | 21000 | Crossarm | Overhead | No | N/A | N/A | Equipment/Facility Failure | Crossarm | N/A | N/A | N/A
20231165N | PG&E | 2023-10-16 | 14:23 | 37.2701 | -122.3135 | Vegetation | N/A | Conifer Forest | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100267726 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-10-16 | 14:22 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20231167 | PG&E | 2023-10-18 | 17:28 | 35.3157 | -119.0063 | Vegetation | N/A | Urban | Less Than .25 Acres | Unknown | N/A | 100155602,10015560,, 100255356,100155601, 100255354 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2023-10-18 | 17:25 | Contact From Object | N/A | Other | Conductor - Primary | Human Error
20231169 | PG&E | 2023-10-18 | 16:14 | 38.2052 | -121.1573 | Vegetation | N/A | Herbaceous | Less than three {3} meters of linear travel | Fire Agency | Fire department | 102088834 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-10-18 | 16:10 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20231168 | PG&E | 2023-10-18 | 13:49 | 38.2987 | -121.6026 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Courtland FD | 101572544 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-10-18 | 13:41 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20231178 | PG&E | 2023-10-20 | 18:50 | 35.7252 | -120.6552 | Vegetation | N/A | Herbaceous | Less than three {3} meters of linear travel | Fire Agency | CAL FIRE | 103009151 | No | 12000 | Pole | Overhead | Yes | 2023-10-20 | 18:43 | Contact From Object | N/A | Vehicle | Pole | Human Error
20231180 | PG&E | 2023-10-21 | 7:58 | 38.3682 | -123.0634 | Vegetation | N/A | Shrub | Less than three {3} meters of linear travel | Utility | N/A | 102007596 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-10-21 | 4:59 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20231182N | PG&E | 2023-10-21 | 14:55 | 38.4127 | -121.6754 | Vegetation | N/A | Agriculture | .26 - 9.99 Acres | Fire Agency | Davis FD | 101650775 | No | 12000 | Pole | Overhead | Yes | 2023-10-21 | 14:45 | Equipment/Facility Failure | Pole | N/A | N/A | N/A
20231184N | PG&E | 2023-10-23 | 2:54 | 37.9342 | -122.0814 | Building | N/A | Urban | Less than three {3} meters of linear travel | Unknown | N/A | 100475863 | No | 21000 | Capacitor Bank | Overhead | No | N/A | N/A | Contamination | N/A | N/A | N/A | N/A
20231192 | PG&E | 2023-10-24 | 11:48 | 38.5375 | -122.8083 | Vegetation | N/A | Barren/Other | Less Than .25 Acres | Fire Agency | SONOMA COUNTY FIRE DIST. | 103983201 | No | 12000 | Recloser | Overhead | Yes | 2023-10-24 | 11:37 | Contact From Object | N/A | Animal | Recloser | Outside Force
20231208 | PG&E | 2023-10-26 | 15:37 | 38.2576 | -122.4422 | Vegetation | N/A | Urban | .26 - 9.99 Acres | Fire Agency | Schell-Vista Fire Protection District | 102006585 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-10-26 | 15:30 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20231209 | PG&E | 2023-10-27 | 14:20 | 37.3937 | -120.6111 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | CAL FIRE | 101190820 | Yes | 750 | Crossarm | Overhead | Yes | 2023-10-27 | 14:19 | Equipment/Facility Failure | Crossarm | N/A | N/A | N/A
20231215 | PG&E | 2023-10-28 | 22:04 | 38.3707 | -121.9814 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Vacaville fire | 101596966 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2023-10-28 | 22:01 | Wire-Wire Contact | N/A | N/A | N/A | Weather
20231218 | PG&E | 2023-10-29 | 5:32 | 35.6533 | -120.3637 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | CAL FIRE | 101865991 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-10-29 | 5:20 | Vandalism/Theft | N/A | N/A | N/A | N/A
20231219 | PG&E | 2023-10-29 | 11:14 | 37.9192 | -122.0371 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Walnut Creek fire department | 103885757 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-10-29 | 11:07 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20231221 | PG&E | 2023-10-29 | 10:23 | 35.5445 | -119.0816 | Vegetation | N/A | Desert Shrub | .26 - 9.99 Acres | Fire Agency | Kern County FD | 103372665 | No | 12000 | Transformer | Overhead | Yes | 2023-10-29 | 9:17 | Contact From Object | N/A | Animal | Transformer | Outside Force
20231231 | PG&E | 2023-10-31 | 9:44 | 35.3191 | -118.8252 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Kern County | 100256882 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-10-31 | 9:41 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20231226 | PG&E | 2023-10-31 | 1:40 | 39.5306 | -121.5542 | Vegetation | N/A | Herbaceous | .26 - 9.99 Acres | Fire Agency | Oroville FD | 100374116 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-10-31 | 1:30 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20231233 | PG&E | 2023-11-01 | 8:45 | 38.0112 | -122.5385 | Vegetation | N/A | Hardwood Woodland | Less Than .25 Acres | Fire Agency | San Rafael FD | 102247960 | Yes | 12000 | Pole | Overhead | Yes | 2023-11-01 | 8:41 | Contact From Object | N/A | Vegetation | Pole | Outside Force
20231239 | PG&E | 2023-11-02 | 14:37 | 34.6126 | -120.2023 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Santa Barbara county fire,Buellton | 101876128 | No | 12000 | Jumper | Overhead | Yes | 2023-11-02 | 14:33 | Equipment/Facility Failure | Jumper | N/A | N/A | N/A
20231242 | PG&E | 2023-11-03 | 7:18 | 36.2228 | -121.7583 | Vegetation | N/A | Conifer Forest | Less Than .25 Acres | Fire Agency | CAL FIRE | 101777291 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-11-03 | 7:13 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20231243 | PG&E | 2023-11-03 | 20:26 | 37.4808 | -122.3153 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 103816180 | Yes | 12000 | Fuse | Overhead | Yes | 2023-11-03 | 20:25 | Equipment/Facility Failure | Fuse | N/A | N/A | N/A
20231246N | PG&E | 2023-11-04 | 10:11 | 40.1432 | -122.3183 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Self Extinguished | N/A | 101524380 | No | 750 | Connector | Overhead | Yes | 2023-11-04 | 10:06 | Equipment/Facility Failure | Connector | N/A | N/A | N/A
20231247N | PG&E | 2023-11-04 | 13:50 | 39.7131 | -121.6632 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 100382866 | Yes | 12000 | Pole | Overhead | Yes | 2023-11-04 | 13:45 | Contact From Object | N/A | Vehicle | Pole | Human Error
20231253 | PG&E | 2023-11-06 | 11:07 | 38.897 | -121.4221 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | Placer County FD | 100042831 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-11-06 | 10:59 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20231274 | PG&E | 2023-11-09 | 10:46 | 36.4718 | -119.1679 | Vegetation | N/A | Herbaceous | 10 - 99 Acres | Fire Agency | CAL FIRE | 100688999 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-11-09 | 10:41 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20231277 | PG&E | 2023-11-10 | 16:36 | 38.1171 | -121.4214 | Vegetation | N/A | Agriculture | Less than three {3} meters of linear travel | Fire Agency | lodi fd | 42593796 | No | 12000 | Recloser | Overhead | Yes | 2023-11-10 | 16:21 | Contact From Object | N/A | Animal | Recloser | Outside Force
20231278 | PG&E | 2023-11-11 | 8:53 | 35.318 | -119.1401 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Bakersfield fire department | 100156005 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-11-11 | 8:51 | Contact From Object | N/A | Other | Conductor - Primary | Other
20231279 | PG&E | 2023-11-12 | 10:31 | 37.8678 | -122.2537 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Berkeley FD | 101442489 | Yes | 240 | Service Drop | Overhead | Yes | 2023-11-12 | 10:30 | Contact From Object | N/A | Vegetation | Service Drop | Outside Force
20231293 | PG&E | 2023-11-15 | 13:50 | 34.858 | -120.4252 | Vegetation | N/A | Urban | Less Than .25 Acres | Utility | N/A | 101924751 | No | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2023-11-15 | 13:26 | Contact From Object | N/A | Vegetation | Conductor - Open Wire Secondary | Outside Force
20231285 | PG&E | 2023-11-15 | 10:45 | 36.1973 | -119.6725 | Vegetation | N/A | Water | Less Than .25 Acres | Self Extinguished | N/A | 100788823 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-11-15 | 10:42 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20231288 | PG&E | 2023-11-15 | 15:20 | 36.3682 | -121.3242 | Vegetation | N/A | Barren/Other | Less Than .25 Acres | Fire Agency | CAL FIRE | 103921055 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-11-15 | 15:19 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20231286 | PG&E | 2023-11-15 | 13:04 | 34.8713 | -120.4253 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Santa Barbara County FD | 101857540 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-11-15 | 12:54 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20231290 | PG&E | 2023-11-15 | 14:00 | 35.4418 | -119.2019 | Vegetation | N/A | Urban | .26 - 9.99 Acres | Fire Agency | Kcfd | 100188569 | Yes | 750 | Conductor - Open Wire Secondary | Overhead | Yes | 2023-11-15 | 13:58 | Contact From Object | N/A | Vegetation | Conductor - Open Wire Secondary | Outside Force
20231295 | PG&E | 2023-11-16 | 8:49 | 35.6159 | -119.8107 | Vegetation | N/A | Herbaceous | Less than three {3} meters of linear travel | Fire Agency | KCFD | 103117885 | No | 21000 | Unknown | Overhead | Yes | 2023-11-16 | 8:48 | Equipment/Facility Failure | Unknown | N/A | N/A | N/A
20231296 | PG&E | 2023-11-16 | 13:05 | 38.1614 | -121.7005 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Rio Vista FD | 101569726 | Yes | 21000 | Conductor - Primary | Overhead | Yes | 2023-11-16 | 12:58 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20231307 | PG&E | 2023-11-21 | 9:47 | 36.2928 | -119.8074 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | Kings fire department | 103849661 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-11-21 | 9:44 | Contact From Object | N/A | Vehicle | Conductor - Primary | Human Error
20231310 | PG&E | 2023-11-22 | 11:29 | 39.0177 | -121.5578 | Vegetation | N/A | Agriculture | Less than three {3} meters of linear travel | Self Extinguished | N/A | 104179176 | No | 21000 | Conductor - Primary | Overhead | Yes | 2023-11-22 | 11:24 | Contact From Object | N/A | Other | Conductor - Primary | Other
20231316 | PG&E | 2023-11-23 | 11:23 | 40.2165 | -122.1957 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Self Extinguished | N/A | 101527906 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-11-23 | 11:26 | Contact From Object | N/A | Vegetation | Conductor - Primary | Outside Force
20231312 | PG&E | 2023-11-24 | 0:03 | 38.5399 | -121.9858 | Vegetation | N/A | Agriculture | 10 - 99 Acres | Fire Agency | CAL FIRE | 101574673 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-11-23 | 23:59 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20231317 | PG&E | 2023-11-24 | 10:30 | 37.9769 | -122.3217 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | San Pablo FD | 101435226 | No | 12000 | Transformer | Subsurface | Yes | 2023-11-24 | 10:29 | Equipment/Facility Failure | Transformer | N/A | N/A | N/A
20231318 | PG&E | 2023-11-25 | 7:04 | 38.4463 | -121.8591 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Fire Agency | Dixon FD | 101580939 | No | 12000 | Automatic Wire Splice | Overhead | Yes | 2023-11-25 | 6:59 | Equipment/Facility Failure | Automatic Wire Splice | N/A | N/A | N/A
20231323 | PG&E | 2023-11-26 | 16:56 | 39.7193 | -122.2111 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | Orland FD | 100367033 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-11-26 | 16:55 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20231321 | PG&E | 2023-11-26 | 5:58 | 38.3967 | -122.8515 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | CAL FIRE | 103874857 | No | 12000 | Automatic Wire Splice | Overhead | Yes | 2023-11-26 | 5:57 | Equipment/Facility Failure | Automatic Wire Splice | N/A | N/A | N/A
20231327 | PG&E | 2023-11-28 | 12:37 | 38.7224 | -120.7918 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | El dorado county fire | 101415136 | No | 12000 | Pothead | Overhead | Yes | 2023-11-28 | 12:31 | Contact From Object | N/A | Animal | Pothead | Outside Force
20231336 | PG&E | 2023-12-04 | 1:41 | 36.7387 | -119.769 | Vegetation | N/A | Urban | Less Than .25 Acres | Fire Agency | FFD | 100864780 | Yes | 12000 | Riser | Overhead | Yes | 2023-12-04 | 1:40 | Equipment/Facility Failure | Riser | N/A | N/A | N/A
20231349 | PG&E | 2023-12-10 | 12:50 | 36.64 | -119.3738 | Vegetation | N/A | Agriculture | Less Than .25 Acres | Customer | N/A | 100735201 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-12-10 | 12:42 | Contact From Object | N/A | Balloon | Conductor - Primary | Outside Force
20231352 | PG&E | 2023-12-13 | 8:47 | 36.9756 | -120.0596 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Fire Agency | MADERA | 101136356 | No | 12000 | Conductor - Primary | Overhead | Yes | 2023-12-13 | 8:46 | Contact From Object | N/A | Animal | Conductor - Primary | Outside Force
20231356 | PG&E | 2023-12-15 | 10:34 | 35.5625 | -118.8695 | Vegetation | N/A | Herbaceous | 100 - 299 Acres | Fire Agency | KCFD | 100203256 and 100236306 | Yes | 21000 | Connector | Overhead | Yes | 2023-12-15 | 10:18 | Equipment/Facility Failure | Connector | N/A | N/A | N/A
20231360 | PG&E | 2023-12-16 | 16:26 | 38.1173 | -122.2431 | Vegetation | N/A | Urban | Less than three {3} meters of linear travel | Customer | N/A | 102274997 | Yes | 4160 | Guy/Span Wire | Overhead | Yes | 2023-12-16 | 16:11 | Contact From Object | N/A | Vehicle | Guy/Span Wire | Human Error
20231361 | PG&E | 2023-12-17 | 0:29 | 35.2155 | -119.4128 | Vegetation | N/A | Agriculture | .26 - 9.99 Acres | Fire Agency | KCFD | 100229361 | No | 12000 | Transformer | Overhead | Yes | 2023-12-17 | 0:23 | Vandalism/Theft | N/A | N/A | N/A | N/A
20231362 | PG&E | 2023-12-17 | 23:35 | 37.1838 | -120.5876 | Vegetation | N/A | Herbaceous | Less Than .25 Acres | Fire Agency | CAL FIRE | 101079878 | Yes | 12000 | Conductor - Primary | Overhead | Yes | 2023-12-17 | 23:28 | Equipment/Facility Failure | Conductor - Primary | N/A | N/A | N/A
20231383N | PG&E | 2023-12-20 | 7:23 | 37.2708 | -121.9459 | Vegetation | N/A | Urban | Structure Only | Fire Agency | SJFD | 107279884 | Yes | 12000 | Unknown | Overhead | Yes | 2023-12-20 | 7:21 | Unknown | N/A | N/A | N/A | N/A