## 2023 CPUC Reportable
Utility Name | Fire Start |  | Location |  |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations
| Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | HFRA | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
SCE | 2023-01-14 | 22:18 | 33.9193 | -118.0784 | Vegetation | Urban | non-HFTD | Less Than .25 Acres | Fire agency | Los Angeles County Fire Department | OH-977927E | Frontier Communications | 12 | Conductor | Overhead | Yes | 2023-01-14 | 18:08 | Contact From Object |  | Vegetation | Electric Facility | Weather
SCE | 2023-02-14 | 21:29 | 33.7099 | -117.9324 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Local FD | OH-1805980E | None | 12 | Other | Overhead | Yes | 2023-02-14 | 21:09 | Equipment failure | Connector |  |  | Unknown
SCE | 2023-02-24 | 6:41 | 36.3202 | -119.294 | Other | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Visalia Fire Department | OH-1757703E | AT&T California | 12 | Conductor | Overhead | Yes | 2023-02-24 | 6:41 | Wire-to-wire contact |  |  |  | Unknown
SCE | 2023-02-25 | 2:15 | 33.9212 | -118.1997 | Other | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Los Angeles County Fire Department | OH-680647E | AT&T California | 16 | Conductor | Overhead | Yes | 2023-02-25 | 1:38 | Lightning | Pole |  |  | Weather
SCE | 2023-02-26 | 16:05 | 33.5824 | -114.6919 | Vegetation | Rural | non-HFTD | Less Than .25 Acres | Fire agency | Riverside County Fire | OH-1992363E | None | 12 | Other | Overhead | Yes | 2023-02-26 | 6:08 | Equipment failure | Insulator |  |  | Weather
SCE | 2023-03-01 | 2:26 | 36.2154 | -119.0963 | Structure | Urban | non-HFTD | Less Than .25 Acres | Fire agency | Tulare County Fire Department | OH-572982E | Frontier Communications | 12 | Conductor | Overhead | Yes | 2023-03-01 | 2:26 | Contact From Object |  | Vegetation | Electric Facility | Weather
SCE | 2023-03-03 | 14:38 | 34.0579 | -117.6826 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Montclair Fire Department | OH-1072092E | Frontier Communications | 12 | Other | Overhead | Yes | 2023-03-03 | 13:07 | Equipment failure | Connector |  |  | Unknown
SCE | 2023-03-14 | 16:48 | 34.2792 | -119.1299 | Other | Urban | HFTD Tier 2 | Less Than .25 Acres | Fire agency | Local FD | OH-1946818E | AT&T California | 16 | Other | Overhead | No |  |  | Equipment failure | Insulator |  |  | Weather
SCE | 2023-04-03 | 16:58 | 34.5475 | -117.2171 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Unknown |  | OH-3006101E | None | 12 | Conductor | Overhead | Yes | 2023-04-03 | 15:48 | Equipment failure | Insulator |  |  | Unknown
SCE | 2023-04-25 | 8:49 | 33.8897 | -117.2305 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Self-extinguished |  | OH-2173288E | Frontier Communications | 12 | Conductor | Overhead | No |  |  | Vandalism/theft | Pole |  |  | Outside Force
SCE | 2023-04-28 | 12:16 | 34.514 | -117.3814 | Vegetation | Rural | non-HFTD | Less Than .25 Acres | Fire agency | Victorville Fire Department | OH-1756806E | None | 12 | Other | Overhead | Yes | 2023-04-28 | 12:16 | Contact From Object |  | Ballons | Electric Facility | Outside Force
SCE | 2023-05-07 | 13:58 | 34.532 | -117.2796 | Vegetation | Rural | non-HFTD | Less Than .25 Acres | Fire agency | Apple Valley Fire Department | OH-81314S | None | 33 | Lightning Arrestor | Overhead | Yes | 2023-05-07 | 13:52 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2023-05-08 | 2:48 | 34.1129 | -117.2252 | Vegetation | Urban | non-HFTD | Less Than .25 Acres | Unknown |  | OH-2357048E | AT&T California | 12 | Conductor | Overhead | No |  |  | Vandalism/theft | Transformer |  |  | Outside Force
SCE | 2023-05-08 | 8:33 | 34.5927 | -117.3256 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Self-extinguished |  | OH-4877541E | None | 33 | Switch | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2023-05-12 | 18:30 | 35.0665 | -118.1825 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Unknown |  | OH-1986855E | AT&T California | 12 | Other | Overhead | No |  |  | Equipment failure | Connector |  |  | Weather
SCE | 2023-05-13 | 9:18 | 34.6754 | -118.0722 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Los Angeles County Fire Department | OH-457620E | None | 12 | Conductor | Overhead | Yes | 2023-05-13 | 8:25 | Contact From Object |  | Vehicle | Pole | Unknown
SCE | 2023-05-13 | 16:39 | 33.8676 | -118.3352 | Vegetation | Urban | non-HFTD | Less Than .25 Acres | Unknown |  | OH-1319282E | None | 16 | Lightning Arrestor | Overhead | No |  |  | Equipment failure | Lightning Arrester |  |  | Unknown
SCE | 2023-05-21 | 22:08 | 33.8087 | -118.1731 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency |  | OH-1709967E | None | 12 | Conductor | Overhead | Yes | 2023-05-21 | 20:25 | Contact From Object |  | Ballons | Electric Facility | Unknown
SCE | 2023-05-22 | 15:38 | 34.0425 | -118.143 | Vegetation | Urban | non-HFTD | Less Than .25 Acres | Fire agency | Local FD | OH-4435916E | AT&T California, Crown Castle NG West | 16 | Other | Overhead | No |  |  | Contact From Object |  | Ballons | Electric Facility | Unknown
SCE | 2023-05-25 | 16:15 | 34.0718 | -118.0755 | Vegetation | Urban | non-HFTD | Less Than .25 Acres | Unknown |  | OH-818975E | AT&T CALIFORNIA, VERIZON WIRELESS, FRONTIER, TELEPORT COMMUNICATIONS AMERICA, LL | 16 | Conductor | Overhead | Yes | 2023-05-25 | 13:53 | Contact From Object |  | Ballons | Electric Facility | Unknown
SCE | 2023-06-01 | 11:59 | 35.293 | -116.082 | Vegetation | Rural | non-HFTD | Less Than .25 Acres | Fire agency |  | OH-4014965E | None | 12 | Transformer | Overhead | Yes | 2023-06-01 | 10:17 | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2023-06-02 | 14:29 | 33.8453 | -116.5135 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency |  | OH-4636036E | Frontier Communications | 12 | Other | Overhead | Yes | 2023-06-02 | 11:44 | Equipment failure | Pole |  |  | Unknown
SCE | 2023-06-04 | 23:59 | 36.0804 | -119.1699 | Vegetation | Rural | non-HFTD | Less Than .25 Acres | Fire agency | Tulare County Fire Department | OH-4672385E | None | 12 | Conductor | Overhead | Yes | 2023-06-04 | 22:05 | Contact From Object |  | Vehicle | Pole | Unknown
SCE | 2023-06-06 | 11:28 | 35.648 | -117.6914 | Other | Urban | non-HFTD | Less Than .25 Acres | Fire agency | Kern County Fire Department | OH-2056033E | None | 12 | Transformer | Overhead | No |  |  | Contact From Object |  | Vehicle | Pole | Unknown
SCE | 2023-06-07 | 16:59 | 35.7491 | -117.8558 | Vegetation | Rural | non-HFTD | Less Than .25 Acres | Unknown | Kern County Fire Department | OH-2110153E | Frontier Communications | 12 | Other | Overhead | Yes | 2023-06-07 | 8:27 | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2023-06-09 | 21:19 | 34.3194 | -119.2905 | Vegetation | Urban | HFTD Tier 3 | Less Than .25 Acres | Fire agency | Ventura County Fire Department | OH-4204614E | None | 16 | Other | Overhead | Yes | 2023-06-09 | 21:19 | Equipment failure | Switch |  |  | Unknown
SCE | 2023-06-16 | 11:27 | 36.2122 | -119.2803 | Vegetation | Rural | non-HFTD | Less Than .25 Acres | Fire agency | Tulare County Fire | OH-2321438E | None | 12 | Lightning Arrestor | Overhead | Yes | 2023-06-16 | 9:59 | Equipment failure | Lightning Arrester |  |  | Unknown
SCE | 2023-06-17 | 16:07 | 37.3804 | -118.489 | Other | Rural | non-HFTD | Less than three (3) meters of linear travel | Fire agency |  | OH-4120889E | Frontier Communications | 12 | Conductor | Overhead | Yes | 2023-06-17 | 16:07 | Contact From Object |  | Vehicle | Pole | Unknown
SCE | 2023-06-22 | 16:00 | 36.312 | -119.1702 | Vegetation | Rural | non-HFTD | Less Than .25 Acres | Fire agency |  | OH-4632054E | None | 12 | Conductor | Overhead | Yes | 2023-06-22 | 15:22 | Equipment failure | Splices |  |  | Unknown
SCE | 2023-06-23 | 3:31 | 35 | -119 | Vegetation | Rural | non-HFTD | .26 - 9.99 Acres | Unknown |  | M120 T5 | None | 220 | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2023-06-26 | 14:00 | 33.9638 | -118.1036 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency |  | OH-856190E | Frontier | 4.16 | Conductor | Overhead | Yes | 2023-06-26 | 13:27 | Equipment failure | Connector |  |  | Unknown
SCE | 2023-07-03 | 9:51 | 33.9848 | -117.8628 | Structure | Unknown | HFTD Tier 2 | Less than three (3) meters of linear travel | Fire agency | Los Angeles County Fire Department | UG-5163274 | None | 12 | Conductor | Underground | No |  |  | Equipment failure | Conductor |  |  | Unknown
SCE | 2023-07-03 | 19:35 | 33.8508 | -116.5275 | Other | Urban | non-HFTD | Less than three (3) meters of linear travel | Self-extinguished |  | OH-4627868E | Frontier | 12 | Conductor | Overhead | Yes | 2023-07-03 | 18:09 | Equipment failure | Cable |  |  | Unknown
SCE | 2023-07-03 | 21:12 | 33.6843 | -117.2097 | Vegetation | Unknown | HFTD Tier 2 | Less than three (3) meters of linear travel | Self-extinguished |  | UG-5536213 | None | 12 | Other | Underground | Yes | 2023-07-03 | 17:57 | Equipment failure | Underground |  |  | Unknown
SCE | 2023-07-05 | 1:24 | 33.7774 | -118.1617 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Self-extinguished |  | OH-797595E | Frontier | 4.16 | Other | Overhead | No |  |  | Equipment failure | Cable |  |  | Unknown
SCE | 2023-07-05 | 8:56 | 34.6471 | -118.1699 | Vegetation | Urban | non-HFTD | .26 - 9.99 Acres | Fire agency | Los Angeles County Fire Department | OH-2038927E | Frontier | 12 | Other | Overhead | Yes | 2023-07-05 | 8:09 | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2023-07-05 | 14:18 | 33.7719 | -117.9103 | Vegetation | Urban | non-HFTD | Less Than .25 Acres | Unknown |  | OH-1253344E | None | 12 | Conductor | Overhead | Yes | 2023-07-05 | 11:33 | Contact From Object |  | Ballons | Electric Facility | Unknown
SCE | 2023-07-06 | 12:00 | 33.7873 | -116.9875 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Self-extinguished |  | OH-2178287E | None | 12 | Conductor | Overhead | No |  |  | Equipment failure | Conductor |  |  | Unknown
SCE | 2023-07-07 | 13:44 | 33.7428 | -117.1648 | Vegetation | Rural | non-HFTD | .26 - 9.99 Acres | Unknown |  | OH-2224882E | Frontier | 12 | Switch | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2023-07-08 | 0:00 | 34.0949 | -117.9014 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency |  | OH-1942404E | Frontier | 12 | Conductor | Overhead | No |  |  | Contact From Object |  | Ballons | Electric Facility | Unknown
SCE | 2023-07-09 | 0:37 | 37.1579 | -118.2985 | Vegetation | Rural | HFTD Tier 3 | Less Than .25 Acres | Fire agency | Cal Fire | OH-12034 | None | 115 | Conductor | Overhead | No |  |  | Equipment failure | Conductor |  |  | Unknown
SCE | 2023-07-10 | 7:10 | 33.7598 | -117.849 | Other | Unknown | non-HFTD | Less than three (3) meters of linear travel | Self-extinguished |  | UG-5071406 | None | 12 | Conductor | Underground | No |  |  | Equipment failure | Cable |  |  | Unknown
SCE | 2023-07-12 | 12:08 | 34.4433 | -119.508 | Vegetation | Rural | HFTD Tier 3 | .26 - 9.99 Acres | Fire agency | Ventura County FD | OH-4425342E | None | 66 | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2023-07-13 | 20:46 | 34.0473 | -117.6743 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Local FD | OH-779457E | None | 12 | Other | Overhead | No |  |  | Equipment failure | Pothead |  |  | Unknown
SCE | 2023-07-14 | 19:04 | 34.0028 | -117.9947 | Other | Urban | HFTD Tier 2 | .26 - 9.99 Acres | Unknown |  | OH-80510E | None | 12 | Other | Overhead | Yes | 2023-07-14 | 12:02 | Equipment failure | Transformer |  |  | Unknown
SCE | 2023-07-15 | 11:48 | 34.5541 | -118.6655 | Vegetation | Rural | HFTD Tier 3 | Less than three (3) meters of linear travel | Fire agency | Local FD | OH-7022774 | None | 220 | Conductor | Overhead | No |  |  | Equipment failure | Conductor |  |  | Unknown
SCE | 2023-07-16 | 1:03 | 34.552 | -118.6621 | Vegetation | Rural | HFTD Tier 3 | Less Than .25 Acres | Fire agency | Local FD | OH-1848178E | None | 16 | Lightning Arrestor | Overhead | No |  |  | Wire-to-wire contact |  |  |  | Unknown
SCE | 2023-07-20 | 12:27 | 33.7153 | -117.1827 | Vegetation | Urban | non-HFTD | .26 - 9.99 Acres | Fire agency | Local FD | OH-4234514E | None | 12 | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2023-07-22 | 14:05 | 36.4028 | -119.0991 | Vegetation | Rural | non-HFTD | Less than three (3) meters of linear travel | Fire agency |  | UG-755266E | None | 12 | Other | Underground | No |  |  | Equipment failure | Conductor |  |  | Unknown
SCE | 2023-07-23 | 9:51 | 33.7509 | -117.1827 | Vegetation | Urban | non-HFTD | .26 - 9.99 Acres | Fire agency | Riverside County Fire | OH-4269395E | None | 12 | Conductor | Overhead | Yes | 2023-07-23 | 9:51 | Contact From Object |  | Ballons | Electric Facility | Outside Force
SCE | 2023-07-25 | 12:39 | 34.1013 | -117.3681 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Rialto Fire Department | ES-8225-0033-XF-2-ABC | None | 12 | Transformer | Overhead | Yes | 2023-07-25 | 12:35 | Vandalism/theft | Transformer |  |  | Outside Force
SCE | 2023-07-26 | 2:52 | 34.548 | -117.2805 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Local FD | UG-5588536 | None | 12 | Other | Underground | No |  |  | Equipment failure | Connector |  |  | Unknown
SCE | 2023-08-04 | 11:39 | 34.2141 | -117.3939 | Vegetation | Urban | HFTD Tier 2 | Less than three (3) meters of linear travel | Fire agency | Local FD | OH-4923136E | None | 12 | Conductor | Overhead | No |  |  | Equipment failure | Connector |  |  | Unknown
SCE | 2023-08-07 | 10:51 | 34.6292 | -118.2365 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Utility |  | OH-1373589E | Frontier Communications | 12 | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2023-08-08 | 5:21 | 34.2432 | -119.2474 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Ventura County FD | OH-1643591E | None | 16 | Conductor | Overhead | No |  |  | Contamination |  |  |  | Weather
SCE | 2023-08-08 | 12:53 | 34.118 | -117.2205 | Structure | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Local FD | OH-225116E | AT&T California | 12 | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2023-08-12 | 20:47 | 33.9282 | -116.4513 | Vegetation | Unknown | non-HFTD | Less than three (3) meters of linear travel | Customer |  | UG-5002996 | None | 12 | Conductor | Underground | Yes | 2023-08-12 | 17:56 | Equipment failure | Cable |  |  | Unknown
SCE | 2023-08-15 | 16:56 | 34.0454 | -118.9351 | Vegetation | Urban | HFTD Tier 3 | Less Than .25 Acres | Fire agency | Local FD | OH-1408752E | Frontier Communications | 16 | Conductor | Overhead | No |  |  | Equipment failure | Insulator |  |  | Unknown
SCE | 2023-08-17 | 13:47 | 34.039 | -118.5868 | Other | Rural | HFTD Tier 2 | Less than three (3) meters of linear travel | Self-extinguished |  | OH-1027887E | FRONTIER,Crown Castle NG West, Inc,VERIZON WIRELESS | 16 | Other | Overhead | Yes | 2023-08-17 | 13:31 | Equipment failure | Transformer |  |  | Unknown
SCE | 2023-08-21 | 12:41 | 34.0134 | -118.1648 | Other | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency |  | OH-937235E | None | 16 | Conductor | Overhead | Yes | 2023-08-21 | 9:43 | Equipment failure | Insulator |  |  | Unknown
SCE | 2023-08-23 | 22:31 | 35.7905 | -119.0266 | Vegetation | Rural | non-HFTD | .26 - 9.99 Acres | Fire agency | Cal Fire | OH-4836501E | None | 12 | Other | Overhead | Yes | 2023-08-23 | 22:32 | Equipment failure | Fuse |  |  | Weather
SCE | 2023-08-29 | 17:02 | 34.1289 | -118.0835 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Los Angeles County Fire Department | OH-1724182E | AT&T California | 4.16 | Conductor | Overhead | Yes | 2023-08-29 | 16:15 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2023-09-02 | 17:15 | 34.0408 | -118.1059 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Local FD | OH-4516571E | AT&T California | 16 | Other | Overhead | Yes | 2023-09-02 | 14:49 | Equipment failure | Pothead |  |  | Weather
SCE | 2023-09-10 | 7:59 | 34.4708 | -117.2494 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Self-extinguished |  | OH-4006526E | None | 12 | Conductor | Overhead | Yes | 2023-09-10 | 7:59 | Contact From Object |  | Ballons | Electric Facility | Outside Force
SCE | 2023-09-10 | 9:30 | 35.9643 | -119.042 | Other | Rural | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Tulare County Fire Department | OH-4864682e | AT&T CALIFORNIA | 12 | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2023-09-12 | 4:10 | 33.9238 | -118.313 | Other | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Los Angeles County Fire Department | OH-831783E | AT&T CALIFORNIA | 16 | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2023-09-14 | 3:00 | 36.0657 | -119.0024 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | porterville fire dept | OH-10262T | AT&T CALIFORNIA | 12 | Fuse | Overhead | Yes | 2023-09-14 | 2:51 | Equipment failure | Cable |  |  | Unknown
SCE | 2023-09-24 | 9:45 | 34.3665 | -116.9158 | Vegetation | Rural | HFTD Tier 2 | Less than three (3) meters of linear travel | Fire agency | San Bernardino County Fire | OH-4962759E | None | 33 | Conductor | Overhead | Yes | 2023-09-24 | 6:44 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2023-09-27 | 10:33 | 34.0192 | -117.1498 | Vegetation | Urban | HFTD Tier 3 | Less than three (3) meters of linear travel | Fire agency |  | OH-4016098E | FRONTIER | 12 | Conductor | Overhead | Yes | 2023-09-27 | 8:00 | Contact From Object |  | 3rd party facility | Electric Facility | Outside Force
SCE | 2023-10-02 | 15:36 | 36.2132 | -119.328 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Tulare County Fire Department | OH-885169E | None | 12 | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2023-10-04 | 17:08 | 36.3593 | -119.1526 | Vegetation | Rural | non-HFTD | .26 - 9.99 Acres | Self-extinguished |  | OH-4622260E | None | 12 | Conductor | Overhead | Yes | 2023-10-04 | 17:07 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2023-10-06 | 23:34 | 34.0051 | -118.0683 | Vegetation | Urban | non-HFTD | Less Than .25 Acres | Fire agency | Los Angeles County Fire Department | OH-4506227E | None | 12 | Other | Overhead | Yes | 2023-10-06 | 23:08 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2023-10-09 | 20:57 | 33.5847 | -117.1179 | Vegetation | Rural | HFTD Tier 2 | .26 - 9.99 Acres | Fire agency | Riverside County Fire Department | OH-4402000E | None | 12 | Conductor | Overhead | Yes | 2023-10-09 | 18:44 | Equipment failure | Splices |  |  | Unknown
SCE | 2023-10-11 | 14:00 | 34.101 | -118.1579 | Other | Urban | non-HFTD | Less Than .25 Acres | Fire agency | Pasadena Fire Department | OH-203013E | AT&T CALIFORNIA | 16 | Conductor | Overhead | Yes | 2023-10-11 | 11:40 | Equipment failure | Splices |  |  | Unknown
SCE | 2023-10-14 | 0:34 | 34.2433 | -119.2154 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Ventura County Fire Department | OH-1024615E | AT&T CALIFORNIA | 16 | Conductor | Overhead | Yes | 2023-10-13 | 23:32 | Equipment failure | Conductor |  |  | Unknown
SCE | 2023-10-23 | 5:31 | 33.8695 | -118.2092 | Other | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Los Angeles Fire Department | OH-4074928e | None | 16 | Conductor | Overhead | Yes | 2023-10-23 | 3:59 | Vandalism/theft | Cable |  |  | Unknown
SCE | 2023-10-26 | 16:44 | 33.9807 | -117.0503 | Vegetation | Rural | HFTD Tier 3 | Less Than .25 Acres | Fire agency | Riverside County Fire Department | OH-4331309E | FRONTIER | 12 | Lightning Arrestor | Overhead | Yes | 2023-10-26 | 14:44 | Equipment failure | Lightning Arrester |  |  | Unknown
SCE | 2023-10-29 | 13:49 | 35.6025 | -119.0875 | Vegetation | Rural | non-HFTD | .26 - 9.99 Acres | Fire agency | Kern County Fire Department | M121T | None | 220 | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2023-10-29 | 18:10 | 35.1323 | -117.9311 | Vegetation | Rural | non-HFTD | Less than three (3) meters of linear travel | Unknown |  | UG-5000049 | None | 12 | Conductor | Underground | Yes | 2023-10-29 | 18:06 | Vandalism/theft | Conductor |  |  | Outside Force
SCE | 2023-10-29 | 18:39 | 34.2566 | -118.6419 | Vegetation | Rural | HFTD Tier 3 | Less Than .25 Acres | Fire agency | Ventura County Fire Department | OH-3004910E | AT&T CALIFORNIA | 16 | Conductor | Overhead | Yes | 2023-10-29 | 13:52 | Equipment failure | Conductor |  |  | Weather
SCE | 2023-10-30 | 3:58 | 34.2191 | -117.6617 | Vegetation | Rural | HFTD Tier 3 | .26 - 9.99 Acres | Fire agency | Angeles Fire | OH-454329E | FRONTIER | 12 | Conductor | Overhead | Yes | 2023-10-30 | 3:00 | Contact From Object |  | Vegetation | Electric Facility | Weather
SCE | 2023-11-08 | 11:09 | 34.0828 | -117.2953 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Unknown |  | UG-5055195 | None | 12 | Transformer | Underground | Yes | 2023-11-08 | 10:26 | Equipment failure | Cable |  |  | Unknown
SCE | 2023-11-15 | 7:40 | 34.0435 | -118.1878 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Los Angeles Fire Department | OH-1614974E | Crown Castle NG West, Inc | 4.16 | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2023-11-20 | 7:45 | 33.7503 | -117.8289 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Orange County Fire Authority | OH-1568821E | None | 12 | Conductor | Overhead | Yes | 2023-11-20 | 6:02 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2023-11-20 | 20:14 | 34.1232 | -117.3217 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Local FD | OH-827372E | FRONTIER | 12 | Conductor | Overhead | Yes | 2023-11-20 | 17:11 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2023-12-08 | 11:02 | 33.7662 | -117.9938 | Vegetation | Urban | non-HFTD | Less Than .25 Acres | Fire agency | Orange County Fire Authority | OH-4400521E | FRONTIER | 12 | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2023-12-10 | 11:13 | 34.4347 | -118.531 | Vegetation | Urban | HFTD Tier 3 | Less Than .25 Acres | Fire agency | Los Angeles County Fire Department | OH-1712771E | None | 16 | Transformer | Overhead | Yes | 2023-12-10 | 7:04 | Equipment failure | Transformer |  |  | Unknown
SCE | 2023-12-10 | 12:16 | 33.8967 | -118.3296 | Structure | Urban | non-HFTD | Less than three (3) meters of linear travel | Fire agency | Los Angeles County Fire Department | OH-1791416E | AT&T CALIFORNIA | 4.16 | Conductor | Overhead | No |  |  | Equipment failure | Conductor |  |  | Unknown
SCE | 2023-12-21 | 17:19 | 33.757 | -116.4397 | Vegetation | Urban | non-HFTD | Less than three (3) meters of linear travel | Self-extinguished |  | UG-5002901 | None | 12 | Other | Underground | Yes | 2023-12-21 | 17:25 | Equipment failure | Connector |  |  | Unknown
SCE | 2023-12-14 | 14:16 | 34.1394 | -117.3793 | Structure | Urban | non-HFTD | Less Than .25 Acres | Fire agency | San Bernardino County Fire | OH-X5249E | AT&T CALIFORNIA | 12 | Conductor | Overhead | No |  |  | Vandalism/theft |  |  |  | Outside Force
Note on B2: Date the event started (Use MM/DD/YY when inputting dates)
Note on C2: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on D2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on E2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on F2: Material involved in the initial fueling of the fire;
Note on G2: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on I2: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on J2: Is who suppressed the fire
Note on L2: Utility’s description of the pole and/or equipment involved.
Note on M2: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on N2: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on O2: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on P2: The equipment involved in the event (overhead, padmounted or subsurface);
Note on Q2: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on R2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on S2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on T2: The suspected cause of the ignition;
Note on U2: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on V2: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on W2: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on X2: Factors that contributed to the ignition;