## Cover sheet
On November 29, 2021, PG&E, SCE and SDG&E jointly provided feedback to the Safety and Enforcement Division (SED), identifying items in the Post Season Data Report (formerly Post-Season Report 2) that were infeasible or not applicable. Accordingly, there are several items throughout this data report that are populated as "N/A" because these data points either cannot be tracked retroactively and/or are not used by PG&E in our PSPS decision making. These data points were also not required by any of the Commission decisions, including Resolution ESRB-8, D.19-05-042 (Phase 1), D.20-05-051 (Phase 2), D.21-06-034 (Phase 3), and D. 21-06-014 (PSPS OII), or the Post Event Report (PER) template provided in October 2021.
In addition, several tables in the Post Season Data Report have footnotes and notes at the bottom of the table. In instances where PG&E needed to provide remarks on an individual metric or data point, notes were created in a column labeled "PG&E Remarks". The PSDR includes the best information currently available to date.

## 1.Instructions
EVENTS TO DATE, JANUARY 1 2021 - DECEMBER 31 2021
Utility | Event Name/ Date of De-en | Beginning | End
SCE | 2021-01-14 | 2021-01-14 | 2021-01-15
SDG&E | Cancelled | 2021-01-14
SCE | 2021-01-16 | 2021-01-16 | 2021-01-17
PG&E | 2021-01-18 | 2021-01-18 | 2021-01-26
SCE | 2021-01-18 | 2021-01-18 | 2021-01-20
SCE | 2021-04-13 | 2021-04-13 | 2021-04-13
SCE | Cancelled | 2021-06-14
PacifiCorp | 2021-08-17 | 2021-08-17 | 2021-08-18
PG&E | 2021-08-17 | 2021-08-17 | 2021-08-19
Liberty | Cancelled | 2021-09-19
PG&E | 2021-09-20 | 2021-09-20 | 2021-09-21
SCE | 2021-09-30 | 2021-09-30 | 2021-09-30
PG&E | 2021-10-11 | 2021-10-11 | 2021-10-14
SCE | 2021-10-11 | 2021-10-11 | 2021-10-12
PG&E | 2021-10-15 | 2021-10-15 | 2021-10-16
SCE | 2021-10-15 | 2021-10-15 | 2021-10-16
SCE | Cancelled | 2021-10-16
SCE | 2021-11-21 | 2021-11-21 | 2021-11-22
SCE | 2021-11-24 | 2021-11-24 | 2021-11-26
SDG&E | 2021-11-24 | 2021-11-24 | 2021-11-26
NOTE:
Workbook is for actual de-energizations only.
INSTRUCTIONS:
See detailed Instructions in Word doc.
1. Do not merge cells.
2. Name file according to the following protocols:
syntax: | <Utility Abbreviation>_PSDR_<Submission Date>
examples: | PGE_PSDR_4-1-2022
PacifiCorp_PSDR_4-1-2022
3. Group the metrics in the Dashboard as organized in the template prior to submission.
Topical Worksheets:
4. Populate all topical worksheets with data from all implemented PSPS events
Dashboard worksheet:
5. Ungroup the relevant set of metrics you want to work with.
6. Direct input data into columns B-L as applicable.
7. Formula reference cells will autopopulate if data is properly entered into the data source cells.
8. Trendline formulas will be added after submission.
9. Use the "Annual or Cumulative" Total column where indicated in the Metrics column.

## 2.Acronyms
Acronym | Stands For
AFN | Access and Functional Needs
CFCI | Critical Facilities and Critical Instrastructure
CSP | Communications Services Provider
EM | Emergency Management
EOC | Emergency Operations Center
ERRA | Energy Resource Recovery Account
GIS | Geographic Information System
HFTD | High Fire-Threat District
JPG | JUPSPSWG
JUPSPSWG | Joint Utility Public Safety Power Shutoff Working Group
LL and BP | Lessons Learned and Best Practices
MBL | Medical Baseline
NIMS | National Incident Management System
PER | Post-Event Report
PII | Personally Identifiable Information
POC | Point of Contact [Utilities use POC to mean "Period of Concern" in a PSPS event]
POSTSR | Post-Season Report
PRESR | Pre-Season Report
PSDR | Post-Season Data Report
PSP | Public Safety Partner
PSPS | Public Safety Power Shutoff
SED | Safety and Enforcement Division
SEMS | Standardized Emergency Management System
WMP | Wildfire Mitigation Plan

## 3.CPUC Definitions
DEFINITIONS
Term | Reference Worksheet | Definition
Accounts | Various | Service points or meter
AFN | Various | See AB 477, effective 9/4/2019
CARE | Various | CARE is a state mandated program. As determined by PU Code Section 739.1(a), annual household must be no greater than 200% of the federal poverty guideline levels.
CFCI type | 14. CONF-CFCI | Worksheet "4. Defn CFCI" and https://www.cisa.gov/critical-infrastructure-sectors
CRC type | 17. CRCs | Indoor (brick and mortar), Outdoor, Mobile (Van)
De-energization Exercise Type | 21. EM and Exercises | See description of exersizes in the HSEEP Manual, Jan. 2020 at https://www.fema.gov/sites/default/files/2020-04/Homeland-Security-Exercise-and-Evaluation-Program-Doctrine-2020-Revision-2-2-25.pdf, pp. 2-6 to 2-11
EV charging station levels | 8. Dashboard | Level 1 Charging: 120-Volt; Connectors Used: J1772, Tesla; Charging Speed: 3 to 5 Miles Per Hour Level 2 Charging: 208-Volt to 240-Volt; Connectors Used: J1772, Tesla; Charging Speed: 12 to 80 Miles Per Hour Level 3 Charging: 400-Volt to 900-Volt (DC Fast Charge & Supercharging); Connectors Used: Combined Charging System (Combo), CHAdeMO & Tesla; Charging Speed: 3 to 20 Miles Per Minute
FERA | Various | FERA is a program established by the Commission for households of three or more having incomes between 200% and 250% of federal poverty guidelines. PU Code Section 739.12
Full-Scale Exercise | 7. Data Dictionary, 21. EM and Exercises | See De-energization Exercise Type above
Functional Exercise | 7. Data Dictionary, 21. EM and Exercises | See De-energization Exercise Type above
HFTD Tier | Various | Tier 1 (High Hazard Zone), 2, and 3 are explained here: https://www.cpuc.ca.gov/industries-and-topics/wildfires/fire-threat-maps-and-fire-safety-rulemaking
Life support | Various | "...those customers that require critical life support equipment at their home." Ibid., p. 43. PG&E uses the terms life support; SCE and SDG&E use the term critical care.
MBL | Various | Defined in D.19-05-042. Established in the State Baseline Act of 1976 (PU Code Section 739 (c). Residential customers who have special medical needs and/or are dependent on life-support equipment. "Life support equipment" means equipment that uses mechanical or artificial means to sustain, restore, or supplant a vital function, or mechanical equipment that is relied upon for mobility both within and outside of buildings. This includes: § All types of respirators, iron lungs, hemodialysis machines, suction machines, electric nerve stimulators, pressure pads and pumps, aerosol tents, electrostatic and ultrasonic nebulizers, compressors, IPBB machines and motorized wheelchairs. Also, in consideration of their increased heating and cooling needs, the Medical Baseline allowance is available to: Paraplegics and quadriplegics, multiple sclerosis patients, scleroderma patients, and people being treated for a life threatening illness or who have a compromised immune system. (https://www.cpuc.ca.gov/medicalbaseline/, accessed April 16, 2021)
Mitigation (PSPS) | 16. Mitigation | Backup generation, Backup storage, Dx microgrid, Islanding, Patrols, Sectionalization, Switching, Temporary substation microgrid, Tx switching, Vegetation management (expedite priority trees that prevent circuit from being removed from scope)
Public Safety Partner | Various | See worksheet "5. Defn PSP"
Table Top Exercise | 7. Data Dictionary, 21. EM and Exercises | See De-energization Exercise Type above

## 4.Defn CFCI
Sector | Entities
Emergency Services Sector | Police Stations
Emergency Services Sector | Fire Stations
Emergency Services Sector | Emergency Operations Centers
Emergency Services Sector | Tribal government providers
Emergency Services Sector | Fire Departments
Emergency Services Sector | Water Plants
Government Facilities Sector | Schools and licensed daycare centers;
Government Facilities Sector | Homeless Shelters
Government Facilities Sector | Community Centers
Government Facilities Sector | Senior Centers
Government Facilities Sector | Independent Living Centers, as defined by the California Department of Rehabilitation
Government Facilities Sector | Voting centers and vote tabulation facilities
Government Facilities Sector | Jails and prisons
Healthcare and Public Health Sector | Public Health Departments
Healthcare and Public Health Sector | Medical facilities
Healthcare and Public Health Sector | hospitals
Healthcare and Public Health Sector | skilled nursing facilities
Healthcare and Public Health Sector | nursing homes
Healthcare and Public Health Sector | blood banks
Healthcare and Public Health Sector | health care facilities centers and hospice facilities
Healthcare and Public Health Sector | dialysis centers
Healthcare and Public Health Sector | hospice facilities
Healthcare and Public Health Sector | Cooling (or Warming) Centers
Healthcare and Public Health Sector | Temporary facilities established for public health emergencies
Water and Wastewater Systems Sector | Facilities associated with the provision of drinking water or processing of wastewater including facilities used to pump, divert, transport, store, treat and deliver water or wastewater
Food and Agriculture Sector | Emergency Feeding Organization, as defined in 7 U.S.C. § 7501. e.
Transportation Systems Sector | transportation facilities and infrastructure
Transportation Systems Sector | facilities associated with automobile, rail, aviation and maritime transportation for civilian and military purposes
Transportation Systems Sector | Traffic Management Systems
Energy Sector | Public and private utility facilities vital to maintaining or restoring normal service, including, but not limited to,
Energy Sector | interconnected publicly-owned utilities and electric cooperatives
Energy Sector | Facilities associated with the provision of drinking water including facilities used to pump, divert, transport, store, treat and deliver water;
Communications Sector | Communication carrier infrastructure including
Communications Sector | selective routers,
Communications Sector | central offices,
Communications Sector | head ends,
Communications Sector | cellular switches,
Communications Sector | remote terminals
Communications Sector | cellular sites (or their functional equivalents)
Chemical Sector | Facilities associated with the provision of manufacturing, maintaining, or distributing hazardous materials and chemicals

## 5.Defn PSP
Public Safety Partners are defined as follows:
· First/Emergency Responders (individuals who, in the early stages of an incident, are responsible for the protection and preservation of life, property, evidence, and the environment), including
· Emergency Response Providers
o public safety emergency response providers at the tribal, federal, state, and local governmental and nongovernmental levels
o fire emergency response providers at the tribal, federal, state, and local governmental and nongovernmental levels
o law enforcement emergency response providers at the tribal, federal, state, and local governmental and nongovernmental levels
o emergency response emergency response providers at the tribal, federal, state, and local governmental and nongovernmental levels
o emergency medical services providers (including hospital emergency facilities) emergency response providers at the tribal, federal, state, and local governmental and nongovernmental levels
o related personnel, agencies and authorities emergency response providers at the tribal, federal, state, and local governmental and nongovernmental levels
· water service providers at the tribal, local, state, and federal level;
· wastewater service providers at the tribal, local, state, and federal level;
· communication service providers at the tribal, local, state, and federal level;
· community choice aggregators (CCAs) at the tribal, local, state, and federal level;
· affected publicly-owned utilities (POUs)/electrical cooperatives at the tribal, local, state, and federal level;
· the Commission;
· Cal OES;
· CAL FIRE

## 6.Utility Definitions
DEFINITIONS
Add terms in alphabetical order
Term | Worksheet Reference | Definition as Understood by the Utility
Acres burned (acres) | Decision Factors | Acres burned in the 8-hour fire spread simulation from Technosylva.
Actual Average Peak Wind Gust during Event (mph) | Decision Factors | The maximum sustained wind gust recorded by weather stations within five miles of the circuit from de-energization time to all-clear time.
Actual Relative Humidity at All Clear (%) | Decision Factors | Minimum relative humidity recorded by all weather stations within five miles of the circuit at the all-clear time.
Actual Relative Humidity During Event (%) | Decision Factors | Minimum relative humidity recorded by all weather stations within five miles of the circuit from de-energization time to all-clear time.
Actual Sustained Wind Speed at All Clear (mph) | Decision Factors | The maximum sustained wind speed recorded by weather stations within five miles of the circuit at the all-clear time.
Actual Sustained Wind Speed during Event (mph) | Decision Factors | The maximum sustained wind speed recorded by weather stations within five miles of the circuit from de-energization time to all-clear time.
Actual Temperature at All Clear(degrees F) | Decision Factors | The maximum temperature recorded by weather stations within five miles of the circuit at the all-clear time.
Actual Temperature during event (degrees F) | Decision Factors | The maximum temperature recorded by weather stations within five miles of the circuit from de-energization time to all-clear time.
Actual Wind gust at All Clear (mph) | Decision Factors | The maximum sustained wind gust recorded by weather stations within five miles of the circuit at the all-clear time.
Actual Wind gust during Event (mph) | Decision Factors | The maximum sustained wind gust recorded by weather stations within five miles of the circuit from de-energization time to all-clear time.
AFN but not MBL | Various | Access and Functional Needs category includes customers enrolled in CARE or FERA; customers that self-identify to receive an in-person visit before disconnection for non-payment (e.g., vulnerable), customers that self-identify has having a person with a disability in the household (e.g., disabled); customers who self-select to receive utility communications in a non-standard format (e.g., in braille or large print); and customers who indicate a non-English language preference
Air Quality (AQI) | Decision Factors | Not currently tracked - Not a factor for PSPS - The Air Quality does not factor into PSPS decision making.
All Clear | Various | Decision to initiate PSPS patrols and re-energization by approving the re-energization of impacted assets within the event footprint as recommended by the PSPS event meteorologist in charge
Assets conditions | Decision Factors | An evaluation of the condition of the asset based on appearance, required maintenance (and relevant tags), working ability, and quality
CFP-2021 LFP-2020 | Decision Factors | The product of probability of catastrophic fire (Prob_Cat) and IPW - probability of ignition (prob_ignition). This product is called the (CFPd) Catastrophic Fire Probability distribution model. Scaled by 1000 to covert to an integer value.
Circuit segment | Data Dictionary | Also known as a Circuit Protection Zones (CPZs) - A CPZ is a segment of a distribution circuit between two protection devices. CPZs are also sometimes referred to as circuit segments.
Dead Fuel Moisture Content 10 hrs | Decision Factors | Dead Fuel Moisture in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
Dead Fuel Moisture Content 100 hrs | Decision Factors | Dead Fuel Moisture in 100-hour moisture class. Can be scaled to percentage by multiplying by 100.
Dead Fuel Moisture Content 1000 hrs | Decision Factors | Dead Fuel Moisture in 1000-hour moisture class. Can be scaled to percentage by multiplying by 100.
Emergency website | Data Dictionary | http://www.pge.com/pspsupdates
End users served by submeters | Data Dictionary | Not currently tracked - PG&E, SCE, and SDG&E jointly submitted comments in the Post Season Data Report template to the SED on 11/29/2021 referencing that the IOUs do not currently track submeters
End-users served by master meters | Data Dictionary | In some locations, including many mobile home parks, a master PG&E meter serves the entire community. If your location is a sub-metered property (Master Meter), the property manager splits the energy costs among all tenants. Tenants pay their energy costs to the property manager, not to PG&E.
Energy Release Component (BTUs psf) | Decision Factors | PG&E does not track for the purposes of PSPS. Our FPI model is used to access the probability of catastrophic fires.
Fire Potential Index (probability outputs) | Decision Factors | Fire Potential Index (FPI) Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
Flame length (ft) | Decision Factors | Flame length in feet on fire front for first 2 hours of fire spread simulation from Technoslyva.
GACC High Risk (yes/no) | Decision Factors | High Risk issued by the Federal North or South Operations Predictive Services.
Gust wind speeds (mph) | Decision Factors | Wind gust in miles per hour at 10 meters above ground level.
Hazards or Threats Scoping Factors | Decision Factors | See Assets conditions, Vegetation conditions, Live field observation conditions, and Structural design wind speed ratings
High Wind Advisory (yes/no) | Decision Factors | High Wind Advisory from the Federal National Weather Service.
High Wind Warning (yes/no) | Decision Factors | High Wind Warning from the Federal National Weather Service.
Ignition Probability Weather Model | Decision Factors | A model that provides estimates of the probability of an ignition given an outage on an hourly basis
Impacted by Transmission | Decision Factors | Distribution lines that would have been de-energized due to de-energization of upstream transmission lines, regardless of whether those distribution lines would have also been de-energized due to direct distribution PSPS.
Live field observation conditions | Decision Factors | Real-time observations of weather stations, satellite data, pressure gradients, real-time field observations from crews and live feeds from Alert Wildfire Camera
Live Fuel Moisture Content-herbaceous (%) | Decision Factors | Live Fuel Moisture Percentage of herbaceous plant species. (% of species that is comprised of water)
Live Fuel Moisture Content-shrub (%) | Decision Factors | Live Fuel Moisture Percentage of Chamise (shrub) plant species. (% of species that is comprised of water)
Live Fuel Moisture Content-woody (%) | Decision Factors | Live Fuel Moisture Percentage of woody plant species. (% of species that is comprised of water)
Medical Baseline (MBL) Customers | Various | MBL customers are PG&E customers who are eligible for MBL tariffs and receive an additional allotment of electricity and/or gas per month. The tariffs are designed to assist residential customers who have special energy needs due to qualifying medical conditions.
Monitoring mode | Data Dictionary | A network of weather stations, high-definition cameras and sensors, as well as state-of-the-art weather forecasting that is used by PG&E and other agencies.
Normalized Difference Vegetation Index | Decision Factors | PG&E do not track for the purposes of PSPS. Our Live Fuel Moisture - Herbaceous model is used to determine the state of the 'green up' and grass/herb receptivity to fire
Other non-account holders | Data Dictionary | PG&E, SCE, and SDG&E jointly provided comments in the Post Season Data Report Template to SED on 11/29 regarding the to reiterate that no definition was provided for 'non-account holder'; therefore, PG&E interpreted it as the same as a sub-meter account.
Peak Gusts wind speeds (mph) | Decision Factors | Wind gust in miles per hour at 10 meters above ground level.
Prob_Ignition (IPW) | Decision Factors | Ignition Probability Weather (IPW) Model Output - Probability of Ignition based on the probability of outages by cause. Ignition component of the CFPD model.
Rate of spread (chains/hr) | Decision Factors | Rate of fire spread in chains per hour for first 2 hours of fire spread simulation from Technoslyva.
Red Flag Warning (yes/no) | Decision Factors | Red Flag Warning from the Federal National Weather Service.
Relative Humidity (%) | Decision Factors | Relative Humidity in percent at 2 meters above ground level.
Run Time (hrs) | Backup Power Resources | Expected run time of generator without refueling estimated based on a 75% load. When information could not be obtained, the run time was estimated on run times of generators with similar capacity (MW). Run times might vary according to generator manufacturer. Barring mechanical failure and refueling the temporary generators have the ability to operate continuously throughout a typical PSPS event.
Santa Ana Wildfire Threat Index | Decision Factors | PG&E does not track for the purposes of PSPS, the SAWTI does not cover the entire PG&E territory
Sectionalization | Mitigation | A device used to mitigate the scope and number of customers subjected to de-energization
Structure identifier | Damages | A unique numerical identifier for circuit structures
Sustained wind speeds (mph) | Decision Factors | Sustained windspeed in miles per hour at 10 meters above ground level.
Sustained Wind Speeds at 50 m (mph) | Decision Factors | Sustained windspeed in miles per hour at 50 meters above ground level.
Switching | Mitigation | Depending on fire risk patterns, distribution switch locations and switching plans maintain service to customers on radial lines that fall outside the high-risk area but are served by lines that pass through the fire risk area. Depending on event scope, we may be able to use back-tie switching to bypass the distribution lines that pass through the de-energization area to keep customers energized from a different set of lines. During this event, distribution switching was not used as a mitigation as there were no opportunities available. This was primarily due to the small scope of the event
System Cooperators | Data Dictionary | All Public Safety Partners in the service area were invited to join for situational awareness
Temperature (degrees F) | Decision Factors | Temperature in Fahrenheit at 2 meters above ground level.
Tree Overstrike | Decision Factors | Sum of tree overstrike in a 2 x 2 km grid cell area in ft.
Vegetation conditions | Decision Factors | The state or quality of the vegetation
Voltage range of distribution lines | Transmission | PG&E defines transmission level customers as customers being served by assets between 4kV and 34kV
Voltage range of transmission lines | Transmission | PG&E defines transmission level customers as customers being served by 60kV assets or higher

## 7. Data Dictionary
Section | Table Parent Name | Metric | Field Description | Field Type | Example | Notes/Calculations
I. Overview | A. PSPS Event Summary | 1. Event Name | Date of De-energization Start spelled out | Text | 2021-10-31
I. Overview | A. PSPS Event Summary | 2. Date of First De-energization | MM/DD/YYYY; Format: Short Date | Date | 2021-10-31
I. Overview | A. PSPS Event Summary | 3. Time of First De-energization | MM/DD/YYYY HH:MM 24-hr; minutes can be :00; Format: Date and Time 24 hr clock | Time | 2021-10-31 16:00
I. Overview | A. PSPS Event Summary | 4. Date of Last Restoration | MM/DD/YYYY; Format: Short Date | Date | 2021-11-02
I. Overview | A. PSPS Event Summary | 5. Time of Last Restoration | MM/DD/YYYY HH:MM 24-hr; minutes can be :00; Format: Date and Time 24 hr clock | Time | 2021-11-02 08:00
I. Overview | A. PSPS Event Summary | 6. Number of Hours De-energized | Calculated from date/time of PSPS beginning/end; Format: General | Integer | 40 | "=(F6-F4)*24"
I. Overview | A. PSPS Event Summary | 7. Number of Days De-energized | Calculated from date/time of PSPS beginning/end; Format: General | Float | 1.6667 | "=F6-F4"
I. Overview | A. PSPS Event Summary | 8. Number of Accounts* Notified | The number of unique customer accounts or service points that were notified irrespective of whether they were de-energized or not. | Integer | 3024
I. Overview | A. PSPS Event Summary | 9. Number of Accounts for which de-energization was cancelled | Accounts that received a notification of de-energization but were not de-energized | Integer | 600
I. Overview | A. PSPS Event Summary | 10. Number of Accounts De-energized |  | Integer | 2424
I. Overview | A. PSPS Event Summary | 11. Number of Accounts that Live in HFTD Tiers 2 or 3* de-energized | HFTD Tiers 2 or 3 that are defined in CPUC HFTD maps issued in D.17-01-009. | Integer | 2000
I. Overview | A. PSPS Event Summary | 12. Number of MBL* Accounts de-energized (in tariff class) | Medical Baseline as identified in a tariff, rate class, preliminary statement, or rule for which a customer meets eligibility requirements | Integer | 450
I. Overview | A. PSPS Event Summary | 13. Number of MBL Accounts that live in HFTD Tiers 2 or 3 that were de-Energized |  | Integer | 375
I. Overview | A. PSPS Event Summary | 14. Number of Life Support* Accounts de-energized (within MBL designation) |  | Integer | 125
I. Overview | A. PSPS Event Summary | 15. Number of AFN*-identified Accounts that are not MBL that were de-energized | Access and Functional Needs as self-identified by the customer and meets definition in California Code, Government Code - GOV § 8593.3 | Integer | 75
I. Overview | A. PSPS Event Summary | 16. Number of de-energized Accounts that requested in-person notification that were not also identified as AFN or MBL |  | Integer | 50
I. Overview | A. PSPS Event Summary | 17. Number of de-energized Accounts that self-identify as having a person with a disability in the household that were not also identified as AFN or MBL |  | Integer | 25
I. Overview | A. PSPS Event Summary | 18. Number of de-energized Accounts in CARE* or FERA* tariff class | California Alternate Rates for Energy (CARE) and Family Electric Rate Assistance (FERA). | Integer | 500
I. Overview | A. PSPS Event Summary | 19. Number of Counties De-energized |  | Integer | 10 | County is de-energized if one or more service points that are de-energized is located in the county.
I. Overview | A. PSPS Event Summary | 20. Number of Tribes De-energized |  | Integer | 8 | Tribe is de-energized if one or more service points that are de-energized is located in the tribe.
I. Overview | A. PSPS Event Summary | 21. Number of CFCI* De-energized | Critical Facilities and Critical Infrastructure | Integer | 200
I. Overview | A. PSPS Event Summary | 22. Number of Transmission lines De-energized |  | Integer | 2
I. Overview | A. PSPS Event Summary | 23. Number of Transmission lines De-energized without advance notice to CAISO |  | Integer | 0
I. Overview | A. PSPS Event Summary | 24. Line miles of transmission lines de-energized | In decimals to the tenth | Float | 45.6
I. Overview | A. PSPS Event Summary | 25. Number of Distribution Circuits De-energized |  | Integer | 55
I. Overview | A. PSPS Event Summary | 26. Line miles of distribution lines de-energized | In decimals to the tenth | Float | 3459.5
I. Overview | A. PSPS Event Summary | 27. Number of de-energized end-users served by sub-meters de-energized | Define "end users served by submeters" in "Utilty Definitions" | Integer | 1200
I. Overview | A. PSPS Event Summary | 28. Number of de-energized end-users served by master meters de-energized | Define "end-users served by master meters" in "Utilty Definitions" | Integer | 1200
I. Overview | A. PSPS Event Summary | 29. Number of de-energized 'other non-account holders'* |  | Integer
I. Overview | A. PSPS Event Summary | 30. Number of local and tribal governments that requested information on MBL or CFCI Accounts impacted during the event. |  | Integer | 6
I. Overview | A. PSPS Event Summary | 31. Number of Damages | Damages as defined in the Post-Event Report template | Integer | 8
I. Overview | A. PSPS Event Summary | 32. Number of Hazards | Hazards as defined in the Post-Event Report template | Integer | 6
II. Delay | A. Delay Requests | 1. Number of requests to delay de-energization. | Number of requests from PSP before de-energization | Integer | 2
II. Delay | A. Delay Requests | 2. Number of circuits for which de-energizing was delayed. | Number of requests from PSP honored before de-energization | Integer | 0
III. Emergency Management | A. EOC | 1. Number of Days in Monitoring Mode* | Define what utility means by "Monitoring Mode" | Integer | 5
III. Emergency Management | A. EOC | 2. Number of hours before first de-energization that Emergency Operations Center (EOC) was established |  | Integer | 72
III. Emergency Management | A. EOC | 3. Number of State Executive Briefings (SEB) Held |  | Integer | 6
III. Emergency Management | A. EOC | 4. Number of Unique Briefing Decks distributed |  | Integer | 6
III. Emergency Management | A. EOC | 5. Number of System Cooperators’* Calls Conducted |  | Integer | 3
III. Emergency Management | A. EOC | 6. Number of PSPS State Notification Forms submitted to Cal OES |  | Integer | 16
III. Emergency Management | A. EOC | 7. Number of News Releases Disseminated |  | Integer | 4
III. Emergency Management | A. EOC | 8. Number of Public Briefings conducted |  | Integer | 2
III. Emergency Management | A. EOC | 9. Number of Days EOC Active |  | Integer | 6 | Count each day EOC was active regardless of time activated or deactivated.
III. Emergency Management | B. State Operations Center | 1. Number of liaisons embedded at State Operations Center | Liaisons from utility. | Integer | 2
III. Emergency Management | C. Liaisons | 1. Number of liaisons embedded at local Emergency Operations Center (County, Tribal or other) | Liaisons from utility. | Integer | 2
III. Emergency Management | C. Liaisons | 2. Number of State or local liaisons embedded at your EOC |  | Integer | 2
III. Emergency Management | C. Liaisons | 3. Number of water or communication infrastructure liaisons embedded at your EOC |  | Integer | 2
III. Emergency Management | D. Training | 1. Number of EOC personnel that received EM training in 2021 | 2021 Cumulative total only (use "annual or cumulative total" column) | Integer | 150
III. Emergency Management | D. Training | 2. Number of Hours EOC personnel were trained in EM in 2021 | 2021 Cumulative total only (use "annual or cumulative total" column) | Integer | 600
III. Emergency Management | E. De-energization Exercises | 1. Number of Tabletop Exercises of four hours or more conducted in 2021 | 2021 Cumulative total only (use "annual or cumulative total" column) | Integer | 2
III. Emergency Management | E. De-energization Exercises | 2. Number of Full-scale or Functional Exercises of more than one day conducted in 2021 | 2021 Cumulative total only (use "annual or cumulative total" column) | Integer | 2
III. Emergency Management | E. De-energization Exercises | 3. Average number of utility personnel participating in all exercises | 2021 Cumulative total only (use "annual or cumulative total" column) | Integer | 500
III. Emergency Management | E. De-energization Exercises | 4. Number of PSP actively participating as a player during the exercises. | 2021 Cumulative total only (use "annual or cumulative total" column) | Integer | 0
III. Emergency Management | E. De-energization Exercises | 5. Number of AFN community members participating as a player during the exercises. | 2021 Cumulative total only (use "annual or cumulative total" column) | Integer | 0
IV. Notification | A. Notification Receipt | 1. Number De-energized Accounts Notified | Accounts that were actually de-energized | Integer | 50000
IV. Notification | A. Notification Receipt | 2. Number De-energized MBL Accounts Notified | MBL Accounts that were actually de-energized | Integer | 5000
IV. Notification | A. Notification Receipt | 3. Number of Positive MBL Accounts Notifications | MBL Accounts that were actually de-energized for which there was a positive confirmation of receipt of notice | Integer | 4500 | Notifications to Medical Baseline or other customers requesting advance notification to which the customer responded as received.
IV. Notification | A. Notification Receipt | 4. Number of de-energized accounts whose contact information was wrong. | Accounts that were actually de-energized | Integer | 500
IV. Notification | A. Notification Receipt | 5. Number of de-energized MBL accounts whose contact information was wrong. | Accounts that were actually de-energized | Integer | 50
IV. Notification | B. Additional Notifications - MBL | 1. Number of In-Person Visits / Doorbell Rings | Accounts that were actually de-energized | Integer | 100
IV. Notification | B. Additional Notifications - MBL | 2. Number of Live Agent Phone Calls | Accounts that were actually de-energized | Integer | 500
IV. Notification | C. Notification Failure Causes | 1. Number of Accounts that did not receive 48–72-hour advance notification | Accounts that were actually de-energized | Integer | 1500 | Notification of priority notification entities only. PSP notification addressed in VI. A.5. below
IV. Notification | C. Notification Failure Causes | 2. Number of Accounts that did not receive 24-48 hours advance notification | Accounts that were actually de-energized | Integer | 1501 | All other affected customers/populations
IV. Notification | C. Notification Failure Causes | 3. Number of Accounts that did not receive 1-4 hour advance notifications. | Accounts that were actually de-energized | Integer | 500 | All affected customers/populations
IV. Notification | C. Notification Failure Causes | 4. Number of Accounts that did not receive any notifications before de-energization. | Accounts that were actually de-energized | Integer | 400 | All affected customers/populations
IV. Notification | C. Notification Failure Causes | 5. Number of Accounts that were not notified at de-energization initiation. | Accounts that were actually de-energized | Integer | 400 | All affected customers/populations
IV. Notification | C. Notification Failure Causes | 6. Number of Accounts that were not notified immediately before re-energization. | Accounts that were actually de-energized | Integer | 400 | All affected customers/populations
IV. Notification | C. Notification Failure Causes | 7. Number of Accounts that were not notified when re-energization is was complete. | Accounts that were actually de-energized | Integer | 400 | All affected customers/populations
IV. Notification | C. Notification Failure Causes | 8. Number of Accounts that did not receive cancellation notification within two hours of the decision to cancel | Accounts that were NOT de-energized. | Integer | 400 | All affected customers/populations
IV. Notification | C. Notification Failure Causes | 9. Number of Accounts that did not receive notification after de-energization because there was no alternate method of contact | Accounts that were actually de-energized | Integer | 250
IV. Notification | D. False Communications | 1. Number of Accounts that were not de-energized after receiving a De-energization Notification | Accounts that were NOT de-energized. | Integer | 600
IV. Notification | D. False Communications | 2. Number of Accounts that were de-energized after receiving a Cancellation Notification | Accounts that were actually de-energized | Integer | 200
V. Public Safety Partners | A. PSP Notification | 1. Number of hours after EOC activated that PSPs were first notified | Leave cell blank if PSPs were notified before EOC was activated. | Integer | 2
V. Public Safety Partners | A. PSP Notification | 2. Number of hours before EOC activated that PSPs were first notified | Leave cell blank if PSPs were notified after EOC was activated. | Integer | 24
V. Public Safety Partners | A. PSP Notification | 3. Number of hours before first de-energization that PSPs were notified |  | Integer | 72
V. Public Safety Partners | A. PSP Notification | 4. Number of PSPs notified at first notice |  | Integer | 600
V. Public Safety Partners | A. PSP Notification | 5. Number of PSP notifications that were not timely |  | Integer | 100
V. Public Safety Partners | B. Portal | 1. Number of PSP Portal Registrations at end of PSPS event | Total number of registrations from PSP. | Integer | 45
V. Public Safety Partners | B. Portal | 2. Number of Portal training events provided to PSP during 2021. | 2021 Cumulative total only (use "annual or cumulative total" column) | Integer | 10
V. Public Safety Partners | B. Portal | 3. Number of events in 2021 for which there is no data available in the portal as of the submission date. | 2021 Cumulative total only (use "annual or cumulative total" column) | Integer | 0
V. Public Safety Partners | B. Portal | 4. Number of PSP Portal Registration requests that were not filled within 24 business hours. | 2021 Cumulative total only (use "annual or cumulative total" column) | Integer | 0
VI. Customer Communication | A. Notification Language | 1. Number of Languages Used in Notifications | Prevalent languages, including English. | Integer | 15 | A language is prevalent if it is spoken by 1,000 or more persons in the utility’s territory or if it is spoken by 5% or more of the population within a “public safety answering point” in the utility territory (D.20-03-004).
VI. Customer Communication | B. Call Center Support Services | 1. Cumulative number PSPS Calls Handled |  | Integer | 4500 | Counted from first notification to full restoration.
VI. Customer Communication | B. Call Center Support Services | 2. Average Response Time for PSPS-related Calls | Time in Minutes; to the tenth | Floating | 2.5
VI. Customer Communication | B. Call Center Support Services | 3. Number of PSPS-related calls handled by Call Center Translation Services |  | Integer | 100
VI. Customer Communication | B. Call Center Support Services | 4. Number of languages supported by Call Center Translation Services |  | Integer | 20
VI. Customer Communication | C. Website Traffic | 1. Number of Emergency Website Visits |  | Integer | 5000
VI. Customer Communication | C. Website Traffic | 2. Number of Website Page Views |  | Integer | 10000
VI. Customer Communication | C. Website Traffic | 3. Number of Emergency Page Views |  | Integer | 5000
VI. Customer Communication | D. Translated Website Visitors | 1. Number of Website Unique Visitors non-English |  | Integer | 2000
VI. Customer Communication | D. Translated Website Visitors | 2. Number of Emergency Website Unique Visitors non-English |  | Integer | 500
VII. Distribution Circuits De-energized | A. Frequency of Circuit De-energized | 1. Name of First most frequently de-energized circuit |  | Text | Argon18 | Name of Circuit calculated from Distribution Table Across All Events
VII. Distribution Circuits De-energized | A. Frequency of Circuit De-energized | 2. Number of Times First most frequently de-energized circuit de-energized |  | Integer | 4 | Calculated from Distribution Table
VII. Distribution Circuits De-energized | A. Frequency of Circuit De-energized | 3. Cumulative total number of customers on the first most frequently de-energized circuit | Calculated from Distribution Table | Integer | 10000 | Sort the distribution circuit list by circuit name. Select the circuit with the most entries irrespective of event. Count all customers de-energized over all of the events in which the circuit was de-energized. In the event of a tie, rank the circuits by number of customers de-energized.
VII. Distribution Circuits De-energized | A. Frequency of Circuit De-energized | 4. Name of Second most frequently de-energized circuit | Name of Circuit calculated from Distribution Table | Text | Xenon54
VII. Distribution Circuits De-energized | A. Frequency of Circuit De-energized | 5. Number of Times Second most frequently de-energized circuit de-energized | Calculated from Distribution Table | Integer | 3
VII. Distribution Circuits De-energized | A. Frequency of Circuit De-energized | 6. Cumulative total number of customers on the second most frequently de-energized circuit | Calculated from Distribution Table | Integer | 8000
VII. Distribution Circuits De-energized | A. Frequency of Circuit De-energized | 7. Name of Third most frequently de-energized circuit | Name of Circuit calculated from Distribution Table | Text | Krypton36
VII. Distribution Circuits De-energized | A. Frequency of Circuit De-energized | 8. Number of Times Third most frequently de-energized circuit de-energized | Calculated from Distribution Table | Integer | 2
VII. Distribution Circuits De-energized | A. Frequency of Circuit De-energized | 9. Cumulative total number of customers on the third most frequently de-energized circuit | Calculated from Distribution Table | Integer | 6000
VII. Distribution Circuits De-energized | B. Duration of Circuits De-energized | 1. Name of Longest (in hours) circuit de-energized. | Calculated from Distribution Table | Text | Germanium32
VII. Distribution Circuits De-energized | B. Duration of Circuits De-energized | 2. Number of Hours that longest de-energized circuit was de-energized | Calculated from Distribution Table for only the single longest de-energization. | Integer | 140
VII. Distribution Circuits De-energized | B. Duration of Circuits De-energized | 3. Number of customers impacted | Calculated from Distribution Table for only those accounts de-energized during the longest single de-energization. | Integer | 5000
VII. Distribution Circuits De-energized | B. Duration of Circuits De-energized | 4. Name of Second Longest (in hours) circuit de-energized. | Calculated from Distribution Table | Text | Neon10
VII. Distribution Circuits De-energized | B. Duration of Circuits De-energized | 5. Number of Hours that longest de-energized circuit was de-energized | Calculated from Distribution Table | Integer | 100
VII. Distribution Circuits De-energized | B. Duration of Circuits De-energized | 6. Number of customers impacted | Calculated from Distribution Table | Integer | 10000
VII. Distribution Circuits De-energized | B. Duration of Circuits De-energized | 7. Name of Third Longest (in hours) circuit de-energized. | Calculated from Distribution Table | Text | Bromine35
VII. Distribution Circuits De-energized | B. Duration of Circuits De-energized | 8. Number of Hours that longest de-energized circuit was de-energized | Calculated from Distribution Table | Integer | 80
VII. Distribution Circuits De-energized | B. Duration of Circuits De-energized | 9. Number of customers impacted | Calculated from Distribution Table | Integer | 14000
VIII. CFCI | A. CFCI De-energized | 1. Number of CFCI de-energized | Irrespective of mitigating backup power. Calculated from CFCI table | Integer | 150
VIII. CFCI | A. CFCI De-energized | 2. Number of Communication Services Providers (CSP) CFCI de-energized. | Irrespective of mitigating backup power. Calculated from CFCI table | Integer | 80
VIII. CFCI | A. CFCI De-energized | 3. Number of Cell Towers de-energized | Irrespective of mitigating backup power. Calculated from CFCI table | Integer | 20
VIII. CFCI | A. CFCI De-energized | 4. Number of Water/Wastewater CFCI de-energized. | Irrespective of mitigating backup power. Calculated from CFCI table | Integer | 15
VIII. CFCI | A. CFCI De-energized | 5. Number of de-energized CFCI that requested backup power. | Calculated from CFCI table | Integer | 25
VIII. CFCI | A. CFCI De-energized | 6. Number of de-energized CFCI that were provided backup power. | Calculated from CFCI table | Integer | 5
VIII. CFCI | A. CFCI De-energized | 7. Number of CFCI that were de-energized during two events. | Irrespective of mitigating backup power. Calculated from CFCI table across all events | Integer | 450
VIII. CFCI | A. CFCI De-energized | 8. Number of CFCI that were de-energized during more than two events. | Irrespective of mitigating backup power. Calculated from CFCI table across all events | Integer | 1000
IX. Backup Power | A. Backup Power Support | 1. Number of Requests for Backup Power |  | Integer | 10
IX. Backup Power | A. Backup Power Support | 2. Percentage of Requests Satisfied (%) |  | Percentile | 80
IX. Backup Power | A. Backup Power Support | 3. Total MW capacity supplied (MW) | in MegaWatts | Integer | 12
IX. Backup Power | A. Backup Power Support | 4. Percentage of backup power supplied that was renewable (%) |  | Percentile | 30
IX. Backup Power | A. Backup Power Support | 5. Number of Requests for Consultative Assistance up to one month prior |  | Integer | 25
IX. Backup Power | B. Backup Power Programs | 1. Applications received for backup generators or storage from the day after the last PSPS through the end of the current one |  | Integer | 8
IX. Backup Power | B. Backup Power Programs | 2. Number of backup generators issued from the day after the last PSPS through the end of the current one |  | Integer | 10
IX. Backup Power | B. Backup Power Programs | 3. Number of backup storage issued from the day after the last PSPS through the end of the current one |  | Integer | 6
IX. Backup Power | C. Microgrids | 1. Number of microgrids that replaced the de-energized load |  | Integer | 5
IX. Backup Power | C. Microgrids | 2. Megawatts of load provided by microgrids (MWh) | in MegaWatts | Integer
IX. Backup Power | C. Microgrids | 3. Percentage of Microgrids in use using renewable fuel (%) |  | Percentile | 20
X. Mitigation | A. Mitigation Deployed | 1. Number of Circuits sectionalized to reduce PSPS scope |  | Integer | 6
XI. CRCs | A. Community Resource Centers | 1. Number of CRCs open during event |  | Integer | 12
XI. CRCs | A. Community Resource Centers | 2. Total Number of Visitors to all CRCs during the event |  | Integer | 1500
XI. CRCs | A. Community Resource Centers | 3. Percentage of CRCs that were indoors (%) |  | Percentile | 50
XI. CRCs | A. Community Resource Centers | 4. Percentage of indoor CRCs that had been opened in the past (reliably placed) (%) |  | Percentile | 70
XI. CRCs | A. Community Resource Centers | 5. Percentage of CRCs that were indoors when AQI was >100 (%) |  | Percentile | 50
XI. CRCs | A. Community Resource Centers | 6. First Longest Distance from each event's CRCs to furthest targeted customer (mi.) | Driving Distance calculated in miles derived from 17. CRCs worksheet | Integer | 45
XI. CRCs | A. Community Resource Centers | 7. Second Longest Distance from each event's CRCs to furthest targeted customer (mi.) | Driving Distance calculated in miles derived from 17. CRCs worksheet | Integer | 35
XI. CRCs | A. Community Resource Centers | 8. Third Longest Distance from each event's CRCs to furthest targeted customer (mi.) | Driving Distance calculated in miles derived from 17. CRCs worksheet | Integer | 25
XII. EV Charging | A. EV Charging Stations | 1. Number of level 3 charging stations* de-energized | Irrespective of mitigating backup power. | Integer | 12
XIII. Restoration | A. Late Restoration | 1. Number of Circuits not Restored within 24 hrs. of all-clear. |  | Integer | 15
XIV. Complaints | A. Complaints | 1. Number of Complaints | Complaints about any aspect of the PSPS event. | Integer | 145
XV. Claims | A. Claims | 1. Number of Claims | Claims related to any aspect of the PSPS event. | Integer | 12
XV. Claims | A. Claims | 2. Total Value of Claims (dollars) | Dollars | Integer | 50000

## 8. Dashboard
Metrics | EXAMPLE | 2021-01-18 | 2021-08-17 | 2021-09-20 | 2021-10-11 | 2021-10-14 | Trendlines | Annual or Cumulative Total | PG&E remarks
I. Overview
A. PSPS Event Summary
1. Event Name |  | 2021-01-18 | 2021-08-17 | 2021-09-20 | 2021-10-11 | 2021-10-14 |  | -
2. Date of First De-energization | 2021-10-31 | 2021-01-18 | 2021-08-17 | 2021-09-20 | 2021-10-11 | 2021-10-15 |  | -
3. Time of First De-energization | 2021-10-31 16:00 | 2021-01-18 23:02 | 2021-08-17 12:51 | 2021-09-20 06:05 | 2021-10-11 01:34 | 2021-10-15 01:00 |  | - | Consistent with PG&E’s ESRB-8 PSPS post-event reports submitted to the CPUC, PG&E has included the earliest customer outage start time as a reflection of the outage time of the circuits, counties, or tribes listed. Note: this may not be representative of what all customers on the circuits, counties, or tribes listed experienced.
4. Date of Last Restoration | 2021-11-02 | 2021-01-26 | 2021-08-20 | 2021-09-21 | 2021-10-14 | 2021-10-16 |  | -
5. Time of Last Restoration | 2021-11-02 08:00 | 2021-01-26 16:50 | 2021-08-20 10:30 | 2021-09-21 16:46 | 2021-10-14 15:22 | 2021-10-16 16:32 |  | - | Consistent with PG&E’s ESRB-8 PSPS post-event reports submitted to the CPUC, we have included the restoration time of the last customer restored as a reflection of the outage restoration time for the circuits listed. Note: this may not be representative of what all customers on the circuit experienced.
6. Number of Hours De-energized | 40 | 186 | 70 | 35 | 86 | 40 |  | 417
7. Number of Days De-energized | 1.6667 | 7.7417 | 2.9021 | 1.4451 | 3.575 | 1.6472 |  | 17.3111
8. Number of Accounts* Notified |  | 22433 | 65861 | 17061 | 46840 | 29114 |  | 181309
9. Number of Accounts for which de-energization was cancelled |  | 17209 | 17669 | 14848 | 22428 | 28440 |  | 100594
10. Number of Accounts De-energized |  | 5099 | 48155 | 2968 | 23504 | 666 |  | 80392
11. Number of Accounts that Live in HFTD Tiers 2 or 3* de-energized |  | 5044 | 38564 | 2300 | 16169 | 622 |  | 62699
12. Number of MBL* Accounts de-energized (in tariff class) |  | 274 | 3856 | 234 | 1738 | 34 |  | 6136
13. Number of MBL Accounts that live in HFTD Tiers 2 or 3 that were de-Energized |  | 274 | 3135 | 192 | 1184 | 34 |  | 4819
14. Number of Life Support* Accounts de-energized (within MBL designation) |  | 185 | 2694 | 162 | 1188 | 26 |  | 4255
15. Number of AFN*-identified Accounts that are not MBL that were de-energized |  | 0 | 4331 | 78 | 7770 | 146 |  | 12325
16. Number of de-energized Accounts that requested in-person notification that were not also identified as AFN or MBL |  | N/A | N/A | N/A | N/A | N/A |  | 0 | PG&E, SCE, and SDG&E jointly provided comments in the Post Season Data Report Template to SED on 11/29 to reiterate that IOUs do not provide an option for customers to request an in-person notification for PSPS Events; however, customers can self-certify for PG&E’s Vulnerable Customer status. In accordance with D.12-03-054, customers that are not enrolled or qualify for the Medical Baseline Program can “certify that they have a serious illness or condition that could become life threatening if service is disconnected.” PG&E uses this designation to make an in-person visit prior to disconnection.
17. Number of de-energized Accounts that self-identify as having a person with a disability in the household that were not also identified as AFN or MBL |  | 0 | 0 | 0 | 0 | 0 |  | 0
18. Number of de-energized Accounts in CARE* or FERA* tariff class |  | 642 | 12492 | 823 | 4915 | 163 |  | 19035
19. Number of Counties De-energized |  | 7 | 13 | 8 | 23 | 1 |  | 52
20. Number of Tribes De-energized |  | 0 | 3 | 1 | 5 | 0 |  | 9
21. Number of CFCI* De-energized |  | 162 | 936 | 115 | 660 | 38 |  | 1911
22. Number of Transmission lines De-energized |  | 0 | 3 | 0 | 3 | 0 |  | 6
23. Number of Transmission lines De-energized without advance notice to CAISO |  | 0 | 0 | 0 | 0 | 0 |  | 0
24. Line miles of transmission lines de-energized |  | 0 | 104.92 | 0 | 55.54 | 0 |  | 160.46
25. Number of Distribution Circuits De-energized |  | 18 | 96 | 16 | 95 | 6 |  | 231
26. Line miles of distribution lines de-energized |  | 521 | 4090 | 324 | 2614 | 61 |  | 7610
27. Number of de-energized end-users served by sub-meters de-energized |  | N/A | N/A | N/A | N/A | N/A |  | N/A | PG&E, SCE, and SDG&E jointly provided comments in the Post Season Data Report Template to SED on 11/29 to reiterate that IOUs do not track number of customers served by sub-meters
28. Number of de-energized end-users served by master meters de-energized |  | 0 | 60 | 0 | 9 | 0 |  | 69
29. Number of de-energized 'other non-account holders' |  | N/A | N/A | N/A | N/A | N/A |  | 0 | PG&E, SCE, and SDG&E jointly provided comments in the Post Season Data Report Template to SED on 11/29 to reiterate that no definition was provided for 'non-account holder'. PG&E interpreted it as the same as a sub-meter account. As stated above in our remarks for PSPS Event Summary metric #27 - "Number of de-energized end-users served by sub-meters de-energized", PG&E does not track number of customers served by sub-meters.
30. Number of local and tribal governments that requested information on MBL or CFCI Accounts impacted during the event. |  | 0 | 0 | 0 | 0 | 0 |  | 0 | All local and tribal governments that requested MBL or CFCI accounts information were provided access to PG&E's PSPS portal.
31. Number of Damages |  | 415 | 7 | 0 | 7 | 1 |  | 430 | For the 08/17 PSPS event, the number reported differs from the one provided in the PER because one hazard was reclassified as a damage during further analysis and validation of the data.
32. Number of Hazards |  | 8 | 3 | 0 | 1 | 0 |  | 12 | For the 08/17 PSPS event, the number reported differs from the one provided in the PER because one hazard was reclassified as a damage during further analysis and validation of the data.
II. Delay
A. Delay Requests
1. Number of requests to delay de-energization. |  | 0 | 0 | 0 | 0 | 0 |  | 0
2. Number of circuits for which de-energizing was delayed. |  | 0 | 0 | 0 | 0 | 0 |  | 0
III. Emergency Management
A. EOC
1. Number of Days in Monitoring Mode |  | - | - | - | - | - |  | 365 | PG&E meteorologists are monitoring for PSPS conditions 365 days a year. Once they see any conditions that may lead to a potential PSPS event, they alert PSPS staff and enter into Readiness posture.
2. Number of hours before first de-energization that Emergency Operations Center (EOC) was established |  | 65 | 48 | 56 | 61 | 157 |  | 387 | EOC was activated for 10/11 event and did not deactivate until after 10/14 event. Hours noted for the 10/14 event are from time of 10/11 activation.
3. Number of State Executive Briefings (SEB) Held |  | 9 | 3 | 3 | 4 | 3 |  | 22
4. Number of Unique Briefing Decks distributed |  | 0 | 4 | 3 | 4 | 3 |  | 14 | As part of the State Executive Briefing, PG&E provided a briefing deck to participants via email prior to the meeting. This was not requested during the January PSPS which explains “0” for the January column. For the August event, there were three SEB briefings held, however four decks were distributed. Explanation for this is that the last State Executive Briefing of the event in August was cancelled and a deck was sent out to the participants with a reminder that the call had been cancelled for the remainder of the event.
5. Number of System Cooperators’* Calls Conducted |  | 4 | 4 | 4 | 4 | 5 |  | 21
6. Number of PSPS State Notification Forms submitted to Cal OES |  | 10 | 11 | 13 | 16 | 19 |  | 69
7. Number of News Releases Disseminated |  | 8 | 5 | 3 | 2 | 2 |  | 20
8. Number of Public Briefings conducted |  | 0 | 0 | 0 | 0 | 0 |  | 0
9. Number of Days EOC Active |  | 6 | 4 | 4 | 4 | 4 |  | 22 | EOC was activated for 10/11 event and did not deactivate until after 10/14 event. EOC was activated a total of 8 days for both events
B. State Operations Center
1. Number of liaisons embedded at State Operations Center |  | 1 | 1 | 1 | 1 | 1 |  | 5 | Virtual support provided on an as needed basis.
C. Liaisons
1. Number of liaisons embedded at local Emergency Operations Center (County, Tribal or other) |  | 5 | 9 | 10 | 16 | 1 |  | 41 | In some instances the limited access to EOC’s resulted in Public Safety Partners virtually embedding with the impacted counties.
2. Number of State or local liaisons embedded at your EOC |  | 0 | 2 | 1 | 2 | 1 |  | 6
3. Number of water or communication infrastructure liaisons embedded at your EOC |  | 0 | 0 | 0 | 0 | 0 |  | 0 | PG&E sent a letter in June 2021 inviting water and communication infrastructure liaisons to the Daily Systemwide Cooperator Calls that are held noon daily for each PSPS event to provide situational awareness updates directly from the leadership within PG&E's EOC. For 2021, no water and communication infrastructure customers requested to be embedded in our EOC.
D. Training
1. Number of EOC personnel that received EM training in 2021 |  | - | - | - | - | - |  | 727 | Many courses are Web based and individual time in the training modules differs.
2. Number of Hours EOC personnel were trained in EM in 2021 |  | - | - | - | - | - |  | 22800 | Many courses are Web based and individual time in the training modules differs.
E. De-energization Exercises
1. Number of Tabletop Exercises of four hours or more conducted in 2021 |  | - | - | - | - | - |  | 2
2. Number of Full-scale or Functional Exercises of more than one day conducted in 2021 |  | - | - | - | - | - |  | 2 | The total annual number includes one 5-day Full-scale Exercise and one 2-day Functional Exercise
3. Average number of utility personnel participating in all exercises |  | - | - | - | - | - |  | ~800
4. Number of PSP actively participating as a player during the exercises. |  | - | - | - | - | - |  | 36
5. Number of AFN community members participating as a player during the exercises. |  | - | - | - | - | - |  | 11
IV. Notification
A. Notification Receipt
1. Number De-energized Accounts Notified |  | 5079 | 47860 | 2212 | 22849 | 665 |  | 78665 | PG&E has provided de-energized customers who received a notification before de-energization
2. Number De-energized MBL Accounts Notified |  | 273 | 3856 | 176 | 1680 | 34 |  | 6019 | PG&E has provided de-energized MBL customers who received a notification before de-energization
3. Number of Positive MBL Accounts Notifications |  | 271 | 3720 | 173 | 1636 | 32 |  | 5832
4. Number of de-energized accounts whose contact information was wrong. |  | 20 | 124 | 6 | 69 | 1 |  | 220
5. Number of de-energized MBL accounts whose contact information was wrong. |  | 0 | 0 | 0 | 0 | 0 |  | 0
B. Additional Notifications - MBL
1. Number of In-Person Visits / Doorbell Rings |  | 74 | 599 | 137 | 194 | 111 |  | 1115
2. Number of Live Agent Phone Calls |  | 5 | 127 | 0 | 1 | 38 |  | 171
C. Notification Failure Causes
1. Number of Accounts that did not receive 48–72-hour advance notification |  | 12 | 305 | 42 | 156 | 0 |  | 515
2. Number of Accounts that did not receive 24-48 hours advance notification |  | 441 | 20049 | 741 | 3086 | 1 |  | 24318
3. Number of Accounts that did not receive 1-4 hour advance notifications. |  | 5071 | 5406 | 2371 | 22816 | 666 |  | 36330
4. Number of Accounts that did not receive any notifications before de-energization. |  | 20 | 266 | 756 | 655 | 1 |  | 1698
5. Number of Accounts that were not notified at de-energization initiation. |  | 5099 | 40917 | 2968 | 22066 | 666 |  | 71716
6. Number of Accounts that were not notified immediately before re-energization. |  | 352 | 9245 | 837 | 3851 | 35 |  | 14320
7. Number of Accounts that were not notified when re-energization is was complete. |  | 1935 | 17952 | 1171 | 2705 | 2 |  | 23765
8. Number of Accounts that did not receive cancellation notification within two hours of the decision to cancel |  | 17356 | 17856 | 4679 | 1137 | 6586 |  | 47614 | PG&E interprets “Number of Accounts that did not receive cancellation notification within two hours of the decision to cancel” as a situation when a customer was not notified within two hours of the decision to cancel the deenergization event for that customer or that they were removed from scope. During the January event, we were not required to provide entities with a cancellation notification within two hours of the decision to cancel prior to the adoption of D.21-06-034; however, PG&E has provided the Jan. 18 data in this report. For the 9/20 event, note that this number has been updated and revised from the one provided in the 10 day report based on further analysis and validation. For explanations, please reference the 10-day reports, Section 5.5 - If the utility fails to provide notifications according to the minimum timelines set forth in D.19-05-042 and D.21-06-034, using the following template to report a breakdown of the notification failure and an explanation of what caused the failure. (D.21-06-014 page 286, SED Additional Information.)
9. Number of Accounts that did not receive notification after de-energization because there was no alternate method of contact |  | 20 | 124 | 6 | 69 | 1 |  | 220
D. False Communications
1. Number of Accounts that were not de-energized after receiving a De-energization Notification |  | 140 | 2744 | 1 | 586 | 0 |  | 3471 | PG&E interprets “Accounts that were not de-energized after receiving a De-energization Notification” as a situation where a customer was not de-energized but was notified that de-energization would occur (e.g., received Warning Notification), and did not receive a cancellation notice before the de-energization start date/time indicated in their Warning Notification. For further explanation of numbers, please reference the 10-day reports, Section 5.7 - Enumerate and explain the cause of any false communications citing the sources of changing data. (D.20-05-051, Appendix A, page 4.). During the August 17, 2021 PSPS event, a total of 2,744 customers were not de-energized after receiving a notification that de-energization would occur (e.g., received Warning Notification), and did not receive a cancellation notice before the de-energization start date/time as indicated in their Warning Notification. For 2,457 of those customers, PG&E monitored the weather and continued to delay the planned de-energization time because the forecasted weather conditions were not materializing. Ultimately, after several delays to de-energizing these customers, PG&E re-evaluated the de-energization decision and based on real-time weather observations, canceled the de-energization. As a result, the cancellation notification to customers was sent after the planned de-energization time indicated in their Warning Notification. The remaining 287 of customers never received a cancellation after their initial warning notification. Since this event, PG&E has built a fully-automated communication on our website to notify customers that the expected de-energization period has surpassed and the de-energization time is being re-assessed due to weather. Customers are able to search their address on our website to retrieve this communication.
2. Number of Accounts that were de-energized after receiving a Cancellation Notification |  | 0 | 37 | 0 | 341 | 0 |  | 378 | PG&E has provided customers where a customer was de-energized after receiving a cancellation notice and no other update notifications, indicating the customer was in scope for de-energization. In the 8/17/2021 and the 10/11/2021 10-day reports, PG&E provides explanations in Section 5.7 - Enumerate and explain the cause of any false communications citing the sources of changing data.
V. Public Safety Partners
A. PSP Notification
1. Number of hours after EOC activated that PSPs were first notified |  | 5.5 | 4.7 | 1.5 | 1 | 0 |  | 12.7 | EOC continued to remain activated from the 10/11 event and going into the 10/14 event; therefore, the number of hours after EOC activated that PSPs were first notified for 10/14/2021 event is zero
2. Number of hours before EOC activated that PSPs were first notified |  | 14 | 1 | 0 | 2.3 | 0 |  | 17.3 | Total number of hours prior to EOC activation that Agency Representatives conducted live calls to county OES, as well as city and tribal contacts as needed, to notify them that PG&E is monitoring a potential PSPS event.
3. Number of hours before first de-energization that PSPs were notified |  | 7.8 | 2.5 | 22.9 | 7.75 | 5.25 |  | 46.2
4. Number of PSPs notified at first notice |  | 315 | 516 | 298 | 584 | S |  | 1713
5. Number of PSP notifications that were not timely |  | 12 | 20 | 19 | 20 | 12 |  | 83
B. Portal
1. Number of PSP Portal Registrations at end of PSPS event |  | 1803 | 2031 | 2066 | 2104 | 2105 |  | 2105 | Number of external users at the conclusion of each PSPS event in 2021
2. Number of Portal training events provided to PSP during 2021. |  | 0 | 2 | 4 | 7 | 7 |  | 20
3. Number of events in 2021 for which there is no data available in the portal as of the submission date. |  | 0 | 0 | 0 | 0 | 0 |  | 0
4. Number of PSP Portal Registration requests that were not filled within 24 business hours. |  | 0 | 0 | 0 | 0 | 0 |  | 0
VI. Customer Communication
A. Notification Language
1. Number of Languages Used in Notifications |  | 5 | 8 | 6 | 6 | 5 |  | 30
B. Call Center Support Services
1. Cumulative number PSPS Calls Handled |  | 2000 | 2591 | 1556 | 1919 | 1034 |  | 9100 | Jan PER Approximates
2. Average Response Time for PSPS-related Calls |  | 0.4 | 0.4 | 0.2 | 0.2 | 0.3 |  | 0.3
3. Number of PSPS-related calls handled by Call Center Translation Services |  | 7300 | 1161 | 4422 | 4958 | 5374 |  | 23215 | Jan PER Approximates
4. Number of languages supported by Call Center Translation Services |  | 28 | 32 | 23 | 26 | 27 |  | 136 | In general, Translation Services are prepared to answer in 200+ languages. For this metric, PG&E is reporting only the count of languages with which calls were conducted.
C. Website Traffic
1. Number of Emergency Website Visits |  | 319000 | 573031 | 303980 | 577182 | 153192 |  | 1926385 | Jan PER Approximates
2. Number of Website Page Views |  | 4373000 | 4334099 | 1147056 | 1044293 | 937102 |  | 11835550 | Jan PER Approximates
3. Number of Emergency Page Views |  | 1142000 | 1125014 | 541927 | 1095116 | 267477 |  | 4171534 | Jan PER Approximates
D. Translated Website Visitors
1. Number of Website Unique Visitors non-English |  | 13001 | 37056 | 810 | 49307 | 48435 |  | 148609 | Note that a single visitor could be counted more than once if the visitor navigates to multiple non-english websites. For example, if a customer first opens the Spanish version of the webpage and then the Portuguese version of the webpage that customer would be double counted.
2. Number of Emergency Website Unique Visitors non-English |  | 2792 | 1870 | 17130 | 1304 | 477 |  | 23573 | Note that a single visitor could be counted more than once if the visitor navigates to multiple non-english websites. For example, if a customer first opens the Spanish version of the webpage and then the Portuguese version of the webpage that customer would be double counted.
VII. Distribution Circuits De-energized
A. Frequency of Circuit De-energized
1. Name of First most frequently de-energized circuit | [7 empty] | CAL WATER 1102
2. Number of Times First most frequently de-energized circuit de-energized | [7 empty] | 3
3. Cumulative total number of customers on the first most frequently de-energized circuit | [7 empty] | 2576 | This metric reports PSPS customer outages; therefore, a customer who was de-energized in more than one event would add more than one to the total.
4. Name of Second most frequently de-energized circuit | [7 empty] | LAMONT 1104
5. Number of Times Second most frequently de-energized circuit de-energized | [7 empty] | 3
6. Cumulative total number of customers on the second most frequently de-energized circuit | [7 empty] | 2408 | This metric reports PSPS customer outages; therefore, a customer who was de-energized in more than one event would add more than one to the total.
7. Name of Third most frequently de-energized circuit | [7 empty] | MAGUNDEN 1108
8. Number of Times Third most frequently de-energized circuit de-energized | [7 empty] | 3
9. Cumulative total number of customers on the third most frequently de-energized circuit | [7 empty] | 2073 | This metric reports PSPS customer outages; therefore, a customer who was de-energized in more than one event would add more than one to the total.
B. Duration of Circuits De-energized
1. Name of Longest (in hours) circuit de-energized. |  | OAKHURST 1103 | BUCKS CREEK 1103 | CORNING 1101 | CALPINE 1144 | TEJON 1102 |  | 0 | For the 10/11/2021, as mentioned in the 10-day report, PG&E was not able to restore Calpine 1144 within 24 Hours of the Weather All Clear as the Calpine 1144 line is not owned by PG&E. At the weather “All Clear”, PG&E requested that Calpine begin patrols of the line, and PG&E was informed that patrols would not begin until the 10/14 PSPS event was completed.
2. Number of Hours that longest de-energized circuit was de-energized |  | 185.0667 | 62.65 | 18.5833 | 79.35 | 39.4167 |  | 385.0667
3. Number of customers impacted |  | 703 | 316 | 841 | 15 | 595 |  | 2470
4. Name of Second Longest (in hours) circuit de-energized. |  | MARIPOSA 2101 | VOLTA 1102 | TEJON 1102 | CALPINE 1146 | CAL WATER 1102 |  | 0 | For the 10/11/2021, as mentioned in the 10-day report, PG&E was not able to restore Calpine 1146 within 24 Hours of the Weather All Clear as the Calpine 1146 line is not owned by PG&E. At the weather “All Clear”, PG&E requested that Calpine begin patrols of the line, and PG&E was informed that patrols would not begin until the 10/14 PSPS event was completed.
5. Number of Hours that longest de-energized circuit was de-energized |  | 184.0167 | 48.0667 | 18.35 | 79.35 | 14.6333 |  | 344.4167
6. Number of customers impacted |  | 1363 | 2584 | 598 | 0 | 13 |  | 4558
7. Name of Third Longest (in hours) circuit de-energized. |  | MARIPOSA 2102 | ELK CREEK 1101 | SCE TEHACHAPI 1101 | RED BLUFF 1103 | MAGUNDEN 1108 |  | 0 | Note for the 9/20/2021 event, SCE Tehachapi 1101 is a circuit owned by Southern California Edison.
8. Number of Hours that longest de-energized circuit was de-energized |  | 133.6333 | 47.5167 | 14.95 | 39.25 | 14.1167 |  | 249.4667
9. Number of customers impacted |  | 81 | 856 | 3 | 214 | 38 |  | 1192
VIII. CFCI
A. CFCI De-energized
1. Number of CFCI de-energized |  | 162 | 936 | 115 | 660 | 38 |  | 1911
2. Number of Communication Services Providers (CSP) CFCI de-energized. |  | 113 | 583 | 92 | 426 | 23 |  | 1237
3. Number of Cell Towers de-energized* |  | N/A | N/A | N/A | N/A | N/A |  | 0 | PG&E, SCE, and SDG&E jointly provided comments in the Post Season Data Report Template to SED on 11/29 to reiterate that these data points either cannot be tracked retroactively and/or are not used by PG&E in our PSPS decision making. These data points were also not required by any of the Commission decisions, including Resolution ESRB-8, D.19-05-042 (Phase 1), D.20-05-051 (Phase 2), D.21-06-034 (Phase 3), and D. 21-06-014 (PSPS OII), or the Post Event Report (PER) template provided in October 2021.
4. Number of Water/Wastewater CFCI de-energized. |  | 90 | 472 | 44 | 353 | 13 |  | 972
5. Number of de-energized CFCI that requested backup power.* |  | 0 | 1 | 2 | 3 | 3 |  | 9 | Customer count provided versus sites.
6. Number of de-energized CFCI that were provided backup power.* |  | 0 | 1 | 2 | 3 | 3 |  | 9 | Customer count provided versus sites.
7. Number of CFCI that were de-energized during two events. |  | - | - | - | - | - |  | 303
8. Number of CFCI that were de-energized during more than two events. |  | - | - | - | - | - |  | 97
IX. Backup Power
A. Backup Power Support
1. Number of Requests for Backup Power |  | 0 | 1 | 2 | 4 | 4 |  | 11
2. Percentage of Requests Satisfied (%) |  | 100% | 100% | 100% | 75% | 100% |  | 95% | One customer was not supported in 10/11 event because they did not meet criteria of CFCI
3. Total MW capacity supplied (MW)* |  | 0 | 0.2 | 0.056 | 1.4 | 0.456 |  | 2.112 | Microgrids are not included in the total MW capacity supplied (MW)
4. Percentage of backup power supplied that was renewable (%) |  | 0% | 0% | 0% | 0% | 0% |  | 0
5. Number of Requests for Consultative Assistance up to one month prior |  | - | - | - | - | - |  | 0
B. Backup Power Programs
1. Applications received for backup generators or storage from the day after the last PSPS through the end of the current one |  | 163 | 717 | 290 | 253 | 38 |  | 1461
2. Number of backup generators issued from the day after the last PSPS through the end of the current one |  | 65 | 392 | 52 | 133 | 27 |  | 669 | PG&E does not physically issue backup generators to customers for the Generator & Battery Rebate Program. For this program, customers purchase their portable generators or portable batteries out of pocket, and PG&E issues rebate payments to them. Therefore, the count includes rebates issues for those who purchased both generators and batteries.
3. Number of backup storage issued from the day after the last PSPS through the end of the current one |  | 1920 | 1739 | 1416 | 847 | 223 |  | 6145 | Weekly reporting is provided by vendors, therefore numbers are approximates to the timeline of day after last PSPS through end of the current PSPS. Appendix D of the Pacific Gas and Electric Company's (U 39 E) 2022 Access and Functional Needs (AFN) Plan for Public Safety Power Shutoff (PSPS) Support provides the Q4 2021 progress report which includes all batteries delivered in 2021.”
C. Microgrids
1. Number of microgrids that replaced the de-energized load |  | 0 | 4 | 0 | 0 | 0 |  | 4
2. Megawatts of load provided by microgrids (MWh) |  | 0 | 9.49 | 0 | 0 | 0 |  | 9.49 | The number differs from what was reported in the PER because the Calistoga (Napa County) microgrid provided a combined 5.99 MW of power to the Calistoga 1101 and Calistoga 1102 circuits. This number differs from what was previously reported in the August 17, 2021 Post Event Report (5.13 MW). This microgrid was the first to utilize a new technology of Tier 4 generator engines and unfortunately experienced some communication errors between engines. The generators supporting the microgrid were ran successfully in test mode but four generators failed when the actual microgrid load was applied during the PSPS event. Therefore, two additional 1 MW generators were deployed to support the microgrid.
3. Percentage of Microgrids in use using renewable fuel (%) |  | 0 | 25% | 0 | 0 | 0 |  | 25%
X. Mitigation
A. Mitigation Deployed
1. Number of Circuits sectionalized to reduce PSPS scope |  | 18 | 84 | 15 | 87 | 6 |  | 210
XI. CRCs
A. Community Resource Centers
1. Number of CRCs open during event |  | 7 | 34 | 9 | 24 | 11 |  | 85
2. Total Number of Visitors to all CRCs during the event |  | 1312 | 3376 | 265 | 5534 | 347 |  | 10834 | The number reported for the Jan 18th event excludes customers who visited CRCs opened only for the January storm event.
3. Percentage of CRCs that were indoors (%) |  | 71.43% | 55.88% | 44.44% | 37.5% | 36.36% |  | 49.12%
4. Percentage of indoor CRCs that had been opened in the past (reliably placed) (%) |  | 40% | 47% | 75% | 78% | 100% |  | 3.4 | Note that many CRC locations were new in 2021 and so could not have been opened in the past.
5. Percentage of CRCs that were indoors when AQI was >100 (%) |  | N/A - no sites over 100 when opened | 67% | N/A - no sites over 100 when opened | N/A - no sites over 100 when opened | N/A - no sites over 100 when opened |  | 0.67 | AQI data referenced is for the hour the site opened. AQI data is pulled from publicly available Purple Air sensors near CRCs where available. Additionally, CRC location decisions are made 1-3 days in advance of a PSPS event to allow for staffing and logistics set up.
6. First Longest Distance from each event's CRCs to furthest targeted customer (mi.) |  | N/A | N/A | N/A | N/A | N/A |  | 0 | When opening CRCs during a PSPS event, PG&E does not use nor calculate radii or exact distance from impacted customers to the CRC as decision criteria for site activation. Instead, we review which cities have a significant number of impacted customers based on the specific scope of the event and select CRCs to activate from our pre-established site portfolio that will best serve those customers and local community needs. In the atypical case where a substantial number of customers are impacted where we don’t have an existing site, we work ad hoc to identify a new site in a location that will serve those customers. We obtain feedback and approval from each county and tribal government to ensure all local entities agree CRC are located in areas that will serve the best interests of the impacted community. During PSPS events there are always some impacted community members located in remote areas where a CRC would be underutilized. We offer other services that are designed to better meet the needs of these community members, such as our portable battery program, and partnerships with 211 and with the California Foundation for Independent Living Centers.
7. Second Longest Distance from each event's CRCs to furthest targeted customer (mi.) |  | N/A | N/A | N/A | N/A | N/A |  | 0 | When opening CRCs during a PSPS event, PG&E does not use nor calculate radii or exact distance from impacted customers to the CRC as decision criteria for site activation. Instead, we review which cities have a significant number of impacted customers based on the specific scope of the event and select CRCs to activate from our pre-established site portfolio that will best serve those customers and local community needs. In the atypical case where a substantial number of customers are impacted where we don’t have an existing site, we work ad hoc to identify a new site in a location that will serve those customers. We obtain feedback and approval from each county and tribal government to ensure all local entities agree CRC are located in areas that will serve the best interests of the impacted community. During PSPS events there are always some impacted community members located in remote areas where a CRC would be underutilized. We offer other services that are designed to better meet the needs of these community members, such as our portable battery program, and partnerships with 211 and with the California Foundation for Independent Living Centers.
8. Third Longest Distance from each event's CRCs to furthest targeted customer (mi.) |  | N/A | N/A | N/A | N/A | N/A |  | 0 | When opening CRCs during a PSPS event, PG&E does not use nor calculate radii or exact distance from impacted customers to the CRC as decision criteria for site activation. Instead, we review which cities have a significant number of impacted customers based on the specific scope of the event and select CRCs to activate from our pre-established site portfolio that will best serve those customers and local community needs. In the atypical case where a substantial number of customers are impacted where we don’t have an existing site, we work ad hoc to identify a new site in a location that will serve those customers. We obtain feedback and approval from each county and tribal government to ensure all local entities agree CRC are located in areas that will serve the best interests of the impacted community. During PSPS events there are always some impacted community members located in remote areas where a CRC would be underutilized. We offer other services that are designed to better meet the needs of these community members, such as our portable battery program, and partnerships with 211 and with the California Foundation for Independent Living Centers.
XII. EV Charging
A. EV Charging Stations
1. Number of level 3 charging stations* de-energized |  | N/A | N/A | N/A | N/A | N/A |  | N/A | EV charging stations are behind the meter and cannot be tracked.
XIII. Restoration
A. Late Restoration
1. Number of Circuits not Restored within 24 hrs. of all-clear. |  | 5 | 6 | 0 | 0 | 0 |  | 11
XIV. Complaints
A. Complaints
1. Number of Complaints |  | 0 | 573 | 96 | 330 | 84 |  | 1083
XV. Claims
A. Claims
1. Number of Claims |  | 5 | 33 | 4 | 18 | 0 |  | 60 | The data provided for claims was aggregated from the information in the "20. Claims" worksheet in this Post Season Data Report. As noted on the "20. Claims" worksheet, claims may not match PER exactly because claims are further investigated post an event and may be recategorized (description, PSPS related, etc.)
2. Total Value of Claims (dollars) |  | 0 | 0 | 0 | 0 | 0 |  | 0

## 9.Decision Factors
[5 empty] | A. Forecast and Reported Meteorology | [13 empty] | B. Reported/Calculated Fire Risk Factors | [8 empty] | C. Model Output | [5 empty] | D. Actual Meteorology | [5 empty] | E. PSPS Risk vs. Benefit
Event Name[1],[2],[3] | Distribution Circuit or Transmission Line Name | Sustained wind speeds (mph) - max | Sustained wind speeds at 50 m (mph0 - max | Gust wind speeds (mph) - max | Peak Gusts wind speeds (mph) - max | Temperature (degrees F) - max | Flame length (ft) - max | Rate of spread (chains/hr) - max | Acres burned (acres) - max | Relative Humidity (%) - min | High Wind Warning (yes/no) | High Wind Advisory (yes/no) | Red Flag Warning (yes/no) | GACC High Risk (yes/no) | Fire Potential Index (probability outputs) -max | Dead Fuel Moisture Content 10 hrs (%) - min | Dead Fuel Moisture Content 100 hrs (%) - min | Dead Fuel Moisture Content 1000 hrs (%) - min | Live Fuel Moisture Content-herbacous (%) - min | Live Fuel Moisture Content-woody (%) - min | Live Fuel Moisture Content-shrub (%) - min | Normalized Difference Vegetation Index | Energy Release Component (BTUs psf) | Santa Ana Wildfire Threat Index | Hazards or Threats Scoping Factors (see Utility Definitions). List all that apply. | Tree Overstike (ft) - max | Prob_Ignition (IPW) - max | CFP-2021 LFP-2020 (2020 distribution protocols used in January Event, and 2020 Transmission protocols used in August event) - max | Impacted by Transmission | Actual Sustained Wind Speed during Event (mph) - max | Actual Wind gust during Event (mph) - max | Actual Average Peak Wind Gust during Event (mph) - max | Actual Temperature during event (degrees F) - max | Actual Relative Humidity During Event (%) - min | Actual Sustained Wind Speed at All Clear (mph) - max | Actual Sustained Wind gust at All Clear (mph) - max | Actual Temperature at All Clear(degrees F) - max | Actual Relative Humidity at All Clear (%) - min | Air Quality (AQI) | PSPS Potential Risk Consequence | PSPS Potential Benefit | PG&E Remarks
2021-01-18 | AUBERRY 1101 | 36.2807 | N/A | 61.6773 | 61.6773 | 58.4913 | N/A | N/A | N/A | 7.0048 | N/A | N/A | NO | NO | 0.31814 | 6.565 | 9.178 | 9.748 | N/A | N/A | 78.9886 | N/A | N/A | N/A | N/A | N/A | N/A | 24.0748 | NO | 37.8 | 66.4 | 66.4 | 65.12 | 9.4 | 6 | 11 | 55.58 | 22.9 | N/A | N/A | N/A | See footnote #1
2021-01-18 | BALCH NO 1 1101 | 40.496 | N/A | 68.8432 | 68.8432 | 66.3906 | N/A | N/A | N/A | 5.1399 | N/A | N/A | NO | NO | 0.33266 | 6.61 | 10.246 | 10.922 | N/A | N/A | 78.4502 | N/A | N/A | N/A | N/A | N/A | N/A | 33.1211 | NO | 26 | 39 | 39 | 60.98 | 10 | 18.4 | 23 | 47.84 | 36.9 | N/A | N/A | N/A | See footnote #1
2021-01-18 | CAL WATER 1102 | 44.7039 | N/A | 75.9966 | 75.9966 | 62.2028 | N/A | N/A | N/A | 8.3126 | N/A | N/A | NO | NO | 0.28588 | 7.101 | 9.768 | 10.684 | N/A | N/A | 74.9654 | N/A | N/A | N/A | N/A | N/A | N/A | 10.287 | NO | 40.1 | 58.5 | 58.5 | 65.48 | 16.6 | 10.2 | 12.3 | 54.5 | 29.9 | N/A | N/A | N/A | See footnote #1
2021-01-18 | DUNLAP 1102 | 41.923 | N/A | 71.2691 | 71.2691 | 59.7865 | N/A | N/A | N/A | 8.9646 | N/A | N/A | NO | NO | 0.35311 | 7.162 | 8.259 | 7.722 | N/A | N/A | 78.8867 | N/A | N/A | N/A | N/A | N/A | N/A | 34.7524 | NO | 34.6 | 51.2 | 51.2 | 62.06 | 12.1 | 7.3 | 9.2 | 52.7 | 22.1 | N/A | N/A | N/A | See footnote #1
2021-01-18 | DUNLAP 1103 | 43.1281 | N/A | 73.3178 | 73.3178 | 61.2411 | N/A | N/A | N/A | 7.9414 | N/A | N/A | NO | NO | 0.36056 | 7.042 | 8.184 | 7.565 | N/A | N/A | 78.2513 | N/A | N/A | N/A | N/A | N/A | N/A | 34.7524 | NO | 34.6 | 51.2 | 51.2 | 62.6 | 12.1 | 7.3 | 9.2 | 52.7 | 22.1 | N/A | N/A | N/A | See footnote #1
2021-01-18 | LAMONT 1102 | 42.5035 | N/A | 72.2559 | 72.2559 | 62.8827 | N/A | N/A | N/A | 8.2878 | N/A | N/A | NO | NO | 0.23597 | 7.177 | 10.293 | 11.423 | N/A | N/A | 74.9086 | N/A | N/A | N/A | N/A | N/A | N/A | 8.4791 | NO | 32.9 | 56.5 | 56.5 | 64.22 | 16.8 | 4.9 | 10.6 | 50.54 | 30.8 | N/A | N/A | N/A | See footnote #1
2021-01-18 | MARIPOSA 2101 | 38.5001 | N/A | 65.4501 | 65.4501 | 62.0127 | N/A | N/A | N/A | 3.6191 | N/A | N/A | NO | NO | 0.28678 | 6.809 | 8.652 | 9.899 | N/A | N/A | 79.9721 | N/A | N/A | N/A | N/A | N/A | N/A | 14.741 | NO | 35 | 77 | 77 | 64.4 | 4 | 8.7 | 22 | 64.4 | 11 | N/A | N/A | N/A | See footnote #1
2021-01-18 | MARIPOSA 2102 | 38.2311 | N/A | 64.9928 | 64.9928 | 58.3165 | N/A | N/A | N/A | 9.0132 | N/A | N/A | NO | NO | 0.14191 | 6.847 | 9.474 | 11.177 | N/A | N/A | 84.9321 | N/A | N/A | N/A | N/A | N/A | N/A | 8.3303 | NO | 31.8 | 62 | 62 | 62.78 | 6.6 | 3.8 | 8 | 62.78 | 13 | N/A | N/A | N/A | See footnote #1
2021-01-18 | MESA 1101 | 28.3254 | N/A | 48.1531 | 48.1531 | 69.2035 | N/A | N/A | N/A | 8.1153 | N/A | N/A | YES | YES | 0.27032 | 5.933 | 7.873 | 9.888 | N/A | N/A | 80.3045 | N/A | N/A | N/A | N/A | N/A | N/A | 8.8676 | NO | 22.6 | 43.6 | 43.6 | 69.8 | 13.1 | 20.8 | 30.5 | 63.14 | 15.4 | N/A | N/A | N/A | See footnote #1
2021-01-18 | OAKHURST 1103 | 37.1134 | N/A | 63.0928 | 63.0928 | 51.3477 | N/A | N/A | N/A | 5.252 | N/A | N/A | NO | NO | 0.32693 | 7.083 | 9.973 | 10.952 | N/A | N/A | 78.8478 | N/A | N/A | N/A | N/A | N/A | N/A | 8.7376 | NO | 23.8 | 53.3 | 53.3 | 61.88 | 7.7 | 1.4 | 3.2 | 44.96 | 27.2 | N/A | N/A | N/A | See footnote #1
2021-01-18 | SAN JOAQUIN #3 1101 | 44.7105 | N/A | 76.0079 | 76.0079 | 54.3068 | N/A | N/A | N/A | 10.7523 | N/A | N/A | NO | NO | 0.38042 | 7.01 | 10.032 | 10.59 | N/A | N/A | 79.4967 | N/A | N/A | N/A | N/A | N/A | N/A | 28.7195 | NO | 17 | 46.3 | 46.3 | 60.98 | 8.9 | 5.7 | 8.3 | 41 | 35.7 | N/A | N/A | N/A | See footnote #1
2021-01-18 | SAN JOAQUIN #3 1103 | 42.6035 | N/A | 72.426 | 72.426 | 53.8313 | N/A | N/A | N/A | 9.2687 | N/A | N/A | NO | NO | 0.35165 | 7.062 | 9.939 | 10.511 | N/A | N/A | 80.8573 | N/A | N/A | N/A | N/A | N/A | N/A | 11.3766 | NO | 23.5 | 52.7 | 52.7 | 60.98 | 8.9 | 6.8 | 10.4 | 41 | 35.7 | N/A | N/A | N/A | See footnote #1
2021-01-18 | SAND CREEK 1103 | 41.2854 | N/A | 70.1852 | 70.1852 | 57.9404 | N/A | N/A | N/A | 7.32 | N/A | N/A | NO | NO | 0.32489 | 7.242 | 8.573 | 9.3 | N/A | N/A | 80.5708 | N/A | N/A | N/A | N/A | N/A | N/A | 27.0635 | NO | 18 | 38 | 38 | 55.94 | 14 | 10.3 | 15.7 | 55.04 | 23 | N/A | N/A | N/A | See footnote #1
2021-01-18 | SANTA MARIA 1108 | 30.5982 | N/A | 52.0169 | 52.0169 | 67.309 | N/A | N/A | N/A | 8.6624 | N/A | N/A | YES | YES | 0.28159 | 5.984 | 7.901 | 9.675 | N/A | N/A | 79.2595 | N/A | N/A | N/A | N/A | N/A | N/A | 8.8676 | NO | 22.6 | 43.6 | 43.6 | 68.9 | 13.1 | 15.5 | 22.6 | 60.44 | 21 | N/A | N/A | N/A | See footnote #1
2021-01-18 | SCE TEHACHAPI 1101 | 48.0703 | N/A | 81.7195 | 81.7195 | 56.2569 | N/A | N/A | N/A | 12.5114 | N/A | N/A | NO | NO | 0.39059 | 7.399 | 9.307 | 10.391 | N/A | N/A | 71.4796 | N/A | N/A | N/A | N/A | N/A | N/A | 39.4357 | NO | 35.9 | 60.2 | 60.2 | 46.04 | 24.4 | 10.4 | 23.5 | 44.96 | 36.1 | N/A | N/A | N/A | See footnote #1
2021-01-18 | SISQUOC 1103 | 29.1796 | N/A | 49.6053 | 49.6053 | 67.451 | N/A | N/A | N/A | 8.5914 | N/A | N/A | YES | YES | 0.27708 | 5.898 | 7.004 | 8.577 | N/A | N/A | 77.2287 | N/A | N/A | N/A | N/A | N/A | N/A | 3.6389 | NO | 35.9 | 60.2 | 60.2 | 46.04 | 27.6 | 10.4 | 23.5 | 44.96 | 36.1 | N/A | N/A | N/A | See footnote #1
2021-01-18 | SO. CAL. EDISON #3 1101 | 38.2278 | N/A | 64.9873 | 64.9873 | 65.025 | N/A | N/A | N/A | 7.4108 | N/A | N/A | NO | NO | 0.34867 | 6.424 | 10.245 | 11.796 | N/A | N/A | 85.104 | N/A | N/A | N/A | N/A | N/A | N/A | 10.8491 | NO | 37.8 | 66.4 | 66.4 | 65.12 | 9.4 | 6.8 | 10.4 | 53.6 | 23.1 | N/A | N/A | N/A | See footnote #1
2021-01-18 | TEJON 1103 | 43.7608 | N/A | 74.3933 | 74.3933 | 62.823 | N/A | N/A | N/A | 10.4981 | N/A | N/A | NO | NO | 0.40102 | 7.281 | 11.323 | 12.871 | N/A | N/A | 74.9528 | N/A | N/A | N/A | N/A | N/A | N/A | 37.9749 | NO | 37 | 57.1 | 57.1 | 64.58 | 17.5 | 5.9 | 9.4 | 50.72 | 39.4 | N/A | N/A | N/A | See footnote #1
2021-08-17 | (Tx) FULTON-CALISTOGA | 32.17 | 46.62 | 43.3 | 43.3 | 94.13 | 29.6 | 45.9 | 1358 | 15 | N/A | N/A | YES | YES | 0.31 | 5.2 | 6.6 | 6.4 | 36.04 | 62.25 | 66.69 | N/A | N/A |  | Assets conditions, Vegetation conditions | Yes | N/A | 0.04759 | NO | 41 | 54.2 | 54.2 | 89.96 | 11.4 | 13.1 | 23.2 | 86.72 | 11.5 | N/A | N/A | N/A | See footnote #1
2021-08-17 | (Tx) LOWER LAKE-HOMESTAKE | 28.31 | 41.39 | 50 | 50 | 93.29 | 12.6 | 67.5 | 4093 | 18 | N/A | N/A | YES | YES | 0.36 | 4.5 | 5.9 | 5.5 | 32.09 | 57.69 | 68.24 | N/A | N/A |  | Assets conditions, Vegetation conditions | Yes | N/A | 0.005136 | NO | 27.6 | 42.9 | 42.9 | 90.86 | 9.4 | 21.7 | 32.5 | 86 | 12 | N/A | 0.025273 | 1209.2836
2021-08-17 | (Tx) ROCK CREEK-POE | 20.16 | 29.95 | 35.3 | 35.3 | 83.9 | 9.5 | 50.4 | 2681 | 26 | N/A | N/A | YES | YES | 0.29 | 5.5 | 6.3 | 5.5 | 47.9 | 73.92 | 70.91 | N/A | N/A |  | Assets conditions, Vegetation conditions | Yes | N/A | 7.5e-05 | NO | 34 | 56 | 56 | 87.98 | 13.4 | 21 | 30 | 74.66 | 27 | N/A | 0.025116 | 143.5531
2021-08-17 | ANDERSON 1101 | 26.47 | 34.52 | 50.06 | 50.06 | 96.6 | 6.92 | 43.3 | 3946.1 | 9.84 | N/A | N/A | YES | YES | 0.65 | 3.4 | 5.5 | 5.1 | 54.27 | 68.56 | 68.65 | N/A | N/A |  | Assets conditions, Vegetation conditions | 3074.9 | 0.00341 | 20.72 | NO | 25 | 40.5 | 40.5 | 94.46 | 10 | 11.3 | 23.2 | 91.4 | 15.8 | N/A | 0.87045 | 1688.9083
2021-08-17 | ANDERSON 1103 | 25.97 | 31.57 | 47.43 | 47.43 | 83.55 | 7.97 | 59.9 | 5983.4 | 13.66 | N/A | N/A | YES | YES | 0.61 | 3.5 | 5.7 | 5.2 | 32.34 | 79.74 | 68.57 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1094.9 | 0.00242 | 14.76 | NO | 25.9 | 42.6 | 42.6 | 93.02 | 6.9 | 14.2 | 24 | 91.4 | 15.6 | N/A | 0.10041 | 1015.4688
2021-08-17 | ANTLER 1101 | 22.9 | 33.35 | 53.42 | 53.42 | 80.22 | 32.97 | 25.5 | 400.3 | 14.63 | N/A | N/A | YES | YES | 0.78 | 3.7 | 6 | 5.3 | 38.46 | 72.34 | 65.83 | N/A | N/A |  | Assets conditions, Vegetation conditions | 49813.6 | 0.00273 | 19.52 | NO | 27.6 | 39.1 | 39.1 | 86.54 | 9 | 23.7 | 40.6 | 71.96 | 27 | N/A | 0.4441 | 36.3142
2021-08-17 | ARBUCKLE 1101 | 21.02 | 31.17 | 44.05 | 44.05 | 94.91 | 8.7 | 54.93 | 5535.6 | 8.88 | N/A | N/A | YES | YES | 0.8 | 3.8 | 5.8 | 5.6 | 31.96 | 61.06 | 69.24 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.00191 | 13.96 | NO | 24.9 | 37.1 | 37.1 | 85.82 | 17.4 | 15.7 | 27.3 | 86.54 | 19.7 | N/A | 0.030191 | 107.5948
2021-08-17 | ARBUCKLE 1104 | 21.2 | 30.96 | 44.21 | 44.21 | 94.76 | 8.82 | 53.04 | 6252.1 | 9 | N/A | N/A | YES | YES | 0.87 | 3.9 | 5.7 | 5.3 | 30.99 | 60.48 | 68.83 | N/A | N/A |  | Assets conditions, Vegetation conditions | 477.9 | 0.00163 | 12.65 | NO | 24.9 | 37.1 | 37.1 | 85.82 | 17.4 | 15.7 | 27.3 | 86.54 | 19.7 | N/A | 0.045415 | 308.2114
2021-08-17 | BIG BEND 1101 | 22.93 | 38.94 | 53.52 | 53.52 | 91.89 | 20.62 | 68.65 | 3804.2 | 10.72 | N/A | N/A | YES | YES | 0.87 | 4.2 | 5.6 | 4.8 | 32.35 | 67 | 65.96 | N/A | N/A |  | Assets conditions, Vegetation conditions | 88659.2 | 0.00579 | 37 | NO | 34 | 56 | 56 | 90.68 | 13.4 | 21 | 30 | 77 | 26.5 | N/A | 0.46662 | 660.875
2021-08-17 | BUCKS CREEK 1103 | 19.12 | 29.85 | 45.71 | 45.71 | 80.77 | 30.25 | 25.9 | 417.4 | 13.18 | N/A | N/A | YES | YES | 0.8 | 4.3 | 5.7 | 5 | 35.66 | 73.28 | 65.4 | N/A | N/A |  | Assets conditions, Vegetation conditions | 5025.3 | 0.00137 | 9.05 | NO | 8.1 | 21.5 | 21.5 | 67.28 | 23.6 | 4.9 | 12.5 | 48.56 | 59.1 | N/A | 0.54612 | 8.5
2021-08-17 | BURNEY 1101 | 21.64 | 30.9 | 51.84 | 51.84 | 69.73 | 29.1 | 20.23 | 629.5 | 19.1 | N/A | N/A | YES | NO | 0.42 | 4.6 | 7 | 5.8 | 55.53 | 85.87 | 62.9 | N/A | N/A |  | Assets conditions, Vegetation conditions | 30933.3 | 0.0032 | 11.93 | NO | 14.9 | 24.6 | 24.6 | 78.98 | 10 | 13.7 | 23.1 | 53.06 | 54.4 | N/A | 0.17973 | 483.525
2021-08-17 | BUTTE 1105 | 18.22 | 29.16 | 42.3 | 42.3 | 91.19 | 9.12 | 40.31 | 2057.2 | 9.14 | N/A | N/A | YES | YES | 0.82 | 4 | 5.6 | 5 | 31.7 | 73.59 | 69.42 | N/A | N/A |  | Assets conditions, Vegetation conditions | 22497.4 | 0.00111 | 7.99 | NO | 13.5 | 26.4 | 26.4 | 83.12 | 15.8 | 9.6 | 16.7 | 74.48 | 19.9 | N/A | 0.11477 | 157.5466
2021-08-17 | CALISTOGA 1101 | 32.17 | 46.62 | 66.78 | 66.78 | 94.13 | 70.99 | 64.92 | 3436.3 | 8.55 | N/A | N/A | YES | YES | 0.89 | 4.1 | 5.7 | 5.2 | 36.04 | 62.25 | 66.69 | N/A | N/A |  | Assets conditions, Vegetation conditions | 69278.3 | 0.00397 | 31.94 | YES | 41 | 54.2 | 54.2 | 88.88 | 11.4 | 14.6 | 26.5 | 84.74 | 14.5 | N/A | 2.8662 | 1128.5096
2021-08-17 | CALISTOGA 1102 | 22.53 | 34.05 | 52.9 | 52.9 | 95.15 | 21.65 | 38.62 | 754.1 | 9.09 | N/A | N/A | YES | YES | 0.85 | 4.7 | 7.4 | 6.8 | 39.01 | 60.27 | 67.29 | N/A | N/A |  | Assets conditions, Vegetation conditions | 69278.3 | 0.00317 | 23.37 | YES | 17.3 | 27.2 | 27.2 | 85.1 | 14.7 | 8.6 | 14.5 | 83.66 | 16 | N/A | 3.6867 | 826.8614
2021-08-17 | CALPINE 1144 | 23.9 | 36.21 | 52.4 | 52.4 | 90.59 | 36.57 | 62.44 | 2638.4 | 7.43 | N/A | N/A | YES | YES | 0.88 | 3.7 | 5.3 | 4.9 | 35.96 | 62.09 | 66.74 | N/A | N/A |  | Assets conditions, Vegetation conditions | 3736.7 | 0.00393 | 29.54 | NO | 39.9 | 48.7 | 48.7 | 85.46 | 13.6 | 15.6 | 28.7 | 85.64 | 12 | N/A | 0.051585 | 43.7466
2021-08-17 | CALPINE 1146 | 18.05 | 28.07 | 42.99 | 42.99 | 85.57 | 13.74 | 38.87 | 1353.4 | 8.8 | N/A | N/A | YES | YES | 0.83 | 4 | 6 | 5.4 | 42.26 | 66.25 | 68.53 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.00103 | 7.52 | NO | 39.9 | 48.7 | 48.7 | 79.16 | 14.2 | 15.6 | 28.7 | 78.44 | 16.6 | N/A | 0.024905 | 15.5
2021-08-17 | CEDAR CREEK 1101 | 32.43 | 48.7 | 72.94 | 72.94 | 80.84 | 75.56 | 53.98 | 1220.7 | 13.89 | N/A | N/A | YES | YES | 0.68 | 3.7 | 5.7 | 5 | 38.61 | 66.71 | 64.21 | N/A | N/A |  | Assets conditions, Vegetation conditions | 87136.2 | 0.00567 | 30.54 | NO | 30.4 | 48.6 | 48.6 | 87.44 | 7.3 | 15.5 | 30.8 | 85.28 | 19.2 | N/A | 0.87725 | 96.8694
2021-08-17 | CLARK ROAD 1102 | 27.14 | 39.09 | 53.52 | 53.52 | 94.24 | 15.08 | 50.75 | 6961.4 | 9.33 | N/A | N/A | YES | YES | 0.91 | 4.1 | 5.5 | 4.8 | 31.61 | 66.19 | 68.33 | N/A | N/A |  | Assets conditions, Vegetation conditions | 21285.1 | 0.00416 | 31.56 | NO | 34 | 56 | 56 | 91.04 | 12.6 | 21 | 30 | 78.44 | 25.1 | N/A | 0.85399 | 1162.7623
2021-08-17 | CLOVERDALE 1102 | 24.92 | 37.35 | 51.68 | 51.68 | 94.76 | 14.13 | 66.51 | 1651.3 | 8.44 | N/A | N/A | YES | YES | 0.81 | 4 | 5.8 | 5.3 | 44.4 | 66.11 | 65.88 | N/A | N/A |  | Assets conditions, Vegetation conditions | 5638 | 0.00217 | 14.59 | NO | 17.6 | 28.9 | 28.9 | 81.68 | 18.8 | 9 | 12.8 | 74.66 | 30.4 | N/A | 0.14864 | 563.075
2021-08-17 | CORNING 1101 | 29.68 | 37.62 | 53.74 | 53.74 | 97.35 | 8.74 | 102 | 15221.5 | 9.49 | N/A | N/A | YES | YES | 0.86 | 3.2 | 5.2 | 5.2 | 30.06 | 67.77 | 68.81 | N/A | N/A |  | Assets conditions, Vegetation conditions | 6259.9 | 0.0026 | 20.76 | NO | 30.3 | 45.3 | 45.3 | 90.86 | 12.4 | 23.4 | 33.7 | 91.04 | 15.7 | N/A | 1.5688 | 1821.2111
2021-08-17 | CORNING 1102 | 33.72 | 45.09 | 74.18 | 74.18 | 96.63 | 59.77 | 110.75 | 19625.6 | 9.35 | N/A | N/A | YES | YES | 0.9 | 3 | 4.8 | 4.7 | 30 | 59.22 | 67.95 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1979 | 0.00244 | 19.4 | NO | 32 | 55 | 55 | 89.96 | 11.3 | 23.5 | 33 | 90.14 | 15.8 | N/A | 0.56172 | 4691.7639
2021-08-17 | CORTINA 1101 | 23.15 | 34.2 | 48.87 | 48.87 | 91.12 | 14.37 | 87.14 | 8907.5 | 8.88 | N/A | N/A | YES | YES | 0.9 | 3.8 | 5.4 | 4.9 | 30.37 | 61.21 | 70.15 | N/A | N/A |  | Assets conditions, Vegetation conditions | 18.4 | 0.00145 | 11.38 | NO | 22.5 | 32.2 | 32.2 | 88.16 | 11.6 | 19.9 | 27.5 | 88.88 | 15 | N/A | 0.038648 | 19.7
2021-08-17 | COTTONWOOD 1101 | 22.65 | 32.89 | 48.06 | 48.06 | 96.23 | 11.37 | 80.73 | 9265 | 9.81 | N/A | N/A | YES | YES | 0.84 | 3.3 | 5.3 | 5.1 | 30.99 | 78.44 | 67.96 | N/A | N/A |  | Assets conditions, Vegetation conditions | 9930 | 0.00303 | 16.45 | NO | 21.7 | 40.5 | 40.5 | 94.46 | 10.9 | 13.8 | 23.1 | 91.4 | 15.9 | N/A | 1.6698 | 793.8
2021-08-17 | COTTONWOOD 1102 | 24.29 | 34.38 | 50.97 | 50.97 | 96.18 | 8.8 | 48.81 | 4919.6 | 9.64 | N/A | N/A | YES | YES | 0.82 | 3.3 | 5.4 | 5 | 32.67 | 62.46 | 68.35 | N/A | N/A |  | Assets conditions, Vegetation conditions | 8310.6 | 0.00313 | 23.69 | NO | 25.7 | 42.8 | 42.8 | 94.46 | 8.6 | 18.2 | 30 | 91.4 | 16.4 | N/A | 1.793 | 2397.4111
2021-08-17 | COTTONWOOD 1103 | 24.28 | 33.52 | 48.11 | 48.11 | 97.61 | 9.69 | 65.02 | 5783.1 | 9.79 | N/A | N/A | YES | YES | 0.86 | 3.4 | 5.5 | 5.2 | 33.11 | 76.67 | 68.07 | N/A | N/A |  | Assets conditions, Vegetation conditions | 9930 | 0.00315 | 18.64 | NO | 20.9 | 40.5 | 40.5 | 94.46 | 7 | 7.7 | 13.9 | 78.08 | 32.7 | N/A | 4.5017 | 2602.8917
2021-08-17 | CRESCENT MILLS 2101 | 12.92 | 17.96 | 31.91 | 31.91 | 75.05 | 6.14 | 20.08 | 950 | 15.11 | N/A | N/A | YES | YES | 0.54 | 4.4 | 6.4 | 5.5 | 46.35 | 75.4 | 65.9 | N/A | N/A |  | Assets conditions, Vegetation conditions | 38601 | 0.0005 | 2.49 | NO | 8.1 | 14 | 14 | 78.08 | 15 | 4.4 | 8.8 | 54.5 | 47 | N/A | 0.23487 | 187.5
2021-08-17 | CRESTA 1101 | 20.16 | 29.95 | 47.97 | 47.97 | 83.9 | 6.08 | 21.79 | 535.3 | 12.85 | N/A | N/A | YES | YES | 0.78 | 4.2 | 5.6 | 4.9 | 47.9 | 73.92 | 70.91 | N/A | N/A |  | Assets conditions, Vegetation conditions | 3924.9 | 0.00154 | 10.81 | NO | 34 | 56 | 56 | 83.84 | 13.6 | 21 | 30 | 72.32 | 28.9 | N/A | 0.026807 | 0.875
2021-08-17 | DESCHUTES 1101 | 22.85 | 34.42 | 47.7 | 47.7 | 86.15 | 11.31 | 66.76 | 9134.6 | 10.7 | N/A | N/A | YES | YES | 0.71 | 3.4 | 5.5 | 5 | 31.52 | 73.91 | 67.1 | N/A | N/A |  | Assets conditions, Vegetation conditions | 47373.6 | 0.00541 | 27.83 | NO | 25.9 | 42.6 | 42.6 | 94.64 | 6.7 | 14.2 | 29.1 | 91.04 | 15.6 | N/A | 0.32372 | 3260.3444
2021-08-17 | DESCHUTES 1104 | 25.97 | 31.57 | 44.99 | 44.99 | 86.87 | 7.97 | 59.9 | 7116.7 | 10.6 | N/A | N/A | YES | YES | 0.65 | 3.3 | 5.6 | 5.1 | 32.34 | 78.21 | 68.36 | N/A | N/A |  | Assets conditions, Vegetation conditions | 7094.3 | 0.00284 | 17.66 | NO | 25.9 | 42.6 | 42.6 | 93.02 | 6.9 | 14.2 | 24 | 91.4 | 15.6 | N/A | 0.47707 | 3261.2194
2021-08-17 | DUNBAR 1101 | 24.16 | 35.53 | 50.3 | 50.3 | 90.7 | 16.45 | 51.95 | 2351.6 | 11.5 | N/A | N/A | YES | YES | 0.86 | 4.7 | 6.9 | 6.1 | 41.43 | 59.76 | 66.83 | N/A | N/A |  | Assets conditions, Vegetation conditions | 23643.9 | 0.00349 | 25.86 | NO | 17.3 | 25.7 | 25.7 | 79.88 | 17.6 | 6.8 | 16.2 | 69.8 | 22.2 | N/A | 0.25628 | 1024.1528
2021-08-17 | DUNBAR 1102 | 14.08 | 20.58 | 29.62 | 29.62 | 91.9 | 6.47 | 17.5 | 325.5 | 10.81 | N/A | N/A | YES | YES | 0.78 | 5.3 | 7.9 | 7.8 | 39.41 | 64.13 | 68.75 | N/A | N/A |  | Assets conditions, Vegetation conditions | 29286.9 | 0.00038 | 2.8 | NO | 14 | 21.3 | 21.3 | 77.9 | 17.9 | 11 | 17.8 | 67.64 | 21.6 | N/A | 0.27922 | 354.4586
2021-08-17 | DUNBAR 1103 | 24.78 | 36.1 | 51.58 | 51.58 | 91.67 | 26.04 | 55.53 | 2100 | 10.87 | N/A | N/A | YES | YES | 0.91 | 4.7 | 6.4 | 5.5 | 39.45 | 61.53 | 65.56 | N/A | N/A |  | Assets conditions, Vegetation conditions | 75579.7 | 0.00221 | 16.91 | NO | 14 | 25.5 | 25.5 | 77.9 | 17.6 | 11 | 17.8 | 67.64 | 19.2 | N/A | 0.48039 | 848.6444
2021-08-17 | ELK CREEK 1101 | 31.37 | 38.67 | 59.51 | 59.51 | 96.05 | 20.22 | 126.66 | 25697.6 | 7.76 | N/A | N/A | YES | YES | 0.92 | 3 | 4.8 | 4.8 | 30 | 56.14 | 68.32 | N/A | N/A |  | Assets conditions, Vegetation conditions | 13262.9 | 0.00211 | 17.27 | NO | 29.8 | 42.2 | 42.2 | 93.92 | 11.3 | 20.9 | 30.5 | 89.96 | 13 | N/A | 1.6147 | 1100.1975
2021-08-17 | GEYSERVILLE 1101 | 18.64 | 24.81 | 37.35 | 37.35 | 91.53 | 7.28 | 20.68 | 384.6 | 10.74 | N/A | N/A | YES | YES | 0.69 | 5 | 7.4 | 6.7 | 56.91 | 62.9 | 65.71 | N/A | N/A |  | Assets conditions, Vegetation conditions | 20051.8 | 0.00039 | 2.04 | NO | 12.5 | 22.4 | 22.4 | 83.66 | 28.8 | 3.9 | 5.9 | 67.46 | 44.7 | N/A | 0.070996 | 94.091
2021-08-17 | GEYSERVILLE 1102 | 26.64 | 39.81 | 55.24 | 55.24 | 96.86 | 12.11 | 61.04 | 1198 | 8.08 | N/A | N/A | YES | YES | 0.88 | 3.8 | 5.8 | 5.3 | 42.96 | 62.25 | 68.01 | N/A | N/A |  | Assets conditions, Vegetation conditions | 5234.6 | 0.00357 | 27.86 | NO | 39.9 | 48.7 | 48.7 | 86.36 | 14.2 | 17.6 | 29.1 | 77.72 | 16.4 | N/A | 0.54921 | 298.6114
2021-08-17 | GIRVAN 1101 | 24.9 | 36.41 | 55.44 | 55.44 | 95.65 | 16.26 | 47.72 | 5108.1 | 9.43 | N/A | N/A | YES | YES | 0.91 | 3.2 | 5.1 | 4.9 | 30.03 | 63.22 | 66.92 | N/A | N/A |  | Assets conditions, Vegetation conditions | 23867.7 | 0.00393 | 30.21 | NO | 25.7 | 42.8 | 42.8 | 96.98 | 8.4 | 19 | 31 | 91.94 | 15 | N/A | 2.2469 | 931.6781
2021-08-17 | GIRVAN 1102 | 22.02 | 32.02 | 48.02 | 48.02 | 96.4 | 10.8 | 55.87 | 5258.1 | 10.32 | N/A | N/A | YES | YES | 0.86 | 3.2 | 5.1 | 4.8 | 37.32 | 61.2 | 66.96 | N/A | N/A |  | Assets conditions, Vegetation conditions | 20596.5 | 0.0027 | 18.43 | NO | 25.7 | 42.8 | 42.8 | 94.64 | 8.4 | 18.2 | 30 | 91.4 | 15.8 | N/A | 1.0928 | 2792.7139
2021-08-17 | GLENN 1101 | 33 | 42.49 | 61.89 | 61.89 | 95.72 | 7.84 | 75.56 | 12471.1 | 9.35 | N/A | N/A | YES | YES | 0.77 | 3.1 | 5 | 4.9 | 30.01 | 60.54 | 69.67 | N/A | N/A |  | Assets conditions, Vegetation conditions | 14.6 | 0.00177 | 12.79 | NO | 30 | 55 | 55 | 89.78 | 11.3 | 22.7 | 32.4 | 89.78 | 16 | N/A | 0.034304 | 5553.7482
2021-08-17 | HIGHLANDS 1102 | 24.08 | 40.14 | 56.76 | 56.76 | 91.37 | 16.41 | 83.81 | 7979.3 | 7.47 | N/A | N/A | YES | YES | 0.91 | 3.7 | 5.7 | 5.2 | 30.51 | 57.86 | 68.55 | N/A | N/A |  | Assets conditions, Vegetation conditions | 927.8 | 0.00175 | 14.25 | NO | 26.7 | 46 | 46 | 85.64 | 9.3 | 22.8 | 39.5 | 82.76 | 14.1 | N/A | 0.042762 | 5870.8816
2021-08-17 | HIGHLANDS 1103 | 28.31 | 41.39 | 66.95 | 66.95 | 93.29 | 13.23 | 64.82 | 5456.5 | 7.09 | N/A | N/A | YES | YES | 0.92 | 3.6 | 5.5 | 5 | 32.09 | 57.69 | 68.24 | N/A | N/A |  | Assets conditions, Vegetation conditions | 22328.7 | 0.00326 | 24.24 | NO | 27.6 | 42.9 | 42.9 | 89.42 | 9.4 | 20.6 | 31.1 | 86.54 | 11.8 | N/A | 2.358 | 5958.9972
2021-08-17 | JAMESON 1102 | 24.76 | 36.34 | 49.98 | 49.98 | 90.84 | 17.93 | 40.07 | 2200.6 | 11.1 | N/A | N/A | NO | YES | 0.9 | 5.1 | 7.8 | 6.7 | 38.03 | 61.5 | 60.73 | N/A | N/A |  | Assets conditions, Vegetation conditions | 5722.9 | 0.0013 | 9.91 | NO | 16.3 | 22.6 | 22.6 | 75.38 | 20.8 | 10.3 | 16.4 | 69.44 | 23.6 | N/A | 0.40804 | 527.1623
2021-08-17 | JAMESON 1105 | 24.76 | 36.34 | 49.98 | 49.98 | 95.18 | 7.03 | 40.26 | 2840.3 | 9.92 | N/A | N/A | YES | YES | 0.9 | 4.7 | 6.5 | 5.8 | 34.62 | 61.23 | 60.43 | N/A | N/A |  | Assets conditions, Vegetation conditions | 3018.1 | 0.00158 | 11.42 | NO | 16.3 | 22.6 | 22.6 | 75.38 | 20.8 | 10.3 | 16.4 | 69.44 | 23.6 | N/A | 0.14158 | 883.7361
2021-08-17 | JESSUP 1101 | 22.7 | 33.35 | 48.26 | 48.26 | 96.25 | 11.99 | 51.55 | 4203.4 | 10.61 | N/A | N/A | YES | YES | 0.91 | 3.3 | 5.4 | 5 | 31.58 | 70.66 | 68.16 | N/A | N/A |  | Assets conditions, Vegetation conditions | 16151 | 0.00331 | 20.4 | NO | 25.7 | 42.8 | 42.8 | 94.46 | 8.6 | 18.2 | 30 | 91.4 | 16.7 | N/A | 2.7063 | 1203.2318
2021-08-17 | JESSUP 1102 | 23.67 | 34.27 | 50.19 | 50.19 | 96.25 | 11.59 | 51.55 | 4754.8 | 10.25 | N/A | N/A | YES | YES | 0.85 | 3.4 | 5.5 | 5.1 | 35.64 | 68.56 | 68.29 | N/A | N/A |  | Assets conditions, Vegetation conditions | 16151 | 0.00426 | 25.97 | NO | 25.7 | 42.8 | 42.8 | 94.64 | 8.6 | 18.2 | 30 | 91.4 | 15.8 | N/A | 2.789 | 2219.3722
2021-08-17 | JESSUP 1103 | 20.76 | 29.22 | 44.35 | 44.35 | 95.77 | 6.65 | 37.38 | 3109.9 | 10.61 | N/A | N/A | YES | YES | 0.64 | 3.4 | 5.6 | 5.2 | 51.92 | 82.79 | 68.93 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2361.8 | 0.0029 | 18.12 | NO | 25 | 40.5 | 40.5 | 94.64 | 10 | 11.8 | 23.2 | 91.4 | 15.8 | N/A | 0.20705 | 1889
2021-08-17 | KESWICK 1101 | 20.97 | 33.55 | 49.65 | 49.65 | 94.56 | 13.85 | 68.85 | 5258.1 | 10.51 | N/A | N/A | YES | YES | 0.88 | 3.2 | 5.2 | 4.8 | 36.77 | 58.96 | 66.04 | N/A | N/A |  | Assets conditions, Vegetation conditions | 8683.8 | 0.00286 | 21.9 | NO | 24.7 | 38 | 38 | 91.4 | 8.4 | 11.2 | 20.7 | 89.6 | 18.6 | N/A | 0.94579 | 1298.2139
2021-08-17 | KONOCTI 1108 | 13.5 | 17.66 | 35.15 | 35.15 | 89.34 | 12.39 | 45.09 | 2534 | 7.74 | N/A | N/A | YES | YES | 0.66 | 3.6 | 5.3 | 5 | 40.64 | 61.03 | 68.07 | N/A | N/A |  | Assets conditions, Vegetation conditions | 5193.5 | 0.00059 | 3.67 | NO | 10.3 | 16.1 | 16.1 | 84.02 | 19 | 5.8 | 11.5 | 73.4 | 19.7 | N/A | 1.2727 | 2762.1028
2021-08-17 | LAKEVILLE 1102 | 22.44 | 32.13 | 46.46 | 46.46 | 86.26 | 5.76 | 43.25 | 2756.8 | 14.85 | N/A | N/A | YES | YES | 0.72 | 5.2 | 6.8 | 5.8 | 38.52 | 64.82 | 68.86 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4259.6 | 0.00102 | 6.28 | NO | 14 | 21.3 | 21.3 | 77 | 23.4 | 11 | 15.6 | 66.74 | 23.8 | N/A | 0.060408 | 894.5105
2021-08-17 | LOGAN CREEK 2102 | 24.85 | 33.66 | 49.75 | 49.75 | 97.17 | 9.92 | 102.3 | 24409.9 | 8.3 | N/A | N/A | YES | YES | 0.79 | 3.1 | 5.2 | 5.2 | 30 | 60.49 | 69.03 | N/A | N/A |  | Assets conditions, Vegetation conditions | 547 | 0.00196 | 14.32 | NO | 34.8 | 45.9 | 45.9 | 89.78 | 11.8 | 23.8 | 32.6 | 90.14 | 15.2 | N/A | 0.039817 | 1378.2333
2021-08-17 | MADISON 1105 | 21.45 | 28.67 | 46.43 | 46.43 | 95.79 | 6.08 | 51.95 | 6869.3 | 8.75 | N/A | N/A | YES | YES | 0.72 | 3.8 | 5.7 | 5.7 | 30.11 | 59.77 | 68.95 | N/A | N/A |  | Assets conditions, Vegetation conditions | 13.4 | 0.00236 | 16.64 | NO | 20.3 | 31.6 | 31.6 | 87.8 | 12.2 | 15.4 | 23.2 | 88.88 | 16.6 | N/A | 0.077555 | 102.7799
2021-08-17 | MADISON 2101 | 26.86 | 38.92 | 51.61 | 51.61 | 95.58 | 10.57 | 66.51 | 8024.6 | 8.47 | N/A | N/A | YES | YES | 0.89 | 3.6 | 5.1 | 4.7 | 30.05 | 57.99 | 69.52 | N/A | N/A |  | Assets conditions, Vegetation conditions | 639.3 | 0.00226 | 17.16 | NO | 31.7 | 52.6 | 52.6 | 89.96 | 12.2 | 19.8 | 34.8 | 91.04 | 15 | N/A | 0.40065 | 550.9318
2021-08-17 | MAXWELL 1105 | 28.21 | 36.31 | 52.53 | 52.53 | 95.75 | 8.68 | 92.06 | 17713.2 | 8.29 | N/A | N/A | YES | YES | 0.85 | 3.5 | 5.2 | 5.1 | 30 | 59.65 | 68.89 | N/A | N/A |  | Assets conditions, Vegetation conditions | 261 | 0.00176 | 14.03 | NO | 24.1 | 35.5 | 35.5 | 88.34 | 12.4 | 18.1 | 25.5 | 88.34 | 15.8 | N/A | 0.099545 | 36.6077
2021-08-17 | MC ARTHUR 1101 | 29.34 | 38.8 | 53.94 | 53.94 | 71.4 | 9.19 | 62.48 | 1979 | 19.5 | N/A | N/A | YES | YES | 0.55 | 4.6 | 7 | 6 | 40.04 | 68.49 | 63.51 | N/A | N/A |  | Assets conditions, Vegetation conditions | 20944 | 0.00329 | 17.85 | NO | 20.6 | 29 | 29 | 77.18 | 9.5 | 6.2 | 17.7 | 52.52 | 53.3 | N/A | 0.09475 | 677.05
2021-08-17 | MIDDLETOWN 1101 | 28.83 | 42.73 | 59.94 | 59.94 | 92.61 | 75.34 | 55.28 | 2686.6 | 7.06 | N/A | N/A | YES | YES | 0.91 | 3.6 | 5.1 | 4.9 | 34.28 | 63.73 | 67.64 | N/A | N/A |  | Assets conditions, Vegetation conditions | 140703.8 | 0.00413 | 27.6 | NO | 41 | 54.2 | 54.2 | 89.6 | 11.4 | 15.6 | 28.7 | 86.54 | 11.8 | N/A | 2.1797 | 2770.7167
2021-08-17 | MIDDLETOWN 1102 | 21.87 | 33.79 | 45.65 | 45.65 | 93.34 | 9.25 | 42.55 | 3373.2 | 6.87 | N/A | N/A | YES | YES | 0.8 | 3.6 | 5.6 | 5.4 | 32.27 | 60.29 | 69.39 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4340.2 | 0.00168 | 11.48 | NO | 12.9 | 22.5 | 22.5 | 90.32 | 9.4 | 12.7 | 24.8 | 78.8 | 16.9 | N/A | 1.2445 | 3307.5583
2021-08-17 | MONTICELLO 1101 | 24.25 | 38.58 | 50.84 | 50.84 | 95.32 | 17.05 | 75.54 | 9764.8 | 8.03 | N/A | N/A | YES | YES | 0.92 | 4.1 | 6.1 | 5.4 | 30.21 | 57.5 | 59.9 | N/A | N/A |  | Assets conditions, Vegetation conditions | 16907.7 | 0.00353 | 25.33 | NO | 26.3 | 38.7 | 38.7 | 88.16 | 11 | 15.2 | 28.9 | 79.88 | 16.7 | N/A | 1.6617 | 236.9444
2021-08-17 | NAPA 1112 | 20.09 | 31.39 | 48.05 | 48.05 | 88.24 | 14.46 | 77.8 | 2855.1 | 10.88 | N/A | N/A | YES | YES | 0.84 | 4.8 | 6.5 | 5.7 | 37.33 | 61.41 | 62.79 | N/A | N/A |  | Assets conditions, Vegetation conditions | 3811.4 | 0.00142 | 10.19 | NO | 16.3 | 22.6 | 22.6 | 80.78 | 20.8 | 10.3 | 16.4 | 69.44 | 23.6 | N/A | 0.074525 | 640.8151
2021-08-17 | OREGON TRAIL 1102 | 20.87 | 29.75 | 44.52 | 44.52 | 82.97 | 6.72 | 37.43 | 2180.2 | 12.29 | N/A | N/A | YES | YES | 0.58 | 3.4 | 5.6 | 5.2 | 40.82 | 73.68 | 70.26 | N/A | N/A |  | Assets conditions, Vegetation conditions | 9578.3 | 0.00279 | 15.37 | NO | 14 | 32.9 | 32.9 | 90.32 | 11.8 | 8.5 | 18.4 | 89.96 | 17.9 | N/A | 0.31074 | 1681.0083
2021-08-17 | OREGON TRAIL 1103 | 23.06 | 31.08 | 47.57 | 47.57 | 84.96 | 12.75 | 60.65 | 6203.6 | 11.17 | N/A | N/A | YES | YES | 0.76 | 3.3 | 5.4 | 5 | 31.91 | 68.22 | 67.62 | N/A | N/A |  | Assets conditions, Vegetation conditions | 14535.1 | 0.00336 | 18.95 | NO | 23.3 | 41.6 | 41.6 | 90.86 | 7.5 | 13.9 | 23.7 | 90.68 | 16.1 | N/A | 1.3588 | 2036.5667
2021-08-17 | OREGON TRAIL 1104 | 20.73 | 29.41 | 44.3 | 44.3 | 84.03 | 6.55 | 37.98 | 2370.3 | 11.58 | N/A | N/A | YES | YES | 0.61 | 3.4 | 5.6 | 5.2 | 37.42 | 76.78 | 69.41 | N/A | N/A |  | Assets conditions, Vegetation conditions | 16831.8 | 0.00336 | 18.95 | NO | 25 | 40 | 40 | 93.02 | 10 | 12 | 22 | 90.68 | 17 | N/A | 0.4087 | 1925.7861
2021-08-17 | ORO FINO 1101 | 18.94 | 30.77 | 44.09 | 44.09 | 86.57 | 44.62 | 22.12 | 826.3 | 10.18 | N/A | N/A | YES | YES | 0.75 | 4.2 | 5.6 | 4.9 | 33.4 | 68.88 | 66.86 | N/A | N/A |  | Assets conditions, Vegetation conditions | 527261.7 | 0.00408 | 23.81 | NO | 11.1 | 21 | 21 | 84.56 | 15.7 | 7.5 | 16.6 | 73.76 | 19.9 | N/A | 3.8988 | 71.0778
2021-08-17 | ORO FINO 1102 | 22.29 | 35.01 | 52.72 | 52.72 | 87.89 | 72.69 | 37.88 | 1202 | 9.77 | N/A | N/A | YES | YES | 0.76 | 4.1 | 5.5 | 4.9 | 32.37 | 73.2 | 64.52 | N/A | N/A |  | Assets conditions, Vegetation conditions | 527261.7 | 0.00617 | 43.17 | NO | 16 | 34 | 34 | 82.94 | 14 | 15 | 33 | 82.04 | 19 | N/A | 2.0313 | 47.9716
2021-08-17 | PANORAMA 1101 | 21.96 | 31.11 | 47.49 | 47.49 | 97.61 | 7.5 | 65.02 | 5274.7 | 9.93 | N/A | N/A | YES | YES | 0.74 | 3.5 | 5.6 | 5.3 | 42.43 | 83.65 | 68.84 | N/A | N/A |  | Assets conditions, Vegetation conditions | 301.6 | 0.00223 | 15.43 | NO | 18.9 | 35.1 | 35.1 | 93.38 | 7 | 13.5 | 25.5 | 91.58 | 15.8 | N/A | 1.4787 | 4389.8771
2021-08-17 | PANORAMA 1102 | 23.72 | 30.08 | 43.32 | 43.32 | 83.94 | 7.38 | 75.01 | 8693.4 | 11.65 | N/A | N/A | YES | YES | 0.67 | 3.6 | 5.6 | 5.1 | 30.18 | 80.81 | 68.66 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1797.4 | 0.00201 | 8.18 | NO | 34 | 45.6 | 45.6 | 91.58 | 8.2 | 24.1 | 35.7 | 91.58 | 15.6 | N/A | 0.042831 | 712.0448
2021-08-17 | PARADISE 1104 | 21.07 | 35.93 | 47.98 | 47.98 | 92.06 | 7.47 | 37.38 | 3035.7 | 9.4 | N/A | N/A | YES | YES | 0.9 | 4.2 | 5.5 | 4.9 | 31.06 | 72.04 | 67.51 | N/A | N/A |  | Assets conditions, Vegetation conditions | 63796 | 0.00629 | 30.27 | NO | 34 | 56 | 56 | 82.94 | 13.6 | 22.1 | 39.5 | 77.36 | 21 | N/A | 2.2766 | 1180.925
2021-08-17 | PARADISE 1105 | 19.4 | 32.87 | 45.14 | 45.14 | 87.89 | 44.62 | 27.74 | 826.3 | 9.77 | N/A | N/A | YES | YES | 0.75 | 4.1 | 5.5 | 4.9 | 32.23 | 68.88 | 66.86 | N/A | N/A |  | Assets conditions, Vegetation conditions | 316958.4 | 0.00629 | 30.27 | NO | 24.6 | 38.6 | 38.6 | 84.56 | 13.6 | 19.9 | 37 | 77.36 | 19.9 | N/A | 1.5171 | 448.9235
2021-08-17 | PARADISE 1106 | 16.01 | 27.95 | 37.6 | 37.6 | 87.07 | 22.08 | 27.74 | 764.7 | 9.91 | N/A | N/A | YES | YES | 0.64 | 4.2 | 5.6 | 4.9 | 32.66 | 74.23 | 67.48 | N/A | N/A |  | Assets conditions, Vegetation conditions | 61401.6 | 0.00145 | 6.17 | NO | 17.2 | 34.8 | 34.8 | 83.12 | 13.6 | 13.5 | 24.5 | 74.48 | 22.6 | N/A | 0.20442 | 171.3111
2021-08-17 | PHILO 1101 | 19.6 | 27.83 | 40.6 | 40.6 | 92.74 | 36.68 | 31.42 | 1030.9 | 9.23 | N/A | N/A | NO | YES | 0.73 | 4.8 | 6.7 | 6.1 | 46.2 | 66.74 | 59.87 | N/A | N/A |  | Assets conditions, Vegetation conditions | 21323.6 | 0.00043 | 2.47 | NO | 12.7 | 18.9 | 18.9 | 78.8 | 33.2 | 2.8 | 4.5 | 66.38 | 33.2 | N/A | 0.28275 | 927.4457
2021-08-17 | PIT NO 7 1101 | 21.02 | 33.87 | 49.06 | 49.06 | 77.58 | 27.83 | 17.4 | 244.1 | 16.08 | N/A | N/A | YES | YES | 0.63 | 3.8 | 6 | 5.3 | 46.78 | 79.47 | 65.57 | N/A | N/A |  | Assets conditions, Vegetation conditions | 36647 | 0.00372 | 23.3 | NO | 22.7 | 46.1 | 46.1 | 84.38 | 10.5 | 15.4 | 30.8 | 81.32 | 21.1 | N/A | 0.027476 | 1
2021-08-17 | PUEBLO 1104 | 23.59 | 35.78 | 51.44 | 51.44 | 93.03 | 15.21 | 71.78 | 3406.7 | 9.59 | N/A | N/A | YES | YES | 0.91 | 4.4 | 6.2 | 5.7 | 35.58 | 57.73 | 61.87 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4277.3 | 0.00269 | 19.77 | NO | 13.9 | 24 | 24 | 86.54 | 15 | 6 | 13 | 71.96 | 21 | N/A | 0.48039 | 358.5318
2021-08-17 | PUEBLO 1105 | 24.84 | 37.27 | 51.53 | 51.53 | 94.48 | 10.61 | 56.45 | 2766.3 | 9.46 | N/A | N/A | YES | YES | 0.89 | 4.8 | 6.8 | 6.1 | 36.46 | 58.55 | 65.64 | N/A | N/A |  | Assets conditions, Vegetation conditions | 3127.2 | 0.00307 | 23.33 | NO | 13.9 | 24 | 24 | 77.9 | 15 | 6 | 13 | 71.96 | 21 | N/A | 0.23158 | 447.875
2021-08-17 | PUEBLO 2102 | 18.22 | 28.3 | 41.22 | 41.22 | 91.6 | 26.04 | 89.08 | 1275.5 | 10.13 | N/A | N/A | YES | YES | 0.85 | 4.7 | 7.1 | 6.4 | 40.38 | 61.96 | 65.56 | N/A | N/A |  | Assets conditions, Vegetation conditions | 75579.7 | 0.00083 | 5.67 | NO | 17.3 | 25.7 | 25.7 | 77.72 | 17.6 | 10.4 | 17.8 | 67.64 | 19.2 | N/A | 0.14511 | 63.0318
2021-08-17 | PUEBLO 2103 | 19.72 | 30.18 | 46.62 | 46.62 | 91.08 | 32.94 | 42.05 | 1326.3 | 10.4 | N/A | N/A | YES | YES | 0.88 | 5 | 6.5 | 5.5 | 40.09 | 62.49 | 65.56 | N/A | N/A |  | Assets conditions, Vegetation conditions | 107640.9 | 0.00214 | 17.08 | NO | 11.4 | 25.5 | 25.5 | 77.72 | 17.6 | 10.4 | 17.8 | 67.64 | 19.2 | N/A | 0.40628 | 480.191
2021-08-17 | PUTAH CREEK 1102 | 22.28 | 35.31 | 46.14 | 46.14 | 96.65 | 6.23 | 51.05 | 2973.9 | 8.58 | N/A | N/A | YES | YES | 0.89 | 3.8 | 5.4 | 4.9 | 30.37 | 58.76 | 64.98 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4835.7 | 0.00176 | 9.76 | NO | 26.3 | 38.7 | 38.7 | 86.18 | 11 | 15.4 | 23.2 | 87.08 | 17.6 | N/A | 0.23149 | 4198.3389
2021-08-17 | PUTAH CREEK 1103 | 20.01 | 27.87 | 42.87 | 42.87 | 96.85 | 5.82 | 44.19 | 6043.8 | 8.54 | N/A | N/A | YES | YES | 0.78 | 4.1 | 6.2 | 5.9 | 30.1 | 59.04 | 69.28 | N/A | N/A |  | Assets conditions, Vegetation conditions | 289.8 | 0.00176 | 11.08 | NO | 11.8 | 24 | 24 | 88.16 | 11 | 11.3 | 18.9 | 78.8 | 20.1 | N/A | 0.094471 | 9987.6495
2021-08-17 | PUTAH CREEK 1105 | 24.87 | 34.59 | 42.08 | 42.08 | 96.13 | 6.49 | 67.41 | 6251.2 | 8.66 | N/A | N/A | YES | YES | 0.64 | 3.8 | 5.6 | 5.3 | 30.33 | 59.63 | 69.11 | N/A | N/A |  | Assets conditions, Vegetation conditions | 39.8 | 0.00092 | 5.15 | NO | 20.3 | 31.6 | 31.6 | 87.98 | 11 | 15.4 | 23.2 | 87.08 | 17.6 | N/A | 0.04034 | 782.5346
2021-08-17 | RED BLUFF 1101 | 27.55 | 33.8 | 48.29 | 48.29 | 97.35 | 7.97 | 81.42 | 12448.9 | 9.14 | N/A | N/A | YES | YES | 0.81 | 3.4 | 5.4 | 5.2 | 30.84 | 68.07 | 68.64 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2955.8 | 0.00224 | 16.89 | NO | 20.9 | 37.9 | 37.9 | 93.56 | 8.2 | 7.6 | 13.9 | 78.08 | 31.5 | N/A | 1.2839 | 5883.4597
2021-08-17 | RED BLUFF 1103 | 27.55 | 33.68 | 51.54 | 51.54 | 97.2 | 7.57 | 84.21 | 12528.2 | 9.14 | N/A | N/A | YES | YES | 0.69 | 3.4 | 5.4 | 5.2 | 31.51 | 81.1 | 69.12 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2592.8 | 0.00265 | 15.41 | NO | 17.5 | 34.8 | 34.8 | 93.2 | 12.2 | 15.3 | 27 | 92.12 | 15.7 | N/A | 0.41838 | 3172.1417
2021-08-17 | RED BLUFF 1104 | 24.24 | 34.47 | 48.11 | 48.11 | 98.3 | 8.36 | 79.83 | 8763.4 | 8.96 | N/A | N/A | YES | YES | 0.86 | 3.4 | 5.5 | 5.1 | 32.12 | 68.07 | 68.07 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2575.6 | 0.00258 | 19.23 | NO | 26 | 39.4 | 39.4 | 93.56 | 7 | 7.6 | 13.9 | 78.08 | 31.5 | N/A | 1.6147 | 3838.5139
2021-08-17 | RED BLUFF 1105 | 23.11 | 33.57 | 47.29 | 47.29 | 97.97 | 7.97 | 63.53 | 4255.8 | 8.05 | N/A | N/A | YES | YES | 0.82 | 3.3 | 5.2 | 5 | 32.34 | 80.47 | 68.29 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1126.1 | 0.00316 | 17.66 | NO | 26 | 39.4 | 39.4 | 93.56 | 7.7 | 7.6 | 13.9 | 78.08 | 31.5 | N/A | 1.8279 | 3301.9583
2021-08-17 | REDBUD 1101 | 27.33 | 42.23 | 57.47 | 57.47 | 90.91 | 15.81 | 72.63 | 7447.4 | 7.36 | N/A | N/A | YES | YES | 0.91 | 3.5 | 5.3 | 5 | 30.65 | 57.86 | 68.32 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2121.2 | 0.00221 | 17.71 | NO | 26.7 | 46 | 46 | 88.34 | 9.3 | 22.8 | 39.5 | 84.38 | 14.1 | N/A | 1.0133 | 1734.3722
2021-08-17 | REDBUD 1102 | 21.88 | 36.74 | 45.31 | 45.31 | 89.78 | 13.25 | 65.62 | 6418.5 | 7.64 | N/A | N/A | YES | YES | 0.9 | 3.8 | 6.1 | 5.5 | 34.06 | 61.5 | 66.79 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2285.8 | 0.00149 | 11.21 | NO | 12.4 | 24.5 | 24.5 | 88.52 | 14.7 | 13.5 | 19.8 | 78.44 | 17 | N/A | 0.12923 | 1208.4207
2021-08-17 | RINCON 1101 | 18.45 | 30.01 | 42.89 | 42.89 | 90.65 | 4.06 | 18.14 | 160.9 | 12.38 | N/A | N/A | YES | YES | 0.86 | 4.8 | 7.6 | 7 | 41.53 | 59.54 | 69.13 | N/A | N/A |  | Assets conditions, Vegetation conditions | 25519.6 | 0.0014 | 9.4 | NO | 17.3 | 25.7 | 25.7 | 78.26 | 17.6 | 5.1 | 16.2 | 69.8 | 22.2 | N/A | 0.062173 | 648.6503
2021-08-17 | RINCON 1103 | 19.94 | 31.45 | 42.89 | 42.89 | 89.62 | 7.27 | 25.7 | 711.5 | 11.1 | N/A | N/A | YES | YES | 0.85 | 4.6 | 7 | 6.4 | 42.68 | 58.9 | 68.06 | N/A | N/A |  | Assets conditions, Vegetation conditions | 99846.7 | 0.00142 | 9.4 | NO | 17.3 | 25.7 | 25.7 | 79.88 | 22.9 | 4.8 | 7.2 | 68.18 | 46.7 | N/A | 0.52098 | 534.2
2021-08-17 | SILVERADO 2102 | 25.02 | 36.39 | 53.82 | 53.82 | 94.81 | 42.35 | 47.07 | 1557.4 | 7.99 | N/A | N/A | YES | YES | 0.92 | 4.5 | 7.3 | 7.1 | 33.03 | 57.59 | 62.79 | N/A | N/A |  | Assets conditions, Vegetation conditions | 6713.5 | 0.00318 | 24.26 | NO | 13.2 | 21 | 21 | 86.18 | 12.9 | 6.7 | 13 | 78.26 | 16.7 | N/A | 0.34628 | 212.8392
2021-08-17 | SILVERADO 2103 | 21.13 | 29.98 | 35.58 | 35.58 | 87.12 | 16.45 | 41.66 | 846.3 | 11.7 | N/A | N/A | YES | YES | 0.8 | 4.7 | 6.5 | 5.9 | 41.58 | 61.06 | 66.36 | N/A | N/A |  | Assets conditions, Vegetation conditions | 3255.9 | 0.00057 | 3.18 | NO | 17.3 | 25.7 | 25.7 | 77.72 | 17.6 | 5.1 | 16.2 | 69.8 | 22.2 | N/A | 0.03041 | 59.9355
2021-08-17 | SILVERADO 2104 | 23.74 | 36.54 | 55.8 | 55.8 | 95.39 | 76.43 | 65.91 | 2703.6 | 7.43 | N/A | N/A | YES | YES | 0.92 | 3.9 | 5.8 | 5.7 | 32.12 | 57.3 | 63 | N/A | N/A |  | Assets conditions, Vegetation conditions | 100456.3 | 0.00535 | 34.97 | NO | 17.3 | 27.2 | 27.2 | 89.06 | 12.1 | 13.1 | 20.9 | 79.88 | 18.5 | N/A | 3.2297 | 411.2361
2021-08-17 | SONOMA 1103 | 24.78 | 35.99 | 51.58 | 51.58 | 90.13 | 8.69 | 32.06 | 883.1 | 11.3 | N/A | N/A | YES | YES | 0.88 | 5.1 | 7.7 | 7 | 39.82 | 62.94 | 68.02 | N/A | N/A |  | Assets conditions, Vegetation conditions | 9832.1 | 0.00221 | 17.08 | NO | 9.5 | 18 | 18 | 77.36 | 17.9 | 10.4 | 17.8 | 67.64 | 21.6 | N/A | 0.090407 | 690.192
2021-08-17 | SONOMA 1104 | 20.01 | 29.58 | 41.35 | 41.35 | 91.74 | 6.69 | 31.81 | 1828.6 | 10.81 | N/A | N/A | YES | YES | 0.78 | 4.9 | 6.2 | 5.4 | 39.37 | 64.15 | 66.63 | N/A | N/A |  | Assets conditions, Vegetation conditions | 10511.2 | 0.00097 | 4.66 | NO | 14 | 21.3 | 21.3 | 77.18 | 17.9 | 11 | 17.8 | 67.64 | 21.6 | N/A | 0.34098 | 1938.4278
2021-08-17 | STILLWATER 1101 | 21.52 | 31.79 | 50.18 | 50.18 | 82.56 | 12.28 | 36.34 | 1744.1 | 12.57 | N/A | N/A | YES | YES | 0.74 | 3.4 | 5.6 | 5.1 | 37.87 | 72.16 | 66.26 | N/A | N/A |  | Assets conditions, Vegetation conditions | 36401.9 | 0.00323 | 22.18 | NO | 27.6 | 41.4 | 41.4 | 90.32 | 11.8 | 17.5 | 27.6 | 89.96 | 17.9 | N/A | 0.85837 | 697.5028
2021-08-17 | STILLWATER 1102 | 21.02 | 29.88 | 44.89 | 44.89 | 84.66 | 9.85 | 44.39 | 3239.1 | 11.66 | N/A | N/A | YES | YES | 0.78 | 3.3 | 5.4 | 5 | 36.16 | 66.01 | 67.61 | N/A | N/A |  | Assets conditions, Vegetation conditions | 26610.9 | 0.00317 | 19.77 | NO | 27.6 | 41.4 | 41.4 | 91.4 | 10 | 17.5 | 27.6 | 90.68 | 17 | N/A | 1.6586 | 1480.5361
2021-08-17 | TYLER 1105 | 27.71 | 34.39 | 52.2 | 52.2 | 96.96 | 8.13 | 94.89 | 12744.5 | 9.61 | N/A | N/A | YES | YES | 0.8 | 3.3 | 5.2 | 5.1 | 30.13 | 68.31 | 68.71 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2404.3 | 0.00265 | 17.15 | NO | 23.4 | 40 | 40 | 93.2 | 12.2 | 17 | 30.3 | 92.12 | 15.7 | N/A | 1.2343 | 2992.2964
2021-08-17 | VACA DIXON 1105 | 23.44 | 28.43 | 45.02 | 45.02 | 96.85 | 6 | 43.55 | 4530.5 | 8.54 | N/A | N/A | YES | YES | 0.8 | 4 | 5.9 | 5.3 | 30.1 | 58.99 | 68.23 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4563.2 | 0.00231 | 11.79 | NO | 26.3 | 38.7 | 38.7 | 88.16 | 11 | 14.5 | 22.5 | 78.8 | 20.1 | N/A | 0.67468 | 9382.1833
2021-08-17 | VACAVILLE 1104 | 22.6 | 34.57 | 46.91 | 46.91 | 94.72 | 5.07 | 28.24 | 503.9 | 10.43 | N/A | N/A | YES | YES | 0.85 | 4.4 | 6.4 | 5.7 | 33.32 | 60.37 | 64.26 | N/A | N/A |  | Assets conditions, Vegetation conditions | 7433.8 | 0.0013 | 10.31 | NO | 26.3 | 38.7 | 38.7 | 77 | 14 | 15.2 | 26.2 | 67.64 | 24 | N/A | 0.067405 | 2578.775
2021-08-17 | VACAVILLE 1108 | 23.51 | 36.48 | 48.71 | 48.71 | 96.33 | 6 | 34.75 | 1566.8 | 8.26 | N/A | N/A | YES | YES | 0.87 | 3.9 | 5.6 | 5 | 31.13 | 58 | 65.41 | N/A | N/A |  | Assets conditions, Vegetation conditions | 7433.8 | 0.00137 | 9.6 | NO | 26.3 | 38.7 | 38.7 | 88.16 | 11 | 14.5 | 21.2 | 78.8 | 20.1 | N/A | 0.54568 | 470.2985
2021-08-17 | VOLTA 1101 | 24.6 | 37.92 | 55.6 | 55.6 | 84.9 | 57.54 | 50.06 | 5525.9 | 11.25 | N/A | N/A | YES | YES | 0.78 | 3.6 | 5.5 | 4.8 | 30.88 | 59.88 | 65.27 | N/A | N/A |  | Assets conditions, Vegetation conditions | 96081.9 | 0.00424 | 26.35 | NO | 34 | 47.7 | 47.7 | 91.76 | 7.4 | 23.6 | 34.1 | 75.56 | 28.9 | N/A | 1.5028 | 140.2383
2021-08-17 | VOLTA 1102 | 23.65 | 39.12 | 55.54 | 55.54 | 80.88 | 38.17 | 122.53 | 1923.7 | 12.47 | N/A | N/A | YES | YES | 0.74 | 3.8 | 5.7 | 4.9 | 35.13 | 65.59 | 64.71 | N/A | N/A |  | Assets conditions, Vegetation conditions | 156058.2 | 0.01268 | 48.6 | NO | 31.6 | 47.7 | 47.7 | 89.96 | 7.4 | 14.5 | 26.6 | 75.56 | 28.9 | N/A | 2.9839 | 65.5068
2021-08-17 | WHITMORE 1101 | 26.47 | 43.26 | 61.73 | 61.73 | 79.98 | 82.98 | 51.1 | 1896.2 | 13.32 | N/A | N/A | YES | YES | 0.63 | 3.6 | 5.6 | 4.9 | 43.98 | 82.33 | 66.9 | N/A | N/A |  | Assets conditions, Vegetation conditions | 125249.6 | 0.00912 | 53.96 | NO | 23 | 45.4 | 45.4 | 85.28 | 8.9 | 22.7 | 38.8 | 70.52 | 27.8 | N/A | 0.34496 | 28.029
2021-08-17 | WILDWOOD 1101 | 14.34 | 20.53 | 33.27 | 33.27 | 90.38 | 9.9 | 35.49 | 2383.5 | 12.11 | N/A | N/A | YES | YES | 0.91 | 3.5 | 5.3 | 4.9 | 30.33 | 63.11 | 68.56 | N/A | N/A |  | Assets conditions, Vegetation conditions | 942.1 | 0.00028 | 2.54 | NO | 21.6 | 36.2 | 36.2 | 86.54 | 17.3 | 4.8 | 9.4 | 70.16 | 25.5 | N/A | 0.036142 | 189.1864
2021-09-20 | ARBUCKLE 1101 | 18.5 | 28.97 | 38.6 | 38.6 | 89.9 | 8.586 | 38.276 | 3503 | 10.1 | N/A | N/A | YES | YES | 0.75 | 6 | 11.8 | 7.53 | 31.5 | 59.486 | 60.6082 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.00084 | 4.85 | NO | 25.3 | 35.9 | 35.9 | 84.2 | 17.8 | 18.3 | 27.6 | 85.28 | 17.1 | N/A | 0.078327 | 20.925
2021-09-20 | ARBUCKLE 1104 | 19.2 | 29.91 | 39.7 | 39.7 | 89.835 | 8.462 | 43.744 | 4217.1 | 10.2 | N/A | N/A | YES | YES | 0.801 | 6 | 11.9 | 7.22 | 31 | 59.042 | 61.0327 | N/A | N/A |  | Assets conditions, Vegetation conditions | 477.9 | 0.00077 | 5.56 | NO | 25.3 | 35.9 | 35.9 | 84.2 | 17.8 | 18.3 | 27.6 | 85.28 | 17.1 | N/A | 0.086112 | 24.375
2021-09-20 | CORNING 1101 | 20.7 | 27.52 | 40.3 | 40.3 | 89.052 | 6.529 | 56.171 | 8209 | 10.2 | N/A | N/A | YES | YES | 0.768 | 6 | 8.9 | 6.63 | 30 | 63.599 | 61.161 | N/A | N/A |  | Assets conditions, Vegetation conditions | 6259.9 | 0.00062 | 3.77 | NO | 24.9 | 36.2 | 36.2 | 86.9 | 14.3 | 22.1 | 30.2 | 87.26 | 14.2 | N/A | 1.2222 | 110.2028
2021-09-20 | CORNING 1102 | 23.4 | 30.53 | 43.6 | 43.6 | 88.754 | 10.463 | 70.139 | 11495 | 8.91 | N/A | N/A | YES | YES | 0.868 | 6 | 8.1 | 6.12 | 30 | 58.538 | 57.1164 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1979 | 0.00087 | 6.47 | NO | 25.3 | 36.2 | 36.2 | 87.08 | 11 | 21.3 | 32 | 87.08 | 11 | N/A | 0.47259 | 305.675
2021-09-20 | CORTINA 1101 | 18.1 | 28.16 | 38.2 | 38.2 | 86.503 | 11.753 | 59.899 | 5450.3 | 10.2 | N/A | N/A | YES | YES | 0.803 | 6 | 10.5 | 6.87 | 30.3 | 59.606 | 61.2125 | N/A | N/A |  | Assets conditions, Vegetation conditions | 18.4 | 0.00049 | 2.92 | NO | 25.2 | 33.9 | 33.9 | 86.72 | 12.7 | 20 | 28.3 | 87.26 | 12.7 | N/A | 0.082219 | 8.6
2021-09-20 | GLENN 1101 | 21.7 | 30.52 | 40.2 | 40.2 | 88.658 | 6.769 | 61.888 | 7436.2 | 9.45 | N/A | N/A | YES | YES | 0.753 | 6 | 8.4 | 6.33 | 30 | 59.462 | 56.7981 | N/A | N/A |  | Assets conditions, Vegetation conditions | 14.6 | 0.00051 | 2.85 | NO | 25.3 | 35 | 35 | 87.08 | 11 | 19.4 | 32 | 87.08 | 11 | N/A | 0.082806 | 317.9957
2021-09-20 | HIGHLANDS 1103 | 27.4 | 41.05 | 60.8 | 60.8 | 86.768 | 11.592 | 54.928 | 4843 | 8.9 | N/A | N/A | YES | YES | 0.878 | 7 | 9.6 | 6.69 | 31.6 | 57.329 | 61.9886 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1149.6 | 0.00332 | 24.9 | NO | 28.8 | 43.9 | 43.9 | 89.78 | 8 | 19.9 | 28.5 | 89.96 | 8 | N/A | 0.11569 | 289.7253
2021-09-20 | MADISON 2101 | 23.3 | 36.48 | 45.5 | 45.5 | 90.317 | 7.543 | 55.823 | 6668.7 | 10.2 | N/A | N/A | YES | YES | 0.789 | 6 | 10.9 | 6.93 | 30.1 | 58.357 | 61.7429 | N/A | N/A |  | Assets conditions, Vegetation conditions | 86.4 | 0.00144 | 9.51 | NO | 28.7 | 47.2 | 47.2 | 87.98 | 14.6 | 17 | 27.7 | 89.96 | 13 | N/A | 0.083776 | 77.8401
2021-09-20 | MAXWELL 1105 | 20.5 | 29.21 | 37.5 | 37.5 | 90.713 | 7.907 | 61.092 | 8669.1 | 9.18 | N/A | N/A | YES | YES | 0.785 | 6 | 9.1 | 7.09 | 30 | 58.573 | 60.8091 | N/A | N/A |  | Assets conditions, Vegetation conditions | 261 | 0.00048 | 3.11 | NO | 23.7 | 34.1 | 34.1 | 90.32 | 10.5 | 16.7 | 23.2 | 90.68 | 10.9 | N/A | 0.11024 | 14.825
2021-09-20 | MONTICELLO 1101 | 23.8 | 37.56 | 49.4 | 49.4 | 87.756 | 8.826 | 51.399 | 3427.3 | 10.5 | N/A | N/A | YES | YES | 0.785 | 7 | 10.7 | 7.27 | 30.2 | 57.284 | 61.7906 | N/A | N/A |  | Assets conditions, Vegetation conditions | 264.8 | 0.0017 | 12.3 | NO | 25.7 | 41.9 | 41.9 | 86.18 | 14.7 | 16.8 | 28.1 | 86.72 | 14.2 | N/A | 0.46134 | 23.85
2021-09-20 | PUTAH CREEK 1105 | 23.4 | 33.6 | 39.4 | 39.4 | 88.769 | 6.224 | 53.586 | 4870.3 | 11.2 | N/A | N/A | YES | YES | 0.59 | 7 | 11.9 | 6.88 | 30.2 | 58.603 | 62.6145 | N/A | N/A |  | Assets conditions, Vegetation conditions | 39.8 | 0.00069 | 3.66 | NO | 25 | 32.5 | 32.5 | 84.92 | 16.2 | 18.7 | 26 | 84.92 | 16 | N/A | 0.082998 | 221.1361
2021-09-20 | SCE TEHACHAPI 1101 | 23.8 | 34.64 | 51.9 | 51.9 | 95.453 | 7.799 | 69.941 | 6683.8 | 6.49 | N/A | N/A | NO | NO | 0.844 | 5 | 8.9 | 6.63 | 30.6 | 62.482 | 65.2674 | N/A | N/A |  | Assets conditions, Vegetation conditions | 53.8 | 0.00316 | 24.1 | NO | 16.4 | 33.2 | 33.2 | 78.26 | 13.1 | 16.4 | 33.2 | 78.98 | 13.2 | N/A | 0.080957 | 2.175
2021-09-20 | TEJON 1102 | 34 | 42.07 | 58.2 | 58.2 | 96.285 | 11.011 | 101.804 | 22114 | 7.09 | N/A | N/A | NO | NO | 0.879 | 4 | 8 | 6.1 | 30 | 57.65 | 60.8947 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2474.7 | 0.00202 | 16.1 | NO | 32.6 | 44.2 | 44.2 | 96.8 | 2 | 22.7 | 32.4 | 96.8 | 3 | N/A | 1.0657 | 899.65
2021-09-20 | TYLER 1105 | 19.6 | 23.07 | 35.3 | 35.3 | 89.349 | 6.224 | 49.808 | 5707.2 | 10.2 | N/A | N/A | YES | YES | 0.657 | 6 | 8.7 | 6.54 | 30.1 | 65.17 | 57.4567 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1480.6 | 0.00044 | 2.5 | NO | 18.6 | 31.7 | 31.7 | 88.34 | 14.5 | 15.7 | 27.3 | 88.7 | 14.5 | N/A | 0.39899 | 96.441
2021-09-20 | VACAVILLE 1104 | 20.5 | 32.32 | 42.4 | 42.4 | 86.239 | 4.351 | 27.588 | 559.12 | 12.3 | N/A | N/A | YES | YES | 0.718 | 7 | 12.5 | 8.05 | 33.1 | 59.402 | 60.8278 | N/A | N/A |  | Assets conditions, Vegetation conditions | 7433.8 | 0.00105 | 5.88 | NO | 25 | 41.9 | 41.9 | 84.92 | 16.2 | 11.5 | 21.4 | 86 | 16 | N/A | 0.11647 | 26.025
2021-09-20 | VACAVILLE 1108 | 24.5 | 36.29 | 50.8 | 50.8 | 86.298 | 3.698 | 21.773 | 592.79 | 12.2 | N/A | N/A | YES | YES | 0.712 | 7 | 10.6 | 6.98 | 32.8 | 57.508 | 60.8328 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2154.1 | 0.00129 | 7.73 | NO | 25 | 41.9 | 41.9 | 83.3 | 16.2 | 15.5 | 24.3 | 84.02 | 16 | N/A | 0.11102 | 17.5
2021-10-11 | (Tx) BUCKS CREEK-ROCK CREEK-CRESTA | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [1] Transmission circuits for this event were only de-energized when all distribution circuits in the downstream substations were de-energized, otherwise those transmission circuits would have remained energized. Because these transmission circuit de-energizations were not directly PSPS related and there were no customer impacts related to the de-energization of the transmission assets, this appendix does not report on them.
2021-10-11 | (Tx) ELK CREEK TAP | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [1] Transmission circuits for this event were only de-energized when all distribution circuits in the downstream substations were de-energized, otherwise those transmission circuits would have remained energized. Because these transmission circuit de-energizations were not directly PSPS related and there were no customer impacts related to the de-energization of the transmission assets, this appendix does not report on them.
2021-10-11 | (Tx) SILVERADO-FULTON JCT | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | [1] Transmission circuits for this event were only de-energized when all distribution circuits in the downstream substations were de-energized, otherwise those transmission circuits would have remained energized. Because these transmission circuit de-energizations were not directly PSPS related and there were no customer impacts related to the de-energization of the transmission assets, this appendix does not report on them.
2021-10-11 | ANDERSON 1103 | 23 | 27 | 43 | 43 | 67 | 6.5 | 50 | 5643 | 12.6 | N/A | N/A | Yes | Yes | 0.62 | 6.9 | 9.3 | 8.4 | 30.9 | 64.7 | 72.8 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1095 | 0.0019 | 11.6 | No | 21 | 35 |  | 66.92 | 13 | 16.2 | 26 | 64.04 | 15.9 | N/A | 0.11896 | 178.0778
2021-10-11 | ANTELOPE 1101 | 26 | 34 | 41 | 41 | 71 | 6.4 | 73 | 9317 | 11.8 | N/A | N/A | Yes | Yes | 0.51 | 6.4 | 9.4 | 8.6 | 30 | 58.9 | 60.4 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0009 | 4.6 | No | 28 | 40.6 |  | 69.98 | 10 | 9.8 | 17.1 | 59.9 | 17 | N/A | 0.040231 | 2.2
2021-10-11 | ARBUCKLE 1101 | 25 | 38 | 53 | 53 | 68 | 9.3 | 49 | 6039 | 13.3 | N/A | N/A | Yes | Yes | 0.72 | 6.4 | 9.1 | 8 | 32.1 | 59.9 | 60 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0048 | 24.6 | No | 28 | 43.2 |  | 65.66 | 14.7 | 19.1 | 30.7 | 61.16 | 21.6 | N/A | 0.032698 | 31.45
2021-10-11 | ARBUCKLE 1104 | 25 | 37 | 52 | 52 | 68 | 9.2 | 56 | 6466 | 13.1 | N/A | N/A | Yes | Yes | 0.78 | 6.4 | 9.1 | 8.1 | 32 | 59.6 | 59.4 | N/A | N/A |  | Assets conditions, Vegetation conditions | 478 | 0.0035 | 25.9 | No | 28 | 43.2 |  | 65.66 | 14.7 | 19.1 | 30.7 | 61.16 | 21.6 | N/A | 0.04447 | 36.5346
2021-10-11 | AVENAL 2101 | 32 | 42 | 51 | 51 | 69 | 6.8 | 83 | 11701 | 12.6 | N/A | N/A | Yes | Yes | 0.63 | 6.6 | 9.3 | 7.9 | 30 | 59.8 | 61.4 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0013 | 7.4 | No | 43 | 61 |  | 66.92 | 15 | 9.4 | 17.6 | 46.76 | 27.2 | N/A | 0.035321 | 64.5994
2021-10-11 | BIG BEND 1101 | 27 | 44 | 62 | 62 | 66 | 19.6 | 54 | 3111 | 10 | N/A | N/A | Yes | Yes | 0.79 | 6.8 | 8.9 | 7.6 | 33.3 | 62 | 66.6 | N/A | N/A |  | Assets conditions, Vegetation conditions | 88659 | 0.0071 | 48 | No | 34 | 55 |  | 67.28 | 11.9 | 16 | 30 | 49.82 | 26.8 | N/A | 0.47873 | 28.1948
2021-10-11 | BRENTWOOD 2105 | 26 | 34 | 51 | 51 | 71 | 7.3 | 99 | 16942 | 13.3 | N/A | N/A | Yes | Yes | 0.65 | 6.6 | 10.8 | 10.1 | 30 | 59.3 | 61.3 | N/A | N/A |  | Assets conditions, Vegetation conditions | 438 | 0.0042 | 21.8 | No | 41 | 56 |  | 65.84 | 15.9 | 23 | 35 | 62.6 | 19.5 | N/A | 0.14826 | 801.1253
2021-10-11 | BUCKS CREEK 1103 | 27 | 42 | 65 | 65 | 51 | 47.4 | 31 | 262 | 14.8 | N/A | N/A | Yes | No | 0.58 | 8.6 | 10.9 | 8 | 41 | 68.9 | 71.6 | N/A | N/A |  | Assets conditions, Vegetation conditions | 76183 | 0.0056 | 23.5 | No | 13.1 | 34.7 |  | 58.1 | 15 | 7.4 | 18.7 | 45.32 | 30.6 | N/A | 0.5464 | 1.05
2021-10-11 | CALISTOGA 1101 | 36 | 47 | 67 | 67 | 68 | 69.3 | 78 | 2773 | 10.2 | N/A | N/A | Yes | Yes | 0.74 | 7 | 10.2 | 8.7 | 36.8 | 61.7 | 62.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | 62182 | 0.0073 | 45 | No | 44.3 | 64.8 |  | 69.62 | 9.6 | 21.1 | 31.7 | 66.02 | 12.4 | N/A | 0.1712 | 76.7194
2021-10-11 | CALPINE 1144 | 27 | 40 | 56 | 56 | 63 | 41.8 | 88 | 2362 | 11.3 | N/A | N/A | Yes | Yes | 0.77 | 7.3 | 9.6 | 8.2 | 37 | 62.2 | 61.3 | N/A | N/A |  | Assets conditions, Vegetation conditions | 3737 | 0.0056 | 39 | No | 32.5 | 45.6 |  | 64.58 | 12.1 | 18.1 | 27.2 | 61.16 | 13.5 | N/A | 0.053051 | 6
2021-10-11 | CALPINE 1146 | 21 | 33 | 50 | 50 | 58 | 41.8 | 45 | 1351 | 12.5 | N/A | N/A | Yes | Yes | 0.7 | 8 | 11.6 | 9.2 | 41.7 | 64.9 | 65.6 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4508 | 0.0044 | 29.4 | No | 32.5 | 44.4 |  | 61.16 | 13.8 | 13.2 | 24.9 | 59.36 | 13.5 | N/A | 0.028773 | 6.5
2021-10-11 | CAMBRIA 1102 | 31 | 46 | 62 | 62 | 73 | 14.3 | 64 | 2543 | 11.8 | N/A | N/A | No | Yes | 0.67 | 6.8 | 11.1 | 9.2 | 52.1 | 62.8 | 65.9 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1535 | 0.0035 | 23.5 | No | 19.1 | 37 |  | 66.74 | 15.6 | 9.6 | 21 | 60.44 | 19.8 | N/A | 0.074092 | 15.95
2021-10-11 | CANTUA 1103 | 31 | 39 | 53 | 53 | 67 | 13.2 | 104 | 20859 | 12.8 | N/A | N/A | Yes | Yes | 0.74 | 6.6 | 9.4 | 8.5 | 30 | 55.5 | 60.7 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0019 | 12.5 | No | 36.6 | 56.9 |  | 61.88 | 14.9 | 21.5 | 34.2 | 53.42 | 24.2 | N/A | 0.032047 | 7.575
2021-10-11 | CARBONA 1101 | 26 | 32 | 43 | 43 | 66 | 6.9 | 55 | 4618 | 15.4 | N/A | N/A | Yes | Yes | 0.6 | 7 | 10.4 | 9.4 | 30 | 59.9 | 62.8 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0014 | 7.1 | No | 38.2 | 50.6 |  | 68 | 22.4 | 20.4 | 27.8 | 49.1 | 28.5 | N/A | 0.032047 | 90.875
2021-10-11 | CHOLAME 2102 | 26 | 38 | 50 | 50 | 73 | 12.1 | 78 | 9101 | 10.3 | N/A | N/A | Yes | Yes | 0.74 | 6.4 | 9.7 | 8.2 | 30 | 57.6 | 58.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | 630 | 0.0034 | 24.8 | No | 28.3 | 43.3 |  | 66.92 | 14 | 11.5 | 20.5 | 52.52 | 24.6 | N/A | 0.082788 | 115.1938
2021-10-11 | CLARK ROAD 1102 | 31 | 40 | 58 | 58 | 70 | 10.4 | 54 | 5177 | 10 | N/A | N/A | Yes | Yes | 0.79 | 6.6 | 8.8 | 7.6 | 32.4 | 61.2 | 64 | N/A | N/A |  | Assets conditions, Vegetation conditions | 29387 | 0.0062 | 48 | No | 34 | 55 |  | 68.72 | 11.2 | 16 | 30 | 51.26 | 24.8 | N/A | 0.85257 | 139.1944
2021-10-11 | CLAYTON 2212 | 26 | 38 | 53 | 53 | 69 | 12.9 | 97 | 16915 | 13.5 | N/A | N/A | Yes | Yes | 0.75 | 6.7 | 10.4 | 9.2 | 30 | 59.6 | 58.7 | N/A | N/A |  | Assets conditions, Vegetation conditions | 13400 | 0.0047 | 33.6 | No | 35.7 | 55.2 |  | 65.84 | 14.7 | 21.2 | 29.4 | 62.6 | 19.5 | N/A | 0.76206 | 226.9225
2021-10-11 | CLOVERDALE 1102 | 21 | 31 | 43 | 43 | 70 | 8.5 | 32 | 893 | 9.1 | N/A | N/A | Yes | Yes | 0.66 | 7.2 | 11.4 | 9.9 | 45 | 61.6 | 65.7 | N/A | N/A |  | Assets conditions, Vegetation conditions | 5638 | 0.0019 | 10.4 | No | 19 | 31.4 |  | 67.46 | 17.8 | 10.9 | 15.2 | 47.12 | 32.1 | N/A | 0.090278 | 42.2873
2021-10-11 | COALINGA NO 1 1108 | 28 | 35 | 49 | 49 | 72 | 12.1 | 87 | 7780 | 10.2 | N/A | N/A | Yes | Yes | 0.77 | 6.1 | 8.7 | 7.5 | 30 | 53.5 | 57.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0027 | 19.6 | No | 20 | 46 |  | 59 | 16 | 8.1 | 23 | 53.06 | 20 | N/A | 0.15481 | 95.1278
2021-10-11 | COALINGA NO 1 1109 | 28 | 36 | 45 | 45 | 72 | 7.5 | 86 | 11153 | 10.8 | N/A | N/A | Yes | Yes | 0.62 | 6.2 | 8.6 | 7.6 | 30 | 59.5 | 61.9 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0022 | 8.2 | No | 36.6 | 56.9 |  | 59 | 16 | 21.5 | 34.2 | 53.06 | 20 | N/A | 0.038594 | 106.7944
2021-10-11 | COALINGA NO 2 1105 | 38 | 50 | 71 | 71 | 70 | 15.9 | 108 | 15447 | 10.9 | N/A | N/A | Yes | Yes | 0.79 | 6 | 8.3 | 7.4 | 30 | 50.5 | 59.9 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0044 | 30 | No | 36.6 | 57 |  | 61.88 | 14.9 | 21.5 | 34.2 | 53.42 | 20 | N/A | 0.17936 | 28.05
2021-10-11 | CORNING 1101 | 27 | 35 | 53 | 53 | 67 | 7.4 | 79 | 9227 | 13.8 | N/A | N/A | Yes | Yes | 0.73 | 6.6 | 9.2 | 8.3 | 30 | 59.1 | 65 | N/A | N/A |  | Assets conditions, Vegetation conditions | 6260 | 0.0048 | 32.2 | No | 28.3 | 40.4 |  | 65.84 | 11.8 | 18.9 | 25.9 | 60.98 | 15 | N/A | 1.1429 | 216.6861
2021-10-11 | CORNING 1102 | 29 | 35 | 57 | 57 | 66 | 40.1 | 80 | 11288 | 12.5 | N/A | N/A | Yes | Yes | 0.8 | 5.9 | 8.5 | 7.2 | 30 | 50 | 58.9 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1979 | 0.0039 | 25 | No | 26 | 41 |  | 64.58 | 12.1 | 14.3 | 25.1 | 60.26 | 15 | N/A | 0.41607 | 744.092
2021-10-11 | CORTINA 1101 | 26 | 38 | 56 | 56 | 63 | 14.3 | 94 | 9928 | 15.1 | N/A | N/A | Yes | Yes | 0.82 | 6.7 | 9.1 | 7.8 | 30.8 | 60.3 | 60.3 | N/A | N/A |  | Assets conditions, Vegetation conditions | 18 | 0.0027 | 21 | No | 30.3 | 47 |  | 66.56 | 11.7 | 20.1 | 28.2 | 62.96 | 16.2 | N/A | 0.039238 | 11.1
2021-10-11 | COTTONWOOD 1103 | 21 | 28 | 44 | 44 | 67 | 6.7 | 47 | 4407 | 13 | N/A | N/A | Yes | Yes | 0.7 | 7 | 9.4 | 8.4 | 36 | 62.3 | 73.8 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2576 | 0.0029 | 16.6 | No | 22 | 35.9 |  | 65.66 | 11.2 | 14.1 | 21.3 | 61.16 | 15.7 | N/A | 0.93467 | 477.741
2021-10-11 | CRESTA 1101 | 22 | 38 | 52 | 52 | 59 | 7.1 | 40 | 1448 | 11.9 | N/A | N/A | Yes | No | 0.68 | 7.4 | 9.1 | 7.8 | 46.8 | 64.5 | 71.3 | N/A | N/A |  | Assets conditions, Vegetation conditions | 3925 | 0.0034 | 19.5 | No | 34 | 55 |  | 58.82 | 15 | 16 | 30 | 44.78 | 30.9 | N/A | 0.030465 | 0.75
2021-10-11 | DESCHUTES 1101 | 21 | 25 | 40 | 40 | 67 | 6.8 | 53 | 6033 | 12.6 | N/A | N/A | Yes | Yes | 0.61 | 7 | 9.1 | 8 | 30.3 | 65 | 72.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | 7738 | 0.0018 | 10.5 | No | 20.4 | 34.7 |  | 64.4 | 15.4 | 16.2 | 26 | 63.68 | 15.9 | N/A | 0.12692 | 154.4994
2021-10-11 | DESCHUTES 1104 | 23 | 27 | 41 | 41 | 67 | 6.6 | 52 | 6038 | 12.7 | N/A | N/A | Yes | Yes | 0.61 | 6.9 | 9.3 | 8.4 | 30.9 | 64.7 | 72.5 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4504 | 0.0016 | 9.8 | No | 21 | 35 |  | 66.92 | 13 | 16.2 | 26 | 64.04 | 15.9 | N/A | 0.14549 | 237.9948
2021-10-11 | DEVILS DEN 1101 | 21 | 31 | 34 | 34 | 71 | 7.7 | 67 | 9521 | 11.9 | N/A | N/A | Yes | Yes | 0.49 | 6.4 | 9.1 | 7.9 | 30 | 61.3 | 61 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0009 | 3.6 | No | 43 | 61 |  | 66.92 | 14.3 | 9.8 | 17.1 | 56.48 | 22.3 | N/A | 0.038594 | 4.775
2021-10-11 | ELK CREEK 1101 | 30 | 39 | 59 | 59 | 66 | 19.8 | 122 | 22616 | 13.1 | N/A | N/A | Yes | Yes | 0.83 | 5.9 | 8.8 | 7.5 | 30 | 55.1 | 56.6 | N/A | N/A |  | Assets conditions, Vegetation conditions | 13263 | 0.0039 | 30.3 | Yes | 30.1 | 44.8 |  | 65.84 | 11.8 | 21 | 30.8 | 64.94 | 8 | N/A | 1.1747 | 196.2373
2021-10-11 | GEYSERVILLE 1102 | 25 | 38 | 50 | 50 | 66 | 12.7 | 67 | 1126 | 9.9 | N/A | N/A | Yes | Yes | 0.73 | 7 | 10.3 | 9.4 | 39.9 | 63.6 | 61.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4996 | 0.0065 | 43.3 | No | 32.5 | 44.4 |  | 69.62 | 12.4 | 26.3 | 35.3 | 49.82 | 26.1 | N/A | 0.074092 | 67.8068
2021-10-11 | GIRVAN 1101 | 24 | 32 | 52 | 52 | 66 | 11.1 | 45 | 4098 | 12.3 | N/A | N/A | Yes | Yes | 0.75 | 7 | 9.6 | 7.8 | 30.1 | 58.1 | 61.8 | N/A | N/A |  | Assets conditions, Vegetation conditions | 23868 | 0.0046 | 28.6 | No | 21 | 37.5 |  | 66.92 | 12.9 | 19 | 32 | 66.02 | 12.9 | N/A | 1.4281 | 176.3336
2021-10-11 | GLENN 1101 | 24 | 30 | 46 | 46 | 66 | 6.6 | 67 | 7454 | 12.9 | N/A | N/A | Yes | Yes | 0.67 | 6.1 | 10 | 9.8 | 30 | 55.6 | 60.1 | N/A | N/A |  | Assets conditions, Vegetation conditions | 15 | 0.0019 | 12.7 | No | 24.5 | 37 |  | 64.58 | 12.1 | 12.5 | 19 | 58.82 | 15 | N/A | 0.035405 | 779.6611
2021-10-11 | GUSTINE 1102 | 27 | 38 | 46 | 46 | 70 | 8.1 | 82 | 8759 | 12.7 | N/A | N/A | Yes | Yes | 0.74 | 6.1 | 9.5 | 9.1 | 30 | 58.2 | 64.1 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0018 | 10.3 | No | 42.7 | 42 |  | 68 | 15 | 38.3 | 21.7 | 62.78 | 17 | N/A | 0.046778 | 347.3861
2021-10-11 | HIGHLANDS 1102 | 24 | 37 | 56 | 56 | 64 | 17.4 | 107 | 9133 | 11 | N/A | N/A | Yes | Yes | 0.79 | 7.4 | 10 | 8.5 | 31.1 | 59.6 | 57.8 | N/A | N/A |  | Assets conditions, Vegetation conditions | 928 | 0.0028 | 21.3 | No | 29 | 53 |  | 61.88 | 13.9 | 20.1 | 36 | 49.82 | 26.6 | N/A | 0.053051 | 961.1778
2021-10-11 | HIGHLANDS 1103 | 27 | 40 | 63 | 63 | 65 | 15.2 | 91 | 5270 | 11 | N/A | N/A | Yes | Yes | 0.77 | 7.3 | 10 | 8.4 | 32.9 | 58.6 | 57.8 | N/A | N/A |  | Assets conditions, Vegetation conditions | 22329 | 0.0069 | 39.4 | No | 28 | 49.8 |  | 65.48 | 9.4 | 16.9 | 33 | 52.52 | 26.4 | N/A | 1.6991 | 929.2444
2021-10-11 | JESSUP 1102 | 22 | 31 | 46 | 46 | 64 | 7.9 | 37 | 2733 | 14.5 | N/A | N/A | Yes | Yes | 0.68 | 7.3 | 10.2 | 8.9 | 35.8 | 61.5 | 76.5 | N/A | N/A |  | Assets conditions, Vegetation conditions | 16151 | 0.0062 | 34.3 | No | 21 | 35 |  | 66.92 | 13 | 19 | 32 | 66.02 | 13.3 | N/A | 0.29272 | 378.4694
2021-10-11 | JOLON 1102 | 30 | 39 | 56 | 56 | 71 | 14.1 | 92 | 13434 | 14.1 | N/A | N/A | Yes | Yes | 0.74 | 7 | 10.5 | 9.4 | 30.1 | 57.9 | 58 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1589 | 0.0034 | 21.3 | No | 24.6 | 45.3 |  | 68 | 17 | 16.9 | 31 | 53.6 | 24 | N/A | 0.97238 | 67.7957
2021-10-11 | JOLON 1103 | 27 | 32 | 51 | 51 | 70 | 9.9 | 68 | 9567 | 14.1 | N/A | N/A | Yes | Yes | 0.72 | 6.9 | 10.2 | 9.1 | 31.5 | 58.6 | 60.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1948 | 0.0027 | 18.2 | No | 24.6 | 45.3 |  | 68 | 17 | 16.9 | 26.9 | 51.98 | 24 | N/A | 0.057907 | 71.6194
2021-10-11 | KANAKA 1101 | 24 | 36 | 55 | 55 | 61 | 76.3 | 30 | 437 | 11.1 | N/A | N/A | Yes | Yes | 0.71 | 7.2 | 9.3 | 8 | 34.3 | 65.9 | 67.3 | N/A | N/A |  | Assets conditions, Vegetation conditions | 46952 | 0.0066 | 40.8 | No | 23.6 | 39.8 |  | 64.4 | 13 | 11.7 | 24 | 49.82 | 25.3 | N/A | 0.043998 | 6.7
2021-10-11 | KETTLEMAN HILLS 2104 | 24 | 34 | 52 | 52 | 70 | 8 | 74 | 14301 | 11.8 | N/A | N/A | Yes | Yes | 0.79 | 6.4 | 8.6 | 7.4 | 30 | 62.8 | 62.4 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0039 | 29.8 | No | 43 | 61 |  | 66.92 | 15 | 9.4 | 17.6 | 46.76 | 27.2 | N/A | 0.03041 | 73.6528
2021-10-11 | KING CITY 1106 | 28 | 34 | 47 | 47 | 68 | 7.9 | 76 | 10422 | 12 | N/A | N/A | Yes | Yes | 0.75 | 6.4 | 9.8 | 9.2 | 30 | 60.5 | 62.9 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0011 | 6.2 | No | 26.2 | 38 |  | 64.4 | 17.9 | 14.1 | 20.7 | 50.36 | 29.1 | N/A | 0.06642 | 65.3111
2021-10-11 | KONOCTI 1102 | 21 | 30 | 48 | 48 | 61 | 17.3 | 66 | 3104 | 12 | N/A | N/A | Yes | Yes | 0.74 | 7.5 | 10 | 8.6 | 38.9 | 60 | 61.8 | N/A | N/A |  | Assets conditions, Vegetation conditions | 33172 | 0.0043 | 26.3 | No | 21.3 | 35 |  | 63.32 | 13.1 | 9.4 | 21.2 | 57.92 | 16 | N/A | 0.10484 | 78.375
2021-10-11 | LAMONT 1102 | 23 | 26 | 37 | 37 | 69 | 5.8 | 51 | 7030 | 17.7 | N/A | N/A | No | No | 0.59 | 6.8 | 9.8 | 8.2 | 30 | 52.4 | 63.3 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0006 | 3.4 | No | 40.2 | 55.7 |  | 62.06 | 24.7 | 8.9 | 12.5 | 45.5 | 39.2 | N/A | 0.03577 | 4.675
2021-10-11 | LAMONT 1104 | 20 | 24 | 34 | 34 | 69 | 4.9 | 47 | 4282 | 17.1 | N/A | N/A | No | No | 0.37 | 6.8 | 10.1 | 8.3 | 30 | 57.2 | 63.4 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0004 | 1.4 | No | 40.2 | 55.7 |  | 64.58 | 21 | 8.9 | 12.5 | 45.5 | 39.2 | N/A | 0.031572 | 3.725
2021-10-11 | LOGAN CREEK 2102 | 27 | 36 | 54 | 54 | 67 | 9 | 94 | 16194 | 13.7 | N/A | N/A | Yes | Yes | 0.79 | 6.2 | 9.4 | 8.1 | 30 | 59.2 | 60.1 | N/A | N/A |  | Assets conditions, Vegetation conditions | 547 | 0.0034 | 24 | No | 30.2 | 41.9 |  | 67.1 | 10.5 | 26 | 34.1 | 66.02 | 11.8 | N/A | 0.039384 | 250.979
2021-10-11 | LONE TREE 2105 | 27 | 34 | 52 | 52 | 70 | 7 | 78 | 11123 | 13.5 | N/A | N/A | Yes | Yes | 0.69 | 6.7 | 10.6 | 9.6 | 30 | 58.6 | 61 | N/A | N/A |  | Assets conditions, Vegetation conditions | 653 | 0.0038 | 21.9 | No | 35.7 | 46.9 |  | 65.84 | 15.9 | 21.2 | 28.3 | 62.6 | 19.5 | N/A | 0.10079 | 2508.0417
2021-10-11 | LOS MOLINOS 1101 | 26 | 31 | 42 | 42 | 68 | N/A | N/A | N/A | 13.5 | N/A | N/A | Yes | Yes | 0.44 | 6.6 | 9.3 | 8.7 | 30.6 | 59.5 | 72 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0011 | 4.8 | No | 26.4 | 39.8 |  | 66.38 | 16.8 | 16.4 | 23.7 | 61.16 | 18.9 | N/A | 0.038058 | 1589.1694
2021-10-11 | LOS OSITOS 2103 | 28 | 35 | 53 | 53 | 66 | 14.5 | 87 | 11256 | 12.8 | N/A | N/A | Yes | Yes | 0.79 | 7 | 9.6 | 8.1 | 30 | 59.3 | 59.8 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0027 | 19.2 | No | 20 | 41 |  | 62.24 | 17 | 6.1 | 26 | 47.48 | 35 | N/A | 0.21864 | 48.992
2021-10-11 | MADISON 1105 | 27 | 37 | 57 | 57 | 69 | 6.9 | 72 | 9130 | 12.6 | N/A | N/A | Yes | Yes | 0.71 | 6.2 | 8.7 | 7.8 | 30.2 | 60 | 59.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | 13 | 0.0057 | 37 | No | 34.1 | 49.3 |  | 66.92 | 12.2 | 21.9 | 28.3 | 64.04 | 16.8 | N/A | 0.08008 | 15.025
2021-10-11 | MADISON 2101 | 31 | 42 | 57 | 57 | 69 | 14.2 | 106 | 7518 | 12.4 | N/A | N/A | Yes | Yes | 0.79 | 6.2 | 8.6 | 7.6 | 30.2 | 53.4 | 57.8 | N/A | N/A |  | Assets conditions, Vegetation conditions | 639 | 0.0048 | 31.6 | No | 31.6 | 51.3 |  | 68 | 11 | 19.7 | 33.8 | 64.04 | 16.8 | N/A | 0.4293 | 194.4444
2021-10-11 | MAGUNDEN 1108 | 20 | 24 | 33 | 33 | 69 | 5 | 49 | 5705 | 17.1 | N/A | N/A | Yes | No | 0.45 | 6.8 | 9.9 | 8.2 | 30 | 57 | 63.3 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0004 | 1.9 | No | 40.2 | 55.7 |  | 64.58 | 21 | 8.8 | 11 | 46.94 | 37 | N/A | 0.044167 | 12.175
2021-10-11 | MAXWELL 1105 | 30 | 41 | 57 | 57 | 68 | 8.9 | 83 | 13461 | 13.4 | N/A | N/A | Yes | Yes | 0.78 | 6 | 8.7 | 7.6 | 30 | 59.5 | 59 | N/A | N/A |  | Assets conditions, Vegetation conditions | 261 | 0.0029 | 20.7 | No | 27.5 | 44.8 |  | 65.84 | 12.6 | 18.5 | 27.8 | 62.42 | 16.8 | N/A | 0.087133 | 15.825
2021-10-11 | MIDDLETOWN 1101 | 32 | 43 | 66 | 66 | 65 | 72.9 | 72 | 2608 | 11 | N/A | N/A | Yes | Yes | 0.79 | 7.1 | 9.4 | 8.2 | 35.2 | 60.3 | 63.5 | N/A | N/A |  | Assets conditions, Vegetation conditions | 42283 | 0.0065 | 42.7 | No | 44.3 | 64.8 |  | 69.62 | 9.4 | 21.1 | 31.7 | 66.02 | 12.4 | N/A | 0.81862 | 930.925
2021-10-11 | MIDDLETOWN 1102 | 27 | 37 | 58 | 58 | 66 | 12.7 | 71 | 5335 | 10.9 | N/A | N/A | Yes | Yes | 0.7 | 7.1 | 9.9 | 8.9 | 33 | 58.6 | 59.4 | N/A | N/A |  | Assets conditions, Vegetation conditions | 5013 | 0.0052 | 32 | No | 31.1 | 48.7 |  | 65.48 | 9.4 | 16.8 | 25.9 | 52.52 | 26.4 | N/A | 3.753 | 517.6778
2021-10-11 | MIDDLETOWN 1103 | 20 | 28 | 45 | 45 | 67 | 12.3 | 65 | 3855 | 11.1 | N/A | N/A | Yes | Yes | 0.74 | 7.2 | 10.2 | 9.4 | 34.2 | 60.6 | 57.8 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1625 | 0.0035 | 19.7 | No | 29.7 | 48.7 |  | 66.92 | 9.4 | 15.1 | 25.9 | 54.14 | 26.4 | N/A | 0.038485 | 42.0944
2021-10-11 | MONTICELLO 1101 | 28 | 42 | 60 | 60 | 70 | 47.1 | 76 | 5202 | 10.9 | N/A | N/A | Yes | Yes | 0.79 | 6.8 | 10.2 | 8.8 | 30.7 | 57.4 | 57.4 | N/A | N/A |  | Assets conditions, Vegetation conditions | 16908 | 0.0066 | 36.8 | No | 40 | 57.1 |  | 69.08 | 11.1 | 24.8 | 34.7 | 61.7 | 20.6 | N/A | 1.9056 | 94.9528
2021-10-11 | OILFIELDS 1103 | 30 | 40 | 48 | 48 | 70 | 7.7 | 71 | 5740 | 14.9 | N/A | N/A | Yes | Yes | 0.71 | 7.3 | 11.7 | 9.9 | 30.9 | 60.5 | 60.7 | N/A | N/A |  | Assets conditions, Vegetation conditions | 491 | 0.0016 | 10 | No | 23.2 | 39.7 |  | 65.12 | 17.6 | 16.7 | 31 | 50.72 | 27.3 | N/A | 0.25699 | 983.7392
2021-10-11 | PANOCHE 1103 | 28 | 34 | 57 | 57 | 67 | 15.3 | 102 | 18866 | 11.1 | N/A | N/A | Yes | Yes | 0.79 | 7.1 | 9.3 | 7.9 | 30 | 53.8 | 60 | N/A | N/A |  | Assets conditions, Vegetation conditions | 96 | 0.0041 | 30.6 | No | 26.9 | 41.7 |  | 61.88 | 14.9 | 12.5 | 21.2 | 54.32 | 21.6 | N/A | 0.079514 | 43.5216
2021-10-11 | PANORAMA 1101 | 21 | 28 | 45 | 45 | 67 | 6.3 | 37 | 2625 | 13 | N/A | N/A | Yes | Yes | 0.61 | 7 | 9.4 | 8.4 | 42.6 | 64.1 | 75.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | 302 | 0.0019 | 10.4 | No | 16 | 28 |  | 64.4 | 15.2 | 12.8 | 25.4 | 63.5 | 16.3 | N/A | 1.0779 | 966.7028
2021-10-11 | PANORAMA 1102 | 24 | 28 | 45 | 45 | 67 | 6.7 | 69 | 7260 | 12.7 | N/A | N/A | Yes | Yes | 0.67 | 6.9 | 9.1 | 8 | 30.2 | 64.7 | 73 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1797 | 0.002 | 11.6 | No | 26 | 41.5 |  | 64.4 | 15.2 | 24.5 | 38.4 | 63.68 | 15.9 | N/A | 0.18926 | 99.4448
2021-10-11 | PERRY 1101 | 28 | 40 | 58 | 58 | 74 | 19.6 | 69 | 5990 | 10.9 | N/A | N/A | No | Yes | 0.74 | 6.9 | 11.4 | 10.3 | 40.6 | 61.6 | 62.6 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2857 | 0.0041 | 26.1 | No | 34.7 | 46.1 |  | 69.08 | 14 | 22.2 | 35.4 | 60.44 | 19.8 | N/A | 0.12265 | 28.4194
2021-10-11 | PUEBLO 1104 | 27 | 41 | 56 | 56 | 63 | 16.1 | 79 | 4558 | 13 | N/A | N/A | Yes | Yes | 0.68 | 7.2 | 10.7 | 9.5 | 36.4 | 59.8 | 57.7 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4277 | 0.0054 | 33.8 | No | 26.4 | 44.8 |  | 69.08 | 9.8 | 16.1 | 26.5 | 61.7 | 19.6 | N/A | 0.090011 | 381.8123
2021-10-11 | PUEBLO 1105 | 27 | 42 | 57 | 57 | 70 | 11.1 | 66 | 3421 | 10.6 | N/A | N/A | Yes | Yes | 0.76 | 6.9 | 11.7 | 9.9 | 37.2 | 61.1 | 58.5 | N/A | N/A |  | Assets conditions, Vegetation conditions | 3127 | 0.0053 | 38 | No | 26.4 | 44.8 |  | 69.44 | 9.8 | 15.1 | 26.3 | 61.7 | 19.6 | N/A | 0.22242 | 320.6586
2021-10-11 | PUTAH CREEK 1102 | 27 | 37 | 52 | 52 | 70 | 7.6 | 56 | 5888 | 12.2 | N/A | N/A | Yes | Yes | 0.78 | 6.4 | 9 | 7.8 | 30.5 | 57.4 | 58.5 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4836 | 0.0067 | 33 | No | 40 | 57.1 |  | 66.56 | 12 | 21.9 | 28.9 | 63.32 | 16.9 | N/A | 0.47895 | 535.9694
2021-10-11 | PUTAH CREEK 1103 | 24 | 34 | 52 | 52 | 70 | 7 | 61 | 6787 | 12.5 | N/A | N/A | Yes | Yes | 0.79 | 6.5 | 9.5 | 8.5 | 31.3 | 61.4 | 58.7 | N/A | N/A |  | Assets conditions, Vegetation conditions | 290 | 0.0045 | 25.8 | No | 24.7 | 44.7 |  | 65.84 | 12 | 15.8 | 26.7 | 63.32 | 16.9 | N/A | 0.12311 | 2742.85
2021-10-11 | PUTAH CREEK 1105 | 32 | 41 | 59 | 59 | 70 | 7.1 | 70 | 7764 | 12.5 | N/A | N/A | Yes | Yes | 0.73 | 6.2 | 8.5 | 7.6 | 30.4 | 59.8 | 58.9 | N/A | N/A |  | Assets conditions, Vegetation conditions | 233 | 0.0067 | 25.7 | No | 34.1 | 49.3 |  | 66.56 | 12 | 21.9 | 28.3 | 63.32 | 16.9 | N/A | 0.088356 | 290.0772
2021-10-11 | RED BLUFF 1101 | 22 | 30 | 43 | 43 | 67 | 7.5 | 58 | 6208 | 13.4 | N/A | N/A | Yes | Yes | 0.73 | 6.9 | 9.8 | 8.7 | 30.4 | 60 | 63.5 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2956 | 0.0032 | 19.6 | No | 22 | 35.9 |  | 66.2 | 11.2 | 14.1 | 21.3 | 61.88 | 15.7 | N/A | 0.93997 | 635.2123
2021-10-11 | RED BLUFF 1103 | 22 | 30 | 44 | 44 | 67 | 6.7 | 52 | 4657 | 13.7 | N/A | N/A | Yes | Yes | 0.63 | 6.9 | 9.8 | 8.7 | 30.8 | 60.7 | 74.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2593 | 0.0037 | 21.4 | No | 14.5 | 29.6 |  | 66.2 | 12.5 | 11.6 | 21 | 61.88 | 18 | N/A | 0.25558 | 425.166
2021-10-11 | RED BLUFF 1104 | 23 | 30 | 46 | 46 | 67 | 8.2 | 62 | 5522 | 12.8 | N/A | N/A | Yes | Yes | 0.76 | 6.9 | 9.4 | 8.3 | 31.4 | 61 | 63.5 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2576 | 0.0044 | 30.1 | No | 22.6 | 46.6 |  | 66.2 | 11.2 | 14.5 | 22.4 | 61.88 | 15.7 | N/A | 1.1761 | 467.442
2021-10-11 | REDBUD 1101 | 23 | 36 | 54 | 54 | 64 | 14.3 | 74 | 5868 | 11 | N/A | N/A | Yes | Yes | 0.78 | 7.2 | 9.5 | 8.4 | 31.2 | 60.3 | 57.8 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2121 | 0.0023 | 16.1 | No | 29 | 53 |  | 64.04 | 13.9 | 20.1 | 36 | 51.8 | 22.8 | N/A | 0.23109 | 236.4198
2021-10-11 | SAN ARDO 1102 | 26 | 39 | 52 | 52 | 67 | 13.7 | 99 | 10674 | 12.7 | N/A | N/A | Yes | Yes | 0.78 | 6.7 | 9.9 | 8.3 | 30.1 | 61.2 | 61.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0023 | 17.3 | No | 18.3 | 31 |  | 60.98 | 17.8 | 8.1 | 15.7 | 53.96 | 22.6 | N/A | 0.043505 | 98.616
2021-10-11 | SAN MIGUEL 1106 | 26 | 31 | 42 | 42 | 71 | 7.8 | 80 | 10718 | 11.4 | N/A | N/A | Yes | Yes | 0.61 | 6.8 | 10.9 | 9.5 | 30 | 60.3 | 60.5 | N/A | N/A |  | Assets conditions, Vegetation conditions | 180 | 0.0009 | 4.8 | No | 24.1 | 40.3 |  | 65.12 | 22.7 | 12.2 | 18.6 | 50.36 | 36.8 | N/A | 0.11941 | 251.9528
2021-10-11 | SANTA NELLA 1104 | 27 | 38 | 43 | 43 | 70 | 6.3 | 72 | 6567 | 12 | N/A | N/A | Yes | Yes | 0.37 | 6.4 | 11.1 | 10.5 | 30 | 59.5 | 64.5 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0012 | 4.3 | No | 42.7 | 42 |  | 68 | 16 | 38.3 | 28.3 | 62.78 | 20.1 | N/A | 0.033684 | 407.5022
2021-10-11 | SILVERADO 2102 | 25 | 35 | 53 | 53 | 69 | 44.3 | 101 | 4323 | 10.9 | N/A | N/A | Yes | Yes | 0.69 | 7 | 11.4 | 10.1 | 33.9 | 58.1 | 57.4 | N/A | N/A |  | Assets conditions, Vegetation conditions | 47610 | 0.0054 | 32.8 | No | 26.4 | 44.8 |  | 69.44 | 9.3 | 15.1 | 26.3 | 61.34 | 19.3 | N/A | 0.58322 | 29.529
2021-10-11 | SILVERADO 2104 | 27 | 41 | 63 | 63 | 69 | 72.6 | 84 | 3185 | 10.6 | N/A | N/A | Yes | Yes | 0.79 | 6.9 | 9.8 | 8.8 | 34.1 | 58 | 57.4 | N/A | N/A |  | Assets conditions, Vegetation conditions | 100456 | 0.0109 | 51.6 | No | 29.7 | 48.7 |  | 69.62 | 9.3 | 20.4 | 32.4 | 61.34 | 19.3 | N/A | 1.2815 | 70.9444
2021-10-11 | SISQUOC 1102 | 16 | 24 | 25 | 25 | 59 | 10.2 | 49 | 4638 | 15.6 | N/A | N/A | No | No | 0.57 | 6.2 | 11.7 | 11 | 37.6 | 58.9 | 60.1 | N/A | N/A |  | Assets conditions, Vegetation conditions | 143 | 0.0002 | 1.2 | No | 9.1 | 26.7 |  | 61.88 | 23.9 | 2 | 6.4 | 54.68 | 26.3 | N/A | 0.040576 | 53.0809
2021-10-11 | SYCAMORE CREEK 1111 | 20 | 28 | 44 | 44 | 71 | 55.6 | 52 | 4212 | 10.3 | N/A | N/A | Yes | Yes | 0.75 | 6.5 | 8.8 | 8 | 30.8 | 57.8 | 69.3 | N/A | N/A |  | Assets conditions, Vegetation conditions | 239103 | 0.0065 | 30.3 | No | 23.3 | 40.4 |  | 66.56 | 12.6 | 5.1 | 8.3 | 49.1 | 25.5 | N/A | 1.0065 | 1108.016
2021-10-11 | TASSAJARA 2104 | 22 | 33 | 47 | 47 | 68 | 6.7 | 65 | 9508 | 13.7 | N/A | N/A | Yes | Yes | 0.7 | 7.2 | 13.4 | 11 | 30.7 | 60.8 | 61 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2004 | 0.0041 | 26.5 | No | 31.9 | 55.2 |  | 66.2 | 14.5 | 20.4 | 29.4 | 63.5 | 18.7 | N/A | 0.050052 | 814.2123
2021-10-11 | TASSAJARA 2112 | 29 | 44 | 60 | 60 | 67 | 14.8 | 90 | 4088 | 13.5 | N/A | N/A | Yes | Yes | 0.74 | 7.2 | 11.9 | 9.2 | 31.8 | 61.2 | 60 | N/A | N/A |  | Assets conditions, Vegetation conditions | 10581 | 0.0048 | 32.2 | No | 31.5 | 55.2 |  | 65.48 | 14.7 | 18.1 | 26.1 | 61.88 | 19.1 | N/A | 0.069693 | 287.7272
2021-10-11 | TEJON 1102 | 40 | 53 | 69 | 69 | 66 | 11.7 | 105 | 16508 | 16.9 | N/A | N/A | No | No | 0.71 | 6.6 | 9.6 | 8.7 | 30 | 60.9 | 57.9 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2475 | 0.0036 | 25 | No | 40.3 | 62.2 |  | 60.98 | 12 | 25.3 | 34.8 | 49.1 | 20 | N/A | 0.86141 | 1360.6972
2021-10-11 | TEJON 1103 | 20 | 23 | 33 | 33 | 69 | 4.7 | 39 | 4100 | 16.3 | N/A | N/A | No | No | 0.4 | 6.8 | 9.8 | 8.3 | 30.1 | 63.9 | 64.9 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4 | 0.0007 | 2.7 | No | 26.5 | 37.9 |  | 62.96 | 21.3 | 9.5 | 11 | 50.36 | 33.6 | N/A | 0.049764 | 9.55
2021-10-11 | TEMPLETON 2110 | 23 | 37 | 48 | 48 | 70 | 13.1 | 41 | 2899 | 14.8 | N/A | N/A | No | Yes | 0.7 | 7.3 | 11.9 | 10.7 | 42.6 | 63.7 | 65.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4588 | 0.0019 | 13.2 | No | 22.3 | 39.8 |  | 65.48 | 16.1 | 19.1 | 35.1 | 56.84 | 24.1 | N/A | 0.091896 | 795.0827
2021-10-11 | TEMPLETON 2113 | 24 | 33 | 44 | 44 | 57 | 13.8 | 76 | 11842 | 17.7 | N/A | N/A | No | Yes | 0.64 | 6.6 | 11.3 | 10 | 30.1 | 60.5 | 58.3 | N/A | N/A |  | Assets conditions, Vegetation conditions | 796 | 0.0008 | 4.5 | No | 23.2 | 44.9 |  | 61.88 | 23.8 | 9.4 | 22.9 | 47.84 | 32.8 | N/A | 0.072443 | 1800.5222
2021-10-11 | TYLER 1105 | 27 | 33 | 46 | 46 | 67 | 7.3 | 72 | 7922 | 13.2 | N/A | N/A | Yes | Yes | 0.7 | 6.8 | 9.2 | 8 | 30.1 | 59.3 | 65.5 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1481 | 0.0037 | 22.9 | No | 20.7 | 38.7 |  | 66.2 | 12.2 | 13.8 | 23.4 | 61.88 | 15.5 | N/A | 0.55798 | 500.0892
2021-10-11 | VACA DIXON 1101 | 31 | 37 | 50 | 50 | 69 | 7 | 59 | 1529 | 12.7 | N/A | N/A | Yes | Yes | 0.4 | 6.5 | 9.8 | 8.9 | 33.6 | 59 | 59.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | 11 | 0.003 | 11 | No | 24.7 | 44.7 |  | 69.08 | 12.4 | 15.8 | 26.8 | 65.84 | 17.3 | N/A | 0.22076 | 1951.3363
2021-10-11 | VACA DIXON 1105 | 31 | 37 | 53 | 53 | 70 | 11.2 | 64 | 5013 | 12.5 | N/A | N/A | Yes | Yes | 0.77 | 6.5 | 9.1 | 8.1 | 30.6 | 59 | 58.7 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4563 | 0.0057 | 39.4 | No | 40 | 57.1 |  | 69.08 | 12 | 19 | 28.9 | 65.84 | 16.9 | N/A | 1.0334 | 3521.4694
2021-10-11 | VACAVILLE 1104 | 26 | 40 | 53 | 53 | 70 | 13.3 | 90 | 5841 | 12.1 | N/A | N/A | Yes | Yes | 0.73 | 6.4 | 10 | 9 | 32.6 | 57.3 | 59.6 | N/A | N/A |  | Assets conditions, Vegetation conditions | 7434 | 0.0056 | 29.4 | No | 22.5 | 44.4 |  | 68.9 | 11.8 | 21.9 | 37.8 | 65.66 | 11.8 | N/A | 1.6292 | 577.3861
2021-10-11 | VACAVILLE 1108 | 29 | 41 | 60 | 60 | 69 | 27.8 | 51 | 2101 | 12.2 | N/A | N/A | Yes | Yes | 0.77 | 6.2 | 9 | 7.8 | 32.1 | 58.9 | 57.8 | N/A | N/A |  | Assets conditions, Vegetation conditions | 7434 | 0.0062 | 39.6 | No | 40 | 57.1 |  | 68 | 12 | 19 | 28.9 | 64.58 | 16.9 | N/A | 0.76197 | 79.4623
2021-10-11 | VACAVILLE 1111 | 26 | 36 | 55 | 55 | 69 | 11.2 | 51 | 1487 | 12.3 | N/A | N/A | Yes | Yes | 0.75 | 6.2 | 9.1 | 8.5 | 33.8 | 58.4 | 59 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4563 | 0.006 | 39.4 | No | 40 | 57.1 |  | 69.08 | 12.4 | 19 | 28.9 | 65.84 | 17.3 | N/A | 3.4796 | 839.875
2021-10-11 | VACAVILLE 1112 | 26 | 36 | 55 | 55 | 69 | 6.5 | 49 | 872 | 12.4 | N/A | N/A | Yes | Yes | 0.44 | 6.3 | 9.5 | 8.9 | 34 | 58.4 | 59.3 | N/A | N/A |  | Assets conditions, Vegetation conditions | 1405 | 0.0053 | 22.8 | No | 24.7 | 44.7 |  | 69.08 | 12.4 | 15.8 | 26.8 | 65.84 | 17.3 | N/A | 0.55177 | 76.7194
2021-10-11 | VASCO 1102 | 25 | 34 | 49 | 49 | 67 | 11.8 | 75 | 8612 | 14.1 | N/A | N/A | Yes | Yes | 0.77 | 7.4 | 11.4 | 9 | 30.6 | 60.2 | 62.3 | N/A | N/A |  | Assets conditions, Vegetation conditions | 994 | 0.004 | 28.5 | No | 38.2 | 56 |  | 68 | 17.4 | 20.4 | 29.7 | 60.62 | 20.2 | N/A | 0.2481 | 617.3281
2021-10-11 | VOLTA 1101 | 21 | 32 | 50 | 50 | 66 | 49.4 | 56 | 5280 | 13 | N/A | N/A | No | No | 0.69 | 6.9 | 9.4 | 8.3 | 30.9 | 65.1 | 60.9 | N/A | N/A |  | Assets conditions, Vegetation conditions | 96082 | 0.0042 | 17.8 | No | 26 | 46.6 |  | 65.66 | 16.4 | 22 | 30.8 | 55.4 | 28.2 | N/A | 0.82988 | 27.225
2021-10-11 | WESTLEY 1103 | 35 | 43 | 57 | 57 | 67 | 8.1 | 85 | 13568 | 15.2 | N/A | N/A | Yes | Yes | 0.79 | 6.5 | 8.9 | 7.9 | 30 | 61.3 | 62.1 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0043 | 33.4 | No | 20.3 | 51.2 |  | 49.64 | 26.4 | 13.7 | 29.4 | 46.22 | 30.7 | N/A | 0.077877 | 32.7611
2021-10-11 | ZACA 1102 | 33 | 44 | 62 | 62 | 60 | 12.3 | 83 | 8426 | 15.5 | N/A | N/A | No | Yes | 0.76 | 5.6 | 10.4 | 10 | 30.6 | 59.5 | 59.6 | N/A | N/A |  | Assets conditions, Vegetation conditions | 411 | 0.0042 | 30.3 | No | 24.2 | 38 |  | 60.08 | 18.8 | 9.4 | 22 | 60.08 | 18.8 | N/A | 0.051198 | 2839.3694
2021-10-14 | CAL WATER 1102 | 15 | 19 | 25 | 25 | 83 | 5 | 42 | 3120 | 7.1 | N/A | N/A | No | No | 0.65 | 4.7 | 7.3 | 7.1 | 30 | 64.9 | 55.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4 | 0.0003 | 1.7 | No | 22.4 | 32.5 |  | 70.7 | 17.6 | 10.2 | 14 | 71.24 | 18.4 | N/A | 0.11476 | 3059.4097
2021-10-14 | LAMONT 1104 | 26 | 36 | 41 | 41 | 84 | 6.1 | 64 | 9008 | 6.7 | N/A | N/A | No | No | 0.47 | 4.8 | 7.5 | 7.4 | 30 | 64.9 | 59.7 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.001 | 3.1 | No | 22.4 | 32.5 |  | 73.4 | 20.2 | 8.3 | 13.8 | 73.4 | 23 | N/A | 0.087314 | 1756.5722
2021-10-14 | MAGUNDEN 1108 | 26 | 36 | 41 | 41 | 86 | 6.1 | 64 | 7162 | 6.4 | N/A | N/A | No | No | 0.57 | 4.8 | 7.4 | 7.3 | 30 | 64.9 | 59.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | N/A | 0.0017 | 3.5 | No | 22.4 | 32.5 |  | 73.4 | 18 | 10.2 | 14 | 73.4 | 18.4 | N/A | 0.17714 | 2714.5445
2021-10-14 | SCE TEHACHAPI 1101 | 23 | 34 | 51 | 51 | 78 | 8 | 74 | 5242 | 7.4 | N/A | N/A | No | No | 0.78 | 5.2 | 7.8 | 7.5 | 31.3 | 63.4 | 64.6 | N/A | N/A |  | Assets conditions, Vegetation conditions | 54 | 0.003 | 23.5 | No | 19.4 | 36.8 |  | 63.86 | 19.7 | 13.7 | 23.5 | 63.86 | 19.7 | N/A | 0.089809 | 3.175
2021-10-14 | TEJON 1102 | 34 | 44 | 59 | 59 | 80 | 10.6 | 99 | 18726 | 7.3 | N/A | N/A | No | No | 0.81 | 5 | 7.2 | 6.9 | 30 | 57.9 | 61.2 | N/A | N/A |  | Assets conditions, Vegetation conditions | 2475 | 0.0038 | 27.5 | No | 34.7 | 47.5 |  | 82.04 | 1 | 23 | 39 | 82.04 | 8.1 | N/A | 1.5669 | 759.1188
2021-10-14 | TEJON 1103 | 13 | 16 | 18 | 18 | 83 | 5.2 | 46 | 2449 | 7.3 | N/A | N/A | No | No | 0.41 | 5.3 | 7.5 | 7.3 | 30.2 | 66.2 | 64.6 | N/A | N/A |  | Assets conditions, Vegetation conditions | 4 | 0.0003 | 1.2 | No | 10.9 | 13 |  | 67.46 | 29.3 | 5.8 | 9.1 | 68 | 29.6 | N/A | 0.11975 | 9.575
[1] Jan 2021 PSPS event was executed under our 2020 PSPS protocols. Items marked N/A for the Jan 2021 event indicate it was not considered in that PSPS event. Our PSPS protocols were enhanced in 2021 and considered more features.
[2] The meteorology data reported for the PSPS events correspond to data from the time period of "De-energization Time" to "All Clear Time". The data will not correspond directly to the 10-Day Report for the listed PSPS events, which capture similar metrics but is reported for a 24hr time period for PSPS events.
[3] Several inputs throughout this table are populated as "N/A". These data points either cannot be tracked retroactively and/or are not used by PG&E in our PSPS decision making. These data points were also not required by any of the Commission decisions, including Resolution ESRB-8, D.19-05-042 (Phase 1), D.20-05-051 (Phase 2), D.21-06-034 (Phase 3), and D. 21-06-014 (PSPS OII), or the Post Event Report (PER) template provided in October 2021

## 10.Distribution
LIST EACH EVENT FOR WHICH A CIRCUIT WAS DE-ENERGIZED FOR EACH COUNTY
Event Name | Circuit Name | County or Tribe | Line miles of circuit{1] | Line miles of circuit in HFTD Tiers 2 and 3[2] | Date De-energized[3] | Time De-energized (24-hr. clock)[3] | “All Clear” declaration date/time | Date Re-energized[4] | Time Re-energized (24-hr. clock)[4] | Total Days De-energized (fractions in tenths) | Total Hours De-energized (Integer) | Total customers de-energized | Residential customers de-energized | Commercial/Industrial customers de-energized | Medical Baseline (MBL) customers de-energized | AFN other than MBL customers de-energized | PG&E remarks
2021-01-18 | AUBERRY 1101 | FRESNO | 76.1407 | 74.3248 | 2021-01-19 01:06 | 1:06 | 2021-01-20 04:22 | 2021-01-20 12:55 | 12:55 | 1.4924 | 36 | 923 | 827 | 94 | 61 | N/A | See footnote #4
2021-01-18 | BALCH NO 1 1101 | FRESNO | 10.8271 | 10.8271 | 2021-01-19 05:53 | 5:53 | 2021-01-20 04:22 | 2021-01-20 09:32 | 9:32 | 1.1521 | 28 | 25 | 13 | 12 | 1 | N/A | See footnote #4
2021-01-18 | CAL WATER 1102 | KERN | 4.2754 | 3.7443 | 2021-01-19 06:49 | 6:49 | 2021-01-20 04:22 | 2021-01-20 08:00 | 8:00 | 1.0493 | 25 | 13 | 0 | 10 | 0 | N/A | See footnote #4
2021-01-18 | DUNLAP 1102 | TULARE, FRESNO | 91.9867 | 83.9103 | 2021-01-19 05:46 | 5:46 | 2021-01-20 04:22 | 2021-01-20 16:20 | 16:20 | 1.4403 | 35 | 663 | 597 | 56 | 28 | N/A | See footnote #4
2021-01-18 | DUNLAP 1103 | TULARE, FRESNO | 45.1545 | 45.1545 | 2021-01-19 02:46 | 2:46 | 2021-01-20 04:22 | 2021-01-20 16:47 | 16:47 | 1.584 | 38 | 477 | 407 | 65 | 19 | N/A | See footnote #4
2021-01-18 | LAMONT 1102 | KERN | 2.638 | 1.3209 | 2021-01-19 06:43 | 6:43 | 2021-01-20 04:22 | 2021-01-20 08:18 | 8:18 | 1.066 | 26 | 5 | 0 | 5 | 0 | N/A | See footnote #4
2021-01-18 | MARIPOSA 2101 | MARIPOSA | 125.8894 | 121.6076 | 2021-01-19 00:09 | 0:09 | 2021-01-19 14:03 | 2021-01-26 16:10 | 16:10 | 7.6674 | 184 | 1363 | 1281 | 79 | 115 | N/A | See footnote #4
2021-01-18 | MARIPOSA 2102 | MARIPOSA | 6.0816 | 6.0816 | 2021-01-19 00:24 | 0:24 | 2021-01-19 14:03 | 2021-01-24 14:02 | 14:02 | 5.5681 | 134 | 81 | 77 | 3 | 6 | N/A | See footnote #4
2021-01-18 | MESA 1101 | SAN LUIS OBISPO, SANTA BARBARA | 18.7056 | 16.6893 | 2021-01-19 08:14 | 8:14 | 2021-01-20 04:22 | 2021-01-20 10:50 | 10:50 | 1.1083 | 27 | 85 | 65 | 14 | 4 | N/A | See footnote #4
2021-01-18 | OAKHURST 1103 | MADERA, MARIPOSA | 33.4104 | 30.8036 | 2021-01-18 23:46 | 23:46 | 2021-01-20 04:22 | 2021-01-26 16:50 | 16:50 | 7.7111 | 185 | 703 | 609 | 94 | 12 | N/A | See footnote #4
2021-01-18 | SAN JOAQUIN #3 1101 | MADERA | 5.3746 | 5.2584 | 2021-01-19 00:23 | 0:23 | 2021-01-20 04:22 | 2021-01-21 17:32 | 17:32 | 2.7146 | 65 | 75 | 73 | 2 | 3 | N/A | See footnote #4
2021-01-18 | SAN JOAQUIN #3 1103 | MADERA | 4.974 | 4.974 | 2021-01-18 23:02 | 23:02 | 2021-01-20 04:22 | 2021-01-23 17:40 | 17:40 | 4.7764 | 115 | 149 | 144 | 5 | 13 | N/A | See footnote #4
2021-01-18 | SAND CREEK 1103 | TULARE | 18.6476 | 18.6476 | 2021-01-19 05:57 | 5:57 | 2021-01-19 14:03 | 2021-01-19 16:39 | 16:39 | 0.44583 | 11 | 161 | 127 | 29 | 3 | N/A | See footnote #4
2021-01-18 | SANTA MARIA 1108 | SAN LUIS OBISPO, SANTA BARBARA | 44.9048 | 38.4324 | 2021-01-19 08:10 | 8:10 | 2021-01-20 04:22 | 2021-01-20 09:44 | 9:44 | 1.0653 | 26 | 202 | 160 | 22 | 6 | N/A | See footnote #4
2021-01-18 | SCE TEHACHAPI 1101 | KERN | 1.1571 | 1.1571 | 2021-01-19 02:36 | 2:36 | 2021-01-20 04:22 | 2021-01-20 09:16 | 9:16 | 1.2778 | 31 | 3 | 2 | 1 | 0 | N/A | See footnote #4
2021-01-18 | SISQUOC 1103 | SANTA BARBARA | 19.8823 | 19.5915 | 2021-01-19 08:06 | 8:06 | 2021-01-20 04:22 | 2021-01-20 09:41 | 9:41 | 1.066 | 26 | 154 | 119 | 24 | 1 | N/A | See footnote #4
2021-01-18 | SO. CAL. EDISON #3 1101 | MADERA, FRESNO | 9.4443 | 8.5367 | 2021-01-19 01:13 | 1:13 | 2021-01-20 04:22 | 2021-01-20 11:39 | 11:39 | 1.4347 | 34 | 15 | 14 | 1 | 2 | N/A | See footnote #4
2021-01-18 | TEJON 1103 | KERN | 1.4609 | 1.4609 | 2021-01-19 06:52 | 6:52 | 2021-01-20 04:22 | 2021-01-20 08:30 | 8:30 | 1.0681 | 26 | 2 | 0 | 2 | 0 | N/A | See footnote #4
2021-08-17 | ANDERSON 1101 | SHASTA | 20.7579 | 16.478 | 2021-08-17 18:04 | 18:04 | 2021-08-18 17:08 | 2021-08-18 20:11 | 20:11 | 1.0882 | 26 | 460 | 361 | 96 | 33 | 75
2021-08-17 | ANDERSON 1103 | SHASTA | 7.7422 | 2.8231 | 2021-08-17 18:50 | 18:50 | 2021-08-18 17:08 | 2021-08-18 20:40 | 20:40 | 1.0764 | 26 | 68 | 63 | 2 | 7 | 19
2021-08-17 | ANTLER 1101 | SHASTA | 48.622 | 45.4714 | 2021-08-17 18:21 | 18:21 | 2021-08-18 09:29 | 2021-08-18 17:19 | 17:19 | 0.95694 | 23 | 346 | 307 | 32 | 30 | 54
2021-08-17 | ARBUCKLE 1101 | COLUSA | 0.61589 | 0 | 2021-08-17 18:34 | 18:34 | 2021-08-18 14:46 | 2021-08-18 16:14 | 16:14 | 0.90278 | 22 | 3 | 2 | 0 | 0 | 0
2021-08-17 | ARBUCKLE 1104 | YOLO, COLUSA | 3.2838 | 1.9232 | 2021-08-17 18:33 | 18:33 | 2021-08-18 14:46 | 2021-08-18 16:45 | 16:45 | 0.925 | 22 | 12 | 8 | 3 | 0 | 1
2021-08-17 | BIG BEND 1101 | BUTTE | 61.6148 | 61.1743 | 2021-08-17 19:20 | 19:20 | 2021-08-19 05:17 | 2021-08-19 10:54 | 10:54 | 1.6486 | 40 | 259 | 233 | 24 | 19 | 65
2021-08-17 | BUCKS CREEK 1103 | PLUMAS | 26.7816 | 25.3736 | 2021-08-17 19:51 | 19:51 | 2021-08-19 05:17 | 2021-08-20 10:30 | 10:30 | 2.6104 | 63 | 316 | 265 | 51 | 4 | 5
2021-08-17 | BURNEY 1101 | SHASTA | 15.5607 | 13.6644 | 2021-08-17 17:32 | 17:32 | 2021-08-18 07:58 | 2021-08-18 11:40 | 11:40 | 0.75556 | 18 | 131 | 100 | 25 | 16 | 10
2021-08-17 | BUTTE 1105 | BUTTE | 5.044 | 5.044 | 2021-08-17 19:00 | 19:00 | 2021-08-18 09:29 | 2021-08-18 14:25 | 14:25 | 0.80903 | 19 | 53 | 51 | 2 | 3 | 9
2021-08-17 | CALISTOGA 1101 | NAPA, SONOMA | 132.1069 | 106.7431 | 2021-08-17 18:40 | 18:40 | 2021-08-18 12:39 | 2021-08-18 19:56 | 19:56 | 1.0528 | 25 | 1603 | 1256 | 240 | 64 | 34
2021-08-17 | CALISTOGA 1102 | NAPA | 57.4694 | 28.6755 | 2021-08-17 19:15 | 19:15 | 2021-08-18 12:39 | 2021-08-18 20:35 | 20:35 | 1.0556 | 25 | 2076 | 1592 | 422 | 63 | 49
2021-08-17 | CALPINE 1144 | SONOMA, LAKE | 31.874 | 31.5233 | 2021-08-17 20:00 | 20:00 | 2021-08-18 12:39 | 2021-08-19 09:11 | 9:11 | 1.5493 | 37 | 15 | 2 | 13 | 0 | 0
2021-08-17 | CALPINE 1146 | SONOMA, LAKE | 5.8295 | 5.8295 | 2021-08-17 20:00 | 20:00 | 2021-08-18 12:39 | 2021-08-19 09:11 | 9:11 | 1.5493 | 37 | 0 | 0 | 0 | 0 | 0
2021-08-17 | CEDAR CREEK 1101 | SHASTA | 115.2441 | 111.2964 | 2021-08-17 17:34 | 17:34 | 2021-08-18 15:24 | 2021-08-19 13:34 | 13:34 | 1.8333 | 44 | 721 | 641 | 74 | 54 | 127
2021-08-17 | CLARK ROAD 1102 | BUTTE | 64.3222 | 59.5701 | 2021-08-17 19:06 | 19:06 | 2021-08-19 05:17 | 2021-08-19 10:11 | 10:11 | 1.6285 | 39 | 490 | 428 | 55 | 50 | 66
2021-08-17 | CLOVERDALE 1102 | SONOMA, MENDOCINO | 17.6354 | 17.6354 | 2021-08-17 19:23 | 19:23 | 2021-08-18 11:38 | 2021-08-18 17:39 | 17:39 | 0.92778 | 22 | 70 | 46 | 9 | 7 | 1
2021-08-17 | CORNING 1101 | TEHAMA | 56.2021 | 49.887 | 2021-08-17 19:16 | 19:16 | 2021-08-18 17:08 | 2021-08-19 11:46 | 11:46 | 1.6875 | 41 | 840 | 772 | 65 | 101 | 331
2021-08-17 | CORNING 1102 | TEHAMA | 83.3634 | 79.8807 | 2021-08-17 19:08 | 19:08 | 2021-08-18 17:08 | 2021-08-19 12:00 | 12:00 | 1.7028 | 41 | 286 | 228 | 48 | 13 | 66
2021-08-17 | CORTINA 1101 | COLUSA | 3.7971 | 1.3221 | 2021-08-17 18:42 | 18:42 | 2021-08-18 14:46 | 2021-08-18 17:22 | 17:22 | 0.94444 | 23 | 8 | 4 | 4 | 1 | 2
2021-08-17 | COTTONWOOD 1101 | SHASTA, TEHAMA | 86.9473 | 70.528 | 2021-08-17 17:38 | 17:38 | 2021-08-18 17:08 | 2021-08-19 13:19 | 13:19 | 1.8201 | 44 | 895 | 831 | 46 | 75 | 218
2021-08-17 | COTTONWOOD 1102 | SHASTA | 79.0523 | 57.022 | 2021-08-17 17:28 | 17:28 | 2021-08-18 17:08 | 2021-08-19 12:08 | 12:08 | 1.7778 | 43 | 962 | 895 | 52 | 97 | 212
2021-08-17 | COTTONWOOD 1103 | SHASTA, TEHAMA | 162.9746 | 139.4863 | 2021-08-17 17:29 | 17:29 | 2021-08-19 05:17 | 2021-08-19 13:04 | 13:04 | 1.816 | 44 | 2435 | 2284 | 117 | 230 | 603
2021-08-17 | CRESCENT MILLS 2101 | PLUMAS | 16.7365 | 7.5017 | 2021-08-17 18:52 | 18:52 | 2021-08-18 07:58 | 2021-08-18 11:26 | 11:26 | 0.69028 | 17 | 92 | 79 | 5 | 8 | 9
2021-08-17 | CRESTA 1101 | BUTTE | 1.5783 | 1.2318 | 2021-08-17 19:18 | 19:18 | 2021-08-19 05:17 | 2021-08-19 12:34 | 12:34 | 1.7194 | 41 | 1 | 0 | 1 | 0 | 0
2021-08-17 | DESCHUTES 1101 | SHASTA | 40.5314 | 34.7246 | 2021-08-17 17:47 | 17:47 | 2021-08-18 17:08 | 2021-08-18 19:56 | 19:56 | 1.0896 | 26 | 253 | 227 | 21 | 18 | 47
2021-08-17 | DESCHUTES 1104 | SHASTA | 30.6934 | 21.4473 | 2021-08-17 18:39 | 18:39 | 2021-08-18 17:08 | 2021-08-19 10:24 | 10:24 | 1.6562 | 40 | 389 | 368 | 17 | 26 | 86
2021-08-17 | DUNBAR 1101 | SONOMA | 13.3096 | 13.0366 | 2021-08-17 18:41 | 18:41 | 2021-08-18 09:29 | 2021-08-18 15:15 | 15:15 | 0.85694 | 21 | 131 | 104 | 21 | 6 | 2
2021-08-17 | DUNBAR 1102 | SONOMA | 11.5986 | 9.3694 | 2021-08-17 18:51 | 18:51 | 2021-08-18 07:58 | 2021-08-18 12:08 | 12:08 | 0.72014 | 17 | 144 | 123 | 14 | 10 | 2
2021-08-17 | DUNBAR 1103 | SONOMA | 29.0509 | 25.5042 | 2021-08-17 18:53 | 18:53 | 2021-08-18 07:58 | 2021-08-18 13:22 | 13:22 | 0.77014 | 18 | 253 | 197 | 41 | 7 | 8
2021-08-17 | ELK CREEK 1101 | COLUSA, GLENN | 174.5795 | 79.4883 | 2021-08-17 12:51 | 12:51 | 2021-08-18 15:24 | 2021-08-19 12:22 | 12:22 | 1.9799 | 48 | 856 | 696 | 132 | 53 | 171
2021-08-17 | GEYSERVILLE 1101 | SONOMA | 25.7037 | 25.7037 | 2021-08-17 19:05 | 19:05 | 2021-08-18 07:58 | 2021-08-18 18:57 | 18:57 | 0.99444 | 24 | 26 | 17 | 6 | 1 | 1
2021-08-17 | GEYSERVILLE 1102 | SONOMA | 53.1951 | 38.9036 | 2021-08-17 18:45 | 18:45 | 2021-08-18 11:38 | 2021-08-18 16:37 | 16:37 | 0.91111 | 22 | 297 | 191 | 65 | 5 | 5
2021-08-17 | GIRVAN 1101 | SHASTA | 152.1507 | 146.1649 | 2021-08-17 17:24 | 17:24 | 2021-08-18 15:24 | 2021-08-19 10:47 | 10:47 | 1.7243 | 41 | 1207 | 1079 | 124 | 102 | 160
2021-08-17 | GIRVAN 1102 | SHASTA | 41.7917 | 41.1567 | 2021-08-17 17:35 | 17:35 | 2021-08-18 17:08 | 2021-08-19 09:18 | 9:18 | 1.6549 | 40 | 581 | 560 | 20 | 46 | 86
2021-08-17 | GLENN 1101 | GLENN | 2.5728 | 0.26324 | 2021-08-17 19:17 | 19:17 | 2021-08-18 16:41 | 2021-08-18 19:39 | 19:39 | 1.0153 | 24 | 5 | 3 | 1 | 0 | 0
2021-08-17 | HIGHLANDS 1102 | LAKE | 7.0385 | 6.8105 | 2021-08-17 19:18 | 19:18 | 2021-08-18 12:39 | 2021-08-19 15:10 | 15:10 | 1.8278 | 44 | 10 | 7 | 3 | 0 | 1
2021-08-17 | HIGHLANDS 1103 | LAKE | 93.1191 | 86.6716 | 2021-08-17 19:13 | 19:13 | 2021-08-18 12:39 | 2021-08-19 15:31 | 15:31 | 1.8458 | 44 | 1325 | 1204 | 91 | 110 | 299
2021-08-17 | JAMESON 1102 | SOLANO | 7.1702 | 7.1702 | 2021-08-17 19:36 | 19:36 | 2021-08-18 07:58 | 2021-08-18 12:48 | 12:48 | 0.71667 | 17 | 217 | 200 | 17 | 14 | 11
2021-08-17 | JAMESON 1105 | SOLANO | 11.7765 | 10.6334 | 2021-08-17 20:00 | 20:00 | 2021-08-18 07:58 | 2021-08-18 12:50 | 12:50 | 0.70139 | 17 | 66 | 46 | 13 | 3 | 2
2021-08-17 | JESSUP 1101 | SHASTA | 72.4604 | 65.2731 | 2021-08-17 17:51 | 17:51 | 2021-08-18 17:08 | 2021-08-19 13:31 | 13:31 | 1.8194 | 44 | 1459 | 1408 | 49 | 147 | 403
2021-08-17 | JESSUP 1102 | SHASTA | 80.4267 | 54.8937 | 2021-08-17 17:35 | 17:35 | 2021-08-18 17:08 | 2021-08-19 16:07 | 16:07 | 1.9389 | 47 | 1504 | 1448 | 55 | 158 | 532
2021-08-17 | JESSUP 1103 | SHASTA | 1.5838 | 0.7778 | 2021-08-17 17:28 | 17:28 | 2021-08-18 17:08 | 2021-08-18 20:56 | 20:56 | 1.1444 | 27 | 113 | 108 | 5 | 4 | 42
2021-08-17 | KESWICK 1101 | SHASTA | 77.219 | 77.0896 | 2021-08-17 18:42 | 18:42 | 2021-08-18 15:24 | 2021-08-19 10:04 | 10:04 | 1.6403 | 39 | 501 | 404 | 94 | 22 | 88
2021-08-17 | KONOCTI 1108 | LAKE | 11.0875 | 6.8256 | 2021-08-17 19:02 | 19:02 | 2021-08-18 09:29 | 2021-08-18 19:04 | 19:04 | 1.0014 | 24 | 707 | 671 | 34 | 57 | 200
2021-08-17 | LAKEVILLE 1102 | SONOMA | 6.639 | 6.3449 | 2021-08-17 19:20 | 19:20 | 2021-08-18 07:58 | 2021-08-18 12:57 | 12:57 | 0.73403 | 18 | 20 | 10 | 6 | 2 | 1
2021-08-17 | LOGAN CREEK 2102 | GLENN | 4.3372 | 3.4777 | 2021-08-17 19:03 | 19:03 | 2021-08-18 15:24 | 2021-08-18 18:05 | 18:05 | 0.95972 | 23 | 8 | 3 | 3 | 0 | 0
2021-08-17 | MADISON 1105 | YOLO | 6.4895 | 0.35006 | 2021-08-17 19:06 | 19:06 | 2021-08-18 14:46 | 2021-08-18 16:43 | 16:43 | 0.90069 | 22 | 31 | 20 | 7 | 1 | 0
2021-08-17 | MADISON 2101 | YOLO | 26.4307 | 4.3485 | 2021-08-17 18:30 | 18:30 | 2021-08-18 14:46 | 2021-08-18 19:34 | 19:34 | 1.0444 | 25 | 222 | 144 | 32 | 5 | 0
2021-08-17 | MAXWELL 1105 | COLUSA | 15.2749 | 3.8977 | 2021-08-17 18:37 | 18:37 | 2021-08-18 15:24 | 2021-08-18 17:59 | 17:59 | 0.97361 | 23 | 44 | 29 | 9 | 1 | 3
2021-08-17 | MC ARTHUR 1101 | LASSEN, SHASTA | 12.885 | 12.3938 | 2021-08-17 17:46 | 17:46 | 2021-08-18 07:58 | 2021-08-19 16:12 | 16:12 | 1.9347 | 46 | 59 | 46 | 13 | 1 | 10
2021-08-17 | MIDDLETOWN 1101 | NAPA, SONOMA, LAKE | 85.487 | 82.5516 | 2021-08-17 19:00 | 19:00 | 2021-08-18 12:39 | 2021-08-19 12:13 | 12:13 | 1.7174 | 41 | 1216 | 1086 | 120 | 62 | 243
2021-08-17 | MIDDLETOWN 1102 | LAKE | 9.8179 | 9.8179 | 2021-08-17 18:45 | 18:45 | 2021-08-18 09:29 | 2021-08-18 16:31 | 16:31 | 0.90694 | 22 | 691 | 674 | 15 | 67 | 137
2021-08-17 | MONTICELLO 1101 | NAPA, SOLANO | 117.7561 | 103.4688 | 2021-08-17 18:32 | 18:32 | 2021-08-18 09:29 | 2021-08-18 19:34 | 19:34 | 1.0431 | 25 | 932 | 718 | 165 | 54 | 22
2021-08-17 | NAPA 1112 | NAPA | 6.5217 | 6.5217 | 2021-08-17 18:38 | 18:38 | 2021-08-18 07:58 | 2021-08-18 13:47 | 13:47 | 0.79792 | 19 | 28 | 19 | 6 | 4 | 1
2021-08-17 | OREGON TRAIL 1102 | SHASTA | 10.3481 | 10.3481 | 2021-08-17 18:35 | 18:35 | 2021-08-18 17:08 | 2021-08-18 20:01 | 20:01 | 1.0597 | 25 | 242 | 238 | 4 | 22 | 35
2021-08-17 | OREGON TRAIL 1103 | SHASTA | 94.333 | 93.2028 | 2021-08-17 18:44 | 18:44 | 2021-08-18 17:08 | 2021-08-19 15:16 | 15:16 | 1.8556 | 45 | 1130 | 1051 | 71 | 87 | 221
2021-08-17 | OREGON TRAIL 1104 | SHASTA | 19.4342 | 16.4498 | 2021-08-17 18:37 | 18:37 | 2021-08-18 17:08 | 2021-08-18 20:42 | 20:42 | 1.0868 | 26 | 325 | 314 | 11 | 25 | 75
2021-08-17 | ORO FINO 1101 | BUTTE | 39.6831 | 39.6831 | 2021-08-17 18:28 | 18:28 | 2021-08-18 09:29 | 2021-08-18 17:57 | 17:57 | 0.97847 | 23 | 2290 | 2215 | 70 | 288 | 982
2021-08-17 | ORO FINO 1102 | BUTTE | 50.8521 | 50.2539 | 2021-08-17 19:01 | 19:01 | 2021-08-18 11:38 | 2021-08-18 18:17 | 18:17 | 0.96944 | 23 | 1185 | 1134 | 49 | 118 | 253
2021-08-17 | PANORAMA 1101 | SHASTA, TEHAMA | 11.374 | 10.4459 | 2021-08-17 17:38 | 17:38 | 2021-08-18 17:08 | 2021-08-18 19:39 | 19:39 | 1.084 | 26 | 791 | 777 | 14 | 93 | 197
2021-08-17 | PANORAMA 1102 | SHASTA, TEHAMA | 12.5542 | 11.8136 | 2021-08-17 19:45 | 19:45 | 2021-08-18 17:08 | 2021-08-19 11:56 | 11:56 | 1.6743 | 40 | 19 | 11 | 5 | 0 | 1
2021-08-17 | PARADISE 1104 | BUTTE | 93.1529 | 62.6636 | 2021-08-17 19:15 | 19:15 | 2021-08-18 09:29 | 2021-08-18 16:23 | 16:23 | 0.88056 | 21 | 1301 | 1210 | 91 | 130 | 174
2021-08-17 | PARADISE 1105 | BUTTE | 42.5998 | 41.9852 | 2021-08-17 18:28 | 18:28 | 2021-08-18 09:29 | 2021-08-18 14:45 | 14:45 | 0.84514 | 20 | 881 | 802 | 79 | 81 | 212
2021-08-17 | PARADISE 1106 | BUTTE | 4.1896 | 4.1896 | 2021-08-17 18:56 | 18:56 | 2021-08-18 09:29 | 2021-08-18 13:28 | 13:28 | 0.77222 | 19 | 107 | 91 | 16 | 9 | 17
2021-08-17 | PHILO 1101 | MENDOCINO | 26.6928 | 26.6928 | 2021-08-17 19:28 | 19:28 | 2021-08-18 07:58 | 2021-08-18 11:27 | 11:27 | 0.66597 | 16 | 146 | 108 | 23 | 4 | 0
2021-08-17 | PIT NO 7 1101 | SHASTA | 2.8406 | 2.8406 | 2021-08-17 17:57 | 17:57 | 2021-08-18 15:24 | 2021-08-18 21:44 | 21:44 | 1.1576 | 28 | 2 | 1 | 1 | 0 | 0
2021-08-17 | PUEBLO 1104 | NAPA | 32.3168 | 30.8756 | 2021-08-17 18:30 | 18:30 | 2021-08-18 09:29 | 2021-08-18 13:58 | 13:58 | 0.81111 | 19 | 257 | 189 | 49 | 16 | 5
2021-08-17 | PUEBLO 1105 | NAPA | 18.9294 | 12.0181 | 2021-08-17 18:31 | 18:31 | 2021-08-18 09:29 | 2021-08-18 15:01 | 15:01 | 0.85417 | 21 | 117 | 71 | 27 | 5 | 2
2021-08-17 | PUEBLO 2102 | NAPA | 7.9581 | 7.9581 | 2021-08-17 18:21 | 18:21 | 2021-08-18 07:58 | 2021-08-18 18:28 | 18:28 | 1.0049 | 24 | 66 | 51 | 14 | 1 | 2
2021-08-17 | PUEBLO 2103 | NAPA | 30.2009 | 29.9041 | 2021-08-17 18:46 | 18:46 | 2021-08-18 07:58 | 2021-08-18 19:25 | 19:25 | 1.0271 | 25 | 216 | 145 | 38 | 4 | 4
2021-08-17 | PUTAH CREEK 1102 | YOLO, SOLANO | 26.6825 | 22.1282 | 2021-08-17 20:51 | 20:51 | 2021-08-18 14:46 | 2021-08-18 17:29 | 17:29 | 0.85972 | 21 | 159 | 114 | 35 | 7 | 0
2021-08-17 | PUTAH CREEK 1103 | YOLO, SOLANO | 4.9351 | 3.4554 | 2021-08-17 18:29 | 18:29 | 2021-08-18 10:20 | 2021-08-18 15:25 | 15:25 | 0.87222 | 21 | 41 | 35 | 2 | 1 | 0
2021-08-17 | PUTAH CREEK 1105 | YOLO | 2.7957 | 1.0761 | 2021-08-17 18:32 | 18:32 | 2021-08-18 14:46 | 2021-08-18 16:42 | 16:42 | 0.92361 | 22 | 9 | 3 | 5 | 0 | 0
2021-08-17 | RED BLUFF 1101 | TEHAMA | 56.7008 | 47.9242 | 2021-08-17 17:55 | 17:55 | 2021-08-19 05:17 | 2021-08-19 13:05 | 13:05 | 1.7986 | 43 | 685 | 648 | 27 | 73 | 30
2021-08-17 | RED BLUFF 1103 | TEHAMA | 18.6068 | 16.7992 | 2021-08-17 17:40 | 17:40 | 2021-08-18 17:08 | 2021-08-19 16:55 | 16:55 | 1.9688 | 47 | 214 | 199 | 14 | 23 | 0
2021-08-17 | RED BLUFF 1104 | YOLO, TEHAMA | 86.4033 | 65.9541 | 2021-08-17 17:43 | 17:43 | 2021-08-19 05:17 | 2021-08-19 13:00 | 13:00 | 1.8035 | 43 | 865 | 753 | 85 | 76 | 0
2021-08-17 | RED BLUFF 1105 | TEHAMA | 34.8664 | 16.3937 | 2021-08-17 17:29 | 17:29 | 2021-08-19 05:17 | 2021-08-19 11:50 | 11:50 | 1.7646 | 42 | 981 | 918 | 49 | 119 | 0
2021-08-17 | REDBUD 1101 | LAKE | 44.3937 | 29.5059 | 2021-08-17 18:52 | 18:52 | 2021-08-18 12:39 | 2021-08-19 15:10 | 15:10 | 1.8458 | 44 | 560 | 513 | 32 | 54 | 158
2021-08-17 | REDBUD 1102 | LAKE | 5.7306 | 5.1262 | 2021-08-17 18:45 | 18:45 | 2021-08-18 09:29 | 2021-08-18 16:44 | 16:44 | 0.91597 | 22 | 59 | 41 | 13 | 4 | 12
2021-08-17 | RINCON 1101 | SONOMA | 13.8378 | 13.8378 | 2021-08-17 19:21 | 19:21 | 2021-08-18 09:29 | 2021-08-18 16:01 | 16:01 | 0.86111 | 21 | 21 | 14 | 7 | 2 | 0
2021-08-17 | RINCON 1103 | SONOMA | 39.9387 | 39.9387 | 2021-08-17 18:55 | 18:55 | 2021-08-18 09:29 | 2021-08-19 02:31 | 2:31 | 1.3167 | 32 | 281 | 234 | 40 | 12 | 10
2021-08-17 | SILVERADO 2102 | NAPA | 33.9967 | 28.6311 | 2021-08-17 18:38 | 18:38 | 2021-08-18 09:29 | 2021-08-18 14:49 | 14:49 | 0.84097 | 20 | 182 | 112 | 38 | 2 | 1
2021-08-17 | SILVERADO 2103 | SONOMA | 1.6787 | 1.6787 | 2021-08-17 19:41 | 19:41 | 2021-08-18 09:29 | 2021-08-18 16:33 | 16:33 | 0.86944 | 21 | 3 | 0 | 3 | 0 | 0
2021-08-17 | SILVERADO 2104 | NAPA | 133.3296 | 104.5606 | 2021-08-17 18:22 | 18:22 | 2021-08-18 09:29 | 2021-08-18 23:55 | 23:55 | 1.2313 | 30 | 1815 | 1516 | 174 | 93 | 52
2021-08-17 | SONOMA 1103 | SONOMA | 5.9369 | 5.9369 | 2021-08-17 19:19 | 19:19 | 2021-08-18 07:58 | 2021-08-18 12:43 | 12:43 | 0.725 | 17 | 37 | 30 | 3 | 3 | 1
2021-08-17 | SONOMA 1104 | SONOMA | 13.438 | 12.6254 | 2021-08-17 19:27 | 19:27 | 2021-08-18 07:58 | 2021-08-18 13:23 | 13:23 | 0.74722 | 18 | 184 | 162 | 20 | 6 | 3
2021-08-17 | STILLWATER 1101 | SHASTA | 36.355 | 35.8345 | 2021-08-17 18:56 | 18:56 | 2021-08-18 17:08 | 2021-08-19 11:59 | 11:59 | 1.7104 | 41 | 706 | 601 | 99 | 57 | 186
2021-08-17 | STILLWATER 1102 | SHASTA | 102.9508 | 101.1686 | 2021-08-17 18:27 | 18:27 | 2021-08-18 17:08 | 2021-08-19 17:13 | 17:13 | 1.9486 | 47 | 1384 | 1338 | 46 | 117 | 325
2021-08-17 | TYLER 1105 | TEHAMA | 95.5095 | 60.3771 | 2021-08-17 18:22 | 18:22 | 2021-08-18 17:08 | 2021-08-19 08:05 | 8:05 | 1.5715 | 38 | 765 | 653 | 70 | 73 | 40
2021-08-17 | VACA DIXON 1105 | SOLANO | 37.4106 | 25.142 | 2021-08-17 18:26 | 18:26 | 2021-08-18 10:20 | 2021-08-18 16:36 | 16:36 | 0.92361 | 22 | 384 | 336 | 41 | 40 | 0
2021-08-17 | VACAVILLE 1104 | SOLANO | 2.3915 | 2.3915 | 2021-08-17 20:36 | 20:36 | 2021-08-18 09:29 | 2021-08-18 14:45 | 14:45 | 0.75625 | 18 | 25 | 24 | 1 | 2 | 3
2021-08-17 | VACAVILLE 1108 | SOLANO | 45.73 | 30.5294 | 2021-08-17 18:28 | 18:28 | 2021-08-18 10:20 | 2021-08-19 09:36 | 9:36 | 1.6306 | 39 | 295 | 212 | 63 | 18 | 10
2021-08-17 | VOLTA 1101 | SHASTA, TEHAMA | 183.1986 | 178.9999 | 2021-08-17 18:20 | 18:20 | 2021-08-19 05:17 | 2021-08-19 16:28 | 16:28 | 1.9222 | 46 | 1126 | 927 | 165 | 69 | 138
2021-08-17 | VOLTA 1102 | SHASTA | 172.2933 | 166.0613 | 2021-08-17 18:23 | 18:23 | 2021-08-19 05:17 | 2021-08-19 18:27 | 18:27 | 2.0028 | 48 | 2584 | 2393 | 180 | 242 | 231
2021-08-17 | WHITMORE 1101 | SHASTA | 55.896 | 52.0286 | 2021-08-17 18:43 | 18:43 | 2021-08-18 09:29 | 2021-08-18 19:00 | 19:00 | 1.0118 | 24 | 271 | 241 | 25 | 19 | 24
2021-08-17 | WILDWOOD 1101 | SHASTA, TEHAMA | 3.7959 | 3.7959 | 2021-08-17 17:44 | 17:44 | 2021-08-18 09:29 | 2021-08-18 21:45 | 21:45 | 1.1674 | 28 | 6 | 3 | 3 | 0 | 1
2021-09-20 | ARBUCKLE 1101 | COLUSA | 0.61589 | 0 | 2021-09-20 06:05 | 6:05 | 2021-09-20 13:52 | 2021-09-20 15:45 | 15:45 | 0.40278 | 10 | 3 | 2 | 0 | 0 | 0
2021-09-20 | ARBUCKLE 1104 | YOLO, COLUSA | 4.9265 | 1.9232 | 2021-09-20 06:09 | 6:09 | 2021-09-20 13:52 | 2021-09-20 15:51 | 15:51 | 0.40417 | 10 | 13 | 9 | 3 | 0 | 1
2021-09-20 | CORNING 1101 | TEHAMA | 56.1996 | 49.8845 | 2021-09-20 06:10 | 6:10 | 2021-09-20 14:34 | 2021-09-21 00:45 | 0:45 | 0.77431 | 19 | 841 | 773 | 65 | 103 | 57
2021-09-20 | CORNING 1102 | TEHAMA | 83.3634 | 79.8807 | 2021-09-20 06:18 | 6:18 | 2021-09-20 14:34 | 2021-09-20 19:13 | 19:13 | 0.53819 | 13 | 291 | 230 | 51 | 15 | 3
2021-09-20 | CORTINA 1101 | COLUSA | 3.7971 | 1.3221 | 2021-09-20 06:11 | 6:11 | 2021-09-20 13:52 | 2021-09-20 16:12 | 16:12 | 0.41736 | 10 | 8 | 4 | 4 | 1 | 0
2021-09-20 | GLENN 1101 | GLENN | 2.5728 | 0.26324 | 2021-09-20 06:33 | 6:33 | 2021-09-20 14:34 | 2021-09-20 16:54 | 16:54 | 0.43125 | 10 | 5 | 3 | 1 | 0 | 0
2021-09-20 | HIGHLANDS 1103 | LAKE | 17.7595 | 17.1309 | 2021-09-20 06:08 | 6:08 | 2021-09-20 16:11 | 2021-09-20 17:49 | 17:49 | 0.48681 | 12 | 51 | 36 | 11 | 3 | 0
2021-09-20 | MADISON 2101 | YOLO | 3.761 | 2.389 | 2021-09-20 06:13 | 6:13 | 2021-09-20 13:52 | 2021-09-20 15:33 | 15:33 | 0.38889 | 9 | 10 | 0 | 10 | 0 | 0
2021-09-20 | MAXWELL 1105 | COLUSA | 15.2749 | 3.8977 | 2021-09-20 06:14 | 6:14 | 2021-09-20 16:11 | 2021-09-20 17:59 | 17:59 | 0.48958 | 12 | 44 | 29 | 9 | 1 | 0
2021-09-20 | MONTICELLO 1101 | NAPA | 3.9076 | 3.9076 | 2021-09-20 06:40 | 6:40 | 2021-09-20 12:25 | 2021-09-20 14:23 | 14:23 | 0.32153 | 8 | 8 | 0 | 7 | 0 | 0
2021-09-20 | PUTAH CREEK 1105 | YOLO | 2.7957 | 1.0761 | 2021-09-20 06:16 | 6:16 | 2021-09-20 13:52 | 2021-09-20 15:17 | 15:17 | 0.37569 | 9 | 9 | 3 | 5 | 0 | 0
2021-09-20 | SCE TEHACHAPI 1101 | KERN | 1.1708 | 1.1708 | 2021-09-21 01:09 | 1:09 | 2021-09-21 11:13 | 2021-09-21 16:06 | 16:06 | 0.62292 | 15 | 3 | 2 | 1 | 0 | 1
2021-09-20 | TEJON 1102 | KERN | 39.2317 | 38.4629 | 2021-09-20 22:25 | 22:25 | 2021-09-21 14:36 | 2021-09-21 16:46 | 16:46 | 0.76458 | 18 | 598 | 482 | 103 | 34 | 14
2021-09-20 | TYLER 1105 | TEHAMA | 50.962 | 48.8093 | 2021-09-20 06:20 | 6:20 | 2021-09-20 14:34 | 2021-09-20 16:42 | 16:42 | 0.43194 | 10 | 237 | 177 | 34 | 15 | 4
2021-09-20 | VACAVILLE 1104 | SOLANO | 22.6984 | 18.0372 | 2021-09-20 06:56 | 6:56 | 2021-09-20 12:25 | 2021-09-20 15:38 | 15:38 | 0.3625 | 9 | 802 | 716 | 76 | 62 | 8
2021-09-20 | VACAVILLE 1108 | SOLANO | 15.0316 | 14.2952 | 2021-09-20 06:18 | 6:18 | 2021-09-20 12:25 | 2021-09-20 14:52 | 14:52 | 0.35694 | 9 | 45 | 17 | 25 | 0 | 0
2021-10-11 | ANDERSON 1103 | SHASTA | 7.7422 | 2.8231 | 2021-10-11 06:20 | 6:20 | 2021-10-11 17:45 | 2021-10-12 09:18 | 9:18 | 1.1236 | 27 | 68 | 63 | 2 | 7 | 25
2021-10-11 | ANTELOPE 1101 | KERN | 3.0685 | 0.91782 | 2021-10-11 07:22 | 7:22 | 2021-10-12 10:23 | 2021-10-12 12:24 | 12:24 | 1.2097 | 29 | 7 | 1 | 6 | 0 | 0
2021-10-11 | ARBUCKLE 1101 | COLUSA | 0.61589 | 0 | 2021-10-11 06:51 | 6:51 | 2021-10-12 12:20 | 2021-10-12 15:06 | 15:06 | 1.3438 | 32 | 3 | 2 | 0 | 0 | 0
2021-10-11 | ARBUCKLE 1104 | YOLO, COLUSA | 3.2838 | 1.9232 | 2021-10-11 07:01 | 7:01 | 2021-10-12 12:20 | 2021-10-12 15:40 | 15:40 | 1.3604 | 33 | 12 | 8 | 3 | 0 | 1
2021-10-11 | AVENAL 2101 | KINGS | 3.0517 | 0 | 2021-10-11 07:35 | 7:35 | 2021-10-12 10:23 | 2021-10-12 17:46 | 17:46 | 1.4243 | 34 | 4 | 0 | 4 | 0 | 0
2021-10-11 | BIG BEND 1101 | BUTTE | 58.5528 | 58.1123 | 2021-10-11 04:02 | 4:02 | 2021-10-12 07:22 | 2021-10-12 11:28 | 11:28 | 1.3097 | 31 | 264 | 238 | 24 | 17 | 93
2021-10-11 | BRENTWOOD 2105 | CONTRA COSTA | 16.5248 | 12.4375 | 2021-10-11 09:11 | 9:11 | 2021-10-12 12:53 | 2021-10-12 17:26 | 17:26 | 1.3438 | 32 | 73 | 34 | 32 | 3 | 4
2021-10-11 | BUCKS CREEK 1103 | PLUMAS | 26.5331 | 25.1252 | 2021-10-11 04:23 | 4:23 | 2021-10-12 07:22 | 2021-10-12 15:20 | 15:20 | 1.4563 | 35 | 314 | 263 | 51 | 4 | 6
2021-10-11 | CALISTOGA 1101 | NAPA | 17.4706 | 16.765 | 2021-10-11 07:11 | 7:11 | 2021-10-12 12:02 | 2021-10-12 15:56 | 15:56 | 1.3646 | 33 | 88 | 62 | 22 | 0 | 6
2021-10-11 | CALPINE 1144 | SONOMA, LAKE | 31.874 | 31.5233 | 2021-10-11 08:01 | 8:01 | 2021-10-12 12:02 | 2021-10-14 15:22 | 15:22 | 3.3063 | 79 | 15 | 2 | 13 | 0 | 0
2021-10-11 | CALPINE 1146 | SONOMA, LAKE | 5.8295 | 5.8295 | 2021-10-11 08:01 | 8:01 | 2021-10-12 12:02 | 2021-10-14 15:22 | 15:22 | 3.3063 | 79 | 0 | 0 | 0 | 0 | 0
2021-10-11 | CAMBRIA 1102 | SAN LUIS OBISPO | 7.902 | 7.902 | 2021-10-11 12:40 | 12:40 | 2021-10-12 08:53 | 2021-10-12 14:41 | 14:41 | 1.084 | 26 | 28 | 23 | 5 | 0 | 5
2021-10-11 | CANTUA 1103 | FRESNO | 3.883 | 0 | 2021-10-11 07:28 | 7:28 | 2021-10-12 10:23 | 2021-10-12 17:16 | 17:16 | 1.4083 | 34 | 2 | 0 | 2 | 0 | 0
2021-10-11 | CARBONA 1101 | SAN JOAQUIN | 1.3598 | 0 | 2021-10-11 08:46 | 8:46 | 2021-10-12 12:53 | 2021-10-12 14:55 | 14:55 | 1.2563 | 30 | 2 | 0 | 1 | 0 | 0
2021-10-11 | CHOLAME 2102 | MONTEREY, SAN LUIS OBISPO | 19.0125 | 9.4591 | 2021-10-11 07:27 | 7:27 | 2021-10-12 08:53 | 2021-10-12 12:49 | 12:49 | 1.2236 | 29 | 33 | 16 | 15 | 1 | 2
2021-10-11 | CLARK ROAD 1102 | BUTTE | 62.1801 | 57.7791 | 2021-10-11 04:07 | 4:07 | 2021-10-12 07:22 | 2021-10-12 10:58 | 10:58 | 1.2854 | 31 | 480 | 419 | 54 | 50 | 101
2021-10-11 | CLAYTON 2212 | CONTRA COSTA | 50.2878 | 47.4556 | 2021-10-11 08:58 | 8:58 | 2021-10-12 12:53 | 2021-10-12 15:51 | 15:51 | 1.2868 | 31 | 522 | 433 | 84 | 53 | 57
2021-10-11 | CLOVERDALE 1102 | SONOMA | 8.6118 | 8.6118 | 2021-10-11 06:35 | 6:35 | 2021-10-12 07:22 | 2021-10-12 10:52 | 10:52 | 1.1785 | 28 | 38 | 23 | 7 | 1 | 0
2021-10-11 | COALINGA NO 1 1108 | FRESNO | 41.6286 | 0 | 2021-10-11 07:48 | 7:48 | 2021-10-12 10:23 | 2021-10-12 18:31 | 18:31 | 1.4465 | 35 | 77 | 53 | 18 | 3 | 7
2021-10-11 | COALINGA NO 1 1109 | FRESNO | 7.9789 | 0 | 2021-10-11 07:29 | 7:29 | 2021-10-12 10:23 | 2021-10-12 20:08 | 20:08 | 1.5271 | 37 | 6 | 0 | 5 | 0 | 0
2021-10-11 | COALINGA NO 2 1105 | FRESNO | 38.2863 | 0 | 2021-10-11 07:22 | 7:22 | 2021-10-12 10:23 | 2021-10-12 15:58 | 15:58 | 1.3583 | 33 | 87 | 60 | 19 | 3 | 13
2021-10-11 | CORNING 1101 | TEHAMA | 65.3587 | 49.8845 | 2021-10-11 01:40 | 1:40 | 2021-10-11 19:43 | 2021-10-12 12:06 | 12:06 | 1.4347 | 34 | 895 | 807 | 73 | 104 | 439
2021-10-11 | CORNING 1102 | TEHAMA | 83.3634 | 79.8807 | 2021-10-11 01:34 | 1:34 | 2021-10-11 19:43 | 2021-10-12 15:20 | 15:20 | 1.5736 | 38 | 292 | 231 | 51 | 15 | 77
2021-10-11 | CORTINA 1101 | COLUSA | 3.7971 | 1.3221 | 2021-10-11 06:57 | 6:57 | 2021-10-12 12:20 | 2021-10-12 14:49 | 14:49 | 1.3278 | 32 | 8 | 4 | 4 | 1 | 2
2021-10-11 | COTTONWOOD 1103 | SHASTA, TEHAMA | 32.2402 | 21.7665 | 2021-10-11 06:20 | 6:20 | 2021-10-11 19:43 | 2021-10-12 10:40 | 10:40 | 1.1806 | 28 | 683 | 634 | 39 | 62 | 209
2021-10-11 | CRESTA 1101 | BUTTE | 0.040276 | 0.040276 | 2021-10-11 08:48 | 8:48 | 2021-10-12 07:22 | 2021-10-12 13:56 | 13:56 | 1.2139 | 29 | 1 | 0 | 1 | 0 | 0
2021-10-11 | DESCHUTES 1101 | SHASTA | 8.5954 | 8.5954 | 2021-10-11 06:32 | 6:32 | 2021-10-11 17:45 | 2021-10-12 11:40 | 11:40 | 1.2139 | 29 | 74 | 69 | 3 | 4 | 13
2021-10-11 | DESCHUTES 1104 | SHASTA | 11.5057 | 8.5134 | 2021-10-11 06:23 | 6:23 | 2021-10-11 17:45 | 2021-10-12 12:14 | 12:14 | 1.2438 | 30 | 88 | 84 | 4 | 6 | 19
2021-10-11 | DEVILS DEN 1101 | KINGS | 6.9434 | 0 | 2021-10-11 07:31 | 7:31 | 2021-10-12 10:23 | 2021-10-12 18:38 | 18:38 | 1.4632 | 35 | 6 | 1 | 5 | 0 | 0
2021-10-11 | ELK CREEK 1101 | COLUSA, GLENN | 182.5563 | 87.4057 | 2021-10-11 04:21 | 4:21 | 2021-10-12 12:20 | 2021-10-12 17:06 | 17:06 | 1.5312 | 37 | 855 | 695 | 132 | 59 | 207
2021-10-11 | GEYSERVILLE 1102 | SONOMA | 16.985 | 15.5356 | 2021-10-11 06:30 | 6:30 | 2021-10-12 07:22 | 2021-10-12 11:09 | 11:09 | 1.1937 | 29 | 28 | 13 | 12 | 0 | 1
2021-10-11 | GIRVAN 1101 | SHASTA | 113.1464 | 109.202 | 2021-10-11 06:38 | 6:38 | 2021-10-11 16:29 | 2021-10-12 11:32 | 11:32 | 1.2042 | 29 | 1090 | 985 | 101 | 83 | 160
2021-10-11 | GLENN 1101 | GLENN | 2.5728 | 0.26324 | 2021-10-11 04:00 | 4:00 | 2021-10-11 19:43 | 2021-10-12 10:36 | 10:36 | 1.275 | 31 | 5 | 3 | 1 | 0 | 0
2021-10-11 | GUSTINE 1102 | MERCED | 10.2784 | 0 | 2021-10-11 08:27 | 8:27 | 2021-10-12 11:19 | 2021-10-12 13:11 | 13:11 | 1.1972 | 29 | 11 | 4 | 4 | 0 | 0
2021-10-11 | HIGHLANDS 1102 | LAKE | 10.4749 | 10.0306 | 2021-10-11 06:41 | 6:41 | 2021-10-12 07:22 | 2021-10-12 12:54 | 12:54 | 1.259 | 30 | 15 | 12 | 3 | 0 | 3
2021-10-11 | HIGHLANDS 1103 | LAKE | 76.16 | 74.8339 | 2021-10-11 06:31 | 6:31 | 2021-10-12 07:22 | 2021-10-12 11:57 | 11:57 | 1.2264 | 29 | 1032 | 956 | 49 | 83 | 264
2021-10-11 | JESSUP 1102 | SHASTA | 12.4139 | 4.599 | 2021-10-11 06:54 | 6:54 | 2021-10-11 16:29 | 2021-10-11 18:53 | 18:53 | 0.49931 | 12 | 199 | 191 | 7 | 12 | 79
2021-10-11 | JOLON 1102 | MONTEREY | 109.1236 | 67.3038 | 2021-10-11 11:35 | 11:35 | 2021-10-12 07:22 | 2021-10-12 16:32 | 16:32 | 1.2062 | 29 | 583 | 418 | 108 | 22 | 75
2021-10-11 | JOLON 1103 | MONTEREY | 19.0427 | 12.704 | 2021-10-11 11:41 | 11:41 | 2021-10-12 07:22 | 2021-10-12 11:54 | 11:54 | 1.009 | 24 | 18 | 0 | 18 | 0 | 0
2021-10-11 | KANAKA 1101 | BUTTE | 5.1544 | 5.1544 | 2021-10-11 05:15 | 5:15 | 2021-10-12 07:22 | 2021-10-12 10:50 | 10:50 | 1.2326 | 30 | 9 | 7 | 1 | 0 | 2
2021-10-11 | KETTLEMAN HILLS 2104 | FRESNO | 5.0441 | 0 | 2021-10-11 07:25 | 7:25 | 2021-10-12 10:23 | 2021-10-12 15:20 | 15:20 | 1.3299 | 32 | 1 | 0 | 1 | 0 | 0
2021-10-11 | KING CITY 1106 | SAN BENITO, MONTEREY | 11.667 | 0 | 2021-10-11 08:20 | 8:20 | 2021-10-12 07:22 | 2021-10-12 17:48 | 17:48 | 1.3944 | 33 | 23 | 19 | 4 | 0 | 3
2021-10-11 | KONOCTI 1102 | LAKE | 9.9428 | 8.9203 | 2021-10-11 06:21 | 6:21 | 2021-10-11 19:43 | 2021-10-12 10:00 | 10:00 | 1.1521 | 28 | 47 | 40 | 4 | 0 | 14
2021-10-11 | LAMONT 1102 | KERN | 2.629 | 1.3131 | 2021-10-11 12:20 | 12:20 | 2021-10-12 05:38 | 2021-10-12 10:58 | 10:58 | 0.94306 | 23 | 5 | 0 | 5 | 0 | 0
2021-10-11 | LAMONT 1104 | KERN | 1.6865 | 1.0614 | 2021-10-11 12:07 | 12:07 | 2021-10-12 05:38 | 2021-10-12 10:57 | 10:57 | 0.95139 | 23 | 2 | 0 | 1 | 0 | 0
2021-10-11 | LOGAN CREEK 2102 | GLENN | 4.3372 | 3.4777 | 2021-10-11 04:02 | 4:02 | 2021-10-11 17:45 | 2021-10-12 10:09 | 10:09 | 1.2549 | 30 | 8 | 3 | 3 | 0 | 0
2021-10-11 | LONE TREE 2105 | CONTRA COSTA | 10.9377 | 9.1573 | 2021-10-11 08:34 | 8:34 | 2021-10-12 12:53 | 2021-10-12 15:56 | 15:56 | 1.3069 | 31 | 44 | 33 | 9 | 1 | 4
2021-10-11 | LOS MOLINOS 1101 | TEHAMA | 0.24834 | 0.18929 | 2021-10-11 06:44 | 6:44 | 2021-10-11 19:43 | 2021-10-12 10:31 | 10:31 | 1.1576 | 28 | 7 | 7 | 0 | 0 | 0
2021-10-11 | LOS OSITOS 2103 | SAN BENITO, MONTEREY, FRESNO | 44.1508 | 0 | 2021-10-11 07:28 | 7:28 | 2021-10-12 07:22 | 2021-10-12 17:36 | 17:36 | 1.4222 | 34 | 116 | 66 | 31 | 3 | 4
2021-10-11 | MADISON 1105 | YOLO | 6.4895 | 0.35006 | 2021-10-11 06:33 | 6:33 | 2021-10-12 12:20 | 2021-10-12 14:41 | 14:41 | 1.3389 | 32 | 31 | 20 | 7 | 1 | 4
2021-10-11 | MADISON 2101 | YOLO | 31.0104 | 5.1874 | 2021-10-11 07:08 | 7:08 | 2021-10-12 12:20 | 2021-10-12 17:30 | 17:30 | 1.4319 | 34 | 242 | 155 | 37 | 5 | 32
2021-10-11 | MAGUNDEN 1108 | KERN | 3.0379 | 2.8064 | 2021-10-11 12:13 | 12:13 | 2021-10-12 05:38 | 2021-10-12 11:01 | 11:01 | 0.95 | 23 | 11 | 8 | 1 | 0 | 0
2021-10-11 | MAXWELL 1105 | COLUSA | 15.2749 | 3.8977 | 2021-10-11 04:23 | 4:23 | 2021-10-12 12:20 | 2021-10-12 14:43 | 14:43 | 1.4306 | 34 | 44 | 29 | 9 | 1 | 2
2021-10-11 | MIDDLETOWN 1101 | NAPA, SONOMA, LAKE | 50.1896 | 41.544 | 2021-10-11 06:14 | 6:14 | 2021-10-12 12:02 | 2021-10-12 16:55 | 16:55 | 1.4451 | 35 | 487 | 411 | 70 | 23 | 108
2021-10-11 | MIDDLETOWN 1102 | LAKE | 58.0717 | 39.2129 | 2021-10-11 06:20 | 6:20 | 2021-10-12 07:22 | 2021-10-12 14:43 | 14:43 | 1.3493 | 32 | 2301 | 2088 | 201 | 186 | 585
2021-10-11 | MIDDLETOWN 1103 | LAKE | 10.7468 | 8.826 | 2021-10-11 06:28 | 6:28 | 2021-10-12 07:22 | 2021-10-12 14:15 | 14:15 | 1.3243 | 32 | 5 | 3 | 0 | 0 | 0
2021-10-11 | MONTICELLO 1101 | NAPA, SOLANO | 133.6795 | 117.1279 | 2021-10-11 06:17 | 6:17 | 2021-10-12 10:23 | 2021-10-12 16:53 | 16:53 | 1.4417 | 35 | 1133 | 905 | 178 | 70 | 126
2021-10-11 | OILFIELDS 1103 | MONTEREY | 20.285 | 18.2781 | 2021-10-11 12:20 | 12:20 | 2021-10-12 07:22 | 2021-10-12 12:05 | 12:05 | 0.98958 | 24 | 177 | 132 | 42 | 9 | 40
2021-10-11 | PANOCHE 1103 | SAN BENITO | 25.4096 | 7.1082 | 2021-10-11 07:46 | 7:46 | 2021-10-12 10:23 | 2021-10-12 14:30 | 14:30 | 1.2806 | 31 | 31 | 8 | 21 | 0 | 1
2021-10-11 | PANORAMA 1101 | SHASTA, TEHAMA | 11.374 | 10.4459 | 2021-10-11 06:56 | 6:56 | 2021-10-11 17:45 | 2021-10-12 10:51 | 10:51 | 1.1632 | 28 | 791 | 777 | 14 | 95 | 294
2021-10-11 | PANORAMA 1102 | SHASTA, TEHAMA | 33.7056 | 28.0857 | 2021-10-11 06:23 | 6:23 | 2021-10-11 17:45 | 2021-10-12 11:41 | 11:41 | 1.2208 | 29 | 120 | 92 | 16 | 8 | 23
2021-10-11 | PERRY 1101 | SAN LUIS OBISPO | 25.5064 | 22.2431 | 2021-10-11 11:48 | 11:48 | 2021-10-12 08:53 | 2021-10-12 12:27 | 12:27 | 1.0271 | 25 | 58 | 43 | 13 | 0 | 3
2021-10-11 | PUEBLO 1104 | NAPA | 6.1095 | 6.1095 | 2021-10-11 06:29 | 6:29 | 2021-10-12 10:23 | 2021-10-12 12:31 | 12:31 | 1.2514 | 30 | 37 | 24 | 7 | 3 | 1
2021-10-11 | PUEBLO 1105 | NAPA | 18.9292 | 12.0179 | 2021-10-11 07:09 | 7:09 | 2021-10-12 10:23 | 2021-10-12 13:29 | 13:29 | 1.2639 | 30 | 117 | 71 | 27 | 4 | 7
2021-10-11 | PUTAH CREEK 1102 | YOLO, SOLANO | 40.7016 | 27.2485 | 2021-10-11 07:39 | 7:39 | 2021-10-12 12:20 | 2021-10-12 18:35 | 18:35 | 1.4556 | 35 | 272 | 185 | 55 | 9 | 18
2021-10-11 | PUTAH CREEK 1103 | YOLO, SOLANO | 5.8592 | 3.7611 | 2021-10-11 07:11 | 7:11 | 2021-10-12 12:20 | 2021-10-12 17:36 | 17:36 | 1.434 | 34 | 57 | 50 | 3 | 3 | 4
2021-10-11 | PUTAH CREEK 1105 | YOLO | 7.6367 | 1.7799 | 2021-10-11 06:47 | 6:47 | 2021-10-12 12:20 | 2021-10-12 17:56 | 17:56 | 1.4646 | 35 | 36 | 19 | 8 | 4 | 1
2021-10-11 | RED BLUFF 1101 | TEHAMA | 72.656 | 47.9218 | 2021-10-11 06:33 | 6:33 | 2021-10-11 19:43 | 2021-10-12 11:37 | 11:37 | 1.2111 | 29 | 1014 | 940 | 64 | 100 | 293
2021-10-11 | RED BLUFF 1103 | TEHAMA | 18.6068 | 16.7992 | 2021-10-11 01:39 | 1:39 | 2021-10-11 19:43 | 2021-10-12 16:54 | 16:54 | 1.6354 | 39 | 214 | 199 | 14 | 22 | 44
2021-10-11 | RED BLUFF 1104 | YOLO, TEHAMA | 86.4033 | 65.9541 | 2021-10-11 06:43 | 6:43 | 2021-10-11 19:43 | 2021-10-12 13:44 | 13:44 | 1.2924 | 31 | 865 | 753 | 85 | 77 | 241
2021-10-11 | REDBUD 1101 | LAKE | 6.9568 | 5.7941 | 2021-10-11 06:18 | 6:18 | 2021-10-12 07:22 | 2021-10-12 12:53 | 12:53 | 1.2743 | 31 | 124 | 119 | 5 | 12 | 49
2021-10-11 | SAN ARDO 1102 | MONTEREY, SAN LUIS OBISPO | 10.2134 | 0 | 2021-10-11 07:34 | 7:34 | 2021-10-12 10:23 | 2021-10-12 16:33 | 16:33 | 1.3743 | 33 | 24 | 13 | 10 | 0 | 0
2021-10-11 | SAN MIGUEL 1106 | MONTEREY, SAN LUIS OBISPO | 18.2512 | 14.5917 | 2021-10-11 11:35 | 11:35 | 2021-10-12 07:22 | 2021-10-12 13:21 | 13:21 | 1.0736 | 26 | 56 | 28 | 10 | 1 | 1
2021-10-11 | SANTA NELLA 1104 | MERCED | 2.3166 | 0 | 2021-10-11 08:34 | 8:34 | 2021-10-12 11:19 | 2021-10-12 13:13 | 13:13 | 1.1937 | 29 | 3 | 0 | 1 | 0 | 0
2021-10-11 | SILVERADO 2102 | NAPA | 60.4272 | 52.5397 | 2021-10-11 06:27 | 6:27 | 2021-10-12 10:23 | 2021-10-12 16:43 | 16:43 | 1.4278 | 34 | 335 | 191 | 76 | 3 | 9
2021-10-11 | SILVERADO 2104 | NAPA | 100.7555 | 71.9622 | 2021-10-11 07:20 | 7:20 | 2021-10-12 10:23 | 2021-10-12 19:13 | 19:13 | 1.4951 | 36 | 774 | 583 | 101 | 33 | 108
2021-10-11 | SISQUOC 1102 | SAN LUIS OBISPO, SANTA BARBARA | 5.5301 | 5.5301 | 2021-10-11 18:04 | 18:04 | 2021-10-12 09:24 | 2021-10-12 13:37 | 13:37 | 0.81458 | 20 | 10 | 6 | 3 | 2 | 0
2021-10-11 | SYCAMORE CREEK 1111 | BUTTE | 55.6961 | 52.9038 | 2021-10-11 04:06 | 4:06 | 2021-10-12 04:13 | 2021-10-12 14:24 | 14:24 | 1.4292 | 34 | 580 | 514 | 57 | 31 | 138
2021-10-11 | TASSAJARA 2104 | ALAMEDA | 2.3725 | 2.2662 | 2021-10-11 08:38 | 8:38 | 2021-10-12 12:53 | 2021-10-12 14:34 | 14:34 | 1.2472 | 30 | 13 | 10 | 3 | 0 | 0
2021-10-11 | TASSAJARA 2112 | CONTRA COSTA | 6.9626 | 6.9626 | 2021-10-11 08:49 | 8:49 | 2021-10-12 12:53 | 2021-10-12 15:15 | 15:15 | 1.2681 | 30 | 25 | 13 | 12 | 1 | 3
2021-10-11 | TEJON 1102 | KERN | 39.2434 | 38.4628 | 2021-10-11 12:41 | 12:41 | 2021-10-12 08:53 | 2021-10-13 01:45 | 1:45 | 1.5444 | 37 | 595 | 479 | 103 | 34 | 160
2021-10-11 | TEJON 1103 | KERN | 6.2382 | 2.9635 | 2021-10-11 12:31 | 12:31 | 2021-10-12 05:38 | 2021-10-12 10:50 | 10:50 | 0.92986 | 22 | 15 | 4 | 10 | 0 | 0
2021-10-11 | TEMPLETON 2110 | SAN LUIS OBISPO | 8.0266 | 8.0266 | 2021-10-11 11:44 | 11:44 | 2021-10-12 08:53 | 2021-10-12 14:33 | 14:33 | 1.1174 | 27 | 39 | 28 | 5 | 0 | 5
2021-10-11 | TEMPLETON 2113 | SAN LUIS OBISPO | 22.2627 | 21.8839 | 2021-10-11 16:10 | 16:10 | 2021-10-12 04:13 | 2021-10-12 10:36 | 10:36 | 0.76806 | 18 | 37 | 24 | 7 | 1 | 3
2021-10-11 | TYLER 1105 | TEHAMA | 95.5017 | 60.3631 | 2021-10-11 01:36 | 1:36 | 2021-10-11 19:43 | 2021-10-12 10:14 | 10:14 | 1.3597 | 33 | 766 | 655 | 69 | 77 | 200
2021-10-11 | VACA DIXON 1101 | SOLANO | 0.78749 | 0.78749 | 2021-10-11 07:01 | 7:01 | 2021-10-12 12:20 | 2021-10-12 14:58 | 14:58 | 1.3313 | 32 | 6 | 4 | 2 | 0 | 0
2021-10-11 | VACA DIXON 1105 | SOLANO | 4.3452 | 1.3989 | 2021-10-11 07:33 | 7:33 | 2021-10-12 12:20 | 2021-10-12 14:31 | 14:31 | 1.2903 | 31 | 61 | 54 | 3 | 6 | 5
2021-10-11 | VACAVILLE 1104 | SOLANO | 17.7524 | 16.7758 | 2021-10-11 06:58 | 6:58 | 2021-10-11 18:51 | 2021-10-12 15:49 | 15:49 | 1.3688 | 33 | 302 | 250 | 41 | 22 | 49
2021-10-11 | VACAVILLE 1108 | SOLANO | 46.5805 | 30.656 | 2021-10-11 07:05 | 7:05 | 2021-10-12 12:20 | 2021-10-12 17:01 | 17:01 | 1.4139 | 34 | 374 | 284 | 70 | 25 | 24
2021-10-11 | VACAVILLE 1111 | SOLANO | 28.9624 | 13.6852 | 2021-10-11 06:55 | 6:55 | 2021-10-12 12:20 | 2021-10-12 17:07 | 17:07 | 1.425 | 34 | 1951 | 1869 | 77 | 215 | 394
2021-10-11 | VACAVILLE 1112 | SOLANO | 2.1346 | 0.20758 | 2021-10-11 06:53 | 6:53 | 2021-10-12 12:20 | 2021-10-12 14:28 | 14:28 | 1.316 | 32 | 316 | 315 | 1 | 20 | 138
2021-10-11 | VASCO 1102 | ALAMEDA | 38.6461 | 33.6476 | 2021-10-11 09:19 | 9:19 | 2021-10-12 12:53 | 2021-10-12 16:50 | 16:50 | 1.3132 | 32 | 134 | 90 | 39 | 10 | 10
2021-10-11 | VOLTA 1101 | TEHAMA | 54.4724 | 54.4724 | 2021-10-11 06:36 | 6:36 | 2021-10-12 00:13 | 2021-10-12 13:42 | 13:42 | 1.2958 | 31 | 604 | 530 | 71 | 27 | 33
2021-10-11 | WESTLEY 1103 | STANISLAUS | 16.6587 | 0.42602 | 2021-10-11 08:42 | 8:42 | 2021-10-12 12:53 | 2021-10-12 14:37 | 14:37 | 1.2465 | 30 | 30 | 4 | 24 | 0 | 0
2021-10-11 | ZACA 1102 | SANTA BARBARA | 5.5908 | 5.5908 | 2021-10-11 18:00 | 18:00 | 2021-10-12 10:23 | 2021-10-12 14:18 | 14:18 | 0.84583 | 20 | 19 | 14 | 5 | 1 | 1
2021-10-14 | CAL WATER 1102 | KERN | 4.2754 | 3.7443 | 2021-10-15 01:00 | 1:00 | 2021-10-15 12:00 | 2021-10-15 15:38 | 15:38 | 0.60972 | 15 | 13 | 0 | 10 | 0 | 0
2021-10-14 | LAMONT 1104 | KERN | 1.6857 | 1.0606 | 2021-10-15 01:09 | 1:09 | 2021-10-15 12:00 | 2021-10-15 15:10 | 15:10 | 0.58403 | 14 | 2 | 0 | 1 | 0 | 0
2021-10-14 | MAGUNDEN 1108 | KERN | 8.133 | 3.9811 | 2021-10-15 01:05 | 1:05 | 2021-10-15 12:00 | 2021-10-15 15:12 | 15:12 | 0.58819 | 14 | 38 | 20 | 9 | 0 | 1
2021-10-14 | SCE TEHACHAPI 1101 | KERN | 1.1708 | 1.1708 | 2021-10-15 01:16 | 1:16 | 2021-10-15 12:00 | 2021-10-15 14:26 | 14:26 | 0.54861 | 13 | 3 | 2 | 1 | 0 | 2
2021-10-14 | TEJON 1102 | KERN | 39.196 | 38.4155 | 2021-10-15 01:07 | 1:07 | 2021-10-16 15:14 | 2021-10-16 16:32 | 16:32 | 1.6424 | 39 | 595 | 479 | 103 | 34 | 161
2021-10-14 | TEJON 1103 | KERN | 6.2382 | 2.9635 | 2021-10-15 01:00 | 1:00 | 2021-10-15 12:00 | 2021-10-15 14:46 | 14:46 | 0.57361 | 14 | 15 | 4 | 10 | 0 | 0
[1] De-energized portion only included in the Line Mile of Circuit column
[2] All circuits with Line miles of circuit in HFTD Tiers 2 and 3 equal to zero cross HFRA areas.
[3] Consistent with PG&E’s ESRB-8 PSPS post-event reports submitted to the CPUC, PG&E has included the earliest customer outage start time as a reflection of the outage time of the circuits listed. Note: this may not be representative of what all customers on the circuits listed experienced.
[4] Consistent with PG&E’s ESRB-8 PSPS post-event reports submitted to the CPUC, we have included the restoration time of the last customer restored as a reflection of the outage restoration time for the circuits listed. Note: this may not be representative of what all customers on the circuits listed experienced.
[5] "AFN other than MBL customers de-energized" rows marked N/A for the Jan 2021 event indicate the information was not tracked.

## 11.Transmission
LIST EACH EVENT FOR WHICH A LINE WAS DE-ENERGIZED FOR EACH COUNTY
Event Name | Transmission Line | Voltage | County or Tribe | Line miles of Tx de-energized* | Line miles of Tx de-energized in HFTD Tiers 2 and 3 | Date De-energized[2] | Time De-energized (24-hr. clock)[2] | “All Clear” declaration date/time | Date Re-energized[3] | Time Re-energized (24-hr. clock)[3] | Total Days De-energized (fractions in tenths) | Total Hours De-energized (Integer) | Number of Distribution Lines Impacted | Total customers de-energized | Residential customers de-energized | Commercial/Industrial customers de-energized | Medical Baseline (MBL) customers de-energized | AFN other than MBL customers de-energized | PG&E remarks
2021-08-17 | FULTON-CALISTOGA | 60 | Lake, Napa, Sonoma | 61.74 | 54.64 | 2021-08-17 18:31 | 18:31 | 8/18/2021 13:10 PM | 8/18/2021 16:29 Line segment between Calistoga and Middletown Remained De-energized for Planned Project Work | 16:29 | 0.9 | 22 | 0 | 0 | 0 | 0 | 0 | 0
2021-08-17 | LOWER LAKE-HOMESTAKE | 115 | Lake, Napa | 16.2 | 15.36 | 2021-08-17 18:32 | 18:32 | 2021-08-18 13:20 | 2021-08-19 13:31 | 13:31 | 1.791 | 43 | 0 | 1 | 0 | 1 | 0 | 0 | Note on "Total customers de-energized" (column O) for the Lower Lake-Homestake transmission line: PG&E defines Transmission level customers as customers being served by 60 kV assets or higher. The customer impacted in this event was not under CAISO Control, thus would not meet the definition of a Transmission Customer per D. 21.06.034.
2021-08-17 | ROCK CREEK-POE | 230 | Butte, Plumas | 26.98 | 26.98 | 2021-08-17 18:38 | 18:38 | 2021-08-19 05:17 | 2021-08-19 12:48 | 12:48 | 1.7569 | 42 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-11 | SILVERADO-FULTON JCT | 115 | Napa, Yolo | 26.16 | 21.87 | 2021-10-11 06:58 | 6:58 | 2021-10-12 12:20 | 2021-10-12 15:16 | 15:16 | 1.3458 | 32 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-11 | BUCKS CREEK-ROCK CREEK-CRESTA | 230 | Butte, Plumas | 9.37 | 9.37 | 2021-10-11 06:54 | 6:54 | 2021-10-12 07:22 | 2021-10-12 10:16 | 10:16 | 1.1403 | 27 | 0 | 0 | 0 | 0 | 0 | 0
2021-10-11 | ELK CREEK TAP | 60 | Glenn | 20.01 | 3.58 | 2021-10-11 06:57 | 6:57 | 2021-10-11 17:45 | 2021-10-12 09:13 | 9:13 | 1.0944 | 26 | 0 | 0 | 0 | 0 | 0 | 0
[1] De-energized portion only
[2] Consistent with PG&E’s ESRB-8 PSPS post-event reports submitted to the CPUC, PG&E has included the earliest customer outage start time as a reflection of the outage time of the circuits listed. Note: this may not be representative of what all customers on the circuits listed experienced.
[3] Consistent with PG&E’s ESRB-8 PSPS post-event reports submitted to the CPUC, we have included the restoration time of the last customer restored as a reflection of the outage restoration time for the circuits listed. Note: this may not be representative of what all customers on the circuits listed experienced.

## 12.Counties
LIST EACH EVENT FOR WHICH A COUNTY WAS DE-ENERGIZED
Event Name | County | Number of Customers De-energized | Beginning Date De-energized{1} | Beginning Time De-energized (24-hr. clock)[1] | Ending Date Re-energized[2] | Ending Time Re-energized (24-hr. clock)[2] | Total Maximum Days De-energized (fractions in tenths) | Total Maximum Hours De-energized (Integer) | PG&E remarks
2021-01-18 | FRESNO | 1816 | 2021-01-19 01:06 | 44215.0458 | 2021-01-20 16:47 | 44216.6993 | 1.6535 | 39.6833
2021-01-18 | KERN | 23 | 2021-01-19 02:36 | 44215.1083 | 2021-01-20 09:17 | 44216.3866 | 1.2782 | 30.6775
2021-01-18 | MADERA | 287 | 2021-01-18 23:02 | 44214.9597 | 2021-01-23 18:56 | 44219.7889 | 4.8292 | 115.9
2021-01-18 | MARIPOSA | 2097 | 2021-01-18 23:46 | 44214.9903 | 2021-01-26 16:50 | 44222.7014 | 7.7111 | 185.0667
2021-01-18 | SAN LUIS OBISPO | 154 | 2021-01-19 08:10 | 44215.3403 | 2021-01-20 10:50 | 44216.4514 | 1.1111 | 26.6667
2021-01-18 | SANTA BARBARA | 287 | 2021-01-19 08:06 | 44215.3375 | 2021-01-20 09:44 | 44216.4056 | 1.0681 | 25.6333
2021-01-18 | TULARE | 435 | 2021-01-19 05:43 | 44215.2382 | 2021-01-20 16:41 | 44216.6951 | 1.4569 | 34.9667
2021-08-17 | BUTTE | 6567 | 2021-08-17 18:28 | 44425.7694 | 2021-08-19 12:34 | 44427.5236 | 1.7542 | 42.1
2021-08-17 | COLUSA | 567 | 2021-08-17 12:51 | 44425.5354 | 2021-08-19 12:22 | 44427.5153 | 1.9799 | 47.5167
2021-08-17 | GLENN | 368 | 2021-08-17 12:51 | 44425.5354 | 2021-08-19 12:22 | 44427.5153 | 1.9799 | 47.5167
2021-08-17 | LAKE | 4562 | 2021-08-17 18:45 | 44425.7812 | 2021-08-19 15:31 | 44427.6465 | 1.8653 | 44.7667
2021-08-17 | LASSEN | 54 | 2021-08-17 17:46 | 44425.7403 | 2021-08-18 12:30 | 44426.5208 | 0.78056 | 18.7333
2021-08-17 | MENDOCINO | 149 | 2021-08-17 19:28 | 44425.8111 | 2021-08-18 17:39 | 44426.7354 | 0.92431 | 22.1833
2021-08-17 | NAPA | 7122 | 2021-08-17 18:21 | 44425.7646 | 2021-08-19 12:13 | 44427.509 | 1.7444 | 41.8667
2021-08-17 | PLUMAS | 408 | 2021-08-17 18:52 | 44425.7861 | 2021-08-20 10:30 | 44428.4375 | 2.6514 | 63.6333
2021-08-17 | SHASTA | 15788 | 2021-08-17 17:24 | 44425.725 | 2021-08-19 18:27 | 44427.7688 | 2.0438 | 49.05
2021-08-17 | SOLANO | 1089 | 2021-08-17 18:26 | 44425.7681 | 2021-08-19 09:36 | 44427.4 | 1.6319 | 39.1667
2021-08-17 | SONOMA | 1610 | 2021-08-17 18:41 | 44425.7785 | 2021-08-19 12:13 | 44427.509 | 1.7306 | 41.5333
2021-08-17 | TEHAMA | 9463 | 2021-08-17 17:29 | 44425.7285 | 2021-08-19 16:55 | 44427.7049 | 1.9764 | 47.4333
2021-08-17 | YOLO | 407 | 2021-08-17 17:47 | 44425.741 | 2021-08-19 13:00 | 44427.5417 | 1.8007 | 43.2167
2021-09-20 | COLUSA | 67 | 2021-09-20 06:05 | 44459.2535 | 2021-09-20 17:59 | 44459.7493 | 0.49583 | 11.9
2021-09-20 | GLENN | 5 | 2021-09-20 06:33 | 44459.2729 | 2021-09-20 16:54 | 44459.7042 | 0.43125 | 10.35
2021-09-20 | KERN | 601 | 2021-09-20 22:25 | 44459.934 | 2021-09-21 16:46 | 44460.6986 | 0.76458 | 18.35
2021-09-20 | LAKE | 51 | 2021-09-20 06:08 | 44459.2556 | 2021-09-20 17:49 | 44459.7424 | 0.48681 | 11.6833
2021-09-20 | NAPA | 8 | 2021-09-20 06:40 | 44459.2778 | 2021-09-20 14:23 | 44459.5993 | 0.32153 | 7.7167
2021-09-20 | SOLANO | 847 | 2021-09-20 06:18 | 44459.2625 | 2021-09-20 15:38 | 44459.6514 | 0.38889 | 9.3333
2021-09-20 | TEHAMA | 1369 | 2021-09-20 06:10 | 44459.2569 | 2021-09-21 00:45 | 44460.0312 | 0.77431 | 18.5833
2021-09-20 | YOLO | 20 | 2021-09-20 06:09 | 44459.2562 | 2021-09-20 15:51 | 44459.6604 | 0.40417 | 9.7
2021-10-11 | ALAMEDA | 147 | 2021-10-11 08:38 | 44480.3597 | 2021-10-12 16:50 | 44481.7014 | 1.3417 | 32.2
2021-10-11 | BUTTE | 1334 | 2021-10-11 04:02 | 44480.1681 | 2021-10-12 14:24 | 44481.6 | 1.4319 | 34.3667
2021-10-11 | COLUSA | 565 | 2021-10-11 04:23 | 44480.1826 | 2021-10-12 17:06 | 44481.7125 | 1.5299 | 36.7167
2021-10-11 | CONTRA COSTA | 664 | 2021-10-11 08:34 | 44480.3569 | 2021-10-12 17:26 | 44481.7264 | 1.3694 | 32.8667
2021-10-11 | FRESNO | 189 | 2021-10-11 07:22 | 44480.3069 | 2021-10-12 20:08 | 44481.8389 | 1.5319 | 36.7667
2021-10-11 | GLENN | 369 | 2021-10-11 04:00 | 44480.1667 | 2021-10-12 17:06 | 44481.7125 | 1.5458 | 37.1
2021-10-11 | KERN | 635 | 2021-10-11 07:22 | 44480.3069 | 2021-10-13 01:45 | 44482.0729 | 1.766 | 42.3833
2021-10-11 | KINGS | 10 | 2021-10-11 07:31 | 44480.3132 | 2021-10-12 18:38 | 44481.7764 | 1.4632 | 35.1167
2021-10-11 | LAKE | 4005 | 2021-10-11 06:14 | 44480.2597 | 2021-10-14 15:22 | 44483.6403 | 3.3806 | 81.1333
2021-10-11 | MERCED | 14 | 2021-10-11 08:27 | 44480.3521 | 2021-10-12 13:13 | 44481.5507 | 1.1986 | 28.7667
2021-10-11 | MONTEREY | 896 | 2021-10-11 07:27 | 44480.3104 | 2021-10-12 17:48 | 44481.7417 | 1.4313 | 34.35
2021-10-11 | NAPA | 2449 | 2021-10-11 06:15 | 44480.2604 | 2021-10-12 19:13 | 44481.8007 | 1.5403 | 36.9667
2021-10-11 | PLUMAS | 314 | 2021-10-11 04:23 | 44480.1826 | 2021-10-12 15:20 | 44481.6389 | 1.4563 | 34.95
2021-10-11 | SAN BENITO | 82 | 2021-10-11 07:28 | 44480.3111 | 2021-10-12 17:36 | 44481.7333 | 1.4222 | 34.1333
2021-10-11 | SAN JOAQUIN | 2 | 2021-10-11 08:46 | 44480.3653 | 2021-10-12 14:55 | 44481.6215 | 1.2563 | 30.15
2021-10-11 | SAN LUIS OBISPO | 231 | 2021-10-11 07:27 | 44480.3104 | 2021-10-12 16:33 | 44481.6896 | 1.3792 | 33.1
2021-10-11 | SANTA BARBARA | 27 | 2021-10-11 18:00 | 44480.75 | 2021-10-12 14:18 | 44481.5958 | 0.84583 | 20.3
2021-10-11 | SHASTA | 1639 | 2021-10-11 06:20 | 44480.2639 | 2021-10-12 12:14 | 44481.5097 | 1.2458 | 29.9
2021-10-11 | SOLANO | 3146 | 2021-10-11 06:27 | 44480.2688 | 2021-10-12 18:35 | 44481.7743 | 1.5056 | 36.1333
2021-10-11 | SONOMA | 77 | 2021-10-11 06:15 | 44480.2604 | 2021-10-14 15:22 | 44483.6403 | 3.3799 | 81.1167
2021-10-11 | STANISLAUS | 30 | 2021-10-11 08:42 | 44480.3625 | 2021-10-12 14:37 | 44481.609 | 1.2465 | 29.9167
2021-10-11 | TEHAMA | 6130 | 2021-10-11 01:34 | 44480.0653 | 2021-10-12 16:54 | 44481.7042 | 1.6389 | 39.3333
2021-10-11 | YOLO | 549 | 2021-10-11 06:33 | 44480.2729 | 2021-10-12 18:35 | 44481.7743 | 1.5014 | 36.0333
2021-10-14 | KERN | 666 | 2021-10-15 01:00 | 44484.0417 | 2021-10-16 16:32 | 44485.6889 | 1.6472 | 39.5333
[1] Consistent with PG&E’s ESRB-8 PSPS post-event reports submitted to the CPUC, PG&E has included the earliest customer outage start time as a reflection of the outage time of the counties listed. Note: this may not be representative of what all customers on the counties listed experienced.
[2] Consistent with PG&E’s ESRB-8 PSPS post-event reports submitted to the CPUC, we have included the restoration time of the last customer restored as a reflection of the outage restoration time for the counties listed. Note: this may not be representative of what all customers on the counties listed experienced.

## 13.Tribes
LIST EACH EVENT FOR WHICH A TRIBE WAS DE-ENERGIZED
Event Name | Tribe | Number of Customers De-energized | Beginning Date De-energized[1] | Beginning Time De-energized (24-hr. clock)[1] | Ending Date Re-energized[2] | Ending Time Re-energized (24-hr. clock)[2] | Total Maximum Days De-energized (fractions in tenths) | Total Maximum Hours De-energized (Integer) | PG&E remarks
2021-08-17 | Cortina Rancheria | 8 | 2021-08-17 18:42 | 44425.7792 | 2021-08-18 17:22 | 44426.7236 | 0.94444 | 22.6667
2021-08-17 | Grindstone Rancheria | 50 | 2021-08-17 18:53 | 44425.7868 | 2021-08-19 12:02 | 44427.5014 | 1.7146 | 41.15
2021-08-17 | Pit River Tribes | 8 | 2021-08-17 17:42 | 44425.7375 | 2021-08-19 12:03 | 44427.5021 | 1.7646 | 42.35
2021-09-20 | Cortina Rancheria | 8 | 2021-09-20 06:11 | 44459.2576 | 2021-09-20 16:12 | 44459.675 | 0.41736 | 10.0167
2021-10-11 | Cortina Rancheria | 8 | 2021-10-11 06:57 | 44480.2896 | 2021-10-12 14:49 | 44481.6174 | 1.3278 | 31.8667
2021-10-11 | Grindstone Rancheria | 50 | 2021-10-11 04:42 | 44480.1958 | 2021-10-12 15:41 | 44481.6535 | 1.4576 | 34.9833
2021-10-11 | Middletown Rancheria | 34 | 2021-10-11 06:15 | 44480.2604 | 2021-10-12 16:07 | 44481.6715 | 1.4111 | 33.8667
2021-10-11 | Mooretown Rancheria | 1 | 2021-10-11 05:15 | 44480.2188 | 2021-10-12 10:50 | 44481.4514 | 1.2326 | 29.5833
2021-10-11 | Yocha Dehe Wintun Nation | 5 | 2021-10-11 07:15 | 44480.3021 | 2021-10-12 17:30 | 44481.7292 | 1.4271 | 34.25
[1] Consistent with PG&E’s ESRB-8 PSPS post-event reports submitted to the CPUC, PG&E has included the earliest customer outage start time as a reflection of the outage time of the tribes listed. Note: this may not be representative of what all customers on the tribes listed experienced.
[2] Consistent with PG&E’s ESRB-8 PSPS post-event reports submitted to the CPUC, we have included the restoration time of the last customer restored as a reflection of the outage restoration time for the tribes listed. Note: this may not be representative of what all customers on the tribes listed experienced.

## 15.Backup Power Resources
LIST EACH GENERATOR or MICROGRID AVAILABLE FOR BACKUP POWER DURING AN EVENT
Event | Generator Type | Size (MW) | Run Time (Hrs.) | Fuel Type | Description | Pre-Staged at Use Site (yes/no) | Located Off-Site (yes/no) | Type of Customer | Customer County or Tribe | Duration of Operation (Hours)[1] | Reason Deployed
2021-08-17 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Ad-hoc request | No | Yes | Water and Wastewater Systems | Tehama | 56 | High Risk to Environment
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Lake | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Shasta | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.4 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Plumas | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Shingletown Microgrid | Yes | No | Microgrid | Shasta | 41 | Pre-staged Microgrid
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Shingletown Microgrid | Yes | No | Microgrid | Shasta | 41 | Pre-staged Microgrid
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Shingletown Microgrid | Yes | No | Microgrid | Shasta | 41 | Pre-staged Microgrid
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Magalia Microgrid | Yes | No | Microgrid | Butte | 20 | Pre-staged Microgrid
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Magalia Microgrid | Yes | No | Microgrid | Butte | 20 | Pre-staged Microgrid
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Magalia Microgrid | Yes | No | Microgrid | Butte | 20 | Pre-staged Microgrid
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Angwin Microgrid | Yes | No | Microgrid | Napa | 20 | Pre-staged Microgrid
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Tuolumne | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Tuolumne | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Tuolumne | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Shasta | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Amador | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Amador | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | HVO Generator | 0.57 | 22 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 22.5 | Pre-staged Microgrid
2021-08-17 | HVO Generator | 1 | 21 | HVO | Calistoga Microgrid | No | Yes | Microgrid | Napa | 4 | Replacement generator
2021-08-17 | HVO Generator | 1 | 21 | HVO | Calistoga Microgrid | No | Yes | Microgrid | Napa | 11 | Replacement generator
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-08-17 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 20.9 | Pre-staged Microgrid
2021-08-17 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 5.7 | Pre-staged Microgrid
2021-08-17 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 4.7 | Pre-staged Microgrid
2021-08-17 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 2.8 | Pre-staged Microgrid
2021-08-17 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 22 | Pre-staged Microgrid
2021-08-17 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 21.7 | Pre-staged Microgrid
2021-08-17 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 5 | Pre-staged Microgrid
2021-08-17 | Diesel Generator | 1.25 | 20 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Calaveras | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Amador | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.02 | 27 | Diesel | Ad-hoc request | No | Yes | Tribal Health | Colusa | 44 | Risk to Public Safety
2021-09-20 | Diesel Generator | 0.036 | 30 | Diesel | Ad-hoc request | No | Yes | Water and Wastewater Systems | Kern | 28 | High Risk to Environment
2021-09-20 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Shasta | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.4 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Plumas | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Tuolumne | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Tuolumne | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Tuolumne | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Shasta | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Amador | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Amador | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 1.25 | 20 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Calaveras | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Amador | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.05 | 25 | Diesel | Ad-hoc request | No | Yes | Water and Wastewater Systems | Kern | 44.1167 | High Risk to Environment
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Ad-hoc request | No | Yes | Government Facilities | Lake | 26 | Replacement generator
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Ad-hoc request | No | Yes | Government Facilities | Lake | 20 | High Risk to Public Safety
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Ad-hoc request | No | Yes | Government Facilities | Lake | 13 | Replacement generator
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Ad-hoc request | No | Yes | Water and Wastewater Systems | Lake | 58.4167 | High Risk to Environment
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Ad-hoc request | No | Yes | Water and Wastewater Systems | Lake | 60.0333 | High Risk to Environment
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Ad-hoc request | No | Yes | Water and Wastewater Systems | Kern | 45.3667 | High Risk to Environment
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Shasta | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.4 | 21 | Diesel | Ad-hoc request | No | Yes | Water and Wastewater Systems | Lake | 59.6667 | High Risk to Environment
2021-10-11 | Diesel Generator | 0.4 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Plumas | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Tuolumne | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Tuolumne | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Tuolumne | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Shasta | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Amador | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Amador | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 1.25 | 20 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Calaveras | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Amador | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Ad-hoc request | No | Yes | Water and Wastewater Systems | Kern | 43.5333 | High Risk to environment
2021-10-14 | Diesel Generator | 0.056 | 25 | Diesel | Ad-hoc request | No | Yes | Water and Wastewater Systems | Glenn | 21.6333 | High Risk to Public Safety
2021-10-14 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.15 | 23 | Diesel | Ad-hoc request | No | Yes | Communications | Tehama | 3.6167 | High Risk to Public Safety
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Ad-hoc request | No | Yes | Water and Wastewater Systems | Kern | 25.0333 | High Risk to environment
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Sacramento | Yes | No | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Shasta | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.4 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Plumas | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Tuolumne | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Tuolumne | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Tuolumne | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Shasta | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Amador | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Amador | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Napa | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 1.25 | 20 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Calaveras | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at ICU Hospital | Yes | No | Healthcare and Public Health | Amador | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in San Leandro. | Yes | No | CRC | Alameda | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Lafayette. | Yes | No | CRC | Contra Costa | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Walnut Creek. | Yes | No | CRC | Humboldt | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in San Rafael. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Suisun City. | Yes | No | CRC | Solano | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in King City. | Yes | No | CRC | Monterey | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in American Canyon. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Saratoga. | Yes | No | CRC | Santa Clara | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Anderson. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Vacaville. | Yes | No | CRC | Solano | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Red Bluff. | Yes | No | CRC | Tehama | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Antioch. | No | Yes | CRC | Contra Costa | N/A [1] | Unit on reserve for CRC
2021-10-14 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Pacifica. | Yes | No | CRC | San Mateo | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Cloverdale. | Yes | No | CRC | Sonoma | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Lakeport. | Yes | No | CRC | Lake | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Novato. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Willits. | Yes | No | CRC | Mendocino | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Santa Rosa. | Yes | No | CRC | Sonoma | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.075 | 25 | Diesel | Unit pre-staged at CRC in Morgan Hill. | Yes | No | CRC | Santa Clara | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.075 | 25 | Diesel | Unit pre-staged at CRC in Los Molinos. | Yes | No | CRC | Tehama | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Fortuna. | Yes | No | CRC | Humboldt | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Marin City. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Salinas. | Yes | No | CRC | Monterey | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Calistoga. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Grass Valley. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Half Moon Bay. | Yes | No | CRC | San Mateo | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Scotts Valley. | Yes | No | CRC | Santa Cruz | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Lakehead. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Sonora. | Yes | No | CRC | Tuolumne | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.064 | 25 | Diesel | Unit pre-staged at CRC in Mi Wuk. | Yes | No | CRC | Tuolumne | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.056 | 25 | Diesel | Unit pre-staged at CRC in Fairfax. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Blue Lake. | Yes | No | CRC | Humboldt | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Laytonville. | Yes | No | CRC | Mendocino | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Napa. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Napa. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Foresthill. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Sheridan. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Anderson. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Downieville. | Yes | No | CRC | Sierra | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Dunlap Area. | Yes | No | CRC | Fresno | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Auberry. | Yes | No | CRC | Fresno | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Tollhouse. | Yes | No | CRC | Fresno | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Arvin. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Lamont. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Lebec. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Taft. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Oakhurst. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Ahwahnee. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Coarsegold. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in North Fork. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Mariposa. | Yes | No | CRC | Mariposa | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Mariposa. | Yes | No | CRC | Mariposa | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Plymouth. | Yes | No | CRC | Amador | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.065 | 25 | Diesel | Unit pre-staged at CRC in Pioneer. | Yes | No | CRC | Amador | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.35 | 25 | Diesel | Unit pre-staged at CRC in Paradise. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Chico. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Oroville. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Bangor. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.065 | 25 | Diesel | Unit pre-staged at CRC in Forest Ranch. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in San Andreas. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Valley Springs. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Mt. Ranch. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Murphys. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in West Point. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.065 | 25 | Diesel | Unit pre-staged at CRC in Colusa. | Yes | No | CRC | Colusa | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Cameron Park. | Yes | No | CRC | El Dorado | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in El Dorado Hills. | Yes | No | CRC | El Dorado | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Grass Valley. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Nevada City. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Penn Valley. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in McArthur. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Burnt Ranch. | Yes | No | CRC | Trinity | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Stonyford. | Yes | No | CRC | Colusa | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in North San Juan. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Alta. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Auburn. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Loomis. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Chester. | Yes | No | CRC | Plumas | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Quincy. | Yes | No | CRC | Plumas | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Alleghany. | Yes | No | CRC | Sierra | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Guerneville. | Yes | No | CRC | Sonoma | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Zamora. | Yes | No | CRC | Yolo | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Camptonville. | Yes | No | CRC | Yuba | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Oakhurst. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.25 | 25 | Diesel | Unit pre-staged at CRC in Gilroy. | Yes | No | CRC | Santa Clara | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Boulder Creek. | Yes | No | CRC | Santa Cruz | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Badger. | Yes | No | CRC | Tulare | N/A [1] | Unit pre-staged at CRC
2021-10-14 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Placerville. | Yes | No | CRC | El Dorado | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in San Leandro. | Yes | No | CRC | Alameda | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Lafayette. | Yes | No | CRC | Contra Costa | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Walnut Creek. | Yes | No | CRC | Humboldt | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in San Rafael. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Suisun City. | Yes | No | CRC | Solano | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in King City. | Yes | No | CRC | Monterey | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in American Canyon. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Saratoga. | Yes | No | CRC | Santa Clara | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Anderson. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Vacaville. | Yes | No | CRC | Solano | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Red Bluff. | Yes | No | CRC | Tehama | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Antioch. | No | Yes | CRC | Contra Costa | N/A [1] | Unit on reserve for CRC
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Pacifica. | Yes | No | CRC | San Mateo | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Cloverdale. | Yes | No | CRC | Sonoma | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Lakeport. | Yes | No | CRC | Lake | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Novato. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Willits. | Yes | No | CRC | Mendocino | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Santa Rosa. | Yes | No | CRC | Sonoma | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.075 | 25 | Diesel | Unit pre-staged at CRC in Morgan Hill. | Yes | No | CRC | Santa Clara | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.075 | 25 | Diesel | Unit pre-staged at CRC in Los Molinos. | Yes | No | CRC | Tehama | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Fortuna. | Yes | No | CRC | Humboldt | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Marin City. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Salinas. | Yes | No | CRC | Monterey | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Calistoga. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Grass Valley. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Half Moon Bay. | Yes | No | CRC | San Mateo | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Scotts Valley. | Yes | No | CRC | Santa Cruz | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Lakehead. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Sonora. | Yes | No | CRC | Tuolumne | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.064 | 25 | Diesel | Unit pre-staged at CRC in Mi Wuk. | Yes | No | CRC | Tuolumne | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.056 | 25 | Diesel | Unit pre-staged at CRC in Fairfax. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Blue Lake. | Yes | No | CRC | Humboldt | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Laytonville. | Yes | No | CRC | Mendocino | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Napa. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Napa. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Foresthill. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Sheridan. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Anderson. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Downieville. | Yes | No | CRC | Sierra | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Dunlap Area. | Yes | No | CRC | Fresno | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Auberry. | Yes | No | CRC | Fresno | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Tollhouse. | Yes | No | CRC | Fresno | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Arvin. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Lamont. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Lebec. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Taft. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Oakhurst. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Ahwahnee. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Coarsegold. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in North Fork. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Mariposa. | Yes | No | CRC | Mariposa | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Mariposa. | Yes | No | CRC | Mariposa | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Plymouth. | Yes | No | CRC | Amador | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.065 | 25 | Diesel | Unit pre-staged at CRC in Pioneer. | Yes | No | CRC | Amador | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.35 | 25 | Diesel | Unit pre-staged at CRC in Paradise. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Chico. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Oroville. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Bangor. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.065 | 25 | Diesel | Unit pre-staged at CRC in Forest Ranch. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in San Andreas. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Valley Springs. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Mt. Ranch. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Murphys. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in West Point. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.065 | 25 | Diesel | Unit pre-staged at CRC in Colusa. | Yes | No | CRC | Colusa | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Cameron Park. | Yes | No | CRC | El Dorado | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in El Dorado Hills. | Yes | No | CRC | El Dorado | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Grass Valley. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Nevada City. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Penn Valley. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in McArthur. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Burnt Ranch. | Yes | No | CRC | Trinity | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Stonyford. | Yes | No | CRC | Colusa | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in North San Juan. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Alta. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Auburn. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Loomis. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Chester. | Yes | No | CRC | Plumas | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Quincy. | Yes | No | CRC | Plumas | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Alleghany. | Yes | No | CRC | Sierra | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Guerneville. | Yes | No | CRC | Sonoma | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Zamora. | Yes | No | CRC | Yolo | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Camptonville. | Yes | No | CRC | Yuba | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Oakhurst. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.25 | 25 | Diesel | Unit pre-staged at CRC in Gilroy. | Yes | No | CRC | Santa Clara | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Boulder Creek. | Yes | No | CRC | Santa Cruz | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Badger. | Yes | No | CRC | Tulare | N/A [1] | Unit pre-staged at CRC
2021-10-11 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Placerville. | Yes | No | CRC | El Dorado | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in San Leandro. | Yes | No | CRC | Alameda | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Lafayette. | Yes | No | CRC | Contra Costa | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Walnut Creek. | Yes | No | CRC | Humboldt | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in San Rafael. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Suisun City. | Yes | No | CRC | Solano | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in King City. | Yes | No | CRC | Monterey | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in American Canyon. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Saratoga. | Yes | No | CRC | Santa Clara | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Anderson. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Vacaville. | Yes | No | CRC | Solano | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Red Bluff. | Yes | No | CRC | Tehama | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Antioch. | No | Yes | CRC | Contra Costa | N/A [1] | Unit on reserve for CRC
2021-09-20 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Pacifica. | Yes | No | CRC | San Mateo | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Cloverdale. | Yes | No | CRC | Sonoma | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Lakeport. | Yes | No | CRC | Lake | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Novato. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Willits. | Yes | No | CRC | Mendocino | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Santa Rosa. | Yes | No | CRC | Sonoma | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.075 | 25 | Diesel | Unit pre-staged at CRC in Morgan Hill. | Yes | No | CRC | Santa Clara | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.075 | 25 | Diesel | Unit pre-staged at CRC in Los Molinos. | Yes | No | CRC | Tehama | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Fortuna. | Yes | No | CRC | Humboldt | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Marin City. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Salinas. | Yes | No | CRC | Monterey | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Calistoga. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Grass Valley. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Half Moon Bay. | Yes | No | CRC | San Mateo | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Scotts Valley. | Yes | No | CRC | Santa Cruz | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Lakehead. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Sonora. | Yes | No | CRC | Tuolumne | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.064 | 25 | Diesel | Unit pre-staged at CRC in Mi Wuk. | Yes | No | CRC | Tuolumne | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.056 | 25 | Diesel | Unit pre-staged at CRC in Fairfax. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Blue Lake. | Yes | No | CRC | Humboldt | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Laytonville. | Yes | No | CRC | Mendocino | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Napa. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Napa. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Foresthill. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Sheridan. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Anderson. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Downieville. | Yes | No | CRC | Sierra | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Dunlap Area. | Yes | No | CRC | Fresno | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Auberry. | Yes | No | CRC | Fresno | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Tollhouse. | Yes | No | CRC | Fresno | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Arvin. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Lamont. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Lebec. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Taft. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Oakhurst. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Ahwahnee. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Coarsegold. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in North Fork. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Mariposa. | Yes | No | CRC | Mariposa | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Mariposa. | Yes | No | CRC | Mariposa | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Plymouth. | Yes | No | CRC | Amador | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.065 | 25 | Diesel | Unit pre-staged at CRC in Pioneer. | Yes | No | CRC | Amador | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.35 | 25 | Diesel | Unit pre-staged at CRC in Paradise. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Chico. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Oroville. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Bangor. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.065 | 25 | Diesel | Unit pre-staged at CRC in Forest Ranch. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in San Andreas. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Valley Springs. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Mt. Ranch. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Murphys. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in West Point. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.065 | 25 | Diesel | Unit pre-staged at CRC in Colusa. | Yes | No | CRC | Colusa | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Cameron Park. | Yes | No | CRC | El Dorado | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in El Dorado Hills. | Yes | No | CRC | El Dorado | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Grass Valley. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Nevada City. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Penn Valley. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in McArthur. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Burnt Ranch. | Yes | No | CRC | Trinity | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Stonyford. | Yes | No | CRC | Colusa | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in North San Juan. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Alta. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Auburn. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Loomis. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Chester. | Yes | No | CRC | Plumas | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Quincy. | Yes | No | CRC | Plumas | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Alleghany. | Yes | No | CRC | Sierra | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Guerneville. | Yes | No | CRC | Sonoma | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Zamora. | Yes | No | CRC | Yolo | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Camptonville. | Yes | No | CRC | Yuba | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Oakhurst. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.25 | 25 | Diesel | Unit pre-staged at CRC in Gilroy. | Yes | No | CRC | Santa Clara | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Boulder Creek. | Yes | No | CRC | Santa Cruz | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Badger. | Yes | No | CRC | Tulare | N/A [1] | Unit pre-staged at CRC
2021-09-20 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Placerville. | Yes | No | CRC | El Dorado | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in San Leandro. | Yes | No | CRC | Alameda | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Lafayette. | Yes | No | CRC | Contra Costa | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Walnut Creek. | Yes | No | CRC | Humboldt | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in San Rafael. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Suisun City. | Yes | No | CRC | Solano | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in King City. | Yes | No | CRC | Monterey | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in American Canyon. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Saratoga. | Yes | No | CRC | Santa Clara | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Anderson. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Vacaville. | Yes | No | CRC | Solano | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Red Bluff. | Yes | No | CRC | Tehama | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Antioch. | No | Yes | CRC | Contra Costa | N/A [1] | Unit on reserve for CRC
2021-08-17 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Pacifica. | Yes | No | CRC | San Mateo | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Cloverdale. | Yes | No | CRC | Sonoma | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Lakeport. | Yes | No | CRC | Lake | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Novato. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Willits. | Yes | No | CRC | Mendocino | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Santa Rosa. | Yes | No | CRC | Sonoma | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.075 | 25 | Diesel | Unit pre-staged at CRC in Morgan Hill. | Yes | No | CRC | Santa Clara | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.075 | 25 | Diesel | Unit pre-staged at CRC in Los Molinos. | Yes | No | CRC | Tehama | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Fortuna. | Yes | No | CRC | Humboldt | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Marin City. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Salinas. | Yes | No | CRC | Monterey | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Calistoga. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Grass Valley. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Half Moon Bay. | Yes | No | CRC | San Mateo | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Scotts Valley. | Yes | No | CRC | Santa Cruz | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Lakehead. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Sonora. | Yes | No | CRC | Tuolumne | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.064 | 25 | Diesel | Unit pre-staged at CRC in Mi Wuk. | Yes | No | CRC | Tuolumne | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.056 | 25 | Diesel | Unit pre-staged at CRC in Fairfax. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Blue Lake. | Yes | No | CRC | Humboldt | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Laytonville. | Yes | No | CRC | Mendocino | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Napa. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Napa. | Yes | No | CRC | Napa | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Foresthill. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Sheridan. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Anderson. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Downieville. | Yes | No | CRC | Sierra | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Dunlap Area. | Yes | No | CRC | Fresno | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Auberry. | Yes | No | CRC | Fresno | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Tollhouse. | Yes | No | CRC | Fresno | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Arvin. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Lamont. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Lebec. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Taft. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Oakhurst. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Ahwahnee. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Coarsegold. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in North Fork. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Mariposa. | Yes | No | CRC | Mariposa | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Mariposa. | Yes | No | CRC | Mariposa | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Plymouth. | Yes | No | CRC | Amador | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.065 | 25 | Diesel | Unit pre-staged at CRC in Pioneer. | Yes | No | CRC | Amador | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.35 | 25 | Diesel | Unit pre-staged at CRC in Paradise. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Chico. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Oroville. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Bangor. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.065 | 25 | Diesel | Unit pre-staged at CRC in Forest Ranch. | Yes | No | CRC | Butte | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in San Andreas. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Valley Springs. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Mt. Ranch. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in Murphys. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.08 | 20 | Diesel | Unit pre-staged at CRC in West Point. | Yes | No | CRC | Calaveras | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.065 | 25 | Diesel | Unit pre-staged at CRC in Colusa. | Yes | No | CRC | Colusa | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Cameron Park. | Yes | No | CRC | El Dorado | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in El Dorado Hills. | Yes | No | CRC | El Dorado | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Grass Valley. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Nevada City. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Penn Valley. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in McArthur. | Yes | No | CRC | Shasta | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.125 | 36 | Diesel | Unit pre-staged at CRC in Burnt Ranch. | Yes | No | CRC | Trinity | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Stonyford. | Yes | No | CRC | Colusa | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in North San Juan. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Alta. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Auburn. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Loomis. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Chester. | Yes | No | CRC | Plumas | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Quincy. | Yes | No | CRC | Plumas | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Alleghany. | Yes | No | CRC | Sierra | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Guerneville. | Yes | No | CRC | Sonoma | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Zamora. | Yes | No | CRC | Yolo | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.04 | 25 | Diesel | Unit pre-staged at CRC in Camptonville. | Yes | No | CRC | Yuba | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Oakhurst. | Yes | No | CRC | Madera | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.25 | 25 | Diesel | Unit pre-staged at CRC in Gilroy. | Yes | No | CRC | Santa Clara | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Boulder Creek. | Yes | No | CRC | Santa Cruz | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.07 | 25 | Diesel | Unit pre-staged at CRC in Badger. | Yes | No | CRC | Tulare | N/A [1] | Unit pre-staged at CRC
2021-08-17 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Placerville. | Yes | No | CRC | El Dorado | N/A [1] | Unit pre-staged at CRC
2021-01-18 | Diesel Generator | 0.06 | 25 | Diesel | Unit on reserve in Benicia | No | Yes | Unit on Reserve | Solano | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.07 | 25 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Benicia | No | Yes | Unit on Reserve | Solano | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged in St Helena | Yes | No | Water and Wastewater Systems | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Benicia | No | Yes | Unit on Reserve | Solano | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged in Mariposa | Yes | No | Government Facilities | Mariposa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.125 | 36 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Benicia | No | Yes | Unit on Reserve | Solano | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Benicia | No | Yes | Unit on Reserve | Solano | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged in Davis | Yes | No | Government Facilities | Yolo | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit pre-staged in St Helena | Yes | No | Healthcare and Public Health | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit pre-staged in Kentfield | Yes | No | Healthcare and Public Health | Marin | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit pre-staged in San Andres | Yes | No | Healthcare and Public Health | Calaveras | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Benicia | No | Yes | Unit on Reserve | Solano | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in French Camp | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged in San Andres | Yes | No | Government Facilities | Calaveras | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged in San Andres | Yes | No | Healthcare and Public Health | Calaveras | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged in Mariposa | Yes | No | Healthcare and Public Health | Mariposa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged in San Andres | Yes | No | Healthcare and Public Health | Calaveras | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged in Mariposa | Yes | No | Healthcare and Public Health | Mariposa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in Monterey | Yes | No | Healthcare and Public Health | Monterey | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit on reserve in Glen Ellen | No | Yes | Unit on Reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at substation in Sausalito. | Yes | No | Substation | Marin | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in Monterey | Yes | No | Healthcare and Public Health | Monterey | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in Sonora | Yes | No | Healthcare and Public Health | Sonora | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in Sonora | Yes | No | Healthcare and Public Health | Sonora | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Fall River Mills | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Fall River Mills | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Fall River Mills | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Fall River Mills | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at substation in Sausalito. | Yes | No | Substation | Marin | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit on reserve in Vallejo | No | Yes | Unit on Reserve | Solano | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Fall River Mills | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit on reserve in Vallejo | No | Yes | Unit on Reserve | Solano | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit on reserve in Vallejo | No | Yes | Unit on Reserve | Solano | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Fall River Mills | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Fall River Mills | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Fall River Mills | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Fall River Mills | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit on reserve in Glen Ellen | No | Yes | Unit on Reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in St Helena | Yes | No | Healthcare and Public Health | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit on reserve in Benicia | No | Yes | Unit on Reserve | Solano | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at substation in Sausalito. | Yes | No | Substation | Marin | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit on reserve in Glen Ellen | No | Yes | Unit on Reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at substation in Sausalito. | Yes | No | Substation | Marin | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Calistoga | Yes | No | Substation | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at substation in Sausalito. | Yes | No | Substation | Marin | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at substation in Sausalito. | Yes | No | Substation | Marin | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in Jackson | Yes | No | Healthcare and Public Health | Amador | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at substation in Sausalito. | Yes | No | Substation | Marin | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at substation in Sausalito. | Yes | No | Substation | Marin | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in Jackson | Yes | No | Healthcare and Public Health | Amador | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at substation in Sausalito. | Yes | No | Substation | Marin | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at substation in Sausalito. | Yes | No | Substation | Marin | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in St Helena | Yes | No | Healthcare and Public Health | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Calistoga | Yes | No | Substation | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at substation in Sausalito. | Yes | No | Substation | Marin | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at CRC in Jackson | Yes | No | Healthcare and Public Health | Amador | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at microgrid in Angwin | Yes | No | Microgrid | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in Monterey | Yes | No | Healthcare and Public Health | Monterey | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Fall River Mills | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Calistoga | Yes | No | Substation | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Fall River Mills | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Calistoga | Yes | No | Substation | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at microgrid in Angwin | Yes | No | Microgrid | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Fall River Mills | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in Monterey | Yes | No | Healthcare and Public Health | Monterey | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in Monterey | Yes | No | Healthcare and Public Health | Monterey | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in San Luis Obispo | Yes | No | Healthcare and Public Health | San Luis Obispo | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in San Luis Obispo | Yes | No | Healthcare and Public Health | San Luis Obispo | 0 | Unit pre-staged, not deployed
2021-01-18 | Gas Generator | 1.3 | 20 | Gas | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Gas Generator | 1.3 | 20 | Gas | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at microgrid in Angwin | Yes | No | Microgrid | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in Jackson | Yes | No | Healthcare and Public Health | Amador | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in Woodland | Yes | No | Food | Yolo | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in Woodland | Yes | No | Food | Yolo | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at microgrid in Angwin | Yes | No | Microgrid | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged in Jackson | Yes | No | Government Facilities | Amador | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Anderson | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Anderson | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Anderson | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Anderson | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Anderson | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Anderson | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Anderson | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Anderson | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Unit pre-staged in Auburn | Yes | No | Water and Wastewater Systems | Placer | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.25 | 20 | Diesel | Unit pre-staged in Auburn | Yes | No | Water and Wastewater Systems | Placer | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.25 | 20 | Diesel | Unit pre-staged in Auburn | Yes | No | Water and Wastewater Systems | Placer | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.25 | 20 | Diesel | Unit pre-staged in Auburn | Yes | No | Water and Wastewater Systems | Placer | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Unit pre-staged in Auburn | Yes | No | Water and Wastewater Systems | Placer | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Chico | No | Yes | Unit on Reserve | Butte | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Chico | No | Yes | Unit on Reserve | Butte | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Chico | No | Yes | Unit on Reserve | Butte | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Chico | No | Yes | Unit on Reserve | Butte | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Grass Valley | Yes | No | Substation | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Oroville | Yes | No | Substation | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Placerville | Yes | No | Substation | El Dorado | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Placerville | Yes | No | Substation | El Dorado | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Placerville | Yes | No | Substation | El Dorado | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Placerville | Yes | No | Substation | El Dorado | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Placerville | Yes | No | Substation | El Dorado | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Plantina | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Plantina | Yes | No | Substation | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Redding | No | Yes | Unit on Reserve | Shasta | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.8 | 21 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.8 | 21 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.8 | 21 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.8 | 21 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.8 | 21 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.8 | 21 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.8 | 21 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.25 | 20 | Diesel | Unit on reserve in San Leandro | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit pre-staged in Shingletown | Yes | No | Food | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.32 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.32 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit pre-staged in Lebec | Yes | No | Water and Wastewater Systems | Kern | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Potter Valley | No | Yes | Unit on Reserve | Mendocino | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Potter Valley | No | Yes | Unit on Reserve | Mendocino | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in El Dorado Hills | Yes | No | CRC | El Dorado | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Salinas | Yes | No | CRC | Monterey | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged in Clearlake | Yes | No | Healthcare and Public Health | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged in Lakeport | Yes | No | Water and Wastewater Systems | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.275 | 25 | Diesel | Unit on reserve in Salida | No | Yes | Unit on Reserve | Stanislaus | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.275 | 25 | Diesel | Unit on reserve in Salida | No | Yes | Unit on Reserve | Stanislaus | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.275 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.275 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.275 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.275 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in San Leandro | Yes | No | CRC | Alameda | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.275 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.275 | 25 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Novato | Yes | No | CRC | Marin | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Cloverdale | Yes | No | CRC | Sonoma | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Anderson | Yes | No | CRC | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Plymouth | Yes | No | CRC | Amador | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Santa Rosa | Yes | No | CRC | Sonoma | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.02 | 27 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.02 | 27 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.02 | 27 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.02 | 27 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in North Clearlake | No | Yes | Unit on Reserve | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Philo | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Unit pre-staged in San Ramon | Yes | No | Energy | Contra Costa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Fort Bragg | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Philo | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Fort Bragg | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Fort Bragg | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Philo | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.6 | 11 | Diesel | Pre-staged at substation in Ukiah | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Ukiah | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at hospital in Lakeport | Yes | No | Healthcare and Public Health | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Ukiah | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Pre-staged at substation in Ukiah | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Fort Bragg | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Fort Bragg | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Fort Bragg | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Elk | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Fort Bragg | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Fort Bragg | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Elk | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Ukiah | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Bodega Bay | Yes | No | Substation | Sonoma | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Fort Bragg | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Bodega Bay | Yes | No | Substation | Sonoma | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Lakeport | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Elk | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Fort Bragg | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Fort Bragg | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Fort Bragg | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Bodega Bay | Yes | No | Substation | Sonoma | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Fort Bragg | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Elk | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at hospital in Clearlake | Yes | No | Healthcare and Public Health | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Elk | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Elk | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Ukiah | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Ukiah | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged in Quincy | Yes | No | Community | Plumas | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at microgrid in Clearlake | Yes | No | Microgrid | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Ukiah | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Hayward | No | Yes | Unit on Reserve | Alameda | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Bodega Bay | Yes | No | Substation | Sonoma | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Bodega Bay | Yes | No | Substation | Sonoma | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Ukiah | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Bodega Bay | Yes | No | Substation | Sonoma | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Ukiah | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Ukiah | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at microgrid in Clearlake | Yes | No | Microgrid | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Ukiah | Yes | No | Substation | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit pre-staged in Fall River Mills | Yes | No | Healthcare and Public Health | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit pre-staged in Clearlake | Yes | No | Healthcare and Public Health | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit pre-staged in Burney | Yes | No | Healthcare and Public Health | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Cameron Park | Yes | No | CRC | El Dorado | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged in Clearlake | Yes | No | Healthcare and Public Health | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Concord | No | Yes | Unit on Reserve | Contra Costa | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged in Lakeport | Yes | No | Healthcare and Public Health | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.3 | 25 | Diesel | Unit pre-staged at CRC in Burnt Ranch | Yes | No | CRC | Trinity | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged in Downieville | Yes | No | Water and Wastewater Systems | Downieville | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Mountain Ranch | Yes | No | CRC | Calaveras | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Valley Springs | Yes | No | CRC | Calaveras | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in San Andreas | Yes | No | CRC | Calaveras | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Oakhurst | Yes | No | CRC | Madera | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Suisun City | Yes | No | CRC | Solano | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Mariposa | Yes | No | CRC | Mariposa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged in Placerville | Yes | No | Energy | El Dorado | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Napa | Yes | No | CRC | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged in Grass Valley | Yes | No | Energy | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Grass Valley | Yes | No | CRC | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Squaw Valley | Yes | No | CRC | Fresno | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Oroville | Yes | No | CRC | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Sonora | Yes | No | CRC | Tuolumne | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in American Canyon | Yes | No | CRC | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Saratoga | Yes | No | CRC | Santa Clara | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Chico | Yes | No | CRC | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Murphy | Yes | No | CRC | Calaveras | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Vacaville | Yes | No | CRC | Solano | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Lakeport | Yes | No | CRC | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Toll House | Yes | No | CRC | Fresno | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Mcarthur | Yes | No | CRC | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Red Bluff | Yes | No | CRC | Tehama | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Coarsegold | Yes | No | CRC | Madera | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Arvin | Yes | No | CRC | Kern | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Nevada City | Yes | No | CRC | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Bangor | Yes | No | CRC | Butte | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Ahwahnee | Yes | No | CRC | Madera | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Lakehead | Yes | No | CRC | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Mi Wuk | Yes | No | CRC | Tuolumne | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Grass Valley | Yes | No | CRC | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Taft | Yes | No | CRC | Kern | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in North Fork | Yes | No | CRC | Madera | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Santa Rosa | No | Yes | Unit on Reserve | Sonoma | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Lamont | Yes | No | CRC | Kern | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Camptonville | Yes | No | CRC | Yuba | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged at CRC in Chester | Yes | No | CRC | Plumas | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Napa | Yes | No | CRC | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Los Molinos | Yes | No | CRC | Tehama | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Colusa | Yes | No | CRC | Colusa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Willits | Yes | No | CRC | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Napa | Yes | No | CRC | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Alta | Yes | No | CRC | Placer | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged in Anderson | Yes | No | CRC | Shasta | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged in Fortuna | Yes | No | CRC | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged in Auburn | Yes | No | CRC | Placer | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in North San Juan | Yes | No | CRC | Nevada | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Laytonville | Yes | No | CRC | Mendocino | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in West Point | Yes | No | CRC | Calaveras | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Alleghany | Yes | No | CRC | Sierra | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Pionner | Yes | No | CRC | Amador | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Blue Lake | Yes | No | CRC | Humboldt | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Downieville | Yes | No | CRC | Downieville | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Calistoga | Yes | No | CRC | Napa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.02 | 27 | Diesel | Unit pre-staged at CRC in Stonyford | Yes | No | CRC | Colusa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.6 | 11 | Diesel | Unit pre-staged at microgrid in Clearlake | Yes | No | Microgrid | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.6 | 11 | Diesel | Unit pre-staged at microgrid in Clearlake | Yes | No | Microgrid | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.6 | 11 | Diesel | Unit pre-staged at microgrid in Clearlake | Yes | No | Microgrid | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.6 | 11 | Diesel | Unit pre-staged at microgrid in Clearlake | Yes | No | Microgrid | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at microgrid in Clearlake | Yes | No | Microgrid | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at microgrid in Clearlake | Yes | No | Microgrid | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at microgrid in Clearlake | Yes | No | Microgrid | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 1.5 | 14 | Diesel | Unit pre-staged at microgrid in Clearlake | Yes | No | Microgrid | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at microgrid in Clearlake | Yes | No | Microgrid | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at microgrid in Clearlake | Yes | No | Microgrid | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at microgrid in Clearlake | Yes | No | Microgrid | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit pre-staged at microgrid in Clearlake | Yes | No | Microgrid | Lake | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.055 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.055 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.055 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.055 | 25 | Diesel | Unit pre-staged in Santa Rosa | Yes | No | Service | Santa Rosa | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.055 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.055 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.055 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.055 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.055 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.055 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit pre-staged in Sonora | Yes | No | Healthcare and Public Health | Sonora | 0 | Unit pre-staged, not deployed
2021-01-18 | Diesel Generator | 0.15 | 29 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.25 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.35 | 25 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Unit on Reserve | Sacramento | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.8 | 21 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.8 | 21 | Diesel | Unit on reserve in Stockton | No | Yes | Unit on Reserve | San Joaquin | 0 | Unit on reserve, not deployed
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit pre-staged at CRC in Antioch. | Yes | No | CRC | Contra Costa | N/A [1] | Unit pre-staged at CRC
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Auberry. | Yes | No | CRC | Fresno | N/A [1] | Unit pre-staged at CRC
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Lebec. | Yes | No | CRC | Kern | N/A [1] | Unit pre-staged at CRC
2021-01-18 | Diesel Generator | 0.056 | 25 | Diesel | Unit pre-staged at CRC in Fairfax. | Yes | No | CRC | Marin | N/A [1] | Unit pre-staged at CRC
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Mariposa. | Yes | No | CRC | Mariposa | N/A [1] | Unit pre-staged at CRC
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Penn Valley. | Yes | No | CRC | Nevada | N/A [1] | Unit pre-staged at CRC
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Loomis. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-01-18 | Diesel Generator | 0.05 | 25 | Diesel | Unit pre-staged at CRC in Sheridan. | Yes | No | CRC | Placer | N/A [1] | Unit pre-staged at CRC
2021-01-18 | Diesel Generator | 0.12 | 36 | Diesel | Unit pre-staged at CRC in Pacifica. | Yes | No | CRC | San Mateo | N/A [1] | Unit pre-staged at CRC
2021-01-18 | Diesel Generator | 0.1 | 15 | Diesel | Unit pre-staged at CRC in Half Moon Bay. | Yes | No | CRC | San Mateo | N/A [1] | Unit pre-staged at CRC
2021-01-18 | Diesel Generator | 0.2 | 29 | Diesel | Unit pre-staged at CRC in Morgan Hill. | Yes | No | CRC | Santa Clara | N/A [1] | Unit pre-staged at CRC
2021-10-14 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | HVO Generator | 0.57 | 22 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | HVO Generator | 1 | 21 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | HVO Generator | 1 | 21 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.57 | 22 | Diesel | Georgetown Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.57 | 22 | Diesel | Georgetown Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.57 | 22 | Diesel | Magalia Microgrid | Yes | No | Microgrid | Butte | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.57 | 22 | Diesel | Magalia Microgrid | Yes | No | Microgrid | Butte | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.57 | 22 | Diesel | Magalia Microgrid | Yes | No | Microgrid | Butte | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pollock Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pollock Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pollock Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.57 | 22 | Diesel | Shingletown Microgrid | Yes | No | Microgrid | Shasta | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.57 | 22 | Diesel | Shingletown Microgrid | Yes | No | Microgrid | Shasta | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.57 | 22 | Diesel | Shingletown Microgrid | Yes | No | Microgrid | Shasta | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Angwin Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Foresthill Microgrid | Yes | No | Microgrid | Placer | 0 | Pre-staged microgrid, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Foresthill Microgrid | Yes | No | Microgrid | Placer | 0 | Pre-staged microgrid, not deployed
2021-10-11 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | HVO Generator | 0.57 | 22 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | HVO Generator | 1 | 21 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | HVO Generator | 1 | 21 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.57 | 22 | Diesel | Georgetown Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.57 | 22 | Diesel | Georgetown Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.57 | 22 | Diesel | Magalia Microgrid | Yes | No | Microgrid | Butte | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.57 | 22 | Diesel | Magalia Microgrid | Yes | No | Microgrid | Butte | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.57 | 22 | Diesel | Magalia Microgrid | Yes | No | Microgrid | Butte | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pollock Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pollock Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pollock Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.57 | 22 | Diesel | Shingletown Microgrid | Yes | No | Microgrid | Shasta | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.57 | 22 | Diesel | Shingletown Microgrid | Yes | No | Microgrid | Shasta | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.57 | 22 | Diesel | Shingletown Microgrid | Yes | No | Microgrid | Shasta | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Angwin Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Foresthill Microgrid | Yes | No | Microgrid | Placer | 0 | Pre-staged microgrid, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Foresthill Microgrid | Yes | No | Microgrid | Placer | 0 | Pre-staged microgrid, not deployed
2021-09-20 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | HVO Generator | 1.14 | 24 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | HVO Generator | 0.57 | 22 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | HVO Generator | 1 | 21 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | HVO Generator | 1 | 21 | HVO | Calistoga Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.57 | 22 | Diesel | Georgetown Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.57 | 22 | Diesel | Georgetown Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.57 | 22 | Diesel | Magalia Microgrid | Yes | No | Microgrid | Butte | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.57 | 22 | Diesel | Magalia Microgrid | Yes | No | Microgrid | Butte | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.57 | 22 | Diesel | Magalia Microgrid | Yes | No | Microgrid | Butte | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pollock Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pollock Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pollock Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.57 | 22 | Diesel | Shingletown Microgrid | Yes | No | Microgrid | Shasta | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.57 | 22 | Diesel | Shingletown Microgrid | Yes | No | Microgrid | Shasta | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.57 | 22 | Diesel | Shingletown Microgrid | Yes | No | Microgrid | Shasta | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Angwin Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Foresthill Microgrid | Yes | No | Microgrid | Placer | 0 | Pre-staged microgrid, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Foresthill Microgrid | Yes | No | Microgrid | Placer | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 0.57 | 22 | Diesel | Georgetown Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 0.57 | 22 | Diesel | Georgetown Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pollock Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pollock Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pollock Microgrid | Yes | No | Microgrid | El Dorado | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Middletown Microgrid | Yes | No | Microgrid | Lake | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Placerville Microgrid | Yes | No | Microgrid | Napa | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Foresthill Microgrid | Yes | No | Microgrid | Placer | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Foresthill Microgrid | Yes | No | Microgrid | Placer | 0 | Pre-staged microgrid, not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Middletown | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Middletown | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Middletown | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Middletown | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Middletown | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Middletown | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Middletown | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Middletown | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 0.5 | 23 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 1 | 21 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Clearlake | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Hartley | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at substation in Konocti | Yes | No | Substation | Lake | 0 | Unit pre-staged and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Unit on reserve in Sacramento | No | Yes | Substation | Sacramento | 0 | Unit on reserve and not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-08-17 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-09-20 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-11 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Hoopa | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at substation in Willow Creek | Yes | No | Substation | Humboldt | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.25 | 22 | Diesel | Pre-staged at Substation in Cloverdale | Yes | No | Substation | Sonoma | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 1.14 | 24 | Diesel | Pre-staged at Point Moretti Substation Davenport | Yes | No | Substation | Santa Cruz | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
2021-10-14 | Diesel Generator | 2 | 11 | Diesel | Pre-staged at Brunswick Substation | Yes | No | Substation | Nevada | N/A | Unit pre-staged, not deployed
[1] Inputs labeled as NA[1] are units connected to an ATS (Automatic Transfer Switch) that turns on automatically during any power outage, impeding to determine the hours of operation for a specific time.
Note: The Backup Power Resources table includes the best information currently available. After consolidating all the backup generation information available for 2021, the following variances with previously reported data are reported:
a. PG&E provided 40.575MW of pre-staged and on-reserve backup generation capacity for critical facilities during all events from August 17, 2021 to the November 14, 2021. This number differs from the total that was previously reported in the events’ Post Event Reports (41.175MW) because two additional 0.3MW generators were reported as pre-staged in ICU hospitals.
b. The Calistoga (Napa County) microgrid provided a combined 5.99 MW during the August 17, 2021 event. This number differs from what was previously reported in the August 17, 2021 Post Event Report (5.13 MW). After further analysis, this microgrid was the first to utilize a new technology of Tier 4 generator engines and experienced communication errors between engines. The generators supporting the microgrid operated successfully in test mode, but four generators failed when the actual microgrid load was applied during the PSPS event. As a result, two additional 1 MW generators were deployed to support the microgrid.

## 16.Mitigation
MITIGATION[1] DEPLOYED FOR BACKUP POWER DURING AN EVENT
Event Name | Circuit Name | County or Tribe | Line miles of circuit* | Line miles of circuit in HFTD Tiers 2 and 3 | Type of Mitigation Deployed | Date Mitigation Deployed | Time Mitigation Deployed (24-hr. clock) | Date Resume Normal Operations (back on grid) | Time Resume Normal Operations (24-hr. clock) | Total Days Mitigation In Use (fractions in tenths) | Total Hours Mitigation In Use (Integer) | Total customers NOT de-energized | Residential customers NOT de-energized | Commercial/Industrial customers NOT de-energized | Medical Baseline (MBL) customers NOT de-energized | AFN other than MBL customers NOT de-energized | Circuit “All Clear” declaration date/time | Circuit Restoration date/time | PG&E Remarks
2021-01-18 | DUNLAP 1103 | MADERA, FRESNO | 32.5029 | 32.5029 | Dx Switching | 2021-01-17 | 13:54 | 2021-01-21 | 13:01 | 4 | 96 | 399 | 350 | 44 | 33 | 89 | 2021-01-20 04:22 | 2021-01-20 16:47
2021-01-18 | MARIPOSA 2101 | KERN | 25.283 | 25.283 | Dx Switching | 2021-01-17 | 12:40 | 2021-01-25 | 13:00 | 8 | 192 | 292 | 271 | 20 | 33 | 62 | 2021-01-19 14:03 | 2021-01-24 14:02
2021-01-18 | SANTA MARIA 1108 | NAPA | 35.9855 | 35.9855 | Dx Switching | 2021-01-18 | 10:14 | 2021-01-20 | 13:29 | 2 | 48 | 219 | 174 | 31 | 9 | 18 | 2021-01-20 04:22 | 2021-01-20 09:44
2021-01-18 | AUBERRY 1101 | SHASTA | 181.5659 | 180.9062 | Sectionalization | 2021-01-19 | 1:06 | 2021-01-20 | 12:55 | 1 | 24 | 1954 | 1751 | 188 | 177 | 0 | 2021-08-19 05:17 | 2021-08-19 18:27
2021-01-18 | BALCH NO 1 1101 | NAPA | 3.8719 | 3.8719 | Sectionalization | 2021-01-19 | 5:53 | 2021-01-20 | 9:32 | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 2021-08-18 12:39 | 2021-08-18 20:35
2021-01-18 | CAL WATER 1102 | SHASTA | 61.4476 | 0 | Sectionalization | 2021-01-19 | 6:49 | 2021-01-20 | 8:00 | 1 | 24 | 2360 | 2168 | 180 | 261 | 0 | 2021-08-18 17:08 | 2021-08-18 20:11
2021-01-18 | DUNLAP 1102 | SHASTA | 0 | 0 | Sectionalization | 2021-01-19 | 5:46 | 2021-01-20 | 16:20 | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 2021-08-18 17:08 | 2021-08-18 20:40
2021-01-18 | DUNLAP 1103 | SHASTA | 32.3998 | 32.3998 | Sectionalization | 2021-01-19 | 2:46 | 2021-01-20 | 16:47 | 1 | 24 | 399 | 349 | 45 | 32 | 0 | 2021-08-18 09:29 | 2021-08-18 17:19
2021-01-18 | LAMONT 1102 | COLUSA | 67.6671 | 2.2183 | Sectionalization | 2021-01-19 | 6:43 | 2021-01-20 | 8:18 | 1 | 24 | 463 | 192 | 153 | 18 | 0 | 2021-08-18 14:46 | 2021-08-18 16:14
2021-01-18 | MARIPOSA 2101 | YOLO, COLUSA | 137.0155 | 135.4132 | Sectionalization | 2021-01-19 | 0:10 | 2021-01-26 | 16:10 | 7 | 168 | 2319 | 2131 | 174 | 161 | 0 | 2021-08-18 14:46 | 2021-08-18 16:45
2021-01-18 | MARIPOSA 2102 | SHASTA | 256.3093 | 241.1004 | Sectionalization | 2021-01-19 | 0:24 | 2021-01-24 | 14:02 | 5 | 120 | 3077 | 2538 | 519 | 204 | 0 | 2021-08-18 07:58 | 2021-08-18 11:40
2021-01-18 | MESA 1101 | BUTTE | 72.9643 | 33.7772 | Sectionalization | 2021-01-19 | 8:14 | 2021-01-20 | 10:50 | 1 | 24 | 1866 | 1457 | 301 | 70 | 0 | 2021-08-18 09:29 | 2021-08-18 14:25
2021-01-18 | OAKHURST 1103 | NAPA, SONOMA | 113.7648 | 111.7386 | Sectionalization | 2021-01-18 | 23:46 | 2021-01-26 | 16:50 | 8 | 192 | 3107 | 2507 | 593 | 221 | 0 | 2021-08-18 12:39 | 2021-08-18 19:56
2021-01-18 | SAN JOAQUIN #3 1101 | SONOMA, LAKE | 20.7132 | 20.8294 | Sectionalization | 2021-01-19 | 0:23 | 2021-01-21 | 17:32 | 2 | 48 | 617 | 513 | 104 | 36 | 0 | 2021-08-18 12:39 | 2021-08-19 09:11
2021-01-18 | SAN JOAQUIN #3 1103 | BUTTE | 51.2175 | 51.2174 | Sectionalization | 2021-01-18 | 23:02 | 2021-01-23 | 17:40 | 5 | 120 | 705 | 614 | 90 | 62 | 0 | 2021-08-19 05:17 | 2021-08-19 10:11
2021-01-18 | SAND CREEK 1103 | SONOMA, MENDOCINO | 131.9052 | 130.1931 | Sectionalization | 2021-01-19 | 5:57 | 2021-01-19 | 16:39 | 0 | 0 | 1436 | 1332 | 67 | 157 | 0 | 2021-08-18 11:38 | 2021-08-18 17:39
2021-01-18 | SANTA MARIA 1108 | TEHAMA | 63.9535 | 36.5482 | Sectionalization | 2021-01-19 | 8:10 | 2021-01-20 | 9:44 | 1 | 24 | 5395 | 4794 | 581 | 148 | 0 | 2021-08-18 17:08 | 2021-08-19 11:46
2021-01-18 | SCE TEHACHAPI 1101 | TEHAMA | 0.28152 | 0.28152 | Sectionalization | 2021-01-19 | 2:36 | 2021-01-20 | 8:48 | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 2021-08-18 17:08 | 2021-08-19 12:00
2021-01-18 | SISQUOC 1103 | COLUSA | 31.276 | 5.87 | Sectionalization | 2021-01-19 | 8:06 | 2021-01-20 | 9:41 | 1 | 24 | 131 | 25 | 69 | 6 | 0 | 2021-08-18 14:46 | 2021-08-18 17:22
2021-01-18 | SO. CAL. EDISON #3 1101 | SHASTA, TEHAMA | 0 | 0.73815 | Sectionalization | 2021-01-19 | 1:13 | 2021-01-20 | 11:39 | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 2021-08-18 17:08 | 2021-08-19 13:19
2021-01-18 | TEJON 1103 | SHASTA | 39.677 | 1.5026 | Sectionalization | 2021-01-19 | 6:52 | 2021-01-20 | 8:30 | 1 | 24 | 129 | 28 | 48 | 0 | 0 | 2021-08-18 17:08 | 2021-08-19 12:08
2021-08-17 | SILVERADO 2104 | MADERA | 2.2423 | 2.2423 | Microgrids | 2021-08-17 21:10 | 44425.8819 | 2021-08-18 17:05 | 44426.7319 | 0.82986 | 19.9167 | 48 | 40 | 8 | 2 | 5 | 2021-01-20 04:22 | 2021-01-23 17:40
2021-08-17 | PARADISE 1105 | TULARE | 1.5727 | 1.5727 | Microgrids | 2021-08-17 18:43 | 44425.7799 | 2021-08-18 14:35 | 44426.6139 | 0.82778 | 19.8667 | 35 | 3 | 32 | 0 | 2 | 2021-01-19 14:03 | 2021-01-19 16:39
2021-08-17 | VOLTA 1102 | SAN LUIS OBISPO, SANTA BARBARA | 3.0227 | 3.0227 | Microgrids | 2021-08-17 18:45 | 44425.7819 | 2021-08-19 11:08 | 44427.4597 | 1.6826 | 40.3833 | 82 | 36 | 44 | 5 | 5 | 2021-01-20 04:22 | 2021-01-20 09:44
2021-08-17 | VOLTA 1102 | KERN | 0 | 0 | Backup Generation | 2021-08-17 11:15 | 44425.4688 | 2021-08-19 16:22 | 44427.6819 | 2.2132 | 53.1167 | 1 | 0 | 1 | 0 | 0 | 2021-01-20 04:22 | 2021-01-20 09:16
2021-08-17 | CALISTOGA 1102 | SANTA BARBARA | 22.6376 | 1.6963 | Microgrids | 2021-08-17 22:07 | 44425.9215 | 2021-08-18 18:29 | 44426.7188 | 0.84861 | 20.3667 | 2902 | 2180 | 711 | 89 | 833 | 2021-01-20 04:22 | 2021-01-20 09:41
2021-08-17 | ANDERSON 1101 | SHASTA, TEHAMA | 7.8735 | 0.36177 | Sectionalization | 2021-08-17 | 18:04 | 2021-08-18 | 20:11 | 1 | 24 | 1214 | 1113 | 100 | 127 | 465 | 2021-08-19 05:17 | 2021-08-19 13:04
2021-08-17 | ANDERSON 1103 | PLUMAS | 27.4586 | 4.5203 | Sectionalization | 2021-08-17 | 18:50 | 2021-08-18 | 20:40 | 1 | 24 | 835 | 734 | 92 | 69 | 99 | 2021-08-18 07:58 | 2021-08-18 11:26
2021-08-17 | ANTLER 1101 | BUTTE | 19.7654 | 21.7982 | Sectionalization | 2021-08-17 | 18:21 | 2021-08-18 | 17:19 | 1 | 24 | 555 | 452 | 94 | 31 | 98 | 2021-08-19 05:17 | 2021-08-19 12:34
2021-08-17 | ARBUCKLE 1101 | SHASTA | 45.671 | 0 | Sectionalization | 2021-08-17 | 18:34 | 2021-08-18 | 16:14 | 1 | 24 | 585 | 432 | 82 | 19 | 0 | 2021-08-18 17:08 | 2021-08-18 19:56
2021-08-17 | ARBUCKLE 1104 | SHASTA | 95.9991 | 4.4409e-16 | Sectionalization | 2021-08-17 | 18:33 | 2021-08-18 | 16:45 | 1 | 24 | 1157 | 823 | 159 | 49 | 1 | 2021-08-18 17:08 | 2021-08-19 10:24
2021-08-17 | BURNEY 1101 | SONOMA | 60.1401 | 52.8985 | Sectionalization | 2021-08-17 | 17:32 | 2021-08-18 | 11:40 | 1 | 24 | 1650 | 1445 | 181 | 144 | 113 | 2021-08-18 09:29 | 2021-08-18 15:15
2021-08-17 | BUTTE 1105 | SONOMA | 44.9324 | 26.2387 | Sectionalization | 2021-08-17 | 19:00 | 2021-08-18 | 14:25 | 1 | 24 | 1023 | 608 | 405 | 39 | 19 | 2021-08-18 07:58 | 2021-08-18 12:08
2021-08-17 | CALISTOGA 1101 | SONOMA | 0 | 0 | Sectionalization | 2021-08-17 | 18:40 | 2021-08-18 | 19:56 | 1 | 24 | 9 | 0 | 2 | 1 | 0 | 2021-08-18 07:58 | 2021-08-18 13:22
2021-08-17 | CALPINE 1146 | COLUSA, GLENN | 0 | 0 | Sectionalization | 2021-08-17 | 20:00 | 2021-08-19 | 9:11 | 2 | 48 | 0 | 0 | 0 | 0 | 0 | 2021-08-18 15:24 | 2021-08-19 12:22
2021-08-17 | CLARK ROAD 1102 | SONOMA | 78.677 | 68.8134 | Sectionalization | 2021-08-17 | 19:06 | 2021-08-19 | 10:11 | 2 | 48 | 641 | 542 | 77 | 49 | 106 | 2021-08-18 07:58 | 2021-08-18 18:57
2021-08-17 | CLOVERDALE 1102 | SONOMA | 108.2696 | 63.9896 | Sectionalization | 2021-08-17 | 19:23 | 2021-08-18 | 17:39 | 1 | 24 | 2480 | 2131 | 269 | 150 | 7 | 2021-08-18 11:38 | 2021-08-18 16:37
2021-08-17 | CORNING 1101 | SHASTA | 110.4658 | 0 | Sectionalization | 2021-08-17 | 19:16 | 2021-08-19 | 11:46 | 2 | 48 | 1496 | 1196 | 181 | 95 | 0 | 2021-08-18 17:08 | 2021-08-19 09:18
2021-08-17 | CORNING 1102 | GLENN | 119.3159 | 0.028029 | Sectionalization | 2021-08-17 | 19:08 | 2021-08-19 | 12:00 | 2 | 48 | 1466 | 1154 | 140 | 85 | 0 | 2021-08-18 16:41 | 2021-08-18 19:39
2021-08-17 | CORTINA 1101 | LAKE | 73.8518 | 0 | Sectionalization | 2021-08-17 | 18:42 | 2021-08-18 | 17:22 | 1 | 24 | 311 | 97 | 68 | 6 | 0 | 2021-08-18 12:39 | 2021-08-19 15:10
2021-08-17 | COTTONWOOD 1101 | LAKE | 17.6887 | 0 | Sectionalization | 2021-08-17 | 17:38 | 2021-08-19 | 13:19 | 2 | 48 | 715 | 648 | 65 | 61 | 0 | 2021-08-18 12:39 | 2021-08-19 15:31
2021-08-17 | COTTONWOOD 1102 | SOLANO | 11.7767 | 0.017203 | Sectionalization | 2021-08-17 | 17:28 | 2021-08-19 | 12:08 | 2 | 48 | 806 | 701 | 101 | 70 | 0 | 2021-08-18 07:58 | 2021-08-18 12:48
2021-08-17 | COTTONWOOD 1103 | SOLANO | 11.7539 | 0.63595 | Sectionalization | 2021-08-17 | 17:29 | 2021-08-19 | 13:04 | 2 | 48 | 305 | 220 | 80 | 18 | 0 | 2021-08-18 07:58 | 2021-08-18 12:50
2021-08-17 | CRESCENT MILLS 2101 | SHASTA | 69.1724 | 40.7311 | Sectionalization | 2021-08-17 | 18:52 | 2021-08-18 | 11:26 | 1 | 24 | 732 | 596 | 109 | 36 | 77 | 2021-08-18 17:08 | 2021-08-19 13:31
2021-08-17 | CRESTA 1101 | SHASTA | 3.8672 | 4.2136 | Sectionalization | 2021-08-17 | 19:18 | 2021-08-19 | 12:34 | 2 | 48 | 0 | 0 | 0 | 0 | 0 | 2021-08-18 17:08 | 2021-08-19 16:07
2021-08-17 | DESCHUTES 1101 | SHASTA | 93.6785 | 75.1446 | Sectionalization | 2021-08-17 | 17:47 | 2021-08-18 | 19:56 | 1 | 24 | 919 | 853 | 51 | 66 | 169 | 2021-08-18 17:08 | 2021-08-18 20:56
2021-08-17 | DESCHUTES 1104 | LAKE | 110.4275 | 59.9319 | Sectionalization | 2021-08-17 | 18:39 | 2021-08-19 | 10:24 | 2 | 48 | 1998 | 1732 | 242 | 164 | 261 | 2021-08-18 09:29 | 2021-08-18 19:04
2021-08-17 | DUNBAR 1101 | SONOMA | 49.7172 | 18.3061 | Sectionalization | 2021-08-17 | 18:41 | 2021-08-18 | 15:15 | 1 | 24 | 3083 | 2812 | 214 | 284 | 136 | 2021-08-18 07:58 | 2021-08-18 12:57
2021-08-17 | DUNBAR 1102 | GLENN | 59.2934 | 45.5759 | Sectionalization | 2021-08-17 | 18:51 | 2021-08-18 | 12:08 | 1 | 24 | 2257 | 2034 | 186 | 105 | 104 | 2021-08-18 15:24 | 2021-08-18 18:05
2021-08-17 | DUNBAR 1103 | YOLO | 57.4551 | 25.7892 | Sectionalization | 2021-08-17 | 18:53 | 2021-08-18 | 13:22 | 1 | 24 | 2113 | 1937 | 137 | 97 | 61 | 2021-08-18 14:46 | 2021-08-18 16:43
2021-08-17 | ELK CREEK 1101 | YOLO | 7.8913 | 7.9166 | Sectionalization | 2021-08-17 | 12:51 | 2021-08-19 | 12:22 | 2 | 48 | 9 | 7 | 2 | 0 | 0 | 2021-08-18 14:46 | 2021-08-18 19:34
2021-08-17 | GEYSERVILLE 1101 | COLUSA | 121.9473 | 47.9658 | Sectionalization | 2021-08-17 | 19:05 | 2021-08-18 | 18:57 | 1 | 24 | 1425 | 923 | 307 | 45 | 0 | 2021-08-18 15:24 | 2021-08-18 17:59
2021-08-17 | GEYSERVILLE 1102 | LASSEN, SHASTA | 75.458 | 20.1436 | Sectionalization | 2021-08-17 | 18:45 | 2021-08-18 | 16:37 | 1 | 24 | 842 | 476 | 199 | 19 | 1 | 2021-08-18 07:58 | 2021-08-19 16:12
2021-08-17 | GIRVAN 1102 | NAPA, SONOMA, LAKE | 44.3603 | 10.159 | Sectionalization | 2021-08-17 | 17:35 | 2021-08-19 | 9:18 | 2 | 48 | 819 | 567 | 241 | 55 | 86 | 2021-08-18 12:39 | 2021-08-19 12:13
2021-08-17 | GLENN 1101 | LAKE | 140.8316 | 0 | Sectionalization | 2021-08-17 | 19:17 | 2021-08-18 | 19:39 | 1 | 24 | 1779 | 1449 | 192 | 112 | 0 | 2021-08-18 09:29 | 2021-08-18 16:31
2021-08-17 | HIGHLANDS 1102 | NAPA, SOLANO | 59.8207 | 32.1626 | Sectionalization | 2021-08-17 | 19:18 | 2021-08-19 | 15:10 | 2 | 48 | 3423 | 3051 | 359 | 361 | 3 | 2021-08-18 09:29 | 2021-08-18 19:34
2021-08-17 | HIGHLANDS 1103 | NAPA | 34.9922 | 26.8185 | Sectionalization | 2021-08-17 | 19:13 | 2021-08-19 | 15:31 | 2 | 48 | 1133 | 942 | 188 | 84 | 219 | 2021-08-18 07:58 | 2021-08-18 13:47
2021-08-17 | JAMESON 1102 | SHASTA | 43.3062 | 6.2924 | Sectionalization | 2021-08-17 | 19:36 | 2021-08-18 | 12:48 | 1 | 24 | 2040 | 1912 | 120 | 158 | 14 | 2021-08-18 17:08 | 2021-08-18 20:01
2021-08-17 | JAMESON 1105 | SHASTA | 76.2786 | 8.042 | Sectionalization | 2021-08-17 | 20:00 | 2021-08-18 | 12:50 | 1 | 24 | 2488 | 1922 | 461 | 93 | 16 | 2021-08-18 17:08 | 2021-08-19 15:16
2021-08-17 | JESSUP 1101 | SHASTA | 15.1016 | 4.9026 | Sectionalization | 2021-08-17 | 17:51 | 2021-08-19 | 13:31 | 2 | 48 | 515 | 383 | 131 | 36 | 43 | 2021-08-18 17:08 | 2021-08-18 20:42
2021-08-17 | JESSUP 1102 | BUTTE | 11.3423 | 0 | Sectionalization | 2021-08-17 | 17:35 | 2021-08-19 | 16:07 | 2 | 48 | 761 | 518 | 238 | 59 | 26 | 2021-08-18 09:29 | 2021-08-18 17:57
2021-08-17 | JESSUP 1103 | BUTTE | 42.4137 | 3.6188 | Sectionalization | 2021-08-17 | 17:28 | 2021-08-18 | 20:57 | 1 | 24 | 1472 | 1325 | 139 | 139 | 9 | 2021-08-18 11:38 | 2021-08-18 18:17
2021-08-17 | KONOCTI 1108 | SHASTA, TEHAMA | 22.361 | 13.8974 | Sectionalization | 2021-08-17 | 19:02 | 2021-08-18 | 19:04 | 1 | 24 | 1288 | 1221 | 64 | 133 | 336 | 2021-08-18 17:08 | 2021-08-18 19:39
2021-08-17 | LAKEVILLE 1102 | SHASTA, TEHAMA | 57.5637 | 13.3687 | Sectionalization | 2021-08-17 | 19:20 | 2021-08-18 | 12:57 | 1 | 24 | 1320 | 1138 | 130 | 88 | 2 | 2021-08-18 17:08 | 2021-08-19 11:56
2021-08-17 | LOGAN CREEK 2102 | BUTTE | 239.056 | 0 | Sectionalization | 2021-08-17 | 19:03 | 2021-08-18 | 18:05 | 1 | 24 | 1373 | 751 | 315 | 49 | 0 | 2021-08-18 09:29 | 2021-08-18 16:23
2021-08-17 | MADISON 1105 | BUTTE | 79.2451 | 0 | Sectionalization | 2021-08-17 | 19:06 | 2021-08-18 | 16:43 | 1 | 24 | 516 | 284 | 104 | 17 | 0 | 2021-08-18 09:29 | 2021-08-18 14:45
2021-08-17 | MADISON 2101 | BUTTE | 150.1331 | 0.83684 | Sectionalization | 2021-08-17 | 18:30 | 2021-08-18 | 19:34 | 1 | 24 | 1739 | 1272 | 277 | 109 | 0 | 2021-08-18 09:29 | 2021-08-18 13:28
2021-08-17 | MAXWELL 1105 | MENDOCINO | 75.4448 | 0 | Sectionalization | 2021-08-17 | 18:37 | 2021-08-18 | 17:59 | 1 | 24 | 750 | 527 | 152 | 27 | 0 | 2021-08-18 07:58 | 2021-08-18 11:27
2021-08-17 | MC ARTHUR 1101 | NAPA | 175.8805 | 59.3907 | Sectionalization | 2021-08-17 | 17:46 | 2021-08-19 | 16:12 | 2 | 48 | 1273 | 913 | 222 | 62 | 83 | 2021-08-18 09:29 | 2021-08-18 13:58
2021-08-17 | MIDDLETOWN 1101 | NAPA | 29.6604 | 13.9082 | Sectionalization | 2021-08-17 | 19:00 | 2021-08-19 | 12:13 | 2 | 48 | 744 | 564 | 168 | 31 | 171 | 2021-08-18 09:29 | 2021-08-18 15:01
2021-08-17 | MIDDLETOWN 1102 | NAPA | 50.694 | 30.9329 | Sectionalization | 2021-08-17 | 18:45 | 2021-08-18 | 16:31 | 1 | 24 | 1634 | 1430 | 195 | 119 | 278 | 2021-08-18 07:58 | 2021-08-18 18:28
2021-08-17 | MONTICELLO 1101 | NAPA | 15.9039 | 14.0948 | Sectionalization | 2021-08-17 | 18:32 | 2021-08-18 | 19:34 | 1 | 24 | 198 | 185 | 13 | 16 | 5 | 2021-08-18 07:58 | 2021-08-18 19:25
2021-08-17 | NAPA 1112 | YOLO, SOLANO | 56.9599 | 13.3219 | Sectionalization | 2021-08-17 | 18:38 | 2021-08-18 | 13:47 | 1 | 24 | 2747 | 2565 | 141 | 146 | 10 | 2021-08-18 14:46 | 2021-08-18 17:29
2021-08-17 | OREGON TRAIL 1102 | YOLO, SOLANO | 45.4195 | 40.5993 | Sectionalization | 2021-08-17 | 18:35 | 2021-08-18 | 20:01 | 1 | 24 | 612 | 547 | 63 | 67 | 145 | 2021-08-18 10:20 | 2021-08-18 15:25
2021-08-17 | OREGON TRAIL 1103 | YOLO | 33.5178 | 31.5515 | Sectionalization | 2021-08-17 | 18:44 | 2021-08-19 | 15:16 | 2 | 48 | 621 | 597 | 22 | 52 | 193 | 2021-08-18 14:46 | 2021-08-18 16:42
2021-08-17 | OREGON TRAIL 1104 | TEHAMA | 38.409 | 28.4952 | Sectionalization | 2021-08-17 | 18:37 | 2021-08-18 | 20:42 | 1 | 24 | 640 | 541 | 95 | 52 | 150 | 2021-08-19 05:17 | 2021-08-19 13:05
2021-08-17 | ORO FINO 1101 | TEHAMA | 0 | 0 | Sectionalization | 2021-08-17 | 18:28 | 2021-08-18 | 17:57 | 1 | 24 | 12 | 9 | 3 | 0 | 0 | 2021-08-18 17:08 | 2021-08-19 16:55
2021-08-17 | ORO FINO 1102 | YOLO, TEHAMA | 63.3775 | 63.9757 | Sectionalization | 2021-08-17 | 19:01 | 2021-08-18 | 18:17 | 1 | 24 | 787 | 704 | 73 | 57 | 143 | 2021-08-19 05:17 | 2021-08-19 13:00
2021-08-17 | PANORAMA 1101 | TEHAMA | 29.4786 | 2.6607 | Sectionalization | 2021-08-17 | 17:38 | 2021-08-18 | 19:39 | 1 | 24 | 674 | 546 | 121 | 55 | 78 | 2021-08-19 05:17 | 2021-08-19 11:50
2021-08-17 | PANORAMA 1102 | LAKE | 80.1414 | 18.729 | Sectionalization | 2021-08-17 | 19:45 | 2021-08-19 | 11:56 | 2 | 48 | 2418 | 2274 | 109 | 257 | 25 | 2021-08-18 12:39 | 2021-08-19 15:10
2021-08-17 | PARADISE 1104 | LAKE | 21.6588 | 9.7139 | Sectionalization | 2021-08-17 | 19:15 | 2021-08-18 | 16:23 | 1 | 24 | 426 | 336 | 90 | 18 | 38 | 2021-08-18 09:29 | 2021-08-18 16:44
2021-08-17 | PARADISE 1105 | SONOMA | 36.0981 | 17.6877 | Sectionalization | 2021-08-17 | 18:28 | 2021-08-18 | 14:45 | 1 | 24 | 821 | 651 | 168 | 56 | 106 | 2021-08-18 09:29 | 2021-08-18 16:01
2021-08-17 | PARADISE 1106 | SONOMA | 25.5888 | 23.7141 | Sectionalization | 2021-08-17 | 18:56 | 2021-08-18 | 13:28 | 1 | 24 | 456 | 392 | 64 | 27 | 62 | 2021-08-18 09:29 | 2021-08-19 02:31
2021-08-17 | PHILO 1101 | NAPA | 72.8271 | 52.5006 | Sectionalization | 2021-08-17 | 19:28 | 2021-08-18 | 11:27 | 1 | 24 | 982 | 768 | 183 | 31 | 0 | 2021-08-18 09:29 | 2021-08-18 14:49
2021-08-17 | PUEBLO 1104 | SONOMA | 38.8716 | 11.4607 | Sectionalization | 2021-08-17 | 18:30 | 2021-08-18 | 13:58 | 1 | 24 | 1718 | 1575 | 111 | 82 | 0 | 2021-08-18 09:29 | 2021-08-18 16:33
2021-08-17 | PUEBLO 1105 | NAPA | 60.1996 | 11.2784 | Sectionalization | 2021-08-17 | 18:31 | 2021-08-18 | 15:01 | 1 | 24 | 1972 | 1731 | 156 | 83 | 4 | 2021-08-18 09:29 | 2021-08-18 23:55
2021-08-17 | PUEBLO 2102 | SONOMA | 115.6966 | 19.7847 | Sectionalization | 2021-08-17 | 18:21 | 2021-08-18 | 18:28 | 1 | 24 | 2155 | 1519 | 410 | 47 | 4 | 2021-08-18 07:58 | 2021-08-18 12:43
2021-08-17 | PUEBLO 2103 | SONOMA | 89.9876 | 18.2921 | Sectionalization | 2021-08-17 | 18:46 | 2021-08-18 | 19:25 | 1 | 24 | 4442 | 4148 | 187 | 340 | 6 | 2021-08-18 07:58 | 2021-08-18 13:23
2021-08-17 | PUTAH CREEK 1102 | SHASTA | 25.7932 | 5.1182 | Sectionalization | 2021-08-17 | 20:51 | 2021-08-18 | 17:29 | 1 | 24 | 691 | 563 | 84 | 40 | 1 | 2021-08-18 17:08 | 2021-08-19 11:59
2021-08-17 | PUTAH CREEK 1103 | TEHAMA | 44.021 | 0.39394 | Sectionalization | 2021-08-17 | 18:29 | 2021-08-18 | 15:25 | 1 | 24 | 2066 | 1835 | 165 | 141 | 0 | 2021-08-18 17:08 | 2021-08-19 08:05
2021-08-17 | PUTAH CREEK 1105 | SOLANO | 87.8802 | 0.70386 | Sectionalization | 2021-08-17 | 18:32 | 2021-08-18 | 16:42 | 1 | 24 | 1018 | 735 | 171 | 34 | 0 | 2021-08-18 10:20 | 2021-08-18 16:36
2021-08-17 | RED BLUFF 1101 | SOLANO | 20.3166 | 0.17038 | Sectionalization | 2021-08-17 | 17:55 | 2021-08-19 | 13:05 | 2 | 48 | 888 | 819 | 69 | 76 | 0 | 2021-08-18 09:29 | 2021-08-18 14:45
2021-08-17 | RED BLUFF 1103 | SOLANO | 27.116 | 0.086786 | Sectionalization | 2021-08-17 | 17:40 | 2021-08-19 | 16:55 | 2 | 48 | 2449 | 2181 | 268 | 198 | 0 | 2021-08-18 10:20 | 2021-08-19 09:36
2021-08-17 | RED BLUFF 1104 | SHASTA | 12.7126 | 1.779 | Sectionalization | 2021-08-17 | 17:43 | 2021-08-19 | 13:00 | 2 | 48 | 640 | 591 | 44 | 59 | 0 | 2021-08-18 09:29 | 2021-08-18 19:00
2021-08-17 | RED BLUFF 1105 | SHASTA, TEHAMA | 11.7482 | 0 | Sectionalization | 2021-08-17 | 17:29 | 2021-08-19 | 11:50 | 2 | 48 | 931 | 658 | 229 | 58 | 0 | 2021-08-18 09:29 | 2021-08-18 21:45
2021-08-17 | REDBUD 1101 | COLUSA | 28.1292 | 16.9511 | Sectionalization | 2021-08-17 | 18:52 | 2021-08-19 | 15:10 | 2 | 48 | 1436 | 1302 | 114 | 127 | 176 | 2021-09-20 13:52 | 2021-09-20 16:12
2021-08-17 | REDBUD 1102 | KERN | 55.7797 | 24.6127 | Sectionalization | 2021-08-17 | 18:45 | 2021-08-18 | 16:44 | 1 | 24 | 3176 | 3010 | 152 | 312 | 728 | 2021-09-21 14:36 | 2021-09-21 16:46
2021-08-17 | RINCON 1101 | COLUSA | 52.4617 | 20.3597 | Sectionalization | 2021-08-17 | 19:21 | 2021-08-18 | 16:01 | 1 | 24 | 3538 | 3316 | 204 | 312 | 162 | 2021-09-20 13:52 | 2021-09-20 15:45
2021-08-17 | RINCON 1103 | YOLO, COLUSA | 21.9612 | 8.5359 | Sectionalization | 2021-08-17 | 18:55 | 2021-08-19 | 2:31 | 2 | 48 | 1535 | 1490 | 42 | 118 | 75 | 2021-09-20 13:52 | 2021-09-20 15:51
2021-08-17 | SILVERADO 2102 | TEHAMA | 95.6628 | 41.3623 | Sectionalization | 2021-08-17 | 18:38 | 2021-08-18 | 14:49 | 1 | 24 | 1116 | 557 | 331 | 10 | 5 | 2021-09-20 14:34 | 2021-09-21 00:45
2021-08-17 | SILVERADO 2103 | TEHAMA | 52.5377 | 10.1466 | Sectionalization | 2021-08-17 | 19:41 | 2021-08-18 | 16:33 | 1 | 24 | 943 | 562 | 221 | 10 | 3 | 2021-09-20 14:34 | 2021-09-20 19:13
2021-08-17 | SILVERADO 2104 | COLUSA | 27.9323 | 20.5651 | Sectionalization | 2021-08-17 | 18:22 | 2021-08-18 | 23:55 | 1 | 24 | 1774 | 1449 | 306 | 68 | 4 | 2021-09-20 13:52 | 2021-09-20 16:12
2021-08-17 | SONOMA 1103 | GLENN | 30.2232 | 8.9793 | Sectionalization | 2021-08-17 | 19:19 | 2021-08-18 | 12:43 | 1 | 24 | 2125 | 1690 | 415 | 72 | 11 | 2021-09-20 14:34 | 2021-09-20 16:54
2021-08-17 | SONOMA 1104 | LAKE | 58.1384 | 14.5659 | Sectionalization | 2021-08-17 | 19:27 | 2021-08-18 | 13:23 | 1 | 24 | 3036 | 2763 | 227 | 117 | 16 | 2021-09-20 16:11 | 2021-09-20 17:49
2021-08-17 | STILLWATER 1101 | YOLO | 0.81646 | 0.40608 | Sectionalization | 2021-08-17 | 18:56 | 2021-08-19 | 11:59 | 2 | 48 | 5 | 5 | 0 | 1 | 1 | 2021-09-20 13:52 | 2021-09-20 15:33
2021-08-17 | TYLER 1105 | COLUSA | 24.9346 | 0.15944 | Sectionalization | 2021-08-17 | 18:22 | 2021-08-19 | 8:05 | 2 | 48 | 1156 | 969 | 173 | 101 | 0 | 2021-09-20 16:11 | 2021-09-20 17:59
2021-08-17 | VACA DIXON 1105 | NAPA, SOLANO | 58.2026 | 0.29301 | Sectionalization | 2021-08-17 | 18:26 | 2021-08-18 | 16:36 | 1 | 24 | 1106 | 997 | 97 | 129 | 0 | 2021-09-20 12:25 | 2021-09-20 14:23
2021-08-17 | VACAVILLE 1104 | YOLO | 35.4049 | 19.9861 | Sectionalization | 2021-08-17 | 20:36 | 2021-08-18 | 14:45 | 1 | 24 | 1356 | 1108 | 235 | 92 | 2 | 2021-09-20 13:52 | 2021-09-20 15:17
2021-08-17 | VACAVILLE 1108 | KERN | 18.8477 | 0.69752 | Sectionalization | 2021-08-17 | 18:28 | 2021-08-19 | 9:36 | 2 | 48 | 1969 | 1735 | 229 | 186 | 0 | 2021-09-21 14:36 | 2021-09-21 16:46
2021-08-17 | WHITMORE 1101 | TEHAMA | 35.9313 | 39.7987 | Sectionalization | 2021-08-17 | 18:43 | 2021-08-18 | 19:00 | 1 | 24 | 243 | 225 | 14 | 14 | 25 | 2021-09-20 14:34 | 2021-09-20 16:42
2021-08-17 | WILDWOOD 1101 | SOLANO | 28.6957 | 28.6957 | Sectionalization | 2021-08-17 | 17:44 | 2021-08-18 | 21:45 | 1 | 24 | 121 | 86 | 32 | 3 | 17 | 2021-09-20 12:25 | 2021-09-20 15:38
2021-09-20 | CORTINA 1101 | MADERA, MARIPOSA | 0 | 0 | Backup Generation | 2021-09-19 14:25 | 44458.6007 | 2021-09-21 14:25 | 44460.6007 | 2 | 48 | 1 | 1 | 0 | 0 | 0 | 2021-09-20 13:52 | 2021-09-20 16:12
2021-09-20 | TEJON 1102 | MADERA | 0 | 0 | Backup Generation | 2021-09-20 13:45 | 44459.5729 | 2021-09-21 13:45 | 44460.5729 | 1 | 24 | 1 | 0 | 1 | 0 | 0 | 2021-01-20 04:22 | 2021-01-21 17:32
2021-09-20 | ARBUCKLE 1101 | SOLANO | 45.671 | 0 | Sectionalization | 2021-09-20 | 6:05 | 2021-09-20 | 15:45 | 0 | 0 | 586 | 433 | 82 | 20 | 15 | 2021-09-20 12:25 | 2021-09-20 14:52
2021-09-20 | ARBUCKLE 1104 | LAKE | 94.3563 | 0 | Sectionalization | 2021-09-20 | 6:09 | 2021-09-20 | 15:51 | 0 | 0 | 1152 | 817 | 158 | 49 | 58 | 2021-10-12 07:22 | 2021-10-12 14:43
2021-09-20 | CORNING 1101 | LAKE | 110.4683 | 0 | Sectionalization | 2021-09-20 | 6:10 | 2021-09-21 | 0:45 | 1 | 24 | 1491 | 1190 | 181 | 97 | 81 | 2021-10-12 07:22 | 2021-10-12 14:43
2021-09-20 | CORNING 1102 | LAKE | 119.3159 | 0.028029 | Sectionalization | 2021-09-20 | 6:18 | 2021-09-20 | 19:13 | 0 | 0 | 1465 | 1156 | 137 | 85 | 79 | 2021-10-12 07:22 | 2021-10-12 14:43
2021-09-20 | CORTINA 1101 | LAKE | 73.8518 | 0 | Sectionalization | 2021-09-20 | 6:11 | 2021-09-20 | 16:12 | 0 | 0 | 312 | 97 | 69 | 6 | 2 | 2021-10-12 07:22 | 2021-10-12 14:43
2021-09-20 | GLENN 1101 | LAKE | 140.8316 | 0 | Sectionalization | 2021-09-20 | 6:33 | 2021-09-20 | 16:54 | 0 | 0 | 1778 | 1448 | 192 | 113 | 84 | 2021-10-12 07:22 | 2021-10-12 14:43
2021-09-20 | HIGHLANDS 1103 | LAKE | 110.3517 | 96.3593 | Sectionalization | 2021-09-20 | 6:08 | 2021-09-20 | 17:49 | 0 | 0 | 2369 | 2072 | 268 | 187 | 60 | 2021-10-12 07:22 | 2021-10-12 14:43
2021-09-20 | MADISON 2101 | KERN | 172.8027 | 2.7963 | Sectionalization | 2021-09-20 | 6:13 | 2021-09-20 | 15:33 | 0 | 0 | 1957 | 1418 | 300 | 114 | 49 | 2021-10-12 08:53 | 2021-10-13 01:45
2021-09-20 | MAXWELL 1105 | KERN | 75.4448 | 0 | Sectionalization | 2021-09-20 | 6:14 | 2021-09-20 | 17:59 | 0 | 0 | 751 | 528 | 152 | 27 | 37 | 2021-10-12 08:53 | 2021-10-13 01:45
2021-09-20 | MONTICELLO 1101 | SOLANO | 129.7524 | 113.656 | Sectionalization | 2021-09-20 | 6:40 | 2021-09-20 | 14:23 | 0 | 0 | 1126 | 905 | 172 | 72 | 9 | 2021-10-11 18:51 | 2021-10-12 15:49
2021-09-20 | PUTAH CREEK 1105 | SOLANO | 87.8802 | 0.70386 | Sectionalization | 2021-09-20 | 6:16 | 2021-09-20 | 15:17 | 0 | 0 | 1020 | 737 | 170 | 36 | 10 | 2021-10-12 12:20 | 2021-10-12 17:07
2021-09-20 | TEJON 1102 | SHASTA | 35.4314 | 0 | Sectionalization | 2021-09-20 | 22:25 | 2021-09-21 | 16:46 | 1 | 24 | 209 | 0 | 188 | 0 | 0 | 2021-10-11 17:45 | 2021-10-12 09:18
2021-09-20 | TYLER 1105 | KERN | 69.4821 | 11.7273 | Sectionalization | 2021-09-20 | 6:20 | 2021-09-20 | 16:42 | 0 | 0 | 1681 | 1443 | 208 | 164 | 31 | 2021-10-12 10:23 | 2021-10-12 12:24
2021-09-20 | VACAVILLE 1104 | COLUSA | 15.0981 | 4.3405 | Sectionalization | 2021-09-20 | 6:56 | 2021-09-20 | 15:38 | 0 | 0 | 1247 | 1041 | 203 | 85 | 28 | 2021-10-12 12:20 | 2021-10-12 15:06
2021-09-20 | VACAVILLE 1108 | YOLO, COLUSA | 49.5462 | 16.9316 | Sectionalization | 2021-09-20 | 6:18 | 2021-09-20 | 14:52 | 0 | 0 | 2222 | 1930 | 271 | 203 | 30 | 2021-10-12 12:20 | 2021-10-12 15:40
2021-10-11 | MIDDLETOWN 1102 | FRESNO | 0 | 0 | Backup Generation | 2021-10-10 20:40 | 44479.8611 | 2021-10-13 08:20 | 44482.3472 | 2.4861 | 59.6667 | 1 | 0 | 1 | 0 | 0 | 2021-01-20 04:22 | 2021-01-20 09:32
2021-10-11 | MIDDLETOWN 1102 | KERN | 0 | 0 | Backup Generation | 2021-10-10 22:15 | 44479.9271 | 2021-10-13 08:40 | 44482.3611 | 2.434 | 58.4167 | 1 | 0 | 1 | 0 | 0 | 2021-01-20 04:22 | 2021-01-20 08:00
2021-10-11 | MIDDLETOWN 1102 | TULARE, FRESNO | 0 | 0 | Backup Generation | 2021-10-10 21:50 | 44479.9097 | 2021-10-13 08:52 | 44482.3694 | 2.4597 | 59.0333 | 1 | 0 | 1 | 0 | 0 | 2021-01-20 04:22 | 2021-01-20 16:20
2021-10-11 | MIDDLETOWN 1102 | TULARE, FRESNO | 0 | 0 | Backup Generation | 2021-10-10 18:16 | 44479.7611 | 2021-10-11 14:00 | 44480.5833 | 0.82222 | 19.7333 | 1 | 0 | 1 | 0 | 0 | 2021-01-20 04:22 | 2021-01-20 16:47
2021-10-11 | MIDDLETOWN 1102 | KERN | 0 | 0 | Backup Generation | 2021-10-12 17:20 | 44481.7222 | 2021-10-13 06:03 | 44482.2521 | 0.52986 | 12.7167 | 1 | 0 | 1 | 0 | 0 | 2021-01-20 04:22 | 2021-01-20 08:18
2021-10-11 | MIDDLETOWN 1102 | MARIPOSA | 0 | 0 | Backup Generation | 2021-10-11 14:30 | 44480.6042 | 2021-10-12 16:50 | 44481.7014 | 1.0972 | 26.3333 | 1 | 0 | 1 | 0 | 0 | 2021-01-19 14:03 | 2021-01-26 16:10
2021-10-11 | TEJON 1102 | MARIPOSA | 0 | 0 | Backup Generation | 2021-10-10 18:05 | 44479.7535 | 2021-10-12 15:27 | 44481.6438 | 1.8903 | 45.3667 | 1 | 0 | 1 | 0 | 0 | 2021-01-19 14:03 | 2021-01-24 14:02
2021-10-11 | TEJON 1102 | SAN LUIS OBISPO, SANTA BARBARA | 0 | 0 | Backup Generation | 2021-10-10 19:20 | 44479.8056 | 2021-10-12 15:27 | 44481.6438 | 1.8382 | 44.1167 | 1 | 0 | 1 | 0 | 0 | 2021-01-20 04:22 | 2021-01-20 10:50
2021-10-11 | VACAVILLE 1104 | BUTTE | 5.9853 | 1.6331 | Dx Switching | 2021-10-11 | 5:40 | 2021-10-12 | 13:36 | 1 | 24 | 652 | 612 | 40 | 49 | 98 | 2021-10-11 18:51 | 2021-10-12 15:49
2021-10-11 | VACAVILLE 1111 | SHASTA | 11.214 | 0.16046 | Dx Switching | 2021-10-11 | 8:02 | 2021-10-13 | 14:01 | 2 | 48 | 1206 | 1193 | 13 | 133 | 149 | 2021-10-12 12:20 | 2021-10-12 17:07
2021-10-11 | ANDERSON 1103 | KINGS | 27.4586 | 4.5203 | Sectionalization | 2021-10-11 | 6:20 | 2021-10-12 | 9:18 | 1 | 24 | 835 | 735 | 91 | 71 | 283 | 2021-10-12 10:23 | 2021-10-12 17:46
2021-10-11 | ANTELOPE 1101 | CONTRA COSTA | 36.9222 | 0 | Sectionalization | 2021-10-11 | 7:22 | 2021-10-12 | 12:24 | 1 | 24 | 82 | 6 | 37 | 3 | 0 | 2021-10-12 12:53 | 2021-10-12 17:26
2021-10-11 | ARBUCKLE 1101 | NAPA, SONOMA | 45.671 | 0 | Sectionalization | 2021-10-11 | 6:51 | 2021-10-12 | 15:06 | 1 | 24 | 589 | 434 | 82 | 21 | 137 | 2021-10-12 12:02 | 2021-10-12 15:56
2021-10-11 | ARBUCKLE 1104 | SONOMA, LAKE | 95.9991 | 0 | Sectionalization | 2021-10-11 | 7:01 | 2021-10-12 | 15:40 | 1 | 24 | 1154 | 818 | 158 | 48 | 368 | 2021-10-12 12:02 | 2021-10-14 15:22
2021-10-11 | AVENAL 2101 | SAN LUIS OBISPO | 64.8179 | 0 | Sectionalization | 2021-10-11 | 7:35 | 2021-10-12 | 17:46 | 1 | 24 | 1930 | 1677 | 218 | 83 | 1254 | 2021-10-12 08:53 | 2021-10-12 14:41
2021-10-11 | BRENTWOOD 2105 | FRESNO | 99.9857 | 0 | Sectionalization | 2021-10-11 | 9:11 | 2021-10-12 | 17:26 | 1 | 24 | 2734 | 2292 | 331 | 220 | 420 | 2021-10-12 10:23 | 2021-10-12 17:16
2021-10-11 | CALISTOGA 1101 | SAN JOAQUIN | 110.0413 | 89.9621 | Sectionalization | 2021-10-11 | 7:11 | 2021-10-12 | 15:56 | 1 | 24 | 1527 | 1193 | 220 | 64 | 134 | 2021-10-12 12:53 | 2021-10-12 14:55
2021-10-11 | CALPINE 1146 | MONTEREY, SAN LUIS OBISPO | 3.5527e-15 | 2.6645e-15 | Sectionalization | 2021-10-11 | 8:01 | 2021-10-14 | 15:22 | 3 | 72 | 0 | 0 | 0 | 0 | 0 | 2021-10-12 08:53 | 2021-10-12 12:49
2021-10-11 | CAMBRIA 1102 | BUTTE | 26.6495 | 11.4541 | Sectionalization | 2021-10-11 | 12:40 | 2021-10-12 | 14:41 | 1 | 24 | 1215 | 1130 | 77 | 37 | 96 | 2021-10-12 07:22 | 2021-10-12 10:58
2021-10-11 | CANTUA 1103 | CONTRA COSTA | 32.2746 | 0 | Sectionalization | 2021-10-11 | 7:28 | 2021-10-12 | 17:16 | 1 | 24 | 183 | 92 | 33 | 4 | 64 | 2021-10-12 12:53 | 2021-10-12 15:51
2021-10-11 | CARBONA 1101 | SONOMA, MENDOCINO | 62.4823 | 0 | Sectionalization | 2021-10-11 | 8:46 | 2021-10-12 | 14:55 | 1 | 24 | 2052 | 1868 | 138 | 102 | 297 | 2021-10-12 07:22 | 2021-10-12 10:52
2021-10-11 | CHOLAME 2102 | FRESNO | 198.6212 | 50.22 | Sectionalization | 2021-10-11 | 7:27 | 2021-10-12 | 12:49 | 1 | 24 | 540 | 214 | 205 | 11 | 19 | 2021-10-12 10:23 | 2021-10-12 18:31
2021-10-11 | CLARK ROAD 1102 | FRESNO | 80.8191 | 70.6044 | Sectionalization | 2021-10-11 | 4:07 | 2021-10-12 | 10:58 | 1 | 24 | 646 | 549 | 77 | 51 | 119 | 2021-10-12 10:23 | 2021-10-12 20:08
2021-10-11 | CLAYTON 2212 | FRESNO | 41.1655 | 4.0521 | Sectionalization | 2021-10-11 | 8:58 | 2021-10-12 | 15:51 | 1 | 24 | 2876 | 2724 | 146 | 244 | 232 | 2021-10-12 10:23 | 2021-10-12 15:58
2021-10-11 | CLOVERDALE 1102 | TEHAMA | 117.2933 | 73.0132 | Sectionalization | 2021-10-11 | 6:35 | 2021-10-12 | 10:52 | 1 | 24 | 2511 | 2152 | 271 | 159 | 381 | 2021-10-11 19:43 | 2021-10-12 12:06
2021-10-11 | COALINGA NO 1 1108 | TEHAMA | 29.1217 | 0 | Sectionalization | 2021-10-11 | 7:48 | 2021-10-12 | 18:31 | 1 | 24 | 2024 | 1892 | 131 | 148 | 890 | 2021-10-11 19:43 | 2021-10-12 15:20
2021-10-11 | COALINGA NO 1 1109 | COLUSA | 27.347 | 0 | Sectionalization | 2021-10-11 | 7:29 | 2021-10-12 | 20:08 | 1 | 24 | 1266 | 1134 | 114 | 47 | 549 | 2021-10-12 12:20 | 2021-10-12 14:49
2021-10-11 | COALINGA NO 2 1105 | SHASTA, TEHAMA | 38.9931 | 0 | Sectionalization | 2021-10-11 | 7:22 | 2021-10-12 | 15:58 | 1 | 24 | 86 | 22 | 37 | 0 | 3 | 2021-10-11 19:43 | 2021-10-12 10:40
2021-10-11 | CORNING 1101 | BUTTE | 101.3093 | 0 | Sectionalization | 2021-10-11 | 1:40 | 2021-10-12 | 12:06 | 1 | 24 | 1433 | 1154 | 171 | 96 | 577 | 2021-10-12 07:22 | 2021-10-12 13:56
2021-10-11 | CORNING 1102 | SHASTA | 119.3159 | 0.028029 | Sectionalization | 2021-10-11 | 1:34 | 2021-10-12 | 15:20 | 1 | 24 | 1466 | 1157 | 137 | 86 | 505 | 2021-10-11 17:45 | 2021-10-12 11:40
2021-10-11 | CORTINA 1101 | SHASTA | 73.8518 | 0 | Sectionalization | 2021-10-11 | 6:57 | 2021-10-12 | 14:49 | 1 | 24 | 313 | 97 | 70 | 6 | 13 | 2021-10-11 17:45 | 2021-10-12 12:14
2021-10-11 | COTTONWOOD 1103 | KINGS | 142.4883 | 118.3557 | Sectionalization | 2021-10-11 | 6:20 | 2021-10-12 | 10:40 | 1 | 24 | 2067 | 1881 | 158 | 190 | 594 | 2021-10-12 10:23 | 2021-10-12 18:38
2021-10-11 | CRESTA 1101 | SONOMA | 5.4052 | 5.4052 | Sectionalization | 2021-10-11 | 8:48 | 2021-10-12 | 13:56 | 1 | 24 | 0 | 0 | 0 | 0 | 0 | 2021-10-12 07:22 | 2021-10-12 11:09
2021-10-11 | DESCHUTES 1101 | SHASTA | 125.6144 | 101.2738 | Sectionalization | 2021-10-11 | 6:32 | 2021-10-12 | 11:40 | 1 | 24 | 1095 | 1008 | 69 | 81 | 220 | 2021-10-11 16:29 | 2021-10-12 11:32
2021-10-11 | DESCHUTES 1104 | GLENN | 129.6151 | 72.8658 | Sectionalization | 2021-10-11 | 6:23 | 2021-10-12 | 12:14 | 1 | 24 | 2303 | 2019 | 256 | 186 | 356 | 2021-10-11 19:43 | 2021-10-12 10:36
2021-10-11 | DEVILS DEN 1101 | MERCED | 39.7811 | 0 | Sectionalization | 2021-10-11 | 7:31 | 2021-10-12 | 18:38 | 1 | 24 | 55 | 8 | 31 | 0 | 1 | 2021-10-12 11:19 | 2021-10-12 13:11
2021-10-11 | GEYSERVILLE 1102 | LAKE | 111.668 | 43.5115 | Sectionalization | 2021-10-11 | 6:30 | 2021-10-12 | 11:09 | 1 | 24 | 1112 | 656 | 250 | 25 | 38 | 2021-10-12 07:22 | 2021-10-12 12:54
2021-10-11 | GIRVAN 1101 | LAKE | 2.6778 | 1.2808 | Sectionalization | 2021-10-11 | 6:38 | 2021-10-12 | 11:32 | 1 | 24 | 121 | 90 | 21 | 24 | 57 | 2021-10-12 07:22 | 2021-10-12 11:57
2021-10-11 | GLENN 1101 | SHASTA | 140.8316 | 0 | Sectionalization | 2021-10-11 | 4:00 | 2021-10-12 | 10:36 | 1 | 24 | 1777 | 1447 | 192 | 113 | 620 | 2021-10-11 16:29 | 2021-10-11 18:53
2021-10-11 | GUSTINE 1102 | BUTTE | 133.9145 | 0 | Sectionalization | 2021-10-11 | 8:27 | 2021-10-12 | 13:11 | 1 | 24 | 2166 | 1488 | 367 | 147 | 628 | 2021-10-12 07:22 | 2021-10-12 10:50
2021-10-11 | HIGHLANDS 1102 | FRESNO | 56.3842 | 28.9425 | Sectionalization | 2021-10-11 | 6:41 | 2021-10-12 | 12:54 | 1 | 24 | 3411 | 3040 | 358 | 373 | 1641 | 2021-10-12 10:23 | 2021-10-12 15:20
2021-10-11 | HIGHLANDS 1103 | SAN BENITO, MONTEREY | 51.9513 | 38.6562 | Sectionalization | 2021-10-11 | 6:31 | 2021-10-12 | 11:57 | 1 | 24 | 1372 | 1137 | 228 | 106 | 519 | 2021-10-12 07:22 | 2021-10-12 17:48
2021-10-11 | JESSUP 1102 | LAKE | 79.3551 | 50.0924 | Sectionalization | 2021-10-11 | 6:54 | 2021-10-11 | 18:53 | 0 | 0 | 2077 | 1779 | 292 | 210 | 752 | 2021-10-11 19:43 | 2021-10-12 10:00
2021-10-11 | KANAKA 1101 | KERN | 75.4045 | 75.0316 | Sectionalization | 2021-10-11 | 5:15 | 2021-10-12 | 10:50 | 1 | 24 | 452 | 414 | 33 | 37 | 135 | 2021-10-12 05:38 | 2021-10-12 10:58
2021-10-11 | KETTLEMAN HILLS 2104 | KERN | 32.327 | 0 | Sectionalization | 2021-10-11 | 7:25 | 2021-10-12 | 15:20 | 1 | 24 | 1000 | 921 | 65 | 40 | 707 | 2021-10-12 05:38 | 2021-10-12 10:57
2021-10-11 | KING CITY 1106 | GLENN | 62.5263 | 0 | Sectionalization | 2021-10-11 | 8:20 | 2021-10-12 | 17:48 | 1 | 24 | 300 | 120 | 108 | 3 | 68 | 2021-10-11 17:45 | 2021-10-12 10:09
2021-10-11 | KONOCTI 1102 | CONTRA COSTA | 146.1216 | 124.5232 | Sectionalization | 2021-10-11 | 6:21 | 2021-10-12 | 10:00 | 1 | 24 | 2780 | 2400 | 287 | 183 | 755 | 2021-10-12 12:53 | 2021-10-12 15:56
2021-10-11 | LAMONT 1102 | TEHAMA | 67.6761 | 2.2262 | Sectionalization | 2021-10-11 | 12:20 | 2021-10-12 | 10:58 | 1 | 24 | 464 | 191 | 154 | 17 | 72 | 2021-10-11 19:43 | 2021-10-12 10:31
2021-10-11 | LAMONT 1104 | SAN BENITO, MONTEREY, FRESNO | 51.9863 | 0.41144 | Sectionalization | 2021-10-11 | 12:07 | 2021-10-12 | 10:57 | 1 | 24 | 315 | 81 | 115 | 5 | 45 | 2021-10-12 07:22 | 2021-10-12 17:36
2021-10-11 | LOGAN CREEK 2102 | YOLO | 239.056 | 0 | Sectionalization | 2021-10-11 | 4:02 | 2021-10-12 | 10:09 | 1 | 24 | 1364 | 746 | 311 | 48 | 214 | 2021-10-12 12:20 | 2021-10-12 14:41
2021-10-11 | LONE TREE 2105 | YOLO | 40.8676 | 2.4715 | Sectionalization | 2021-10-11 | 8:34 | 2021-10-12 | 15:56 | 1 | 24 | 2172 | 1851 | 318 | 162 | 356 | 2021-10-12 12:20 | 2021-10-12 17:30
2021-10-11 | LOS MOLINOS 1101 | KERN | 56.9174 | 0 | Sectionalization | 2021-10-11 | 6:44 | 2021-10-12 | 10:31 | 1 | 24 | 982 | 827 | 86 | 83 | 287 | 2021-10-12 05:38 | 2021-10-12 11:01
2021-10-11 | LOS OSITOS 2103 | COLUSA | 145.5679 | 0 | Sectionalization | 2021-10-11 | 7:28 | 2021-10-12 | 17:36 | 1 | 24 | 1352 | 1001 | 227 | 26 | 393 | 2021-10-12 12:20 | 2021-10-12 14:43
2021-10-11 | MADISON 1105 | NAPA, SONOMA, LAKE | 79.2451 | 0 | Sectionalization | 2021-10-11 | 6:33 | 2021-10-12 | 14:41 | 1 | 24 | 518 | 285 | 104 | 17 | 104 | 2021-10-12 12:02 | 2021-10-12 16:55
2021-10-11 | MADISON 2101 | LAKE | 145.5534 | 0 | Sectionalization | 2021-10-11 | 7:08 | 2021-10-12 | 17:30 | 1 | 24 | 1731 | 1264 | 274 | 108 | 371 | 2021-10-12 07:22 | 2021-10-12 14:43
2021-10-11 | MAGUNDEN 1108 | LAKE | 35.124 | 1.1767 | Sectionalization | 2021-10-11 | 12:13 | 2021-10-12 | 11:01 | 1 | 24 | 1669 | 1530 | 96 | 115 | 1035 | 2021-10-12 07:22 | 2021-10-12 14:15
2021-10-11 | MAXWELL 1105 | MONTEREY | 75.4448 | 4.4409e-16 | Sectionalization | 2021-10-11 | 4:23 | 2021-10-12 | 14:43 | 1 | 24 | 752 | 529 | 152 | 26 | 184 | 2021-10-12 07:22 | 2021-10-12 12:05
2021-10-11 | MIDDLETOWN 1101 | SAN BENITO | 64.9578 | 54.9159 | Sectionalization | 2021-10-11 | 6:14 | 2021-10-12 | 16:55 | 1 | 24 | 1485 | 1249 | 219 | 72 | 377 | 2021-10-12 10:23 | 2021-10-12 14:30
2021-10-11 | MIDDLETOWN 1102 | SHASTA, TEHAMA | 2.4402 | 1.5379 | Sectionalization | 2021-10-11 | 6:20 | 2021-10-12 | 14:43 | 1 | 24 | 18 | 10 | 8 | 0 | 3 | 2021-10-11 17:45 | 2021-10-12 10:51
2021-10-11 | MIDDLETOWN 1103 | SHASTA, TEHAMA | 30.9915 | 17.2163 | Sectionalization | 2021-10-11 | 6:28 | 2021-10-12 | 14:15 | 1 | 24 | 136 | 93 | 32 | 6 | 11 | 2021-10-11 17:45 | 2021-10-12 11:41
2021-10-11 | OILFIELDS 1103 | SAN LUIS OBISPO | 154.6943 | 127.6238 | Sectionalization | 2021-10-11 | 12:20 | 2021-10-12 | 12:05 | 1 | 24 | 2286 | 2032 | 207 | 90 | 197 | 2021-10-12 08:53 | 2021-10-12 12:27
2021-10-11 | PANOCHE 1103 | NAPA | 102.9923 | 37.2609 | Sectionalization | 2021-10-11 | 7:46 | 2021-10-12 | 14:30 | 1 | 24 | 287 | 111 | 120 | 2 | 11 | 2021-10-12 10:23 | 2021-10-12 12:31
2021-10-11 | PANORAMA 1101 | NAPA | 29.4786 | 2.6607 | Sectionalization | 2021-10-11 | 6:56 | 2021-10-12 | 10:51 | 1 | 24 | 672 | 543 | 122 | 54 | 205 | 2021-10-12 10:23 | 2021-10-12 13:29
2021-10-11 | PANORAMA 1102 | YOLO, SOLANO | 58.99 | 2.4569 | Sectionalization | 2021-10-11 | 6:23 | 2021-10-12 | 11:41 | 1 | 24 | 2310 | 2185 | 99 | 251 | 885 | 2021-10-12 12:20 | 2021-10-12 18:35
2021-10-11 | PERRY 1101 | YOLO, SOLANO | 65.041 | 45.4095 | Sectionalization | 2021-10-11 | 11:48 | 2021-10-12 | 12:27 | 1 | 24 | 3441 | 2884 | 515 | 127 | 403 | 2021-10-12 12:20 | 2021-10-12 17:36
2021-10-11 | PUEBLO 1104 | YOLO | 65.0789 | 36.2268 | Sectionalization | 2021-10-11 | 6:29 | 2021-10-12 | 12:31 | 1 | 24 | 1940 | 1744 | 151 | 94 | 64 | 2021-10-12 12:20 | 2021-10-12 17:56
2021-10-11 | PUEBLO 1105 | TEHAMA | 60.1999 | 11.2786 | Sectionalization | 2021-10-11 | 7:09 | 2021-10-12 | 13:29 | 1 | 24 | 1974 | 1731 | 158 | 83 | 238 | 2021-10-11 19:43 | 2021-10-12 11:37
2021-10-11 | PUTAH CREEK 1102 | TEHAMA | 11.774 | 0 | Sectionalization | 2021-10-11 | 7:39 | 2021-10-12 | 18:35 | 1 | 24 | 576 | 492 | 62 | 38 | 129 | 2021-10-11 19:43 | 2021-10-12 16:54
2021-10-11 | PUTAH CREEK 1103 | YOLO, TEHAMA | 43.0969 | 0.088246 | Sectionalization | 2021-10-11 | 7:11 | 2021-10-12 | 17:36 | 1 | 24 | 2048 | 1817 | 165 | 142 | 606 | 2021-10-11 19:43 | 2021-10-12 13:44
2021-10-11 | PUTAH CREEK 1105 | LAKE | 83.0393 | 6.6613e-16 | Sectionalization | 2021-10-11 | 6:47 | 2021-10-12 | 17:56 | 1 | 24 | 996 | 725 | 166 | 32 | 149 | 2021-10-12 07:22 | 2021-10-12 12:53
2021-10-11 | RED BLUFF 1101 | MONTEREY, SAN LUIS OBISPO | 4.3614 | 0.17285 | Sectionalization | 2021-10-11 | 6:33 | 2021-10-12 | 11:37 | 1 | 24 | 559 | 524 | 35 | 53 | 247 | 2021-10-12 10:23 | 2021-10-12 16:33
2021-10-11 | RED BLUFF 1103 | MONTEREY, SAN LUIS OBISPO | 27.116 | 0.086784 | Sectionalization | 2021-10-11 | 1:39 | 2021-10-12 | 16:54 | 1 | 24 | 2447 | 2179 | 267 | 198 | 1065 | 2021-10-12 07:22 | 2021-10-12 13:21
2021-10-11 | RED BLUFF 1104 | MERCED | 12.7126 | 1.779 | Sectionalization | 2021-10-11 | 6:43 | 2021-10-12 | 13:44 | 1 | 24 | 640 | 591 | 44 | 56 | 193 | 2021-10-12 11:19 | 2021-10-12 13:13
2021-10-11 | REDBUD 1101 | NAPA | 65.566 | 40.6629 | Sectionalization | 2021-10-11 | 6:18 | 2021-10-12 | 12:53 | 1 | 24 | 1870 | 1693 | 142 | 173 | 625 | 2021-10-12 10:23 | 2021-10-12 16:43
2021-10-11 | SAN ARDO 1102 | NAPA | 115.0521 | 0 | Sectionalization | 2021-10-11 | 7:34 | 2021-10-12 | 16:33 | 1 | 24 | 608 | 355 | 162 | 10 | 134 | 2021-10-12 10:23 | 2021-10-12 19:13
2021-10-11 | SAN MIGUEL 1106 | SAN LUIS OBISPO, SANTA BARBARA | 57.699 | 24.0229 | Sectionalization | 2021-10-11 | 11:35 | 2021-10-12 | 13:21 | 1 | 24 | 251 | 150 | 62 | 8 | 21 | 2021-10-12 09:24 | 2021-10-12 13:37
2021-10-11 | SANTA NELLA 1104 | BUTTE | 58.0231 | 0 | Sectionalization | 2021-10-11 | 8:34 | 2021-10-12 | 13:13 | 1 | 24 | 949 | 707 | 129 | 44 | 387 | 2021-10-12 04:13 | 2021-10-12 14:24
2021-10-11 | SILVERADO 2102 | ALAMEDA | 69.2323 | 17.4536 | Sectionalization | 2021-10-11 | 6:27 | 2021-10-12 | 16:43 | 1 | 24 | 964 | 479 | 292 | 8 | 39 | 2021-10-12 12:53 | 2021-10-12 14:34
2021-10-11 | SILVERADO 2104 | CONTRA COSTA | 60.5063 | 53.1636 | Sectionalization | 2021-10-11 | 7:20 | 2021-10-12 | 19:13 | 1 | 24 | 2813 | 2377 | 382 | 132 | 445 | 2021-10-12 12:53 | 2021-10-12 15:15
2021-10-11 | SISQUOC 1102 | KERN | 115.6445 | 49.1524 | Sectionalization | 2021-10-11 | 18:04 | 2021-10-12 | 13:37 | 1 | 24 | 518 | 251 | 132 | 8 | 57 | 2021-10-12 08:53 | 2021-10-13 01:45
2021-10-11 | SYCAMORE CREEK 1111 | KERN | 26.6286 | 0.51436 | Sectionalization | 2021-10-11 | 4:06 | 2021-10-12 | 14:24 | 1 | 24 | 1513 | 1076 | 431 | 75 | 360 | 2021-10-12 05:38 | 2021-10-12 10:50
2021-10-11 | TASSAJARA 2104 | SAN LUIS OBISPO | 50.3089 | 8.6809 | Sectionalization | 2021-10-11 | 8:38 | 2021-10-12 | 14:34 | 1 | 24 | 2787 | 2673 | 113 | 139 | 191 | 2021-10-12 08:53 | 2021-10-12 14:33
2021-10-11 | TASSAJARA 2112 | SAN LUIS OBISPO | 49.9594 | 12.4475 | Sectionalization | 2021-10-11 | 8:49 | 2021-10-12 | 15:15 | 1 | 24 | 2409 | 2213 | 196 | 126 | 82 | 2021-10-12 04:13 | 2021-10-12 10:36
2021-10-11 | TEJON 1102 | TEHAMA | 35.4197 | 0 | Sectionalization | 2021-10-11 | 12:41 | 2021-10-13 | 1:45 | 2 | 48 | 208 | 0 | 187 | 0 | 0 | 2021-10-11 19:43 | 2021-10-12 10:14
2021-10-11 | TEJON 1103 | SOLANO | 34.8997 | 0 | Sectionalization | 2021-10-11 | 12:31 | 2021-10-12 | 10:50 | 1 | 24 | 117 | 24 | 40 | 0 | 1 | 2021-10-12 12:20 | 2021-10-12 14:58
2021-10-11 | TEMPLETON 2110 | SOLANO | 201.7627 | 132.2754 | Sectionalization | 2021-10-11 | 11:44 | 2021-10-12 | 14:33 | 1 | 24 | 3042 | 2484 | 425 | 111 | 332 | 2021-10-12 12:20 | 2021-10-12 14:31
2021-10-11 | TEMPLETON 2113 | SOLANO | 331.5224 | 183.4347 | Sectionalization | 2021-10-11 | 16:10 | 2021-10-12 | 10:36 | 1 | 24 | 5369 | 4536 | 650 | 275 | 795 | 2021-10-11 18:51 | 2021-10-12 15:49
2021-10-11 | TYLER 1105 | SOLANO | 24.9424 | 0.17347 | Sectionalization | 2021-10-11 | 1:36 | 2021-10-12 | 10:14 | 1 | 24 | 1149 | 963 | 172 | 104 | 471 | 2021-10-12 12:20 | 2021-10-12 17:01
2021-10-11 | VACA DIXON 1101 | SOLANO | 25.2675 | 1.3769 | Sectionalization | 2021-10-11 | 7:01 | 2021-10-12 | 14:58 | 1 | 24 | 1079 | 908 | 170 | 89 | 85 | 2021-10-12 12:20 | 2021-10-12 17:07
2021-10-11 | VACA DIXON 1105 | SOLANO | 91.2681 | 24.0361 | Sectionalization | 2021-10-11 | 7:33 | 2021-10-12 | 14:31 | 1 | 24 | 1432 | 1282 | 134 | 166 | 130 | 2021-10-12 12:20 | 2021-10-12 14:28
2021-10-11 | VACAVILLE 1104 | ALAMEDA | 20.044 | 5.6019 | Sectionalization | 2021-10-11 | 6:58 | 2021-10-12 | 15:49 | 1 | 24 | 1748 | 1507 | 239 | 125 | 386 | 2021-10-12 12:53 | 2021-10-12 16:50
2021-10-11 | VACAVILLE 1108 | SHASTA, TEHAMA | 17.9973 | 0.57086 | Sectionalization | 2021-10-11 | 7:05 | 2021-10-12 | 17:01 | 1 | 24 | 1904 | 1671 | 229 | 178 | 421 | 2021-10-12 00:13 | 2021-10-12 13:42
2021-10-11 | VACAVILLE 1111 | STANISLAUS | 1.668 | 0 | Sectionalization | 2021-10-11 | 6:55 | 2021-10-12 | 17:07 | 1 | 24 | 134 | 104 | 29 | 8 | 26 | 2021-10-12 12:53 | 2021-10-12 14:37
2021-10-11 | VACAVILLE 1112 | SANTA BARBARA | 22.3806 | 0.17538 | Sectionalization | 2021-10-11 | 6:53 | 2021-10-12 | 14:28 | 1 | 24 | 2233 | 2195 | 38 | 217 | 609 | 2021-10-12 10:23 | 2021-10-12 14:18
2021-10-11 | VASCO 1102 | KERN | 64.9626 | 14.8748 | Sectionalization | 2021-10-11 | 9:19 | 2021-10-12 | 16:50 | 1 | 24 | 1511 | 1307 | 178 | 73 | 181 | 2021-10-16 15:14 | 2021-10-16 16:32
2021-10-11 | VOLTA 1101 | KERN | 117.8069 | 115.664 | Sectionalization | 2021-10-11 | 6:36 | 2021-10-12 | 13:42 | 1 | 24 | 686 | 546 | 109 | 44 | 149 | 2021-10-16 15:14 | 2021-10-16 16:32
2021-10-11 | WESTLEY 1103 | TEHAMA | 82.8591 | 0 | Sectionalization | 2021-10-11 | 8:42 | 2021-10-12 | 14:37 | 1 | 24 | 939 | 617 | 150 | 19 | 382 | #N/A | #N/A
2021-10-11 | ZACA 1102 | COLUSA, GLENN | 101.6632 | 76.6421 | Sectionalization | 2021-10-11 | 18:00 | 2021-10-12 | 14:18 | 1 | 24 | 1393 | 998 | 313 | 31 | 46 | #N/A | #N/A
2021-10-14 | TEJON 1102 | TULARE, FRESNO | 0 | 0 | Backup Generation | 2021-10-12 15:28 | 44481.6444 | 2021-10-13 16:30 | 44482.6875 | 1.0431 | 25.0333 | 1 | 0 | 1 | 0 | 0 | 2021-01-20 04:22 | 2021-01-20 16:47
2021-10-14 | TEJON 1102 | MARIPOSA | 0 | 0 | Backup Generation | 2021-10-12 15:28 | 44481.6444 | 2021-10-14 11:00 | 44483.4583 | 1.8139 | 43.5333 | 1 | 0 | 1 | 0 | 0 | 2021-01-19 14:03 | 2021-01-26 16:10
2021-10-14 | CORNING 1102 | SAN LUIS OBISPO, SANTA BARBARA | 0 | 0 | Backup Generation | 2021-10-13 12:53 | 44482.5368 | 2021-10-13 16:30 | 44482.6875 | 0.15069 | 3.6167 | 1 | 0 | 1 | 0 | 0 | Not de-energized; circuit was removed from scope | Not de-energized; circuit was removed from scope.
2021-10-14 | ELK CREEK 1101 | FRESNO | 0 | 0 | Backup Generation | 2021-10-13 13:22 | 44482.5569 | 2021-10-14 11:00 | 44483.4583 | 0.90139 | 21.6333 | 1 | 0 | 1 | 0 | 0 | Not de-energized; circuit was removed from scope | Not de-energized; circuit was removed from scope.
2021-10-14 | CAL WATER 1102 | KERN | 61.4476 | 0 | Sectionalization | 2021-10-15 | 1:00 | 2021-10-15 | 15:38 | 0 | 0 | 2417 | 2219 | 186 | 263 | 327 | 2021-10-15 12:00 | 2021-10-15 15:38
2021-10-14 | LAMONT 1104 | KERN | 51.9871 | 0.41225 | Sectionalization | 2021-10-15 | 1:09 | 2021-10-15 | 15:10 | 0 | 0 | 315 | 81 | 115 | 5 | 45 | 2021-10-15 12:00 | 2021-10-15 15:10
2021-10-14 | MAGUNDEN 1108 | KERN | 30.0289 | 0.0019972 | Sectionalization | 2021-10-15 | 1:05 | 2021-10-15 | 15:12 | 0 | 0 | 1642 | 1518 | 88 | 115 | 1033 | 2021-10-15 12:00 | 2021-10-15 15:12
2021-10-14 | SCE TEHACHAPI 1101 | KERN | 0.26781 | 0.26781 | Sectionalization | 2021-10-15 | 1:16 | 2021-10-15 | 14:26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-10-15 12:00 | 2021-10-15 14:26
2021-10-14 | TEJON 1102 | KERN | 35.467 | 0 | Sectionalization | 2021-10-15 | 1:07 | 2021-10-16 | 16:32 | 1 | 24 | 208 | 0 | 187 | 0 | 0 | 2021-10-16 15:14 | 2021-10-16 16:32
2021-10-14 | TEJON 1103 | KERN | 34.8997 | 0 | Sectionalization | 2021-10-15 | 1:00 | 2021-10-15 | 14:46 | 0 | 0 | 117 | 24 | 40 | 0 | 1 | 2021-10-15 12:00 | 2021-10-15 14:46
[1] PSPS Mitigation includes - Backup generation, Backup storage, Dx microgrid, Islanding, Patrols, Sectionalization, Dx Switching, Temporary substation microgrid, Tx switching, Vegetation management (expedite priority trees that prevent circuit from being removed from scope)

## 17.CRCs
LIST EACH EVENT FOR WHICH A CRC WAS OPENED
Event Name | CRC Location | County or Tribe | Radius Served by the CRC (approximate distance in miles)1 | Date Service Area De-energized2 | Time Service Area De-energized (24-hr. clock) | Date CRC Opened | Time CRC Opened | Date Service Area Re-energized | Time Service Area Re-energized (24-hr. clock)2 | Date CRC Closed | Time CRC Closed | Total Days Opened (fractions in tenths of 14-hr. span) | Total Hours Opened (Integer) | Type of CRC (Indoor, Outdoor, Mobile) | Amenities (list each separated by commas) | Average AQI during Operation3 | Was CRC powered by Backup Generation? (yes/no)4 | PG&E Remarks
2021-01-18 | 33049 Auberry Rd Auberry 93602 | Fresno |  | 2021-01-19 | 9:06 | 2021-01-19 | 8:00 | 2021-01-20 | 20:55 | 2021-01-20 | 18:30 | 1.8462 | 24 | Indoor | Wi-Fi, Restrooms, Blankets, Water and Snacks, Device Charging, Medical Device Charging, Cooling/Heating, Ice | 14 | No
2021-01-18 | 30733 E Kings Canyon Rd Dunlap Area 93675 | Fresno |  | 2021-01-19 | 10:46 | 2021-01-19 | 8:00 | 2021-01-21 | 0:47 | 2021-01-20 | 18:30 | 1.8462 | 24 | Indoor | Wi-Fi, Restrooms, Blankets, Water and Snacks, Device Charging, Medical Device Charging, Cooling/Heating, Ice | Not available | No | No Purple Air sensors were available in the immediate area and/or those available did not have in-event data.
2021-01-18 | 33087 Rd 228 North Fork 93643 | Madera |  | 2021-01-19 | 7:02 | 2021-01-20 | 8:00 | 2021-01-25 | 19:35 | 2021-01-22 | 17:00 | 2.7692 | 36 | Indoor | Wi-Fi, Restrooms, Blankets, Water and Snacks, Device Charging, Medical Device Charging, Cooling/Heating, Ice | 25 | No | *Note that this CRC also supported the subsequent wind event.
2021-01-18 | 50200 High School Rd Oakhurst 93644 | Madera |  | 2021-01-19 | 7:46 | 2021-01-19 | 8:00 | 2021-01-24 | 18:36 | 2021-01-23 | 17:00 | 4.8462 | 63 | Indoor | Wi-Fi, Restrooms, Blankets, Water and Snacks, Device Charging, Medical Device Charging, Cooling/Heating, Ice | 59 | No | *Note that this CRC also supported the subsequent wind event.
2021-01-18 | 5089 Cole Rd Bootjack 95338 | Mariposa |  | 2021-01-19 | 8:09 | 2021-01-19 | 8:00 | 2021-01-27 | 0:10 | 2021-01-23 | 17:00 | 4.8462 | 63 | Indoor | Wi-Fi, Restrooms, Blankets, Water and Snacks, Device Charging, Medical Device Charging, Cooling/Heating, Ice | 36 | No | *Note that this CRC also supported the subsequent wind event.
2021-01-18 | 1230 Trouville Ave Grover Beach 93433 | San Luis Obispo |  | 2021-01-19 | 16:14 | 2021-01-19 | 8:00 | 2021-01-20 | 18:50 | 2021-01-20 | 12:45 | 1.4038 | 18 | Micro | Wi-Fi, Restrooms, Blankets, Water and Snacks, Device Charging, Medical Device Charging | 8 | Yes
2021-01-18 | 1550 S College Dr Santa Maria 93454 | Santa Barbara |  | 2021-01-19 | 16:06 | 2021-01-19 | 8:00 | 2021-01-20 | 18:50 | 2021-01-20 | 12:30 | 1.3846 | 18 | Micro | Wi-Fi, Restrooms, Blankets, Water and Snacks, Device Charging, Medical Device Charging | 38 | Yes
2021-08-17 | 286 Rockerfeller Rd, Berry Creek, CA 95916 | Butte |  | N/A | N/A | 2021-08-17 | 17:00 | N/A | N/A | 2021-08-19 | 13:00 | 1.7143 | 24 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 318 | Yes
2021-08-17 | 14098 Skyway Rd, Magalia, CA 95954 | Butte |  | 2021-08-18 | 1:28 | 2021-08-17 | 17:00 | 2021-08-19 | 0:57 | 2021-08-19 | 13:00 | 1.7143 | 24 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 153 | Yes
2021-08-17 | 2959 Lower Wyandotte Rd, Oroville, CA 95966 | Butte |  | N/A | N/A | 2021-08-17 | 17:00 | N/A | N/A | 2021-08-19 | 13:00 | 1.7143 | 24 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 164 | No
2021-08-17 | 6626 Skyway, Paradise, CA 95969 | Butte |  | 2021-08-18 | 1:36 | 2021-08-17 | 17:00 | 2021-08-19 | 17:11 | 2021-08-19 | 13:00 | 1.7143 | 24 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 185 | No
2021-08-17 | 229 Market St, Stonyford, CA 95979 | Colusa |  | 2021-08-17 | 19:51 | 2021-08-17 | 17:00 | 2021-08-19 | 19:22 | 2021-08-19 | 13:00 | 1.7143 | 24 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 176 | Yes
2021-08-17 | 5562 Clayton Rd, Concord, CA 94521 | Contra Costa |  | N/A | N/A | 2021-08-17 | 17:00 | N/A | N/A | 2021-08-18 | 13:00 | 0.71429 | 10 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 35 | Yes
2021-08-17 | 3430 Co Rd 309, Elk Creek, CA 95939 | Glenn |  | 2021-08-17 | 20:13 | 2021-08-17 | 17:00 | 2021-08-19 | 19:02 | 2021-08-19 | 13:00 | 1.7143 | 24 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 176 | Yes
2021-08-17 | 3245 Bowers Ave, Clearlake, CA 95422 | Lake |  | 2021-08-18 | 1:46 | 2021-08-17 | 17:00 | 2021-08-19 | 22:31 | 2021-08-19 | 13:00 | 1.7143 | 24 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 36 | No
2021-08-17 | 12502 Foot hill Blvd, Clearlake Oaks, CA 95423 | Lake |  | 2021-08-18 | 1:45 | 2021-08-17 | 17:00 | 2021-08-19 | 2:29 | 2021-08-18 | 15:00 | 0.85714 | 12 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 86 | Yes
2021-08-17 | 15780 Bottlerock Rd, Cobb, CA 95426 | Lake |  | 2021-08-18 | 1:45 | 2021-08-17 | 17:00 | 2021-08-19 | 21:42 | 2021-08-19 | 13:00 | 1.7143 | 24 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 159 | Yes
2021-08-17 | 7130 Red Hills Rd, Kelseyville, CA 95451 | Lake |  | 2021-08-18 | 2:02 | 2021-08-17 | 19:00 | 2021-08-19 | 2:04 | 2021-08-19 | 13:00 | 1.5714 | 22 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 187 | Yes
2021-08-17 | 76201 Covelo Rd, Covelo, CA 95428 | Mendocino |  | N/A | N/A | 2021-08-17 | 17:00 | N/A | N/A | 2021-08-18 | 13:00 | 0.71429 | 10 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 23 | Yes
2021-08-17 | 44400 Willis Ave, Laytonville, CA 95454 | Mendocino |  | N/A | N/A | 2021-08-17 | 17:00 | N/A | N/A | 2021-08-18 | 13:00 | 0.71429 | 10 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 152 | No
2021-08-17 | 1775 N State St, Ukiah, CA 95482 | Mendocino |  | N/A | N/A | 2021-08-17 | 19:00 | N/A | N/A | 2021-08-18 | 13:00 | 0.57143 | 8 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 40 | Yes
2021-08-17 | 35 La Jota Dr, Angwin, CA 94508 | Napa |  | 2021-08-18 | 1:22 | 2021-08-17 | 17:00 | 2021-08-19 | 19:13 | 2021-08-18 | 22:00 | 1.3571 | 19 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 105 | Yes
2021-08-17 | 970 Petrified Forest Rd, Calistoga, CA 94515 | Napa |  | 2021-08-18 | 1:40 | 2021-08-17 | 17:00 | 2021-08-19 | 2:18 | 2021-08-18 | 22:00 | 1.3571 | 19 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 27 | Yes
2021-08-17 | 2590 1st St, Napa, CA 94558 | Napa |  | 2021-08-18 | 1:30 | 2021-08-17 | 17:00 | 2021-08-19 | 2:34 | 2021-08-18 | 22:00 | 1.3571 | 19 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 54 | No
2021-08-17 | 1255 Oak Ave, St. Helena, CA 94574 | Napa |  | 2021-08-18 | 1:21 | 2021-08-17 | 17:00 | 2021-08-19 | 1:28 | 2021-08-18 | 22:00 | 1.3571 | 19 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 52 | Yes
2021-08-17 | 2004 E Main St, Quincy, CA 95971 | Plumas |  | 2021-08-18 | 1:52 | 2021-08-17 | 17:00 | 2021-08-19 | 21:36 | 2021-08-19 | 13:00 | 1.7143 | 24 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | Not available | No | No Purple Air sensors were available in the immediate area and/or those available did not have in-event data.
2021-08-17 | 2081 Frontier Trail, Anderson, CA 96007 | Shasta |  | 2021-08-18 | 0:28 | 2021-08-17 | 17:00 | 2021-08-19 | 22:25 | 2021-08-19 | 13:00 | 1.7143 | 24 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 191 | No
2021-08-17 | 5400 Happy Valley Rd, Anderson, CA 96007 | Shasta |  | 2021-08-18 | 0:24 | 2021-08-17 | 17:00 | 2021-08-19 | 23:07 | 2021-08-19 | 13:00 | 1.7143 | 24 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 285 | Yes
2021-08-17 | 20814 Mammoth Dr, Lakehead, CA 96051 | Shasta |  | 2021-08-18 | 1:21 | 2021-08-17 | 17:00 | 2021-08-19 | 0:19 | 2021-08-19 | 13:00 | 1.7143 | 24 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 221 | No
2021-08-17 | 100 Mercy Oaks Dr, Redding, CA 96003 | Shasta |  | 2021-08-18 | 0:35 | 2021-08-17 | 17:00 | 2021-08-20 | 0:13 | 2021-08-19 | 13:00 | 1.7143 | 24 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 195 | No
2021-08-17 | 29632 CA-299, Round Mountain, CA 96084 | Shasta |  | 2021-08-18 | 0:32 | 2021-08-17 | 17:00 | 2021-08-19 | 21:57 | 2021-08-19 | 13:00 | 1.7143 | 24 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 195 | Yes
2021-08-17 | 514 Miners St, Alleghany, CA 95910 | Sierra |  | N/A | N/A | 2021-08-17 | 17:00 | N/A | N/A | 2021-08-18 | 13:00 | 0.71429 | 10 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 175 | No
2021-08-17 | 327 Main St, Downieville, CA 95936 | Sierra |  | N/A | N/A | 2021-08-17 | 17:00 | N/A | N/A | 2021-08-18 | 13:00 | 0.71429 | 10 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 175 | No
2021-08-17 | 2001 N Village Pkwy, Vacaville, CA 95688 | Solano |  | 2021-08-18 | 1:26 | 2021-08-17 | 17:00 | 2021-08-19 | 16:36 | 2021-08-19 | 13:00 | 1.7143 | 24 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 153 | No
2021-08-17 | 1 Citrus Fair Dr, Cloverdale, CA 95425 | Sonoma |  | 2021-08-18 | 1:45 | 2021-08-17 | 17:00 | 2021-08-19 | 16:11 | 2021-08-18 | 22:00 | 1.3571 | 19 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 61 | No
2021-08-17 | 2500 Patio Ct., Santa Rosa, CA 95409 | Sonoma |  | 2021-08-18 | 1:55 | 2021-08-17 | 19:00 | 2021-08-18 | 23:01 | 2021-08-18 | 22:00 | 1.2143 | 17 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 50 | No
2021-08-17 | 252 W Spain St, Sonoma, CA 95476 | Sonoma |  | 2021-08-18 | 1:46 | 2021-08-17 | 19:00 | 2021-08-19 | 2:25 | 2021-08-18 | 22:00 | 1.2143 | 17 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 57 | Yes
2021-08-17 | 19001 Bowman Rd, Cottonwood, CA 96022 | Tehama |  | 2021-08-18 | 0:28 | 2021-08-17 | 17:00 | 2021-08-19 | 20:19 | 2021-08-19 | 13:00 | 1.7143 | 24 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 181 | Yes
2021-08-17 | 17605 Park Terrace Rd, Rancho Tehama, CA 96021 | Tehama |  | 2021-08-18 | 1:22 | 2021-08-17 | 17:00 | 2021-08-19 | 19:00 | 2021-08-19 | 13:00 | 1.7143 | 24 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 134 | Yes
2021-08-17 | 7575 CA-16, Guinda, CA 95637 | Yolo |  | 2021-08-18 | 1:30 | 2021-08-17 | 17:00 | 2021-08-19 | 2:34 | 2021-08-18 | 22:00 | 1.3571 | 19 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 180 | Yes
2021-08-17 | 9185 Marysville Rd, Oregon House, CA 95962 | Yuba |  | N/A | N/A | 2021-08-17 | 17:00 | N/A | N/A | 2021-08-18 | 13:00 | 0.71429 | 10 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 46 | No
2021-09-20 | Stonyford Community Center/Hall, 229 Market St, Stonyford, CA 95979 | Colusa |  | 2021-09-20 | 13:08 | 2021-09-20 | 8:00 | 2021-09-21 | 0:59 | 2021-09-20 | 12:54 | 0.35714 | 5 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 5 | No
2021-09-20 | Elk Creek Junior Senior High School, 3430 Co Rd 309, Elk Creek, CA 95939 | Glenn |  | N/A | N/A | 2021-09-20 | 8:00 | N/A | N/A | 2021-09-20 | 12:54 | 0.35714 | 5 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 7 | Yes
2021-09-20 | El Tejon Unified School District, 4337 Lebec Rd, Lebec, CA 93243 | Kern |  | 2021-09-21 | 5:25 | 2021-09-21 | 8:00 | 2021-09-21 | 23:46 | 2021-09-21 | 18:00 | 0.71429 | 10 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 38 | Yes
2021-09-20 | Highways 128/121 and Steele Canyon, 6003 Monticello Rd, Napa, CA 94558 | Napa |  | 2021-09-20 | 13:08 | 2021-09-20 | 8:00 | 2021-09-21 | 0:49 | 2021-09-20 | 11:30 | 0.28571 | 4 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 6 | Yes
2021-09-20 | Pacific Union College, 35 La Jota Dr, Angwin, CA 94508 | Napa |  | N/A | N/A | 2021-09-20 | 8:00 | N/A | N/A | 2021-09-20 | 11:30 | 0.28571 | 4 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 8 | Yes
2021-09-20 | Happy Valley Community Center, 5400 Happy Valley Rd, Anderson, CA 96007 | Shasta |  | N/A | N/A | 2021-09-20 | 8:00 | N/A | N/A | 2021-09-20 | 13:01 | 0.35714 | 5 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 3 | No
2021-09-20 | Mercy Oaks, 100 Mercy Oaks Dr, Redding, CA 96003 | Shasta |  | N/A | N/A | 2021-09-20 | 8:00 | N/A | N/A | 2021-09-20 | 13:01 | 0.35714 | 5 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 3 | No
2021-09-20 | S&S Supply, 2700 Maxwell Way, Fairfield, CA 94534 | Solano |  | 2021-09-20 | 13:56 | 2021-09-20 | 8:00 | 2021-09-20 | 14:19 | 2021-09-20 | 11:30 | 0.28571 | 4 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 9 | Yes
2021-09-20 | Rancho Tehama Association, 17605 Park Terrace Rd, Rancho Tehama, CA 96022 | Tehama |  | 2021-09-20 | 13:10 | 2021-09-20 | 8:00 | 2021-09-21 | 7:45 | 2021-09-20 | 20:00 | 0.85714 | 12 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 10 | Yes
2021-10-11 | 9932 Cohasset Rd, Cohasset (Chico), CA 95973 | Butte |  | 2021-10-11 | 11:06 | 2021-10-11 | 08:00 | 2021-10-12 | 21:24 | 2021-10-12 | 16:30 | 1.6429 | 23 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 17 | Yes
2021-10-11 | 6626 Skyway, Paradise, CA 95969 | Butte |  | 2021-10-11 | 11:02 | 2021-10-11 | 08:00 | 2021-10-12 | 18:25 | 2021-10-12 | 16:30 | 1.6429 | 23 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 1 | No
2021-10-11 | 229 Market St, Stonyford, CA 95979 | Colusa |  | 2021-10-11 | 11:25 | 2021-10-11 | 08:00 | 2021-10-13 | 0:06 | 2021-10-12 | 19:00 | 1.7857 | 25 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 1 | Yes
2021-10-11 | 5562 Clayton Rd, Concord, CA 94521 | Contra Costa |  | 2021-10-11 | 15:34 | 2021-10-11 | 08:00 | 2021-10-13 | 0:21 | 2021-10-12 | 19:00 | 1.7857 | 25 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 3 | Yes
2021-10-11 | 25 W Polk Street, Coalinga, CA 93210 | Fresno |  | 2021-10-11 | 14:22 | 2021-10-11 | 08:00 | 2021-10-13 | 3:08 | 2021-10-12 | 20:30 | 1.9286 | 27 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 3 | Yes
2021-10-11 | 3430 Co Rd 309, Elk Creek, CA 95939 | Glenn |  | 2021-10-11 | 11:21 | 2021-10-11 | 08:00 | 2021-10-12 | 22:41 | 2021-10-12 | 19:00 | 1.7857 | 25 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 1 | Yes
2021-10-11 | 2132 Lebec Road, Lebec, CA 93243 | Kern |  | 2021-10-11 | 19:41 | 2021-10-11 | 08:00 | 2021-10-13 | 8:45 | 2021-10-12 | 22:00 | 2 | 28 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 4 | Yes
2021-10-11 | 12502 Foot hill Blvd, Clearlake Oaks, CA 95423 | Lake |  | 2021-10-11 | 13:18 | 2021-10-11 | 08:00 | 2021-10-12 | 18:04 | 2021-10-12 | 19:00 | 1.7857 | 25 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 1 | Yes
2021-10-11 | 15780 Bottlerock Rd, Cobb, CA 95426 | Lake |  | 2021-10-11 | 13:21 | 2021-10-11 | 08:00 | 2021-10-14 | 22:22 | 2021-10-12 | 19:00 | 1.7857 | 25 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 3 | No
2021-10-11 | 22223 CA- 29, Middletown, CA 95461 | Lake |  | 2021-10-11 | 13:14 | 2021-10-11 | 08:00 | 2021-10-12 | 23:55 | 2021-10-12 | 19:00 | 1.7857 | 25 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 1 | Yes
2021-10-11 | 18090 Hidden Valley Rd, Hidden Valley Lake, CA 95467 | Lake |  | 2021-10-11 | 13:20 | 2021-10-11 | 08:00 | 2021-10-12 | 21:43 | 2021-10-12 | 19:00 | 1.7857 | 25 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 2 | Yes
2021-10-11 | 625 Division St., King City, CA 93930 | Monterey |  | 2021-10-11 | 14:28 | 2021-10-11 | 08:00 | 2021-10-13 | 0:48 | 2021-10-12 | 20:30 | 1.9286 | 27 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 11 | No
2021-10-11 | 68025 Jolon Rd, Lockwood, CA 93932 | Monterey |  | 2021-10-11 | 18:35 | 2021-10-11 | 08:00 | 2021-10-12 | 23:24 | 2021-10-12 | 20:30 | 1.9286 | 27 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 13 | Yes
2021-10-11 | 6003 Monticello Rd, Napa, CA 94558 | Napa |  | 2021-10-11 | 13:17 | 2021-10-11 | 08:00 | 2021-10-12 | 23:57 | 2021-10-12 | 20:00 | 1.5714 | 22 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 1 | Yes
2021-10-11 | 35 La Jota Dr, Angwin, CA 94508 | Napa |  | 2021-10-11 | 13:15 | 2021-10-11 | 08:00 | 2021-10-13 | 2:13 | 2021-10-12 | 20:00 | 1.8571 | 26 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 1 | Yes
2021-10-11 | 2004 E Main St, Quincy, CA 95971 | Plumas |  | 2021-10-11 | 11:26 | 2021-10-11 | 08:00 | 2021-10-12 | 21:25 | 2021-10-12 | 16:30 | 1.6429 | 23 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 11 | No
2021-10-11 | 5400 Happy Valley Rd, Anderson, CA 96007 | Shasta |  | 2021-10-11 | 13:38 | 2021-10-11 | 08:00 | 2021-10-12 | 17:50 | 2021-10-12 | 14:00 | 1.4286 | 20 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 1 | No
2021-10-11 | 2081 Frontier Trail, Anderson, CA 96007 | Shasta |  | 2021-10-11 | 13:20 | 2021-10-11 | 08:00 | 2021-10-12 | 19:14 | 2021-10-12 | 14:00 | 1.4286 | 20 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 1 | No
2021-10-11 | 29632 CA-299, Round Mountain, CA 96084 | Shasta |  | 2021-10-11 | 13:41 | 2021-10-11 | 08:00 | 2021-10-12 | 20:39 | 2021-10-12 | 10:00 | 1.1429 | 16 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 1 | Yes
2021-10-11 | 2001 N Village Pkwy, Vacaville, CA 95688 | Solano |  | 2021-10-11 | 13:53 | 2021-10-11 | 08:00 | 2021-10-13 | 0:33 | 2021-10-12 | 19:00 | 1.7857 | 25 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 4 | No
2021-10-11 | 17605 Park Terrace Road, Corning, CA 96021 | Tehama |  | 2021-10-11 | 8:34 | 2021-10-11 | 08:00 | 2021-10-12 | 22:20 | 2021-10-12 | 17:00 | 1.6429 | 23 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | Not available | Yes | No Purple Air sensors were available in the immediate area and/or those available did not have in-event data.
2021-10-11 | 19001 Bowman Rd, Cottonwood, CA 96022 | Tehama |  | 2021-10-11 | 13:20 | 2021-10-11 | 08:00 | 2021-10-12 | 20:44 | 2021-10-12 | 17:00 | 1.6429 | 23 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 1 | Yes
2021-10-11 | 7575 CA-16, Guinda, CA 95637 | Yolo |  | 2021-10-11 | 14:09 | 2021-10-11 | 08:00 | 2021-10-13 | 0:30 | 2021-10-12 | 20:00 | 1.8571 | 26 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 2 | Yes
2021-10-11 | 1 PG&E Way, Winters, CA 95694 | Yolo |  | 2021-10-11 | 13:47 | 2021-10-11 | 08:00 | 2021-10-13 | 1:35 | 2021-10-12 | 20:00 | 1.8571 | 26 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 5 | Yes
2021-10-14 | 6626 Skyway, Paradise, CA 95969 | Butte |  | N/A | N/A | 2021-10-14 | 08:00 | N/A | N/A | 2021-10-14 | 09:30 | 0.14286 | 2 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 3 | No
2021-10-14 | 2959 Lower Wyandotte Rd, Oroville, CA 95966 | Butte |  | N/A | N/A | 2021-10-14 | 08:00 | N/A | N/A | 2021-10-14 | 09:30 | 0.14286 | 2 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 16 | No
2021-10-14 | 229 Market St, Stonyford, CA 95979 | Colusa |  | N/A | N/A | 2021-10-14 | 08:00 | N/A | N/A | 2021-10-14 | 12:00 | 0.28571 | 4 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 3 | No
2021-10-14 | 3430 Co Rd 309, Elk Creek, CA 95939 | Glenn |  | N/A | N/A | 2021-10-14 | 08:00 | N/A | N/A | 2021-10-14 | 10:30 | 0.21429 | 3 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 3 | Yes
2021-10-14 | 2132 Lebec Road, Lebec, CA 93243 | Kern |  | 2021-10-15 | 8:07 | 2021-10-14 | 08:00 | 2021-10-15 | 22:50 | 2021-10-16 | 18:30 | 2.7857 | 39 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 13 | Yes
2021-10-14 | 6003 Monticello Rd, Napa, CA 94558 | Napa |  | N/A | N/A | 2021-10-14 | 08:00 | N/A | N/A | 2021-10-14 | 09:30 | 0.14286 | 2 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 5 | Yes
2021-10-14 | 29632 CA-299, Round Mountain, CA 96084 | Shasta |  | N/A | N/A | 2021-10-14 | 08:00 | N/A | N/A | 2021-10-14 | 10:30 | 0.21429 | 3 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 1 | Yes
2021-10-14 | 2001 N Village Pkwy, Vacaville, CA 95688 | Solano |  | N/A | N/A | 2021-10-14 | 08:00 | N/A | N/A | 2021-10-14 | 09:30 | 0.14286 | 2 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice | 41 | No
2021-10-14 | 35 Country Club Road, Fairfield, CA 94534 | Solano |  | N/A | N/A | 2021-10-14 | 08:00 | N/A | N/A | 2021-10-14 | 09:30 | 0.14286 | 2 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 8 | Yes
2021-10-14 | 17605 Park Terrace Road, Corning, CA 96021 | Tehama |  | N/A | N/A | 2021-10-14 | 08:00 | N/A | N/A | 2021-10-14 | 10:30 | 0.21429 | 3 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 4 | Yes
2021-10-14 | 7575 CA-16, Guinda, CA 95637 | Yolo |  | N/A | N/A | 2021-10-14 | 08:00 | N/A | N/A | 2021-10-14 | 09:30 | 0.14286 | 2 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging | 33 | Yes
[1] When opening CRCs during a PSPS event, PG&E does not use nor calculate radii or exact distance from impacted customers to the CRC as decision criteria for site activation. Instead, we review which cities have a significant number of impacted customers based on the specific scope of the event and select CRCs to activate from our pre-established site portfolio that will best serve those customers and local community needs. In the atypical case where a substantial number of customers are impacted where we don’t have an existing site, we work ad hoc to identify a new site in a location that will serve those customers. We obtain feedback and approval from each county and tribal government to ensure all local entities agree CRC are located in areas that will serve the best interests of the impacted community. During PSPS events there are always some impacted community members located in remote areas where a CRC would be underutilized. We offer other services that are designed to better meet the needs of these community members, such as our portable battery program, and partnerships with 211 and with the California Foundation for Independent Living Centers.
[2] De-energization and re-energization times reflect de-energization and re-energization of nearby customers, not necessarily the CRC itself. N/A indicates the area was not de-energized.
[3] Average AQI during operation is pulled from publicly available Purple Air monitors near the CRC site. In some instances, there were no Purple Air monitors available near the CRC and/or the data for CRC operating times was entirely or partially unavailble. Purple Air monitors use power and wifi, so are impacted by PSPS events.
[4] Mobile and Micro CRCs are powered by generation brought in during the event. Mobile units are powered by the sprinter van which is specially equipped with an inverter. Micro CRCs are powered by either a small generator or other portable source. Indoor CRCs are equipped with temporary generation. Some generators are site owned, others are rented by PG&E for PSPS season.

## 18.Damages
LIST EACH EVENT FOR WHICH DAMAGES WERE DOCUMENTED
Event Name | Circuit Name | County or Tribe | Structure Identifier | Identify if Tier 2, Tier 3, Zone 1 (Tier 1 High Hazard Zones), or Non-HFTD | Type of Damage | Description of Damage
2021-01-18 | Dunlap 1102 | Fresno | 100775250 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | San Joaquin #3 1103 | Madera | 101059160 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | San Joaquin #3 1103 | Madera | 101059158 | Tier 3 | Vegetation | Damaged pole
2021-01-18 | San Joaquin #3 1103 | Madera | 101059626 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103958370 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074515 | Tier 2 | Vegetation | Damaged pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074517 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074520 | Tier 2 | Wind Related | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101074526 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | San Joaquin #3 1103 | Madera | 101059186 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075651 | Tier 2 | Wind Related | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101074926 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074921 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074494 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074495 | Tier 2 | Vegetation | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016931 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103949436 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016873 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016871 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016870 | Tier 3 | Wind Related | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103925516 | Tier 3 | Wind Related | Broken insulator
2021-01-18 | Mariposa 2101 | Mariposa | 101074710 | Tier 2 | Wind Related | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 103228025 | Tier 3 | Wind Related | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103206333 | Tier 3 | Wind Related | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103206328 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016686 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016857 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103209299 | Tier 3 | Wind Related | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103209752 | Tier 3 | Wind Related | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101021918 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101021919 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103206443 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103209873 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016855 | Tier 3 | Wind Related | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103210245 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103979882 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103207935 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103207404 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Madera | 101023383 | Tier 3 | Wind Related | Broken cutout
2021-01-18 | Oakhurst 1103 | Madera | 101026019 | Tier 3 | Wind Related | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103206436 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Madera | 101023393 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Madera | 103088892 | Tier 3 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074575 | Tier 2 | Wind Related | Damaged pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074581 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074583 | Tier 2 | Wind Related | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101074929 | Tier 2 | Wind Related | Damaged pole
2021-01-18 | Mariposa 2101 | Mariposa | 103313620 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101075001 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103201352 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101075000 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103980089 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103201349 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103201790 | Tier 3 | Wind Related | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 103201661 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103201346 | Tier 3 | Wind Related | Broken insulator
2021-01-18 | Oakhurst 1103 | Mariposa | 103203388 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103376720 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103201343 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103977107 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103977105 | Tier 3 | Wind Related | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103201566 | Tier 3 | Wind Related | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103977106 | Tier 3 | Wind Related | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 103201359 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101021937 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103212489 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103201362 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103779468 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103212494 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103203439 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103203447 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103212498 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103980090 | Tier 3 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101021938 | Tier 3 | Wind Related | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 103208355 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103208350 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103209079 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016847 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101021927 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016905 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016875 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016881 | Tier 2 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103206897 | Tier 2 | Wind Related | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101074969 | Tier 2 | Wind Related | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101075012 | Tier 2 | Wind Related | Broken insulator
2021-01-18 | Oakhurst 1103 | Mariposa | 103228238 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103210435 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016908 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103210595 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103575981 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103210353 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016910 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016911 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103359839 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101074928 | Tier 2 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103210613 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | San Joaquin #3 1101 | Madera | 101057957 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | San Joaquin #3 1101 | Madera | 103204921 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016634 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016638 | Tier 2 | Vegetation | Damaged pole
2021-01-18 | San Joaquin #3 1101 | Madera | 103218587 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016647 | Tier 2 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103899259 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103229302 | Tier 3 | Vegetation | Broken insulator
2021-01-18 | Oakhurst 1103 | Mariposa | 103209065 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016643 | Tier 2 | Wind Related | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103206279 | Tier 2 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103209072 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016636 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016630 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 103206284 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103206305 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016840 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103995138 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103939361 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103899262 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016834 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 104008459 | Tier 2 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103206211 | Tier 3 | Wind Related | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016894 | Tier 3 | Wind Related | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016892 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103899258 | Tier 3 | Wind Related | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101016895 | Tier 3 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103208913 | Tier 2 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016843 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103971197 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103980298 | Tier 3 | Wind Related | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103952582 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016909 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103788995 | Tier 3 | Vegetation | Damaged pole
2021-01-18 | Mariposa 2101 | Mariposa | 101066731 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101078766 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101078726 | Tier 3 | Vegetation | Broken insulator
2021-01-18 | Mariposa 2101 | Mariposa | 101078725 | Tier 3 | Vegetation | Broken insulator
2021-01-18 | Mariposa 2101 | Mariposa | 103340919 | Tier 3 | Vegetation | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101078772 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101066915 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101066539 | Tier 3 | Vegetation | Damaged pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074529 | Tier 2 | Wind Related | Damaged pole
2021-01-18 | Mariposa 2101 | Mariposa | 101065560 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101073359 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | San Joaquin #3 1103 | Madera | NA | Tier 3 | Vegetation | Guy and anchor damage
2021-01-18 | Mariposa 2101 | Mariposa | 101073284 | Tier 2 | Vegetation | Broken Transformer
2021-01-18 | Mariposa 2101 | Mariposa | 101073445 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101065555 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103829441 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074609 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074595 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 104008354 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103382716 | Tier 3 | Vegetation | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101065599 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103210021 | Tier 3 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016095 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016085 | Tier 3 | Vegetation | Damaged pole
2021-01-18 | Mariposa 2101 | Mariposa | 101065566 | Tier 2 | Vegetation | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016012 | Tier 3 | Vegetation | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103949742 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101016092 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 103216422 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103216426 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Madera | 101026059 | Tier 3 | Wind Related | Broken crossarm
2021-01-18 | Oakhurst 1103 | Madera | 101025582 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Madera | 101025583 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Madera | 101025587 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Madera | 101025590 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016330 | Tier 2 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Madera | 101026010 | Tier 3 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016590 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103151436 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101016166 | Tier 3 | Wind Related | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101021916 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103229028 | Tier 2 | Wind Related | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016600 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103968161 | Tier 3 | Wind Related | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 103206840 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016331 | Tier 2 | Wind Related | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101021920 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103818254 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016632 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103202104 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103217291 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101077102 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103206832 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016337 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103232495 | Tier 2 | Vegetation | Guy and anchor damage
2021-01-18 | Oakhurst 1103 | Mariposa | 101016339 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103790372 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101077131 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103217277 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103206903 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101074723 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074727 | Tier 2 | Vegetation | Tree leaning into line
2021-01-18 | Mariposa 2101 | Mariposa | 101074648 | Tier 2 | Vegetation | Broken tie wire
2021-01-18 | Mariposa 2101 | Mariposa | 104003604 | Tier 2 | Vegetation | Tree leaning into line
2021-01-18 | Mariposa 2101 | Mariposa | 101074711 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103338299 | Tier 2 | Vegetation | Broken tie wire
2021-01-18 | Mariposa 2101 | Mariposa | 101074627 | Tier 2 | Vegetation | Damaged pole
2021-01-18 | Mariposa 2101 | Mariposa | 101066977 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101074628 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016592 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101073591 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Madera | 101026020 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074895 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103206866 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Madera | 101026021 | Tier 3 | Vegetation | Damaged pole
2021-01-18 | Oakhurst 1103 | Madera | 101026022 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103217609 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 103319735 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 102317617 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Madera | 101026028 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103206876 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101066981 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103206871 | Tier 2 | Vegetation | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016343 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Madera | 101026038 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 103356779 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Madera | 101026040 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103218148 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Madera | 103381265 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Madera | 103381266 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Madera | 101026043 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101016683 | Tier 2 | Vegetation | Broken Transformer
2021-01-18 | Mariposa 2101 | Mariposa | 101074582 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103825095 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Madera | 101026044 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075641 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103217120 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103825150 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Madera | 101026046 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Madera | 101026045 | Tier 3 | Vegetation | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103218777 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101021936 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101016586 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 103968792 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Madera | 103381248 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016587 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101074730 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074729 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103208394 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016623 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 103947843 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016682 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101016648 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016649 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 103217173 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101016676 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103217162 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016674 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 103216569 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103217239 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Madera | 101017369 | Tier 3 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103231765 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Madera | 101017368 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016597 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016553 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103970397 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103216599 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075044 | Tier 2 | Wind Related | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 103957340 | Tier 2 | Wind Related | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016581 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016543 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016596 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103202058 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101076371 | Tier 3 | Vegetation | Damaged pole
2021-01-18 | Mariposa 2101 | Mariposa | 101074591 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101074626 | Tier 2 | Vegetation | Damaged pole
2021-01-18 | Mariposa 2101 | Mariposa | 103338300 | Tier 2 | Wind Related | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101074714 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103995963 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101076368 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | San Joaquin #3 1101 | Madera | 103919468 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Madera | 101026085 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 103376855 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Madera | 103983591 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101076358 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101076086 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101075876 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101075874 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101075873 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101075875 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101076402 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101075872 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103958468 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101076397 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101076463 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101076404 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101076464 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101087120 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101074650 | Tier 2 | Wind Related | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101017442 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101017443 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101017437 | Tier 3 | Vegetation | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101017447 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103980299 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101017449 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101017450 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101017451 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101017453 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103381249 | Tier 3 | Vegetation | Damaged pole
2021-01-18 | Mariposa 2101 | Mariposa | 103952363 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Madera | 101017444 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Madera | 101017431 | Tier 3 | Wind Related | Broken tie wire
2021-01-18 | Oakhurst 1103 | Madera | 101017433 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Madera | 101017432 | Tier 3 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103218338 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101073569 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103227806 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Madera | 101017429 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 103322386 | Tier 2 | Wind Related | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 103218335 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016561 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Madera | 101017428 | Tier 3 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101073571 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103217216 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101073588 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016573 | Tier 2 | Vegetation | Broken Under-Arm Bus
2021-01-18 | Oakhurst 1103 | Madera | 102317620 | Tier 3 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 103763693 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101016571 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Madera | 101017424 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Oakhurst 1103 | Madera | 101017425 | Tier 3 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103218344 | Tier 2 | Vegetation | Damaged pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103952740 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016570 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103217229 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 101016507 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016563 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 104010980 | Tier 3 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016565 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016512 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 101016569 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Oakhurst 1103 | Mariposa | 103207410 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Oakhurst 1103 | Mariposa | 103963513 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 101016568 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103206312 | Tier 3 | Vegetation | Broken conductor
2021-01-18 | Oakhurst 1103 | Mariposa | 103817966 | Tier 2 | Vegetation | Broken Connector
2021-01-18 | Mariposa 2101 | Mariposa | 101075508 | Tier 2 | Wind Related | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101075537 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075538 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103337970 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101078516 | Tier 2 | Vegetation | Broken Cutout
2021-01-18 | Mariposa 2101 | Mariposa | 101075532 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101075523 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075524 | Tier 2 | Wind Related | Broken insulator
2021-01-18 | Mariposa 2101 | Mariposa | 101075525 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075527 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075561 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101075558 | Tier 2 | Wind Related | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 103208293 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103208286 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103338306 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101074995 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101075579 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075560 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 103983943 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101075037 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075541 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 103958371 | Tier 2 | Wind Related | Damaged pole
2021-01-18 | Mariposa 2101 | Mariposa | 103581574 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101066417 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101075240 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075241 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Oakhurst 1103 | Madera | 101026029 | Tier 3 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075252 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075251 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075245 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101075237 | Tier 2 | Wind Related | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101072586 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101072629 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101072590 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101072626 | Tier 2 | Wind Related | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 101072592 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101072632 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103208318 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103781750 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 103337057 | Tier 3 | Vegetation | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101066871 | Tier 3 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101064719 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 103950831 | Tier 3 | Wind Related | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101074602 | Tier 2 | Wind Related | Broken insulator
2021-01-18 | Mariposa 2101 | Mariposa | 101073267 | Tier 2 | Wind Related | Broken insulator
2021-01-18 | Mariposa 2101 | Mariposa | 101073266 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101073381 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101073379 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101073383 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101073270 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103952233 | Tier 3 | Wind Related | Broken tie wire
2021-01-18 | Mariposa 2101 | Mariposa | 103854176 | Tier 3 | Wind Related | Broken tie wire
2021-01-18 | Mariposa 2102 | Mariposa | 103219163 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | San Joaquin #3 1103 | Madera | 101059184 | Tier 3 | Wind Related | Broken pole
2021-01-18 | Mariposa 2102 | Mariposa | 101077945 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2102 | Mariposa | 101077971 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075138 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103338298 | Tier 2 | Wind Related | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101075093 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075160 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103376864 | Tier 2 | Wind Related | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101073450 | Tier 2 | Wind Related | Broken insulator
2021-01-18 | Mariposa 2101 | Mariposa | 101073455 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101073447 | Tier 2 | Vegetation | Broken tie wire
2021-01-18 | Mariposa 2101 | Mariposa | 101073426 | Tier 2 | Vegetation | Damaged pole
2021-01-18 | Mariposa 2101 | Mariposa | 103340879 | Tier 2 | Vegetation | Broken conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101073409 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101073537 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 103207988 | Tier 2 | Vegetation | Broken tie wire
2021-01-18 | Mariposa 2101 | Mariposa | 103338302 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 103376863 | Tier 2 | Vegetation | Broken crossarm
2021-01-18 | Mariposa 2101 | Mariposa | 103581921 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101075250 | Tier 2 | Vegetation | Damaged conductor
2021-01-18 | Mariposa 2101 | Mariposa | 101015460 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075249 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101015459 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075157 | Tier 2 | Vegetation | Broken pole
2021-01-18 | Mariposa 2101 | Mariposa | 101075883 | Tier 3 | Wind Related | Broken Cutouts
2021-01-18 | Oakhurst 1103 | Mariposa | 101016080 | Tier 3 | Vegetation | Damaged conductor
2021-08-17 | Pueblo 2103 | Napa | 102269654 | Tier 3 | Wind Related | Broken Ground
2021-08-17 | Keswick 1101 | Shasta | 103923363 | Tier 3 | Wind Related | Broken tie wire
2021-08-17 | Cedar Creek 1101 | Shasta | 101474218 | Tier 2 | Wind Related | Damaged conductor
2021-08-17 | Anderson 1101 | Shasta | 101493379 | Tier 2 | Vegetation | Broken conductor
2021-08-17 | Keswick 1101 | Shasta | 103920243 | Tier 3 | Wind Related | Broken tie wire
2021-08-17 | Stillwater 1102 | Shasta | 101474634 | Tier 2 | Vegetation | Broken conductor
2021-08-17 | Pueblo 2103 | Napa | 102270992 | Tier 3 | Wind Related | Broken tie wire
2021-10-11 | Madison 2101 | Yolo | 101603139 | Non-HFTD | Wind Related | Broken Lightning Arrester
2021-10-11 | King City 1106 | San Benito | 101733238 | Non-HFTD | Vegetation | Damaged conductor
2021-10-11 | Tejon 1102 | Kern | 104051916 | Tier 2 | Vegetation | Damaged conductor
2021-10-11 | Tejon 1102 | Kern | 100222627 | Tier 2 | Vegetation | Broken pole
2021-10-11 | Tejon 1102 | Kern | 100199245 | Tier 2 | Vegetation | Broken crossarm
2021-10-11 | Madison 2101 | Yolo | 103919009 | Non-HFTD | Wind Related | Broken Lightning Arrester
2021-10-11 | Vacaville 1104 | Solano | 101662296 | Tier 2 | Wind Related | Broken crossarm
2021-10-14 | Tejon 1102 | Kern | 103775928 | Tier 2 | Vegetation | Damaged conductor
[1] For the 8/17 event, one hazard was reclassified as a damage during further analysis and validation of the data.

## 19.Hazards
LIST EACH EVENT FOR WHICH DAMAGES WERE DOCUMENTED
Event Name | County or Tribe | Structure Identifier | Identify if Tier 2, Tier 3, Zone 1 (Tier 1 High Hazard Zones), or Non-HFTD | Type of Hazard | Description of Hazard
2021-01-18 | Mariposa 2101 | 101078620 | Tier 2 | Vegetation | Tree branch on line
2021-01-18 | Mariposa 2101 | 101075076 | Tier 2 | Vegetation | Tree branch on line
2021-01-18 | Dunlap 1102 | 100776220 | Tier 2 | Vegetation | Tree leaning into line
2021-01-18 | Oakhurst 1103 | 101017448 | Tier 3 | Vegetation | Tree leaning into line
2021-01-18 | Oakhurst 1103 | 101017056 | Tier 3 | Vegetation | Tree leaning into line
2021-01-18 | Mariposa 2101 | 101073459 | Tier 2 | Vegetation | Tree leaning into line
2021-01-18 | Dunlap 1102 | 100774352 | Tier 2 | Vegetation | Tree leaning into line
2021-01-18 | Dunlap 1103 | 100761796 | Tier 2 | Vegetation | Tree leaning into line
2021-08-17 | Pueblo 2103 | 102269729 | Tier 3 | Vegetation | Tree branch on line
2021-08-17 | Pueblo 2103 | 103781539 | Tier 3 | Vegetation | Tree leaning into line
2021-08-17 | Middletown 1101 | 102166579 | Tier 3 | Vegetation | Tree leaning into line
2021-10-11 | Clark Road 1102 | 100375430 | Tier 2 | Vegetation | Tree branch on line
[1] For the 8/17 event, one hazard was reclassified as a damage during further analysis and validation of the data.

## 20.Claims
LIST EACH EVENT FOR WHICH CLAIMS[1] WERE RECEIVED
Event Name | Circuit Associated with the Claim | County or Tribe of the Service Point | Description of Claim | Type of Claim | Value of Claim | Resolution: Payment Made, Payment Denied, or Pending | Describe any changes made to business processes, procedures, or policies as a result of the claim | PG&E remarks
2021-01-18 | OAKHURST 1103 | MADERA | Property Damage | Property Damage | N/A | Payment Denied | None
2021-01-18 | INDIAN FLAT 1104 | MARIPOSA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None | *These are claims that the customer had reported as being related to PSPS, however our data reflects that these customers were not de-energized or were not on any circuits that were de-energized for any of these events.
2021-01-18 | MARIPOSA 2102 | MARIPOSA | Property Damage | Property Damage | N/A | Payment Denied | None
2021-01-18 | MARIPOSA 2101 | MARIPOSA | Bus. Interr./Econ. Loss (No Prop. Dmg.) | Bus. Interr./Econ. Loss (No Prop. Dmg.) | N/A | Payment Denied | None
2021-01-18 | MARIPOSA 2101 | MARIPOSA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | OREGON TRAIL 1104 | SHASTA | Bus. Interr./Econ. Loss (No Prop. Dmg.) | Bus. Interr./Econ. Loss (No Prop. Dmg.) | N/A | Payment Denied | None
2021-08-17 | SILVERADO 2104 | NAPA | Bus. Interr./Econ. Loss (No Prop. Dmg.) | Bus. Interr./Econ. Loss (No Prop. Dmg.) | N/A | Payment Denied | None
2021-08-17 | STILLWATER 1102 | SHASTA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | MIDDLETOWN 1101 | LAKE | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | COTTONWOOD 1103 | TEHAMA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | STILLWATER 1102 | SHASTA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | ORO FINO 1101 | BUTTE | Property Damage | Property Damage | N/A | Payment Denied | None
2021-08-17 | GIRVAN 1102 | SHASTA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | MIDDLETOWN 1101 | LAKE | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | RED BLUFF 1105 | TEHAMA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | PARADISE 1105 | BUTTE | Bus. Interr./Econ. Loss (No Prop. Dmg.) | Bus. Interr./Econ. Loss (No Prop. Dmg.) | N/A | Payment Denied | None
2021-08-17 | HIGHLANDS 1103 | LAKE | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | COTTONWOOD 1103 | TEHAMA | Bus. Interr./Econ. Loss (No Prop. Dmg.) | Bus. Interr./Econ. Loss (No Prop. Dmg.) | N/A | Payment Denied | None
2021-08-17 | JESSUP 1102 | SHASTA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | ANDERSON 1101 | SHASTA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | HIGHLANDS 1103 | LAKE | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | HIGHLANDS 1103 | LAKE | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | VOLTA 1101 | TEHAMA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | COTTONWOOD 1102 | SHASTA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | COTTONWOOD 1103 | TEHAMA | Property Damage | Property Damage | N/A | Payment Denied | None
2021-08-17 | GIRVAN 1101 | SHASTA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | COTTONWOOD 1102 | SHASTA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | MIDDLETOWN 1101 | LAKE | Property Damage | Property Damage | N/A | Payment Denied | None
2021-08-17 | RED BLUFF 1105 | TEHAMA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | RED BLUFF 1104 | TEHAMA | Prop. Dmg. w/ Bus. Interr./Econ Loss | Prop. Dmg. w/ Bus. Interr./Econ Loss | N/A | Payment Denied | None
2021-08-17 | RED BLUFF 1104 | TEHAMA | Bus. Interr./Econ. Loss (No Prop. Dmg.) | Bus. Interr./Econ. Loss (No Prop. Dmg.) | N/A | Payment Denied | None
2021-08-17 | VOLTA 1102 | SHASTA | Property Damage | Property Damage | N/A | Payment Denied | None
2021-08-17 | CLARK ROAD 1102 | BUTTE | Property Damage | Property Damage | N/A | Payment Denied | None
2021-08-17 | VACA DIXON 1105 | SOLANO | Property Damage | Property Damage | N/A | Payment Denied | None
2021-08-17 | STILLWATER 1101 | SHASTA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-08-17 | VOLTA 1102 | SHASTA | Bus. Interr./Econ. Loss (No Prop. Dmg.) | Bus. Interr./Econ. Loss (No Prop. Dmg.) | N/A | Payment Denied | None
2021-08-17 | CEDAR CREEK 1101 | SHASTA | Bus. Interr./Econ. Loss (No Prop. Dmg.) | Bus. Interr./Econ. Loss (No Prop. Dmg.) | N/A | Payment Denied | None
2021-08-17 | ORO FINO 1101 | BUTTE | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-09-20 | VOLTA 1102 | SHASTA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None | *These are claims that the customer had reported as being related to PSPS, however our data reflects that these customers were not de-energized or were not on any circuits that were de-energized for any of these events.
2021-09-20 | CORNING 1102 | TEHAMA | Property Damage | Property Damage | N/A | Payment Denied | None
2021-09-20 | TEJON 1102 | KERN | Bus. Interr./Econ. Loss (No Prop. Dmg.) | Bus. Interr./Econ. Loss (No Prop. Dmg.) | N/A | Payment Denied | None
2021-09-20 | TEJON 1102 | KERN | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-10-11 | PANORAMA 1101 | TEHAMA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-10-11 | MIDDLETOWN 1102 | LAKE | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-10-11 | JOLON 1102 | MONTEREY | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-10-11 | VACAVILLE 1112 | SOLANO | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-10-11 | VACAVILLE 1111 | SOLANO | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-10-11 | JOLON 1102 | MONTEREY | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-10-11 | VACAVILLE 1112 | SOLANO | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-10-11 | WOODLAND 1110 | YOLO | Property Damage | Property Damage | N/A | Payment Denied | None | *These are claims that the customer had reported as being related to PSPS, however our data reflects that these customers were not de-energized or were not on any circuits that were de-energized for any of these events.
2021-10-11 | VACAVILLE 1104 | SOLANO | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-10-11 | VACAVILLE 1111 | SOLANO | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-10-11 | TEJON 1102 | KERN | Property Damage | Property Damage | N/A | Payment Denied | None
2021-10-11 | VACAVILLE 1111 | SOLANO | Bus. Interr./Econ. Loss (No Prop. Dmg.) | Bus. Interr./Econ. Loss (No Prop. Dmg.) | N/A | Payment Denied | None
2021-10-11 | TEJON 1102 | KERN | Property Damage | Property Damage | N/A | Payment Denied | None
2021-10-11 | JOLON 1102 | MONTEREY | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-10-11 | MIDDLETOWN 1102 | LAKE | Property Damage | Property Damage | N/A | Payment Denied | None
2021-10-11 | TEJON 1102 | KERN | Bus. Interr./Econ. Loss (No Prop. Dmg.) | Bus. Interr./Econ. Loss (No Prop. Dmg.) | N/A | Payment Denied | None
2021-10-11 | CLAYTON 2212 | CONTRA COSTA | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
2021-10-11 | PUTAH CREEK 1102 | YOLO | Food Loss Only | Food Loss Only | N/A | Payment Denied | None
[1] Claims may not match PER exactly because claims are further investigated and may be recategorized (description, PSPS related, etc.)

## 21.EM and Exercises
COMPLETE THE FOUR TABLES BELOW
1. De-Energization Exercises
2. Event EOC and Liaisons
3. EOC-Related Training
4. Other EOC-standup for Training or Actual Event
1. LIST DATA FOR EACH DE-ENERGIZATION EXERCISE
| Exercise Date | Exercise Type (see Definitions) | Number of utility personnel participating in the exercises | Number of PSP actively participating as a player during the exercise. | Number of AFN community members participating as a player during the exercise. | Percentage of exercise materials[1] distributed in advance of the exercise.
| 2021-05-12 | Table Top | 53 | 12 | 11 | 100
| 5/24/21-5/28/21 | Full Scale | 450 | 7 | 0 | 100
| 2021-07-14 | Table Top | 60 | 9 | 0 | 100
| 8/26/21-8/27/21 | Functional | 300 | 10 | 2 | 100
[1] All materials that could be distributed in advance of exercise were distributed. Slide decks and materials developed as part of exercise were not distributed.
2. LIST DATA FOR EACH EVENT'S EOC and LIAISONS
| Event Date | Agency Affiliation of liaisons embedded at your EOC (separate names by commas) | Agency EOCs at which utility personnel were embedded (separate names by commas)
| 2021-01-18 | N/A | N/A
| 2021-08-17 | Cal OES, CPUC | N/A
| 2021-09-20 | Cal OES | N/A
| 2021-10-11 | Cal OES | N/A
| 2021-10-14 | Cal OES | N/A
Insert Additional Rows as Necessary
3. LIST DATA FOR ALL EOC-RELATED TRAINING
| SEMS/NIMS or Equivalent Course | Training Provider | Number of Hours of Training | Number of Personnel Earning a Certificate for the Course
| ICS 100 | FEMA[1] | 4 | 130
| ICS 200 | FEMA[1] | 4 | 131
| ICS 700 | FEMA[1] | 4 | 129
| ICS 800 | FEMA[1] | 4 | 126
| SEMS G606 | CSTI[2] | 2 | 174
| IS 368 | FEMA[1] | 2 | 138
| G-197 | URTA[3] | 8 | 1
| G-775 | URTA[3] | 16 | 0
| G-191 | URTA[3] | 8 | 0
| G-626 | URTA[3] | 8 | 0
| ICS 300 | URTA[3] | 24 | 292
| ICS 400 | URTA[3] | 16 | 221
[1] Web-based Training from FEMA
[2] Web-based Training from CSTI
[3] Instructor-led from Contractor
4. LIST OTHER NON-PSPS EVENTS FOR WHICH YOUR EOC WAS ACTIVATED e.g., ROLLING BLACKOUT, HEAT STORM -- TRAINING or ACTUAL EVENTS
| Type of Event | Start of Event | End of Event | Training?
| Wild Fire TTX | 2022-04-21 | 2021-04-21 | Yes
| Cyber TTX | 2021-01-12 | 2021-01-12 | Yes
| Capacity Shortage TTX | 2021-06-30 | 2021-06-30 | Yes
| Grid Ex FE | 2021-11-15 | 2021-11-16 | Yes
| 1-26-21 Atmospheric River Event | 2021-01-27 | 2021-01-31 | No
| 7-9-21 Capacity Event | 2021-07-09 | 2021-07-12 | No
| 7-14-21 Dixie Fire | 2021-07-14 | 2021-08-13 | No
| 10-24-21 Atmospheric River | 2021-10-21 | 2021-10-28 | No
| 12-13-21 Winter Storm | 2021-12-13 | 2021-12-17 | No
| 12-20-21 LOG4J Vulnerability Event | 2021-12-20 | 2021-12-24 | No
| 12-27-21 Snow Event | 2021-12-28 | 2021-01-08 | No