## Pipeline Leaks
[Company Name], [Date Submitted]
Rulemaking (R.) 15-01-008 to Adopt Rules and Procedures Governing Commission Regulated Natural Gas Pipelines and Facilities to Reduce Natural Gas Leaks Consistent with Senate Bill 1371, Leno.
In Response to Data Request, R15-01-008, 2026 June Report
Appendix 4; Rev. 03/26/2026
Notes:
Use a formula-derived value with the formula used in the Annual Emissions column. Do not use a copy and paste-as-value.
At the end of Annual Emissions Column, add a summation total in a cell for a column total, and then highlight orange.
If all the mains and services are not surveyed annually, use the tab "Unsurveyed Pipeline Leaks" to estimate emissions.
Do not record above ground MSA leaks on this tab. Use Appendix 6 instead. Do continue to list above ground leaks associated with the Distribution Main & Services pipeline system.
After completing the tab on "Pipeline Leaks" and "Unsurveyed Pipeline Leaks," fill in the table for "Pipeline Leak Summary."
Distribution Main & Service Pipeline Leaks: | [15 empty] | Note: No change to O&M leak duration for this reporting year.
ID | Geographic Location | Pipe Classification | Pipe Material | Pipe Size (nominal) | Pipe Age (months) | Pressure (psi) | Leak Grade | Upgraded Leak Grade or Downgraded Leak Grade | Above Ground or Below Ground | Leak Discovery Method | Discovery Date (MM/DD/YY) | Re-Grade Date (MM/DD/YY) | Repair Date (MM/DD/YY) | Scheduled Repair Date (MM/DD/YY) | Reason for Not Scheduling a Repair | Number of Days Leaking | Number of Days to Repair | Emission Factor (Mscf/Day) | Annual Emissions (Mscf) | Explanatory Notes / Comments
[18 empty] | Sum Total Emissions from leaks carried over from before 2025 | 0 | Provided as an example.
[18 empty] | Sum Total Emissions from leaks discovered in 2025 | 0 | Provided as an example.
[18 empty] | Sum Total Emissions from O&M Leaks discovered in 2025 | 0 | Provided as an example.
[18 empty] | Grand Total of all 2025 emissions from leaks | 0 | Provided as an example.
Note on B13: GIS, zip code, or equivalent
Note on C13: MA = distribution main, above ground MB = distribution main, below ground DA = distribution service, above ground DB = distribution service, below ground
Note on D13: C = copper CI = cast iron P = plastics (Acetyl, ABS, PE, PVC, etc.) PB = cathodically protected steel, bare PC = cathodically protected steel, coated UB = unprotected steel, bare UC = unprotected steel, coated
Note on G13: MOP = maximum operating pressure over the past year
Note on H13: If the utility uses grades for above ground leaks, it is unnecessary to use the AH,AN, or AM designations. 1 = grade 1 2 = grade 2 2+ = grade 2+ 3 = grade 3 AH = Above Ground Hazardous synonymous with Grade 1. AN = Above Ground Non-Hazardous, synonymous with Grade 2 and 2+. AM = Above Ground Non-Hazardous Minor (akin to grade 3 below ground leak). N = non-graded or ungraded
Note on I13: U: Upgraded Leak such as a grade 2 or 3 leak that was surveyed again and changed designation to grade 1 or 2. D: downgraded leak, such as a grade 1 or 2 leak that was surveyed again and changed designation to grade 2 or 3.
Note on J13: A = Above Ground B = below ground
Note on K13: S = Routine Leak Survey (This discovery method should be parsed and the emissions summarized into leaks carried over from before 2016, and those detected in 2016. The totals for these subcategories should be carried over to column C43 through D63 on the Unsurveyed Pipeline Leaks tab.) M = O&M (E.G. O&M Activities, Third party reports, customer odor reports etc.) O = Other (This will be grouped with M in the summary categorization of leaks.)
Note on N13: Date that the pipeline repair stopped the leak. Any associated blowdowns resulting from the repair should be included in the blowdowns tab.
Note on O13: If leak is open, specify the scheduled date of repair; Otherwise type "M," signifying that the leak is being monitored with no scheduled date of repair; Then, provide the reason for not scheduling a repair in Column P.
Note on P13: If Repair Date is blank, and Scheduled Repair Date (Column O) = "M," provide the reason for not scheduling a repair.
Note on Q13: If the leak was discovered by survey in the year of interest, then assume leaking from January 1st of subject year thru repair date or December 31st of subject year, which ever is earlier. (E.G. Days Leaking = Repair - Jan 1st + 1 day.) (For days leaking for leaks carried over use January 1st as start date for emissions calculations.) For O&M discovered leaks, assume that the leak begins with the discovery date thru repair date or December 31st of subject year, whichever is earlier.
Note on R13: Use only Repair-Discovery +1. Do not use January 1st for time to repair. For regraded leaks, use Repair Date - Regrade Date +1.

## Unknown Leaks
[Company Name], [Date Submitted]
Rulemaking (R.) 15-01-008 to Adopt Rules and Procedures Governing Commission Regulated Natural Gas Pipelines and Facilities to Reduce Natural Gas Leaks Consistent with Senate Bill 1371, Leno.
In Response to Data Request, R15-01-008, 2026 June Report
Appendix 4; Rev. 03/26/2026
Notes:
Please show the calculation for determining the total emissions. If additional worksheets are necessary, please include those to show intermediate calculations, such as the formula for the Risk-Based Survey Method.
Definitions in Data Request R15-01-008, 2026 June Report
If highlighted cells are filled in, the other cells will auto-populate
The number of miles surveyed (Column C) should be the number of unique miles surveyed, and should not include any repeated miles surveyed multiple times per year.
To clarify the the definition of O&M Leaks (Column O), the following criteria for O&M Leaks should be met: (1) occur stochastically across the whole territory, (2) are reported by customers, (3) found quickly after occurring, (4) found independently of survey activities but would have been found later by surveyors, and (5) considered a small number of leaks.
To clarify the the definition of Survey Leaks (Column G), the following criteria for Survey Leaks should be met: (1) found from company employees or contractors actively searching for leaks (2) including, but not limited to, compliance survey leaks and non-compliance survey leaks (e.g. Super Emitter Programs, Aerial Methane Mapping, Corrosion Surveying.)
Summary of Data by Pipeline Facility/Material and Results for Annual System Leak Rate and Resulting Number of Unknown Leaks for Each Pipeline Facility/Material
Facility/Material | Total System Miles per material type | Miles on Annual Survey [MX,A] | Miles on Multi-Year Survey Cycles [MXTot] | Survey Interval (yrs) [I] | Miles Surveyed Annually from Multi-Year Survey Cycles [MX,I] | Total # of Leaks Detected from Survey [NX,L] | If using a 3-year trailing leak rate average then include - 2023 Annual Leak Rate [RX,1] | If using a 3-year trailing leak rate average then include - 2024 Annual Leak Rate [RX,2] | 2025 Annual Leak Rate [RX,3] | If applicable, then calculate the 3-year Average Leak Rate [Leaks / Mile / Yr] | # of Unknown Leaks | Total # of Leaks Detected from O&M* [NX,O]
Main/Vintage* Plastic |  |  |  | 1 |  |  |  |  | 0 | 0 | 0
Main/Plastic |  |  |  | 3 |  |  |  |  | 0 | 0 | 0
Main/Plastic |  |  |  | 4 |  |  |  |  | 0 | 0 | 0
Main/Plastic |  |  |  | 5 |  |  |  |  | 0 | 0 | 0
Main/Unprotected Steel |  |  |  | 3 |  |  |  |  | 0 | 0 | 0
Main/Unprotected Steel |  |  |  | 4 |  |  |  |  | 0 | 0 | 0
Main/Unprotected Steel |  |  |  | 5 |  |  |  |  | 0 | 0 | 0
Main/Vintage* Protected Steel |  |  |  | 1 |  |  |  |  | 0 | 0 | 0
Main/Protected Steel |  |  |  | 3 |  |  |  |  | 0 | 0 | 0
Main/Protected Steel |  |  |  | 4 |  |  |  |  | 0 | 0 | 0
Main/Protected Steel |  |  |  | 5 |  |  |  |  | 0 | 0 | 0
Service/Vintage* Plastic |  |  |  | 1 |  |  |  |  | 0 | 0 | 0
Service/Plastic |  |  |  | 3 |  |  |  |  | 0 | 0 | 0
Service/Plastic |  |  |  | 4 |  |  |  |  | 0 | 0 | 0
Service/Plastic |  |  |  | 5 |  |  |  |  | 0 | 0 | 0
Service/Unprotected Steel |  |  |  | 3 |  |  |  |  | 0 | 0 | 0
Service/Unprotected Steel |  |  |  | 4 |  |  |  |  | 0 | 0 | 0
Service/Unprotected Steel |  |  |  | 5 |  |  |  |  | 0 | 0 | 0
Service/Vintage* Protected Steel |  |  |  | 1 |  |  |  |  | 0 | 0 | 0
Service/Protected Steel |  |  |  | 3 |  |  |  |  | 0 | 0 | 0
Service/Protected Steel |  |  |  | 4 |  |  |  |  | 0 | 0 | 0
Service/Protected Steel |  |  |  | 5 |  |  |  |  | 0 | 0 | 0
Service/Copper |  |  |  | 3 |  |  |  |  | 0 | 0 | 0
Service/Copper |  |  |  | 4 |  |  |  |  | 0 | 0 | 0
Service/Copper |  |  |  | 5 |  |  |  |  | 0 | 0 | 0
Total | 0 | 0 | 0 | N/A | 0 | 0 |  |  |  | N/A | 0 | 0
*Definitions for "vintage" materials:
Vintage Plastic
Vintage Protected Steel
Estimated Emissions by Pipeline Facility/Material for Each Leakage Category
Leakage Category | Emission Factor (Mscf/day/leak) | 2025 Emissions from Leaks detected Prior to 2025 (Mscf) | 2025 Emissions from Leaks Detected from 2025 Survey (Mscf) | 2025 Emissions from O&M* Leaks Detected in 2025 (Mscf) | 2025 Estimated Emissions from Unknown Leaks (Mscf) | Total Estimated 2025 Emissions from Distribution Pipelines (Mscf)
Facility/Material
Main/Vintage* Plastic | 0.2988 |  |  |  | 0 | 0
Main/Plastic | 0.2988 |  |  |  | 0 | 0
Main/Plastic | 0.2988 |  |  |  | 0 | 0
Main/Plastic | 0.2988 |  |  |  | 0 | 0
Main/Unprotected Steel | 0.1548 |  |  |  | 0 | 0
Main/Unprotected Steel | 0.1548 |  |  |  | 0 | 0
Main/Unprotected Steel | 0.1548 |  |  |  | 0 | 0
Main/Vintage* Protected Steel | 0.0612 |  |  |  | 0 | 0
Main/Protected Steel | 0.0612 |  |  |  | 0 | 0
Main/Protected Steel | 0.0612 |  |  |  | 0 | 0
Main/Protected Steel | 0.0612 |  |  |  | 0 | 0
Service/Vintage* Plastic | 0.0089 |  |  |  | 0 | 0
Service/Plastic | 0.0089 |  |  |  | 0 | 0
Service/Plastic | 0.0089 |  |  |  | 0 | 0
Service/Plastic | 0.0089 |  |  |  | 0 | 0
Service/Unprotected Steel | 0.06 |  |  |  | 0 | 0
Service/Unprotected Steel | 0.06 |  |  |  | 0 | 0
Service/Unprotected Steel | 0.06 |  |  |  | 0 | 0
Service/Vintage* Protected Steel | 0.0276 |  |  |  | 0 | 0
Service/Protected Steel | 0.0276 |  |  |  | 0 | 0
Service/Protected Steel | 0.0276 |  |  |  | 0 | 0
Service/Protected Steel | 0.0276 |  |  |  | 0 | 0
Service/Copper | 0.0226 |  |  |  | 0 | 0
Service/Copper | 0.0226 |  |  |  | 0 | 0
Service/Copper | 0.0226 |  |  |  | 0 | 0
Total | N/A | 0 | 0 | 0 | 0 | 0
O&M leaks include any other pipeline leaks that are discovered during the year from operations and maintenance activity, third party and gas odor reports, etc. that are not accounted for in other categories of this worksheet.
The cells below should be used for calculating emissions when a risk based leak detection and repair practice is used by the Utility. This table is intended to help categorize emissions associated with large leaks (Super Emitters (SEs)), and non-large leaks (non-SEs).
|  | 2025 Emissions from Leaks detected Prior to 2025 (Mscf) | 2025 Emissions from Leaks Detected from 2025 Survey (Mscf) | 2025 Emissions from O&M* Leaks Detected in 2025 (Mscf) | 2025 Estimated Emissions from Unknown Leaks (Mscf) | Total Estimated 2025 Emissions from Distribution Pipelines (Mscf)
Large Leak Emitter Program
Compliance Leak Survey - Non-LL | [5 empty] | 0
Compliance Leak Survey - LL | [5 empty] | 0
Large Leak Emitter Program Outside Compliance Area - Non-LL | [5 empty] | 0
Large Leak Emitter Program Outside Compliance Area - LL | [5 empty] | 0
O&M - Non-LL | [5 empty] | 0
O&M - LL | [5 empty] | 0
TOTAL |  | 0 | 0 | 0 | 0 | 0
Please Provide the following: | Total Count
The portion of the survey mileage that includes mileage that is surveyed multiple times per year. Repeated mileage will not be accounted for in the unknown leak calculation.
𝑹_(𝑿,𝟑)=𝑵_(𝑿,𝑳)/(𝑴_(𝑿,𝑨)+(𝑰×𝑴_(𝑿,𝑰)))
(𝑹_𝑿 ) ̅=𝟏/𝟑 ∑_(𝒊=𝟏)^𝟑▒𝑹_(𝑿,𝒊)
𝑵_(𝑿,𝒖𝒏𝒌 )=(𝑹_𝑿 ) ̅×(𝑴_𝑿^𝑻𝒐𝒕−𝑴_(𝑿,𝑰) )×𝑰/𝟐
Note on L14: If the operator changed the leak survey cycle during the report year that requires more detailed calculations based on the approved calculation methodology to determine the number of unknown leaks an additional worksheet may be added to show the calculations.
Note on B47: Charkowicz, Ed: Where a modified EF is calculated for estimating emissions of LL/SE leaks adn non-LL/SE leaks, provide an additional worksheet which shows all the calculations used to arrive at any EF's used to estimate emissions, when a LL/SE program is used. There should be a clear link or path that shows the source of any EF used for emissions values.
Note on E47: O&M Sources Include: O&M Activities Customer Odor Reports Third Party Reports and other.
Note on F47: Calculation based on the input from column J above.
Note on A78: Charkowicz, Ed: The Utility should determine the best method for breaking down the emissions into these categories. The methodology should be clear and traceable by staff.
Note on E79: O&M Sources Include: O&M Activities Customer Odor Reports Third Party Reports and other.
Note on F79: Calculation based on the input from column J above.

## Pipeline Leaks Summary
[Company Name], [Date Submitted]
Rulemaking (R.) 15-01-008 to Adopt Rules and Procedures Governing Commission Regulated Natural Gas Pipelines and Facilities to Reduce Natural Gas Leaks Consistent with Senate Bill 1371, Leno.
In Response to Data Request, R15-01-008, 2026 June Report
Appendix 4; Rev. 03/26/2026
The designated fields highlighted yellow are optional.
This summary purposefully should exclude damages, blowdowns, component emissions and component leaks.
| Count of Leaks Carried over from Prior Year | Count of Leaks Discovered in the Year of Interest | Count of Leaks Repaired in the Year of Interest | Average Days to Repair Leaks | Count of Estimated Unsurveyed Leaks in the Year of Interest | Count of Remaining Leaks at final day of the Year of Interest (12/31/25) | Emissions from Leaks Carried over from Prior Year. | Emissions from Leaks Discovered in the Year of Interest. | Emissions from Estimated Unsurveyed Leaks in the Year of Interest | Total Emissions in the Year of Interest [Mscf of Natural Gas]
Grade 1 | [5 empty] | 0 |  |  | NA | 0 | x
Grade 2 | [5 empty] | 0 |  |  | NA | 0
Grade 3 | [5 empty] | 0 |  |  | NA | 0
Graded Leak Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Above Ground Hazardous | [5 empty] | 0
Above Ground Non-Hazardous | [5 empty] | 0
Above Ground Non-Hazardous Minor | [5 empty] | 0
AG Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total of All Leaks | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Main/Plastic
Main/Unprotected Steel
Main/Protected Steel
Service/Plastic
Service/Unprotected Steel
Service/Protected Steel
Service/Copper
Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large Leak or Super Emitter Program Categorization
Compliance Leak Survey - Non-LL | [5 empty] | 0 |  |  |  | 0
Compliance Leak Survey - LL | [5 empty] | 0 |  |  |  | 0
Large Leak/Super Emitter Program Outside Compliance Area - Non-LL | [5 empty] | 0 |  |  |  | 0
Large Leak/Super Emitter Program Outside Compliance Area - LL | [5 empty] | 0 |  |  |  | 0
O&M - Non-LL | [5 empty] | 0 |  |  |  | 0
O&M - LL | [5 empty] | 0 |  |  |  | 0
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Change Due to LL/SE Program on 2025: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
% Change Due to LL/SE Program on 2025: | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on B9: Based on a leak start date prior to the first day of the year of interest.
Note on C9: The total number of leaks by grade or category discovered in the year of interest. If a leak is downgraded to not leaking, do not count it.
Note on E9: The average days to repair leaks should be baase on the formula: (Repair Date/Time minus Discovery Date/Time) plus (one day, unless using a discrete time stamp for leak repairs), then take the sum and divide by number of leaks repaired by grade to get the average days to repair.
Note on F9: For leaks identified in Unsurveyed areas extrapolate the proportion of leak counts by grade that were found in the respective areas based on the year or periods used to estimate the unsurveyed leak count. If the unsurveyed leak count was based on the current year leak count by grade detected then use the current proportion of graded leak count applied to the unsurveyed leaks.
Note on G9: This count is only of the actual leaks detected in the operator's system that have not been repaired as of 12/31 of the year of interest.
Note on H9: Based on a leak start date prior to the first day of the year of interest. This includes leaks discovered through O&M and survey activities.
Note on I9: The total number of leaks by grade or category discovered in the year of interest. This includes leaks discovered through O&M and survey activities.
Note on J9: The emissions by grade would be on the same basis that used to extrapolate the count of leaks in the unsurveyed areas. For example: For leaks identified in Unsurveyed areas extrapolate the proportion of leak emissions by grade that were found in the respective areas based on the year or periods used to estimate the unsurveyed leak count. If the unsurveyed leak count was based on the current year leaks detected then use the current proportion of graded leaks applied to the unsurveyed leak emissions.

## All Damages
[Company Name], [Date Submitted]
Rulemaking (R.) 15-01-008 to Adopt Rules and Procedures Governing Commission Regulated Natural Gas Pipelines and Facilities to Reduce Natural Gas Leaks Consistent with Senate Bill 1371, Leno.
In Response to Data Request, R15-01-008, 2026 June Report
Appendix 4; Rev. 03/26/2026
Notes:
Use a formula-derived value with the formula used in the Annual Emissions column. Do not use a copy and paste-as-value.
At the end of Annual Emissions Column, add a summation total in a cell for a column total, and then highlight orange.
Distribution Main & Service Pipeline Damage (3rd party dig-ins, natural disasters, etc.):
ID | Geographic Location | Damage Type | Pipe Classification | Pipe Material | Pipe Size (nominal) | Pipe Age (months) | Pressure (psi) | Leak Grade | Above Ground or Below Ground | Discovery Date (MM/DD/YY) | Repair Date (MM/DD/YY) | Number of Days Leaking | Emission Factor or Engineering Estimate (Mscf/Day) | Annual Emissions (Mscf) | Explanatory Notes / Comments
[13 empty] | Sum Total | 0 | Provided as an example.
Note on B10: GIS, zip code, or equivalent
Note on C10: E = excavation damage N = natural force damage O = other outside force damage
Note on D10: MA = distriibution main, above ground MB = distriibution main, below ground DA = distribution service, above ground DB = distribution service, below ground
Note on E10: C = copper CI = cast iron P = plastics (Acetal, ABS, PE, PVC, etc.) PB = cathodically protected steel, bare PC = cathodically protected steel, coated UB = unprotected steel, bare UC = unptotected steel, coated
Note on H10: MOP = maximum operating pressure over the past year
Note on I10: 1 = grade 1 2 = grade 2 2+ = grade 2+ 3 = grade 3 N = Non-Graded
Note on J10: AH = above ground, hazardous AN = above ground, non-hazardous B = below ground
Note on M10: If date and time stamp are reliable and used consistently by respondent, then emissions may be calculated based on actual time leaking. E.G. Repair time - damage event time = duration of event. If respondent has average or historical leak duration based on the nature and circumstances of damages, then these may be applied to like damage events. The emissions factors should be adequately supported and explained in the filing. If actual time stamps and historical averages are not available, then whole days should be used in the engineering calculation. The leak begins with the damage event date thru repair date or December 31st of subject year, whichever is later. E.G. Days Leaking = Repair date - date of damage + 1 day.

## Blowdowns
[Company Name], [Date Submitted]
Rulemaking (R.) 15-01-008 to Adopt Rules and Procedures Governing Commission Regulated Natural Gas Pipelines and Facilities to Reduce Natural Gas Leaks Consistent with Senate Bill 1371, Leno.
In Response to Data Request, R15-01-008 2026 June Report
Appendix 4; Rev. 03/26/2026
Notes:
Use a formula-derived value with the formula used in the Annual Emissions column. Do not use a copy and paste-as-value.
At the end of Annual Emissions Column, add a summation total in a cell for a column total, and then highlight orange.
Distribution Main & Service Pipeline Blowdowns:
ID | Geographic Location | Number of Blowdown Events | Pipe Size (nominal) | Length of Pipe | Pressure (psi) | Annual Emissions (Mscf) | Explanatory Notes / Comments
[5 empty] | Sum Total | 0 | Provided as an example.
Note on B10: GIS, zip code, or equivalent
Note on C10: If counting a series of small blowdowns associated with services such as MSA replacement, or Service pipe of small diameter or section length then enter total and the formula in the explanation column.
Note on F10: MOP = maximum operating pressure over the past year

## Component Vented Emissions
[Company Name], [Date Submitted]
Rulemaking (R.) 15-01-008 to Adopt Rules and Procedures Governing Commission Regulated Natural Gas Pipelines and Facilities to Reduce Natural Gas Leaks Consistent with Senate Bill 1371, Leno.
In Response to Data Request, R15-01-008 2026 June Report
Appendix 4; Rev. 03/26/2026
Notes:
Use a formula-derived value with the formula used in the Annual Emissions column. Do not use a copy and paste-as-value.
At the end of Annual Emissions Column, add a summation total in a cell for a column total, and then highlight orange.
The emissions captured on this tab represent the emissions associated with the operational design and function of the component. Any intentional release of natural gas for safety or maintenance purposes should be included on the Blowdowns worksheet.
Distribution Main & Service Pipeline Component Vented Emissions (see note above):
Total Number of Devices | Device Type | Bleed Rate | Manufacturer | Engineering or Manufacturer's based Estimate of Emissions | Annual Emissions (Mscf) | Explanatory Notes / Comments
0
|  |  |  | Sum Total | 0 | Provided as an example.
Note on B11: P = pneumatic device H = hydraulic valve operator T = turbine valve operator PR = pressure relief valve O = other devices
Note on C11: L = low bleed I = intermittent bleed H = high bleed NA = not applicable

## Component Fugitive Leaks
[Company Name], [Date Submitted]
Rulemaking (R.) 15-01-008 to Adopt Rules and Procedures Governing Commission Regulated Natural Gas Pipelines and Facilities to Reduce Natural Gas Leaks Consistent with Senate Bill 1371, Leno.
In Response to Data Request, R15-01-008 2026 June Report
Appendix 4; Rev. 03/26/2026
Notes:
Use a formula-derived value with the formula used in the Annual Emissions column. Do not use a copy and paste-as-value.
At the end of Annual Emissions Column, add a summation total in a cell for a column total, and then highlight orange.
The emissions captured on this tab represent the emissions associated unintentional leaks that if repaired would not leaking. If the component is releasing gas or "bleeding" as a result of its design or function then it is not to be captured in this tab.
Distribution Main & Service Pipeline Component Fugitive Leaks (see note above):
Total Number of Devices | Device Type | Bleed Rate | Manufacturer | Discovery Date (MM/DD/YY) | Repair Date (MM/DD/YY) | Number of Days Leaking | Emission Factor (Mscf/day) | Annual Emission (Mscf) | Explanatory Notes / Comments
[7 empty] | Sum total | 0 | Provided as an example.
Note on B11: P = pneumatic device H = hydraulic valve operator T = turbine valve operator PR = pressure relief valve O = other devices
Note on C11: L = low bleed I = intermittent bleed H = high bleed NA = not applicable
Note on E11: List the actual discovery date. If the leak was discovered in the year of interest, then we will assume the component was leaking from the beginning of the year for emissions reporting purposes.
Note on F11: Date that the component repair stopped the leak. Any associated blowdowns as a result of the repair should be included in the blowdowns tab.
Note on G11: Assume Leaking from January 1 of subject year or prior survey date, whichever is later, thru the repair date (if repaired in year of interest) or December 31 of subject year, whichever is earlier. For O&M discovered leaks, assume that the leak begins with the discovery date thru repair date or December 31st of subject year, whichever is earlier.

## Column Header & Description
Appendix 4; Rev. 03/26/2026
Header column "Comment" boxes displayed below for reference.
Column Heading | Description and Definition of Required Contents (IF not self-explanatory)
Pipeline Leaks
ID
Geographic Location | GIS, zip code, or equivalent
Pipe Classification | MA = distribution main, above ground MB = distribution main, below ground DA = distribution service, above ground DB = distribution service, below ground
Pipe Material | C = copper CI = cast iron P = plastics (Acetyl, ABS, PE, PVC, etc.) PB = cathodically protected steel, bare PC = cathodically protected steel, coated UB = unprotected steel, bare UC = unprotected steel, coated
Pipe Size (nominal)
Pipe Age (months)
Pressure (psi) | MOP = maximum operating pressure over the past year
Leak Grade | If the utility uses grades for above ground leaks, it is unnecessary to use the AH,AN, or AM designations. 1 = grade 1 2 = grade 2 2+ = grade 2+ 3 = grade 3 AH = Above Ground Hazardous synonymous with Grade 1. AN = Above Ground Non-Hazardous, synonymous with Grade 2 and 2+. AM = Above Ground Non-Hazardous Minor (akin to grade 3 below ground leak). N = non-graded or ungraded
Upgraded Leak Grade or Downgraded Leak Grade | U: Upgraded Leak such as a grade 2 or 3 leak that was surveyed again and changed designation to grade 1 or 2. D: downgraded leak, such as a grade 1 or 2 leak that was surveyed again and changed designation to grade 2 or 3.
Above Ground or Below Ground | A = Above Ground B = below ground
Leak Discovery Method | S = Routine Leak Survey (This discovery method should be parsed and the emissions summarized into leaks carried over from before 2016, and those detected in 2016. The totals for these subcategories should be carried over to column C43 through D63 on the Unsurveyed Pipeline Leaks tab.) M = O&M (E.G. O&M Activities, Third party reports, customer odor reports etc.) O = Other (This will be grouped with M in the summary categorization of leaks.)
Discovery Date (MM/DD/YY)
Re-Grade Date (MM/DD/YY)
Repair Date (MM/DD/YY) | Date that the pipeline repair stopped the leak. Any associated blowdowns resulting from the repair should be included in the blowdowns tab.
Scheduled Repair Date (MM/DD/YY) | If leak is open, specify the scheduled date of repair; Otherwise type "M," signifying that the leak is being monitored with no scheduled date of repair; Then, provide the reason for not scheduling a repair in Column P.
Reason for Not Scheduling a Repair | If Repair Date is blank, and Scheduled Repair Date (Column O) = "M", then provide the reason for not scheduling a repair.
Number of Days Leaking | If the leak was discovered by survey in the year of interest, then assume leaking from January 1st of subject year thru repair date or December 31st of subject year, which ever is earlier. (E.G. Days Leaking = Repair - Jan 1st + 1 day.) (For days leaking for leaks carried over use January 1st as start date for emissions calculations.) For O&M discovered leaks, assume that the leak begins with the discovery date thru repair date or December 31st of subject year, whichever is earlier.
Number of Days to Repair | Use only Repair-Discovery +1. Do not use January 1st for time to repair. For regraded leaks, use Repair Date - Regrade Date +1.
Emission Factor (Mscf/Day)
Annual Emissions (Mscf)
Explanatory Notes / Comments
Unknown Leaks
Facility/Material
Total System Miles per material type
Miles on Annual Survey [MX,A]
Miles on Multi-Year Survey Cycles [MXTot]
Survey Interval (yrs) [I]
Miles Surveyed Annually from Multi-Year Survey Cycles [MX,I]
Total # of Leaks Detected from Survey [NX,L]
If using a 3-year trailing leak rate average then include - 2019 Annual Leak Rate [RX,1]
If using a 3-year trailing leak rate average then include - 2020 Annual Leak Rate [RX,2]
2022 Annual Leak Rate [RX,3]
If applicable, then calculate the 3-year Average Leak Rate [Leaks / Mile / Yr]
# of Unknown Leaks
Total # of Leaks Detected from O&M* [NX,O]
Pipeline Leaks Summary
Count of Leaks Carried over from Prior Year | Based on a leak start date prior to the first day of the year of interest.
Count of Leaks Discovered in the Year of Interest | The total number of leaks by grade or category discovered in the year of interest. If a leak is downgraded to not leaking, do not count it.
Count of Leaks Repaired in the Year of Interest
Average Days to Repair Leaks | The average days to repair leaks should be baase on the formula: (Repair Date/Time minus Discovery Date/Time) plus (one day, unless using a discrete time stamp for leak repairs), then take the sum and divide by number of leaks repaired by grade to get the average days to repair.
Count of Estimated Unsurveyed Leaks in the Year of Interest | For leaks identified in Unsurveyed areas extrapolate the proportion of leak counts by grade that were found in the respective areas based on the year or periods used to estimate the unsurveyed leak count. If the unsurveyed leak count was based on the current year leak count by grade detected then use the current proportion of graded leak count applied to the unsurveyed leaks.
Count of Remaining Leaks at final day of the Year of Interest (12/31/xx) | This count is only of the actual leaks detected in the operator's system that have not been repaired as of 12/31 of the year of interest.
Emissions from Leaks Carried over from Prior Year. | Based on a leak start date prior to the first day of the year of interest. This includes leaks discovered through O&M and survey activities.
Emissions from Leaks Discovered in the Year of Interest. | The total number of leaks by grade or category discovered in the year of interest. This includes leaks discovered through O&M and survey activities.
Emissions from Estimated Unsurveyed Leaks in the Year of Interest | The emissions by grade would be on the same basis that used to extrapolate the count of leaks in the unsurveyed areas. For example: For leaks identified in Unsurveyed areas extrapolate the proportion of leak emissions by grade that were found in the respective areas based on the year or periods used to estimate the unsurveyed leak count. If the unsurveyed leak count was based on the current year leaks detected then use the current proportion of graded leaks applied to the unsurveyed leak emissions.
Total Emissions in the Year of Interest [Mscf of Natural Gas]
All Damages
ID
Geographic Location | GIS, zip code, or equivalent
Damage Type | E = excavation damage N = natural force damage O = other outside force damage
Pipe Classification | MA = distriibution main, above ground MB = distriibution main, below ground DA = distribution service, above ground DB = distribution service, below ground
Pipe Material | C = copper CI = cast iron P = plastics (Acetal, ABS, PE, PVC, etc.) PB = cathodically protected steel, bare PC = cathodically protected steel, coated UB = unprotected steel, bare UC = unptotected steel, coated
Pipe Size (nominal)
Pipe Age (months)
Pressure (psi) | MOP = maximum operating pressure over the past year
Leak Grade | 1 = grade 1 2 = grade 2 2+ = grade 2+ 3 = grade 3 N = Non-Graded
Above Ground or Below Ground | AH = above ground, hazardous AN = above ground, non-hazardous B = below ground
Discovery Date (MM/DD/YY)
Repair Date (MM/DD/YY)
Number of Days Leaking | If date and time stamp are reliable and used consistently by respondent, then emissions may be calculated based on actual time leaking. E.G. Repair time - damage event time = duration of event. If respondent has average or historical leak duration based on the nature and circumstances of damages, then these may be applied to like damage events. The emissions factors should be adequately supported and explained in the filing. If actual time stamps and historical averages are not available, then whole days should be used in the engineering calculation. The leak begins with the damage event date thru repair date or December 31st of subject year, whichever is later. E.G. Days Leaking = Repair date - date of damage + 1 day.
Emission Factor or Engineering Estimate (Mscf/Day)
Annual Emissions (Mscf)
Explanatory Notes / Comments
Blowdowns
ID
Geographic Location | GIS, zip code, or equivalent
Number of Blowdown Events | If counting a series of small blowdowns associated with services such as MSA replacement, or Service pipe of small diameter or section length then enter total and the formula in the explanation column.
Pipe Size (nominal)
Length of Pipe
Pressure (psi) | MOP = maximum operating pressure over the past year
Annual Emissions (Mscf)
Explanatory Notes / Comments
Component Vented Emissions
Total Number of Devices
Device Type | P = pneumatic device H = hydraulic valve operator T = turbine valve operator PR = pressure relief valve O = other devices
Bleed Rate | L = low bleed I = intermittent bleed H = high bleed NA = not applicable
Manufacturer
Engineering or Manufacturer's based Estimate of Emissions
Annual Emissions (Mscf)
Explanatory Notes / Comments
Component Fugitive Leaks
Total Number of Devices
Device Type | P = pneumatic device H = hydraulic valve operator T = turbine valve operator PR = pressure relief valve O = other devices
Bleed Rate | L = low bleed I = intermittent bleed H = high bleed NA = not applicable
Manufacturer
Discovery Date (MM/DD/YY) | List the actual discovery date. If the leak was discovered in the year of interest, then we will assume the component was leaking from the beginning of the year for emissions reporting purposes.
Repair Date (MM/DD/YY) | Date that the component repair stopped the leak. Any associated blowdowns as a result of the repair should be included in the blowdowns tab.
Number of Days Leaking | Assume Leaking from January 1 of subject year or prior survey date, whichever is later, thru the repair date (if repaired in year of interest) or December 31 of subject year, whichever is earlier. For O&M discovered leaks, assume that the leak begins with the discovery date thru repair date or December 31st of subject year, whichever is earlier.
Emission Factor (Mscf/day)
Annual Emission (Mscf)
Explanatory Notes / Comments
𝑹_(𝑿,𝟑)=𝑵_(𝑿,𝑳)/(𝑴_(𝑿,𝑨)+(𝑰×𝑴_(𝑿,𝑰)))
(𝑹_𝑿 ) ̅=𝟏/𝟑 ∑_(𝒊=𝟏)^𝟑▒𝑹_(𝑿,𝒊)
𝑵_(𝑿,𝒖𝒏𝒌 )=(𝑹_𝑿 ) ̅×(𝑴_𝑿^𝑻𝒐𝒕−𝑴_(𝑿,𝑰) )×𝑰/𝟐
Note on A38: If the operator changed the leak survey cycle during the report year that requires more detailed calculations based on the approved calculation methodology to determine the number of unknown leaks an additional worksheet may be added to show the calculations.