## Emission Factors 2025
[Company Name], [Date Submitted]
Rulemaking (R.) 15-01-008 to Adopt Rules and Procedures Governing Commission Regulated Natural Gas Pipelines and Facilities to Reduce Natural Gas Leaks Consistent with Senate Bill 1371, Leno.
In Response to Data Request, R15-01-008 2025 June Report
Appendix 9; Rev. 03/27/2025
System Categories | Emission Source Categories | Emission Factor Sources | Description [in natural gas volume]
Transmission Pipeline | Transmission Pipeline Leaks | Engineering Estimate | Emissions estimated from size of breach / pressure / duration calculation
| All damages (as defined by PHMSA) | Engineering Estimate | Emissions estimated either from modelling or size of breach / pressure / duration
| Transmission Pipeline Blowdowns | Engineering Estimate | Unique equipment volume (corrected for pressure and temperature)
| Pneumatic Devices - Pneumatic/Hydraulic Valve Operators, and Turbine Valve Operators | MRR | Low Continuous Bleed = 0.0336 Mscf/day/dev Intermittent Bleed = 0.0576 Mscf/day/dev High Continuous Bleed = 0.4457 Mscf/day/dev Hydraulic Valve Operator = TBD Turbine Valve Operator = TBD
| Pressure Relief Valves | MRR | Pressure relief valve = 0.9518 Mscf/day/dev
| Odorizer (Odorizer and Gas Sampling Vents) | TCR | 1.27 Mscf/yr/odorizer (if manufacturing specs are available, use the manufacting specs instead of the default emission factor)
Transmission M&R | M&R Stations - Direct Industrial Sales | MRR | # of leaks > 10,000 ppm x Subpart W EF (ref: Table W-3 of Subpart W of Part 98) Direct Sale = 12.2 Mscf/yr/station (ref: Table W-4 of Subpart W of Part 98) Compressor Components Continuous Low Bleed = 0.163 Mscf/day/dev Continuous High Bleed = 0.720 Mscf/day/dev Intermittent Bleed = 0.055 Mscf/day/dev Non-compressor Components Valve = 0.154 Mscf/day/dev Connector = 0.137 Mscf/day/dev Open-ended line = 0.270 Mscf/day/dev Pressure relief valve = 0.048 Mscf/day/dev Meter = 0.070 Mscf/day/dev Other = 0.098 Mscf/day/dev
| M&R Stations - Transmission-to-Transmission Company Interconnect | MRR | # of leaks > 10,000 x Subpart W EF (ref: Table W-3 of Subpart W of Part 98) Trans-to-trans = 1554.8 Mscf/yr/stations (ref: Table W-4 of Subpart W of Part 98) Compressor Components Continuous Low Bleed = 0.163 Mscf/day/dev Continuous High Bleed = 0.720 Mscf/day/dev Intermittent Bleed = 0.055 Mscf/day/dev Non-compressor Components Valve = 0.154 Mscf/day/dev Connector = 0.137 Mscf/day/dev Open-ended line = 0.270 Mscf/day/dev Pressure relief valve = 0.048 Mscf/day/dev Meter = 0.070 Mscf/day/dev Other = 0.098 Mscf/day/dev
| Transmission M&R Leaks | MRR | (ref: Table W-4 of Subpart W of Part 98) Compressor Components Continuous Low Bleed = 0.163 Mscf/day/dev Continuous High Bleed = 0.720 Mscf/day/dev Intermittent Bleed = 0.055 Mscf/day/dev Non-compressor Components Valve = 0.154 Mscf/day/dev Connector = 0.137 Mscf/day/dev Open-ended line = 0.270 Mscf/day/dev Pressure relief valve = 0.048 Mscf/day/dev Meter = 0.070 Mscf/day/dev Other = 0.098 Mscf/day/dev
| Transmission M&R blowdown | Engineering Estimate | Unique equipment volume (corrected for pressure and temperature)
Transmission Compressor Stations | Compressor station - Equipment leaks from valves, connectors, open ended lines, pressure relief valves, and meters (using leak detection) | MRR | Leaker EFs-Compressor Station (Component Leaks identified per survey use the following EFs) # of leaks > 10,000 ppm x Subpart W EF (ref: Table W-3 of Subpart W of Part 98) Compressor Components Valve = 0.3562Mscf/day/dev Connector = 0.1342 Mscf/day/dev Open-Ended Line = 0.4145 Mscf/day/dev Pressure Relief Valve = 0.9518 Mscf/day/dev Meter = 0.4639 Mscf/day/dev Other = 0.0984 Mscf/day/dev Non-compressor components Valve = 0.1541 Mscf/day/dev Connector = 0.1370 Mscf/day/dev Open-ended line = 0.2705 Mscf/day/dev Pressure relief valve = 0.0482 Mscf/day/dev Meter = 0.0703 Mscf/day/dev Other = 0.0984 Mscf/day/dev
| Compressor Station - Transmission storage tanks | MRR | Direct measurement of tank vapor vent stack + operating hours (pg 218-219 of Regulation for MRR)
| Compressors (Centrifugal) - Transmission--data collection will require time spent in modes (active, pressurized idle, de-pressurized idle), compressor venting | MRR | Direct measurement x operating hours (operating mode)
| Compressors (Reciprocating) - Transmission--data collection will require time spent in modes (active, pressurized idle, de-pressurized idle)compressor rod packing venting | MRR | Direct measurement x operating hours (operating mode)
| Compressor station - Equipment and pipeline blowdowns | MRR | Eq. W - 14A # of blowdowns * piping volume
| Compressor Station - Natual gas pneumatic device venting | MRR | Low Continuous Bleed = 0.0336 Mscf/day/dev Intermittent Bleed = 0.0576 Mscf/day/dev High Continuous Bleed = 0.4457 Mscf/day/dev
Distribution Mains and Services Pipelines | Distribution Mains (Below-Ground Leaks) | GRI (1996) | Unprotected Steel Main = 0.1548 Mscf/day/leak Protected Steel Main = 0.0612 Mscf/day/leak Plastic Main = 0.2988 Mscf/day/leak
| Distribution Mains (Above Ground Leaks) - Not MSA | GRI (1996) | Unprotected Steel Main = 0.1548 Mscf/day/leak Protected Steel Main = 0.0612 Mscf/day/leak Plastic Main = 0.2988 Mscf/day/leak
| Distribution Service (Below-Ground Leaks) | GRI (1996) | Copper = 0.0226 Mscf/day/leak Unprotected Steel Service = 0.0600 Mscf/day/leak Protected Steel Servce = 0.0276 Mscf/day/leak Plastic Service = 0.0089 Msc/day/leak
| Distribution Service (Above-Ground Leaks) - Not MSA | GRI (1996) | Copper = 0.0226 Mscf/day/leak Unprotected Steel Service = 0.0600 Mscf/day/leak Protected Steel Servce = 0.0276 Mscf/day/leak Plastic Service = 0.0089 Msc/day/leak
| Distribution Main, Pressure Relief Valves | MRR | Pressure relief valve = 0.00696 Mscf/day/dev
| Distribution Mains and Services blowdown | MRR | Equation W-14A , Eq. W-35 , Eq. W-36
| All damages (as defined by PHMSA) | MRR | Equation W-14A , Eq. W-35 , Eq. W-36
| Pneumatic Devices - Pneumatic/Hydraulic Valve Operators, and Turbine Valve Operators | Engineering Estimate | Manufacturer Supplied Information (e.g., Bristol, Becker, Moore, etc)
Distribution M&R Stations | Distribution Above grade M&R Station Leaks ( > 300 psi) | GRI (1996) | 1,684.5 Mscf/yr/station
| Distribution Above grade M&R Station Leaks (100 - 300 psi) | GRI (1996) | 896.5 Mscf/yr/station
| Distribution Above grade M&R Station Leaks ( < 100 psi) | GRI (1996) | 40.6 Mscf/yr/station
| Distribution Below grade M&R Station Leaks (> 300 psi) | GRI (1996) | 12.176 Mscf/yr/station
| Distribution Below grade M&R Station Leaks (100 - 300 psi) | GRI (1996) | 1.840 Mscf/yr/station
| Distribution Below grade M&R Station Leaks (< 100 psi) | GRI (1996) | 0.964 Mscf/yr/station
| Distribution M&R Station, Leaker Based | MRR | Leaker EFs (Component Leaks identified per survey use the following EFs) Connector = 0.041Mscf/day/dev Block Valve = 0.013 Mscf/day/dev Control Valve = 0.224 Mscf/day/dev Pressure Relief Valve = 0.006 Mscf/day/dev Orifice Meter = 0.005 Mscf/day/dev Regulator = 0.019 Mscf/day/dev Open-Ended Line = 0.627 Mscf/day/dev
| M&R Stations - Farm Taps | MRR | # of leaks > 10,000 ppm x Subpart W EF (ref: Table W-3 of Subpart W of Part 98) Farm Tap = 12.2 Mscf/yr/station (ref: Table W-6 of Subpart W of Part 98) Leaker EFs (Component Leaks identified per survey use the following EFs) Connector = 0.041Mscf/day/dev Block Valve = 0.013 Mscf/day/dev Control Valve = 0.224 Mscf/day/dev Pressure Relief Valve = 0.006 Mscf/day/dev Orifice Meter = 0.005 Mscf/day/dev Regulator = 0.019 Mscf/day/dev Open-Ended Line = 0.627 Mscf/day/dev
| Distribution M&R Station Blowdowns | Engineering Estimate | Average Pressure x Average Volume x # of inspections & Maintenance Activities
| Distribution M&R Station Pneumatics | Engineering Estimate | Manufacturer Supplied Information (e.g., Bristol, Bettis Actuators, etc)
Commercial, Industrial and Residential Meters | Residential Meters | GRI (1996) | 0.148 Mscf/yr/meter
| Commercial and Industrial Meters | GRI (1996) | 0.051 Mscf/yr/meter
| Vented Emission from MSA | Engineering Estimate | Estimated volume release by MSA and activity type
Underground Storage | Dehydrator Vents - Storage (dehydrator vent emissions tab) | GRI (1996) | One of the following three cases per dehydrator facility 1. Glycol dehydrator with VRU and thermal oxidizer = 0 Mscf 2. Glycol dehydrator with no control device = Engineering Estimate 3. Desiccant dehydrator = 2.23E-03 mt CH4/MMscf (Alternative: Eq. 5 in MRR)
| Storage - piping leakage (compressor and component fugitive leaks tab) | MRR | Leaker EFs-Storage Station, Gas Service (Component Leaks identified per survey use the following EFs) Connector = 0.1342 Mscf/day/dev Valve = 0.3562 Mscf/day/dev Pressure Relief Valve = 0.9518 Mscf/day/dev Open-Ended Line = 0.4145 Mscf/day/dev Meter = 0.4639 Mscf/day/dev Other = 0.0984 Mscf/day/dev Population EFs-Storage Wellheads, Gas Service (For all un-surveyed components use the following EFs) Connector = 0.0002 Mscf/day/dev Valve = 0.0024 Mscf/day/dev Pressure Relief Valve = 0.0041 Mscf/day/dev Open Ended Line = 0.0007 Mscf/day/dev
| Storage - surface casing leakage (storage leaks and emissions tab) | Engineering Estimate | TBD
| Storage - Wellhead leakage (storage leaks and emissions tab) | MRR | Leaker EFs-Storage Wellheads, Gas Service (Component Leaks identified per survey use the following EFs) Connector (other than flanges) = 0.0288 Mscf/day/dev Valve = 0.1080 Mscf/day/dev Pressure Relief Valve = 0.0984 Mscf/day/dev Open-Ended Line = 0.0600 Mscf/day/dev Flange = 0.0912 Mscf/day/dev Other = 0.0984 Mscf/day/dev Population EFs-Storage Wellheads, Gas Service (For all un-Surveyed components, use the following EFs) Connector = 0.0002 Mscf/day/dev Valve = 0.0024 Mscf/day/dev Pressure Relief Valve = 0.0041 Mscf/day/dev Open-Ended Line = 0.0007 Mscf/day/dev
| Storage - Compressor & blowdowns (Blowdowns tab) | Engineering Estimate | Eq. 13 of MRR (piping volume x # of blowdowns)
| Storage - Wellhead Rework blowdown and bring-in (Blowdowns tab) | Engineering Estimate | Eq. 9,10,11,12 of MRR
| Pressure Relief Valves (Component Vented Emissions tab) | MRR | Pressure relief vallve = 0.9518 Mscf/day/dev.
| Pneumatic Devices - Pneumatic/Hydraulic Valve Operators, and Turbine Valve Operators (Component Vented Emissions tab) | MRR | Low Continuous Bleed = 0.0336 Mscf/day/dev Intermittent Bleed = 0.0576 Mscf/day/dev High Continuous Bleed = 0.4457 Mscf/day/dev Hydraulic Valve Operator = TBD Turbine Valve Operator = TBD