## 2017 Data Set
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations |  |  |  |  | Notes (Optional):
| Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
PG&E | 2017-01-01 15:59 | 15:57 | 38.6629 | -121.748 | Vegetation | Urban | < 3 Meters | Fire Agency | Woodland fire dept 530-666-8920 | 101589774 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-01-01 15:59 | 15:57 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-01-10 | 15:55 | 38.7538 | -121.1564 | Building | Urban | Structure Only | Unknown | N.A. | 100065079 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-01-10 | 15:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-01-18 | 15:34 | 37.3839 | -121.8088 | Building | Urban | Structure Only | Unknown | N.A. | 100564835 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-01-18 | 15:34 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-01-29 09:46 | 09:45 | 38.3616 | -121.9509 | Building | Urban | Structure Only | Fire Agency | Unknown | T8550 | Unknown | 12000 | Transformer | Subsurface | Yes | 2017-01-29 09:46 | 09:45 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-02-03 10:01 | 10:00 | 37.5615 | -122.0277 | Vegetation | Urban | < 3 Meters | Fire Agency | jeff | 100938466 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-02-03 10:01 | 10:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-02-07 04:50 | 04:50 | 38.4331 | -122.719 | Building | Urban | Structure Only | Fire Agency | Santa Rosa Fire Dept | 102014637 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-02-07 04:50 | 04:50 | Other | N.A. | N.A. | N.A. | Unknown
PG&E | 2017-03-16 12:44 | 12:43 | 38.2718 | -122.0197 | Other | Urban | < 0.25 Acres | Fire Agency | Unknown | 101561532 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-03-16 12:44 | 12:43 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-03-17 09:37 | 09:37 | 38.1153 | -121.4222 | Other | Rural | Structure Only | Fire Agency | 911 | 102044732 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 2017-03-17 09:37 | 09:37 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused
PG&E | 2017-03-19 17:06 | 17:06 | 39.7621 | -121.8525 | Vegetation | Urban | < 3 Meters | Fire Agency | CHICO FIRE DEPT 911 | 100441377 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-03-19 17:06 | 17:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-03-23 07:04 | 07:04 | 37.3697 | -121.8522 | Other | Urban | < 3 Meters | Fire Agency | SJFD disp 408-277-8950 Icident# F170829041 | 103485262 | Unknown | 12000 | Transformer | Subsurface | Yes | 2017-03-23 07:04 | 07:04 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-03-28 12:18 | 12:15 | 34.8809 | -120.4199 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 103397961 | YES | 12000 | Conductor | Overhead | Yes | 2017-03-28 12:18 | 12:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-04-01 15:01 | 14:54 | 37.1882 | -120.9576 | Vegetation | Rural | < 0.25 Acres | Fire Agency | engine 74 mrced fire agency | 102318665 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-04-01 15:01 | 14:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-04-04 13:36 | 13:29 | 35.6885 | -120.7653 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101945026 | None | 12000 | Conductor | Overhead | Yes | 2017-04-04 13:36 | 13:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-04-04 18:18 | 14:54 | 37.2958 | -121.933 | Vegetation | Urban | < 3 Meters | Customer | N.A. | 100591136 | None | 12000 | Conductor | Overhead | Yes | 2017-04-04 18:18 | 14:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-04-10 16:38 | 16:35 | 35.6175 | -119.743 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 100128630 | Unknown | 21000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-04-13 14:08 | 14:21 | 37.7967 | -121.2521 | Other | Urban | Structure Only | Fire Agency | MANTECA CITY | 102104500 | VERIZON CALIFORNIA | 17000 | Conductor | Overhead | Yes | 2017-04-13 14:08 | 14:21 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-04-16 15:33 | 15:14 | 35.5805 | -119.1423 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103833904 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-04-16 15:33 | 15:14 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-04-20 20:19 | 20:14 | 37.3741 | -120.7169 | Vegetation | Urban | < 3 Meters | Fire Agency | 209-966-3621 | 101205903 | Unknown | 12000 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-04-23 07:32 | 7:10 | 36.0735 | -120.9345 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101726333 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-04-23 07:32 | 7:10 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-04-24 11:57 | 11:52 | 36.1899 | -121.1513 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101718856 | None | 12000 | Conductor | Overhead | Yes | 2017-04-24 11:57 | 11:52 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | tie wire
PG&E | 2017-04-25 12:39 | 12:38 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 2017-04-25 12:39 | 12:38 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-04-25 18:26 | 18:26 | 36.2373 | -119.7807 | Other | Rural | Structure Only | Self Extinguished | N.A. | 100716676 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-04-25 18:26 | 18:26 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-04-26 16:17 | 15:55 | 38.1561 | -121.6789 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT KENNY WILLIAMS (707)374-2233 | 103826165 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-04-26 16:17 | 15:55 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's nest
PG&E | 2017-04-28 07:18 | 5:55 | 34.5885 | -120.1057 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 805-683-2724 | 101900122 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-04-28 07:18 | 5:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-04-28 14:41 | 14:35 | 37.1247 | -121.6249 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Cal Fire | 103098414 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-04-28 14:41 | 14:35 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-04-28 16:21 | 15:49 | 38.7679 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chris paper fire investigator, 530/677-1868. incident #caaeuo11821 | 101409833 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 2017-04-28 16:21 | 15:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-04-29 15:29 | 15:07 | 37.0349 | -119.5242 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100678661 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-04-29 15:29 | 15:07 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-04-30 09:35 | 9:32 | 35.6349 | -118.9563 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 661-324-6551 | 100216308 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-04-30 09:35 | 9:32 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-05-01 | 14:20 | 36.0227 | -119.9584 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CORCORAN STATION 559-992-2156 | Pole 076/015 | Unknown | 70000 | Conductor | Overhead | Yes | 2017-05-01 | 14:20 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's nest
PG&E | 2017-05-03 10:05 | 10:04 | 36.8161 | -119.632 | Vegetation | Rural | < 0.25 Acres | Fire Agency | eng 44 Eric connors 559-324-2294 | 100770906 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-05-03 10:05 | 10:04 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-05-03 13:06 | 12:51 | 38.1908 | -121.6615 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103834798 | None | 21000 | Conductor | Overhead | Yes | 2017-05-03 13:06 | 12:51 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-05-04 16:21 | 16:19 | 35.5573 | -120.7535 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101934476 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-05-04 16:21 | 16:19 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-05-05 15:52 | 15:52 | 40.3776 | -123.0019 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101501566 | None | 12000 | Conductor | Overhead | Yes | 2017-05-05 15:52 | 15:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-05-06 02:26 | 1:56 | 37.33 | -120.833 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103834182 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-05-06 02:26 | 1:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-05-06 11:23 | 11:18 | 40.7951 | -124.029 | Vegetation | Rural | < 3 Meters | Fire Agency | chief rick harden 7074423352 | 103661154 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-05-06 11:23 | 11:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-05-06 13:07 | 12:43 | 40.7623 | -124.162 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100998152 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-05-06 13:07 | 12:43 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-05-06 15:37 | 15:00 | 39.2458 | -123.7785 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102185559 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-05-06 15:37 | 15:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-05-06 16:04 | 23:46 | 36.1654 | -120.3737 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 100741510 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-05-06 16:04 | 23:46 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-05-09 11:18 | 11:15 | 40.0597 | -122.1889 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101531151 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-05-09 11:18 | 11:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-05-09 15:58 | 15:57 | 39.5465 | -121.8567 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100404826 | Unknown | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown
PG&E | 2017-05-09 18:41 | 18:26 | 40.8689 | -123.5156 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | todd wright fire chief. 5307392493 | 103796045 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-05-09 18:41 | 18:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-05-12 | 15:16 | 38.8507 | -121.3168 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102347828 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-05-12 | 15:16 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused
PG&E | 2017-05-13 | 21:49 | 39.6784 | -121.778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 100355502 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-05-13 | 21:49 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown
PG&E | 2017-05-14 | 11:59 | 38.0798 | -122.8665 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102247059 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-05-14 | 11:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-05-14 | 16:09 | 35.6017 | -119.6566 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | 661-391-7000 | 100131572 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-05-14 | 16:09 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-05-15 | 3:05 | 35.6261 | -120.8962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101873299 | Unknown | 21000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-05-15 13:05 | 13:05 | 38.1969 | -121.4095 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102071491 | Unknown | 12000 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-05-15 16:14 | 16:00 | 37.1766 | -119.8189 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SHAUN FAIRBANKS 559-683-4823 | 101108423 | SIERRA | 21000 | Conductor | Overhead | Yes | 2017-05-15 16:14 | 16:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-05-15 21:06 | 20:57 | 38.6725 | -122.0456 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101589358 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-05-15 21:06 | 20:57 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown
PG&E | 2017-05-16 17:27 | 17:21 | 35.3759 | -119.1441 | Vegetation | Urban | < 0.25 Acres | Fire Agency | 324-6551 | 103264300 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-05-16 17:27 | 17:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-05-17 | 14:49 | 37.225 | -120.4833 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101154662 | Unknown | 12000 | Transformer | Overhead | Yes | 2017-05-17 | 14:49 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown | Transformer fuse
PG&E | 2017-05-17 | 15:13 | 36.2486 | -121.0383 | Other | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101764465 | None | 12000 | Conductor | Overhead | Yes | 2017-05-17 | 15:13 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-05-19 | 9:37 | 40.0334 | -122.0989 | Vegetation | Rural | < 0.25 Acres | Fire Agency | INCIDENT NUMBER 004751 | 101534483 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-05-19 | 9:37 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown | secondary riser
PG&E | 2017-05-19 | 10:52 | 37.2086 | -121.0968 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 044/004 | Unknown | 115000 | Conductor | Overhead | Yes | 2017-05-19 | 10:52 | Contamination | N.A. | N.A. | N.A. | Unknown
PG&E | 2017-05-20 | 12:20 | 36.6528 | -119.8012 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100649202 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-05-20 | 12:20 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown | secondary riser
PG&E | 2017-05-21 | 11:36 | 39.4277 | -121.698 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100379216 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-05-21 | 11:36 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-05-21 | 22:47 | 38.0645 | -122.5698 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 102238142 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 2017-05-21 | 22:47 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-05-22 | 5:39 | 36.3753 | -121.048 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101770874 | Unknown | 21000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown
PG&E | 2017-05-22 | 17:52 | 37.7545 | -121.4193 | Vegetation | Urban | < 0.25 Acres | Fire Agency | TRACY | 102119359 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-05-22 | 17:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-05-24 16:25 | 16:24 | 38.834 | -121.1197 | Vegetation | Rural | < 3 Meters | Fire Agency | Fire Capt | 103838109 | None | 12000 | Conductor | Overhead | Yes | 2017-05-24 16:25 | 16:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-05-25 11:21 | 11:09 | 37.4526 | -121.889 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | ERIC EMMANUELE OFFICE (408)586-3365 DIRECT (408)586-3383 | 100557380 | Unknown | 12000 | Transformer | Overhead | Yes | 2017-05-25 11:21 | 11:09 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-05-25 15:05 | 15:05 | 36.5217 | -121.8473 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Buddy Bloxham 831-236-5659 | 101778611 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-05-25 15:05 | 15:05 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-05-25 17:36 | 16:55 | 38.3986 | -122.9876 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 101974034 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-05-25 17:36 | 16:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-05-29 18:30 | 18:29 | 39.2245 | -121.3753 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101304842 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-05-30 | 11:40 | 36.8005 | -121.7702 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101707398 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-05-30 | 11:40 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-05-31 02:15 | 2:06 | 38.754 | -121.2238 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Placer Co. fire | 100063341 | ROSEVILLE | 12000 | Conductor | Overhead | Yes | 2017-05-31 02:15 | 2:06 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused
PG&E | 2017-05-31 05:52 | 5:24 | 37.0275 | -120.0707 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101113852 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-05-31 05:52 | 5:24 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-06-01 09:13 | 9:11 | 40.183 | -122.2665 | Vegetation | Rural | < 0.25 Acres | Fire Agency | MARK FRITZ | 101546068 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-01 09:13 | 9:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-01 21:50 | 21:35 | 41.0557 | -121.3869 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101550337 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 2017-06-01 21:50 | 21:35 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-06-01 22:24 | 22:14 | 36.6539 | -121.6292 | Vegetation | Rural | < 3 Meters | Fire Agency | Salinas FD | 101732390 | Unknown | 12000 | Lightning Arrestor | Overhead | Yes | 2017-06-01 22:24 | 22:14 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown
PG&E | 2017-06-03 13:35 | 13:26 | 38.9017 | -121.2056 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100043664 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-06-03 13:35 | 13:26 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-06-03 20:52 | 20:52 | 36.8323 | -119.6333 | Vegetation | Rural | < 3 Meters | Fire Agency | CLOVIS F.D. CHIEF | 100768082 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-03 20:52 | 20:52 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-04 00:08 | 00:08 | 36.982 | -120.0347 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Mike Gomez 559 906-1621 Incident #17cammu011185 | 103837406 | None | 12000 | Conductor | Overhead | Yes | 2017-06-04 00:08 | 00:08 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused
PG&E | 2017-06-04 13:13 | 13:12 | 36.7459 | -120.0602 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100645872 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-04 13:13 | 13:12 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-05 07:05 | 0:52 | 38.2342 | -121.2131 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 102083982 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 2017-06-05 07:05 | 0:52 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-06-05 08:01 | 7:56 | 37.8568 | -120.8815 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 209 5523911 | 102333651 | None | 17000 | Conductor | Overhead | Yes | 2017-06-05 08:01 | 7:56 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-05 17:15 | 17:12 | 36.9424 | -121.4612 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Leo Alvarez 831-6364324 | 101717332 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-06-05 17:15 | 17:12 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-06-06 09:21 | 9:15 | 36.4543 | -119.1338 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TIM ROGERS, 559-358-7120 | 102306658 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-06 09:21 | 9:15 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-06-06 09:49 | 09:48 | 36.9986 | -120.9369 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 101199765 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-06 09:49 | 09:48 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-06 13:39 | 13:39 | 38.1711 | -121.6782 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101666656 | FRONTIER COMMUNICATI | 21000 | Fuse | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-07 | 13:25 | 35.094 | -119.4161 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100192567 | Unknown | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-07 10:39 | 10:13 | 39.5603 | -122.1077 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 103838281 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-07 10:39 | 10:13 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-06-08 | 5:33 | 36.2388 | -120.3016 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100743822 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-08 | 5:33 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-08 00:40 | 0:26 | 37.1276 | -120.0193 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Jeff Mc Carroll (559) 806 - 8815 | 103205823 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-08 00:40 | 0:26 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused
PG&E | 2017-06-08 15:19 | 15:08 | 34.6058 | -120.0214 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SHAWN STEINER | 101947678 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-08 15:19 | 15:08 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-06-09 10:41 | 10:40 | 36.6956 | -119.7186 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FRESNO COUNTY | 100793555 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-09 10:41 | 10:40 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-06-09 13:30 | 13:27 | 36.7382 | -119.8204 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FFD INC # 703 4018 | 100895732 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-09 13:30 | 13:27 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-09 17:20 | 17:20 | 35.7974 | -120.5389 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 103406061 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-09 17:20 | 17:20 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-06-10 07:38 | 07:37 | 35.4359 | -120.4957 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101890429 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-06-10 07:38 | 07:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-12 15:28 | 15:28 | 36.9672 | -120.0931 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101136946 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-12 15:28 | 15:28 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused
PG&E | 2017-06-12 18:04 | 18:04 | 35.3638 | -118.8256 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 103371824 | Unknown | 12000 | Transformer | Overhead | Yes | 2017-06-12 18:04 | 18:04 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's nest
PG&E | 2017-06-13 | 14:30 | 37.8526 | -122.1853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Tower 005/035c | Unknown | 115000 | Conductor | Overhead | Yes | 2017-06-13 | 14:30 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused
PG&E | 2017-06-14 22:23 | 22:23 | 39.7559 | -121.5934 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100324481 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 2017-06-14 22:23 | 22:23 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown
PG&E | 2017-06-15 04:31 | 2:58 | 40.299 | -122.4318 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101511631 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-06-15 04:31 | 2:58 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft
PG&E | 2017-06-15 05:57 | 5:02 | 36.8261 | -121.6746 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101712958 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-06-15 05:57 | 5:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-15 08:08 | 7:39 | 39.2276 | -121.2348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE CHIEF | 103676075 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-06-15 08:08 | 7:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-15 15:04 | 15:01 | 39.3913 | -123.3054 | Vegetation | Rural | < 0.25 Acres | Fire Agency | STEPHEN | 103838176 | YES | 12000 | Conductor | Overhead | Yes | 2017-06-15 15:04 | 15:01 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-06-15 16:22 | 16:21 | 38.7088 | -122.9016 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101957366 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-06-15 16:22 | 16:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-15 17:30 | 17:18 | 38.797 | -121.2069 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Cal Fire | 100058437 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-06-15 17:30 | 17:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-16 14:04 | 13:50 | 35.4505 | -120.6169 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101889864 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-06-16 14:04 | 13:50 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-16 14:23 | 14:22 | 36.845 | -120.0192 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 101212782 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-06-16 14:23 | 14:22 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-16 16:37 | 16:17 | 39.2226 | -121.0041 | Vegetation | Rural | < 3 Meters | Fire Agency | GVFIRE | 100036908 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-16 16:37 | 16:17 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused
PG&E | 2017-06-16 18:06 | 17:59 | 37.3094 | -122.0472 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100555441 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-06-16 18:06 | 17:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-16 19:15 | 19:14 | 38.3443 | -122.7812 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101970801 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-06-16 19:15 | 19:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-16 22:30 | 22:30 | 38.0373 | -122.1847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101424286 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-06-16 22:30 | 22:30 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown
PG&E | 2017-06-17 02:53 | 02:53 | 37.3357 | -120.583 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101147424 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-17 02:53 | 02:53 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-06-17 15:57 | 15:49 | 36.939 | -119.6846 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 103406061 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-06-17 15:57 | 15:49 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-18 | 23:49 | 39.1949 | -122.9632 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102160857 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-18 | 23:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-18 12:22 | 12:22 | 36.7258 | -119.7907 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100894729 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-06-18 12:22 | 12:22 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-18 13:10 | 13:10 | 38.237 | -122.6702 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 102007208 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-06-18 13:10 | 13:10 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown
PG&E | 2017-06-18 18:09 | 18:09 | 37.5517 | -122.2925 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100309893 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-06-18 18:09 | 18:09 | Equipment/ Facility Failure | Guy/Span Wire | N.A. | N.A. | Unknown
PG&E | 2017-06-18 20:16 | 20:16 | 38.8884 | -122.0204 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101650987 | None | 12000 | Lightning Arrestor | Overhead | Yes | 2017-06-18 20:16 | 20:16 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown
PG&E | 2017-06-18 21:39 | 21:07 | 37.8397 | -121.2864 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102085809 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-18 21:39 | 21:07 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-06-18 22:12 | 22:12 | 38.539 | -122.792 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 102029435 | Unknown | 12000 | Other | Overhead | Yes | 2017-06-18 22:12 | 22:12 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown
PG&E | 2017-06-18 23:13 | 23:12 | 36.7575 | -119.6646 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100780126 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-06-18 23:31 | 23:31 | 38.8973 | -121.2947 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 103782395 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-18 23:31 | 23:31 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-06-19 01:23 | 01:23 | 35.3676 | -118.9552 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100252360 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 2017-06-19 01:23 | 01:23 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-06-19 13:52 | 13:51 | 39.9063 | -122.1766 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 103841797 | YES | 12000 | Conductor | Overhead | Yes | 2017-06-19 13:52 | 13:51 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused
PG&E | 2017-06-19 16:19 | 16:18 | 37.7927 | -121.2306 | Other | Urban | Structure Only | Utility: PG&E | N.A. | 103582825 | Unknown | 17000 | Transformer | Subsurface | Yes | 2017-06-19 16:19 | 16:18 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-06-19 16:27 | 16:26 | 37.9378 | -120.609 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101282825 | Unknown | 17000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Recloser | N.A. | N.A. | Unknown
PG&E | 2017-06-19 18:17 | 17:31 | 36.7627 | -120.3758 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 101094343 | Unknown | 12000 | Transformer | Overhead | Yes | 2017-06-19 18:17 | 17:31 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-06-19 18:29 | 18:00 | 38.455 | -121.8242 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101594910 | PACIFIC BELL | 12000 | Lightning Arrestor | Overhead | Yes | 2017-06-19 18:29 | 18:00 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown
PG&E | 2017-06-19 20:22 | 20:22 | 38.1012 | -120.8697 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101233468 | Unknown | 12000 | Transformer | Overhead | Yes | 2017-06-19 20:22 | 20:22 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-06-20 00:50 | 00:49 | 39.749 | -121.8998 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 100437523 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-06-20 00:50 | 00:49 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-06-20 09:13 | 09:12 | 39.1975 | -121.495 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101306700 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-20 09:13 | 09:12 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-06-20 10:08 | 10:08 | 39.0367 | -121.0763 | Vegetation | Urban | < 3 Meters | Fire Agency | JERRY GOOD 530 268-0844 | 100023174 | None | 12000 | Conductor | Overhead | Yes | 2017-06-20 10:08 | 10:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-20 13:37 | 13:37 | 37.9247 | -122.0895 | Vegetation | Urban | < 3 Meters | Fire Agency | contra costa fire | 100476159 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | Yes | 2017-06-20 13:37 | 13:37 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown
PG&E | 2017-06-20 15:18 | 15:17 | 40.1126 | -123.7677 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 100987107 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-20 15:18 | 15:17 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-20 15:19 | 11:51 | 40.3156 | -124.0611 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101006039 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-20 15:19 | 11:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-20 18:33 | 18:32 | 37.9281 | -121.2332 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 102132644 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-20 18:33 | 18:32 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-06-20 22:18 | 20:46 | 38.9076 | -121.2603 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100085621 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-06-20 22:18 | 20:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-20 23:17 | 23:16 | 35.6375 | -120.8566 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101873622 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-20 23:17 | 23:16 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-06-21 08:41 | 08:41 | 39.17 | -122.1573 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101637081 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-21 08:41 | 08:41 | Contact From Object | N.A. | Other | Electric Facility | Human Error | helicopter
PG&E | 2017-06-21 14:23 | 14:23 | 38.9921 | -121.3536 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100027499 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 2017-06-21 14:23 | 14:23 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-22 10:07 | 9:36 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown
PG&E | 2017-06-22 11:21 | 16:30 | 39.6131 | -121.6872 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 100347529 | None | 12000 | Conductor | Overhead | Yes | 2017-06-22 11:21 | 16:30 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-22 17:54 | 18:07 | 38.7583 | -120.7176 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101401088 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-22 17:54 | 18:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused
PG&E | 2017-06-22 19:02 | 19:29 | 35.5889 | -120.6691 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101912249 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-06-22 19:02 | 19:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-06-23 13:01 | 13:00 | 39.3051 | -122.4862 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 100329817 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-06-23 13:01 | 13:00 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft
PG&E | 2017-06-23 19:20 | 20:09 | 40.3856 | -122.2841 | Vegetation | Urban | < 0.25 Acres | Fire Agency | kieth foster 530-347-4737 | 101505644 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-23 19:20 | 20:09 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster bank
PG&E | 2017-06-23 19:39 | 19:23 | 39.7829 | -121.867 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100397376 | None | 12000 | Conductor | Overhead | Yes | 2017-06-23 19:39 | 19:23 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-24 10:32 | 10:31 | 38.9438 | -121.0447 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100090318 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 2017-06-24 10:32 | 10:31 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 2017-06-24 15:06 | 14:51 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown
PG&E | 2017-06-24 22:27 | 22:27 | 38.2908 | -120.849 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CONTACT BOBBY BOWMAN | 101238865 | None | 12000 | Conductor | Overhead | Yes | 2017-06-24 22:27 | 22:27 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-25 | 18:18 | 37.3236 | -120.5591 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101159230 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-25 | 0.7625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-25 02:47 | 0:23 | 39.4043 | -123.3869 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102193088 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-06-25 02:47 | 0:23 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown
PG&E | 2017-06-25 06:15 | 6:02 | 39.0774 | -121.5294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101314125 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-25 06:15 | 6:02 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown
PG&E | 2017-06-25 15:38 | 15:37 | 34.9395 | -119.6925 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | 805-686-5074 | 100191652 | None | 12000 | Conductor | Overhead | Yes | 2017-06-25 15:38 | 15:37 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown
PG&E | 2017-06-25 22:15 | 22:14 | 39.025 | -121.5787 | Vegetation | Rural | < 3 Meters | Fire Agency | Olivehurst FD | 101314072 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-06-25 22:15 | 22:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-26 08:23 | 8:18 | 37.2733 | -120.5257 | Vegetation | Rural | < 0.25 Acres | Self Extinguished | N.A. | 103218794 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-06-26 08:23 | 8:18 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-06-26 16:37 | 14:29 | 35.9782 | -120.1169 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | HENNAGIN 559 386 555 | 103243976 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-06-26 16:37 | 14:29 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-27 09:28 | 9:23 | 37.9559 | -122.6176 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | marin county fire | 102260068 | UNFILED | 12000 | Conductor | Overhead | Yes | 2017-06-27 09:28 | 9:23 | Other | N.A. | N.A. | N.A. | Unknown
PG&E | 2017-06-27 18:25 | 17:47 | 39.5126 | -122.2033 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100341056 | None | 21000 | Conductor | Overhead | Yes | 2017-06-27 18:25 | 17:47 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-28 09:58 | 09:57 | 35.9055 | -120.8421 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 101765453 | Unknown | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown
PG&E | 2017-06-28 13:13 | 13:09 | 34.9276 | -119.6204 | Building | Rural | Structure Only | Fire Agency | (805)683-2724) | 100190548 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-06-28 13:13 | 13:09 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-06-29 18:31 | 18:31 | 38.4445 | -122.8999 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 102021185 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-06-29 18:31 | 18:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-06-29 22:11 | 21:55 | 35.9804 | -121.0956 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 103312369 | Unknown | 12000 | Transformer | Overhead | Yes | 2017-06-29 22:11 | 21:55 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-06-30 | 10:24 | 39.0262 | -121.5432 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101341770 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-06-30 | 10:24 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-06-30 01:20 | 01:20 | 39.821 | -121.5883 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103840463 | YES | 12000 | Conductor | Overhead | Yes | 2017-06-30 01:20 | 01:20 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-06-30 23:55 | 23:54 | 38.5794 | -122.8835 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 101958804 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-06-30 23:55 | 23:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-07-01 | 12:02 | 39.8209 | -121.6418 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 003/039 | Unknown | 60000 | Conductor | Overhead | Yes | 2017-07-01 | 12:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-07-01 03:55 | 3:54 | 36.9995 | -119.9765 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 2099663621 | 101015895 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-07-01 03:55 | 3:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-01 04:43 | 3:12 | 38.1952 | -122.9197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103855493 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-01 04:43 | 3:12 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown
PG&E | 2017-07-01 10:44 | 10:41 | 39.2779 | -121.6875 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101294919 | Unknown | 12000 | Other | Overhead | Yes | 2017-07-01 10:44 | 10:41 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-07-02 | 13:28 | 39.8605 | -121.6274 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 000/017c | Unknown | 60000 | Conductor | Overhead | Yes | 2017-07-02 | 13:28 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-07-02 03:55 | 3:49 | 36.9588 | -120.8927 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101205043 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-02 03:55 | 3:49 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | Third-party caused
PG&E | 2017-07-03 20:28 | 20:26 | 38.7923 | -120.9438 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101388730 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 2017-07-03 20:28 | 20:26 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-07-04 13:59 | 13:56 | 40.383 | -122.315 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101506140 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-07-04 13:59 | 13:56 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-07-04 16:25 | 16:16 | 38.8763 | -121.1318 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100050181 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-07-04 16:25 | 16:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-04 20:17 | 20:16 | 40.4228 | -122.3975 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SCOTT CORN 530-448-2414 | 101481860 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-07-04 20:17 | 20:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-07-05 03:50 | 3:25 | 38.6845 | -121.0118 | Vegetation | Urban | < 0.25 Acres | Fire Agency | JUSTIN RHAMES | 101380157 | PACIFIC BELL | 21000 | Fuse | Overhead | Yes | 2017-07-05 03:50 | 3:25 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-07-05 12:11 | 11:58 | 39.2105 | -121.2266 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVE ROBERTSON 530 906 4892 | 100010286 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-07-05 12:11 | 11:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-05 20:56 | 20:54 | 35.6847 | -120.11 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 661-324-6551 LOG325962 | 100171224 | Unknown | 21000 | Capacitor Bank | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-07-06 | 15:18 | 36.7402 | -119.7613 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 100864107 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-07-06 | 15:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused
PG&E | 2017-07-06 14:04 | 14:02 | 39.3009 | -122.5173 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100414219 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-06 14:04 | 14:02 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | Third-party caused
PG&E | 2017-07-06 20:07 | 20:07 | 39.5987 | -121.9099 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100436921 | None | 12000 | Conductor | Overhead | Yes | 2017-07-06 20:07 | 20:07 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-07-06 23:33 | 23:30 | 35.5562 | -120.7552 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101934472 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-07-06 23:33 | 23:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-07 | 15:09 | 40.9054 | -122.3806 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101455950 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-07 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-07 20:49 | 14:31 | 37.499 | -119.799 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVEN WARD OFFICE 209-966-3542 CELL559-706-8811 | 103855637 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-07-07 20:49 | 14:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor
PG&E | 2017-07-08 04:06 | 4:03 | 38.5535 | -121.5368 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101584938 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-07-08 04:06 | 4:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-08 16:02 | 15:59 | 37.2822 | -122.0189 | Other | Urban | < 0.25 Acres | Fire Agency | Unknown | 100540958 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-07-08 16:02 | 15:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-08 18:23 | 18:16 | 35.4653 | -120.6713 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 103392970 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-07-08 18:23 | 18:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-08 19:23 | 18:49 | 40.2935 | -122.4089 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | TOM STROING, RED BLUFF | 101526269 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-07-08 19:23 | 18:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-09 07:22 | 7:07 | 36.5092 | -121.4465 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103011964 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-09 07:22 | 7:07 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-07-09 11:06 | 11:00 | 39.4201 | -121.5439 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100394209 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-07-09 11:06 | 11:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-10 09:08 | 09:07 | 38.2074 | -121.2335 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102083900 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-07-10 09:08 | 09:07 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-07-10 12:34 | 12:32 | 40.2603 | -123.8253 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103139646 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-10 12:34 | 12:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-10 16:41 | 16:39 | 36.962 | -120.8584 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | EFRAIN CHAVARRIA | 101203174 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-10 16:41 | 16:39 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-07-10 18:00 | 17:00 | 37.3768 | -122.3597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | David Hibdon 831-254-1763 | 100270370 | Unknown | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-11 08:14 | 8:11 | 38.1337 | -121.1054 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102072316 | None | 21000 | Other | Overhead | Yes | 2017-07-11 08:14 | 8:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-07-11 11:53 | 11:53 | 38.0338 | -121.3224 | Vegetation | Urban | < 0.25 Acres | Utility: PG&E | N.A. | 102118581 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-07-11 11:53 | 11:53 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown
PG&E | 2017-07-11 13:56 | 13:56 | 39.4506 | -121.7153 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chip fowler | 100423597 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-07-11 13:56 | 13:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-11 22:13 | 22:12 | 37.0122 | -121.9497 | Vegetation | Rural | < 3 Meters | Fire Agency | CAPT PHIL CRAMBLET 831-479-6842 | 101676689 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 2017-07-11 22:13 | 22:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-12 | 16:04 | 40.6531 | -122.3343 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 000/001 | Unknown | 60000 | Conductor | Overhead | Yes | 2017-07-12 | 16:04 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-07-12 05:52 | 05:51 | 38.3932 | -121.8044 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101584920 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-12 05:52 | 05:51 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-07-12 10:49 | 10:48 | 36.9625 | -120.0463 | Other | Urban | < 0.25 Acres | Fire Agency | Barbera Riley 661-5499 ext. 2 | 103222654 | None | 0 – 750 | Conductor | Overhead | Yes | 2017-07-12 10:49 | 10:48 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-07-12 15:09 | 15:09 | 37.1491 | -122.0037 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 103565794 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-07-12 15:09 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-12 20:22 | 20:21 | 40.0808 | -123.8339 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103841917 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-12 20:22 | 20:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-13 | 5:13 | 38.1201 | -122.1858 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Tower 025/173 | Unknown | 115000 | Conductor | Overhead | Yes | 2017-07-13 | 5:13 | Contact From Object | N.A. | Other | Electric Facility | Other | bird material
PG&E | 2017-07-13 07:44 | 07:43 | 39.4064 | -122.1263 | Vegetation | Rural | < 3 Meters | Fire Agency | AXS-N/A FIRE NEAR POLE PER FD. NO STDBY. WANT CHECK OF POLE 530-458-0200 | 100406386 | None | 0 – 750 | Conductor | Overhead | Yes | 2017-07-13 07:44 | 07:43 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-07-13 19:30 | 19:29 | 36.8504 | -119.55 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | chis waters bat.chief 559-281-4308 | 100728986 | Unknown | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-07-14 17:55 | 17:54 | 37.7095 | -121.2921 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TRACY | 102070196 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-14 17:55 | 17:54 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-07-15 14:35 | 14:34 | 39.6231 | -121.5328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | russ fowler | 100404385 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-15 14:35 | 14:34 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-15 14:57 | 14:56 | 37.3074 | -122.0355 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100538519 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-07-15 14:57 | 14:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-15 20:17 | 20:16 | 39.459 | -121.5313 | Vegetation | Rural | < 3 Meters | Fire Agency | oroville station | 100429093 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-15 20:17 | 20:16 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-07-15 21:01 | 21:01 | 38.2128 | -121.834 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101658237 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-07-15 21:01 | 21:01 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown
PG&E | 2017-07-16 10:40 | 10:39 | 40.3414 | -123.8786 | Vegetation | Rural | < 3 Meters | Fire Agency | 707-726-1280 | 100990019 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-16 10:40 | 10:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-16 11:59 | 11:59 | 36.6669 | -121.7515 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101761892 | None | 21000 | Fuse | Overhead | Yes | 2017-07-16 11:59 | 11:59 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown
PG&E | 2017-07-16 12:10 | 12:10 | 35.6613 | -120.922 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101942626 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-07-16 12:10 | 12:10 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-07-16 17:07 | 17:07 | 37.3441 | -122.0363 | Vegetation | Urban | < 3 Meters | Fire Agency | sunnyvale fire | 100532224 | PACIFIC BELL | 0 – 750 | Transformer | Overhead | Yes | 2017-07-16 17:07 | 17:07 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-07-17 07:40 | 07:39 | 40.1653 | -122.2228 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101543808 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-07-17 07:40 | 07:39 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-07-17 10:01 | 10:00 | 35.956 | -120.8515 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101765495 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-17 10:01 | 10:00 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown
PG&E | 2017-07-17 18:59 | 18:58 | 38.8885 | -121.9898 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Dunnigan Fire Dept | 101602915 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-07-17 18:59 | 18:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-18 | 11:30 | 38.0484 | -120.5565 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 012/071 | Unknown | 115000 | Conductor | Overhead | Yes | 2017-07-18 | 11:30 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-07-18 | 21:40 | 38.0031 | -122.2093 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | Pole 000/002 to 000/003 | Unknown | 60000 | Conductor | Overhead | Yes | 2017-07-18 | 21:40 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-07-18 07:39 | 07:39 | 38.0704 | -120.5452 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101269434 | Unknown | 0 – 750 | Other | Overhead | Yes | 2017-07-18 07:39 | 07:39 | Other | N.A. | N.A. | N.A. | Unknown
PG&E | 2017-07-18 11:46 | 11:45 | 36.8308 | -119.8623 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100624764 | PACIFIC BELL | 21000 | Capacitor Bank | Overhead | Yes | 2017-07-18 11:46 | 11:45 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown
PG&E | 2017-07-19 | 5:52 | 37.0905 | -119.6047 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Tower 003/001 | Unknown | 115000 | Conductor | Overhead | Yes | 2017-07-19 | 5:52 | Contact From Object | N.A. | Other | Electric Facility | Unknown
PG&E | 2017-07-19 09:33 | 09:33 | 35.3446 | -118.8609 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 100159158 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 2017-07-19 09:33 | 09:33 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown
PG&E | 2017-07-19 17:20 | 17:19 | 39.4124 | -123.8123 | Vegetation | Rural | < 0.25 Acres | Fire Agency | DRUE RHOADS 707 964 5673 | 102201550 | YES | 12000 | Conductor | Overhead | Yes | 2017-07-19 17:20 | 17:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-20 | 20:57 | 37.7361 | -122.4921 | Building | Urban | Structure Only | Unknown | N.A. | 101813719 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-07-20 | 20:57 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown
PG&E | 2017-07-20 01:47 | 01:46 | 36.5254 | -119.682 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100830639 | Unknown | 0 – 750 | Lightning Arrestor | Overhead | Yes | 2017-07-20 01:47 | 01:46 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown
PG&E | 2017-07-20 04:27 | 04:27 | 38.0642 | -120.8711 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | chris costales 209 754 2735 | 102142834 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-20 04:27 | 04:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-07-20 13:46 | 13:45 | 35.0804 | -120.5538 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | PAUL LEE 805 903-3416 INC # 8291 | 101941116 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-20 13:46 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown
PG&E | 2017-07-20 17:01 | 17:00 | 37.9265 | -121.232 | Vegetation | Urban | < 3 Meters | Customer | N.A. | 103384380 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | Yes | 2017-07-20 17:01 | 17:00 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown
PG&E | 2017-07-21 | 13:27 | 38.2685 | -120.9372 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101245524 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-21 | 13:27 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-07-21 | 20:26 | 41.0655 | -121.3932 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101549629 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-21 | 20:26 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-07-22 12:26 | 12:25 | 40.8795 | -123.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Josh , comander chief of forest service. | 100980577 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-22 12:26 | 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused
PG&E | 2017-07-22 14:38 | 14:38 | 37.2994 | -122.1631 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100265488 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-22 14:38 | 14:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-22 16:02 | 16:01 | 40.8314 | -124.0539 | Vegetation | Rural | < 0.25 Acres | Fire Agency | BATTALION CHIEF CURT WATKINS, 707-825.2000 | 100983827 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-07-22 16:02 | 16:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused
PG&E | 2017-07-23 09:22 | 09:22 | 40.642 | -122.2302 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT? | 101459708 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 2017-07-23 09:22 | 09:22 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-07-23 16:33 | 16:32 | 36.2405 | -119.8128 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Brandon Jones (559) 852-2884 | 100783832 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-23 16:33 | 16:32 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-07-23 18:25 | 18:25 | 39.6723 | -123.5336 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103823226 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-23 18:25 | 18:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-23 19:42 | 19:41 | 36.2171 | -119.9097 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Brandon Jones (559) 852-2884 | 103846605 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-23 19:42 | 19:41 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-07-24 14:02 | 14:01 | 37.2635 | -122.3364 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike klink 650-879-0121 | 100322130 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-07-24 14:02 | 14:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-07-24 16:07 | 16:07 | 37.2537 | -121.9676 | Vegetation | Urban | < 0.25 Acres | Fire Agency | C1702050039 | 103447162 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-07-24 16:07 | 16:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-24 19:31 | 19:31 | 38.3519 | -120.7103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-24 19:31 | 19:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-24 21:45 | 21:45 | 35.6024 | -120.9211 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101860186 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-24 21:45 | 21:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-25 15:52 | 15:51 | 38.3779 | -122.5388 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102031447 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-25 15:52 | 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-25 19:13 | 19:12 | 39.5997 | -121.4449 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100403612 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-25 19:13 | 19:12 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-07-26 06:55 | 06:55 | 36.7812 | -119.7553 | Vegetation | Urban | < 3 Meters | Fire Agency | FRESNO FIRE, BATALION 1, FULMER 559 993 2661 | 100866522 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-07-26 06:55 | 06:55 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-07-28 | 14:02 | 40.9997 | -121.9579 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101512624 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-28 | 14:02 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-07-28 16:57 | 16:57 | 35.4727 | -120.9908 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | TOM MCEWEN 805-903-3409 | 101933868 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-28 16:57 | 16:57 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-07-28 19:21 | 19:20 | 35.7276 | -120.9903 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Luis Obispo CDF | 101945496 | None | 21000 | Conductor | Overhead | Yes | 2017-07-28 19:21 | 19:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-29 13:19 | 13:18 | 39.4631 | -121.4595 | Vegetation | Rural | < 0.25 Acres | Fire Agency | russ fowler 530 521 8056 | 103846763 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-29 13:19 | 13:18 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-07-29 13:28 | 13:28 | 35.4523 | -120.3834 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101889516 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-07-29 13:28 | 13:28 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-07-29 14:52 | 14:52 | 37.06 | -122.0011 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Scotts Valley Fire Dept. | 101679068 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 2017-07-29 14:52 | 14:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-07-29 17:57 | 17:56 | 37.0251 | -121.5358 | Vegetation | Rural | < 3 Meters | Fire Agency | GEORGE MARSHALL | 100610842 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-07-29 17:57 | 17:56 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-07-29 18:09 | 18:08 | 37.9487 | -121.3457 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 102126507 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-29 18:09 | 18:08 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-07-29 20:46 | 20:45 | 35.4517 | -120.6171 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101941008 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-07-29 20:46 | 20:45 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | Third-party caused
PG&E | 2017-07-30 09:47 | 09:46 | 38.9132 | -122.6179 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike wink | 102151066 | None | 0 – 750 | Conductor | Overhead | Yes | 2017-07-30 09:47 | 09:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-07-31 12:58 | 12:58 | 37.0971 | -122.2797 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101679025 | Unknown | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-07-31 14:11 | 14:10 | 35.9787 | -120.111 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 100695130 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-07-31 14:11 | 14:10 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-07-31 14:42 | 14:41 | 38.7967 | -121.1329 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103782414 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-07-31 14:42 | 14:41 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-01 12:23 | 12:23 | 36.0412 | -119.5053 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100661556 | Unknown | 0 – 750 | Other | Overhead | Yes | 2017-08-01 12:23 | 12:23 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown
PG&E | 2017-08-02 | 9:42 | 39.2274 | -123.1081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 5/0 | None | 60000 | Conductor | Overhead | Yes | 2017-08-02 | 9:42 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-08-02 06:01 | 5:54 | 40.7986 | -123.3961 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 100974913 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-02 06:01 | 5:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-02 09:06 | 8:58 | 37.5618 | -121.9486 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FREMONT FIRE DEPT. 911 | 100940374 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 2017-08-02 09:06 | 8:58 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown
PG&E | 2017-08-02 17:09 | 17:04 | 37.3163 | -122.0723 | Vegetation | Urban | < 0.25 Acres | Fire Agency | TONY RAINIERI 408-378-4010 | 100534186 | Unknown | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-08-02 18:20 | 18:16 | 37.393 | -120.6213 | Vegetation | Urban | < 3 Meters | Fire Agency | 2099663621 | 101190510 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 2017-08-02 18:20 | 18:16 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-08-03 11:01 | 10:53 | 39.0732 | -121.0868 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100072742 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-08-03 11:01 | 10:53 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-08-03 11:28 | 11:16 | 38.1192 | -122.5015 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SSR172150008 | 102227219 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-03 11:28 | 11:16 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-08-03 22:45 | 22:44 | 39.0711 | -121.487 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | ART PAQUETTE 530-633-0861 | 101335644 | PACIFIC BELL | 12000 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown
PG&E | 2017-08-04 09:54 | 09:54 | 38.6039 | -121.0592 | Vegetation | Rural | < 3 Meters | Fire Agency | D. Franks 530-622-3858, Incident #022602 | 101411052 | PACIFIC BELL | 21000 | Capacitor Bank | Overhead | Yes | 2017-08-04 09:54 | 09:54 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown
PG&E | 2017-08-04 18:21 | 18:14 | 35.6193 | -120.6589 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101912293 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 2017-08-04 18:21 | 18:14 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown
PG&E | 2017-08-05 08:33 | 08:33 | 38.4583 | -120.8695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JEFF MICHEL- 530 409 2223 | 101236223 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-08-05 08:33 | 08:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-08-05 18:13 | 18:08 | 39.0968 | -123.2147 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102196629 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-05 18:13 | 18:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-05 18:21 | 18:09 | 36.9675 | -120.0899 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | 911 | 101136476 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-05 18:21 | 18:09 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-08-05 19:43 | 19:21 | 36.7691 | -119.6101 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100725102 | Unknown | 12000 | Other | Overhead | Yes | 2017-08-05 19:43 | 19:21 | Equipment/ Facility Failure | Recloser | N.A. | N.A. | Unknown
PG&E | 2017-08-06 11:38 | 11:38 | 36.5857 | -121.7121 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101747125 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-06 11:38 | 11:38 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-08-06 19:23 | 18:21 | 40.6012 | -122.2346 | Vegetation | Rural | < 3 Meters | Fire Agency | 17CASH4007992 | 101470083 | Unknown | 12000 | Other | Overhead | Yes | 2017-08-06 19:23 | 18:21 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike
PG&E | 2017-08-08 | 13:46 | 38.4366 | -122.726 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | Tower 005/090 | None | 115000 | Conductor | Overhead | Yes | 2017-08-08 | 13:46 | Contact From Object | N.A. | Other | Electric Facility | Human Error
PG&E | 2017-08-08 00:42 | 0:36 | 35.4269 | -119.0572 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 100167715 | PACIFIC BELL | 12000 | Unknown | Subsurface | Yes | 2017-08-08 00:42 | 0:36 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-08-08 04:23 | 4:10 | 38.4949 | -122.6685 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 102025742 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 2017-08-08 04:23 | 4:10 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-08-08 11:28 | 11:27 | 37.0445 | -121.6343 | Vegetation | Urban | < 3 Meters | Utility: PG&E | N.A. | 100613200 | VERIZON CALIFORNIA | 21000 | Capacitor Bank | Overhead | Yes | 2017-08-08 11:28 | 11:27 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown
PG&E | 2017-08-08 20:35 | 20:35 | 37.2637 | -119.7103 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TROY CHEEK1-209-966-3621 | 103793352 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-08-08 20:35 | 20:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-09 11:29 | 11:29 | 38.6532 | -120.6273 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101402496 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 2017-08-09 11:29 | 11:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-08-11 07:56 | 07:55 | 38.2649 | -120.9748 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101253880 | None | 12000 | Conductor | Overhead | Yes | 2017-08-11 07:56 | 07:55 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-08-12 09:09 | 09:08 | 34.6689 | -120.0286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103391912 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-12 09:09 | 09:08 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | wire cut
PG&E | 2017-08-13 13:11 | 13:11 | 38.5094 | -122.77 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 101961046 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-08-13 13:11 | 13:11 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-08-14 | 6:14 | 40.1164 | -123.8064 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100986364 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-14 | 6:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-14 | 23:52 | 37.1272 | -122.1689 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 015/127 | None | 60000 | Conductor | Overhead | Yes | 2017-08-14 | 23:52 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-08-14 07:56 | 07:56 | 39.1794 | -120.9761 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100083743 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-08-14 07:56 | 07:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-08-15 19:29 | 19:28 | 39.5037 | -121.2783 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 100396172 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-08-15 19:29 | 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-16 | 20:24 | 35.7813 | -119.9153 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Span 0/6 to 0/7 | None | 70000 | Conductor | Overhead | Yes | 2017-08-16 | 20:24 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-08-17 | 2:33 | 39.1934 | -121.4227 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 101304315 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-17 | 2:33 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | pole cut down
PG&E | 2017-08-17 | 15:15 | 39.3703 | -121.0484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PHIL MICHAEL 265-2894 INCIENT # CA NEV 21642 | 100083029 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-08-17 | 15:15 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-08-18 | 17:09 | 37.0921 | -121.6691 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100608897 | VERIZON CALIFORNIA | 21000 | Conductor | Overhead | Yes | 2017-08-18 | 17:09 | Other | N.A. | N.A. | N.A. | Human Error | CIP contractor
PG&E | 2017-08-19 | 11:31 | 37.6891 | -121.2506 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102053834 | Unknown | 17000 | Conductor | Overhead | Yes | 2017-08-19 | 11:31 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-08-19 | 21:16 | 40.5752 | -122.2985 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464623 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-08-19 | 21:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-20 | 11:38 | 39.2764 | -122.1407 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101634861 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-20 | 11:38 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-08-21 | 15:07 | 38.608 | -122.3531 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Aaron Latta 707 339 2918 | 102254922 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-08-21 | 15:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-21 | 19:31 | 39.7258 | -121.8205 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100341323 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-08-21 | 19:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-22 | 14:17 | 38.4902 | -122.8918 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 102001687 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-08-22 | 14:17 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-08-24 | 6:32 | 36.5905 | -119.5929 | Vegetation | Rural | < 3 Meters | Fire Agency | ca fku 012333 | 100897456 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-24 | 6:32 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-08-25 | 9:47 | 39.0251 | -121.5775 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101314075 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-08-25 | 9:47 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-26 | 7:10 | 38.8252 | -121.3953 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100101888 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-08-26 | 7:10 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | Third-party caused
PG&E | 2017-08-26 | 20:39 | 38.4707 | -122.6472 | Vegetation | Urban | < 3 Meters | Fire Agency | Santa Rosa Fire Dept | 101966474 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-08-26 | 20:39 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-08-26 | 20:53 | 38.7066 | -121.0193 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101382231 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-08-26 | 20:53 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-08-27 | 18:11 | 37.9916 | -121.3479 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Unknown | 103193823 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-08-27 | 18:11 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-08-27 | 20:04 | 38.9165 | -121.151 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-477-0641 x7, log 22629 | 100077184 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-08-27 | 20:04 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-27 | 22:16 | 37.3585 | -120.8503 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CHRIS ALLEN 209-634-7086 | 103346364 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-27 | 22:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-28 | 6:32 | 35.4218 | -119.0304 | Vegetation | Urban | < 0.25 Acres | Fire Agency | BCFD/KCFD 661-324-6551 | 103139674 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-08-28 | 6:32 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-08-28 | 8:36 | 35.7245 | -119.5341 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100171751 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-28 | 8:36 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-08-28 | 9:14 | 38.7443 | -122.6491 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 103781085 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-08-28 | 9:14 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-08-28 | 10:07 | 39.0472 | -120.7859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FORESTHILL | 100019525 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-28 | 10:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused
PG&E | 2017-08-28 | 13:55 | 37.6857 | -120.8067 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 102327313 | None | 0 – 750 | Conductor | Overhead | Yes | 2017-08-28 | 13:55 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-08-28 | 14:06 | 38.634 | -122.4194 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102253236 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-08-28 | 14:06 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-08-28 | 14:23 | 38.5054 | -120.7592 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101260228 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 2017-08-28 | 14:23 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown
PG&E | 2017-08-28 | 14:59 | 40.2853 | -123.8728 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 100990599 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-28 | 14:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-28 | 23:56 | 40.1197 | -123.644 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103844288 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-28 | 23:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-29 | 6:08 | 38.2365 | -122.4608 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101998998 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-29 | 6:08 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-08-29 | 10:27 | 38.3687 | -122.0012 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 101661402 | PACIFIC BELL | 12000 | Lightning Arrestor | Overhead | Yes | 2017-08-29 | 10:27 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-08-29 | 10:40 | 38.2066 | -121.1576 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102082031 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-29 | 10:40 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-08-29 | 12:49 | 37.4507 | -119.6454 | Vegetation | Rural | > 5000 Acres | Fire Agency | USFS | 101017368 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-29 | 12:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor
PG&E | 2017-08-29 | 15:54 | 38.302 | -122.5431 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 911 | 102026119 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 2017-08-29 | 15:54 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-08-30 | 16:17 | 35.3528 | -119.0538 | Vegetation | Urban | < 0.25 Acres | Fire Agency | BCFD/KCFD 661-324-6551 | 100145928 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-08-30 | 16:17 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-08-30 | 18:21 | 40.6243 | -122.3039 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CASHU008896 | 103151338 | YES | 12000 | Conductor | Overhead | Yes | 2017-08-30 | 18:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-30 | 22:37 | 38.9993 | -120.9887 | Vegetation | Rural | < 3 Meters | Fire Agency | Andy 530-889-0111 | 100026238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-08-30 | 22:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-30 | 22:39 | 38.1662 | -121.9381 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | suisun | 103850994 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-30 | 22:39 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown
PG&E | 2017-08-31 | 6:42 | 35.616 | -120.8577 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Derrick | 101860075 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-08-31 | 6:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-31 | 11:33 | 37.1379 | -121.9966 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100519201 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-08-31 | 11:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-31 | 11:51 | 38.3917 | -122.3195 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102291943 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 2017-08-31 | 11:51 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-08-31 | 21:07 | 41.0605 | -124.1038 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100977438 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-31 | 21:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-08-31 | 22:50 | 36.815 | -119.7763 | Vegetation | Urban | < 3 Meters | Customer | N.A. | 100851402 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-08-31 | 22:50 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-09-01 | 6:09 | 36.1949 | -120.7079 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101705717 | Unknown | 12000 | Fuse | Overhead | Yes | 2017-09-01 | 6:09 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown
PG&E | 2017-09-01 | 8:00 | 37.3757 | -119.8886 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101067028 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-09-01 | 8:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-01 | 12:07 | 40.5938 | -124.136 | Vegetation | Rural | < 3 Meters | Fire Agency | DISPATCH FIRE 707-725-7550 | 100993250 | PACIFIC BELL | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown
PG&E | 2017-09-01 | 12:52 | 37.1667 | -121.7069 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100601982 | VERIZON CALIFORNIA | 21000 | Conductor | Overhead | Yes | 2017-09-01 | 12:52 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown
PG&E | 2017-09-01 | 12:59 | 38.4527 | -122.7845 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102015626 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 2017-09-01 | 12:59 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-09-01 | 17:48 | 36.6518 | -121.7249 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MCFD | 103155761 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-01 | 17:48 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-09-01 | 18:42 | 38.2939 | -122.5039 | Other | Rural | < 0.25 Acres | Fire Agency | BOB NORRBOM 707 996 2102 | 101982894 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 2017-09-01 | 18:42 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown
PG&E | 2017-09-02 | 12:01 | 37.6645 | -121.9223 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 100956020 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 2017-09-02 | 12:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-02 | 16:18 | 37.269 | -121.8056 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100584311 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-09-02 | 16:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-09-02 | 18:00 | 37.9338 | -122.4069 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102347407 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-09-02 | 18:00 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-09-03 | 7:12 | 37.3743 | -122.2184 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Local | 100270106 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-03 | 7:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-03 | 12:52 | 37.2162 | -119.4807 | Vegetation | Rural | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103345573 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-09-03 | 12:52 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-03 | 17:52 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 2017-09-03 | 17:52 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike
PG&E | 2017-09-03 | 22:57 | 36.0953 | -120.517 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | CHRIS CHRISTOPHERSON 559-281-4320 | 100739435 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-09-03 | 22:57 | Contact Between Third Party Facility on Pole and Supply Lines | N.A. | N.A. | N.A. | Weather
PG&E | 2017-09-04 | 0:57 | 36.8024 | -119.8254 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100856132 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-09-04 | 0:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-04 | 3:29 | 39.8317 | -121.8444 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102300100 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-09-04 | 6:43 | 37.4546 | -121.9331 | Other | Rural | Structure Only | Customer | N.A. | 100557780 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 2017-09-04 | 6:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-09-05 | 1:24 | 39.4317 | -121.5529 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100420238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-09-05 | 1:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-05 | 6:58 | 39.6727 | -123.5128 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 102194697 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 2017-09-05 | 6:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-05 | 7:20 | 39.7109 | -121.7972 | Vegetation | Rural | < 3 Meters | Fire Agency | (530) 538-6841 | 100355255 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-05 | 7:20 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown
PG&E | 2017-09-05 | 13:51 | 38.1897 | -121.3175 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103218208 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-05 | 13:51 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-09-05 | 17:51 | 38.3407 | -122.2578 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 102284869 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-09-05 | 17:51 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-09-06 | 19:26 | 40.8392 | -122.3635 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103643183 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-06 | 19:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-06 | 20:08 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-06 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-08 | 4:47 | 38.7478 | -120.859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101391575 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-09-08 | 4:47 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-08 | 17:21 | 38.6039 | -120.9275 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101379094 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 2017-09-08 | 17:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-08 | 21:14 | 37.9604 | -120.3764 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | John Lite 209-984-5623 | 101042521 | Unknown | 17000 | Conductor | Overhead | Yes | 2017-09-08 | 21:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-09 | 18:36 | 36.6618 | -121.5477 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101769870 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-09 | 18:36 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-09-10 | 1:22 | 39.2599 | -121.4902 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | TYLER LOPEZ | 101289867 | None | 12000 | Conductor | Overhead | Yes | 2017-09-10 | 1:22 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-09-10 | 16:30 | 37.3039 | -120.5275 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Merced County FD | 101161316 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-09-10 | 16:30 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-09-11 | 7:18 | 37.0008 | -121.6667 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100621936 | VERIZON CALIFORNIA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-11 | 8:50 | 36.9515 | -121.842 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101790954 | PACIFIC BELL | 21000 | Fuse | Overhead | Yes | 2017-09-11 | 8:50 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike
PG&E | 2017-09-11 | 23:50 | 40.8672 | -124.0883 | Vegetation | Urban | < 3 Meters | Fire Agency | BOB | 100964579 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-11 | 23:50 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-09-12 | 9:24 | 39.741 | -121.6079 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 100330302 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-09-12 | 9:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-09-12 | 17:18 | 39.4511 | -121.6052 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | tom klage 530 538-7888 | 100419482 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-12 | 17:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-14 | 11:02 | 39.1111 | -121.5565 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101320308 | None | 12000 | Switch | Overhead | Yes | 2017-09-14 | 11:02 | Equipment/ Facility Failure | Switch | N.A. | N.A. | Unknown
PG&E | 2017-09-14 | 12:09 | 39.5039 | -121.5453 | Vegetation | Urban | < 0.25 Acres | Fire Agency | 530-538-2448 | 100372805 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-14 | 12:09 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-09-14 | 14:06 | 40.2942 | -123.8174 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100989497 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-14 | 14:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-15 | 14:55 | 39.7461 | -121.4885 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100335239 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-15 | 14:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-17 | 15:05 | 36.6473 | -119.3861 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 100738741 | VERIZON CALIFORNIA | 0 – 750 | Conductor | Overhead | Yes | 2017-09-17 | 15:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-17 | 17:38 | 38.9946 | -121.0261 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100029537 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-09-17 | 17:38 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-09-18 | 13:01 | 39.3889 | -121.4054 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 103795057 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-09-18 | 13:01 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-09-18 | 15:10 | 39.6013 | -122.0555 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103849874 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-18 | 15:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-18 | 18:01 | 38.2197 | -122.543 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101997149 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-18 | 18:01 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-09-18 | 19:01 | 38.0742 | -122.8286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102229215 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-09-18 | 19:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-18 | 23:50 | 37.9088 | -120.4865 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | incident comander geoff marshall 209-419-4407 | 101040882 | Unknown | 17000 | Conductor | Overhead | Yes | 2017-09-18 | 23:50 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-09-19 | 19:13 | 35.4784 | -119.2959 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100207112 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-19 | 19:13 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused
PG&E | 2017-09-20 | 2:06 | 37.2597 | -122.3222 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100322388 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-09-20 | 2:06 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-09-20 | 8:41 | 36.9404 | -120.9014 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 2/6 - Arburua Tap | None | 70000 | Conductor | Overhead | Yes | 2017-09-20 | 8:41 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's nest
PG&E | 2017-09-21 | 8:39 | 39.6147 | -121.7258 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 100347380 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-09-21 | 8:39 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-09-22 | 14:28 | 36.0961 | -120.0577 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SAME AS TAG. FD NOT STANDING BY UPON ARRIVAL | 100663084 | Unknown | 12000 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown
PG&E | 2017-09-23 | 9:16 | 37.0127 | -120.6256 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101181497 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-23 | 9:16 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown
PG&E | 2017-09-23 | 14:17 | 40.6509 | -122.2974 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DARREN STEWART 448-2421 | 101467221 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-09-23 | 14:17 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused
PG&E | 2017-09-24 | 2:13 | 38.1046 | -120.989 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 016/297 | Unknown | 60000 | Conductor | Overhead | Yes | 2017-09-24 | 2:13 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-09-24 | 7:54 | 37.4014 | -122.0274 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100515206 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-09-24 | 7:54 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-09-24 | 16:42 | 38.3869 | -122.9667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DOUG JONES | 101973946 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-09-24 | 16:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-25 | 19:49 | 36.8137 | -121.721 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | Tower 058/249 | Unknown | 230000 | Conductor | Overhead | Yes | 2017-09-25 | 19:49 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown
PG&E | 2017-09-26 | 17:44 | 38.0643 | -122.8056 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102228291 | Unknown | 12000 | Other | Overhead | Yes | 2017-09-26 | 17:44 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-09-27 | 9:11 | 39.0163 | -122.8685 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102143577 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 2017-09-27 | 9:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-09-27 | 12:12 | 39.4845 | -121.3545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | bill lopez cell 530 521-8052 | 100429924 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 2017-09-27 | 12:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-09-27 | 19:06 | 40.7592 | -123.995 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103660812 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-09-27 | 19:06 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-09-28 | 18:28 | 37.9884 | -122.097 | Vegetation | Urban | < 3 Meters | Fire Agency | (510)374-7070 | 103627505 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-09-28 | 18:28 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | Third-party caused
PG&E | 2017-09-29 | 2:01 | 39.5317 | -122.1857 | Vegetation | Urban | < 3 Meters | Unknown | N.A. | 100419384 | Unknown | 21000 | Transformer | Padmounted | Yes | 2017-09-29 | 2:01 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-09-30 | 15:08 | 37.4109 | -121.1747 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Tower 030/132 | None | 230000 | Conductor | Overhead | Yes | 2017-09-30 | 15:08 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | Third-party caused
PG&E | 2017-10-01 | 7:24 | 37.914 | -122.3771 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101437028 | Unknown | 12000 | Transformer | Overhead | Yes | 2017-10-01 | 7:24 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-10-01 | 16:11 | 39.797 | -122.1185 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103850270 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-10-01 | 16:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-10-01 | 23:51 | 40.0192 | -122.1452 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MARK FRITZ | 101534592 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-01 | 23:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-10-02 | 2:55 | 37.3314 | -120.5243 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101160137 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-02 | 2:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-10-02 | 7:07 | 38.2949 | -122.1066 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101658181 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 2017-10-02 | 7:07 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown
PG&E | 2017-10-02 | 12:22 | 39.6313 | -122.0069 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 103224422 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-02 | 12:22 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-10-02 | 14:56 | 38.9102 | -120.9185 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100110800 | None | 21000 | Other | Overhead | Yes | 2017-10-02 | 14:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-10-02 | 16:05 | 38.7182 | -120.9756 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101375963 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-10-02 | 16:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-10-02 | 17:30 | 38.3634 | -122.2846 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102282538 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-10-03 | 17:48 | 35.1084 | -119.3786 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | span 001/019 - 001/020 | Unknown | 70000 | Conductor | Overhead | Yes | 2017-10-03 | 17:48 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown
PG&E | 2017-10-04 | 12:20 | 37.8169 | -121.2715 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LATHROP | 102091094 | Unknown | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-10-04 | 23:42 | 38.6554 | -120.9934 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101375442 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 2017-10-04 | 23:42 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-10-05 | 0:20 | 38.0052 | -121.7545 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 100456226 | Unknown | 21000 | Switch | Subsurface | Yes | 2017-10-05 | 0:20 | Equipment/ Facility Failure | Switch | N.A. | N.A. | Unknown
PG&E | 2017-10-05 | 10:57 | 39.4664 | -122.167 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100343435 | PACIFIC BELL | 21000 | Other | Overhead | Yes | 2017-10-05 | 10:57 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's Nest
PG&E | 2017-10-06 | 7:24 | 38.5607 | -121.7642 | Vegetation | Urban | < 3 Meters | Fire Agency | 5307583600 | 101639481 | PACIFIC BELL | 12000 | Lightning Arrestor | Overhead | Yes | 2017-10-06 | 7:24 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown
PG&E | 2017-10-06 | 12:03 | 39.4645 | -122.1124 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100344016 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-10-06 | 12:03 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-10-06 | 16:04 | 40.9712 | -124.0372 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JO BOB | 100978977 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-06 | 16:04 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-10-07 | 10:11 | 37.1988 | -121.8325 | Vegetation | Urban | < 0.25 Acres | Fire Agency | JOHN PAVLOFF | 100600703 | PACIFIC BELL | 21000 | Other | Overhead | Yes | 2017-10-07 | 10:11 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-10-08 | 5:11 | 40.3252 | -124.2881 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100987374 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 2017-10-08 | 5:11 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-10-08 | 16:41 | 39.589 | -122.2015 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100341037 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-10-08 | 16:41 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-10-08 | 16:43 | 40.8876 | -123.9918 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 100972408 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-08 | 16:43 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-10-08 | 17:39 | 38.5331 | -121.5424 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101585529 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-08 | 17:39 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-10-08 | 19:11 | 37.2071 | -121.862 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100622560 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-10-08 | 19:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-10-08 | 19:44 | 39.7446 | -121.597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100330456 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-08 | 19:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-10-08 | 20:35 | 39.6315 | -121.4225 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100347747 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-08 | 20:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-10-08 | 21:10 | 39.4554 | -121.0498 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100099226 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-08 | 21:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm
PG&E | 2017-10-08 | 21:46 | 39.2595 | -120.9965 | Vegetation | Urban | < 0.25 Acres | Fire Agency | PHILLIP NUNNICK 530 273-3158 INCENDENT # 26264 | 100072730 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 2017-10-08 | 21:46 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown
PG&E | 2017-10-08 | 22:19 | 39.7371 | -121.6464 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 103319605 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-10-08 | 22:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm
PG&E | 2017-10-08 | 22:30 | 38.3226 | -121.9431 | Vegetation | Rural | < 0.25 Acres | Fire Agency | vaca | 101561309 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 2017-10-08 | 22:30 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown
PG&E | 2017-10-08 | 22:54 | 35.5528 | -118.9681 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | span 7/87-7/88, Vedder Tap | Unknown | 115000 | Conductor | Overhead | Yes | 2017-10-08 | 22:54 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-10-08 | 22:58 | 39.3642 | -121.1131 | Vegetation | Rural | < 3 Meters | Fire Agency | INCIDENT NUMBER 26268 | 100068104 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-10-08 | 22:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm
PG&E | 2017-10-08 | 23:51 | 38.2758 | -121.9617 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 707-428-7305 | 101660727 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-10-08 | 23:51 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown
PG&E | 2017-10-09 | 1:02 | 38.7037 | -120.6725 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101408485 | Unknown | 21000 | Other | Overhead | Yes | 2017-10-09 | 1:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm
PG&E | 2017-10-09 | 1:13 | 38.101 | -122.2196 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 102218775 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm
PG&E | 2017-10-09 | 1:25 | 38.1906 | -121.9497 | Vegetation | Rural | 10 - 99 Acres | Unknown | N.A. | 101559973 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-10-09 | 1:25 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown
PG&E | 2017-10-09 | 1:29 | 37.8416 | -121.9583 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100501933 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-10-09 | 1:29 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-10-09 | 1:45 | 38.8576 | -122.7221 | Vegetation | Rural | < 0.25 Acres | Fire Agency | wink | 103570679 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-09 | 1:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm
PG&E | 2017-10-09 | 2:27 | 37.7293 | -122.1378 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100903727 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-10-09 | 2:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-10-09 | 4:36 | 38.2643 | -122.0488 | Vegetation | Urban | < 3 Meters | Fire Agency | Fairfield | 101660707 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-10-09 | 4:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm
PG&E | 2017-10-09 | 12:05 | 35.4067 | -118.9623 | Vegetation | Urban | < 3 Meters | Customer | N.A. | 100252698 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-10-09 | 12:05 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-10-10 | 13:36 | 38.931 | -123.3023 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102214553 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-10-10 | 13:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-10-10 | 16:17 | 38.3148 | -122.7067 | Vegetation | Urban | .26 - 9.99 Acres | Unknown | N.A. | 101996286 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-10-10 | 16:17 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-10-10 | 16:29 | 37.2559 | -121.9586 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100542800 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 2017-10-10 | 16:29 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-10-11 | 11:57 | 38.5015 | -123.0237 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101974930 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-11 | 11:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-10-11 | 16:41 | 38.679 | -121.9487 | Vegetation | Rural | < 3 Meters | Fire Agency | ESPARTO FIRE PROTECTION DISTRICT- (530) 787-3300 | 101591668 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-10-11 | 16:41 | Unknown | N.A. | N.A. | N.A. | Unknown
PG&E | 2017-10-13 | 8:30 | 38.0234 | -122.5376 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 102246021 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 2017-10-13 | 8:30 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-10-13 | 10:27 | 37.0561 | -122.0206 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Scotts Valley Fire Dept. | 101677721 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-10-13 | 10:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-10-13 | 19:15 | 36.9415 | -120.0397 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101224900 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-10-13 | 19:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused
PG&E | 2017-10-13 | 22:19 | 39.7648 | -121.6307 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100325368 | PACIFIC BELL | 0 – 750 | Transformer | Overhead | Yes | 2017-10-13 | 22:19 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-10-14 | 8:37 | 37.3944 | -122.0915 | Building | Urban | Structure Only | Fire Agency | Unknown | 100513237 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 2017-10-14 | 8:37 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-10-14 | 14:43 | 40.1122 | -122.1737 | Vegetation | Rural | < 0.25 Acres | Self Extinguished | N.A. | 101539953 | None | 12000 | Fuse | Overhead | Yes | 2017-10-14 | 14:43 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown
PG&E | 2017-10-15 | 13:15 | 37.3855 | -121.8133 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | SA JOSE FD | 100563705 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-15 | 13:15 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-10-16 | 12:10 | 36.5831 | -121.9368 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101781248 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-10-16 | 12:10 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error
PG&E | 2017-10-16 | 12:20 | 37.72 | -122.0687 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100900970 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-10-16 | 12:20 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error
PG&E | 2017-10-16 | 12:26 | 36.6641 | -121.0995 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Nick Shawkey E4462 209-402-1645 Cover Engine from Tuolumne Calaveras Unit | 101689865 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-10-16 | 12:26 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-10-17 | 18:22 | 35.4257 | -119.0297 | Vegetation | Urban | < 3 Meters | Self Extinguished | N.A. | 100144662 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | Yes | 2017-10-17 | 18:22 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown
PG&E | 2017-10-18 | 13:58 | 37.636 | -122.0793 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100952408 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-10-18 | 13:58 | Contact From Object | N.A. | Vehicle | N.A. | Human Error
PG&E | 2017-10-20 | 5:59 | 36.7475 | -119.763 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100859697 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-20 | 5:59 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown
PG&E | 2017-10-20 | 6:18 | 39.2922 | -121.0157 | Vegetation | Rural | < 3 Meters | Fire Agency | PHILLIP NUNNINK INCIDENT # 27272 | 100087647 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-10-20 | 6:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-10-20 | 9:06 | 36.036 | -120.058 | Vegetation | Rural | 300 - 999 Acres | Fire Agency | Unknown | Pole 009/009 | Unknown | 70000 | Conductor | Overhead | Yes | 2017-10-20 | 9:06 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's nest
PG&E | 2017-10-20 | 13:43 | 35.353 | -119.9873 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Kevin McLean Office(805)593-3421, Cell(805)903-3421 | 100136483 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-20 | 13:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-10-20 | 13:45 | 34.5532 | -120.5303 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 101921492 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-20 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown
PG&E | 2017-10-20 | 14:00 | 36.9216 | -119.7283 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100727124 | Unknown | 21000 | Fuse | Overhead | Yes | 2017-10-20 | 14:00 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown
PG&E | 2017-10-21 | 15:08 | 39.064 | -122.7765 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102155186 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-10-21 | 15:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-10-21 | 16:05 | 37.5911 | -122.0099 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Unknown | 103516949 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-10-21 | 16:05 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | Third-party caused
PG&E | 2017-10-23 | 19:34 | 36.0772 | -121.019 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101763398 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-23 | 19:34 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-10-23 | 21:24 | 37.3713 | -122.348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100270421 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-23 | 21:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-10-24 | 15:23 | 36.8599 | -121.7947 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101789001 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 2017-10-24 | 15:23 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-10-26 | 10:53 | 36.4036 | -121.9122 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101777002 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-26 | 10:53 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown
PG&E | 2017-10-28 | 15:26 | 39.4516 | -123.3838 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102209084 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-10-28 | 15:26 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error
PG&E | 2017-10-28 | 20:08 | 35.0222 | -118.7691 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100223850 | Unknown | 12000 | Fuse | Overhead | Yes | 2017-10-28 | 20:08 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown
PG&E | 2017-10-31 | 18:56 | 39.0034 | -121.6907 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | Pole 010/208 | Unknown | 60000 | Conductor | Overhead | Yes | 2017-10-31 | 18:56 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | Third-party caused
PG&E | 2017-10-31 | 21:02 | 39.1119 | -122.9163 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Structure 020/003 | Unknown | 60000 | Conductor | Overhead | Yes | 2017-10-31 | 21:02 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown
PG&E | 2017-11-06 | 9:59 | 37.146 | -121.6675 | Vegetation | Rural | < 0.25 Acres | Fire Agency | INCIDENT # 1717CASCU008183 | 103570543 | YES | 21000 | Conductor | Overhead | Yes | 2017-11-06 | 9:59 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-11-06 | 15:06 | 38.2998 | -122.503 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101982913 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-11-06 | 15:06 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-11-08 07:12 | 07:11 | 37.7367 | -120.3459 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101191714 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-11-08 07:12 | 07:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-11-08 14:53 | 14:53 | 37.792 | -122.2221 | Building | Urban | Structure Only | Fire Agency | Unknown | 101352529 | Unknown | 4000 | Conductor | Overhead | Yes | 2017-11-08 14:53 | 14:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-11-11 12:17 | 11:57 | 35.1191 | -120.3936 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Jordan Dayley ph#929-3911,engine#3467 | 101931190 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-11-11 12:17 | 11:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-11-12 19:45 | 19:44 | 36.7378 | -119.7769 | Building | Urban | < 0.25 Acres | Fire Agency | capt will johnson | 100871063 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 2017-11-12 19:45 | 19:44 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown
PG&E | 2017-11-14 07:43 | 07:43 | 37.324 | -120.8146 | Vegetation | Rural | < 3 Meters | Fire Agency | cammu #023223 | 103853299 | Unknown | 12000 | Transformer | Overhead | Yes | 2017-11-14 07:43 | 07:43 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown
PG&E | 2017-11-17 09:53 | 09:53 | 37.0802 | -120.0194 | Other | Rural | < 3 Meters | Utility: PG&E | N.A. | 101029626 | Unknown | 12000 | Fuse | Overhead | Yes | 2017-11-17 09:53 | 09:53 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown
PG&E | 2017-11-20 08:33 | 08:32 | 38.7584 | -120.8439 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101389405 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-11-20 08:33 | 08:32 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-11-20 20:06 | 20:05 | 35.4995 | -118.9099 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 661-324-6551 | 103782809 | None | 0 – 750 | Conductor | Overhead | Yes | 2017-11-20 20:06 | 20:05 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-11-21 11:55 | 11:55 | 37.6101 | -121.3332 | Vegetation | Rural | < 0.25 Acres | Fire Agency | tracy fire dept | 102053617 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-11-21 11:55 | 11:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-11-22 14:03 | 13:44 | 36.752 | -121.6636 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103154362 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-11-22 14:03 | 13:44 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown
PG&E | 2017-11-23 16:34 | 16:29 | 35.7755 | -120.6941 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101860971 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-11-23 16:34 | 16:29 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-11-24 10:33 | 10:33 | 36.6213 | -120.0617 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | KERMAN FIRE DEP. | 100700090 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-11-24 10:33 | 10:33 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-11-25 06:51 | 6:29 | 36.0144 | -119.9556 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 100693913 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-11-25 06:51 | 6:29 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-11-26 10:16 | 10:10 | 36.7098 | -119.5632 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100815464 | VERIZON CALIFORNIA | 0 – 750 | Conductor | Overhead | Yes | 2017-11-26 10:16 | 10:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused
PG&E | 2017-11-27 06:24 | 06:23 | 36.6942 | -121.6583 | Vegetation | Urban | < 3 Meters | Fire Agency | 831-758-7261 | 101723997 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-11-27 06:24 | 06:23 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-11-27 11:11 | 11:11 | 37.1296 | -122.3124 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100268264 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-11-27 11:11 | 11:11 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-11-28 15:50 | 15:49 | 36.4974 | -119.7909 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 100806272 | Unknown | 12000 | Other | Overhead | Yes | 2017-11-28 15:50 | 15:49 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown
PG&E | 2017-11-29 17:35 | 17:34 | 38.6841 | -120.6546 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 101419450 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 2017-11-29 17:35 | 17:34 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-12-07 12:26 | 12:25 | 34.7115 | -120.1772 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 015/220 | Unknown | 115000 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown
PG&E | 2017-12-12 04:57 | 4:40 | 39.7711 | -121.5973 | Building | Urban | Structure Only | Fire Agency | paradise fire city department | 100324902 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 2017-12-12 04:57 | 4:40 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown
PG&E | 2017-12-13 | 12:13 | 35.5922 | -120.6474 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103390807 | Unknown | 21000 | Other | Overhead | Yes | 2017-12-13 | 12:13 | Equipment/ Facility Failure | Recloser | N.A. | N.A. | Unknown
PG&E | 2017-12-14 | 1:33 | 37.1979 | -121.8375 | Building | Rural | Structure Only | Fire Agency | Unknown | 100622323 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-12-14 | 1:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-12-14 | 17:16 | 34.5878 | -120.3566 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101911004 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 2017-12-14 | 17:16 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-12-16 | 7:01 | 39.7447 | -122.1961 | Building | Urban | Structure Only | Fire Agency | ORLAND CITY FIRE DEPT | 100428554 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-12-16 | 7:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-12-16 | 11:51 | 38.8171 | -122.7041 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Shawn Ohare | 102167231 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-12-16 | 11:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-12-16 | 13:39 | 37.9702 | -121.6409 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE CAPTAIN ON DUTY | 100473121 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 2017-12-16 | 13:39 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown
PG&E | 2017-12-16 | 16:03 | 35.6593 | -120.4946 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103131190 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-12-16 | 16:03 | Other | N.A. | N.A. | N.A. | Unknown
PG&E | 2017-12-19 | 7:05 | 36.2715 | -120.3927 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100745841 | Unknown | 12000 | Fuse | Overhead | Yes | 2017-12-19 | 7:05 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-12-19 | 16:55 | 35.2309 | -119.5984 | Vegetation | Rural | < 0.25 Acres | Fire Agency | KC FIRE DEPT | 100165540 | Unknown | 21000 | Conductor | Overhead | Yes | 2017-12-19 | 16:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-12-19 | 19:45 | 40.7271 | -122.3263 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101457738 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-12-19 | 19:45 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown
PG&E | 2017-12-20 07:55 | 07:54 | 37.4012 | -122.3606 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100318864 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 2017-12-20 07:55 | 07:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown
PG&E | 2017-12-20 14:04 | 14:03 | 35.6646 | -121.244 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103857828 | Unknown | 12000 | Fuse | Overhead | No |  |  | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown
PG&E | 2017-12-20 16:05 | 16:04 | 34.6105 | -120.3218 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101906902 | VERIZON CALIFORNIA | 12000 | Fuse | Overhead | Yes | 2017-12-20 16:05 | 16:04 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown
PG&E | 2017-12-22 14:38 | 14:38 | 35.3375 | -119.0637 | Building | Urban | Structure Only | Fire Agency | Unknown | 5895SW | Unknown | 21000 | Switch | Subsurface | Yes | 2017-12-22 14:38 | 14:38 | Equipment/ Facility Failure | Switch | N.A. | N.A. | Unknown
PG&E | 2017-12-24 | 6:41 | 37.4444 | -122.1898 | Building | Urban | Structure Only | Fire Agency | Menlo Park FD | 103511827 | Unknown | 4000 | Conductor | Overhead | Yes | 2017-12-24 | 6:41 | Contact From Object | N.A. | Animal | Electric Facility | Unknown
PG&E | 2017-12-24 03:54 | 03:53 | 40.4618 | -122.3277 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101496394 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-12-24 03:54 | 03:53 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | Third-party caused
PG&E | 2017-12-29 | 16:31 | 37.8517 | -122.1586 | Vegetation | Rural | < 3 Meters | Fire Agency | 925-933-1313 | 100488954 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown

## CPUC Sample Interactive
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Suspected Cause |  |  |  |  | Notes (Optional):
| Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Ignition Cause | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
BVES | 2012-06-16 | 13:30 | 34.0498 | -118.2499 | Vegetation | Rural | Less Than .25 Acres | Customer |  | P1235 |  | 12000 | Capacitor Bank | Padmounted | Yes | 2012-06-16 | 13:30 | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Weather
Kirkwood Meadows | 2012-06-16 | 14:07 | 34.0498 | -118.2499 | Building | Urban | .26 - 9.99 Acres | Fire Agency | LA County | Pole in rear of 32 5th Street | AT&T | 21000 | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Communication Facility | Human Error
Liberty Energy | 2012-06-16 | 14:38 | 34.0498 | -118.2499 | Other |  | 10 - 99 Acres | Self Extinguished |  | P2535 | None | 21000 | Fuse | Overhead |  |  |  | Contact From Object |  | Balloons | Electric Facility | Unknown
PacifiCorp | 2012-06-16 | 14:53 | 34.0498 | -118.2499 |  |  | 100 - 299 Acres | Unknown |  | Pole at intersection of Main and 4th |  | 120 | Lightning Arrestor | Subsurface |  |  |  | Contact From Object |  | Other | Pole | Outside Force
PG&E | 2012-06-16 | 14:55 | 34.0498 | -118.2499 |  |  | 300 - 999 Acres | Utility |  | P125646 |  | 21000 | Other |  |  |  |  | Contact From Object |  | Vegetation | Pole | Other
SCE | 2012-06-16 | 0:23 | 34.0498 | -118.2499 |  |  | 1000 - 4999 Acres |  |  | B125456 |  | 21000 | Switch |  |  |  |  | Contact From Object |  | Vehicle | Pole
SDG&E | 2012-01-01 | 13:30 |  |  |  |  | Greater than 5000 Acres | [5 empty] | Transformer |  |  |  |  | Contamination
[7 empty] | Less than three (3) meters of linear travel | [10 empty] | Equipment/Facility Failure | Capacitor Bank
[7 empty] | Structure Only | [10 empty] | Equipment/Facility Failure | Conductor
[18 empty] | Equipment/Facility Failure | Fuse
[18 empty] | Equipment/Facility Failure | Insulator
[18 empty] | Equipment/Facility Failure | Lightning Arrestor
[18 empty] | Equipment/Facility Failure | Pole
[18 empty] | Equipment/Facility Failure | Guy/Span Wire
[18 empty] | Equipment/Facility Failure | Other
[18 empty] | Equipment/Facility Failure | Protective Relay
[18 empty] | Equipment/Facility Failure | Crossarm
[18 empty] | Equipment/Facility Failure | Recloser
[18 empty] | Equipment/Facility Failure | Sectionalizer
[18 empty] | Equipment/Facility Failure | Splice/Clamp/Connector
[18 empty] | Equipment/Facility Failure | Switch
[18 empty] | Equipment/Facility Failure | Transformer
[18 empty] | Equipment/Facility Failure | Voltage Regulator
Normal Operation
Other
Unknown
Vandalism/Theft
Wire-Wire Contact
Note on A1: Name of utility reporting the event
Note on X1: An Optional Field, list additional information that could be useful when examining data.
Note on B2: Date the event started (Use MM/DD/YY when inputting dates)
Note on C2: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on D2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on E2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on F2: Material involved in the initial fueling of the fire;
Note on G2: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on H2: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on I2: Is who suppressed the fire
Note on J2: If the fire was suppressed by a fire agency or agencies, insert the lead agency when one or more agency was involved
Note on K2: Utility’s description of the pole and/or equipment involved.
Note on L2: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on M2: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on N2: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on O2: The equipment involved in the event (overhead, padmounted or subsurface);
Note on P2: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on Q2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on R2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on S2: The suspected cause of the ignition;
Note on T2: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on U2: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on V2: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on W2: Factors that contributed to the ignition;

## CPUC Drop Downs
BVES | Building | Rural | Customer | Capacitor Bank | Padmounted | Contact Between Third Party Facility on Pole and Supply Lines | Animal | Human Error | Yes | Less Than .25 Acres | Communication Facility | Capacitor Bank
Kirkwood Meadows | Other | Urban | Fire Agency | Conductor | Overhead | Contact From Object | Balloons | None | No | .26 - 9.99 Acres | Electric Facility | Conductor
Liberty Energy | Vegetation |  | Self Extinguished | Fuse | Subsurface | Contamination | Other | Other |  | 10 - 99 Acres | Pole | Fuse
PacifiCorp |  |  | Unknown | Lightning Arrestor |  | Equipment/Facility Failure | Vegetation | Outside Force |  | 100 - 299 Acres |  | Insulator
PG&E |  |  | Utility | Other |  | Normal Operation | Vehicle | Unknown |  | 300 - 999 Acres |  | Lightning Arrestor
SCE |  |  |  | Switch |  | Other |  | Weather |  | 1000 - 4999 Acres |  | Pole
SDG&E |  |  |  | Transformer |  | Unknown |  |  |  | Greater than 5000 Acres |  | Guy/Span Wire
[6 empty] | Vandalism/Theft |  |  |  | Less than three (3) meters of linear travel |  | Other
[6 empty] | Wire-Wire Contact |  |  |  | Structure Only |  | Protective Relay
Crossarm
Recloser
Sectionalizer
Splice/Clamp/Connector
Switch
Transformer
Voltage Regulator
Note on G2: To be used when contact between a supply facility and non-supply facility on a pole occurred. Note: This field does not specify which facility caused the contact, only that the contact occurred.
Note on G3: Use when contact from outside object caused the incidnet.
Note on G4: Should be used when outside contaminates effect the utility's facilities. Examples: Smoke caused a phase to phase arc which resulted in a fire. Dirt and salt allowed tracking on an insultor, which caused a crossarm to catch on fire and then resulted in a vegetation fire.
Note on G5: A cessation of normal operation
Note on G6: To be used when the supply facility operated normally. Example: A fuse oprated and material fell onto vegetation and started a fire.
Note on G9: This field would include those fires started from gunshots that broke electric equipment, attempted theft of copper cable, etc.
Note on G10: To be used when to two or more supply conductors contact each other.