## 2022
Columns removed due to confidential nature: Address, EMT/SAP Description, Latitude, Longitude, AV - Mapping Details - Name,Desc,Lat,Long,Color,Symbol
Data can be provided to CPUC upon request.
MDF ID | In EMT | In ProntoForms | In GCM | DiRT Investigation Documents on Sharepoint | Event Date | Month Name | Month | Year | EMT # | ARCHIVED Event Number | PM Number | Notification/Leak# | County | PG&E Region | PG&E Division | DiRT Division | City | ARCHIVED Valid for STIP (Yes/No) | Dig-in Description | Coating/Wrap Damage | Facility Type | Gas Release? | Excavation Method | Work Performed Type | Root Cause | Valid USA? | USA Ticket # | Contact Type | Damage Caused By | Contractor Name | Line Use | ARCHIVED PG&E At-Fault | L&M Error? | At-Fault Error Type | At-Fault Comment | ARCHIVED Contractor Liable | Quarter | ARCHIVED UCON Member | ARCHIVED Gold Shovel 2nd Party Contractor? | ARCHIVED ISN Number | Within Last 12 Months? | Mapping Color | PG&E Group | Late Ticket Dig-In | Exclusion Reason | Reporting Type | Reported in Year | Date Discovered | Pipe Size | Depth of Facility | Minutes of Gas Release | Reason for No USA | Date Discovered Month | Date Discovered Month Name | Date Discovered Year | Locator Status | CLSB # | Hand Tools
18193 | x | x | x | Yes | 2022-01-03 | Jan | 1 | 2022 | 72132 |  | 45106779 | 122546254 | San Joaquin | Central Valley | Stockton | South | Stockton | Yes | A homeowner damaged a 1/2" plastic gas service line with a post hole digger while excavating for a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-03 | ½” | 18 | 8 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | Yes
18191 | x | x | x | Yes | 2022-01-03 | Jan | 1 | 2022 | 72123 |  |  | 122545952 | Contra Costa | Bay Area | Diablo | South | Orinda | Yes | Engelhart Construction damaged a 1/2" plastic gas service line with a shovel while repairing a water line. No USA ticket. | No | Gas Line | Yes | Shovel | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Englehart Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-03 | ½” | 22 | 31 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 1 | Jan | 2022 |  |  | Yes
18190 | x | x | x | Yes | 2022-01-03 | Jan | 1 | 2022 | 72130 |  |  | 122546079 | Fresno | Central Valley | Fresno | South | Fresno | Yes | A friend of the homeowner damaged a 1/2" plastic gas service line with a shovel while excavating to locate a septic tank. No USA ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-03 | ½” | 24 | 23 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | Yes
18189 | x | x | x | Yes | 2022-01-03 | Jan | 1 | 2022 | 72122 |  | 45106701 | 122545544 | Contra Costa | Bay Area | Diablo | South | Clayton | Yes | Concrete Visions damaged a 1/2' plastic gas service line with a mini excavator while excavating for a residential sewer line. No USA ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Concrete Visions | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-03 | ½” | 22 | 27 | Knew About USA Ticket Requirement But Chose Not to Call | 1 | Jan | 2022 |  |  | No
18200 | x | x | x | Yes | 2022-01-04 | Jan | 1 | 2022 | 72166 |  | 45107330 | 122549041 | Stanislaus | Central Valley | Yosemite | South | Turlock | Yes | A handyman damaged a 1/2" plastic gas service line with a post hole digger while installing a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-04 | ½” | 34 | 12 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | Yes
18199 | x | x | x | Yes | 2022-01-04 | Jan | 1 | 2022 | 72150 |  | 45107326 | 122548821 | Monterey | Central Coast | Central Coast | South | Monterey | Yes | A Ramirez Plumbing damaged a 2" plastic gas main with an excavator while repairing a residential sewer lateral. Expired USA ticket, failed to maintain marks. | No | Gas Line | Yes | Excavator | Sewer | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | No (expired) | X132101976 | Dig-In to PG&E Underground | 3rd Party-Contractor | A Ramirez Plumbing | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-04 | 2” | 30 | 32 | N/A | 1 | Jan | 2022 |  |  | No
18198 | x | x | x | Yes | 2022-01-04 | Jan | 1 | 2022 | 72170 |  | 45107337 | 122550048 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | A homeowner damaged a 1/2" plastic gas service line with a shovel while removing a tree. No USA ticket. | No | Gas Line | Yes | Shovel | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-04 | ½” | 24 | 30 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | Yes
18197 | x | x | x | Yes | 2022-01-04 | Jan | 1 | 2022 | 72145 |  | 45107187 | 122547727 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | A property owner damaged a 3/4" steel gas service line with an excavator while replacing a sewer line. No USA ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-04 | ¾” | 12 | 27 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | No
18196 | x | x | x | Yes | 2022-01-04 | Jan | 1 | 2022 | 72144 |  | 45106910 | 122547938 | Contra Costa | Bay Area | Diablo | South | Lafayette | Yes | Blue Wagon Landscaping & Design damaged a 1" plastic gas service line with a probe while excavating for a drainage line. Expired USA ticket, failed to renew ticket and maintain marks. | No | Gas Line | Yes | Probing Tool | Drainage Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | No (expired) | X105402525 | Dig-In to PG&E Underground | 3rd Party-Contractor | Bluewagon Landscaping & Design | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-04 | 1” | 28 | 81 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 1 | Jan | 2022 |  |  | Yes
18195 | x | x | x | Yes | 2022-01-04 | Jan | 1 | 2022 | 72169 |  |  | 122549839 | Fresno | Central Valley | Fresno | South | Fresno | Yes | USA Directional Bore damaged an unmapped 1" plastic gas service stub with a directional bore while installing telecommunication conduit. Valid USA ticket - records error | No | Gas Line | Yes | Boring Equipment | Telecommunications | Incorrect Facility Records / Maps | Yes | X134103013 | Dig-In to PG&E Underground | 3rd Party-Contractor | USA Directional Bore | Distribution Service |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-04 | 1” | 42 | 46 | N/A | 1 | Jan | 2022 |  |  | No
18194 | x | x | x | Yes | 2022-01-04 | Jan | 1 | 2022 | 72155 |  | 45107367 | 122548751 | Monterey | Central Coast | Central Coast | South | Carmel Valley | Yes | A handyman damaged a 1/2" plastic gas service line with a shovel while installing a patio drainage system. No USA ticket. | No | Gas Line | Yes | Shovel | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-04 | ½” | 26 | 25 | Knew About USA Ticket Requirement But Chose Not to Call | 1 | Jan | 2022 |  |  | Yes
18205 | x | x | x | Yes | 2022-01-05 | Jan | 1 | 2022 | 72194 |  | 45107998 | 122552703 | Alameda | Central Coast | Mission | South | Union City | Yes | Bailey Fence Company severed a 1/2" plastic gas service line with an auger while installing a fence post. No USA ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Bailey Fence Company, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-05 | ½” | 30 | 26 | Knew About USA Ticket Requirement But Chose Not to Call | 1 | Jan | 2022 |  |  | No
18204 | x | x |  | Yes | 2022-01-05 | Jan | 1 | 2022 | 72609 |  |  |  | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Ashbury General Contracting and Engineering damaged a 2" plastic gas main with a shovel while remodeling a home. USA ticket, but the ticket was closed due to no delineations. The contractor was using the markings placed for another contractor. Failed to dig with care. | No | Gas Line | No | Shovel | Site Development | Failed to Dig with Care | Yes | X118900564 / X121603090 | Dig-In to PG&E Underground | 3rd Party-Contractor | Asbury General Contracting and Engineering | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-05 | 2” | 42 | 0 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 1 | Jan | 2022 |  |  | Yes
18203 | x | x | x | Yes | 2022-01-05 | Jan | 1 | 2022 | 72207 |  |  | 122553546 | Sacramento | Northern | Sacramento | North | Folsom | Yes | Teichert Pipelines damaged a 1/2" plastic gas service line with a sharpshooter shovel while excavating for a gas service and main replacement project as a 2nd party for PG&E. Valid USA ticket, failed to maintain marks. | No | Gas Line | Yes | Shovel | Gas | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | X116000186 | Dig-In to PG&E Underground | 2nd Party-Contractor | Teichert Pipelines | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-01-05 | ½” | 27 | 50 | N/A | 1 | Jan | 2022 |  |  | Yes
18202 | x | x | x | Yes | 2022-01-05 | Jan | 1 | 2022 | 72201 |  | 45108571 | 122553954 | Napa | Bay Area | North Bay | North | Calistoga | Yes | Bill Nance Construction damaged a 1/2" plastic gas service line with a shovel while digging for a sewer tie in. No USA ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Bill Nance Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-05 | ½” | 24 | 18 | Knew About USA Ticket Requirement But Chose Not to Call | 1 | Jan | 2022 |  |  | Yes
18201 | x | x | x | Yes | 2022-01-05 | Jan | 1 | 2022 | 72214 |  | 45108611 | 122554528 | Contra Costa | Bay Area | Diablo | South | Antioch | Yes | Mike McCall Landscaping damaged a 1" plastic gas service line with a shovel while installing drainage lines. Valid USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Drainage Work | Failed to Dig with Care | Yes | X136401023 | Dig-In to PG&E Underground | 3rd Party-Contractor | Mike McCall Landscape | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-05 | 1” | 18 | 47 | N/A | 1 | Jan | 2022 |  |  | Yes
18209 | x | x | x | Yes | 2022-01-06 | Jan | 1 | 2022 | 72241 |  | 45110260 | 122560716 | Monterey | Central Coast | Central Coast | South | Seaside | Yes | BuildX Construction damaged a 1/2" plastic gas service line with a shovel while repairing a sewer lateral. Valid USA ticket, failed to dig with care and excavated outside of delineated area. | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | X136201384 | Dig-In to PG&E Underground | 3rd Party-Contractor | BuildX Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-06 | ½” | 20 | 42 | N/A | 1 | Jan | 2022 |  |  | Yes
18208 | x | x |  | Yes | 2022-01-06 | Jan | 1 | 2022 | 72409 |  |  |  | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | MGE Underground damaged the wrap on a 3/4" steel gas service line with vacuum equipment while performing electric work for PG&E. Valid USA ticket, inadequate excavation practices. | Yes | Gas Line | No | Vacuum Equipment | Electric Work | Inadequate Excavation Practices | Yes | X128702587 | Dig-In to PG&E Underground | 2nd Party-Contractor | MGE Underground | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Orange | PG&E GC Electric |  |  | 2nd Party Gas | Yes | 2022-01-06 | ¾” | 52 | 0 | N/A | 1 | Jan | 2022 |  |  | No
18207 | x | x | x | Yes | 2022-01-06 | Jan | 1 | 2022 | 72231 |  | 45110266 | 122560927 | Tehama | Northern | North Valley | North | Cottonwood | Yes | Northstate Excavating damaged a 1/2" plastic gas service line with a backhoe while trenching for utilities. Valid USA ticket, failed to expose facility with hand tools. | No | Gas Line | Yes | Backhoe/Trackhoe | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X200402693 | Dig-In to PG&E Underground | 3rd Party-Contractor | Northstate Excavating | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-06 | ½” | 30 | 36 | N/A | 1 | Jan | 2022 |  |  | No
18206 | x | x |  | Yes | 2022-01-06 | Jan | 1 | 2022 | 72244 |  |  |  | Sacramento | Northern | Sacramento | North | Citrus Heights | Yes | NV Communications damaged a 1/2"Aldyl-A long-side service stub while directional drilling to install telecommunication lines. Valid USA ticket, facility was not marked - records error | No | Gas Line | Yes | Drilling Equipment | Telecommunications | Incorrect Facility Records / Maps | Yes | X132700396 | Dig-In to PG&E Underground | 3rd Party-Contractor | NV Communications | Distribution Service |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-06 | ½” | 31 | 98 | N/A | 1 | Jan | 2022 |  |  | No
18212 | x | x | x | Yes | 2022-01-07 | Jan | 1 | 2022 | 72278 |  |  | 122565863 | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Mr. Rooter Plumbing damaged a 1/2" plastic gas service line with a shovel while repairing a sewer lateral. No USA ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Mr Rooter Plumbing | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-07 | ½” | 18 | 10 | Excavator Asserted They Could Not Wait | 1 | Jan | 2022 |  |  | Yes
18211 | x | x | x | Yes | 2022-01-07 | Jan | 1 | 2022 | 72284 |  | 45112066 | 122567189 | Marin | Bay Area | North Bay | North | Larkspur | Yes | Veterans Pipeline Construction damaged an unmarked 1/2" plastic gas service line with an excavator while trenching to install electric facilities. Valid USA ticket, facility was not marked - locator error. | No | Gas Line | Yes | Excavator | Electric Work | Facility Was Not Located or Marked | Yes | X116202453 | Dig-In to PG&E Underground | 2nd Party-Contractor | Veteran Pipeline Construction | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q1 |  |  |  | Yes | Orange | PG&E Division Electric |  |  | 2nd Party Gas | Yes | 2022-01-07 | ½” | 20 | 30 | N/A | 1 | Jan | 2022 | Bargaining Unit |  | No
18210 | x | x | x | Yes | 2022-01-07 | Jan | 1 | 2022 | 72271 |  |  | 122567700 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Westech Systems, hired as a sub-contractor for NexGen Construction, damaged an unmarked 1" plastic gas service line with a mini excavator while excavating to tie-in and install risers. Westech previously installed the electric and gas subsurface facilities, but never called for remarks of these subsurface installations. Valid USA ticket, failed to request remarks. | No | Gas Line | Yes | Excavator | Electric Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | X115303160 | Dig-In to PG&E Underground | 3rd Party-Contractor | Westech Systems Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-07 | 1” | 42 | 29 | N/A | 1 | Jan | 2022 |  |  | No
18214 | x | x | x | Yes | 2022-01-08 | Jan | 1 | 2022 | 72319 |  | 45114082 | 122576975 | Sonoma | Northern | Sonoma | North | Sonoma | Yes | Cooke Construction damaged a 1" plastic gas service line with a backhoe while completing foundation work. The facility was accurately marked for another contractor. No USA ticket, failed to expose facility with hand tools. | No | Gas Line | Yes | Backhoe/Trackhoe | Foundation Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Cooke Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-08 | 1” | 36 | 37 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 1 | Jan | 2022 |  |  | No
18216 | x | x |  | Yes | 2022-01-09 | Jan | 1 | 2022 | 72342 |  |  |  | Marin | Bay Area | North Bay | North | Novato | Yes | A homeowner damaged a 3/4" steel gas service line with a pickaxe while excavating for a fence. No USA ticket. | No | Gas Line | Yes | Pickaxe | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-09 | ¾” | 19 | 136 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | Yes
18215 | x | x | x | Yes | 2022-01-09 | Jan | 1 | 2022 | 72347 |  |  | 122583313 | Kern | Central Valley | Kern | South | Bakersfield | Yes | PG&E Electric M&C damaged a 1/2" plastic gas service line with a shovel while excavating to expose a faulty secondary leg. Emergency USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | X200900171 | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Electric | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Blue | PG&E Division Electric |  |  | 1st Party Gas | Yes | 2022-01-09 | ½” | 46 | 60 | N/A | 1 | Jan | 2022 |  |  | Yes
18226 | x | x | x | Yes | 2022-01-10 | Jan | 1 | 2022 | 72364 |  |  | 122596275 | Alameda | Central Coast | Mission | South | Sunol | Yes | A laborer, hired by the homeowner, damaged a 1/2" plastic gas service line while removing a tree stump. The laborer tied a chain around a tree stump and severed the facility while pulling the tree stump out of the ground. No USA ticket. | No | Gas Line | Yes | Other Driven Machinery | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-10 | ½” | 12 | 31 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | No
18225 | x | x | x | Yes | 2022-01-10 | Jan | 1 | 2022 | 72359 |  |  | 122594647 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | City of San Francisco Water Department damaged a mismarked 1/2" plastic gas service line with a shovel while excavating for new water service installations. Valid USA ticket, facility was mismarked - locator error. | No | Gas Line | Yes | Shovel | Water | Incorrect Information or Marks | Yes | W132800090 | Dig-In to PG&E Underground | 3rd Party-Government Entity | City of San Francisco | Distribution Service |  | Yes | Locator Error - Mismark | Locator failed to follow the difficult to locate process, specifically the Locator did not escalate. The Locator did not trust their signal and a better sweep may have helped. |  | 2022 Q1 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-01-10 | ½” | 36 | 23 | N/A | 1 | Jan | 2022 | Bargaining Unit |  | Yes
18224 | x |  | x |  | 2022-01-10 | Jan | 1 | 2022 | 72383 |  | 45119091 | 122600051 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Per SAP, a homeowner damaged a 1/2" plastic gas service line with a pick axe while installing a drain. No USA ticket. | No | Gas Line | Yes | Pickaxe | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-10 | 1/2" | 24 | 14 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | Yes
18222 | x | x | x | Yes | 2022-01-10 | Jan | 1 | 2022 | 72430 |  | 45121785 | 122606131 | Santa Clara | Central Coast | De Anza | Central | Los Gatos | Yes | Ed Linstrom Landscape damaged a 1" plastic gas service line with a shovel while removing a tree stump. No USA ticket. | No | Gas Line | Yes | Shovel | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Ed Linstrom Landscape | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-10 | 1” | 21 | 37 | Excavator Did Not Believe a USA Ticket was Required | 1 | Jan | 2022 |  |  | Yes
18221 | x | x | x | Yes | 2022-01-10 | Jan | 1 | 2022 | 72366 |  | 45118586 | 122595084 | Nevada | Northern | Sierra | North | Grass Valley | Yes | A homeowner damaged a 1/2" plastic gas service line with an auger while installing a fence. No USA ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-10 | ½” | 24 | 16 | Excavator Did Not Believe a USA Ticket was Required | 1 | Jan | 2022 |  |  | No
18220 | x | x | x | Yes | 2022-01-10 | Jan | 1 | 2022 | 72378 |  | 45119092 | 122600053 | Placer | Northern | Sierra | North | Granite Bay | Yes | A homeowner damaged a 1/2" plastic gas service line with an auger while installing a fence post. No USA ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-10 | ½” | 20 | 68 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 1 | Jan | 2022 |  |  | No
18219 | x | x | x | Yes | 2022-01-10 | Jan | 1 | 2022 | 72362 |  | 45118582 | 122594842 | Sacramento | Northern | Sacramento | North | Folsom | Yes | Rescue Concrete damaged a 1" plastic gas service line with a mini excavator while installing footing for a fence. USA ticket, failed to delineate job site. | No | Gas Line | Yes | Excavator | Fencing | Failed to Delineate Work Site With Required Markings | Yes | X136400937 | Dig-In to PG&E Underground | 3rd Party-Contractor | Rescue Concrete | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-10 | 1” | 23 | 85 | N/A | 1 | Jan | 2022 |  |  | No
18218 | x | x | x | Yes | 2022-01-10 | Jan | 1 | 2022 | 72372 |  | 45119034 | 122597683 | Contra Costa | Bay Area | Diablo | South | Antioch | Yes | Alltech Gates & Entry Controls damaged a 1" plastic gas service line with a shovel while installing a new fence post. Expired USA ticket, excavated outside of delineated area. | No | Gas Line | Yes | Shovel | Fencing | Excavated outside delineated area | No (expired) | X130501966 | Dig-In to PG&E Underground | 3rd Party-Contractor | Alltech Gates & EntryControls, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-10 | 1” | 18 | 28 | Expired USA ticket | 1 | Jan | 2022 |  |  | Yes
18217 | x | x |  | Yes | 2022-01-10 | Jan | 1 | 2022 | 72363 |  |  |  | Contra Costa | Bay Area | Diablo | South | Alamo | Yes | Atlantis Pools damaged a 1/2" plastic gas service line with a shovel while installing a new solar electric line. No USA ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Atlantis Pools | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-10 | ½” | 18 | 31 | Excavator Did Not Believe a USA Ticket was Required | 1 | Jan | 2022 |  |  | Yes
18228 | x | x | x | Yes | 2022-01-11 | Jan | 1 | 2022 | 72398 |  | 45120775 | 122602496 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Hylan West damaged a 3" steel gas service line while directionally drilling to install telecommunication conduit. Valid USA ticket, failed to maintain clearance. | No | Gas Line | Yes | Drilling Equipment | Telecommunications | Excavator Failed to Maintain Clearance After Verifying Marks | Yes | X129300737 | Dig-In to PG&E Underground | 3rd Party-Contractor | Hylan West, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-11 | 3" | 43 | 215 | N/A | 1 | Jan | 2022 |  |  | No
18227 | x | x | x | Yes | 2022-01-11 | Jan | 1 | 2022 | 72387 |  |  | 122600812 | Sonoma | Northern | Sonoma | North | Petaluma | Yes | Environmental Designs damaged a 1/2" plastic gas service line with a shovel while excavating to install an electrical conduit. Valid USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | X200500425 | Dig-In to PG&E Underground | 3rd Party-Contractor | Environmental Design Inc | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-11 | ½” | 34 | 50 | N/A | 1 | Jan | 2022 |  |  | Yes
18237 | x | x | x | Yes | 2022-01-12 | Jan | 1 | 2022 | 72439 |  | 45122180 | 122607044 | Stanislaus | Central Valley | Yosemite | South | Waterford | Yes | Golden State Construction damaged a 1/2" plastic gas service line with a shovel while replacing conduit. Valid USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | W200502143 | Dig-In to PG&E Underground | 3rd Party-Contractor | Golden State Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-12 | ½” | 24 | 43 | N/A | 1 | Jan | 2022 |  |  | Yes
18236 | x |  |  |  | 2022-01-12 | Jan | 1 | 2022 | 72426 |  |  |  | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | MGE Underground damaged the wrap on a 3/4" steel gas service line with vacuum equipment while performing electric work for PG&E. Valid USA ticket, inadequate excavation practices. | Yes | Gas Line | No | Vacuum Equipment | Electric Work | Inadequate Excavation Practices | Yes | X128702587 | Dig-In to PG&E Underground | 2nd Party-Contractor | MGE Underground | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Orange | PG&E GC Electric |  |  | 2nd Party Gas | Yes | 2022-01-12 | 3/4" | 52 | 0 | N/A | 1 | Jan | 2022 |  |  | No
18235 | x | x | x | Yes | 2022-01-12 | Jan | 1 | 2022 | 72420 |  | 45122186 | 122607281 | San Mateo | Central Coast | Peninsula | Central | San Carlos | Yes | Power Engineering Construction damaged a 1" plastic gas service line with a steel probe while excavating for a sewer project. Valid USA ticket, failed to dig with care. | No | Gas Line | Yes | Probing Tool | Sewer | Failed to Dig with Care | Yes | W201000216 | Dig-In to PG&E Underground | 3rd Party-Contractor | Power Engineering Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-12 | 1” | 32 | 54 | N/A | 1 | Jan | 2022 |  |  | Yes
18234 | x | x | x | Yes | 2022-01-12 | Jan | 1 | 2022 | 72442 |  | 45122287 | 122608413 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | CableCom damaged a 1" plastic gas service line with a horizontal directional drill while installing telecommunication conduit. Valid USA ticket, failed to maintain clearance. | No | Gas Line | Yes | Drilling Equipment | Telecommunications | Excavator Failed to Maintain Clearance After Verifying Marks | Yes | W128600395 | Dig-In to PG&E Underground | 3rd Party-Contractor | CableCom | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-12 | 1” | 44 | 62 | N/A | 1 | Jan | 2022 |  |  | No
18233 | x | x | x | Yes | 2022-01-12 | Jan | 1 | 2022 | 72427 |  | 45121688 | 122605712 | Santa Clara | Central Coast | San Jose | Central | Morgan Hill | Yes | Trinchero Construction damaged a 1" plastic gas service line while attempting to loosen the bolts on a water main coupler with a metal bar. The contractor missed the bolt and hit the gas pipe, causing a release of gas. Valid USA ticket, failed to protect an exposed facility. | No | Gas Line | Yes | Other Hand Tools | Water | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X101200620 | Dig-In to PG&E Underground | 3rd Party-Contractor | Trinchero Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-12 | 1” | 57 | 26 | N/A | 1 | Jan | 2022 |  |  | Yes
18232 | x | x | x | Yes | 2022-01-12 | Jan | 1 | 2022 | 72423 |  |  | 122605580 | San Joaquin | Central Valley | Stockton | South | Lathrop | Yes | PG&E Electric damaged a 4" plastic gas main with an auger while installing a new power pole and anchor. There was a valid USA ticket and the facility that was damaged was not field marked for the current USA ticket. However, the facility was accurately marked and the marks were still present for an expired USA ticket. Failed to expose the facility with hand tools prior to using mechanized equipment. | No | Gas Line | Yes | Auger | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W200500126 | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Electric | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Blue | PG&E GC Electric |  |  | 1st Party Gas | Yes | 2022-01-12 | 4" | 126 | 126 | N/A | 1 | Jan | 2022 |  |  | No
18231 | x | x | x | Yes | 2022-01-12 | Jan | 1 | 2022 | 72441 |  |  | 122607047 | Sacramento | Northern | Sacramento | North | Citrus Heights | Yes | NV Communications damaged a 1/2" plastic gas service line with a sharp shooter shovel while installing telecommunication conduit. Valid USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Dig with Care | Yes | X132700341 | Dig-In to PG&E Underground | 3rd Party-Contractor | NV Communications | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-12 | ½” | 38 | 33 | N/A | 1 | Jan | 2022 |  |  | Yes
18230 | x | x | x | Yes | 2022-01-12 | Jan | 1 | 2022 | 72428 |  |  | 122608125 | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | Pavement Recycling Systems, Inc damaged a 6" steel gas main while performing soil mixing excavation. USA ticket, excavated prior to receiving a positive response. | No | Gas Line | Yes | Other Driven Machinery | Road Work | Excavated Prior to Receiving a Positive Response From All Utilities | Yes | X201000975 | Dig-In to PG&E Underground | 3rd Party-Contractor | Pavement Recycling Systems, Inc. | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-12 | 6" | 18 | 111 | N/A | 1 | Jan | 2022 |  |  | No
18229 | x | x | x | Yes | 2022-01-12 | Jan | 1 | 2022 | 72437 |  |  | 122606644 | Placer | Northern | Sierra | North | Auburn | Yes | Beyond Cool Plumbing cut a 1/2" plastic gas service line with a Sawzall while excavating a trench to install a sewer drain. No USA ticket. | No | Gas Line | Yes | Cutting Machine | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Beyond Cool Plumbing | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-12 | ½” | 31 | 25 | Knew About USA Ticket Requirement But Chose Not to Call | 1 | Jan | 2022 |  |  | No
18241 | x | x | x | Yes | 2022-01-13 | Jan | 1 | 2022 | 72468 |  |  | 122611310 | Stanislaus | Central Valley | Yosemite | South | Turlock | Yes | T&N Plumbing & Electric Inc. damaged a 2" plastic gas main with an excavator while working at a housing development. No USA ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | T&N Plumbing & Electric Inc. | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-13 | 2” | 36 | 40 | Knew About USA Ticket Requirement But Chose Not to Call | 1 | Jan | 2022 |  |  | No
18239 | x | x |  | Yes | 2022-01-13 | Jan | 1 | 2022 | 72610 |  |  |  | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | J Flores Construction discovered damage to a 2" plastic gas main. It is believed the damage occurred through improper backfill by an unknown contractor. Failed to protect an exposed facility. | No | Gas Line | No | Other | Site Development | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X108904181 | Dig-In to PG&E Underground | 3rd Party-Contractor | Unknown | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-13 | 2” |  | 0 | N/A | 1 | Jan | 2022 |  |  | No
18238 | x | x | x | Yes | 2022-01-13 | Jan | 1 | 2022 | 72460 |  |  | 122610338 | Nevada | Northern | Sierra | North | Grass Valley | Yes | Comfort Plumbing Service damaged a 1/2" plastic gas service line with a shovel while installing a sewer line. Valid USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | X135001315 | Dig-In to PG&E Underground | 3rd Party-Contractor | Comfort Plumbing Service | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-13 | ½” | 18 | 15 | N/A | 1 | Jan | 2022 |  |  | Yes
18244 | x | x | x | Yes | 2022-01-14 | Jan | 1 | 2022 | 72517 |  | 45123808 | 122615559 | Shasta | Northern | North Valley | North | Redding | Yes | Antonsen Construction damaged a 1/2" plastic gas service line with an excavator while trenching to tie-in a sewer line. No USA ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Antonsen Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-14 | ½” | 32 | 10 | Knew About USA Ticket Requirement But Chose Not to Call | 1 | Jan | 2022 |  |  | No
18243 | x | x | x | Yes | 2022-01-14 | Jan | 1 | 2022 | 72499 |  | 45123691 | 122613654 | Marin | Bay Area | North Bay | North | Novato | Yes | Bay Area Underpinning damaged a 1" plastic gas service line while driving stakes into the ground for concrete foundation. Valid USA ticket, inadequate excavation practices. | No | Gas Line | Yes | Stake | Foundation Work | Inadequate Excavation Practices | Yes | X135501160 | Dig-In to PG&E Underground | 3rd Party-Contractor | Bay Area Underpinning | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-14 | 1” | 24 | 43 | N/A | 1 | Jan | 2022 |  |  | Yes
18242 | x | x | x | Yes | 2022-01-14 | Jan | 1 | 2022 | 72498 |  | 45123738 | 122613779 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | The City of Modesto damaged a 1/2" plastic gas service line with a backhoe while trenching for a water main. The City of Modesto exposed a 3/4" steel, unmapped abandoned service. Valid USA ticket, failed to expose facility. | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X133302026 | Dig-In to PG&E Underground | 3rd Party-Government Entity | City of Modesto | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-01-14 | ½” | 55 | 90 | N/A | 1 | Jan | 2022 |  |  | No
18247 | x | x | x | Yes | 2022-01-15 | Jan | 1 | 2022 | 72538 |  |  | 122616649 | Alameda | Bay Area | East Bay | Central | Oakland | Yes | A homeowner damaged a 1/2" plastic gas service line with a pickaxe while installing a new water drain. No USA ticket. | No | Gas Line | Yes | Pickaxe | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-15 | ½” | 24 | 27 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | Yes
18246 | x | x | x | Yes | 2022-01-15 | Jan | 1 | 2022 | 72544 |  |  | 122616498 | San Mateo | Central Coast | Peninsula | Central | Burlingame | Yes | JLB Builders damaged a 1/2" plastic gas service line with a shovel while installing foundation supports for a secondary deck. No USA ticket. | No | Gas Line | Yes | Shovel | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | JLB Builders | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-15 | ½” | 18 | 4 | Knew About USA Ticket Requirement But Chose Not to Call | 1 | Jan | 2022 |  |  | Yes
18245 | x | x |  | Yes | 2022-01-15 | Jan | 1 | 2022 | 72545 |  |  |  | Kern | Central Valley | Kern | South | Bakersfield | Yes | A homeowner damaged the wrap on a 3/4" steel gas service line with a shovel while removing a fence post. No USA ticket. | Yes | Gas Line | No | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-15 | ¾” |  | 0 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 1 | Jan | 2022 |  |  | Yes
18250 | x | x | x | Yes | 2022-01-16 | Jan | 1 | 2022 | 72563 |  | 45126621 | 122621168 | Alameda | Central Coast | Mission | South | San Leandro | Yes | An unlicensed worker, hired by the homeowner, damaged a 1 1/4" steel gas service line with a stump grinder while removing a tree stump. No USA ticket. | No | Gas Line | Yes | Stump Grinder | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-16 | 1 ¼” | 12 | 12 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | No
18249 | x | x | x | Yes | 2022-01-16 | Jan | 1 | 2022 | 72569 |  |  | 122785655 | Fresno | Central Valley | Fresno | South | Fresno | Yes | A homeowner damaged a 1/2" plastic gas service line with a shovel while trenching for a sewer line. No USA ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-16 | ½” | 12 | 28 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | Yes
18248 | x | x | x | Yes | 2022-01-16 | Jan | 1 | 2022 | 72546 |  |  | 122616645 | Alameda | Central Coast | Mission | South | Fremont | Yes | RB Landscaping damaged a 1/2" plastic gas service line with a shovel while trenching for electrical upgrades. No USA ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | RB Landscaping | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-16 | ½” | 29 | 63 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 1 | Jan | 2022 |  |  | Yes
18251 | x | x | x | Yes | 2022-01-17 | Jan | 1 | 2022 | 72593 |  |  | 122619058 | Alameda | Central Coast | Mission | South | Pleasanton | Yes | NC Marble & Stone damaged a 4" plastic gas main with a shovel while planting trees for a property owner. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | NC Marble & Stone | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-17 | 4" | 26 | 163 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 1 | Jan | 2022 |  |  | Yes
18258 | x | x | x | Yes | 2022-01-18 | Jan | 1 | 2022 | 72616 |  |  | 122622301 | Amador | Central Valley | Stockton | South | Sutter Creek | Yes | A homeowner damaged a 1/2" plastic gas service line with a mini excavator while excavating for sewer and water line installation. Valid USA ticket, failed to expose facility with hand tools. | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W201100509 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-18 | ½” | 26 | 31 | N/A | 1 | Jan | 2022 |  |  | No
18257 | x | x |  | Yes | 2022-01-18 | Jan | 1 | 2022 | 72701 |  |  |  | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Mears damaged the wrap on a 6" steel main with vacuum equipment while exposing facilities for a telecommunication project. Valid USA ticket, inadequate excavation projects. | Yes | Gas Line | No | Vacuum Equipment | Telecommunications | Inadequate Excavation Practices | Yes | X136300345 | Dig-In to PG&E Underground | 3rd Party-Contractor | Mears | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-18 | 6" | 51 | 0 | N/A | 1 | Jan | 2022 |  |  | No
18256 | x | x | x | Yes | 2022-01-18 | Jan | 1 | 2022 | 72643 |  | 45127166 | 122623506 | Marin | Bay Area | North Bay | North | Kentfield | Yes | A handyman damaged a 1/2" plastic gas service line with a post hole digger while repairing a rotten deck for the homeowner. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-18 | ½” | 8 | 34 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | Yes
18255 | x | x | x | Yes | 2022-01-18 | Jan | 1 | 2022 | 72635 |  | 35318126 | 122623101 | Marin | Bay Area | North Bay | North | Kentfield | Yes | Calel Construction Company damaged a 1/2" plastic gas service line with a digging bar while excavating to replace a storm drain. No USA ticket, failed to dig with care. | No | Gas Line | Yes | Digging Bar | Drainage Work | Failed to Dig with Care | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Gary Wanegar Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-18 | ½” | 33 | 36 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 1 | Jan | 2022 |  |  | Yes
18254 | x | x | x | Yes | 2022-01-18 | Jan | 1 | 2022 | 72612 |  | 45126675 | 122621448 | Solano | Northern | Vacaville | North | Fairfield | Yes | Odyssey Landscaping Company damaged a 1" plastic gas service line with a mini excavator while trenching for drainage lines. No USA ticket. | No | Gas Line | Yes | Excavator | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Odyssey Landscaping Company Inc | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-18 | 1” | 20 | 31 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | No
18253 | x | x | x | Yes | 2022-01-18 | Jan | 1 | 2022 | 72634 |  | 45127095 | 122623137 | Santa Clara | Central Coast | De Anza | Central | Cupertino | Yes | TKS Construction damaged a 1" plastic gas service line with an excavator while trenching for foundation. Expired USA ticket, ticket was closed as no conflict - records error. | No | Gas Line | Yes | Excavator | Foundation Work | Incorrect Facility Records / Maps | Yes | W133600143 | Dig-In to PG&E Underground | 3rd Party-Contractor | TKS Construction | Distribution Service |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-18 | 1” | 120 | 21 | N/A | 1 | Jan | 2022 |  |  | No
18262 | x | x | x | Yes | 2022-01-19 | Jan | 1 | 2022 | 72663 |  | 45128042 | 122625744 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Vogue Homes damaged a 1/2" plastic gas service line with a shovel while repairing a water line. Expired USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Water | Failed to Dig with Care | No (expired) | W131300275 | Dig-In to PG&E Underground | 3rd Party-Contractor | Vogue Homes | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-19 | ½” | 16 | 32 | Expired USA ticket | 1 | Jan | 2022 |  |  | Yes
18261 | x | x | x | Yes | 2022-01-19 | Jan | 1 | 2022 | 72666 |  |  | 122626072 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | The City of Modesto damaged a 1/2" plastic gas service line with a shovel while installing a water service line. Valid USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Water | Failed to Dig with Care | Yes | X135600493 | Dig-In to PG&E Underground | 3rd Party-Government Entity | City of Modesto | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-01-19 | ½” | 30 | 25 | N/A | 1 | Jan | 2022 |  |  | Yes
18259 | x | x | x | Yes | 2022-01-19 | Jan | 1 | 2022 | 72667 |  |  | 122626591 | Kern | Central Valley | Kern | South | Bakersfield | Yes | Camarillo Drilling damaged a 1" plastic gas service line while boring to install telecommunication conduit. Valid USA ticket, failed to expose facility with hand tools. | No | Gas Line | Yes | Boring Equipment | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W200600344 | Dig-In to PG&E Underground | 3rd Party-Contractor | Camarillo Drilling | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-19 | 1” | 82 | 40 | N/A | 1 | Jan | 2022 |  |  | No
18268 | x | x | x | Yes | 2022-01-20 | Jan | 1 | 2022 | 72695 |  |  | 122774431 | Santa Cruz | Central Coast | Central Coast | South | Scotts Valley | Yes | K&D Landscaping cut a 3/4" steel gas service line with a Sawzall while cutting tree roots. Expired USA ticket, failed to protect an exposed facility. | No | Gas Line | Yes | Cutting Machine | Drainage Work | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | No (expired) | X133302412 | Dig-In to PG&E Underground | 3rd Party-Contractor | K&D Landscaping | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-20 | ¾” | 36 | 55 | Expired USA ticket | 1 | Jan | 2022 |  |  | No
18267 | x | x | x | Yes | 2022-01-20 | Jan | 1 | 2022 | 72718 |  |  | 122778426 | San Mateo | Central Coast | Peninsula | Central | San Mateo | Yes | XL Linghang damaged a 1/2" plastic gas service line with a shovel while installing irrigation lines. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | XL Linghang | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-20 | ½” | 22 | 40 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 1 | Jan | 2022 |  |  | Yes
18266 | x | x | x | Yes | 2022-01-20 | Jan | 1 | 2022 | 72708 |  |  | 122775668 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Cratus Inc damaged a 2" plastic gas main with a mini excavator while installing a new connector for the San Francisco Water Department. Valid USA ticket, failed to expose the facility with hand tools and maintain field marks. | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X106901111 | Dig-In to PG&E Underground | 3rd Party-Contractor | Cratus Inc | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-20 | 2” | 48 | 81 | N/A | 1 | Jan | 2022 |  |  | No
18265 | x | x | x | Yes | 2022-01-20 | Jan | 1 | 2022 | 72715 |  | 45137059 | 122775827 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | A relative of the homeowner damaged a 1/2" plastic gas service line with a shovel while excavating to install an electric panel. Valid USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | W201300142 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-20 | ½” | 26 | 18 | N/A | 1 | Jan | 2022 |  |  | Yes
18273 | x | x | x | Yes | 2022-01-21 | Jan | 1 | 2022 | 72738 |  |  | 122788828 | Kern | Central Valley | Kern | South | Tehachapi | Yes | Outsource Utility Contractor damaged an exposed 1/2" plastic gas service line with an auger while replacing support structures for So Cal Edison. Valid USA ticket, failed to protect an exposed facility. | No | Gas Line | Yes | Auger | Pole/Post Installation | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | W200600694 | Dig-In to PG&E Underground | 3rd Party-Contractor | Outsource Utility Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-21 | ½” | 24 | 78 | N/A | 1 | Jan | 2022 |  |  | No
18272 | x | x | x | Yes | 2022-01-21 | Jan | 1 | 2022 | 72733 |  |  | 122785926 | Butte | Northern | North Valley | North | Paradise | Yes | Advanced Telecommunications damaged a partially exposed 1" plastic gas service stub with a shovel while installing telecommunication conduit for the Paradise Camp Fire rebuild project. Valid USA ticket, failed to protect an exposed facility. | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X127803321 | Dig-In to PG&E Underground | 3rd Party-Contractor | Advanced Telecommunications | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-21 | 1” | 36 | 19 | N/A | 1 | Jan | 2022 |  |  | Yes
18271 | x | x | x | Yes | 2022-01-21 | Jan | 1 | 2022 | 72753 |  | 45142433 | 122788953 | Contra Costa | Bay Area | Diablo | South | Orinda | Yes | A homeowner damaged a 1/2" plastic gas service line with a bobcat bulldozer while performing landscaping. Valid USA ticket, failed to protect the partially exposed facility. | No | Gas Line | Yes | Bulldozer | Landscaping | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X201202217 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-21 | ½” | 18 | 71 | N/A | 1 | Jan | 2022 |  |  | No
18270 | x | x |  | No | 2022-01-21 | Jan | 1 | 2022 | 72736 |  |  |  | Fresno | Central Valley | Fresno | South | Fresno | Yes | An unknown contractor damaged a 1" plastic gas service line with a shovel. Expired USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Unknown | Failed to Dig with Care | No (expired) | X135500641 | Dig-In to PG&E Underground | 3rd Party-Contractor | Unknown | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-21 | 1” | 54 | 48 | N/A | 1 | Jan | 2022 |  |  | Yes
18277 | x | x | x | Yes | 2022-01-22 | Jan | 1 | 2022 | 72783 |  |  | 122791922 | Santa Clara | Central Coast | San Jose | Central | Santa Clara | Yes | Hammond Construction damaged a 2" plastic gas main with an excavator while attempting to expose a storm drain. Expired USA ticket, failed to maintain marks. | No | Gas Line | Yes | Excavator | Drainage Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | No (expired) | X132201540, X132201517, X132201525 | Dig-In to PG&E Underground | 3rd Party-Contractor | C. Hammond Construction | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-22 | 2” | 36 | 142 | Expired USA ticket | 1 | Jan | 2022 |  |  | No
18276 | x | x | x | Yes | 2022-01-22 | Jan | 1 | 2022 | 72772 |  |  | 122790271 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Maxton Builders damaged a 1/2" plastic branch service with a shovel while installing drainage lines. No USA ticket. | No | Gas Line | Yes | Shovel | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Maxton Builders | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-22 | ½” | 18 | 27 | Believed They Knew Where Underground Utility was From Previous Knowledge | 1 | Jan | 2022 |  |  | Yes
18275 | x | x | x | Yes | 2022-01-22 | Jan | 1 | 2022 | 72779 |  |  | 122790458 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Daniel Usbaldo Garcia (a California state licensed contractor) damaged a 1/2" plastic gas service line with a shovel while trenching for an electric conduit. Valid USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | X134302613 | Dig-In to PG&E Underground | 3rd Party-Contractor | Daniel Usbaldo Garcia | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-22 | ½” | 24 | 4 | N/A | 1 | Jan | 2022 |  |  | Yes
18274 | x | x | x | Yes | 2022-01-22 | Jan | 1 | 2022 | 72776 |  |  | 122790459 | Fresno | Central Valley | Fresno | South | Fresno | Yes | A worker hired by the homeowner damaged a 1/2" plastic gas service line with a shovel while repairing a sewer line. No USA ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-22 | ½” | 17 | 26 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | Yes
18284 | x | x | x | Yes | 2022-01-24 | Jan | 1 | 2022 | 72851 |  |  | 122795425 | Amador | Central Valley | Stockton | South | Sutter Creek | Yes | A homeowner damaged a 1/2" plastic gas service line with a 3/4" steel and 1/2" plastic gas service line with an excavator while landscaping. No USA ticket. | No | Gas Line | Yes | Excavator | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-24 | ¾” | 8 | 60 | Knew About USA Ticket Requirement But Chose Not to Call | 1 | Jan | 2022 |  |  | No
18283 | x | x |  | Yes | 2022-01-24 | Jan | 1 | 2022 | 72850 |  |  |  | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Albert's Plumbing damaged an exposed 1 1/4" plastic gas main with a hatchet while removing tree roots for a sewer lateral repair. Valid USA ticket, failed to protect the exposed facility. | No | Gas Line | Yes | Other Hand Tools | Sewer | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X201900394 | Dig-In to PG&E Underground | 3rd Party-Contractor | Albert’s Plumbing | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-24 | 1 ¼” | 24 | 41 | N/A | 1 | Jan | 2022 |  |  | Yes
18282 | x | x | x | Yes | 2022-01-24 | Jan | 1 | 2022 | 72853 |  |  | 122796876 | Santa Clara | Central Coast | San Jose | Central | Santa Clara | Yes | M&G Hauling damaged a 3/4" steel gas service line with a skid steer while excavating for foundation work. No USA ticket. | No | Gas Line | Yes | Skid Steer | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | M & G Hauling Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-24 | ¾” | 24 | 43 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 1 | Jan | 2022 |  |  | No
18281 | x | x | x | Yes | 2022-01-24 | Jan | 1 | 2022 | 72856 |  |  | 122795880 | San Mateo | Central Coast | Peninsula | Central | Redwood City | Yes | Central Pacific Engineering damaged a 3/4" steel gas service line with a trencher while excavating to replace a clogged storm drain. Valid USA ticket, failed to expose facility with hand tools. | No | Gas Line | Yes | Trencher | Drainage Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X201802462 | Dig-In to PG&E Underground | 3rd Party-Contractor | Central Pacific Engineering LLC | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-24 | ¾” | 26 | 49 | N/A | 1 | Jan | 2022 |  |  | No
18280 | x | x | x | Yes | 2022-01-24 | Jan | 1 | 2022 | 72854 |  |  | 122795793 | San Joaquin | Central Valley | Stockton | South | Lodi | Yes | Security Paving Company damaged a 2" plastic gas main with an excavator while installing a drainage system. Valid USA ticket, failed to maintain marks or request remarks. | No | Gas Line | Yes | Excavator | Drainage Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | X133700439 | Dig-In to PG&E Underground | 3rd Party-Contractor | Security Paving Company Inc. | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-24 | 2” | 55 | 76 | N/A | 1 | Jan | 2022 |  |  | No
18279 | x |  | x |  | 2022-01-24 | Jan | 1 | 2022 | 72845 |  |  | 122794118 | Fresno | Central Valley | Fresno | South | Fresno | Yes | USA Directional Bore damaged a 1/2" plastic gas service line with a mini excavator while excavating for a fiber optic project. Valid USA ticket, failed to expose facility with hand tools. | No | Gas Line | Yes | Excavator | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X201901518 | Dig-In to PG&E Underground | 3rd Party-Contractor | USA Directional Bore | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-24 | 1/2" | 36 | 43 | N/A | 1 | Jan | 2022 |  |  | No
18278 | x | x | x | Yes | 2022-01-24 | Jan | 1 | 2022 | 72846 |  |  | 122795797 | Kern | Central Valley | Kern | South | Bakersfield | Yes | DOD Construction damaged a 1" plastic gas service line with a backhoe while excavating to build curb and gutter approaches. Valid USA ticket, facility was not marked - locator error. | No | Gas Line | Yes | Backhoe/Trackhoe | Curb/Sidewalk Work | Facility Was Not Located or Marked | Yes | X201801604 | Dig-In to PG&E Underground | 3rd Party-Contractor | DOD Construction | Distribution Service |  | Yes | Locator Error - No Mark | Felt rushed, 2 minute rule, did not cofirm with map. |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-24 | 1” | 22 | 55 | N/A | 1 | Jan | 2022 | Bargaining Unit |  | No
18287 | x | x | x | Yes | 2022-01-25 | Jan | 1 | 2022 | 72894 |  | 45147430 | 122881200 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | An unlicensed subcontractor for S & Y Corp damaged a 1/2" plastic gas service line with a shovel while installing a fence. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-25 | ½” | 24 | 58 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | Yes
18286 | x | x | x | Yes | 2022-01-25 | Jan | 1 | 2022 | 72895 |  |  | 122881255 | Marin | Bay Area | North Bay | North | Fairfax | Yes | An unlicensed gardener damaged a 1" plastic gas service line with a pickaxe while removing tree roots. No USA ticket. | No | Gas Line | Yes | Pickaxe | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-25 | 1” | 29 | 71 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | Yes
18285 | x | x |  | Yes | 2022-01-25 | Jan | 1 | 2022 | 72880 |  |  |  | Sacramento | Northern | Sacramento | North | Elk Grove | Yes | JD Pasquetti damaged a 2" plastic gas main with a mini excavator while excavating to repair a sinkhole. Valid USA ticket, failed to expose the facility with hand tools. | No | Gas Line | Yes | Excavator | Blading/Lot Grading | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X120101679 | Dig-In to PG&E Underground | 3rd Party-Contractor | JD Pasquetti | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-25 | 2” | 35 | 57 | N/A | 1 | Jan | 2022 |  |  | No
18298 | x | x | x | Yes | 2022-01-26 | Jan | 1 | 2022 | 72933 |  |  | 122886512 | Sutter | Northern | Sierra | North | Yuba City | Yes | Superior Concrete damaged a 1/2" plastic gas service line with a mini excavator while installing a sidewalk. Valid USA ticket, failed to expose facility with hand tools. | No | Gas Line | Yes | Excavator | Curb/Sidewalk Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X201301569 | Dig-In to PG&E Underground | 3rd Party-Contractor | Superior Concrete | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-26 | ½” | 40 | 39 | N/A | 1 | Jan | 2022 |  |  | No
18297 | x | x | x | Yes | 2022-01-26 | Jan | 1 | 2022 | 72916 |  |  | 122885463 | Contra Costa | Bay Area | Diablo | South | Walnut Creek | Yes | Mountain Cascade damaged an exposed 1" plastic gas service line with an excavator while performing a water pipeline project for EBMUD. Valid USA ticket, failed to protect an exposed facility. | No | Gas Line | Yes | Excavator | Water | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X113902383 | Dig-In to PG&E Underground | 3rd Party-Contractor | Mountain Cascade | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-26 | 1” | 36 | 56 | N/A | 1 | Jan | 2022 |  |  | No
18296 | x | x | x | Yes | 2022-01-26 | Jan | 1 | 2022 | 72943 |  |  | 122887176 | Napa | Bay Area | North Bay | North | St Helena | Yes | Underground Construction damaged a 1" plastic gas line with a sharpshooter shovel while replacing a gas line for PG&E. Valid USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | X201701538 | Dig-In to PG&E Underground | 2nd Party-Contractor | Underground Construction Company | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Orange | PG&E Division Gas |  |  | 2nd Party Gas | Yes | 2022-01-26 | 1” | 36 | 14 | N/A | 1 | Jan | 2022 |  |  | Yes
18295 | x | x | x | Yes | 2022-01-26 | Jan | 1 | 2022 | 72944 |  | 45152556 | 122893970 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Elite Private Landscaping damaged a 2" plastic gas line with a trencher while landscaping. No USA ticket. | No | Gas Line | Yes | Trencher | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Elite Private Landscaping | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-26 | 2” | 32 | 56 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 1 | Jan | 2022 |  |  | No
18294 | x | x | x | Yes | 2022-01-26 | Jan | 1 | 2022 | 72927 |  | 45149077 | 122886167 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Dainamic Builders damaged a 1" plastic gas service line with a backhoe while repairing a sewer line. No USA ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Dainamic Builders | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-26 | 1” | 25 | 26 | Believed They Knew Where Underground Utility was From Previous Knowledge | 1 | Jan | 2022 |  |  | No
18292 | x |  |  |  | 2022-01-26 | Jan | 1 | 2022 | 72932 |  |  |  | Butte | Northern | North Valley | North | Paradise | Yes | Dudley Excavating damaged the tracer wire on a 1" plastic gas service line while boring for telecommunication installation. Valid USA ticket, failed to protect an exposed facility. | No | Gas Line | No | Boring Equipment | Telecommunications | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X201202196 | Dig-In to PG&E Underground | 3rd Party-Contractor | Dudley's Excavating Inc | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-26 | 1" |  | 0 | N/A | 1 | Jan | 2022 |  |  | No
18291 | x | x | x | Yes | 2022-01-26 | Jan | 1 | 2022 | 72914 |  |  | 122886655 | Alameda | Central Coast | Mission | South | Livermore | Yes | Bothman Construction damaged a 1 1/4" plastic gas main with a mini excavator while exposing a sewer line. Valid USA ticket, failed to expose facility with hand tools. | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W119700258 | Dig-In to PG&E Underground | 3rd Party-Contractor | Robert A Bothman Construction | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-26 | 1 ¼” | 33 | 60 | N/A | 1 | Jan | 2022 |  |  | No
18290 | x | x | x | Yes | 2022-01-26 | Jan | 1 | 2022 | 72920 |  |  | 122886799 | Solano | Northern | Vacaville | North | Fairfield | Yes | Any Fence (unlicensed contractor) damaged a 1/2" plastic gas service line with a posthole digger while installing a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-26 | ½” | 25 | 39 | Knew About USA Ticket Requirement But Chose Not to Call | 1 | Jan | 2022 |  |  | Yes
18289 | x | x | x | Yes | 2022-01-26 | Jan | 1 | 2022 | 72924 |  |  | 122886015 | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | Engineered Soil Repairs damaged a 1/2" plastic gas service line with a shovel while excavating to install utilities. No USA ticket. | No | Gas Line | Yes | Shovel | Pipeline Work - Liquid | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Engineered Soil Repairs | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-26 | ½” | 12 | 49 | Excavator Did Not Believe a USA Ticket was Required | 1 | Jan | 2022 |  |  | Yes
18308 | x | x | x | Yes | 2022-01-27 | Jan | 1 | 2022 | 72980 |  |  | 122891782 | Yolo | Northern | Vacaville | North | West Sacramento | Yes | Ochoa Backhoe Service damaged a 2" plastic gas main with a backhoe while installing a new water and sewer service. Valid USA ticket, ticket was incorrectly marked as "No PGE" - locator error. | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | Facility Was Not Located or Marked | Yes | X201101329 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ochoa Backhoe Service | Distribution Main |  | Yes | Locator Error - No Mark | Felt rushed to locate and mark, 2 minute rule and count service |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-27 | 2” |  | 46 | N/A | 1 | Jan | 2022 | Bargaining Unit |  | No
18307 | x |  |  |  | 2022-01-27 | Jan | 1 | 2022 | 72966 |  |  |  | Santa Clara | Central Coast | De Anza | Central | Sunnyvale | Yes | California Utility Co damaged a 4" plastic gas main while boring in utilities. Valid USA ticket, failed to expose facility with hand tools. | No | Gas Line | Yes | Boring Equipment | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W136300119 | Dig-In to PG&E Underground | 3rd Party-Contractor | California Utility Company | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-27 | 4" | 35 | 137 | N/A | 1 | Jan | 2022 |  |  | No
18306 | x | x | x | Yes | 2022-01-27 | Jan | 1 | 2022 | 72960 |  |  | 122891101 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Redwood Residential damaged a 1/2" plastic gas service line with a post hole digger while replacing a fence. Valid USA ticket, failed to dig with care. | No | Gas Line | Yes | Post-Hole Digger | Fencing | Failed to Dig with Care | Yes | X201800564 | Dig-In to PG&E Underground | 3rd Party-Contractor | Redwood Residential Fence | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-27 | ½” | 32 | 38 | N/A | 1 | Jan | 2022 |  |  | Yes
18304 | x | x |  | Yes | 2022-01-27 | Jan | 1 | 2022 | 72979 |  |  |  | Alameda | Bay Area | East Bay | Central | Oakland | Yes | The Plumbing Ministry damaged a 3/4" steel gas service line while pipe bursting for a sewer lateral replacement project. Valid USA ticket, facility was not marked - locator error. | No | Gas Line | Yes | Boring Equipment | Sewer | Facility Was Not Located or Marked | Yes | X202001932 | Dig-In to PG&E Underground | 3rd Party-Contractor | The Plumbing Ministry | Distribution Service |  | Yes | Locator Error - No Mark | Felt rushed to locate and mark, 2 minute rule and count service |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-27 | ¾” | 24 | 84 | N/A | 1 | Jan | 2022 | Bargaining Unit |  | No
18303 | x | x | x | Yes | 2022-01-27 | Jan | 1 | 2022 | 72959 |  |  | 122888643 | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Pacific Trenchless damaged a 1/2" plastic gas service line with a shovel while excavating for a sewer main and lateral installation. Valid USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | X201002269 | Dig-In to PG&E Underground | 3rd Party-Contractor | Pacific Trenchless | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-27 | ½” | 42 | 26 | N/A | 1 | Jan | 2022 |  |  | Yes
18301 | x | x | x | Yes | 2022-01-27 | Jan | 1 | 2022 | 72970 |  |  | 122891042 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | MI Electric damaged a 1/2" plastic gas service line with a shovel while installing an upgraded electric panel. The facility was accurately marked for another contractor. No USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | MI Electric | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-27 | ½” | 24 | 19 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 1 | Jan | 2022 |  |  | Yes
18300 | x | x | x | Yes | 2022-01-27 | Jan | 1 | 2022 | 72972 |  |  | 122891553 | Santa Cruz | Central Coast | Central Coast | South | Felton | Yes | An unlicensed worker damaged a 1/2" plastic gas service line with a post hole digger while installing a retaining wall. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-27 | ½” | 30 | 36 | Knew About USA Ticket Requirement But Chose Not to Call | 1 | Jan | 2022 |  |  | Yes
18311 | x | x | x | Yes | 2022-01-28 | Jan | 1 | 2022 | 73006 |  |  | 122895856 | Mendocino | Bay Area | North Bay | North | Willits | Yes | A homeowner damaged a 1/2" plastic gas service line with a mini excavator while replacing a gate post. No USA ticket. | No | Gas Line | Yes | Excavator | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-28 | ½” | 28 | 4 | Knew About USA Ticket Requirement But Chose Not to Call | 1 | Jan | 2022 |  |  | No
18310 | x | x | x | Yes | 2022-01-28 | Jan | 1 | 2022 | 73003 |  | 45153160 | 122895453 | Humboldt | Northern | Humboldt | North | Eureka | Yes | Coldwell Banker (property management) damaged a 1/2" plastic gas service line with a post hole digger while installing a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Caldwell Banker Cutten Realty Property Management | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-28 | ½” | 28 | 32 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | Yes
18309 | x | x |  | Yes | 2022-01-28 | Jan | 1 | 2022 | 72987 |  |  |  | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | EBMUD damaged a 1" plastic gas service line with a backhoe while excavating to repair a water line. Valid USA ticket, facility was not marked - locator error. | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Facility Was Not Located or Marked | Yes | X202502985 | Dig-In to PG&E Underground | 3rd Party-Government Entity | EBMUD | Distribution Service |  | Yes | Locator Error - No Mark | Felt rushed. Did not locate A to B and failed to escalate. |  | 2022 Q1 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-01-28 | 1” | 36 | 50 | N/A | 1 | Jan | 2022 | Bargaining Unit |  | No
18318 | x | x | x | Yes | 2022-01-29 | Jan | 1 | 2022 | 73013 |  | 45153411 | 122896193 | Yolo | Northern | Vacaville | North | West Sacramento | Yes | Weber General Engineering damaged a 2" plastic gas main with a grader while lot grading. Expired USA ticket, failed to maintain marks or request remarks. | No | Gas Line | Yes | Grader/Scraper | Blading/Lot Grading | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | No (expired) | W111700462 | Dig-In to PG&E Underground | 3rd Party-Contractor | Weber General Engineering Inc | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-29 | 2” | 24 | 46 | Expired USA ticket | 1 | Jan | 2022 |  |  | No
18316 | x | x | x | Yes | 2022-01-29 | Jan | 1 | 2022 | 73026 |  |  | 122896269 | Mendocino | Northern | Sonoma | North | Redwood Valley | Yes | A homeowner damaged a 1 1/4" plastic gas main with an excavator while excavating for water. No USA ticket. | No | Gas Line | Yes | Excavator | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-29 | 1 ¼” | 36 | 64 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | No
18315 | x | x | x | Yes | 2022-01-29 | Jan | 1 | 2022 | 73014 |  |  | 122896316 | Santa Clara | Central Coast | De Anza | Central | Los Altos | Yes | Moon Valley Nurseries damaged a 1/2" plastic gas service line with a shovel while excavating to plant a tree. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Moon Valley Nursery | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-29 | ½” | 20 | 22 | Pending | 1 | Jan | 2022 |  |  | Yes
18314 | x | x | x | Yes | 2022-01-29 | Jan | 1 | 2022 | 73018 |  |  | 122896482 | Marin | Bay Area | North Bay | North | Larkspur | Yes | An employee of the homeowner damaged a 1/2" plastic gas service line with a shovel while landscaping. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-29 | ½” | 18 | 16 | No Knowledge of USA Ticketing Process | 1 | Jan | 2022 |  |  | Yes
18313 | x | x | x | Yes | 2022-01-29 | Jan | 1 | 2022 | 73024 |  |  | 122900663 | Alameda | Central Coast | Mission | South | Fremont | Yes | A homeowner damaged a 1/2" plastic gas service line with a shovel while excavating for concrete forms for a retaining wall. No USA ticket. | No | Gas Line | Yes | Shovel | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-29 | ½” | 6 | 16 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 1 | Jan | 2022 |  |  | Yes
18325 | x |  | x |  | 2022-01-31 | Jan | 1 | 2022 | 73097 |  |  | 122902747 | Fresno | Central Valley | Fresno | South | Kerman | Yes | A friend of the homeowner damaged a 1/2" plastic gas service line with a shovel while removing a tree from the property. No USA ticket. | No | Gas Line | Yes | Shovel | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-31 | 1/2" | 24 | 11 | Pending | 1 | Jan | 2022 |  |  | Yes
18324 | x |  | x |  | 2022-01-31 | Jan | 1 | 2022 | 73094 |  |  | 122902926 | Fresno | Central Valley | Fresno | South | Fresno | Yes | A friend of the homeowner damaged a 1/2" plastic gas service line with an excavator while installing a septic tank. No USA ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-01-31 | 1/2" | 20 | 45 | Pending | 1 | Jan | 2022 |  |  | No
18323 | x | x | x | Yes | 2022-01-31 | Jan | 1 | 2022 | 73093 |  |  | 122902377 | Sacramento | Northern | Sacramento | North | Folsom | Yes | LCM Concrete Construction Company damaged a 1/2" plastic gas service line with a skid steer while grading a residential driveway. The facility was accurately marked for another ticket. No USA ticket, failed to expose facility with hand tools. | No | Gas Line | Yes | Skid Steer | Blading/Lot Grading | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | LCM Concrete Construction Company | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-31 | 1/2" | 6 | 26 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 1 | Jan | 2022 |  |  | No
18322 | x | x | x | Yes | 2022-01-31 | Jan | 1 | 2022 | 73086 |  |  | 122901984 | Sacramento | Northern | Sacramento | North | Carmichael | Yes | JD Utility Services damaged a 3/4" steel gas service line while horizontal directional drilling. Valid USA ticket, facility was not marked - locator error. | No | Gas Line | Yes | Boring Equipment | Telecommunications | Facility Was Not Located or Marked | Yes | X130502959 | Dig-In to PG&E Underground | 3rd Party-Contractor | JD Utility Services | Distribution Service |  | Yes | Locator Error - No Mark | Felt rushed to locate and mark, 2 minute rule and use hook point as a tool. Review the map before closing ticket. |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-31 | ¾” | 78 | 99 | N/A | 1 | Jan | 2022 | Bargaining Unit |  | No
18321 | x | x | x | Yes | 2022-01-31 | Jan | 1 | 2022 | 73079 |  |  | 122902655 | Santa Cruz | Central Coast | Central Coast | South | Aptos | Yes | Lindex Excavating damaged a 1/2" plastic gas service line with a shovel while installing underground utilities. Expired USA ticket, failed to dig with care. | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | No (expired) | W133500170 | Dig-In to PG&E Underground | 3rd Party-Contractor | Lindex Excavation | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-01-31 | ½” | 24 | 9 | Expired USA ticket | 1 | Jan | 2022 |  |  | Yes
18327 | x | x | x | x | 2022-02-01 | Feb | 2 | 2022 | 73136 |  | 45159928 | 122912683 | Santa Clara | Central Coast | San Jose | Central | Morgan Hill | Yes | A laborer, hired by High Point Holdings LLC, damaged a 1/2" plastic gas service line with a shovel while removing a retaining wall/deck. No USA ticket. | No | Gas Line | Yes | Shovel | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-01 | ½” | 24 | 8 | Excavator Did Not Believe a USA Ticket was Required | 2 | Feb | 2022 |  |  | Yes
18326 | x | x | x |  | 2022-02-01 | Feb | 2 | 2022 | 73133 |  | 45160674 | 122915405 | Monterey | Central Coast | Central Coast | South | Carmel | Yes | Hastings Construction damaged a 1/2" plastic gas service line with a shovel while repairing a sewer lateral. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | W201200408 | Dig-In to PG&E Underground | 3rd Party-Contractor | Hastings Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-01 | ½” | 36 | 12 | N/A | 2 | Feb | 2022 |  |  | Yes
18334 | x | x | x |  | 2022-02-02 | Feb | 2 | 2022 | 73172 |  | 45161079 | 122917667 | Yolo | Northern | Vacaville | North | Woodland | Yes | PG&E GC damaged a 2" plastic gas main with a backhoe while attempting to lower the gas main. Valid USA ticket. PG&E at-fault - Wire Error | No | Gas Line | Yes | Backhoe/Trackhoe | Gas | Locating Wire Missing or Broken | Yes | X120500204 | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Gas | Distribution Main |  | Yes | Wire Error |  |  | 2022 Q1 |  |  |  | Yes | Blue | PG&E Division Electric |  |  | 1st Party Gas | Yes | 2022-02-02 | 2” | 29 | 0 | N/A | 2 | Feb | 2022 |  |  | No
18333 | x | x | x | x | 2022-02-02 | Feb | 2 | 2022 | 73161 |  |  | 122916657 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Lanco General damaged a 1" plastic gas service line with a shovel while trenching for a new footing area for a building. No USA ticket. | No | Gas Line | Yes | Shovel | Building Construction | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Lanco General | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-02 | 1” | 24 | 13 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | Yes
18332 | x | x | x | x | 2022-02-02 | Feb | 2 | 2022 | 73174 |  | 45161200 | 122918159 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while building a retaining wall. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-02 | ½” | 16 | 44 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | Yes
18331 | x | x | x |  | 2022-02-02 | Feb | 2 | 2022 | 73150 |  |  | 122916105 | San Mateo | Central Coast | Peninsula | Central | Redwood City | Yes | Granite Rock Construction damaged a 1" plastic gas service line with a steel probe while trying to locate the buried line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Probing Tool | Sewer | Failed to Dig with Care | Yes | W108900303 | Dig-In to PG&E Underground | 3rd Party-Contractor | Granite Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-02 | 1” | 30 | 53 | N/A | 2 | Feb | 2022 |  |  | Yes
18330 | x | x | x | x | 2022-02-02 | Feb | 2 | 2022 | 73169 |  | 45161007 | 122917138 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while locating a plumbing issue with a laundry machine. No USA ticket. | No | Gas Line | Yes | Shovel | Pipeline Work - Liquid | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-02 | ½” | 24 | 18 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | Yes
18339 | x | x | x | x | 2022-02-03 | Feb | 2 | 2022 | 73238 |  |  | 122922345 | San Mateo | Central Coast | Peninsula | Central | San Mateo | Yes | Del Conte’s M&H Landscape Construction damaged a 3/4" steel gas service line with a mini-excavator while removing trees. No USA ticket. | No | Gas Line | Yes | Excavator | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Del Conte’s M&H Landscape Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-03 | ¾” | 12 | 44 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | No
18337 | x | x | x |  | 2022-02-03 | Feb | 2 | 2022 | 73236 |  |  | 122922123 | San Mateo | Central Coast | Peninsula | Central | El Granada | Yes | Andreini & Sons Inc damaged a 2" plastic gas main with an excavator while exposing electrical conduit near exposed gas main. Valid USA ticket. Failed to protect subsurface facility | No | Gas Line | Yes | Excavator | Sewer | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X201003134 | Dig-In to PG&E Underground | 3rd Party-Contractor | Andreini & Sons Inc | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-03 | 2” | 40 | 63 | N/A | 2 | Feb | 2022 |  |  | No
18336 | x | x | x | x | 2022-02-03 | Feb | 2 | 2022 | 73229 |  |  | 122921742 | Placer | Northern | Sierra | North | Auburn | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while installing new fence posts. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-03 | ½” | 30 | 20 | Believed They Knew Where Underground Utility was From Previous Knowledge | 2 | Feb | 2022 |  |  | Yes
18335 | x | x | x | x | 2022-02-03 | Feb | 2 | 2022 | 73207 |  | 45163998 | 122920570 | San Joaquin | Central Valley | Stockton | South | Stockton | Yes | Felkins Excavation damaged a 1" plastic gas service line with a front loader with a backhoe attachment while building a foundation. No USA ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Felkins Excavation | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-03 | 1” | 20 | 18 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 2 | Feb | 2022 |  |  | No
18344 | x | x | x | x | 2022-02-04 | Feb | 2 | 2022 | 73293 |  | 45165734 | 122927272 | Sacramento | Northern | Sacramento | North | Elk Grove | Yes | Homeowner damaged a 1/2" plastic gas service line with a pickaxe while digging a fence post. No USA ticket. | No | Gas Line | Yes | Pickaxe | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-04 | ½” | 23 | 46 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | Yes
18343 | x | x | x |  | 2022-02-04 | Feb | 2 | 2022 | 73265 |  |  | 122926751 | San Mateo | Central Coast | Peninsula | Central | Hillsborough | Yes | Babel Construction damaged a 1/2" plastic gas service line with an excavator while digging a trench for a new drainage line. Expired USA ticket. | No | Gas Line | Yes | Excavator | Drainage Work | No USA Ticket | No (expired) | W126000206 | Dig-In to PG&E Underground | 3rd Party-Contractor | Babel Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-04 | ½” | 36 | 24 | Expired USA ticket | 2 | Feb | 2022 |  |  | No
18342 | x | x | x |  | 2022-02-04 | Feb | 2 | 2022 | 73283 |  | 45165591 | 122927081 | Sacramento | Northern | Sacramento | North | Citrus Heights | Yes | Ghita Underground Engineering damaged a 1/2" plastic gas service line with a shovel while excavating for telecommunications installation. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Dig with Care | Yes | X131902777 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ghita Underground Engineering Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-04 | ½” | 32 | 23 | N/A | 2 | Feb | 2022 |  |  | Yes
18341 | x | x | x |  | 2022-02-04 | Feb | 2 | 2022 | 73259 |  | 45165567 | 122925248 | Humboldt | Northern | Humboldt | North | Arcata | Yes | Danco Construction damaged a 1/2" plastic gas service line with a backhoe while preparing a construction site for new utilities. Valid USA ticket. Excavated outside delineated area | No | Gas Line | Yes | Backhoe/Trackhoe | Site Development | Excavated outside delineated area | Yes | X201401122 | Dig-In to PG&E Underground | 3rd Party-Contractor | Danco Builders | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-04 | ½” | 12 | 20 | N/A | 2 | Feb | 2022 |  |  | No
18347 | x | x | x |  | 2022-02-05 | Feb | 2 | 2022 | 73309 |  | 45165962 | 122928178 | Santa Clara | Central Coast | De Anza | Central | Mountain View | Yes | Flowrite Inc. damaged a 1/2" plastic gas service line with a shovel while installing electrical conduit. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | W132200146 | Dig-In to PG&E Underground | 3rd Party-Contractor | Flowrite Inc | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-05 | ½” | 46 | 25 | N/A | 2 | Feb | 2022 |  |  | Yes
18346 | x | x | x |  | 2022-02-05 | Feb | 2 | 2022 | 73314 |  | 45165967 | 122928225 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Homeowner damaged a 1" plastic gas service line with an auger while excavating for a fence. No USA ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-05 | 1” | 45 | 8 | Excavator Did Not Believe a USA Ticket was Required | 2 | Feb | 2022 |  |  | No
18345 | x | x | x | x | 2022-02-05 | Feb | 2 | 2022 | 73305 |  | 45165909 | 122927888 | Merced | Central Valley | Yosemite | South | Atwater | Yes | Homeowner damaged a 1/2" plastic gas service line with a backhoe while removing a tree stump. No USA ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-05 | ½” | 24 | 104 | Excavator Did Not Believe a USA Ticket was Required | 2 | Feb | 2022 |  |  | No
18348 | x | x | x | x | 2022-02-06 | Feb | 2 | 2022 | 73334 |  |  | 122928632 | Contra Costa | Bay Area | East Bay | Central | Richmond | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a shovel while installing new drainage next to a house. No USA ticket. | No | Gas Line | Yes | Shovel | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-06 | ½” | 24 | 20 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | Yes
18351 | x | x | x |  | 2022-02-07 | Feb | 2 | 2022 | 73370 |  |  | 122942618 | Yuba | Northern | Sierra | North | Marysville | Yes | Quattuor Construction Inc damaged a 1/2" plastic gas service line with a mini-backhoe while installing telecommunication lines. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X132200987 | Dig-In to PG&E Underground | 3rd Party-Contractor | Quattuor Construction Inc | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-07 | ½” | 32 | 19 | N/A | 2 | Feb | 2022 |  |  | No
18350 | x | x |  |  | 2022-02-07 | Feb | 2 | 2022 | 73354 |  |  |  | Santa Clara | Central Coast | De Anza | Central | Sunnyvale | Yes | Intregrum Construction damaged a 3/4" steel gas service line with a shovel while installing a new sewer line. Valid USA ticket. Excavated prior to receiving positive response. | Yes | Gas Line | No | Shovel | Sewer | Excavated Prior to Receiving a Positive Response From All Utilities | Yes | W202500452 | Dig-In to PG&E Underground | 3rd Party-Contractor | Intregrum Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-07 | ¾” | 19 |  | N/A | 2 | Feb | 2022 |  |  | Yes
18349 | x | x | x | x | 2022-02-07 | Feb | 2 | 2022 | 73367 |  | 45166525 | 122941736 | Kern | Central Valley | Kern | South | Bakersfield | Yes | MD Demolition damaged a 1" plastic insert which was supplied with gas via a 4" plastic main with an excavator while demolishing a structure. No USA ticket. | No | Gas Line | Yes | Excavator | Building Demolition | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | MD Demolition | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-07 | 1” | 6 | 11 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 2 | Feb | 2022 |  |  | No
18358 | x | x | x | x | 2022-02-08 | Feb | 2 | 2022 | 73433 |  | 45168106 | 122948227 | Santa Cruz | Central Coast | Central Coast | South | Watsonville | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while planting a tree. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-08 | ½” | 30 | 18 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | Yes
18357 | x | x | x |  | 2022-02-08 | Feb | 2 | 2022 | 73420 |  |  | 122947218 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Roger Dean Park damaged a 1" plastic gas service line with a mini-excavator while installing electric lines for a swimming pool. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X202701456 | Dig-In to PG&E Underground | 3rd Party-Contractor | Roger Dean Park | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-08 | 1” | 24 | 6 | N/A | 2 | Feb | 2022 |  |  | No
18355 | x | x | x | x | 2022-02-08 | Feb | 2 | 2022 | 73401 |  | 45167768 | 122945746 | Marin | Bay Area | North Bay | North | Greenbrae | Yes | Clough Construction damaged a 1/2" plastic gas service line inserted into 3/4" steel with a digging bar while excavating postholes to install a new fence. No USA ticket. | No | Gas Line | Yes | Digging Bar | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Clough Constuction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-08 | ½” | 24 | 65 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | Yes
18354 | x | x | x |  | 2022-02-08 | Feb | 2 | 2022 | 73412 |  | 45167848 | 122946278 | Sonoma | Northern | Sonoma | North | Rohnert Park | Yes | Cultivated Landscape Management damaged a 1" plastic gas service line with a trencher while installing irrigation lines. Valid USA ticket. Excavated Prior to Legal Excavation Start Date and Time | No | Gas Line | Yes | Trencher | Irrigation | Excavated prior to legal excavation start date and time | Yes | X203901524 | Dig-In to PG&E Underground | 3rd Party-Contractor | Cultivated Landscape Management | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-08 | 1” | 18 | 35 | N/A | 2 | Feb | 2022 |  |  | No
18353 | x | x | x |  | 2022-02-08 | Feb | 2 | 2022 | 73419 |  |  | 122963858 | Santa Clara | Central Coast | De Anza | Central | Mountain View | Yes | Marvin Davis Construction damaged a 1/2" plastic gas service line with a shovel while exposing the marked gas line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | X203100119 | Dig-In to PG&E Underground | 3rd Party-Contractor | Marvin Davis Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-08 | ½” | 35 | 20 | N/A | 2 | Feb | 2022 |  |  | Yes
18365 | x | x | x |  | 2022-02-09 | Feb | 2 | 2022 | 73482 |  |  | 122952031 | Fresno | Central Valley | Fresno | South | San Joaquin | Yes | Glasco General Engineering damaged a 2" plastic gas main with a shovel while preparing for an EFV valve installation. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | W123700181 | Dig-In to PG&E Underground | 3rd Party-Contractor | Glasco General Engineering | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-09 | 2” | 26 | 69 | N/A | 2 | Feb | 2022 |  |  | Yes
18364 | x | x | x |  | 2022-02-09 | Feb | 2 | 2022 | 73449 |  |  | 122950127 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Landscape Development damaged a 1" plastic gas service line with a digging bar while installing sprinklers. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Digging Bar | Irrigation | Incorrect Facility Records / Maps | Yes | X203500630 | Dig-In to PG&E Underground | 3rd Party-Contractor | Landscape Development Inc | Distribution Service |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-09 | 1” | 30 | 63 | N/A | 2 | Feb | 2022 |  |  | Yes
18363 | x | x | x | x | 2022-02-09 | Feb | 2 | 2022 | 73513 |  | 45174106 | 122966541 | Butte | Northern | North Valley | North | Chico | Yes | Earl's Plumbing damaged a 1" plastic gas service line with a shovel while locating a sewer line. No USA ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Earl's Plumbing | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-09 | 1” | 20 | 20 | Excavator Did Not Believe a USA Ticket was Required | 2 | Feb | 2022 |  |  | Yes
18362 | x | x |  | x | 2022-02-09 | Feb | 2 | 2022 | 73452 |  |  |  | Yolo | Northern | Vacaville | North | West Sacramento | Yes | Homeowner damaged a 3/4" steel gas service line with an excavator while removing a tree stump. No USA ticket. | No | Gas Line | No | Excavator | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-09 | ¾” |  |  | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | No
18361 | x | x | x | x | 2022-02-09 | Feb | 2 | 2022 | 73492 |  | 45173000 | 122964468 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while installing new fence posts. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-09 | ½” | 30 | 49 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | Yes
18360 | x | x | x |  | 2022-02-09 | Feb | 2 | 2022 | 73447 |  |  | 122948845 | Monterey | Central Coast | Central Coast | South | Soledad | Yes | PG&E Electric damaged a 1/2" plastic gas service line with a shovel while repairing a PG&E electric secondary facility. No USA ticket. This was related to a power outage so this qualifies as an emergency exception for no USA. Secondary cause was failing to dig with care | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Electric | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Blue | PG&E Division Electric |  |  | 1st Party Gas | Yes | 2022-02-09 | ½” | 42 | 53 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | Yes
18359 | x | x | x |  | 2022-02-09 | Feb | 2 | 2022 | 73471 |  | 45168606 | 122950669 | Marin | Bay Area | North Bay | North | San Anselmo | Yes | Amesos Plumbing damaged a 1/2" plastic gas service line inserted into 3/4" steel with a shovel while installing a new sewer lateral. Valid USA ticket. PG&E at-fault - Wire Error | No | Gas Line | Yes | Shovel | Sewer | Locating Wire Missing or Broken | Yes | X200701104 | Dig-In to PG&E Underground | 3rd Party-Contractor | Amesos Plumbing | Distribution Service |  | Yes | Wire Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-09 | ½” | 18 | 32 | N/A | 2 | Feb | 2022 |  |  | Yes
18374 | x | x | x |  | 2022-02-10 | Feb | 2 | 2022 | 73529 |  |  | 122966700 | San Mateo | Central Coast | Peninsula | Central | Redwood City | Yes | Loza And Sons Inc damaged a 1/2" plastic gas service line with an excavator while installing a new driveway. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Driveway Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W204000441 | Dig-In to PG&E Underground | 3rd Party-Contractor | Loza And Sons Inc | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-10 | ½” | 10 | 28 | N/A | 2 | Feb | 2022 |  |  | No
18373 | x | x | x | x | 2022-02-10 | Feb | 2 | 2022 | 73500 |  |  | 122964499 | Sonoma | Northern | Sonoma | North | Petaluma | Yes | Studio 101 General Building Contractors damaged a 1/2" plastic gas service line with backhoe while digging a trench for a new electric line. No USA ticket. | No | Gas Line | No | Backhoe/Trackhoe | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Studio 101 General Building Contractors | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-10 | ½” | 24 | 32 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | No
18372 | x | x | x | x | 2022-02-10 | Feb | 2 | 2022 | 73506 |  |  | 122964747 | Fresno | Central Valley | Fresno | South | Fresno | Yes | JD Home Rentals damaged a 1/2" plastic gas service line with a skid steer brush cutter while removing brush and garbage. No USA ticket. | No | Gas Line | Yes | Skid Steer | Other | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | JD Home Rentals | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-10 | ½” | 8 | 53 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | No
18371 | x | x | x |  | 2022-02-10 | Feb | 2 | 2022 | 73531 |  |  | 122967452 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | San Francisco Water Department damaged a 1" plastic gas service line with a backhoe while repairing a leaking water service. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X202501638 | Dig-In to PG&E Underground | 3rd Party-Government Entity | San Francisco Water Department | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-02-10 | 1” | 33 | 30 | N/A | 2 | Feb | 2022 |  |  | No
18370 | x | x | x | x | 2022-02-10 | Feb | 2 | 2022 | 73515 |  | 45174022 | 122965959 | Napa | Bay Area | North Bay | North | Yountville | Yes | RJL Construction damaged a 1/2" plastic gas service line with a shovel while digging a trench for a new gas service line. No USA ticket. | No | Gas Line | Yes | Shovel | Gas | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-10 | ½” | 26 | 32 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | Yes
18369 | x | x | x |  | 2022-02-10 | Feb | 2 | 2022 | 73503 |  |  | 122965124 | San Joaquin | Central Valley | Stockton | South | Lathrop | Yes | Valley Unique Electric Inc. damaged a 1" plastic tee attached to a 2" main with a backhoe while exposing conduit. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Backhoe/Trackhoe | Electric Work | Facility Was Not Located or Marked | Yes | X134801194 | Dig-In to PG&E Underground | 3rd Party-Contractor | Valley Unique Electric Inc. | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-10 | 1” | 26 | 66 | N/A | 2 | Feb | 2022 | Bargaining Unit |  | No
18367 | x | x | x |  | 2022-02-10 | Feb | 2 | 2022 | 73533 |  |  | 122967226 | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | Homeowner damaged a 1/2" plastic gas service line with a pickaxe while planting a plant. No USA ticket. | No | Gas Line | Yes | Pickaxe | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-10 | ½” | 15 | 27 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | Yes
18379 | x | x | x |  | 2022-02-11 | Feb | 2 | 2022 | 73561 |  |  | 122971255 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Environmental Landscaping Solutions damaged a 1" plastic gas service line with an excavator while installing drain pipe. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Drainage Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X203802882 | Dig-In to PG&E Underground | 3rd Party-Contractor | Environmental Landscape Solutions | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red | PG&E GDGC |  |  | 3rd Party Gas | Yes | 2022-02-11 | 1” | 34 | 56 | N/A | 2 | Feb | 2022 |  |  | No
18377 | x | x | x | x | 2022-02-11 | Feb | 2 | 2022 | 73562 |  |  | 122971104 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Green Earth Heating & Air damaged a 3/4" steel gas service line with a skid steer while removing a driveway. No USA ticket. | No | Gas Line | No | Skid Steer | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Green Earth Heating &Air | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-11 | ¾” | 3 |  | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 2 | Feb | 2022 |  |  | No
18375 | x | x | x |  | 2022-02-11 | Feb | 2 | 2022 | 73543 |  |  | 122971402 | Alameda | Bay Area | East Bay | Central | Albany | Yes | Massoumi Impact Construction Inc damaged a 1/2" plastic gas service line inserted into 3/4" steel with an excavator while installing new pavement. Valid USA ticket. PG&E at-fault - Locator Error - Mismark | No | Gas Line | Yes | Excavator | Driveway Work | Incorrect Information or Marks | Yes | X202600619 | Dig-In to PG&E Underground | 3rd Party-Contractor | Massoumi Impact Construction Inc | Distribution Service |  | Yes | Locator Error - Mismark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-11 | ½” | 19 | 54 | N/A | 2 | Feb | 2022 | Bargaining Unit |  | No
18383 | x | x |  | x | 2022-02-12 | Feb | 2 | 2022 | 73590 |  |  |  | Kern | Central Valley | Kern | South | Bakersfield | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a pickaxe while trenching doing irrigation work. No USA ticket. | No | Gas Line | No | Pickaxe | Irrigation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-12 | ½” | 18 |  | Excavator Did Not Believe a USA Ticket was Required | 2 | Feb | 2022 |  |  | Yes
18382 | x | x | x | x | 2022-02-12 | Feb | 2 | 2022 | 73597 |  |  | 122978032 | Placer | Northern | Sierra | North | Auburn | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while trying to locate a water leak in the homes sprinkler system. No USA ticket. | No | Gas Line | Yes | Shovel | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-12 | ½” | 22 | 46 | Excavator Did Not Believe a USA Ticket was Required | 2 | Feb | 2022 |  |  | Yes
18380 | x | x | x | x | 2022-02-12 | Feb | 2 | 2022 | 73584 |  |  | 122977317 | Kings | Central Valley | Fresno | South | Avenal | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while performing landscaping. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-12 | ½” | 18 | 6 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | Yes
18391 | x | x | x |  | 2022-02-14 | Feb | 2 | 2022 | 73640 |  |  | 122981653 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Sonic damaged a 1/2" plastic gas service line with boring equipment while installing telecommunication conduit. Valid USA ticket. PG&E at-fault - Wire Error | No | Gas Line | Yes | Boring Equipment | Telecommunications | Locating Wire Missing or Broken | Yes | X203201140 | Dig-In to PG&E Underground | 3rd Party-Contractor | Sonic | Distribution Service |  | Yes | Wire Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-14 | ½” | 38 | 198 | N/A | 2 | Feb | 2022 |  |  | No
18390 | x | x | x | x | 2022-02-14 | Feb | 2 | 2022 | 73657 |  |  | 122981486 | Placer | Northern | Sierra | North | Granite Bay | Yes | Hunter Construction damaged a 2" gas main with a mini-excavator while excavating for the construction of a guest home. No USA ticket. | No | Gas Line | Yes | Excavator | Building Construction | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Hunter Construction | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-14 | 2” | 36 | 84 | Excavator Did Not Believe a USA Ticket was Required | 2 | Feb | 2022 |  |  | No
18389 | x | x | x | x | 2022-02-14 | Feb | 2 | 2022 | 73665 |  | 45177356 | 122982486 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Redwood Engineering damaged a 1/2" plastic gas service line inserted into 3/4" steel with an excavator while installing a new sidewalk. No USA ticket. | No | Gas Line | Yes | Excavator | Curb/Sidewalk Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Redwood Engineering | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-14 | ½” | 8 | 33 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | No
18388 | x | x |  |  | 2022-02-14 | Feb | 2 | 2022 | 73649 |  |  |  | Contra Costa | Bay Area | East Bay | Central | Kensington | Yes | EBMUD damaged a 1/2" plastic gas service line with a shovel while doing a water main installation. Valid USA ticket. Failed to dig with care | No | Gas Line | No | Shovel | Water | Failed to Dig with Care | Yes | X135101181 | Dig-In to PG&E Underground | 3rd Party-Government Entity | EBMUD | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-02-14 | ½” |  |  | N/A | 2 | Feb | 2022 |  |  | Yes
18387 | x | x | x |  | 2022-02-14 | Feb | 2 | 2022 | 73662 |  | 45177761 | 122983157 | Kern | Central Valley | Kern | South | Bakersfield | Yes | Underground Express damaged a 1/2" plastic gas service line with a shovel while installing telecommunication support. Valid USA ticket. PG&E at-fault - Locator Error - Mismark | No | Gas Line | Yes | Shovel | Telecommunications | Incorrect information or marks | Yes | X203102179 | Dig-In to PG&E Underground | 3rd Party-Contractor | Underground Express | Distribution Service |  | Yes | Locator Error - Mismark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-14 | ½” | 30 | 15 | N/A | 2 | Feb | 2022 | Bargaining Unit |  | Yes
18386 | x | x | x | x | 2022-02-14 | Feb | 2 | 2022 | 73642 |  |  | 122982080 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | Bright Plant Solar damaged a 1/2" plastic gas service line with a roto hammer drill bit while installing copper ground rods. No USA ticket. | No | Gas Line | Yes | Drilling Equipment | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Bright planet solar | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-14 | ½” | 18 | 52 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | No
18385 | x | x | x |  | 2022-02-14 | Feb | 2 | 2022 | 73637 |  |  | 122981891 | Fresno | Central Valley | Fresno | South | Fresno | Yes | West Valley Construction damaged a 1/2" plastic gas service line inserted into 1 1/4" steel with a shovel while trying to clear an area around the exposed gas line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | X130002051 | Dig-In to PG&E Underground | 2nd Party-Contractor | West Valley Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-02-14 | ½” | 24 | 40 | N/A | 2 | Feb | 2022 |  |  | Yes
18396 | x | x | x | x | 2022-02-15 | Feb | 2 | 2022 | 73685 |  |  | 122984892 | Sonoma | Northern | Sonoma | North | Sonoma | Yes | Arrowtown Construction damaged a 1" plastic gas service line with a shovel while digging a trench for new electric service. No USA ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Arrowtown Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-15 | 1” | 38 | 12 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | Yes
18395 | x | x | x | x | 2022-02-15 | Feb | 2 | 2022 | 73684 |  |  | 122984621 | San Joaquin | Central Valley | Stockton | South | Woodbridge | Yes | Platinum Landscape Design and Maintenance (unlicensed) damaged a 1/2" plastic gas service line with a post-hole digger while doing yard drainage. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-15 | ½” | 32 | 25 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | Yes
18394 | x | x |  | x | 2022-02-15 | Feb | 2 | 2022 | 73679 |  |  |  | Solano | Northern | Vacaville | North | Fairfield | Yes | Advantage Total Protection damaged a 1 1/4" plastic gas service line with an excavator while installing electrical lines. No USA ticket. | No | Gas Line | Yes | Excavator | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Advantage Total Protection | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-15 | 1 ¼” | 28 | 36 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | No
18393 | x | x | x |  | 2022-02-15 | Feb | 2 | 2022 | 73681 |  |  | 122984305 | Kern | Central Valley | Kern | South | Bakersfield | Yes | HP Communication damaged a 2" plastic gas main with a shovel while installing telecommunication facilities. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X203302832 | Dig-In to PG&E Underground | 3rd Party-Contractor | HP Communications | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-15 | 2” | 37 | 54 | N/A | 2 | Feb | 2022 |  |  | Yes
18392 | x | x | x | x | 2022-02-15 | Feb | 2 | 2022 | 73676 |  |  | 122984232 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Freedom Pools damaged a 1/2" plastic gas service line with a skid steer while installing a pool. No USA ticket. | No | Gas Line | Yes | Skid Steer | Other | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Freedom Pools | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-15 | ½” | 24 | 13 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | No
18404 | x | x | x |  | 2022-02-16 | Feb | 2 | 2022 | 73716 |  |  | 122988315 | Kern | Central Valley | Kern | South | Ridgecrest | Yes | HP Communication damaged a 2" plastic gas main with a micro-trencher while installing telecommunication facilities. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Trencher | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X201402441 | Dig-In to PG&E Underground | 3rd Party-Contractor | HP Communications | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-16 | 2” | 11 | 117 | N/A | 2 | Feb | 2022 |  |  | No
18403 | x | x |  | x | 2022-02-16 | Feb | 2 | 2022 | 73751 |  |  |  | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Homeowner damaged a 1 1/4" plastic gas service line with a pickaxe while trying to find a water leak. No USA ticket. | No | Gas Line | Yes | Pickaxe | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-16 | 1 ¼” | 12 | 45 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | Yes
18402 | x | x | x | x | 2022-02-16 | Feb | 2 | 2022 | 73724 |  |  | 122987912 | Sutter | Northern | Sierra | North | Live Oak | Yes | Homeowner (Jenkins Farms) damaged a 1 1/4" steel gas service line with a trencher while installing a new irrigation line. No USA ticket. | No | Gas Line | Yes | Trencher | Irrigation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow | PG&E GC Gas |  |  | 3rd Party Gas | Yes | 2022-02-16 | 1 ¼” | 16 | 28 | Excavator Did Not Believe a USA Ticket was Required | 2 | Feb | 2022 |  |  | No
18401 | x | x | x | x | 2022-02-16 | Feb | 2 | 2022 | 73738 |  |  | 122988990 | San Mateo | Central Coast | Peninsula | Central | Emerald Lake Hills | Yes | Bowie Construction & Engineering Inc damaged a 1/2" plastic gas service line with a shovel while evening out the grade of a new driveway. No USA ticket. | No | Gas Line | Yes | Shovel | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Bowie Construction & Engineering Inc | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-16 | ½” | 16 | 25 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 2 | Feb | 2022 |  |  | Yes
18399 | x | x |  |  | 2022-02-16 | Feb | 2 | 2022 | 73719 |  |  |  | Contra Costa | Bay Area | East Bay | Central | Richmond | Yes | Lone Star Landscaping damaged a 1/2" plastic gas service line inserted into 3/4" steel with a shovel while trying to locate the facility. Valid USA ticket. PG&E at-fault - Locator Error - Mismark | No | Gas Line | Yes | Shovel | Irrigation | Incorrect Information or Marks | Yes | X204003470 | Dig-In to PG&E Underground | 3rd Party-Contractor | Lone Star Landscaping Inc. | Distribution Service |  | Yes | Locator Error - Mismark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-16 | ½” | 20 | 5 | N/A | 2 | Feb | 2022 | Bargaining Unit |  | Yes
18398 | x | x | x | x | 2022-02-16 | Feb | 2 | 2022 | 73752 |  | 45179493 | 122991021 | Madera | Central Valley | Yosemite | South | Madera | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence post. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-16 | ½” | 33 | 54 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | Yes
18397 | x | x | x |  | 2022-02-16 | Feb | 2 | 2022 | 73721 |  |  | 122987721 | Monterey | Central Coast | Central Coast | South | Salinas | Yes | JR Custom Harvesting damaged a 1 1/4" plastic gas service line with an excavator while installing water lines. No USA ticket. | No | Gas Line | Yes | Excavator | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | JR Custom Harvesting | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-16 | 1 ¼” | 30 | 30 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | No
18406 | x | x | x | x | 2022-02-17 | Feb | 2 | 2022 | 73794 |  |  | 122994759 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a drill while installing a new deck. No USA ticket. | No | Gas Line | Yes | Drilling Equipment | Other | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-17 | ½” | 12 | 52 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | No
18413 | x | x | x |  | 2022-02-18 | Feb | 2 | 2022 | 73811 |  |  | 122999195 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Pacific Parks Landscaping damaged a 1" plastic gas service line with a pickaxe while installing drain pipe. No USA ticket. A USA ticket was created after the dig-in occurred. | No | Gas Line | Yes | Pickaxe | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Pacific Parks Landscaping | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-18 | 1” | 17 | 45 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | Yes
18412 | x | x | x | x | 2022-02-18 | Feb | 2 | 2022 | 73812 |  |  | 122997291 | El Dorado | Northern | Sierra | North | El Dorado Hills | Yes | Next Gen Excavating Inc damaged a 1/2" plastic gas service line with a backhoe while excavating for underground utilities for new house construction. No USA ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Building Construction | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Next Gen Excavating Inc | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-18 | ½” | 41 | 66 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | No
18411 | x | x | x | x | 2022-02-18 | Feb | 2 | 2022 | 73827 |  |  | 122999075 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while installing a new gas line. No USA ticket. | No | Gas Line | Yes | Shovel | Gas | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-18 | ½” | 30 | 17 | Believed They Knew Where Underground Utility was From Previous Knowledge | 2 | Feb | 2022 |  |  | Yes
18410 | x | x |  |  | 2022-02-18 | Feb | 2 | 2022 | 73828 |  |  |  | Sacramento | Northern | Sacramento | North | Sacramento | Yes | City of Sacramento damaged the tracer wire for a 2" plastic gas main with a backhoe while excavating for a sewer lateral. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | No | Backhoe/Trackhoe | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X126401183 | Dig-In to PG&E Underground | 3rd Party-Government Entity | City of Sacramento | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-02-18 | 2” | 47 | 0 | N/A | 2 | Feb | 2022 |  |  | No
18409 | x | x |  |  | 2022-02-18 | Feb | 2 | 2022 | 73839 |  |  |  | Santa Clara | Central Coast | De Anza | Central | Cupertino | Yes | HMR Construction damaged the wrap on a 3/4" steel gas service line with a shovel while installing a new sewer line. Valid USA ticket. Failed to dig with care | Yes | Gas Line | No | Shovel | Sewer | Failed to Dig with Care | Yes | X204502496 | Dig-In to PG&E Underground | 3rd Party-Contractor | HMR Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-18 | ¾” | 16 |  | N/A | 2 | Feb | 2022 |  |  | Yes
18415 | x | x | x |  | 2022-02-19 | Feb | 2 | 2022 | 73862 |  |  | 123001791 | Humboldt | Northern | Humboldt | North | McKinleyville | Yes | Homeowner damaged 1" plastic gas service line with a post-hole digger while installing a fence post. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-19 | 1” | 30 | 14 | Excavator Did Not Believe a USA Ticket was Required | 2 | Feb | 2022 |  |  | Yes
18416 | x | x | x | x | 2022-02-20 | Feb | 2 | 2022 | 73887 |  |  | 123000961 | Fresno | Central Valley | Fresno | South | San Joaquin | Yes | Red Phoenix Construction damaged a 1/2" plastic gas service line with a shovel while installing new gas lines. No USA ticket. | No | Gas Line | Yes | Shovel | Gas | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Red Phoenix Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-20 | ½” | 40 | 137 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 2 | Feb | 2022 |  |  | Yes
18417 | x | x | x | x | 2022-02-21 | Feb | 2 | 2022 | 73918 |  |  | 123001376 | Alameda | Central Coast | Mission | South | Hayward | Yes | Bridge of Faith Church (property owner) damaged a 1/2" plastic gas service line inserted into 2" steel with a shovel while replacing a sewer pipe. No USA ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-21 | ½” | 19 | 65 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | Yes
18422 | x | x | x |  | 2022-02-22 | Feb | 2 | 2022 | 73926 |  |  | 123002293 | San Joaquin | Central Valley | Stockton | South | Lathrop | Yes | R. L. Friend Construction Inc. damaged a 1/2" plastic gas service line with an excavator while installing water pipe. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W135101067 | Dig-In to PG&E Underground | 3rd Party-Contractor | R. L. Friend Construction Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-22 | ½” | 46 | 30 | N/A | 2 | Feb | 2022 |  |  | No
18420 | x | x | x |  | 2022-02-22 | Feb | 2 | 2022 | 73927 |  |  | 123002887 | Contra Costa | Central Coast | Mission | South | San Ramon | Yes | AMM Fencing damaged a 1/2" plastic gas service line with a digging bar while replacing a fence post. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Digging Bar | Fencing | Failed to Dig with Care | Yes | X204603375 | Dig-In to PG&E Underground | 3rd Party-Contractor | AMM Fencing | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-22 | ½” | 54 | 57 | N/A | 2 | Feb | 2022 |  |  | Yes
18419 | x | x | x |  | 2022-02-22 | Feb | 2 | 2022 | 73930 |  |  | 123017895 | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Andes Construction damaged a 1/2" plastic gas service line with a shovel while doing a sewer main replacement. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | X204001647 | Dig-In to PG&E Underground | 3rd Party-Contractor | Andes Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-22 | ½” | 40 | 42 | N/A | 2 | Feb | 2022 |  |  | Yes
18418 | x | x |  | x | 2022-02-22 | Feb | 2 | 2022 | 73939 |  |  |  | Butte | Northern | North Valley | North | Chico | Yes | Cassa Commercial Electric damaged the wrap on a 2" steel gas main with a shovel while installing an electrical vault. No USA ticket. Primary cause was failure to protect subsurface facility | Yes | Gas Line | No | Shovel | Electric Work | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Cassa Commercial Electric | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-22 | 2” | 32 |  | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | Yes
18428 | x | x | x |  | 2022-02-23 | Feb | 2 | 2022 | 73996 |  |  | 123008596 | Placer | Northern | Sierra | North | Lincoln | Yes | GP Development damaged a 1" plastic gas service line with a backhoe while trenching for new commercial construction. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Building Construction | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X203801614 | Dig-In to PG&E Underground | 3rd Party-Contractor | GP Development | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-23 | 1” | 43 | 23 | N/A | 2 | Feb | 2022 |  |  | No
18427 | x | x | x |  | 2022-02-23 | Feb | 2 | 2022 | 73995 |  |  | 123011720 | San Mateo | Central Coast | Peninsula | Central | San Mateo | Yes | Andreini Brothers damaged a 3/4" steel gas service line with an excavator while doing street repaving. Valid USA ticket. PG&E at-fault - Locator Error - Mismark | No | Gas Line | Yes | Excavator | Road Work | Incorrect Information or Marks | Yes | X202000127 | Dig-In to PG&E Underground | 3rd Party-Contractor | Andreini Brothers | Distribution Service |  | Yes | Locator Error - Mismark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-23 | ¾” | 18 | 18 | N/A | 2 | Feb | 2022 | Bargaining Unit |  | No
18426 | x | x | x | x | 2022-02-23 | Feb | 2 | 2022 | 73999 |  |  | 123008592 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Alcazar Concrete damaged a 1" plastic gas service line with a excavator while trenching for a new water line. No USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Alcazar Concrete | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-23 | 1” | 30 | 37 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 2 | Feb | 2022 |  |  | No
18425 | x | x |  |  | 2022-02-23 | Feb | 2 | 2022 | 73974 |  |  |  | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Teichert Construction damaged 3/4" steel gas service line with a skid steer while doing sidewalk and gutter repairs. Valid USA ticket. Failed to maintain marks | No | Gas Line | Yes | Skid Steer | Curb/Sidewalk Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | X120800914 | Dig-In to PG&E Underground | 3rd Party-Contractor | Teichert Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-23 | ¾” | 16 | 38 | N/A | 2 | Feb | 2022 |  |  | No
18423 | x | x | x | x | 2022-02-23 | Feb | 2 | 2022 | 73975 |  |  | 123007307 | San Mateo | Central Coast | Peninsula | Central | San Carlos | Yes | ZM Bestbuild damaged a 1/2" plastic gas service line with a shovel while putting in a new driveway. No USA ticket. | No | Gas Line | Yes | Shovel | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | ZM Bestbuild | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red | PG&E Division Gas |  |  | 3rd Party Gas | Yes | 2022-02-23 | ½” | 10 | 11 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | Yes
18434 | x | x |  |  | 2022-02-24 | Feb | 2 | 2022 | 74064 |  |  |  | Stanislaus | Central Valley | Yosemite | South | Hughson | Yes | Krueger Fence damaged a 1/2" plastic gas service line with a shovel while replacing a fence. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Krueger Fence | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-24 | ½” | 24 | 32 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | Yes
18433 | x | x | x |  | 2022-02-24 | Feb | 2 | 2022 | 74049 |  |  | 123018908 | Fresno | Central Valley | Fresno | South | Clovis | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while removing a stump. No USA ticket. | No | Gas Line | Yes | Shovel | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-24 | ½” | 24 | 26 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | Yes
18432 | x | x | x |  | 2022-02-24 | Feb | 2 | 2022 | 74033 |  |  | 123017992 | Solano | Northern | Vacaville | North | Fairfield | Yes | American Underground damaged a 1/2" plastic gas service line with a shovel while trying to expose the marked gas line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | X204501590 | Dig-In to PG&E Underground | 3rd Party-Contractor | American Underground | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-24 | ½” | 38 | 31 | N/A | 2 | Feb | 2022 |  |  | Yes
18431 | x | x | x |  | 2022-02-24 | Feb | 2 | 2022 | 74047 |  |  | 123021585 | Solano | Northern | Vacaville | North | Vacaville | Yes | Bay Pacific Pipeline damaged a 2" plastic gas main with an mini-excavator while removing a sewer line. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W203300325 | Dig-In to PG&E Underground | 3rd Party-Contractor | Bay Pacific Pipeline | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-24 | 2” | 44 | 37 | N/A | 2 | Feb | 2022 |  |  | No
18430 | x | x | x |  | 2022-02-24 | Feb | 2 | 2022 | 74059 |  |  | 123019580 | Sonoma | Northern | Sonoma | North | Petaluma | Yes | KOA Campground (property owner) damaged a 1 1/4" plastic gas service line with a backhoe while installing telecommunication conduit. No USA ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Telecommunications | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-24 | 1 ¼” | 35 | 111 | Believed They Knew Where Underground Utility was From Previous Knowledge | 2 | Feb | 2022 |  |  | No
18429 | x | x |  |  | 2022-02-24 | Feb | 2 | 2022 | 74048 |  |  |  | Contra Costa | Bay Area | Diablo | South | Walnut Creek | Yes | Miller Pipeline damaged a 1/2" plastic gas service line with a shovel while doing gas line replacement for PG&E. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | X133603047 | Dig-In to PG&E Underground | 2nd Party-Contractor | Miller Pipeline | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Orange | PG&E Division Gas |  |  | 2nd Party Gas | Yes | 2022-02-24 | ½” | 18 | 79 | N/A | 2 | Feb | 2022 |  |  | Yes
18440 | x | x | x |  | 2022-02-25 | Feb | 2 | 2022 | 74098 |  |  | 123030413 | Contra Costa | Bay Area | East Bay | Central | El Cerrito | Yes | Darcy & Harty Construction Inc damaged a 1/2" plastic gas service line inserted into 3/4" steel with an backhoe while removing asphalt. Valid USA ticket. Facility embedded in concrete | No | Gas Line | Yes | Backhoe/Trackhoe | Road Work | Facility Embedded in Concrete | Yes | X127703507 | Dig-In to PG&E Underground | 3rd Party-Contractor | Darcy & Harty Construction Inc | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-25 | ½” | 6 | 120 | N/A | 2 | Feb | 2022 |  |  | No
18439 | x | x |  |  | 2022-02-25 | Feb | 2 | 2022 | 74113 |  |  |  | Contra Costa | Bay Area | Diablo | South | Danville | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a shovel while installing a fence post. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-25 | ½” | 18 | 49 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | Yes
18438 | x | x | x |  | 2022-02-25 | Feb | 2 | 2022 | 74126 |  |  | 123029903 | Sacramento | Northern | Sacramento | North | Carmichael | Yes | Homeowner damaged 3/4" steel gas line with a mini-excavator while cleaning up after demolishing a building. No USA ticket. | No | Gas Line | Yes | Excavator | Building Demolition | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-25 | ¾” | 14 | 40 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | No
18436 | x | x |  |  | 2022-02-25 | Feb | 2 | 2022 | 74122 |  |  |  | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Subterra Construction Inc. damaged a 1/2" plastic gas service line inserted into 3/4" steel with a saw cutter while excavating for a new sewer main. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Cutting Machine | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X201402423 | Dig-In to PG&E Underground | 3rd Party-Contractor | Subterra Construction Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-25 | 1” | 10 | 70 | N/A | 2 | Feb | 2022 |  |  | No
18435 | x | x | x |  | 2022-02-25 | Feb | 2 | 2022 | 74123 |  |  | 123033816 | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Janco Industries damaged a 2" plastic gas main with an excavator while excavating for a future building foundation. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Foundation Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X204201606 | Dig-In to PG&E Underground | 3rd Party-Contractor | Janco Industries | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-25 | 2” | 40 | 2 | N/A | 2 | Feb | 2022 |  |  | No
18442 | x | x | x |  | 2022-02-26 | Feb | 2 | 2022 | 74159 |  |  | 123031105 | Fresno | Central Valley | Fresno | South | Selma | Yes | Homeowner damaged 1" plastic gas service line with a shovel while installing a french drain system. No USA ticket. | No | Gas Line | Yes | Shovel | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-26 | 1” | 24 | 107 | Believed They Knew Where Underground Utility was From Previous Knowledge | 2 | Feb | 2022 |  |  | Yes
18441 | x | x | x |  | 2022-02-26 | Feb | 2 | 2022 | 74144 |  |  | 123030751 | San Joaquin | Central Valley | Stockton | South | Lodi | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence post. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-02-26 | ½” | 30 | 41 | No Knowledge of USA Ticketing Process | 2 | Feb | 2022 |  |  | Yes
18452 | x |  |  |  | 2022-02-28 | Feb | 2 | 2022 | 74207 |  |  |  | Yolo | Northern | Vacaville | North | West Sacramento | Yes | Weber General Engineering damaged a 2" plastic gas main line with a backhoe doing unknown work. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Unknown | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X121403409 | Dig-In to PG&E Underground | 3rd Party-Contractor | Weber General Engineering Inc | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-28 | 2” | 23 | 34 | N/A | 2 | Feb | 2022 |  |  | No
18451 | x | x |  |  | 2022-02-28 | Feb | 2 | 2022 | 74228 |  |  |  | Stanislaus | Central Valley | Yosemite | South | Turlock | Yes | MHK Construction damaged a transmission line with a shovel while installing a water irrigation box. Valid USA ticket. Failed to dig with care | No | Gas Line | No | Shovel | Water | Failed to Dig with Care | Yes | X203900571 | Dig-In to PG&E Underground | 3rd Party-Contractor | MHK Construction Inc. | Transmission Line |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-28 | 8" |  |  | N/A | 2 | Feb | 2022 |  |  | Yes
18450 | x | x |  |  | 2022-02-28 | Feb | 2 | 2022 | 74229 |  |  |  | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Kingdom Concrete damaged a 1/2" plastic gas service line with a shovel while excavating for a new foundation. No USA ticket. | No | Gas Line | Yes | Shovel | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Kingdom Concrete | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-28 | ½” | 12 | 37 | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | Yes
18449 | x | x | x |  | 2022-02-28 | Feb | 2 | 2022 | 74200 |  |  | 123033104 | Sacramento | Northern | Sacramento | North | Citrus Heights | Yes | Daniel Design and Build damaged a 1/2" plastic gas service line with a shovel while installing a new gas houseline. No USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Daniel Design and Build | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-28 | ½” | 12 | 51 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 2 | Feb | 2022 |  |  | Yes
18448 | x | x | x |  | 2022-02-28 | Feb | 2 | 2022 | 74201 |  |  | 123033011 | San Joaquin | Central Valley | Stockton | South | Stockton | Yes | Imperial Electric Service damaged 1" plastic gas service line with an excavator while trenching for electric cable installation. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X203500738 | Dig-In to PG&E Underground | 3rd Party-Contractor | Imperial Electric Service | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-28 | 1” | 24 | 13 | N/A | 2 | Feb | 2022 |  |  | No
18447 | x | x |  |  | 2022-02-28 | Feb | 2 | 2022 | 74209 |  |  |  | Alameda | Bay Area | East Bay | Central | Alameda | Yes | Westland Contractors damaged a 1/2" plastic gas service line with a shovel while excavating for a future sewer main replacement. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | X204000625 | Dig-In to PG&E Underground | 3rd Party-Contractor | Westland Contractors, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-28 | ½” | 36 | 18 | N/A | 2 | Feb | 2022 |  |  | Yes
18446 | x | x |  |  | 2022-02-28 | Feb | 2 | 2022 | 74219 |  |  |  | Alameda | Central Coast | Mission | South | Fremont | Yes | Nieves Bros Inc. damaged the wrap on a 3/4" steel gas service line with a shovel while digging a trench for electrical upgrade. No USA ticket | Yes | Gas Line | No | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Nieves Bros Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-28 | ¾” | 24 |  | Knew About USA Ticket Requirement But Chose Not to Call | 2 | Feb | 2022 |  |  | Yes
18445 | x |  |  |  | 2022-02-28 | Feb | 2 | 2022 | 74205 |  |  |  | Solano | Northern | Vacaville | North | Suisun City | Yes | Cupertino Electric damaged a 3/4" steel gas service line with an excavator while doing unknown work. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Gas | Incorrect Facility Records / Maps | Yes | W134800205 | Dig-In to PG&E Underground | 2nd Party-Contractor | Cupertino Electric | Distribution Service |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-02-28 | ½” |  | 8 | N/A | 2 | Feb | 2022 |  |  | No
18444 | x | x |  |  | 2022-02-28 | Feb | 2 | 2022 | 74226 |  |  |  | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a shovel while excavating for a new foundation. No USA ticket. | No | Gas Line | Yes | Shovel | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-02-28 | ½” | 18 | 10 | Excavator Did Not Believe a USA Ticket was Required | 2 | Feb | 2022 |  |  | Yes
18459 | x | x | x |  | 2022-03-01 | Mar | 3 | 2022 | 74275 |  | 45199282 | 123056807 | Butte | Northern | North Valley | North | Chico | Yes | Lighthouse Electric damaged a 1/2" plastic gas service line with a grounding rod while it was being installed. No USA ticket. | No | Gas Line | Yes | Grounding Rod | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Lighthouse Electric | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-01 | ½” | 22 | 43 | Excavator Did Not Believe a USA Ticket was Required | 3 | Mar | 2022 |  |  | Yes
18458 | x | x | x |  | 2022-03-01 | Mar | 3 | 2022 | 74250 |  |  | 123036512 | Placer | Northern | Sierra | North | Rocklin | Yes | Stronghold Engineering damaged a 1 1/4" gas service line with a backhoe while doing building construction work. No USA ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Building Construction | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Stronghold Engineering | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-01 | 1 ¼” | 34 | 15 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 3 | Mar | 2022 |  |  | No
18456 | x | x | x |  | 2022-03-01 | Mar | 3 | 2022 | 74258 |  | 45194017 | 123037081 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a post-hole digger while fixing the railing on a deck. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Other | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-01 | ½” | 18 | 68 | Excavator Did Not Believe a USA Ticket was Required | 3 | Mar | 2022 |  |  | Yes
18467 | x | x | x |  | 2022-03-02 | Mar | 3 | 2022 | 74319 |  |  | 123043648 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Utility Construction Services damaged a 1 1/4" plastic gas service line with a mini-excavator while performing electric work for PG&E Electric. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Electric Work | Incorrect Facility Records / Maps | Yes | X204703198 | Dig-In to PG&E Underground | 2nd Party-Contractor | Utility Construction Services | Distribution Service |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Orange | PG&E GC Electric |  |  | 2nd Party Gas | Yes | 2022-03-02 | 1 ¼” | 49 | 36 | N/A | 3 | Mar | 2022 |  |  | No
18466 | x | x | x |  | 2022-03-02 | Mar | 3 | 2022 | 74316 |  | 45196003 | 123043868 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | Soleeva Energy Inc. damaged a 1/2" plastic gas service line with a pickaxe while installing conduit for a new electric/solar system. No USA ticket. | No | Gas Line | Yes | Pickaxe | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Soleeva Energy Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-02 | ½” | 36 | 24 | Excavator Did Not Believe a USA Ticket was Required | 3 | Mar | 2022 |  |  | Yes
18465 | x | x | x |  | 2022-03-02 | Mar | 3 | 2022 | 74310 |  | 45195911 | 123043374 | Shasta | Northern | North Valley | North | Redding | Yes | Horizon Electric damaged a 1" plastic gas service line with a sledgehammer while installing a grounding rod. No USA ticket. | No | Gas Line | Yes | Other Hand Tools | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Horizon Electric | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-02 | 1” | 45 | 46 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18464 | x | x | x |  | 2022-03-02 | Mar | 3 | 2022 | 74303 |  |  | 123042403 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Aztecs A J Landscape damaged a 1/2" plastic gas service line with a shovel while installing a drainage pipe. Valid USA ticket. Excavated prior to legal excavation start date and time | No | Gas Line | No | Shovel | Drainage Work | Excavated prior to legal excavation start date and time | Yes | X205700293 | Dig-In to PG&E Underground | 3rd Party-Contractor | Aztecs A.J | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-02 | ½” | 18 |  | N/A | 3 | Mar | 2022 |  |  | Yes
18463 | x | x | x |  | 2022-03-02 | Mar | 3 | 2022 | 74335 |  |  | 123045436 | Santa Clara | Central Coast | San Jose | Central | Gilroy | Yes | Del Toro Roll Off & Disposal Service damaged a 3/4" steel gas service line with a skid steer while clearing a field of debris. No USA ticket. | No | Gas Line | Yes | Skid Steer | Site Development | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Del Toro Roll Off & Disposal Service | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-02 | ¾” | 24 | 136 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 3 | Mar | 2022 |  |  | No
18462 | x | x |  |  | 2022-03-02 | Mar | 3 | 2022 | 74326 |  |  |  | Marin | Bay Area | North Bay | North | Corte Madera | Yes | Homeowner damaged the wrap on 3/4" steel gas service line with a shovel while building a play structure. No USA ticket. | Yes | Gas Line | No | Shovel | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-02 | ¾” | 18 | 0 | Knew About USA Ticket Requirement But Chose Not to Call | 3 | Mar | 2022 |  |  | Yes
18472 | x | x | x |  | 2022-03-03 | Mar | 3 | 2022 | 74372 |  |  | 123049654 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | San Francisco Department of Public Works damaged a 1/2" plastic gas service line with a shovel while installing a sewer lateral. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | X203401801 | Dig-In to PG&E Underground | 3rd Party-Government Entity | San Francisco Department of Public Works | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-03-03 | ½” | 25 | 43 | N/A | 3 | Mar | 2022 |  |  | Yes
18471 | x | x | x |  | 2022-03-03 | Mar | 3 | 2022 | 74384 |  | 45197370 | 123049801 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a shovel while installing a new water line. No USA ticket. | No | Gas Line | Yes | Shovel | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-03 | ½” | 18 | 7 | Knew About USA Ticket Requirement But Chose Not to Call | 3 | Mar | 2022 |  |  | Yes
18470 | x | x |  |  | 2022-03-03 | Mar | 3 | 2022 | 74385 |  |  |  | Contra Costa | Bay Area | East Bay | Central | Rodeo | Yes | L R Gomez Construction damaged a 1/2" plastic gas service line with an excavator while removing a tree stump. Expired USA ticket. Primary cause was failed to expose with hand tools | No | Gas Line | Yes | Excavator | Tree Removal/Stump Grinding | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No (expired) | X126600242 | Dig-In to PG&E Underground | 3rd Party-Contractor | L R Gomez Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-03 | ½” | 24 | 22 | Expired USA ticket | 3 | Mar | 2022 |  |  | No
18477 | x | x | x |  | 2022-03-04 | Mar | 3 | 2022 | 74396 |  |  | 123053728 | Contra Costa | Bay Area | Diablo | South | Orinda | Yes | Aaron Chapman Builders damaged a 1/2" plastic gas service line with a jackhammer while excavating a post hole. No USA ticket. | No | Gas Line | Yes | Jackhammer | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Aaron Chapman Builders | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-04 | ½” | 18 | 59 | Excavator Did Not Believe a USA Ticket was Required | 3 | Mar | 2022 |  |  | No
18476 | x | x | x |  | 2022-03-04 | Mar | 3 | 2022 | 74419 |  | 45198289 | 123053723 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Fantastic Rooter damaged a 3/4" steel gas service line with a sawzall while installing a water line. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Cutting Machine | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X206100265 | Dig-In to PG&E Underground | 3rd Party-Contractor | Fantastic Rooter | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-04 | ¾” | 24 | 33 | N/A | 3 | Mar | 2022 |  |  | No
18475 | x | x | x |  | 2022-03-04 | Mar | 3 | 2022 | 74427 |  | 45198584 | 123054431 | Alameda | Central Coast | Mission | South | Hayward | Yes | F. Lunas Construction damaged a 1/2" plastic gas service line with a shovel while doing a sewer line extension. Valid USA ticket. Failed to dig with care | No | Gas Line | No | Shovel | Sewer | Failed to Dig with Care | Yes | X202701074 | Dig-In to PG&E Underground | 3rd Party-Contractor | F. Lunas Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-04 | ½” | 28 | 15 | N/A | 3 | Mar | 2022 |  |  | Yes
18474 | x | x | x |  | 2022-03-04 | Mar | 3 | 2022 | 74421 |  |  | 123053062 | Monterey | Central Coast | Central Coast | South | Salinas | Yes | Cal Green Construction damaged a 1/2" plastic gas service line with an unknown tool while replacing water lines. No USA ticket. Please see DIRT documents for details on what occurred | No | Gas Line | No | Unknown | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Cal Green Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-04 | ½” |  | 30 | Other | 3 | Mar | 2022 |  |  | No
18473 | x | x | x |  | 2022-03-04 | Mar | 3 | 2022 | 74430 |  |  | 123054925 | Fresno | Central Valley | Fresno | South | Sanger | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while replacing a fence post. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-04 | ½” | 20 | 48 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18482 | x | x | x |  | 2022-03-05 | Mar | 3 | 2022 | 74449 |  | 45198865 | 123055758 | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Homeowner damaged a 1" plastic gas service line inserted into 1 1/4" steel with a shovel while constructing a pedestrian walkway. No USA ticket. | No | Gas Line | Yes | Shovel | Curb/Sidewalk Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-05 | 1” | 16 | 23 | Believed They Knew Where Underground Utility was From Previous Knowledge | 3 | Mar | 2022 |  |  | Yes
18481 | x | x | x |  | 2022-03-05 | Mar | 3 | 2022 | 74457 |  |  | 123056067 | San Mateo | Central Coast | Peninsula | Central | San Bruno | Yes | Kingdom Pipelines Inc. damaged a 1 1/4" plastic gas service line with a excavator while doing water line installations. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Excavator | Water | Facility was not located or marked | Yes | X201902262 | Dig-In to PG&E Underground | 3rd Party-Contractor | Kingdom Pipeline, Inc. | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-05 | 1 ¼” | 45 | 40 | N/A | 3 | Mar | 2022 | Bargaining Unit |  | No
18480 | x | x | x |  | 2022-03-05 | Mar | 3 | 2022 | 74455 |  | 45198866 | 123056056 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a shovel while installing irrigation pipes. No USA ticket. Primary root cause was failure to protect exposed facility | No | Gas Line | Yes | Shovel | Irrigation | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-05 | ½” | 20 | 36 | Knew About USA Ticket Requirement But Chose Not to Call | 3 | Mar | 2022 |  |  | Yes
18479 | x | x | x |  | 2022-03-05 | Mar | 3 | 2022 | 74450 |  | 45198864 | 123055667 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while installing new fence posts. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-05 | ½” | 19 | 10 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18483 | x | x | x |  | 2022-03-06 | Mar | 3 | 2022 | 74468 |  | 45198969 | 123056441 | Mendocino | Northern | Humboldt | North | Willits | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while excavating for new fence posts. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-06 | ½” | 24 | 115 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18491 | x | x | x |  | 2022-03-07 | Mar | 3 | 2022 | 74518 |  |  | 123059997 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | The Developer damaged a 1/2" plastic gas service line with a pickaxe while doing driveway widening. Contractor was using homeowners USA ticket and did not have one of their own. Primary cause of incident is failed to dig with care | No | Gas Line | Yes | Pickaxe | Driveway Work | Failed to Dig with Care | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | The Developer | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-07 | ½” | 16 | 27 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 3 | Mar | 2022 |  |  | Yes
18490 | x | x | x |  | 2022-03-07 | Mar | 3 | 2022 | 74490 |  | 45199457 | 123057800 | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a shovel while installing a new retaining wall. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-07 | ½” | 24 | 26 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18489 | x | x | x |  | 2022-03-07 | Mar | 3 | 2022 | 74484 |  |  | 123057777 | Contra Costa | Bay Area | Diablo | South | Orinda | Yes | Golden Star Construction damaged a 1/2" plastic gas service line with a shovel while repairing a retaining wall. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Golden Star Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-07 | ½” | 18 | 27 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18488 | x | x | x |  | 2022-03-07 | Mar | 3 | 2022 | 74536 |  | 45200515 | 123061254 | San Joaquin | Central Valley | Stockton | South | Acampo | Yes | PG&E Electric damaged a 1" plastic gas main with a shovel while doing electric repairs. No USA ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Electric | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Blue | PG&E Division Electric |  |  | 1st Party Gas | Yes | 2022-03-07 | 1” | 42 | 99 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 3 | Mar | 2022 |  |  | Yes
18487 | x | x | x |  | 2022-03-07 | Mar | 3 | 2022 | 74517 |  |  | 123084533 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | PG&E Gas damaged a 4" steel gas main inserted into 8" steel casing with a backhoe mounted breaking hammer while exposing and identifying the 4" main. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X205000033 | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Gas | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Blue | PG&E Division Gas |  |  | 1st Party Gas | Yes | 2022-03-07 | 4" | 29 | 129 | N/A | 3 | Mar | 2022 |  |  | No
18486 | x | x | x |  | 2022-03-07 | Mar | 3 | 2022 | 74485 |  | 45199559 | 123059176 | Solano | Northern | Vacaville | North | Dixon | Yes | Munoz Landscapes damaged a 1" plastic gas service line with a trencher while trenching for irrigation lines. No USA ticket. There were existing marks for another contractor that were correct so primary root cause is failure to expose facility with hand tools | No | Gas Line | Yes | Trencher | Irrigation | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Munoz Landscapes | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-07 | 1” | 2 | 22 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 3 | Mar | 2022 |  |  | No
18484 | x | x |  |  | 2022-03-07 | Mar | 3 | 2022 | 74515 |  |  |  | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | Matthews Concrete damaged a 3/4" steel gas service line with a skid steer while replacing a driveway. No USA ticket. | No | Gas Line | No | Skid Steer | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Matthews Concrete | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-07 | ¾” | 24 |  | Knew About USA Ticket Requirement But Chose Not to Call | 3 | Mar | 2022 |  |  | No
18502 | x | x | x |  | 2022-03-08 | Mar | 3 | 2022 | 74574 |  | 45201700 | 123064038 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Unlicensed Contractor damaged a 1" plastic gas service line with a jackhammer while repairing landscape irrigation. No USA ticket. | No | Gas Line | Yes | Jackhammer | Irrigation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-08 | 1” | 25 | 50 | Excavator Did Not Believe a USA Ticket was Required | 3 | Mar | 2022 |  |  | No
18501 | x | x | x |  | 2022-03-08 | Mar | 3 | 2022 | 74587 |  | 45201927 | 123066590 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Garney Pacific, Inc damaged a 1/2" plastic gas service line with an excavator while installing a water main. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X204200479 | Dig-In to PG&E Underground | 3rd Party-Contractor | Garney Pacific, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-08 | ½” | 44 | 8 | N/A | 3 | Mar | 2022 |  |  | No
18500 | x | x | x |  | 2022-03-08 | Mar | 3 | 2022 | 74577 |  | 45201114 | 123064253 | Stanislaus | Central Valley | Yosemite | South | Turlock | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while removing tree roots. No USA ticket. | No | Gas Line | Yes | Shovel | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-08 | ½” | 30 | 19 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18499 | x | x | x |  | 2022-03-08 | Mar | 3 | 2022 | 74557 |  |  | 123084826 | Contra Costa | Bay Area | Diablo | South | Oakley | Yes | G&S Paving, Inc. damaged a 1/2" plastic gas service line with a shovel while removing a tree stump. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Tree Removal/Stump Grinding | Failed to Dig with Care | Yes | X206101602 | Dig-In to PG&E Underground | 3rd Party-Contractor | G&S Paving, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-08 | ½” | 20 | 31 | N/A | 3 | Mar | 2022 |  |  | Yes
18498 | x | x | x |  | 2022-03-08 | Mar | 3 | 2022 | 74568 |  |  | 123063651 | Contra Costa | Bay Area | Diablo | South | Orinda | Yes | Sewer Works damaged a 3/4" steel gas service line with an excavator while installing a new sewer lateral. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Sewer | Incorrect Facility Records / Maps | Yes | X206001001 | Dig-In to PG&E Underground | 3rd Party-Contractor | Sewer Works Inc. | Distribution Service |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-08 | ¾” | 36 | 174 | N/A | 3 | Mar | 2022 |  |  | No
18497 | x | x | x |  | 2022-03-08 | Mar | 3 | 2022 | 74542 |  | 45200978 | 123062190 | Alameda | Bay Area | East Bay | Central | Alameda | Yes | ARB Inc damaged a 1 1/4" plastic gas main with a sharp shooter shovel while excavating for gas main replacement. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | X204502554 | Dig-In to PG&E Underground | 2nd Party-Contractor | ARB Inc | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-03-08 | 1 ¼” | 29 | 41 | N/A | 3 | Mar | 2022 |  |  | Yes
18496 | x | x |  |  | 2022-03-08 | Mar | 3 | 2022 | 74583 |  |  |  | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Homeowner damaged the wrap on a 3/4 inch steel gas service line with a shovel while doing sewer repair. No USA ticket. | Yes | Gas Line | No | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-08 | ¾” | 24 | 0 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18495 | x | x | x |  | 2022-03-08 | Mar | 3 | 2022 | 74592 |  |  | 123069077 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | San Francisco Water Department (SFWD) damaged a 2" plastic gas main with a backhoe while excavating near the water main. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X206701069 | Dig-In to PG&E Underground | 3rd Party-Government Entity | San Francisco Water Department | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-03-08 | 2” | 21 | 65 | N/A | 3 | Mar | 2022 |  |  | No
18494 | x | x | x |  | 2022-03-08 | Mar | 3 | 2022 | 74569 |  | 45203623 | 123071696 | Alameda | Central Coast | Mission | South | Castro Valley | Yes | United Constructors Inc damaged a 1/2" plastic gas service line with a skid steer while clearing an area for development. No USA ticket. | No | Gas Line | Yes | Skid Steer | Site Development | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | United Constructors Inc | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-08 | ½” | 12 | 14 | Knew About USA Ticket Requirement But Chose Not to Call | 3 | Mar | 2022 |  |  | No
18493 | x | x | x |  | 2022-03-08 | Mar | 3 | 2022 | 74570 |  |  | 123068993 | Butte | Northern | North Valley | North | Oroville | Yes | PG&E Gas damaged a 2" steel gas main with a backhoe while doing gas work. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X204800533 | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Gas | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Blue | PG&E Division Gas |  |  | 1st Party Gas | Yes | 2022-03-08 | 2” | 15 | 75 | N/A | 3 | Mar | 2022 |  |  | No
18492 | x | x | x |  | 2022-03-08 | Mar | 3 | 2022 | 74585 |  |  | 123066333 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Ongaro And Sons Plumbing damaged a 3/4" steel gas main with a digging bar while installing water lines. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Digging Bar | Water | Failed to Dig with Care | Yes | W135600143 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ongaro And Sons Plumbing | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-08 | ¾” | 4 | 59 | N/A | 3 | Mar | 2022 |  |  | Yes
18508 | x | x | x |  | 2022-03-09 | Mar | 3 | 2022 | 74611 |  |  | 123071560 | Fresno | Central Valley | Fresno | South | Clovis | Yes | 559 Pro Landscaping damaged a 1/2" plastic gas service line with a post-hole digger while installing fencing. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Post-Hole Digger | Fencing | Failed to Dig with Care | Yes | W205400080 | Dig-In to PG&E Underground | 3rd Party-Contractor | 559 Pro Landscaping | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-09 | ½” | 34 | 70 | N/A | 3 | Mar | 2022 |  |  | Yes
18506 | x | x | x |  | 2022-03-09 | Mar | 3 | 2022 | 74643 |  | 45204020 | 123074115 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while installing new fencing. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-09 | ½” | 22 | 22 | Excavator Did Not Believe a USA Ticket was Required | 3 | Mar | 2022 |  |  | Yes
18505 | x | x | x |  | 2022-03-09 | Mar | 3 | 2022 | 74642 |  |  | 123073906 | Contra Costa | Bay Area | Diablo | South | Concord | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-09 | ½” | 18 | 20 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 3 | Mar | 2022 |  |  | Yes
18504 | x | x | x |  | 2022-03-09 | Mar | 3 | 2022 | 74634 |  |  | 123072923 | San Joaquin | Central Valley | Stockton | South | Lodi | Yes | INTREN, LLC. damaged a 2" steel gas main with a auger while replacing a power pole. Valid USA ticket. Failed to maintain marks | No | Gas Line | Yes | Auger | Pole/Post Installation | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | X206301351 | Dig-In to PG&E Underground | 2nd Party-Contractor | Intren | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Orange | PG&E Division Electric |  |  | 2nd Party Gas | Yes | 2022-03-09 | 2” | 64 | 191 | N/A | 3 | Mar | 2022 |  |  | No
18503 | x | x | x |  | 2022-03-09 | Mar | 3 | 2022 | 74629 |  | 35332260 | 123073186 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Rolfe Construction Co damaged a 3/4" steel gas service line with an excavator while installing a new sewer line. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Excavator | Sewer | Facility was not located or marked | Yes | X204002177 | Dig-In to PG&E Underground | 3rd Party-Contractor | Rolfe Construction Company | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-09 | ¾” | 21 | 38 | N/A | 3 | Mar | 2022 | Bargaining Unit |  | No
18515 |  | x |  |  | 2022-03-10 | Mar | 3 | 2022 | 74665 |  |  | 123085867 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Homeowner damaged 1'plastic gas service line with a digging bar while building a hand rail for the front stairs of the residence. No USA ticket. | No | Gas Line | Yes | Digging Bar | Other | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-10 | 1” | 20 | 67 | Knew About USA Ticket Requirement But Chose Not to Call | 3 | Mar | 2022 |  |  | Yes
18513 | x | x | x |  | 2022-03-10 | Mar | 3 | 2022 | 74679 |  |  | 123086859 | San Joaquin | Central Valley | Stockton | South | Tracy | Yes | Dream Home Builders damaged a 1/2" plastic gas service line with a shovel while trenching to install electrical conduit. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | X206802810 | Dig-In to PG&E Underground | 3rd Party-Contractor | Dream Home Builders | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-10 | ½” | 36 | 85 | N/A | 3 | Mar | 2022 |  |  | Yes
18512 | x | x | x |  | 2022-03-10 | Mar | 3 | 2022 | 74676 |  |  | 123086677 | San Joaquin | Central Valley | Stockton | South | Lodi | Yes | JAG Concrete Inc. damaged a 1/2" plastic gas service line with a shovel while creating a trench for the installation of gas pipes. No USA ticket. | No | Gas Line | Yes | Shovel | Gas | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | JAG Concrete Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-10 | ½” | 30 | 34 | Believed They Knew Where Underground Utility was From Previous Knowledge | 3 | Mar | 2022 |  |  | Yes
18511 | x | x | x |  | 2022-03-10 | Mar | 3 | 2022 | 74664 |  | 45208404 | 123085599 | Alameda | Central Coast | Mission | South | Livermore | Yes | MCH Electric damaged a 1 1/4" plastic gas service line with a backhoe while re-routing electric conduit. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W015400087 | Dig-In to PG&E Underground | 3rd Party-Contractor | MCH Electric | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-10 | 1 ¼” | 30 | 45 | N/A | 3 | Mar | 2022 |  |  | No
18510 | x | x | x |  | 2022-03-10 | Mar | 3 | 2022 | 74662 |  |  | 123087979 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | City of San Jose damaged a 1/2" plastic gas service line with a backhoe while repairing a sewer lateral. Valid USA ticket. Failed to maintain marks | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | X204201553 | Dig-In to PG&E Underground | 3rd Party-Government Entity | City of San Jose | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-03-10 | ½” | 42 | 28 | N/A | 3 | Mar | 2022 |  |  | No
18509 | x | x | x |  | 2022-03-10 | Mar | 3 | 2022 | 74686 |  |  | 123090096 | Yuba | Northern | Sierra | North | Marysville | Yes | Lamont construction damaged a 1' plastic gas service line with a backhoe while excavating a trench (doing curb/sidewalk work). Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Backhoe/Trackhoe | Curb/Sidewalk Work | Facility was not located or marked | Yes | X205403087 | Dig-In to PG&E Underground | 3rd Party-Contractor | Lamont Construction | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-10 | 1” | 28 | 8 | N/A | 3 | Mar | 2022 | Bargaining Unit |  | No
18521 | x | x | x |  | 2022-03-11 | Mar | 3 | 2022 | 74722 |  |  | 123092191 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Martin General Engineering damaged a 1/2" plastic gas service line with a mini-excavator for a storm drain install. Valid USA ticket. PG&E at-fault - Other Error - Construction Error | No | Gas Line | Yes | Excavator | Drainage Work | Incorrect information or marks | Yes | X202501719 | Dig-In to PG&E Underground | 3rd Party-Contractor | Martin General Engineering | Distribution Service |  | Yes | Other Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-11 | ½” | 46 | 55 | N/A | 3 | Mar | 2022 |  |  | No
18520 | x | x | x |  | 2022-03-11 | Mar | 3 | 2022 | 74724 |  |  | 123092117 | Butte | Northern | North Valley | North | Paradise | Yes | C & C Utility Inc. damaged a 1" plastic gas service line with an excavator while excavating a trench for a new electric facility. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Electric Work | Incorrect Facility Records / Maps | Yes | X132101187 | Dig-In to PG&E Underground | 2nd Party-Contractor | C & C Utility Inc. | Distribution Service |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Orange | PG&E GC Electric |  |  | 2nd Party Gas | Yes | 2022-03-11 | 1” | 65 | 15 | N/A | 3 | Mar | 2022 |  |  | No
18519 | x | x | x |  | 2022-03-11 | Mar | 3 | 2022 | 74715 |  |  | 123091811 | Yuba | Northern | Sierra | North | Marysville | Yes | St Francis Electric damaged a 1/2" plastic gas service line with a shovel while potholing for line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | X205501027 | Dig-In to PG&E Underground | 3rd Party-Contractor | St Francis Electric Inc | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-11 | ½” | 14 | 14 | N/A | 3 | Mar | 2022 |  |  | Yes
18518 | x | x | x |  | 2022-03-11 | Mar | 3 | 2022 | 74725 |  |  | 123092557 | Sacramento | Northern | Sacramento | North | Orangevale | Yes | Zentner Construction damaged a 1/2" plastic gas service line with a shovel while exposing the facility. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Water | Failed to Dig with Care | Yes | W206600306 | Dig-In to PG&E Underground | 3rd Party-Contractor | Zentner Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-11 | ½” | 18 | 21 | N/A | 3 | Mar | 2022 |  |  | Yes
18523 | x | x | x |  | 2022-03-12 | Mar | 3 | 2022 | 74744 |  |  | 123094521 | San Mateo | Central Coast | Peninsula | Central | Burlingame | Yes | Unlicensed Contractor damaged 3/4" steel gas service line with a skid steer while doing landscaping. No USA ticket. | No | Gas Line | Yes | Skid Steer | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-12 | ¾” | 12 | 51 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | No
18522 | x | x | x |  | 2022-03-12 | Mar | 3 | 2022 | 74748 |  |  | 123095270 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | Sun run damaged 3/4" steel gas service line with a hand drill while installing a grounding rod. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Drilling Equipment | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X206803526 | Dig-In to PG&E Underground | 3rd Party-Contractor | Sun Run | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-12 | ¾” | 28 | 205 | N/A | 3 | Mar | 2022 |  |  | No
18525 | x | x | x |  | 2022-03-13 | Mar | 3 | 2022 | 74757 |  |  | 123095642 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Homeowner damaged a 1 1/4" plastic gas service line with a mini-excavator while doing a water line repair. No USA ticket. | No | Gas Line | Yes | Excavator | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-13 | 1 ¼” | 36 | 5 | Excavator Did Not Believe a USA Ticket was Required | 3 | Mar | 2022 |  |  | No
18524 | x | x | x |  | 2022-03-13 | Mar | 3 | 2022 | 74763 |  |  | 123100958 | Monterey | Central Coast | Central Coast | South | Carmel | Yes | Unlicensed Contractor damaged a 1" plastic gas service line with a shovel while removing fence posts. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-13 | 1” | 15 | 9 | Knew About USA Ticket Requirement But Chose Not to Call | 3 | Mar | 2022 |  |  | Yes
18534 | x | x | x |  | 2022-03-14 | Mar | 3 | 2022 | 74793 |  |  | 123097549 | Kern | Central Valley | Kern | South | Bakersfield | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while removing a tree stump. No USA ticket. | No | Gas Line | Yes | Shovel | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-14 | ½” | 16 | 31 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18533 | x | x | x |  | 2022-03-14 | Mar | 3 | 2022 | 74807 |  |  | 123098915 | Contra Costa | Bay Area | Diablo | South | Oakley | Yes | Sanco Pipelines damaged a 1/2" plastic gas service line inserted into 3/4" steel with a excavator while installing a new sewer main. Valid USA ticket. Failed to protect subsurface installation | No | Gas Line | Yes | Excavator | Sewer | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X202801653 | Dig-In to PG&E Underground | 3rd Party-Contractor | Sanco Pipelines | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-14 | ½” | 24 | 49 | N/A | 3 | Mar | 2022 |  |  | No
18531 | x | x |  |  | 2022-03-14 | Mar | 3 | 2022 | 74792 |  |  |  | Sacramento | Northern | Sacramento | North | Carmichael | Yes | JT Utility Services Inc. damaged a 3/4" steel gas service line with a mini-excavator while installing a telecommunication vault. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Telecommunications | Incorrect Facility Records / Maps | Yes | X204800264 | Dig-In to PG&E Underground | 3rd Party-Contractor | JT Utility Services Inc. | Distribution Service |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-14 | ¾” | 14 | 50 | N/A | 3 | Mar | 2022 |  |  | No
18530 | x | x | x |  | 2022-03-14 | Mar | 3 | 2022 | 74801 |  |  | 123097597 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | R&R Pacific Construction damaged a 2" plastic gas main with an auger for street light installation. Valid USA ticket. Failed to maintain marks | No | Gas Line | Yes | Auger | Street Light Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | X201702534 | Dig-In to PG&E Underground | 3rd Party-Contractor | R&R Pacific Construction | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-14 | 2” | 46 | 57 | N/A | 3 | Mar | 2022 |  |  | No
18529 | x | x | x |  | 2022-03-14 | Mar | 3 | 2022 | 74810 |  |  | 123098426 | Sonoma | Northern | Sonoma | North | Healdsburg | Yes | Homeowners tenant damaged a 1 1/4" plastic gas main with a mini-excavator while installing a driveway. Homeowner knew about ticket requirement but did not tell tenant. No USA ticket. | No | Gas Line | Yes | Excavator | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-14 | 1 ¼” | 24 | 89 | Knew About USA Ticket Requirement But Chose Not to Call | 3 | Mar | 2022 |  |  | No
18527 | x | x | x |  | 2022-03-14 | Mar | 3 | 2022 | 74822 |  |  | 123099659 | Yolo | Northern | Vacaville | North | Woodland | Yes | Unlicensed Contractor damaged a 1" plastic gas service line inserted into 1 1/4" plastic with a digging bar while installing a fence post. No USA ticket. | No | Gas Line | Yes | Digging Bar | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-14 | 1” | 12 | 72 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18526 | x | x | x |  | 2022-03-14 | Mar | 3 | 2022 | 74777 |  |  | 123096605 | San Mateo | Central Coast | Peninsula | Central | Pacifica | Yes | City of Pacifica Sewer Department damaged a 1/2" plastic gas service line with a steel probe while attempting to locate a sewer cleanout. No USA ticket. | No | Gas Line | Yes | Probing Tool | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Government Entity | City of Pacifica Sewer Department | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-03-14 | ½” | 24 | 34 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 3 | Mar | 2022 |  |  | Yes
18540 | x | x | x |  | 2022-03-15 | Mar | 3 | 2022 | 74838 |  |  | 123102465 | Kern | Central Valley | Kern | South | Bakersfield | Yes | Pacific Irrigation damaged a 1/2" plastic gas service line with a mini-excavator while doing a water valve replacement. No USA ticket. | No | Gas Line | Yes | Excavator | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Pacific Irrigation | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-15 | ½” | 33 | 15 | Believed They Knew Where Underground Utility was From Previous Knowledge | 3 | Mar | 2022 |  |  | No
18539 | x | x |  |  | 2022-03-15 | Mar | 3 | 2022 | 74853 |  |  |  | Butte | Northern | North Valley | North | Chico | Yes | Cantalupo Construction damaged the wrap on 3/4" steel gas service line with a shovel while connecting electrical conduit to a new building. No USA ticket. | Yes | Gas Line | No | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Cantalupo Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-15 | ¾” | 12 | 0 | Excavator Did Not Believe a USA Ticket was Required | 3 | Mar | 2022 |  |  | Yes
18538 | x |  |  |  | 2022-03-15 | Mar | 3 | 2022 | 74844 |  |  |  | Monterey | Central Coast | Central Coast | South | Carmel | Yes | MGE Underground damaged the wrap on a 3/4" steel gas service line with hydro vac equipment doing unknown work. No USA ticket. Inadequate excavation practices | Yes | Gas Line | No | Vacuum Equipment | Unknown | Inadequate Excavation Practices | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | MGE Underground | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-15 | ¾” |  | 0 | Other | 3 | Mar | 2022 |  |  | No
18537 | x | x | x |  | 2022-03-15 | Mar | 3 | 2022 | 74839 |  |  | 123102880 | Contra Costa | Bay Area | East Bay | Central | Richmond | Yes | Pacific Directional Boring damaged a 1/2" plastic gas service line with boring equipment while excavating for future conduit. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Boring Equipment | Other | Facility was not located or marked | Yes | X206203144 | Dig-In to PG&E Underground | 3rd Party-Contractor | Precision Directional Boring | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-15 | ½” | 38 | 58 | N/A | 3 | Mar | 2022 | Bargaining Unit |  | No
18536 | x | x | x |  | 2022-03-15 | Mar | 3 | 2022 | 74832 |  |  | 123102594 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Timberworks Construction Services damaged a 1" plastic gas service line with a probe while trying to locate a water main. No USA ticket. | No | Gas Line | Yes | Probing Tool | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Timberworks Construction Services | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-15 | 1” | 29 | 82 | Believed They Knew Where Underground Utility was From Previous Knowledge | 3 | Mar | 2022 |  |  | Yes
18535 | x | x | x |  | 2022-03-15 | Mar | 3 | 2022 | 74833 |  |  | 123102148 | San Joaquin | Central Valley | Stockton | South | Lathrop | Yes | PG&E Gas damaged a 1/2" plastic gas service line with a probe while identifying and locating subsurface installations. Valid USA ticket. Other error | No | Gas Line | Yes | Probing Tool | Gas | Other | No | N/A | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Gas | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Blue | Other |  |  | 1st Party Gas | Yes | 2022-03-15 | ½” | 24 | 80 | Other | 3 | Mar | 2022 |  |  | Yes
18549 | x | x | x |  | 2022-03-16 | Mar | 3 | 2022 | 74887 |  |  | 123109851 | Marin | Bay Area | North Bay | North | Novato | Yes | Empire Earthworks damaged a 4" plastic gas service line with boring equipment while installing fiber telecommunication lines. Expired USA ticket. Primary root cause was failed to expose facility with hand tools | No | Gas Line | Yes | Boring Equipment | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No (expired) | X201102376 & X201102350 | Dig-In to PG&E Underground | 3rd Party-Contractor | Empire Earthworks HDD | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-16 | 4" | 42 | 94 | Expired USA ticket | 3 | Mar | 2022 |  |  | No
18548 | x | x | x |  | 2022-03-16 | Mar | 3 | 2022 | 74870 |  |  | 123106715 | Monterey | Central Coast | Central Coast | South | King City | Yes | Swift Tectonics damaged a 4" plastic gas main with an excavator while installing a water main. Expired USA ticket. Primary cause was failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No (expired) | X120803406/X114000717 | Dig-In to PG&E Underground | 3rd Party-Contractor | Swift Tectonics | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-16 | 4" | 22 | 58 | Expired USA ticket | 3 | Mar | 2022 |  |  | No
18547 | x | x | x |  | 2022-03-16 | Mar | 3 | 2022 | 74902 |  |  | 123109353 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | CBF Inc. damaged a 1" plastic gas service line with a reciprocating saw while installing electrical conduit. Valid USA ticket. Failed to protect an exposed facility | No | Gas Line | Yes | Cutting Machine | Electric Work | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | CBF Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-16 | 1” | 24 | 12 | Other | 3 | Mar | 2022 |  |  | No
18546 | x | x | x |  | 2022-03-16 | Mar | 3 | 2022 | 74901 |  |  | 123109152 | Fresno | Central Valley | Fresno | South | Fresno | Yes | A Marc of Excellence damaged a 1" plastic gas service line with a mini-excavator while installing electric facilities. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Electric Work | Incorrect Facility Records / Maps | Yes | X204900250 | Dig-In to PG&E Underground | 3rd Party-Contractor | A Marc of Excellence Construction | Distribution Service |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-16 | 1” | 18 | 27 | N/A | 3 | Mar | 2022 |  |  | No
18545 | x | x |  |  | 2022-03-16 | Mar | 3 | 2022 | 74909 |  |  |  | Contra Costa | Bay Area | Diablo | South | Martinez | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while replacing a fence. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-16 | ½” | 24 | 32 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18544 | x | x | x |  | 2022-03-16 | Mar | 3 | 2022 | 74927 |  |  | 123111336 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while replacing a fence. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Fencing | Failed to Dig with Care | Yes | X206202803 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-16 | ½” | 36 | 29 | N/A | 3 | Mar | 2022 |  |  | Yes
18543 | x | x |  |  | 2022-03-16 | Mar | 3 | 2022 | 74889 |  |  |  | Contra Costa | Bay Area | Diablo | South | Lafayette | Yes | Juan Franco Construction damaged a 1/2" plastic gas service line with an excavator while doing site development. Valid USA ticket. PG&E at-fault - Wire Error | No | Gas Line | Yes | Excavator | Site Development | Locating Wire Missing or Broken | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Juan Franco Construction | Distribution Service |  | Yes | Wire Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-16 | ½” | 24 | 15 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 3 | Mar | 2022 |  |  | No
18542 | x | x | x |  | 2022-03-16 | Mar | 3 | 2022 | 74880 |  |  | 123112211 | Alameda | Central Coast | Mission | South | Hayward | Yes | MCH Electric damaged a 1" plastic gas service line with an excavator while rerouting electrical conduits. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W131300213 | Dig-In to PG&E Underground | 3rd Party-Contractor | MCH Electric | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-16 | 1 ¼” | 41 | 20 | N/A | 3 | Mar | 2022 |  |  | No
18541 | x | x | x |  | 2022-03-16 | Mar | 3 | 2022 | 74922 |  | 45218764 | 123150138 | Santa Clara | Central Coast | De Anza | Central | Saratoga | Yes | Lu Construction damaged a 1 1/4" steel gas main with a shovel while installing new utilities for an ADU. Expired USA ticket. Primary cause was failed to dig with care | No | Gas Line | Yes | Shovel | Building Construction | Failed to Dig with Care | No (expired) | W132600157 | Dig-In to PG&E Underground | 3rd Party-Contractor | Lu Construction | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-16 | 1 ¼” | 36 | 119 | Expired USA ticket | 3 | Mar | 2022 |  |  | Yes
18556 | x | x |  |  | 2022-03-17 | Mar | 3 | 2022 | 74944 |  |  |  | Monterey | Central Coast | Central Coast | South | King City | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a shovel while installing a driveway. No USA ticket. | No | Gas Line | Yes | Shovel | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-17 | ½” | 24 | 25 | Knew About USA Ticket Requirement But Chose Not to Call | 3 | Mar | 2022 |  |  | Yes
18555 | x | x |  |  | 2022-03-17 | Mar | 3 | 2022 | 74939 |  |  |  | Alameda | Bay Area | East Bay | Central | Alameda | Yes | J. H. Fitzmaurice Inc. damaged a 1 1/4" plastic gas main with a shovel while relocating a storm drain. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Drainage Work | Failed to Dig with Care | Yes | X130900771 | Dig-In to PG&E Underground | 3rd Party-Contractor | J. H. Fitzmaurice Inc. | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-17 | 1 ¼” | 20 | 97 | N/A | 3 | Mar | 2022 |  |  | Yes
18553 | x | x | x |  | 2022-03-17 | Mar | 3 | 2022 | 74980 |  |  | 123146191 | Monterey | Central Coast | Central Coast | South | Monterey | Yes | JC Macias Inc damaged a 1/2" plastic gas service line with a shovel while doing fencing work. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Fencing | Failed to Dig with Care | Yes | X205201547 | Dig-In to PG&E Underground | 3rd Party-Contractor | JC Macias Inc | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-17 | ½” | 6 | 19 | N/A | 3 | Mar | 2022 |  |  | Yes
18552 | x | x |  |  | 2022-03-17 | Mar | 3 | 2022 | 74935 |  |  |  | Santa Clara | Central Coast | San Jose | Central | Gilroy | Yes | Homeowner damaged 2" plastic gas service line (idle) with a pickaxe while doing unknown work. No USA ticket. | No | Gas Line | Yes | Pickaxe | Unknown | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-17 | 2” | 30 | 76 | Other | 3 | Mar | 2022 |  |  | Yes
18551 | x | x | x |  | 2022-03-17 | Mar | 3 | 2022 | 74956 |  |  | 123143986 | Santa Cruz | Central Coast | Central Coast | South | Scotts Valley | Yes | Homeowner damaged a 1/2" plastic gas service line with a digging bar while installing a new fence. No USA ticket. | No | Gas Line | Yes | Digging Bar | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-17 | ½” | 36 | 77 | Believed They Knew Where Underground Utility was From Previous Knowledge | 3 | Mar | 2022 |  |  | Yes
18550 | x | x | x |  | 2022-03-17 | Mar | 3 | 2022 | 74969 |  |  | 123145189 | Butte | Northern | North Valley | North | Chico | Yes | SEFNCO damaged a 1" plastic gas service line with a shovel while removing a blockage from a telecommunications conduit. No USA ticket. | No | Gas Line | Yes | Shovel | Telecommunications | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | SEFNCO | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-17 | 1” | 38 | 44 | Knew About USA Ticket Requirement But Chose Not to Call | 3 | Mar | 2022 |  |  | Yes
18560 | x | x | x |  | 2022-03-18 | Mar | 3 | 2022 | 74993 |  |  | 123149800 | Contra Costa | Bay Area | Diablo | South | Oakley | Yes | Evergreen Landscape Solutions, Inc. damaged a 3/4" steel gas service line with a trencher while installing new drainage lines. Valid USA ticket. Excavated prior to receiving a positive response from all utilities | No | Gas Line | Yes | Trencher | Drainage Work | Excavated Prior to Receiving a Positive Response From All Utilities | Yes | X207602891 | Dig-In to PG&E Underground | 3rd Party-Contractor | Evergreen Landscape | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-18 | ¾” | 24 | 30 | N/A | 3 | Mar | 2022 |  |  | No
18559 | x | x | x |  | 2022-03-18 | Mar | 3 | 2022 | 75035 |  |  | 123153874 | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | Onsite Commercial Services damaged a 1" plastic gas service line with boring equipment while installing new telecommunication conduit. Valid USA ticket. Failed to maintain clearance after verifying marks | No | Gas Line | No | Boring Equipment | Telecommunications | Excavator Failed to Maintain Clearance After Verifying Marks | Yes | X203401867 | Dig-In to PG&E Underground | 3rd Party-Contractor | On-Site Commercial Services | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-18 | 1" | 41 |  | N/A | 3 | Mar | 2022 |  |  | No
18558 | x | x | x |  | 2022-03-18 | Mar | 3 | 2022 | 75012 |  |  | 123151408 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Allstar Plumbing damaged a 1/2" plastic gas service line with a shovel while repairing a sewer line. No USA ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Allstar Plumbing | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-18 | ½” | 29 | 23 | Knew About USA Ticket Requirement But Chose Not to Call | 3 | Mar | 2022 |  |  | Yes
18561 | x | x | x |  | 2022-03-19 | Mar | 3 | 2022 | 75047 |  |  | 123155928 | Monterey | Central Coast | Central Coast | South | Seaside | Yes | Homeowner damaged a 1/2" plastic gas service line inserted into 3/4" copper with a skid steer while grading for dirt removal. No USA ticket. | No | Gas Line | Yes | Skid Steer | Blading/Lot Grading | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-19 | ½” | 24 | 150 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | No
18566 | x | x | x |  | 2022-03-21 | Mar | 3 | 2022 | 75106 |  |  | 123161439 | Monterey | Central Coast | Central Coast | South | Las Lomas | Yes | West Valley Construction damaged a 1/2" plastic gas service line with an excavator while excavating a water main. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Water | Incorrect Facility Records / Maps | Yes | W201300347 | Dig-In to PG&E Underground | 3rd Party-Contractor | West Valley Construction | Distribution Service |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-21 | ½” | 43 | 32 | N/A | 3 | Mar | 2022 |  |  | No
18565 | x | x | x |  | 2022-03-21 | Mar | 3 | 2022 | 75096 |  |  | 123160726 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | PG&E Gas damaged a 2" plastic gas main with a backhoe while installing new gas lines. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X207402672 | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Gas | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Blue | PG&E GDGC |  |  | 1st Party Gas | Yes | 2022-03-21 | 2” | 43 | 32 | N/A | 3 | Mar | 2022 |  |  | No
18564 | x | x | x |  | 2022-03-21 | Mar | 3 | 2022 | 75131 |  |  | 123163169 | Contra Costa | Bay Area | Diablo | South | Moraga | Yes | Cliff Swisher Custom Concrete, Inc. damaged a 1/2" plastic gas service line with an excavator while installing a landscape concrete patio. No USA ticket. | No | Gas Line | Yes | Excavator | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Cliff Swisher Custom Concrete Inc | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-21 | ½” | 18 | 60 | Excavator Did Not Believe a USA Ticket was Required | 3 | Mar | 2022 |  |  | No
18563 | x | x | x |  | 2022-03-21 | Mar | 3 | 2022 | 75112 |  |  | 123163154 | San Mateo | Central Coast | Peninsula | Central | Menlo Park | Yes | Casey Construction damaged a 3/4" steel gas service line with an excavator while doing a water main replacement. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Excavator | Water | Facility was not located or marked | Yes | X203501602 | Dig-In to PG&E Underground | 3rd Party-Contractor | Casey Construction | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-21 | ¾” | 36 | 29 | N/A | 3 | Mar | 2022 | Bargaining Unit |  | No
18575 | x | x |  |  | 2022-03-22 | Mar | 3 | 2022 | 75173 |  |  |  | Fresno | Central Valley | Fresno | South | Clovis | Yes | Jerry's Trenching Service damaged a 4" plastic gas main with a sharp shooter shovel while installing telecommunication cables. Valid USA ticket. Failed to dig with care | No | Gas Line | No | Shovel | Telecommunications | Failed to Dig with Care | Yes | X206001214 | Dig-In to PG&E Underground | 3rd Party-Contractor | Jerry's Trenching Service | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-22 | 4" | 29 |  | N/A | 3 | Mar | 2022 |  |  | Yes
18574 | x | x | x |  | 2022-03-22 | Mar | 3 | 2022 | 75155 |  |  | 123164911 | Solano | Bay Area | North Bay | North | Vallejo | Yes | Vino Contracting damaged a 3/4" steel gas service line with a sawzall while trying to remove a tree root as part of installing a new sewer line. Valid USA ticket. The tree root had grown completely around the gas pipe so there was nothing that could have been done to avoid the dig-in. | No | Gas Line | Yes | Cutting Machine | Sewer | Other | Yes | W207300126 | Dig-In to PG&E Underground | 3rd Party-Contractor | Vino Contracting | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-22 | ¾” | 24 | 88 | N/A | 3 | Mar | 2022 |  |  | No
18573 | x | x |  |  | 2022-03-22 | Mar | 3 | 2022 | 75182 |  |  |  | Sacramento | Northern | Sacramento | North | Fair Oaks | Yes | Sacramento Area Sewer District damaged a 1/2" plastic gas service line with a shovel while doing sewer line repair. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | X206902164 | Dig-In to PG&E Underground | 3rd Party-Government Entity | SMUD | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-03-22 | ½” | 48 | 31 | N/A | 3 | Mar | 2022 |  |  | Yes
18572 | x | x | x |  | 2022-03-22 | Mar | 3 | 2022 | 75195 |  | 45225237 | 123168797 | Shasta | Northern | North Valley | North | Redding | Yes | Homeowner damaged a 1/2" plastic gas service line with a backhoe while exposing a sewer line. No USA ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-22 | ½” | 26 | 30 | Believed They Knew Where Underground Utility was From Previous Knowledge | 3 | Mar | 2022 |  |  | No
18571 | x | x | x |  | 2022-03-22 | Mar | 3 | 2022 | 75150 |  |  | 123168082 | Contra Costa | Bay Area | Diablo | South | Oakley | Yes | Sanco Pipelines damaged a 1/2" plastic gas service line with an excavator while installing a new sewer lateral. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Sewer | Incorrect Facility Records / Maps | Yes | X202801653 | Dig-In to PG&E Underground | 3rd Party-Contractor | Sanco Pipelines | Distribution Service |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-22 | ½” | 40 | 31 | N/A | 3 | Mar | 2022 |  |  | No
18570 | x | x | x |  | 2022-03-22 | Mar | 3 | 2022 | 75180 |  |  | 123166923 | San Mateo | Central Coast | Peninsula | Central | San Mateo | Yes | All Fence damaged a 1/2" plastic gas service line with a post-hole digger while removing a fence post. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | All Fence Company | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-22 | ½” | 20 | 26 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 3 | Mar | 2022 |  |  | Yes
18569 | x | x | x |  | 2022-03-22 | Mar | 3 | 2022 | 75154 |  |  | 123166092 | Santa Clara | Central Coast | De Anza | Central | Monte Sereno | Yes | Marquez Landscape damaged a 1/2" plastic gas service line with a shovel while planting a tree. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Marquez Landscape | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-22 | ½” | 38 | 10 | Believed They Knew Where Underground Utility was From Previous Knowledge | 3 | Mar | 2022 |  |  | Yes
18568 | x | x |  |  | 2022-03-22 | Mar | 3 | 2022 | 75168 |  |  |  | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Discount Plumbing Rooter Inc. damaged a 1/2" plastic gas service line with a shovel while installing a new house trap. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | X207401358 | Dig-In to PG&E Underground | 3rd Party-Contractor | Discount Plumbing & Rooter | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-22 | ½” | 22 | 24 | N/A | 3 | Mar | 2022 |  |  | Yes
18584 | x | x | x |  | 2022-03-23 | Mar | 3 | 2022 | 75225 |  |  | 123172673 | Marin | Bay Area | North Bay | North | Novato | Yes | KJ Woods Construction damaged a 1/2" plastic gas service line with an excavator while installing a new sewer main. Valid USA ticket. PG&E at-fault - Wire Error | No | Gas Line | Yes | Excavator | Sewer | Locating Wire Missing or Broken | Yes | X202700303 | Dig-In to PG&E Underground | 3rd Party-Contractor | KJ Woods Construction | Distribution Service |  | Yes | Wire Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-23 | ½” | 42 | 20 | N/A | 3 | Mar | 2022 |  |  | No
18583 | x | x | x |  | 2022-03-23 | Mar | 3 | 2022 | 75211 |  |  | 123177273 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | AAA Concrete damaged a 1/2" plastic gas service line with a jackhammer while doing foundation work. No USA ticket. | No | Gas Line | Yes | Jackhammer | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | A A A Concrete | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-23 | ½” | 24 | 182 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 3 | Mar | 2022 |  |  | No
18582 | x | x | x |  | 2022-03-23 | Mar | 3 | 2022 | 75244 |  |  | 123173460 | Sacramento | Northern | Sacramento | North | Elk Grove | Yes | Rooter Hero damaged a 2" plastic gas main with boring equipment while doing a sewer line replacement. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Boring Equipment | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X208003169 | Dig-In to PG&E Underground | 3rd Party-Contractor | Rooter Hero | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-23 | 2” | 45 | 113 | N/A | 3 | Mar | 2022 |  |  | No
18581 | x | x | x |  | 2022-03-23 | Mar | 3 | 2022 | 75234 |  |  | 123173299 | Humboldt | Northern | Humboldt | North | Arcata | Yes | G R Sundberg Inc. damaged a 1" plastic gas service line with an excavator while installing a new sewer lateral. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Excavator | Sewer | Facility was not located or marked | Yes | X205901939 | Dig-In to PG&E Underground | 3rd Party-Contractor | G R Sundberg Inc. | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-23 | 1” | 30 | 49 | N/A | 3 | Mar | 2022 | Bargaining Unit |  | No
18579 | x | x | x |  | 2022-03-23 | Mar | 3 | 2022 | 75228 |  |  | 123172719 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Nerviani Paving damaged a 1" plastic gas service line with a shovel while removing a post as part of replacing a driveway. No USA ticket. | No | Gas Line | Yes | Shovel | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Nerviani Paving | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-23 | 1” | 20 | 50 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 3 | Mar | 2022 |  |  | Yes
18578 | x | x | x |  | 2022-03-23 | Mar | 3 | 2022 | 75218 |  |  | 123172006 | Contra Costa | Bay Area | Diablo | South | Concord | Yes | Fitzpatrick’s Landscaping, Fencing & Maintenance damaged a 1/2" plastic gas service line with a post-hole digger while digging a fence post hole. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Fitzpatrick’s Landscaping, Fencing & Maintenance | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-23 | ½” | 18 | 16 | Excavator Did Not Believe a USA Ticket was Required | 3 | Mar | 2022 |  |  | Yes
18577 | x | x | x |  | 2022-03-23 | Mar | 3 | 2022 | 75208 |  |  | 123172823 | Sacramento | Northern | Sacramento | North | Rancho Cordova | Yes | Anrak Corporation damaged a 3/4" steel gas service line with a pavement grinder in preparation for a repave. No USA ticket. | No | Gas Line | Yes | Other Driven Machinery | Road Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Anrak Corporation | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-23 | ¾” | 6 | 70 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 3 | Mar | 2022 |  |  | No
18576 | x | x | x |  | 2022-03-23 | Mar | 3 | 2022 | 75254 |  |  | 123176442 | San Mateo | Central Coast | Peninsula | Central | Burlingame | Yes | Homeowner damaged a 1/2" plastic gas service line with an unknown tool while digging a hole for a fence post. No USA ticket. | No | Gas Line | Yes | Unknown | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-23 | ½” | 18 | 11 | Other | 3 | Mar | 2022 |  |  | No
18589 | x |  | x |  | 2022-03-24 | Mar | 3 | 2022 | 75278 |  |  | 123179709 | San Joaquin | Central Valley | Stockton | South | Manteca | Yes | Golden State Utility damaged a 2" plastic gas main with a mini-excavator doing unknown work. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | No | Excavator | Unknown | Incorrect Facility Records / Maps | Yes | X203502375 | Dig-In to PG&E Underground | 3rd Party-Contractor | Golden State Utility | Distribution Main |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-24 | 2” |  |  | N/A | 3 | Mar | 2022 |  |  | No
18587 | x | x | x |  | 2022-03-24 | Mar | 3 | 2022 | 75299 |  |  | 123183861 | San Joaquin | Central Valley | Stockton | South | Stockton | Yes | Homeowner damaged a 1" plastic gas service line with a shovel while installing irrigation lines. No USA ticket. | No | Gas Line | Yes | Shovel | Irrigation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-24 | 1” | 24 | 21 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18586 | x | x | x |  | 2022-03-24 | Mar | 3 | 2022 | 75279 |  | 45227148 | 123179996 | Stanislaus | Central Valley | Yosemite | South | Turlock | Yes | Veteran Pipeline Construction Inc. damaged a 1/2" plastic gas service line with a shovel while doing gas pipe replacement. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | X200300563 | Dig-In to PG&E Underground | 2nd Party-Contractor | Veteran Pipeline Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-03-24 | ½” | 28 | 29 | N/A | 3 | Mar | 2022 |  |  | Yes
18585 | x | x | x |  | 2022-03-24 | Mar | 3 | 2022 | 75277 |  |  | 123182881 | Santa Clara | Central Coast | De Anza | Central | Monte Sereno | Yes | Gonzalez Concrete damaged a 1 1/4" steel gas main with a front loader while pouring a concrete driveway pad. No USA ticket. | No | Gas Line | Yes | Front Loader | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Gonzalez Concrete | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-24 | 1 ¼” | 34 | 50 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 3 | Mar | 2022 |  |  | No
18592 | x | x | x |  | 2022-03-25 | Mar | 3 | 2022 | 75348 |  |  | 123195200 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Custom Construction damaged a 1/2" plastic gas service line with a shovel while excavating for a drainage ditch. No USA ticket. | No | Gas Line | Yes | Shovel | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Custom Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-25 | ½” | 31 | 23 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 3 | Mar | 2022 |  |  | Yes
18596 | x |  | x |  | 2022-03-26 | Mar | 3 | 2022 | 75375 |  |  | 123198248 | Santa Clara | Central Coast | De Anza | Central | Mountain View | Yes | GMJ Construction damaged a 1/2" plastic gas service line with a shovel while installing a new electrical panel. No USA ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | GMJ Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-26 | ½” | 32 | 52 | Other | 3 | Mar | 2022 |  |  | Yes
18595 | x | x | x |  | 2022-03-26 | Mar | 3 | 2022 | 75378 |  |  | 123198244 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Homeowner damaged a 1" plastic gas service line with a sawzall while cutting tree roots as part of a landscaping project. No USA ticket. | No | Gas Line | Yes | Cutting Machine | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-26 | 1” | 19 | 92 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 3 | Mar | 2022 |  |  | No
18594 | x | x | x |  | 2022-03-26 | Mar | 3 | 2022 | 75364 |  | 45231560 | 123197784 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while installing a new fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-26 | ½” | 26 | 37 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18593 | x |  |  |  | 2022-03-26 | Mar | 3 | 2022 | 75380 |  |  |  | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | City of San Francisco Water damaged a 1/2" plastic gas service line with a backhoe while repairing a water leak. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X208200232 | Dig-In to PG&E Underground | 3rd Party-Government Entity | San Francisco Water Department | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-03-26 | ½” | 24 | 21 | N/A | 3 | Mar | 2022 |  |  | No
18597 | x | x |  |  | 2022-03-27 | Mar | 3 | 2022 | 75394 |  |  |  | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Homeowner damaged a 1/2" plastic gas service line with a sawzall while removing a tree. No USA ticket. | No | Gas Line | Yes | Cutting Machine | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-27 | ½” | 16 | 110 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | No
18600 | x | x | x |  | 2022-03-28 | Mar | 3 | 2022 | 75418 |  |  | 123204025 | San Mateo | Central Coast | Peninsula | Central | Burlingame | Yes | City of Burlingame damaged a 1" plastic gas service line with a steel probe while attempting to locate the marked gas line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Probing Tool | Water | Failed to Dig with Care | Yes | X208101971 | Dig-In to PG&E Underground | 3rd Party-Government Entity | City of Burlingame | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-03-28 | 1” | 26 | 41 | N/A | 3 | Mar | 2022 |  |  | Yes
18599 | x | x | x |  | 2022-03-28 | Mar | 3 | 2022 | 75415 |  |  | 123202787 | Marin | Bay Area | North Bay | North | Novato | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while installing a new french drain. Expired USA ticket. Primary cause was failed to dig with care | No | Gas Line | Yes | Shovel | Drainage Work | Failed to Dig with Care | No (expired) | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-28 | ½” | 35 | 69 | Expired USA ticket | 3 | Mar | 2022 |  |  | Yes
18598 | x |  | x |  | 2022-03-28 | Mar | 3 | 2022 | 75419 |  |  | 123204336 | San Mateo | Central Coast | Peninsula | Central | Hillsborough | Yes | Phoenix Electric damaged a 1/2" plastic gas service line with a shovel while performing landscaping. Expired USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Shovel | Landscaping | Facility was not located or marked | No (expired) | W204000271 | Dig-In to PG&E Underground | 3rd Party-Contractor | Phoenix Electric Co | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-28 | ½” | 12 | 22 | Expired USA ticket | 3 | Mar | 2022 | Bargaining Unit |  | Yes
18610 | x | x |  |  | 2022-03-29 | Mar | 3 | 2022 | 75477 |  |  |  | Sacramento | Northern | Sacramento | North | Elk Grove | Yes | Quest Media damaged a 1/2" plastic gas service line with boring equipment while installing telecommunication conduit. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Boring Equipment | Telecommunications | Incorrect Facility Records / Maps | Yes | X205902129 | Dig-In to PG&E Underground | 3rd Party-Contractor | Quest Media | Distribution Service |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-29 | ½” | 25 | 81 | N/A | 3 | Mar | 2022 |  |  | No
18609 | x | x |  |  | 2022-03-29 | Mar | 3 | 2022 | 75479 |  |  |  | Fresno | Central Valley | Fresno | South | Fresno | Yes | KJ Worldwide damaged a 1" plastic gas service line with a post-hole digger while installing a fence post. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | KJ Worldwide | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-29 | 1” | 18 | 23 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18608 | x | x | x |  | 2022-03-29 | Mar | 3 | 2022 | 75472 |  |  | 123209896 | Santa Cruz | Central Coast | Central Coast | South | Ben Lomond | Yes | Jim Walters Tractor damaged a 1 1/4" plastic gas main with an auger attached to an excavator while installing fencing. No USA ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Jim Walters Tractor | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-29 | 1 ¼” | 30 | 53 | Knew About USA Ticket Requirement But Chose Not to Call | 3 | Mar | 2022 |  |  | No
18607 | x | x |  |  | 2022-03-29 | Mar | 3 | 2022 | 75443 |  |  |  | San Mateo | Central Coast | Peninsula | Central | Moss Beach | Yes | Lopez Fence, LLC damaged a 1/2" plastic gas service line with a sharp shooter shovel while removing a fence. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Lopez Fence, LLC | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-29 | ½” | 30 | 60 | Knew About USA Ticket Requirement But Chose Not to Call | 3 | Mar | 2022 |  |  | Yes
18604 | x | x | x |  | 2022-03-29 | Mar | 3 | 2022 | 75432 |  |  | 123206552 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | SEFNCO damaged a 1/2" plastic gas service line with a mini-excavator while installing telecommunication lines. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X206202436 | Dig-In to PG&E Underground | 3rd Party-Contractor | SEFNCO | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-29 | ¼” | 25 | 18 | N/A | 3 | Mar | 2022 |  |  | No
18603 | x | x |  |  | 2022-03-29 | Mar | 3 | 2022 | 75467 |  |  |  | Kern | Central Valley | Kern | South | Bakersfield | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while digging a trench for a sewer main. No USA ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-29 | ½” | 31 | 79 | Other | 3 | Mar | 2022 |  |  | Yes
18616 | x | x |  |  | 2022-03-30 | Mar | 3 | 2022 | 75527 |  |  |  | Sacramento | Northern | Sacramento | North | Elk Grove | Yes | Golden State Utility damaged a 1/2" plastic gas service line with boring equipment while installing telecommunication conduit. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Boring Equipment | Telecommunications | Incorrect Facility Records / Maps | Yes | X205500468 | Dig-In to PG&E Underground | 3rd Party-Contractor | Golden State Utility | Distribution Service |  | Yes | Records Error |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-30 | ½” | 33 | 58 | N/A | 3 | Mar | 2022 |  |  | No
18615 | x | x | x |  | 2022-03-30 | Mar | 3 | 2022 | 75496 |  |  | 123212002 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Athenour & Sons Landscaping damaged a 1/2" plastic gas service line with a shovel while removing a plant. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Athenour & Sons Landscaping | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-30 | ½” | 18 | 18 | Knew About USA Ticket Requirement But Chose Not to Call | 3 | Mar | 2022 |  |  | Yes
18614 | x | x | x |  | 2022-03-30 | Mar | 3 | 2022 | 75507 |  |  | 123215416 | Contra Costa | Bay Area | Diablo | South | Brentwood | Yes | Hennessey’s Fencing damaged a 1/2" plastic gas service line with a shovel while digging a fence post hole. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Shovel | Fencing | Facility was not located or marked | Yes | X208102054 | Dig-In to PG&E Underground | 3rd Party-Contractor | Hennessey’s Fencing | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-30 | ½” | 18 | 26 | N/A | 3 | Mar | 2022 | Bargaining Unit |  | Yes
18612 | x | x |  |  | 2022-03-30 | Mar | 3 | 2022 | 75501 |  |  |  | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | De Silva Gates Construction damaged a 1 1/4" plastic gas service line with an excavator while grading for a new parking pad. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Blading/Lot Grading | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X203201334 | Dig-In to PG&E Underground | 3rd Party-Contractor | De Silva Gates Construction | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-30 | 1 ¼” | 26 | 44 | N/A | 3 | Mar | 2022 |  |  | No
18626 | x |  |  |  | 2022-03-31 | Mar | 3 | 2022 | 75567 |  |  |  | San Mateo | Central Coast | Peninsula | Central | Atherton | Yes | West Valley Construction damaged a 2" inch conduit containing cathodic protection wires with a trencher while installing a new water main. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | No | Trencher | Water | Facility was not located or marked | Yes | X133503178 | Dig-In to PG&E Underground | 3rd Party-Contractor | West Valley Construction | Distribution Main |  | Yes | Locator Error - No Mark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-31 |  |  |  | N/A | 3 | Mar | 2022 | Bargaining Unit |  | No
18625 | x | x |  |  | 2022-03-31 | Mar | 3 | 2022 | 75568 |  |  |  | Yolo | Northern | Vacaville | North | West Sacramento | Yes | Brown Construction damaged a 2" plastic gas main with a mini-excavator while trying to locate the line. Expired USA ticket. Primary cause was failure to expose facility with hand tools | No | Gas Line | No | Excavator | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No (expired) | X123901437 | Dig-In to PG&E Underground | 3rd Party-Contractor | Brown Construction | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-31 | 2” |  |  | Expired USA ticket | 3 | Mar | 2022 |  |  | No
18624 | x |  | x |  | 2022-03-31 | Mar | 3 | 2022 | 75592 |  |  | 123222979 | Yolo | Northern | Vacaville | North | Woodland | Yes | J&D Excavation damaged a 2" plastic gas main with an excavator while removing gas lines. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W206300095 | Dig-In to PG&E Underground | 2nd Party-Contractor | J&D Excavation | Distribution Main |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-03-31 | 2” | 56 | 87 | N/A | 3 | Mar | 2022 |  |  | No
18623 | x | x |  |  | 2022-03-31 | Mar | 3 | 2022 | 75554 |  |  |  | Kern | Central Valley | Kern | South | Taft | Yes | Homeowner damaged the wrap on a 3/4" steel gas service line with a shovel while removing a tree stump. No USA ticket. | Yes | Gas Line | No | Shovel | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-31 | ¾” | 18 | 0 | No Knowledge of USA Ticketing Process | 3 | Mar | 2022 |  |  | Yes
18622 | x | x |  |  | 2022-03-31 | Mar | 3 | 2022 | 75543 |  |  | 123218030 | Stanislaus | Central Valley | Yosemite | South | Turlock | Yes | All World Electric Inc damaged a 1" plastic gas service line with an excavator while installing electrical conduit. No USA ticket. Primary cause was failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | All World Electric Inc | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-31 | 1” | 38 | 22 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 3 | Mar | 2022 |  |  | No
18621 | x |  | x |  | 2022-03-31 | Mar | 3 | 2022 | 75551 |  |  | 123219846 | Yolo | Northern | Vacaville | North | Winters | Yes | Homeowner damaged a 1/2" plastic gas service line with a backhoe while fixing a broken water valve. No USA ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-31 | ½” | 36 | 25 | Believed They Knew Where Underground Utility was From Previous Knowledge | 3 | Mar | 2022 |  |  | No
18620 | x |  | x |  | 2022-03-31 | Mar | 3 | 2022 | 75546 |  |  | 123218816 | San Mateo | Central Coast | Peninsula | Central | San Mateo | Yes | Columbia Electric damaged a 1/2" plastic gas service line with a trencher while installing new conduit. Valid USA ticket. PG&E at-fault - Locator Error - Mismark | No | Gas Line | Yes | Trencher | Telecommunications | Incorrect information or marks | Yes | X206202495 | Dig-In to PG&E Underground | 3rd Party-Contractor | Columbia Electric | Distribution Service |  | Yes | Locator Error - Mismark |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-31 | ½” | 20 | 27 | N/A | 3 | Mar | 2022 | Bargaining Unit |  | No
18619 | x | x | x |  | 2022-03-31 | Mar | 3 | 2022 | 75590 |  |  | 123223034 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Homeowner damaged a 1" plastic gas service line with a post-hole digger while installing a fence. Valid USA ticket. Excavated outside of delineated area | No | Gas Line | Yes | Post-Hole Digger | Fencing | Excavated Outside Delineated Area | Yes | X208001928 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-03-31 | 1” | 27 | 43 | N/A | 3 | Mar | 2022 |  |  | Yes
18617 | x | x | x |  | 2022-03-31 | Mar | 3 | 2022 | 75588 |  |  | 123223092 | Santa Clara | Central Coast | De Anza | Central | Los Gatos | Yes | Green Grass Property Maintenance damaged a 1/2" plastic gas service line with a shovel while digging a trench as part of some landscape work. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Green Grass Property Maintenance | Distribution Service |  | No | N/A |  |  | 2022 Q1 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-03-31 | ½” | 19 | 32 | Excavator Did Not Believe a USA Ticket was Required | 3 | Mar | 2022 |  |  | Yes
18630 | x | x | x | x | 2022-04-01 | Apr | 4 | 2022 | 75637 |  |  | 123229566 | Kern | Central Valley | Kern | South | Bakersfield | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while replacing a sewer pipe. No USA ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-01 | ½” | 25 | 20 | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | Yes
18629 | x | x |  | x | 2022-04-01 | Apr | 4 | 2022 | 75628 |  |  |  | San Mateo | Central Coast | Peninsula | Central | San Mateo | Yes | Jay Designs damaged a 3/4" steel gas service line with a skid loader while excavating for a new driveway. No USA ticket. | No | Gas Line | No | Skid Steer | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Jay Designs | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-01 | ¾” |  |  | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 4 | Apr | 2022 |  |  | No
18628 | x | x | x | x | 2022-04-01 | Apr | 4 | 2022 | 75612 |  |  | 123230691 | Alameda | Central Coast | Mission | South | Fremont | Yes | All American Fence Corporation damaged a 1 1/4" plastic gas service line with an auger while installing posts. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Auger | Pole/Post Installation | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X208302205 | Dig-In to PG&E Underground | 3rd Party-Contractor | All American Fence Corporation | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-01 | 1 ¼” | 48 | 33 | N/A | 4 | Apr | 2022 |  |  | No
18627 | x | x | x | x | 2022-04-01 | Apr | 4 | 2022 | 75647 |  |  | 123231000 | San Mateo | Central Coast | Peninsula | Central | Daly City | Yes | Patrick Coakley Construction damaged a 3/4" steel gas service line with a sawzall while installing drainage line for new construction. No USA ticket. | No | Gas Line | Yes | Cutting Machine | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Patrick Coakley Constuction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-01 | ¾” | 12 | 34 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 4 | Apr | 2022 |  |  | No
18632 | x | x | x | x | 2022-04-02 | Apr | 4 | 2022 | 75659 |  |  | 123236147 | Fresno | Central Valley | Fresno | South | Selma | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while digging fence posts. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-02 | ½” | 36 | 53 | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | Yes
18638 | x | x | x | x | 2022-04-04 | Apr | 4 | 2022 | 75690 |  |  | 123240358 | San Mateo | Central Coast | Peninsula | Central | Redwood City | Yes | Makoni Construction damaged a 1/2" plastic gas service line inserted into 3/4" steel with a shovel while exposing the gas line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Water | Failed to Dig with Care | Yes | X206701990 | Dig-In to PG&E Underground | 3rd Party-Contractor | Makoni Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-04 | ½” | 36 | 40 | N/A | 4 | Apr | 2022 |  |  | Yes
18637 | x | x | x | x | 2022-04-04 | Apr | 4 | 2022 | 75717 |  |  | 123248661 | Solano | Northern | Vacaville | North | Vacaville | Yes | Hines Custom Fence damaged a 1/2" plastic gas service line with a digging bar while digging a post hole for a fence. No USA ticket. | No | Gas Line | Yes | Digging Bar | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Hines Custom Fence | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-04 | ½” | 26 | 29 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 4 | Apr | 2022 |  |  | Yes
18636 | x | x | x | x | 2022-04-04 | Apr | 4 | 2022 | 75704 |  |  | 123241673 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Anvil Builders damaged a 1/2" plastic gas service line with a sharpshooter shovel while replacing Aldyl-A pipe. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | X200300266 | Dig-In to PG&E Underground | 2nd Party-Contractor | Anvil Builders | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-04-04 | ½” | 25 | 35 | N/A | 4 | Apr | 2022 |  |  | Yes
18635 | x | x | x | x | 2022-04-04 | Apr | 4 | 2022 | 75718 |  |  | 123243296 | Placer | Northern | Sierra | North | Roseville | Yes | Concrete Value Corp damaged a 2" plastic gas main with a backhoe while installing a new sewer line. No USA ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Concrete Value Corp | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-04 | 2” | 36 | 56 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 4 | Apr | 2022 |  |  | No
18634 | x | x | x | x | 2022-04-04 | Apr | 4 | 2022 | 75682 |  |  | 123241878 | Santa Clara | Central Coast | San Jose | Central | Milpitas | Yes | Urata & Sons Concrete damaged a 1" plastic gas service line with an auger while drilling a post hole. No USA ticket. | No | Gas Line | Yes | Auger | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Urata & Sons Concrete | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-04 | 1” | 20 | 74 | Knew About USA Ticket Requirement But Chose Not to Call | 4 | Apr | 2022 |  |  | No
18633 | x | x | x | x | 2022-04-04 | Apr | 4 | 2022 | 75707 |  |  | 123241639 | Yuba | Northern | Sierra | North | Marysville | Yes | Advanced Telecommunications damaged a 1 1/4" plastic gas main with a shovel while exposing the gas line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | X208302818 | Dig-In to PG&E Underground | 3rd Party-Contractor | Advanced Telecommunications | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-04 | 1 ¼” | 18 | 26 | N/A | 4 | Apr | 2022 |  |  | Yes
18646 | x | x | x | x | 2022-04-05 | Apr | 4 | 2022 | 75775 |  |  | 123248537 | Butte | Northern | North Valley | North | Paradise | Yes | Outback Construction damaged a 3/4" steel gas stub attached to a 4" main with vacuum equipment while tunneling under the line. Valid USA ticket. Failed to protect exposed facility | No | Gas Line | Yes | Vacuum Equipment | Electric Work | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X201101634 | Dig-In to PG&E Underground | 2nd Party-Contractor | Outback Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-04-05 | ¾” | 42 | 167 | N/A | 4 | Apr | 2022 |  |  | No
18645 | x | x |  |  | 2022-04-05 | Apr | 4 | 2022 | 75753 |  |  |  | Alameda | Central Coast | Mission | South | Fremont | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while doing landscaping. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-05 | ½” | 12 | 35 | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | Yes
18644 | x | x | x | x | 2022-04-05 | Apr | 4 | 2022 | 75764 |  |  |  | Kern | Central Valley | Kern | South | Bakersfield | Yes | AC Electrical damaged a 1" plastic gas service line with an mini-excavator while creating footings for a solar array platform. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Other | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X208802232 | Dig-In to PG&E Underground | 3rd Party-Contractor | AC Electric | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-05 | 1” | 18 | 37 | N/A | 4 | Apr | 2022 |  |  | No
18643 | x | x | x | x | 2022-04-05 | Apr | 4 | 2022 | 75747 |  |  | 123247796 | Contra Costa | Bay Area | Diablo | South | Orinda | Yes | KJ Woods Construction damaged 1' plastic gas service line with a shovel while doing a sewer main installation. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | X206902622 | Dig-In to PG&E Underground | 3rd Party-Contractor | KJ Woods Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-05 | 1” | 28 | 22 | N/A | 4 | Apr | 2022 |  |  | Yes
18642 | x | x | x | x | 2022-04-05 | Apr | 4 | 2022 | 75750 |  |  | 123248337 | Kern | Central Valley | Kern | South | North Edwards | Yes | UC Fence damaged a 1/2" plastic gas service line with a post-hole digger while installing a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | UC Fence | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-05 | ½” | 24 | 50 | Knew About USA Ticket Requirement But Chose Not to Call | 4 | Apr | 2022 |  |  | Yes
18641 | x | x | x | x | 2022-04-05 | Apr | 4 | 2022 | 75761 |  |  | 123250235 | Colusa | Northern | Sacramento | North | Colusa | Yes | Mobile Communication Services damaged a 1/2" plastic gas service line with boring equipment while installing conduit. Valid USA ticket. Excavator failed to maintain clearance after verifying marks | No | Gas Line | Yes | Boring Equipment | Electric Work | Excavator Failed to Maintain Clearance After Verifying Marks | Yes | W208000337 | Dig-In to PG&E Underground | 3rd Party-Contractor | Mobile Communication Services | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-05 | ½” | 46 | 76 | N/A | 4 | Apr | 2022 |  |  | No
18639 | x | x | x | x | 2022-04-05 | Apr | 4 | 2022 | 75738 |  |  | 123251793 | San Mateo | Central Coast | Peninsula | Central | Atherton | Yes | Double O Engineering damaged a 3/4" steel gas service line with a power saw while digging a trench for a drainage system. Valid USA ticket. PG&E at-fault - Locator Error - Mismark | No | Gas Line | Yes | Cutting Machine | Drainage Work | Incorrect information or marks | Yes | W205600159 | Dig-In to PG&E Underground | 3rd Party-Contractor | Double O Engineering | Distribution Service |  | Yes | Locator Error - Mismark |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-05 | ¾” | 20 | 43 | N/A | 4 | Apr | 2022 | Bargaining Unit |  | No
18654 | x | x |  | x | 2022-04-06 | Apr | 4 | 2022 | 75830 |  |  |  | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | RAD Communications damaged the wrap on 12 marked a 3/4" steel gas service lines with vacuum equipment while doing telecommunication work. Valid USA ticket. Inadequate excavation practices | Yes | Gas Line | No | Vacuum Equipment | Telecommunications | Inadequate Excavation Practices | Yes | X208001602 | Dig-In to PG&E Underground | 3rd Party-Contractor | RAD Communications | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-06 | ¾” | 24 | 0 | N/A | 4 | Apr | 2022 |  |  | No
18653 | x | x | x |  | 2022-04-06 | Apr | 4 | 2022 | 75789 |  |  | 123255196 | Glenn | Northern | North Valley | North | Orland | Yes | Santos Excavating damaged a 1" plastic gas service line with an excavator while doing a road widening project. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Road Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X203200942 | Dig-In to PG&E Underground | 3rd Party-Contractor | Santos Excavating | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-06 | 1” | 18 | 28 | N/A | 4 | Apr | 2022 |  |  | No
18652 | x | x | x | x | 2022-04-06 | Apr | 4 | 2022 | 75799 |  |  | 123259048 | Sonoma | Northern | Sonoma | North | Windsor | Yes | Ghilotti Construction damaged a 1" plastic gas service line with a backhoe while building round-a-bout. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Road Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X123500066 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ghilotti Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-06 | 1” | 36 | 33 | N/A | 4 | Apr | 2022 |  |  | No
18651 | x | x | x | x | 2022-04-06 | Apr | 4 | 2022 | 75785 |  |  | 123258279 | San Mateo | Central Coast | Peninsula | Central | Menlo Park | Yes | Bannister Custom Homes damaged a 1/2" plastic gas service line with a shovel while moving the gas line inside of a trench. No USA ticket. Primary cause of dig-in was failure to protect exposed facility. | No | Gas Line | Yes | Shovel | Gas | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Bannister Custom Homes | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-06 | ½” | 28 | 14 | Believed They Knew Where Underground Utility was From Previous Knowledge | 4 | Apr | 2022 |  |  | Yes
18650 | x | x |  |  | 2022-04-06 | Apr | 4 | 2022 | 75813 |  |  |  | San Joaquin | Central Valley | Stockton | South | Manteca | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while removing a fence post. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-06 | ½” | 31 | 8 | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | Yes
18649 | x | x | x | x | 2022-04-06 | Apr | 4 | 2022 | 75834 |  |  | 123259288 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Qualtek Wireless LLC damaged a 1/2" plastic gas service line with a sharp shooter shovel while doing a telecommunication install. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Dig with Care | Yes | W206200167 | Dig-In to PG&E Underground | 3rd Party-Contractor | Qualtek Wireless LLC | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-06 | ½” | 27 | 42 | N/A | 4 | Apr | 2022 |  |  | Yes
18648 | x | x |  | x | 2022-04-06 | Apr | 4 | 2022 | 75795 |  |  |  | Sacramento | Northern | Sacramento | North | Rancho Cordova | Yes | Lat Long Infrastructure of California damaged a 3/4" steel gas service line with a micro-trencher while doing a telecommunication install. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Trencher | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X209402378 | Dig-In to PG&E Underground | 3rd Party-Contractor | Lat Long Infrastructure of California | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-06 | ¾” | 11 | 46 | N/A | 4 | Apr | 2022 |  |  | No
18647 | x | x |  | x | 2022-04-06 | Apr | 4 | 2022 | 75804 |  |  |  | San Mateo | Central Coast | Peninsula | Central | South San Francisco | Yes | ARB Inc damaged a 1/2" plastic gas service line with a sharp shooter shovel while exposing the gas line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | X136401645 | Dig-In to PG&E Underground | 2nd Party-Contractor | ARB Inc | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-04-06 | ½” | 24 | 78 | N/A | 4 | Apr | 2022 |  |  | Yes
18661 | x | x | x | x | 2022-04-07 | Apr | 4 | 2022 | 75863 |  |  | 123264756 | San Mateo | Central Coast | Peninsula | Central | Menlo Park | Yes | JC Tree Care damaged a 1/2" plastic gas service line with a shovel while excavating for a french drain. No USA ticket. | No | Gas Line | Yes | Shovel | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | JC Tree Care | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-07 | ½” | 24 | 30 | Excavator Did Not Believe a USA Ticket was Required | 4 | Apr | 2022 |  |  | Yes
18660 | x | x |  |  | 2022-04-07 | Apr | 4 | 2022 | 75889 |  |  |  | Sonoma | Northern | Sonoma | North | Petaluma | Yes | V B E Inc. damaged a 2" plastic gas main with an excavator while doing telecommunications work. VBE pot-holed and found an abandoned line they thought was the 2" main. The 2" main was accurately marked so contractor at-fault for not identifying it. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W209100352 | Dig-In to PG&E Underground | 3rd Party-Contractor | V B E Inc | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-07 | 2” | 30 | 87 | N/A | 4 | Apr | 2022 |  |  | No
18659 | x | x | x | x | 2022-04-07 | Apr | 4 | 2022 | 75875 |  |  | 123264805 | San Mateo | Central Coast | Peninsula | Central | Menlo Park | Yes | Open Remodel LLC damaged a 1/2" plastic gas service line with a shovel while digging a trench for drainage. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Drainage Work | Failed to Dig with Care | Yes | X208103235 | Dig-In to PG&E Underground | 3rd Party-Contractor | Open Remodel LLC | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-07 | ½” | 36 | 30 | N/A | 4 | Apr | 2022 |  |  | Yes
18658 | x | x |  | x | 2022-04-07 | Apr | 4 | 2022 | 75878 |  |  |  | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while installing a fence. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-07 | ½” | 24 | 72 | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | Yes
18657 |  | x |  |  | 2022-04-07 | Apr | 4 | 2022 | 75896 |  |  |  | San Joaquin | Central Valley | Stockton | South | Tracy | Yes | MCH Electric damaged the wrap on transmission line 002 (26" steel) with vacuum equipment while potholing for the line. Valid USA. Inadequate excavation practices | Yes | Gas Line | No | Vacuum Equipment | Landscaping | Inadequate Excavation Practices | Yes | W201200192 | Dig-In to PG&E Underground | 3rd Party-Contractor | MCH Electric | Transmission Line |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-07 | 26" | 65 |  | N/A | 4 | Apr | 2022 |  |  | No
18655 | x | x |  |  | 2022-04-07 | Apr | 4 | 2022 | 75870 |  |  |  | Solano | Northern | Vacaville | North | Fairfield | Yes | Future Energy Savers damaged a 1/2" plastic gas service line and direct buried secondary cable with a jackhammer while digging a new electric service trench. Expired USA. Primary cause was excavating outside delineated area. See companion dig-in OIS 1665172 | No | Gas Line | Yes | Jackhammer | Electric Work | Excavated Outside Delineated Area | No (expired) | W201900329 W201900325 | Dig-In to PG&E Underground | 3rd Party-Contractor | Future Energy Savers | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-07 | ½” | 30 | 20 | Expired USA ticket | 4 | Apr | 2022 |  |  | No
18666 | x | x | x | x | 2022-04-08 | Apr | 4 | 2022 | 75939 |  |  | 123274133 | Monterey | Central Coast | Central Coast | South | Salinas | Yes | PSTS Septic Tank Service damaged a 1/2" plastic gas service line with a excavator while installing a sewer leach line. No USA ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | PSTS Septic Tank Service | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-08 | ½” | 52 | 38 | Knew About USA Ticket Requirement But Chose Not to Call | 4 | Apr | 2022 |  |  | No
18665 | x | x | x |  | 2022-04-08 | Apr | 4 | 2022 | 75936 |  |  | 123276438 | Contra Costa | Bay Area | Diablo | South | Walnut Creek | Yes | Basset Engineering damaged a 2" plastic gas main with a hand held power saw while excavating to install sewer lines. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Cutting Machine | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X209101601 | Dig-In to PG&E Underground | 3rd Party-Contractor | Basset Engineering | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-08 | 2” | 18 | 64 | N/A | 4 | Apr | 2022 |  |  | No
18664 | x | x |  | x | 2022-04-08 | Apr | 4 | 2022 | 75923 |  |  |  | Butte | Northern | North Valley | North | Chico | Yes | Mike Jackson Construction damaged a 1 1/4" plastic gas service stub with a backhoe while preparing a trench for the stub to be connected to a gas meter. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X209401852 | Dig-In to PG&E Underground | 3rd Party-Contractor | Mike Jackson Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-08 | 1 ¼” | 42 | 26 | N/A | 4 | Apr | 2022 |  |  | No
18662 | x | x |  | x | 2022-04-08 | Apr | 4 | 2022 | 75962 |  |  |  | Santa Clara | Central Coast | De Anza | Central | Sunnyvale | Yes | HB Design and Construction damaged the wrap on a 3/4" steel gas service line with a shovel while pouring a foundation for a home addition. No USA ticket. | Yes | Gas Line | No | Shovel | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | HB Design and Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-08 | ¾” | 18 | 0 | Excavator Did Not Believe a USA Ticket was Required | 4 | Apr | 2022 |  |  | Yes
18667 | x | x | x | x | 2022-04-09 | Apr | 4 | 2022 | 75978 |  | 45247398 | 123279993 | Butte | Northern | North Valley | North | Durham | Yes | Homeowner damaged a 1" plastic gas service line with a probe while doing landscaping. No USA ticket. | No | Gas Line | Yes | Probing Tool | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-09 | 1” | 36 | 24 | Believed They Knew Where Underground Utility was From Previous Knowledge | 4 | Apr | 2022 |  |  | Yes
18669 | x | x | x |  | 2022-04-10 | Apr | 4 | 2022 | 75996 |  |  | 123294099 | San Joaquin | Central Valley | Stockton | South | Lathrop | Yes | Montes Brothers Construction damaged a 1 1/4" plastic gas service line with an excavator while trenching to install new sewer line. No USA ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Montes Brothers Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-10 | 1 ¼” | 36 | 131 | Excavator Did Not Believe a USA Ticket was Required | 4 | Apr | 2022 |  |  | No
18668 | x | x | x | x | 2022-04-10 | Apr | 4 | 2022 | 75994 |  |  | 123294094 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Homeowner damaged a 1 1/4" plastic gas service line with a mini-excavator while digging a drainage ditch. No USA ticket but there were marks from a previous locate. Primary cause was failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Drainage Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No (expired) | X209402982 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-10 | 1 ¼” | 36 | 30 | Expired USA ticket | 4 | Apr | 2022 |  |  | No
18679 | x | x | x |  | 2022-04-11 | Apr | 4 | 2022 | 76010 |  |  | 123295965 | Butte | Northern | North Valley | North | Paradise | Yes | Outback Utilities damaged a 1/2" plastic gas service line with a shovel while performing a gas service line replacement. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | X208802441 | Dig-In to PG&E Underground | 2nd Party-Contractor | Outback Utilities | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-04-11 | ½” | 7 | 24 | N/A | 4 | Apr | 2022 |  |  | Yes
18678 | x | x | x | x | 2022-04-11 | Apr | 4 | 2022 | 76024 |  |  | 123300192 | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | Goodman Landscape Design damaged a 1" plastic gas service line with a metal forming stake while installing new landscaping. No USA ticket. | No | Gas Line | Yes | Stake | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Goodman Landscape Design | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-11 | 1” | 24 | 60 | Excavator Did Not Believe a USA Ticket was Required | 4 | Apr | 2022 |  |  | Yes
18677 | x | x | x | x | 2022-04-11 | Apr | 4 | 2022 | 76016 |  |  | 123297323 | Sacramento | Northern | Sacramento | North | Citrus Heights | Yes | Fiberco General Engineering damaged a 2" plastic gas main with boring equipment while installing telecommunication conduit. No USA ticket. Fiberco were using marks from a private locate company. The company did not map the gas main. | No | Gas Line | Yes | Boring Equipment | Telecommunications | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Fiberco General Engineering | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-11 | 2” | 29 | 129 | Other | 4 | Apr | 2022 |  |  | No
18676 | x | x | x | x | 2022-04-11 | Apr | 4 | 2022 | 76030 |  |  | 123300337 | Alameda | Central Coast | Mission | South | Pleasanton | Yes | GLO Electric damaged a 1/2" plastic gas service line with a shovel while exposing the gas line. Expired USA ticket. Marks were accurate. Primary cause was failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | No (expired) | X206001124 | Dig-In to PG&E Underground | 3rd Party-Contractor | GLO Electric | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-11 | ½” | 20 | 28 | Expired USA ticket | 4 | Apr | 2022 |  |  | Yes
18675 | x | x | x | x | 2022-04-11 | Apr | 4 | 2022 | 76019 |  | 45252117 | 123297308 | Stanislaus | Central Valley | Yosemite | South | Turlock | Yes | All World Electric Inc. damaged a 1/2" plastic gas service line with a shovel while trenching for the installation of electric conduit. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | W209000097 | Dig-In to PG&E Underground | 3rd Party-Contractor | All World Electric Inc | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-11 | ½” | 48 | 34 | N/A | 4 | Apr | 2022 |  |  | Yes
18674 | x | x | x | x | 2022-04-11 | Apr | 4 | 2022 | 76018 |  |  | 123297760 | Santa Cruz | Central Coast | Central Coast | South | Mount Hermon | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while trying to find a leak in the sprinkler system. No USA ticket. | No | Gas Line | Yes | Shovel | Irrigation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-11 | ½” | 18 | 35 | Believed They Knew Where Underground Utility was From Previous Knowledge | 4 | Apr | 2022 |  |  | Yes
18672 | x | x | x | x | 2022-04-11 | Apr | 4 | 2022 | 76013 |  |  | 123296333 | Monterey | Central Coast | Central Coast | South | Salinas | Yes | Helix Electric damaged a 1/2" plastic gas service line with a shovel while potholing. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | X205902581 | Dig-In to PG&E Underground | 2nd Party-Contractor | Helix Electric | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GC Electric |  |  | 2nd Party Gas | Yes | 2022-04-11 | ½” | 24 | 18 | N/A | 4 | Apr | 2022 |  |  | Yes
18671 | x | x | x | x | 2022-04-11 | Apr | 4 | 2022 | 76025 |  |  | 123300017 | San Mateo | Central Coast | Peninsula | Central | Redwood City | Yes | Automatic Gate Masters & Garage Door damaged a 1" plastic gas service line with a post-hole digger while digging a post hole. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Automatic Gate Masters & Garage Door | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-11 | 1” | 20 | 31 | Excavator Did Not Believe a USA Ticket was Required | 4 | Apr | 2022 |  |  | Yes
18670 | x | x | x | x | 2022-04-11 | Apr | 4 | 2022 | 76014 |  |  | 123296952 | Sonoma | Northern | Sonoma | North | Healdsburg | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while replacing a fence. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-11 | ½” | 28 | 63 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 4 | Apr | 2022 |  |  | Yes
18683 | x | x | x |  | 2022-04-12 | Apr | 4 | 2022 | 76056 |  |  | 123303192 | Solano | Northern | Vacaville | North | Fairfield | Yes | Pacific Utility Construction damaged a 1/2" plastic gas service line with a mini-excavator while doing telecommunications work. Valid USA ticket. A section of discarded pipe was mis-identified as a live line (see investigation notes for full description of what occurred). PG&E at-fault - Other Error | No | Gas Line | Yes | Excavator | Telecommunications | Incorrect information or marks | Yes | X206901472 | Dig-In to PG&E Underground | 3rd Party-Contractor | Pacific Utility Construction | Distribution Service |  | Yes | Other Error |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-12 | ½” | 31 | 21 | N/A | 4 | Apr | 2022 |  |  | No
18682 | x | x | x | x | 2022-04-12 | Apr | 4 | 2022 | 76057 |  |  | 123311264 | Santa Clara | Central Coast | San Jose | Central | Milpitas | Yes | Granite Rock damaged a 1" plastic gas service line with an excavator while doing site development. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Site Development | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X208402251 | Dig-In to PG&E Underground | 3rd Party-Contractor | Granite Rock | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-12 | 1” | 24 | 73 | N/A | 4 | Apr | 2022 |  |  | No
18681 | x | x | x |  | 2022-04-12 | Apr | 4 | 2022 | 76101 |  |  | 123314279 | Shasta | Northern | North Valley | North | Redding | Yes | Jason Abel Construction Inc damaged a 4" steel gas main with a backhoe while doing a sewer line replacement. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W205500385 | Dig-In to PG&E Underground | 3rd Party-Contractor | Jason Abel Construction | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-12 | 4" | 22 | 143 | N/A | 4 | Apr | 2022 |  |  | No
18680 | x | x |  |  | 2022-04-12 | Apr | 4 | 2022 | 76071 |  |  |  | Santa Clara | Central Coast | San Jose | Central | Morgan Hill | Yes | HCI LLC. Damaged a 1/2" plastic gas service line with a shovel to open a trench next to a telecommunication splice box. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Shovel | Telecommunications | Facility was not located or marked | Yes | X208402251 | Dig-In to PG&E Underground | 3rd Party-Contractor | HCI Inc. | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-12 | ½” | 24 | 30 | N/A | 4 | Apr | 2022 | Bargaining Unit |  | Yes
18690 | x | x | x |  | 2022-04-13 | Apr | 4 | 2022 | 76111 |  |  | 123320417 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | Lewis & Tibbits damaged a 3/4" steel gas service line with a saw cutting machine while doing water work. Valid USA ticket. Facility was embedded in asphalt material | No | Gas Line | Yes | Cutting Machine | Water | Facility Embedded in Concrete | Yes | X208901859 | Dig-In to PG&E Underground | 3rd Party-Contractor | Lewis & Tibbits | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-13 | ¾” | 5 | 79 | N/A | 4 | Apr | 2022 |  |  | No
18689 | x | x | x |  | 2022-04-13 | Apr | 4 | 2022 | 76145 |  |  | 123325820 | Santa Clara | Central Coast | De Anza | Central | Mountain View | Yes | Aspen Residential damaged a 1 1/4" plastic gas service line with an excavator while maintaining/installing sewer lines. No USA ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Aspen Residential | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-13 | 1 ¼” | 36 | 29 | Believed They Knew Where Underground Utility was From Previous Knowledge | 4 | Apr | 2022 |  |  | No
18688 | x | x | x |  | 2022-04-13 | Apr | 4 | 2022 | 76132 |  |  | 123320300 | Fresno | Central Valley | Fresno | South | Clovis | Yes | M&M Pools / Premier Pools damaged a 1" plastic gas service line with a trencher while installing a gas line. Valid USA ticket. Excavated outside of delineated area | No | Gas Line | Yes | Trencher | Gas | Excavated Outside Delineated Area | Yes | X209000752 | Dig-In to PG&E Underground | 3rd Party-Contractor | M&M Pools and Designs | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-13 | 1” | 24 | 171 | N/A | 4 | Apr | 2022 |  |  | No
18687 | x | x | x |  | 2022-04-13 | Apr | 4 | 2022 | 76106 |  |  | 123315563 | Solano | Northern | Vacaville | North | Fairfield | Yes | Ghilotti Construction damaged a 1" plastic gas service line with an excavator while installing a new water line. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Water | Incorrect Facility Records / Maps | Yes | X203800425 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ghilotti Construction | Distribution Service |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-13 | 1” | 53 | 51 | N/A | 4 | Apr | 2022 |  |  | No
18685 | x | x | x |  | 2022-04-13 | Apr | 4 | 2022 | 76109 |  |  | 123317077 | Yolo | Northern | Vacaville | North | Woodland | Yes | Wahlund Construction damaged a 1/2" plastic gas service line with an excavator while installing new water lines. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Excavator | Water | Facility was not located or marked | Yes | X208902961 | Dig-In to PG&E Underground | 3rd Party-Contractor | Wahlund Construction | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-13 | ½” | 28 | 61 | N/A | 4 | Apr | 2022 | Bargaining Unit |  | No
18684 | x | x |  |  | 2022-04-13 | Apr | 4 | 2022 | 76122 |  |  |  | Marin | Bay Area | North Bay | North | Tiburon | Yes | Creative Concrete Design damaged a 1/2" plastic gas service line with a sawzall while removing a driveway. Valid USA ticket. Failed to maintain field marks | No | Gas Line | Yes | Cutting Machine | Driveway Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | X208701597 | Dig-In to PG&E Underground | 3rd Party-Contractor | Creative Concrete Design | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-13 | ½” | 9 | 26 | N/A | 4 | Apr | 2022 |  |  | No
18693 | x | x |  |  | 2022-04-14 | Apr | 4 | 2022 | 76184 |  |  |  | Alameda | Central Coast | Mission | South | Hayward | Yes | Inder Design Build LLC damaged a 3/4" steel gas service line with an excavator while grading site for installation of a foundation. Valid USA ticket. Site was cleared as no conflict. Primary cause is excavation outside delineated area | No | Gas Line | Yes | Excavator | Blading/Lot Grading | Excavated Outside Delineated Area | Yes | X207502345 | Dig-In to PG&E Underground | 3rd Party-Contractor | Inder Design Build LLC | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-14 | ¾” | 24 | 29 | Excavator believed a USA ticket was obtained by their company / representative | 4 | Apr | 2022 |  |  | No
18692 | x | x |  |  | 2022-04-14 | Apr | 4 | 2022 | 76169 |  |  |  | Contra Costa | Bay Area | Diablo | South | Antioch | Yes | Sandstone Environmental Engineering damaged a 1/2" plastic gas service line with an excavator while repairing a sewer line. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X209601698 | Dig-In to PG&E Underground | 3rd Party-Contractor | Sandstone Environmental Engineering, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-14 | ½” | 28 | 31 | N/A | 4 | Apr | 2022 |  |  | No
18691 | x | x |  |  | 2022-04-14 | Apr | 4 | 2022 | 76164 |  |  |  | Santa Clara | Central Coast | San Jose | Central | Morgan Hill | Yes | Flowrite Inc. damaged a 1" plastic gas service line with a backhoe while expanding a trench for a pending electric tie in. No USA ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Flowrite Inc | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-14 | 1” | 35 | 26 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 4 | Apr | 2022 |  |  | No
18701 | x | x | x |  | 2022-04-15 | Apr | 4 | 2022 | 76210 |  |  | 123339340 | Marin | Bay Area | North Bay | North | Novato | Yes | Homeowner damaged a 1/2" plastic gas service line with a crowbar while removing a shed. No USA ticket. | No | Gas Line | Yes | Other Hand Tools | Building Demolition | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-15 | ½” | 28 | 74 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 4 | Apr | 2022 |  |  | Yes
18700 | x | x | x |  | 2022-04-15 | Apr | 4 | 2022 | 76207 |  |  | 123345091 | Contra Costa | Bay Area | Diablo | South | Oakley | Yes | R&R Pacific Construction damaged a 1/2" plastic gas service line with an excavator while installing a water line. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Water | Incorrect Facility Records / Maps | Yes | X208301111 | Dig-In to PG&E Underground | 3rd Party-Contractor | R&R Pacific Construction | Distribution Service |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-15 | ½” | 30 | 10 | N/A | 4 | Apr | 2022 |  |  | No
18699 | x | x | x |  | 2022-04-15 | Apr | 4 | 2022 | 76193 |  |  | 123336010 | San Mateo | Central Coast | Peninsula | Central | Redwood City | Yes | West Valley Construction damaged a 1/2" plastic gas service line with an excavator while doing a gas main install. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Gas | Incorrect Facility Records / Maps | Yes | X206603281 | Dig-In to PG&E Underground | 2nd Party-Contractor | West Valley Construction | Distribution Service |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-04-15 | ½” | 20 | 14 | N/A | 4 | Apr | 2022 |  |  | No
18697 | x |  | x |  | 2022-04-15 | Apr | 4 | 2022 | 76203 |  | 45257203 |  | Madera | Central Valley | Yosemite | South | Madera | Yes | Asphalt Design damaged a 4" plastic gas main with a min-excavator while creating a driveway approach. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Driveway Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X118700766 | Dig-In to PG&E Underground | 3rd Party-Contractor | Asphalt Designs | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-15 | 4" | 32 | 72 | N/A | 4 | Apr | 2022 |  |  | No
18696 | x | x | x |  | 2022-04-15 | Apr | 4 | 2022 | 76228 |  |  | 123341772 | Contra Costa | Bay Area | Diablo | South | Walnut Creek | Yes | Golden Road Inc. (real estate company) damaged a 1" plastic gas service line with a backhoe while doing landscaping. No USA ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Golden Road Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-15 | 1” | 32 | 25 | Other | 4 | Apr | 2022 |  |  | No
18695 | x | x | x |  | 2022-04-15 | Apr | 4 | 2022 | 76192 |  |  | 123335065 | San Joaquin | Central Valley | Stockton | South | Lodi | Yes | Dietle Plumbing damaged a 2" plastic gas main with a hand tool 2-3 months prior to discovery date of damage. Dietle does not believe they caused the damage but PG&E experts believe it was them. The work performed type was sewer tie in. No USA ticket. Dietle acknowledged there were marks for other utilities present. They did not obtain a USA ticket themselves. | No | Gas Line | Yes | Other Hand Tools | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Dietle Plumbing | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-15 | 2” | 48 | 36 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 4 | Apr | 2022 |  |  | Yes
18694 | x | x | x |  | 2022-04-15 | Apr | 4 | 2022 | 76209 |  | 45257235 | 123339476 | Yuba | Northern | Sierra | North | Olivehurst | Yes | MP Nexlevel damaged a 1/2" plastic gas service line with a backhoe while installing new telecommunications lines. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W208200354 | Dig-In to PG&E Underground | 3rd Party-Contractor | MP Nexlevel | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-15 | ½” | 34 | 14 | N/A | 4 | Apr | 2022 |  |  | No
18703 | x |  |  |  | 2022-04-16 | Apr | 4 | 2022 | 76243 |  |  |  | Contra Costa | Bay Area | Diablo | South | Oakley | Yes | R&R Pacific Construction damaged a 1/2" plastic gas service line with a backhoe while trenching for a sewer line. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X208301111 | Dig-In to PG&E Underground | 3rd Party-Contractor | R&R Pacific Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-16 | ½” | 24 | 86 | N/A | 4 | Apr | 2022 |  |  | No
18702 | x | x | x |  | 2022-04-16 | Apr | 4 | 2022 | 76248 |  |  | 123345177 | Kern | Central Valley | Kern | South | Bakersfield | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while installing a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-16 | ½” | 20 | 62 | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | Yes
18704 | x | x | x |  | 2022-04-17 | Apr | 4 | 2022 | 76255 |  |  | 123345483 | Alameda | Central Coast | Mission | South | Hayward | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-17 | ½” | 28 | 38 | Excavator Did Not Believe a USA Ticket was Required | 4 | Apr | 2022 |  |  | Yes
18711 | x | x | x |  | 2022-04-18 | Apr | 4 | 2022 | 76305 |  |  | 123358138 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | SEFNCO damaged a 1" plastic gas service line with a shovel while exposing a telecommunications line. Valid USA ticket. Excavated outside delineated area | No | Gas Line | Yes | Shovel | Telecommunications | Excavated Outside Delineated Area | Yes | X208100993 | Dig-In to PG&E Underground | 3rd Party-Contractor | SEFNCO | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-18 | 1” | 41 | 30 | N/A | 4 | Apr | 2022 |  |  | Yes
18710 | x | x | x |  | 2022-04-18 | Apr | 4 | 2022 | 76286 |  |  | 123356073 | Yolo | Northern | Vacaville | North | Winters | Yes | Homeowner damaged a 1" plastic gas service line with a post-hole digger while installing a new fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-18 | 1” | 22 | 42 | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | Yes
18709 | x |  | x |  | 2022-04-18 | Apr | 4 | 2022 | 76273 |  |  | 123350139 | San Joaquin | Central Valley | Stockton | South | French Camp | Yes | Trinity Development & Construction damaged a 2" plastic gas main with an auger while installing irrigation at a new housing development. No USA ticket. | No | Gas Line | Yes | Auger | Irrigation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Trinity Development & Construction | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-18 | 2” | 36 | 9 | Other | 4 | Apr | 2022 |  |  | No
18708 | x | x | x |  | 2022-04-18 | Apr | 4 | 2022 | 76306 |  |  | 123358133 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | One Source Plumbing & Rooter damaged a 1/2" plastic gas service line with a shovel while replacing water and sewer lines. Valid USA ticket. Primary cause was failed to delineate work site with required markings | No | Gas Line | Yes | Shovel | Water | Failed to Delineate Work Site With Required Markings | Yes | X210202215 | Dig-In to PG&E Underground | 3rd Party-Contractor | One Source Plumbing & Rooter, zinc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-18 | ½” | 15 | 24 | N/A | 4 | Apr | 2022 |  |  | Yes
18830 | x | x | x | x | 2022-04-19 | Apr | 4 | 2022 | 77306 |  |  | 123569902 | Sacramento | Northern | Sacramento | North | Fair Oaks | Yes | On April 19, 2022, Fair Oaks Water District bent a 2" steel gas stub with a backhoe. This was a grade 1 leak report in April but was changed to a dig-in in May. The date discovered is May 11. Valid USA ticket. PG&E at-fault - Lcoator Error - Mismark | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Incorrect Information or Marks | Yes | X210200754 | Dig-In to PG&E Underground | 3rd Party-Government Entity | Fair Oaks Water District | Distribution Service |  | Yes | Locator Error - Mismark |  |  | 2022 Q2 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-05-11 | 2” | 26 | 8 | N/A | 5 | May | 2022 | Bargaining Unit | N/A | No
18719 |  | x |  |  | 2022-04-19 | Apr | 4 | 2022 | 76350 |  |  |  | San Mateo | Central Coast | Peninsula | Central | Redwood City | Yes | Preston Pipelines damaged the wrap on an 8" steel gas main with vacuum equipment while attempting to locate the main. Valid USA ticket. Inadequate excavation practices. | Yes | Gas Line | No | Vacuum Equipment | Pipeline Work - Liquid | Inadequate Excavation Practices | Yes | X209503160 | Dig-In to PG&E Underground | 3rd Party-Contractor | Preston Pipelines | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-19 | 8" | 36 | 0 | N/A | 4 | Apr | 2022 |  |  | No
18718 | x | x | x |  | 2022-04-19 | Apr | 4 | 2022 | 76337 |  |  | 123370483 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | PG&E Gas damaged a 2" plastic gas main with an excavator while doing a gas main replacement. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X210201123 | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Gas | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Blue | PG&E GDGC |  |  | 1st Party Gas | Yes | 2022-04-19 | 2” | 48 | 111 | N/A | 4 | Apr | 2022 |  |  | No
18716 | x | x | x |  | 2022-04-19 | Apr | 4 | 2022 | 76343 |  |  | 123367696 | San Mateo | Central Coast | Peninsula | Central | San Carlos | Yes | Casey Construction damaged a 1/2" plastic gas service line with an excavator while digging a trench for new electric conduits. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Electric Work | Incorrect Facility Records / Maps | Yes | X210400950 | Dig-In to PG&E Underground | 3rd Party-Contractor | Casey Construction | Distribution Service |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-19 | 1” | 18 | 29 | N/A | 4 | Apr | 2022 |  |  | No
18715 | x | x | x |  | 2022-04-19 | Apr | 4 | 2022 | 76329 |  |  | 123363790 | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Homeowner damaged a 1/2" plastic gas service line with a digging bar while constructing a platform for garbage cans. No USA ticket. | No | Gas Line | Yes | Digging Bar | Other | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-19 | ½” | 24 | 11 | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | Yes
18714 | x | x | x |  | 2022-04-19 | Apr | 4 | 2022 | 76321 |  |  | 123362109 | San Joaquin | Central Valley | Stockton | South | Tracy | Yes | Samco Construction Inc damaged a 1/2" plastic gas service line with a shovel while upgrading the residential electric line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | X113001082 | Dig-In to PG&E Underground | 3rd Party-Contractor | Samco Construction Inc | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-19 | ½” | 36 | 11 | N/A | 4 | Apr | 2022 |  |  | Yes
18713 | x | x | x |  | 2022-04-19 | Apr | 4 | 2022 | 76357 |  |  | 123371927 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | San Francisco Water Department damaged a 2" plastic gas main with a backhoe while repairing a broken water main. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X210502407 | Dig-In to PG&E Underground | 3rd Party-Government Entity | San Francisco Water Department | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-04-19 | 2” | 39 | 83 | N/A | 4 | Apr | 2022 |  |  | No
18712 | x | x | x |  | 2022-04-19 | Apr | 4 | 2022 | 76347 |  |  | 123369290 | Contra Costa | Bay Area | Diablo | South | Moraga | Yes | STC Netcom, Inc. damaged a 4" plastic gas main with a shovel while installing telecommunication lines. No USA ticket. | No | Gas Line | Yes | Shovel | Telecommunications | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | STC Netcom, Inc. | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-19 | 4" | 42 | 161 | Excavator Did Not Believe a USA Ticket was Required | 4 | Apr | 2022 |  |  | Yes
18726 | x | x | x |  | 2022-04-20 | Apr | 4 | 2022 | 76410 |  |  | 123380956 | Placer | Northern | Sierra | North | Roseville | Yes | Juan Excavator Service damaged a 2" plastic gas main with a mini-excavator while doing site development. Valid USA ticket. | No | Gas Line | Yes | Excavator | Site Development | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Juan Excavator Service | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-20 | 2” | 56 | 77 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 4 | Apr | 2022 |  |  | No
18725 | x | x | x |  | 2022-04-20 | Apr | 4 | 2022 | 76393 |  |  | 123379421 | Alameda | Central Coast | Mission | South | Dublin | Yes | DL Construction damaged a 1" plastic gas service line with a shovel while exposing the gas line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | W208800160 | Dig-In to PG&E Underground | 3rd Party-Contractor | DL Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-20 | 1” | 48 | 40 | N/A | 4 | Apr | 2022 |  |  | Yes
18722 | x | x |  |  | 2022-04-20 | Apr | 4 | 2022 | 76411 |  |  |  | Sutter | Northern | Sierra | North | Yuba City | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while installing a mailbox post. No USA ticket. | No | Gas Line | Yes | Shovel | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-20 | ½” | 34 | 88 | Excavator Did Not Believe a USA Ticket was Required | 4 | Apr | 2022 |  |  | Yes
18721 | x | x |  |  | 2022-04-20 | Apr | 4 | 2022 | 76372 |  |  |  | Madera | Central Valley | Yosemite | South | Madera | Yes | Tri County Excavation damaged a 1" plastic gas purge point attached to a 2" plastic gas main with a scraper while leveling a site for a new housing development. No USA ticket. | No | Gas Line | Yes | Grader/Scraper | Site Development | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Tri County Excavation Inc | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-20 | 1” | 4 | 143 | Knew About USA Ticket Requirement But Chose Not to Call | 4 | Apr | 2022 |  |  | No
18720 | x | x | x |  | 2022-04-20 | Apr | 4 | 2022 | 76400 |  |  | 123379715 | Alameda | Bay Area | East Bay | Central | Alameda | Yes | LTG Construction damaged a 1" plastic gas service line with a wooden stake while doing foundation work. Expired USA ticket. Primary cause was failure to maintain field marks | No | Gas Line | Yes | Stake | Foundation Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | No (expired) | X134101019 | Dig-In to PG&E Underground | 3rd Party-Contractor | LTG Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-20 | 1” | 19 | 22 | Expired USA ticket | 4 | Apr | 2022 |  |  | Yes
18730 | x | x |  |  | 2022-04-21 | Apr | 4 | 2022 | 76425 |  |  |  | Sacramento | Northern | Sacramento | North | Elk Grove | Yes | Golden State Utility damaged a 1/2" plastic gas service line with boring equipment while installing telecommunication conduit. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Boring Equipment | Telecommunications | Facility was not located or marked | Yes | X205500244 | Dig-In to PG&E Underground | 3rd Party-Contractor | Golden State Utility | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-21 | ½” | 27 | 97 | N/A | 4 | Apr | 2022 | Bargaining Unit |  | No
18729 | x | x | x |  | 2022-04-21 | Apr | 4 | 2022 | 76419 |  |  | 123383677 | Marin | Bay Area | North Bay | North | Novato | Yes | Homeowner damaged a 1" plastic gas service line with a metal stake while building a fence. No USA ticket. | No | Gas Line | Yes | Stake | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-21 | 1” | 24 | 56 | Knew About USA Ticket Requirement But Chose Not to Call | 4 | Apr | 2022 |  |  | Yes
18727 | x | x | x |  | 2022-04-21 | Apr | 4 | 2022 | 76418 |  |  | 123384031 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Unlicensed contractor damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-21 | ½” | 18 | 28 | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | Yes
18735 | x | x | x |  | 2022-04-22 | Apr | 4 | 2022 | 76446 |  |  | 123397438 | Contra Costa | Bay Area | East Bay | Central | Kensington | Yes | EBMUD damaged a 1/2" steel gas service line with an excavator while doing a water main installation. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | No | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X135101170 | Dig-In to PG&E Underground | 3rd Party-Government Entity | EBMUD | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Green |  | Confirmed Late Tickets with Dig-Ins |  | 3rd Party Gas | Yes | 2022-04-22 | ½” |  |  | N/A | 4 | Apr | 2022 |  |  | No
18734 | x | x | x |  | 2022-04-22 | Apr | 4 | 2022 | 76450 |  |  | 123393619 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Teichert Pipelines damaged a 1/2" plastic gas service line with a shovel while locating the gas line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | X200403145 | Dig-In to PG&E Underground | 2nd Party-Contractor | Teichert Pipelines | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-04-22 | ½” | 13 | 22 | N/A | 4 | Apr | 2022 |  |  | Yes
18733 | x | x | x |  | 2022-04-22 | Apr | 4 | 2022 | 76460 |  |  | 123396894 | Santa Clara | Central Coast | San Jose | Central | Milpitas | Yes | 804 Construction damaged a 1/2" plastic gas service line with a shovel while trenching for new electrical upgrades. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | X209402963 | Dig-In to PG&E Underground | 3rd Party-Contractor | 804 Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-22 | ½” | 27 | 23 | N/A | 4 | Apr | 2022 |  |  | Yes
18736 | x | x | x |  | 2022-04-23 | Apr | 4 | 2022 | 76486 |  |  | 123403954 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence post. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-23 | ½” | 30 | 4 | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | Yes
18740 | x | x | x |  | 2022-04-25 | Apr | 4 | 2022 | 76511 |  |  | 123409940 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Homeowner damaged a 1/2" plastic gas service line inserted into steel with a backhoe while repairing a sewer line. No USA ticket. | No | Gas Line | No | Backhoe/Trackhoe | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-25 | ½” |  |  | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | No
18739 | x | x | x |  | 2022-04-25 | Apr | 4 | 2022 | 76552 |  |  | 123420686 | Sonoma | Northern | Sonoma | North | Sebastopol | Yes | Heritage Fence damaged a 1/2" plastic gas service line inserted into 3/4" steel with a auger attached to a skid steer while replacing a fence. Valid USA ticket. Excavated outside delineated area | No | Gas Line | Yes | Auger | Fencing | Excavated Outside Delineated Area | Yes | X211101810 | Dig-In to PG&E Underground | 3rd Party-Contractor | Heritage Fence | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-25 | ½” | 30 | 59 | N/A | 4 | Apr | 2022 |  |  | No
18738 | x | x | x |  | 2022-04-25 | Apr | 4 | 2022 | 76539 |  |  | 123411139 | Napa | Bay Area | North Bay | North | Calistoga | Yes | Duckworth Backhoe damaged a 2" plastic gas service line with a excavator while installing electrical conduit. Expired USA ticket. Primary cause was failure to protect exposed facility | No | Gas Line | Yes | Excavator | Electric Work | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X206301905 | Dig-In to PG&E Underground | 3rd Party-Contractor | Duckworth Backhoe | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-25 | 2” | 52 | 75 | Expired USA ticket | 4 | Apr | 2022 |  |  | No
18737 | x | x | x |  | 2022-04-25 | Apr | 4 | 2022 | 76526 |  |  | 123420270 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while planting a tree. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-25 | ½” | 3 | 35 | Excavator Did Not Believe a USA Ticket was Required | 4 | Apr | 2022 |  |  | Yes
18748 | x | x | x |  | 2022-04-26 | Apr | 4 | 2022 | 76592 |  |  | 123426839 | Yuba | Northern | Sierra | North | Marysville | Yes | Takehara Landscaping damaged a 1/2" plastic gas service line with a pickaxe while installing irrigation. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Pickaxe | Irrigation | Failed to Dig with Care | Yes | X204901667 | Dig-In to PG&E Underground | 3rd Party-Contractor | Takehara Landscaping | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-26 | ½” | 28 | 5 | N/A | 4 | Apr | 2022 |  |  | Yes
18747 | x | x | x |  | 2022-04-26 | Apr | 4 | 2022 | 76558 |  |  | 123424270 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence post. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-26 | ½” | 36 | 23 | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | Yes
18746 | x |  | x |  | 2022-04-26 | Apr | 4 | 2022 | 76620 |  |  | 123433378 | San Joaquin | Central Valley | Stockton | South | Lodi | Yes | Racardis damaged a 1" plastic gas service line with a backhoe while conducting excavations on his property related to property development. Valid USA ticket. Excavated prior to receiving a positive response from all utilities | No | Gas Line | Yes | Backhoe/Trackhoe | Site Development | Excavated Prior to Receiving a Positive Response From All Utilities | Yes | X210903005 | Dig-In to PG&E Underground | 3rd Party-Contractor | Racardos | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-26 | 1” | 42 | 117 | N/A | 4 | Apr | 2022 |  |  | No
18745 | x | x | x |  | 2022-04-26 | Apr | 4 | 2022 | 76603 |  | 45268130 | 123429969 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | All Bay Plumbing damaged a 1/2" plastic gas service line with a shovel while replacing a sewer. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | W211200287 | Dig-In to PG&E Underground | 3rd Party-Contractor | All Bay Plumbing | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-26 | ½” | 24 | 22 | N/A | 4 | Apr | 2022 |  |  | Yes
18744 | x | x | x |  | 2022-04-26 | Apr | 4 | 2022 | 76610 |  |  | 123431657 | Yolo | Northern | Vacaville | North | Woodland | Yes | Epic Pools and Landscape damaged a 1/2" plastic gas service line with a pickaxe while doing water work. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Pickaxe | Water | Failed to Dig with Care | Yes | X210102394 | Dig-In to PG&E Underground | 3rd Party-Contractor | Epic Pools and Landscaping | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-26 | ½” | 20 | 18 | N/A | 4 | Apr | 2022 |  |  | Yes
18743 | x | x | x |  | 2022-04-26 | Apr | 4 | 2022 | 76578 |  | 45267918 | 123425562 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Homeowner damaged a 1/2" plastic gas service line with a pickaxe while trenching for electric facilities. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Pickaxe | Electric Work | Failed to Dig with Care | Yes | W209400201 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-26 | ½” | 24 | 23 | N/A | 4 | Apr | 2022 |  |  | Yes
18742 | x | x | x |  | 2022-04-26 | Apr | 4 | 2022 | 76567 |  |  | 123424651 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | PG&E Gas damaged a 1/2" plastic gas service line with an excavator while installing a new gas main. Valid USA ticket. PG&E at-fault - Locator Error - Mismark | No | Gas Line | Yes | Excavator | Gas | Incorrect information or marks | Yes | X203902293 | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Gas | Distribution Service |  | Yes | Locator Error - Mismark |  |  | 2022 Q2 |  |  |  | Yes | Blue | PG&E GDGC |  |  | 1st Party Gas | Yes | 2022-04-26 | ½” | 31 | 14 | N/A | 4 | Apr | 2022 | Bargaining Unit |  | No
18741 | x | x | x |  | 2022-04-26 | Apr | 4 | 2022 | 76616 |  |  | 123433377 | Sonoma | Northern | Sonoma | North | Petaluma | Yes | New Visions Building and Specialties Inc. damaged a 1 1/4" plastic gas service line with a probe while installing electrical conduit. No USA ticket. | No | Gas Line | Yes | Probing Tool | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | New Visions Building and Specialties Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-26 | 1 ¼” | 52 | 108 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 4 | Apr | 2022 |  |  | Yes
18751 | x | x | x |  | 2022-04-27 | Apr | 4 | 2022 | 76638 |  |  | 123439162 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Homeowner damaged a 3/4" steel gas service line with a sawzall while removing retaining walls. No USA ticket. | No | Gas Line | Yes | Cutting Machine | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-27 | ¾” | 10 | 39 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 4 | Apr | 2022 |  |  | No
18750 | x |  | x |  | 2022-04-27 | Apr | 4 | 2022 | 76637 |  |  | 123436768 | Alameda | Bay Area | Mission | South | Union City | Yes | Diablo Plumbing damaged a 1 1/4" plastic gas service line with a excavator while replacing a sewer line. No USA ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Diablo Plumbing | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-27 | 1 ¼” | 24 | 30 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 4 | Apr | 2022 |  |  | No
18749 | x | x | x |  | 2022-04-27 | Apr | 4 | 2022 | 76645 |  | 45269468 | 123438636 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | City of Modesto damaged a 2" plastic gas main with a 1/2" steel cable attached to a reamer while while replacing a water pipe. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Other Driven Machinery | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X211001701 | Dig-In to PG&E Underground | 3rd Party-Government Entity | City of Modesto | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-04-27 | 2” | 18 | 71 | N/A | 4 | Apr | 2022 |  |  | No
18757 | x | x |  |  | 2022-04-28 | Apr | 4 | 2022 | 76697 |  |  |  | San Mateo | Central Coast | Peninsula | Central | East Palo Alto | Yes | Preston Pipelines damaged a 4" plastic gas main with an excavator while installing electrical conduit. Valid USA ticket. PG&E at-fault - Locator Error - Mismark | No | Gas Line | Yes | Excavator | Electric Work | Incorrect information or marks | Yes | X205600126 | Dig-In to PG&E Underground | 3rd Party-Contractor | Preston Pipelines | Distribution Main |  | Yes | Locator Error - Mismark |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-28 | 4" | 48 | 197 | N/A | 4 | Apr | 2022 | Bargaining Unit |  | No
18756 | x |  |  |  | 2022-04-28 | Apr | 4 | 2022 | 76716 |  |  | 123456220 | Alameda | Bay Area | Mission | South | Newark | Yes | LS Construction damaged 2" plastic gas main with an excavator while doing a service line upgrade. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X211500029 | Dig-In to PG&E Underground | 3rd Party-Contractor | LS Construction | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-28 | 2” | 60 | 71 | N/A | 4 | Apr | 2022 |  |  | No
18755 | x | x |  |  | 2022-04-28 | Apr | 4 | 2022 | 76719 |  |  | 123451381 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Teichert Pipelines damaged a 1/2" plastic gas service line with a trencher while replacing Aldyl-A gas lines. Valid USA ticket. PG&E at-fault - Other Error | No | Gas Line | Yes | Trencher | Gas | Incorrect information or marks | Yes | X200403182 | Dig-In to PG&E Underground | 2nd Party-Contractor | Teichert Pipelines | Distribution Service |  | Yes | Other Error |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-04-28 | ½” | 24 | 50 | N/A | 4 | Apr | 2022 |  |  | No
18754 | x |  |  |  | 2022-04-28 | Apr | 4 | 2022 | 76695 |  |  | 123446529 | Alameda | Bay Area | Mission | South | Fremont | Yes | PL Fence damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence post. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | PL Fence | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-28 | ½” | 25 | 38 | Knew About USA Ticket Requirement But Chose Not to Call | 4 | Apr | 2022 |  |  | Yes
18752 | x | x |  |  | 2022-04-28 | Apr | 4 | 2022 | 76715 |  |  | 123449984 | Placer | Northern | Sierra | North | Auburn | Yes | Homeowner damaged a 3/4" steel gas service line with a concrete saw while doing storm drain/culvert work. No USA ticket. | No | Gas Line | Yes | Cutting Machine | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-28 | ¾” | 4 | 48 | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | No
18762 | x |  |  |  | 2022-04-29 | Apr | 4 | 2022 | 76752 |  |  | 123457559 | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while planting a plant. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-29 | ½” |  | 33 | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | Yes
18761 | x |  |  |  | 2022-04-29 | Apr | 4 | 2022 | 76742 |  |  | 123456964 | Shasta | Northern | North Valley | North | Redding | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a digging bar while building a new fence. No USA ticket. | No | Gas Line | Yes | Digging Bar | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-29 | ½” | 22 | 42 | Other | 4 | Apr | 2022 |  |  | Yes
18760 | x | x | x |  | 2022-04-29 | Apr | 4 | 2022 | 76739 |  |  | 123458258 | El Dorado | Northern | Sierra | North | El Dorado Hills | Yes | Lemoore Fencing damaged a 1/2" plastic gas service line with a post-hole digger while hand digging fence posts. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Lemoore Fencing | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-29 | ½” | 25 | 66 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 4 | Apr | 2022 |  |  | Yes
18759 | x |  |  |  | 2022-04-29 | Apr | 4 | 2022 | 76733 |  |  | 123455377 | Marin | Bay Area | North Bay | North | San Rafael | Yes | St. Francis Electric damaged a 1" plastic gas service line with an excavator while installing telecommunicaton lines. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Telecommunications | Incorrect Facility Records / Maps | Yes | X207001704 | Dig-In to PG&E Underground | 3rd Party-Contractor | St. Francis Electric | Distribution Service |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-04-29 | 1” |  | 82 | N/A | 4 | Apr | 2022 |  |  | No
18764 | x | x |  |  | 2022-04-30 | Apr | 4 | 2022 | 76784 |  |  | 123466378 | Fresno | Central Valley | Fresno | South | Selma | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while removing a tree stump. No USA ticket. | No | Gas Line | Yes | Shovel | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-30 | ½” | 18 | 37 | No Knowledge of USA Ticketing Process | 4 | Apr | 2022 |  |  | Yes
18763 | x |  |  |  | 2022-04-30 | Apr | 4 | 2022 | 76786 |  |  | 123467596 | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | Homeowner damaged a 1/2" plastic gas service line inserted into 3/4" steel gas with a shovel while planting a plant. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-04-30 | ½” | 15 | 40 | Other | 4 | Apr | 2022 |  |  | Yes
18769 | x | x | x | x | 2022-05-01 | May | 5 | 2022 | 76808 |  |  | 123469480 | Kern | Central Valley | Kern | South | Bakersfield | Yes | Homeowner damaged a 1/2" plastic gas service line with an auger while extending a fence. No USA ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-01 | ½” | 30 | 83 | Knew About 811 Process, But Asserted They Didn’t Want to Wait the Required Time for Markings | 5 | May | 2022 |  | N/A | No
18776 | x | x |  | x | 2022-05-02 | May | 5 | 2022 | 76822 |  |  |  | Sacramento | Northern | Sacramento | North | Orangevale | Yes | Homeowner damaged a 3/4" steel gas service line with a skid steer while installing a retaining wall. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | No | Skid Steer | Landscaping | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W205500139 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-02 | ¾” |  | 0 | N/A | 5 | May | 2022 |  | N/A | No
18775 | x | x | x | x | 2022-05-02 | May | 5 | 2022 | 76862 |  |  | 123478438 | Marin | Bay Area | North Bay | North | San Rafael | Yes | Arntz Builders damaged a 1" plastic gas service line with a shovel while building a concrete ramp into a commercial building. No USA ticket. | No | Gas Line | Yes | Shovel | Building Construction | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Arntz Builders | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-02 | 1” | 18 | 18 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2022 |  | 856393 | Yes
18774 | x | x | x | x | 2022-05-02 | May | 5 | 2022 | 76835 |  |  | 123475811 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Rossetti & Sons Construction damaged a 1/2" plastic gas service line with a pickaxe while installing irrigation lines. No USA ticket. | No | Gas Line | Yes | Pickaxe | Irrigation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Rossetti & Sons Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-02 | ½” | 10 | 16 | Believed They Knew Where Underground Utility was From Previous Knowledge | 5 | May | 2022 |  | 791569 | Yes
18773 | x | x | x | x | 2022-05-02 | May | 5 | 2022 | 76844 |  |  | 123477061 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Marin Building & Development damaged a 1/2" plastic gas service line with an excavator while doing various landscaping. No USA ticket. | No | Gas Line | Yes | Excavator | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Marin Building & Development Inc | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-02 | ½” | 8 | 23 | Other | 5 | May | 2022 |  | 1064435 | No
18772 | x | x | x | x | 2022-05-02 | May | 5 | 2022 | 76857 |  |  | 123477949 | Yuba | Northern | Sierra | North | Marysville | Yes | Lemon construction damaged a 1/2" plastic gas service line with a backhoe while installing new sidewalks. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Curb/Sidewalk Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X204801483 | Dig-In to PG&E Underground | 3rd Party-Contractor | Lemon Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-02 | ½” | 33 | 34 | N/A | 5 | May | 2022 |  |  | No
18771 | x | x | x | x | 2022-05-02 | May | 5 | 2022 | 76877 |  |  | 123482138 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Homeowner damaged 1" plastic gas service line with an excavator while planting some trees. No USA ticket. | No | Gas Line | Yes | Excavator | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-02 | 1” | 18 | 53 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | N/A | No
18770 | x | x | x | x | 2022-05-02 | May | 5 | 2022 | 76866 |  |  | 123479466 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Hoseley Corporation damaged a 1/2" plastic gas service line with a mini-excavator while excavating a roadway. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Road Work | Incorrect Facility Records / Maps | Yes | X031000628 | Dig-In to PG&E Underground | 3rd Party-Contractor | Hoseley Corporation | Distribution Service |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-02 | ½” | 23 | 28 | N/A | 5 | May | 2022 |  | 1000494 | No
18783 | x | x | x | x | 2022-05-03 | May | 5 | 2022 | 76903 |  | 45277579 | 123488287 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Warren’s Masonry damaged a 1/2" plastic gas service line with a shovel while creating a foundation for a masonry wall. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Foundation Work | Failed to Dig with Care | Yes | X209500500 | Dig-In to PG&E Underground | 3rd Party-Contractor | Warren’s Masonry | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-03 | ½” | 27 | 33 | N/A | 5 | May | 2022 |  | 1033577 | Yes
18782 | x | x | x | x | 2022-05-03 | May | 5 | 2022 | 76943 |  |  | 123490531 | Contra Costa | Bay Area | Diablo | South | Discovery Bay | Yes | Homeowner damaged a 1" plastic gas service line with a shovel while installing a new electric line. No USA ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-03 | 1” | 18 | 14 | No Knowledge of USA Ticketing Process | 5 | May | 2022 |  | N/A | Yes
18781 | x | x | x | x | 2022-05-03 | May | 5 | 2022 | 76950 |  |  | 123492112 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with an excavator while replacing a septic system. No USA ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-03 | 1” | 60 | 80 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | N/A | No
18780 | x | x | x | x | 2022-05-03 | May | 5 | 2022 | 76914 |  |  | 123491081 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Jesse Concrete Inc damaged a 1/2" plastic gas service line with a sawzall while cutting tree roots around the exposed facility. Valid USA ticket. Failed to protect subsurface installation. | No | Gas Line | Yes | Cutting Machine | Driveway Work | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | W211100499 | Dig-In to PG&E Underground | 3rd Party-Contractor | Jesse Concrete, Inc | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-03 | ½” | 10 | 48 | N/A | 5 | May | 2022 |  | 1013013 | No
18779 | x | x | x | x | 2022-05-03 | May | 5 | 2022 | 76949 |  |  | 123491215 | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while doing fence work. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-03 | ½” | 18 | 36 | No Knowledge of USA Ticketing Process | 5 | May | 2022 |  | N/A | Yes
18778 | x | x | x | x | 2022-05-03 | May | 5 | 2022 | 76947 |  |  | 123491177 | Monterey | Central Coast | Central Coast | South | Seaside | Yes | Homeowner damaged a 1/2" plastic gas service line with a pickaxe while digging a post hole. No USA ticket. | No | Gas Line | Yes | Pickaxe | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-03 | ½” | 16 | 31 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | N/A | Yes
18794 | x | x | x | x | 2022-05-04 | May | 5 | 2022 | 76973 |  |  | 123495714 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Sinclair Concrete damaged a 1" damaged a 1/2" plastic gas service line with a backhoe while excavating for a foundation. No USA ticket. Contractor was digging under another companies ticket and the marks were accurate. Primary cause was failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Foundation Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Sinclair Concrete | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-04 | 1” | 24 | 22 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2022 |  | 587839 | No
18792 | x | x | x | x | 2022-05-04 | May | 5 | 2022 | 76964 |  |  | 123499182 | Alameda | Central Coast | Mission | South | Fremont | Yes | Henkels & McCoy damaged a 2" plastic gas main with a backhoe while installing new gas service lines. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X203303342 | Dig-In to PG&E Underground | 2nd Party-Contractor | Henkels & McCoy | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-05-04 | 2” | 40 | 45 | N/A | 5 | May | 2022 |  | 183393 | No
18791 | x | x |  | x | 2022-05-04 | May | 5 | 2022 | 77007 |  |  |  | Yuba | Northern | Sierra | North | Marysville | Yes | Teichert Construction damaged a 1/2" plastic gas service line with a backhoe while installing new underground utilities. Valid USA ticket. See documentation for further root cause analysis | No | Gas Line | Yes | Backhoe/Trackhoe | Gas | Other | Yes | X204902550 | Dig-In to PG&E Underground | 3rd Party-Contractor | Teichert Construction | Distribution Service |  | Yes | Other Error |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-04 | ½” | 36 | 26 | N/A | 5 | May | 2022 |  | 8 | No
18790 | x | x | x | x | 2022-05-04 | May | 5 | 2022 | 76963 |  |  | 123495630 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Rosemont Construction damaged a 1/2" plastic gas service line with a shovel while excavating for a new sewer line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | X201701220 | Dig-In to PG&E Underground | 3rd Party-Contractor | Rosemont Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-04 | ½” | 15 | 17 | N/A | 5 | May | 2022 |  | 482113 | Yes
18789 | x | x | x | x | 2022-05-04 | May | 5 | 2022 | 76970 |  |  | 123495963 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Homeowner damaged a 1" plastic gas service line with a shovel while installing a new water line. No USA ticket. | No | Gas Line | Yes | Shovel | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-04 | 1” | 28 | 43 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2022 |  | N/A | Yes
18788 | x | x |  | x | 2022-05-04 | May | 5 | 2022 | 77009 |  |  |  | Sutter | Northern | Sierra | North | Yuba City | Yes | Advanced Telecommunications damaged a 2" plastic gas main with boring equipment while installing new telecommunication conduit. Valid USA ticket. Failed to maintain clearance | No | Gas Line | Yes | Boring Equipment | Telecommunications | Excavator Failed to Maintain Clearance After Verifying Marks | Yes | X211500311 | Dig-In to PG&E Underground | 3rd Party-Contractor | Advanced Telecommunications | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-04 | 2” | 65 | 227 | N/A | 5 | May | 2022 |  | 803509 | No
18787 | x | x |  | x | 2022-05-04 | May | 5 | 2022 | 76982 |  |  |  | Contra Costa | Bay Area | East Bay | Central | Rodeo | Yes | Miller Pipeline damaged a 1/2" plastic gas service line with a pneumatic chipping hammer while doing gas main and service replacements. Valid USA ticket. Line was exposed when damaged. Failed to protect exposed facility | No | Gas Line | Yes | Other Hand Machinery | Gas | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X206803134 | Dig-In to PG&E Underground | 2nd Party-Contractor | Miller Pipeline | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GTGC |  |  | 2nd Party Gas | Yes | 2022-05-04 | ½” | 36 | 19 | N/A | 5 | May | 2022 |  | 978749 | No
18785 | x | x |  | x | 2022-05-04 | May | 5 | 2022 | 76983 |  |  |  | Alameda | Central Coast | Mission | South | Dublin | Yes | San Ramon Concrete damaged a 3/4" steel gas service line with a skid steer while replacing a driveway. No USA ticket. | Yes | Gas Line | No | Skid Steer | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | San Ramon Concrete | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-04 | ¾” | 8 | 0 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2022 |  | 761564 | No
18804 | x | x | x | x | 2022-05-05 | May | 5 | 2022 | 77053 |  |  | 123516938 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while doing a post hole for a mailbox. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-05 | ½” | 18 | 6 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | N/A | Yes
18803 | x | x | x | x | 2022-05-05 | May | 5 | 2022 | 77035 |  |  | 123516659 | Contra Costa | Bay Area | Diablo | South | Orinda | Yes | Rooter Hero Plumbing damaged a 1" plastic gas service line while pipe bursting to install a new sewer line. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Pipe Bursting | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X211902468 | Dig-In to PG&E Underground | 3rd Party-Contractor | Rooter Hero Plumbing | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-05 | 1” | 20 | 118 | N/A | 5 | May | 2022 |  | 1028886 | No
18802 | x | x | x | x | 2022-05-05 | May | 5 | 2022 | 77036 |  |  | 123515652 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Trinity Building damaged a 1" plastic gas service line with a digging bar while installing electrical to an ADU. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Digging Bar | Electric Work | Failed to Dig with Care | Yes | X126303342 | Dig-In to PG&E Underground | 3rd Party-Contractor | Trinity Building | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-05 | 1” | 28 | 43 | N/A | 5 | May | 2022 |  | 928369 | Yes
18801 | x | x | x | x | 2022-05-05 | May | 5 | 2022 | 77043 |  |  | 123515925 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Maggiora & Ghilotti Inc damaged a 1" plastic gas service line with a probe while replacing a water main. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Probing Tool | Water | Failed to Dig with Care | Yes | X207701293 | Dig-In to PG&E Underground | 3rd Party-Contractor | Maggiora & Ghilotti Inc | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-05 | 1” | 36 | 24 | N/A | 5 | May | 2022 |  | 226767 | Yes
18800 | x | x | x | x | 2022-05-05 | May | 5 | 2022 | 77049 |  |  | 123518905 | Sonoma | Northern | Sonoma | North | Sebastopol | Yes | Homeowner damaged a 2" plastic gas service line with a bulldozer with ripper blade while trenching for vineyard rows. No USA ticket. | No | Gas Line | Yes | Bulldozer | Agriculture | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-05 | 2” | 30 | 90 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | N/A | No
18799 | x | x |  | x | 2022-05-05 | May | 5 | 2022 | 77064 |  |  |  | Monterey | Central Coast | Central Coast | South | Salinas | Yes | Vandervort Backhoe Service damaged a 4" plastic gas main with a trench attachment on a skid steer while installing new gas lines. No USA ticket. | No | Gas Line | Yes | Skid Steer | Gas | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Vandervort Backhoe Service | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-05 | 4" | 48 | 151 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | 894693 | No
18798 | x | x |  | x | 2022-05-05 | May | 5 | 2022 | 77021 |  |  |  | Alameda | Bay Area | East Bay | Central | Alameda | Yes | West Valley Construction damaged a 1" plastic gas service line with a shovel while performing gas service replacements. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | X203402535 | Dig-In to PG&E Underground | 2nd Party-Contractor | West Valley Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-05-05 | 1” | 20 | 34 | N/A | 5 | May | 2022 |  | 174968 | Yes
18797 | x | x |  | x | 2022-05-05 | May | 5 | 2022 | 77047 |  |  |  | Merced | Central Valley | Yosemite | South | Merced | Yes | Midcal Pipeline & Utilities damaged a 1/2" plastic gas service line with a backhoe while replacing a sidewalk. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Backhoe/Trackhoe | Curb/Sidewalk Work | Facility was not Located or Marked | Yes | X209002933 | Dig-In to PG&E Underground | 3rd Party-Contractor | Midcal Pipeline & Utilities | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-05 | ½” | 20 | 33 | N/A | 5 | May | 2022 | Bargaining Unit | 455113 | No
18796 | x | x |  | x | 2022-05-05 | May | 5 | 2022 | 77058 |  |  |  | Monterey | Central Coast | Central Coast | South | Salinas | Yes | First Light Farm Services damaged a 4" steel gas main with a tractor while ripping agriculture property. No USA ticket. | No | Gas Line | Yes | Tractor | Agriculture | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | First Light Farm Services | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-05 | 4" | 30 | 121 | No Knowledge of USA Ticketing Process | 5 | May | 2022 |  |  | No
18810 | x | x | x | x | 2022-05-06 | May | 5 | 2022 | 77086 |  |  | 123524520 | Yolo | Northern | Vacaville | North | Woodland | Yes | Argonaut Constructors damaged a 1/2" plastic gas service line with a backhoe while installing new water and sewer facilities. Valid USA ticket. Failed to maintain clearance | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Excavator Failed to Maintain Clearance After Verifying Marks | Yes | X206600087 | Dig-In to PG&E Underground | 3rd Party-Contractor | Argonaut Constructors | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-06 | ½” | 40 | 51 | N/A | 5 | May | 2022 |  | 171432 | No
18809 | x | x | x | x | 2022-05-06 | May | 5 | 2022 | 77096 |  |  | 123529959 | Santa Cruz | Central Coast | Central Coast | South | Watsonville | Yes | MGE Underground damaged a 2" plastic gas main with boring equipment while installing electric lines. Valid USA ticket. PG&E at-fault - Locator Error - Mismarked | No | Gas Line | Yes | Boring Equipment | Electric Work | Incorrect Information or Marks | Yes | X211600873 | Dig-In to PG&E Underground | 2nd Party-Contractor | MGE Underground | Distribution Main |  | Yes | Locator Error - Mismark |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GC Electric |  |  | 2nd Party Gas | Yes | 2022-05-06 | 2” | 38 | 85 | N/A | 5 | May | 2022 | Bargaining Unit | 765025 | No
18808 | x | x |  |  | 2022-05-06 | May | 5 | 2022 | 77110 |  |  |  | Napa | Bay Area | North Bay | North | Napa | Yes | Homeowner damaged a 3/4" steel gas service line with a bobcat while grading his front yard. No USA ticket. | Yes | Gas Line | No | Backhoe/Trackhoe | Blading/Lot Grading | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-06 | ¾” |  | 0 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | N/A | No
18807 | x | x |  | x | 2022-05-06 | May | 5 | 2022 | 77095 |  |  |  | Santa Clara | Central Coast | San Jose | Central | Milpitas | Yes | Synergy 768 Inc. damaged a 1/2" plastic gas service line with a battery powered saw while installing electrical conduit. No USA ticket. | No | Gas Line | Yes | Cutting Machine | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Synergy 768 Inc | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-06 | ½” | 48 | 42 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2022 |  | 994847 | No
18806 | x | x | x | x | 2022-05-06 | May | 5 | 2022 | 77087 |  |  | 123524785 | Stanislaus | Central Valley | Yosemite | South | Oakdale | Yes | City of Oakdale damaged a 2" plastic gas main with a backhoe while repairing a water pipe. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Facility was not Located or Marked | Yes | X212302337 | Dig-In to PG&E Underground | 3rd Party-Government Entity | City of Oakdale | Distribution Main |  | Yes | Locator Error - No Mark |  |  | 2022 Q2 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-05-06 | 2” | 36 | 48 | N/A | 5 | May | 2022 | Contractor |  | No
18811 | x | x | x | x | 2022-05-08 | May | 5 | 2022 | 77149 |  |  | 123538362 | Contra Costa | Bay Area | Diablo | South | Concord | Yes | North Bay Construction damaged a 1" plastic gas service line with boring equipment while installing fiber optics line. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Boring Equipment | Telecommunications | Incorrect Facility Records / Maps | Yes | X212303284 | Dig-In to PG&E Underground | 3rd Party-Contractor | North Bay Construction | Distribution Service |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-08 | 1” | 45 | 223 | N/A | 5 | May | 2022 |  | 1059727 | No
18817 | x | x | x | x | 2022-05-09 | May | 5 | 2022 | 77204 |  |  | 123546865 | San Mateo | Central Coast | Peninsula | Central | El Granada | Yes | ARB Inc damaged 1 1/4" plastic gas main with an excavator while installing a new water main. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Water | Incorrect Facility Records / Maps | Yes | X203303562 | Dig-In to PG&E Underground | 2nd Party-Contractor | ARB Inc | Distribution Main |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-05-09 | 2” | 40 | 119 | N/A | 5 | May | 2022 |  | 194079 | No
18816 | x | x | x | x | 2022-05-09 | May | 5 | 2022 | 77195 |  |  | 123545095 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Teichert Pipelines damaged a 1/2" plastic gas service line with a trencher while installing a new mother service. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Trencher | Gas | Facility was not Located or Marked | Yes | X200403193 | Dig-In to PG&E Underground | 2nd Party-Contractor | Teichert Pipelines | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-05-09 | ½” | 24 | 101 | N/A | 5 | May | 2022 | Contractor | 985344 | No
18815 | x | x |  | x | 2022-05-09 | May | 5 | 2022 | 77193 |  |  |  | Marin | Bay Area | North Bay | North | Ross | Yes | Nina Construction damaged a 1/2" plastic gas service line with a shovel while digging a post hole for a new deck. No USA ticket. | No | Gas Line | Yes | Shovel | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Nina Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-09 | ½” | 12 | 35 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | 746802 | Yes
18814 | x | x | x | x | 2022-05-09 | May | 5 | 2022 | 77207 |  |  | 123545541 | Marin | Bay Area | North Bay | North | Kentfield | Yes | CR North Bay Inc damaged a 3/4" steel gas service line with a sawzall while installing electrical conduit. No USA ticket. | No | Gas Line | Yes | Cutting Machine | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | CR North Bay Inc | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-09 | ¾” | 8 | 46 | Believed They Knew Where Underground Utility was From Previous Knowledge | 5 | May | 2022 |  | 967927 | No
18813 | x | x | x | x | 2022-05-09 | May | 5 | 2022 | 77210 |  | 45285971 | 123545936 | Monterey | Central Coast | Central Coast | South | Salinas | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while exposing a sewer line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | X212201110 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-09 | ½” | 40 | 24 | N/A | 5 | May | 2022 |  | N/A | Yes
18812 | x | x | x | x | 2022-05-09 | May | 5 | 2022 | 77182 |  |  | 123542574 | Contra Costa | Bay Area | Diablo | South | Antioch | Yes | Sandstone Environmental Engineering, Inc. damaged a 1/2" plastic gas service line with a pickaxe while exposing the gas line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Pickaxe | Sewer | Failed to Dig with Care | Yes | X209601698 | Dig-In to PG&E Underground | 3rd Party-Contractor | Sandstone Environmental Engineering, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-09 | ½” | 36 | 30 | N/A | 5 | May | 2022 |  | 878348 | Yes
18820 | x | x | x | x | 2022-05-10 | May | 5 | 2022 | 77255 |  |  | 123562786 | San Mateo | Central Coast | Peninsula | Central | Burlingame | Yes | Cratus Inc damaged a 1 1/4" plastic gas main with an excavator while installing a new water main. Valid USA ticket. PG&E at-fault - Locator Error - Mismarked | No | Gas Line | Yes | Excavator | Water | Incorrect Information or Marks | Yes | X127301428 | Dig-In to PG&E Underground | 3rd Party-Contractor | Cratus Inc | Distribution Main |  | Yes | Locator Error - Mismark |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-10 | 1 ¼” | 36 | 111 | N/A | 5 | May | 2022 | Bargaining Unit | 987888 | No
18819 | x | x | x | x | 2022-05-10 | May | 5 | 2022 | 77240 |  | 45291203 | 123561341 | Merced | Central Valley | Yosemite | South | Denair | Yes | Mountain Cascade damaged a 1/2" plastic gas service line with a backhoe while installing a concrete vault for fiber installation. Valid USA ticket. Failed to maintain marks | No | Gas Line | Yes | Backhoe/Trackhoe | Telecommunications | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | X124403133 | Dig-In to PG&E Underground | 3rd Party-Contractor | Mountain Cascade | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-10 | ½” | 36 | 20 | N/A | 5 | May | 2022 |  | 422496 | No
18818 | x | x | x | x | 2022-05-10 | May | 5 | 2022 | 77262 |  |  | 123574440 | Kern | Central Valley | Kern | South | Ridgecrest | Yes | S&B Construction damaged a 1/2" plastic gas service line with boring equipment while installing telecommunication facilities. Valid USA ticket. Failed to maintain clearance | No | Gas Line | Yes | Boring Equipment | Telecommunications | Excavator Failed to Maintain Clearance After Verifying Marks | Yes | X212204344 | Dig-In to PG&E Underground | 3rd Party-Contractor | S&B Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-10 | ½” | 33 | 44 | N/A | 5 | May | 2022 |  | 1022104 | No
18829 | x | x | x | x | 2022-05-11 | May | 5 | 2022 | 77328 |  |  | 123572891 | Fresno | Central Valley | Fresno | South | Clovis | Yes | Browning Contractors damaged a 2" plastic gas main with a backhoe while installing electrical conduit. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X212401275 | Dig-In to PG&E Underground | 3rd Party-Contractor | Browning Contractors | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-11 | 2” | 24 | 118 | N/A | 5 | May | 2022 |  | 771084 | No
18828 | x | x | x | x | 2022-05-11 | May | 5 | 2022 | 77299 |  |  | 123570593 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | J Flores Construction damaged a 1/2" plastic gas service line with an excavator while installing a new sewer main. Valid USA ticket. Failed to protect subsurface installation | No | Gas Line | Yes | Excavator | Sewer | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X211802843 | Dig-In to PG&E Underground | 3rd Party-Contractor | J Flores Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-11 | ½” | 48 | 73 | N/A | 5 | May | 2022 |  | 705393 | No
18827 | x | x |  | x | 2022-05-11 | May | 5 | 2022 | 77286 |  |  |  | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Northwest General Engineering damaged a 4" plastic gas main with a digging bar while doing sidewalk replacements. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Digging Bar | Curb/Sidewalk Work | Failed to Dig with Care | Yes | X021202640 | Dig-In to PG&E Underground | 3rd Party-Contractor | Northwest General Engineering | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-11 | 4" | 38 | 148 | N/A | 5 | May | 2022 |  | 781913 | Yes
18826 | x | x | x | x | 2022-05-11 | May | 5 | 2022 | 77291 |  |  | 123568606 | Alameda | Central Coast | Mission | South | Hayward | Yes | Yes Construction Group damaged a 1" plastic gas service line with a backhoe while doing an electrical upgrade. No USA ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Yes Construction Group | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-11 | 1” | 26 | 34 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | 890448 | No
18824 | x | x |  | x | 2022-05-11 | May | 5 | 2022 | 77329 |  |  |  | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Homeowner damaged a 1" plastic gas service line with a shovel while repairing a sewer lateral. No USA ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-11 | 1” | 20 | 60 | No Knowledge of USA Ticketing Process | 5 | May | 2022 |  | N/A | Yes
18823 | x | x | x | x | 2022-05-11 | May | 5 | 2022 | 77298 |  |  | 123570981 | Contra Costa | Bay Area | Diablo | South | Danville | Yes | Unlicensed contractor damaged a 1/2" plastic gas service line with a pickaxe while installing irrigation lines. No USA ticket for damaging party. There were accurate marks for another contractor so primary cause of dig-in is failed to dig with care | No | Gas Line | Yes | Pickaxe | Irrigation | Failed to Dig with Care | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-11 | ½” | 18 | 17 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2022 |  | N/A | Yes
18822 | x | x |  | x | 2022-05-11 | May | 5 | 2022 | 77327 |  |  |  | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while excavating for a new fence. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-11 | ½” | 19 | 54 | No Knowledge of USA Ticketing Process | 5 | May | 2022 |  | N/A | Yes
18821 | x | x | x | x | 2022-05-11 | May | 5 | 2022 | 77307 |  |  | 123574750 | Santa Clara | Central Coast | San Jose | Central | Morgan Hill | Yes | HCI Inc. damaged a 1/2" plastic gas service line with a shovel while installing telecommunication lines. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Dig with Care | Yes | X212203970 | Dig-In to PG&E Underground | 3rd Party-Contractor | HCI Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-11 | ½” | 35 | 55 | N/A | 5 | May | 2022 |  | 378587 | Yes
18841 | x | x | x | x | 2022-05-12 | May | 5 | 2022 | 77340 |  |  | 123574989 | Madera | Central Valley | Yosemite | South | Madera | Yes | Landscape Development damaged a 4" plastic gas main with a trencher while installing irrigation lines. Expired USA ticket. Primary cause was faulted to maintain marks | No | Gas Line | Yes | Trencher | Irrigation | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | No (expired) | X207001030 | Dig-In to PG&E Underground | 3rd Party-Contractor | Landscape Development Inc | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-12 | 4" | 12 | 166 | Expired USA ticket | 5 | May | 2022 |  | 450067 | No
18840 | x | x |  | x | 2022-05-12 | May | 5 | 2022 | 77381 |  |  |  | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | SF Gonzalez Concrete, Inc. damaged a 1 1/4" gas service line with a pickaxe while removing tree roots related to installing a retaining wall. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Pickaxe | Landscaping | Failed to Dig with Care | Yes | X206602532 | Dig-In to PG&E Underground | 3rd Party-Contractor | SF Gonzalez Concrete, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-12 | 1 ¼” | 18 | 4 | N/A | 5 | May | 2022 |  | 450067 | Yes
18839 | x | x |  | x | 2022-05-12 | May | 5 | 2022 | 77362 |  |  |  | Colusa | Northern | Sacramento | North | Colusa | Yes | Affinity Ground Works damaged a 1/2" plastic gas service line with a micro-trencher while installing telecommunication lines. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Trencher | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W205300260 | Dig-In to PG&E Underground | 3rd Party-Contractor | Affinity Groundworks | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-12 | ½” | 10 | 75 | N/A | 5 | May | 2022 |  | 971074 | No
18838 | x | x | x | x | 2022-05-12 | May | 5 | 2022 | 77349 |  |  | 123577680 | Napa | Bay Area | North Bay | North | Napa | Yes | Quality Inc. damaged a 1/2" plastic gas service line with an excavator while installing french drains. No USA ticket. | No | Gas Line | Yes | Excavator | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Quality Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-12 | ½” | 30 | 31 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | 855199 | No
18836 | x | x | x | x | 2022-05-12 | May | 5 | 2022 | 77387 |  |  | 123581573 | San Mateo | Central Coast | Peninsula | Central | Woodside | Yes | Ferrari Construction damaged a 1" plastic gas service line with an excavator while installing a new electric service. No USA ticket. | No | Gas Line | Yes | Excavator | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Ferrari Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-12 | 1” | 30 | 46 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2022 |  | 1011613 | No
18835 | x | x |  | x | 2022-05-12 | May | 5 | 2022 | 77369 |  |  |  | Monterey | Central Coast | Central Coast | South | Salinas | Yes | Don Chapin Co damaged a 1/2" plastic gas service line with an excavator while exposing the accurately marked gas line. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Tree Removal/Stump Grinding | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X206902585 | Dig-In to PG&E Underground | 3rd Party-Contractor | Don Chapin Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-12 | ½” | 53 | 44 | N/A | 5 | May | 2022 |  | 406512 | No
18834 | x | x | x | x | 2022-05-12 | May | 5 | 2022 | 77382 |  |  | 123582067 | Sonoma | Northern | Sonoma | North | Sonoma | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while repairing a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-12 | ½” | 30 | 48 | No Knowledge of USA Ticketing Process | 5 | May | 2022 |  | N/A | Yes
18833 | x | x |  | x | 2022-05-12 | May | 5 | 2022 | 77366 |  |  |  | Marin | Bay Area | North Bay | North | San Rafael | Yes | RV Stich Construction damaged a 2" gas service line with drilling equipment while installing a grounding rod. No USA ticket. | No | Gas Line | Yes | Drilling Equipment | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | RV Stich Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-12 | 2” | 30 | 49 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 5 | May | 2022 |  | 710391 | No
18832 | x | x | x | x | 2022-05-12 | May | 5 | 2022 | 77358 |  |  | 123580757 | Solano | Bay Area | North Bay | North | Vallejo | Yes | HP Communications damaged a 1/2" plastic gas service line with a shovel while installing new ground boxes for AT&T. No USA ticket. | No | Gas Line | Yes | Shovel | Telecommunications | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | HP Communications | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-12 | ½” | 26 | 25 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 5 | May | 2022 |  | 752762 | Yes
18831 | x | x |  | x | 2022-05-12 | May | 5 | 2022 | 77388 |  |  |  | Contra Costa | Bay Area | Diablo | South | Moraga | Yes | Terra Landscape damaged a 3/4" steel gas service line with a trencher while installing a new BBQ area. No USA ticket. | No | Gas Line | Yes | Trencher | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Terra Landscape | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-12 | ¾” | 18 | 59 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | 655977 | No
18846 | x | x | x | x | 2022-05-13 | May | 5 | 2022 | 77400 |  |  | 123586616 | Marin | Bay Area | North Bay | North | Tiburon | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a post-hole digger while building a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-13 | ½” | 27 | 39 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | N/A | Yes
18845 | x | x |  | x | 2022-05-13 | May | 5 | 2022 | 77424 |  |  |  | Marin | Bay Area | North Bay | North | San Rafael | Yes | FH Landscaping damaged a 1/2" plastic gas service line with a pickaxe while cleaning up leaves. No USA ticket. | No | Gas Line | Yes | Pickaxe | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | FH Landscaping | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-13 | ½” | 3 | 28 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2022 |  | 1079266 | Yes
18844 | x | x | x | x | 2022-05-13 | May | 5 | 2022 | 77427 |  |  | 123592481 | Alameda | Central Coast | Mission | South | Livermore | Yes | Homeowner damaged a 1/2" plastic gas service line with a backhoe while doing sewer repair. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X211800344 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-13 | ½” | 24 | 14 | N/A | 5 | May | 2022 |  | N/A | No
18848 | x | x | x | x | 2022-05-14 | May | 5 | 2022 | 77439 |  |  | 123596663 | Contra Costa | Bay Area | Diablo | South | Moraga | Yes | Gandara’s Construction Company damaged a 1/2" plastic gas service line with a shovel while doing an electric panel upgrade. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | W213200088 | Dig-In to PG&E Underground | 3rd Party-Contractor | Gandara’s Construction Company | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-14 | ½” | 24 | 46 | N/A | 5 | May | 2022 |  | 1070810 | Yes
18849 | x | x | x | x | 2022-05-15 | May | 5 | 2022 | 77460 |  |  | 123605089 | Alameda | Central Coast | Mission | South | Hayward | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while moving a plant. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-15 | ½” | 8 | 21 | No Knowledge of USA Ticketing Process | 5 | May | 2022 |  | N/A | Yes
18863 | x | x |  | x | 2022-05-16 | May | 5 | 2022 | 77495 |  |  |  | Fresno | Central Valley | Fresno | South | Clovis | Yes | Haydon Construction damaged a 8" steel gas main with an excavator while installing a sewer line. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | No | Excavator | Sewer | Incorrect Facility Records / Maps | Yes | X210101653 | Dig-In to PG&E Underground | 3rd Party-Contractor | Haydon Construction | Distribution Main |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-16 | 8" | 108 | 0 | N/A | 5 | May | 2022 |  | 458977 | No
18862 | x | x | x | x | 2022-05-16 | May | 5 | 2022 | 77483 |  |  | 123606648 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Valverde Construction damaged a 1" plastic gas service line with an excavator while installing a storm drain. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Drainage Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X028102235 | Dig-In to PG&E Underground | 3rd Party-Contractor | Valverde Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-16 | 1” | 30 | 52 | N/A | 5 | May | 2022 |  | 276468 | No
18860 | x | x | x | x | 2022-05-16 | May | 5 | 2022 | 77510 |  |  | 123610421 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Trenchless Company damaged a 1/2" plastic gas service line with a shovel while sewer line install. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | X212403164 | Dig-In to PG&E Underground | 3rd Party-Contractor | Trenchless Company | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-16 | ½” | 22 | 36 | N/A | 5 | May | 2022 |  | 775703 | Yes
18859 | x | x | x | x | 2022-05-16 | May | 5 | 2022 | 77475 |  |  | 123604316 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Team Ghilotti damaged a 3/4" steel gas service line with an excavator while doing sewer replacement. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X034200623 | Dig-In to PG&E Underground | 3rd Party-Contractor | Team Ghilotti | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-16 | ¾” | 30 | 112 | N/A | 5 | May | 2022 |  | 895384 | No
18858 | x | x |  | x | 2022-05-16 | May | 5 | 2022 | 77484 |  |  |  | Yolo | Northern | Vacaville | North | Davis | Yes | McGuire & Hester damaged the wrap on a 12" steel gas transmission line with vacuum equipment while ding road work. Valid USA ticket. Inadequate excavation practices | Yes | Gas Line | No | Vacuum Equipment | Road Work | Inadequate Excavation Practices | Yes | X212303651 | Dig-In to PG&E Underground | 3rd Party-Contractor | McGuire & Hester | Transmission Line |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-16 | 12" | 46 | 0 | N/A | 5 | May | 2022 |  | 95879 | No
18857 | x | x | x | x | 2022-05-16 | May | 5 | 2022 | 77523 |  |  | 123612300 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while installing a water line. No USA ticket. | No | Gas Line | Yes | Shovel | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-16 | ½” | 36 | 19 | No Knowledge of USA Ticketing Process | 5 | May | 2022 |  | N/A | Yes
18856 | x | x | x | x | 2022-05-16 | May | 5 | 2022 | 77476 |  |  | 123607181 | San Mateo | Central Coast | Peninsula | Central | Hillsborough | Yes | Truscapes Landscape Construction damaged a 1" plastic gas service line with a shovel while digging fence post holes. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Truscapes Landscape Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-16 | 1” | 28 | 91 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2022 |  | 1069510 | Yes
18855 | x | x | x | x | 2022-05-16 | May | 5 | 2022 | 77520 |  |  |  | Contra Costa | Bay Area | Diablo | South | Antioch | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while digging a post hole for a retaining wall. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-16 | ½” | 20 | 42 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | N/A | Yes
18854 | x | x | x | x | 2022-05-16 | May | 5 | 2022 | 77472 |  |  | 123605055 | Tehama | Northern | North Valley | North | Cottonwood | Yes | Ultra Fencing damaged a 1" plastic gas service line with a auger while constructing a fence. No USA ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Ultra Fencing | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-16 | 1” | 24 | 13 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 5 | May | 2022 |  | 892267 | No
18853 | x | x | x | x | 2022-05-16 | May | 5 | 2022 | 77480 |  |  | 123607082 | Tehama | Northern | North Valley | North | Corning | Yes | Henkels & McCoy damaged a 1" plastic gas service line with a shovel while exposing the accurately marked gas line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | X206603113 | Dig-In to PG&E Underground | 2nd Party-Contractor | Henkels & McCoy | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-05-16 | 1” | 15 | 13 | N/A | 5 | May | 2022 |  |  | Yes
18852 | x | x |  | x | 2022-05-16 | May | 5 | 2022 | 77518 |  |  |  | Marin | Bay Area | North Bay | North | Tiburon | Yes | McCaffrey Brothers Construction damaged a 3/4" steel gas service line with an excavator while building an Accessory Dwelling Unit. No USA ticket. | No | Gas Line | No | Excavator | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | McCaffrey Brothers Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-16 | 1” | 12 | 0 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 5 | May | 2022 |  | 871947 | No
18851 | x | x | x | x | 2022-05-16 | May | 5 | 2022 | 77515 |  |  | 123611393 | Monterey | Central Coast | Central Coast | South | Carmel | Yes | Monterey Design & Build damaged a 1/2" plastic gas service line with a shovel while installing a septic clean out. No USA ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Monterey Design & Build | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-16 | ½” | 29 | 22 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | 1076891 | Yes
18850 | x | x | x | x | 2022-05-16 | May | 5 | 2022 | 77498 |  |  | 123607180 | Monterey | Central Coast | Central Coast | South | Monterey | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence. Expired USA ticket. Failed to dig with care | No | Gas Line | Yes | Post-Hole Digger | Fencing | Failed to Dig with Care | No (expired) | X207502812 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-16 | ½” | 34 | 29 | Expired USA ticket | 5 | May | 2022 |  | N/A | Yes
18868 | x | x | x | x | 2022-05-17 | May | 5 | 2022 | 77557 |  |  | 123617333 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence post. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-17 | ½” | 30 | 26 | No Knowledge of USA Ticketing Process | 5 | May | 2022 |  | N/A | Yes
18867 | x | x |  | x | 2022-05-17 | May | 5 | 2022 | 77544 |  |  |  | Contra Costa | Bay Area | Diablo | South | Lafayette | Yes | Basset Engineering damaged a 1" plastic gas service line with an excavator while doing sewer main replacements. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X209600849 | Dig-In to PG&E Underground | 3rd Party-Contractor | Basset Engineering | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-17 | 1” | 48 | 13 | N/A | 5 | May | 2022 |  | 1070288 | No
18866 | x | x |  | x | 2022-05-17 | May | 5 | 2022 | 77565 |  |  |  | Yuba | Northern | Sierra | North | Marysville | Yes | Teichert Construction damaged a 1/2" plastic gas service line with an excavator while installing an underground electric facility. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X204902550 | Dig-In to PG&E Underground | 3rd Party-Contractor | Teichert Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-17 | ½” | 48 | 26 | N/A | 5 | May | 2022 |  | 8 | No
18865 | x | x | x | x | 2022-05-17 | May | 5 | 2022 | 77542 |  |  | 123615289 | Yolo | Northern | Vacaville | North | Woodland | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with an auger while installing new fencing. No USA ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-17 | ½” | 17 | 11 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  |  | No
18864 | x | x | x | x | 2022-05-17 | May | 5 | 2022 | 77545 |  |  | 123620489 | Contra Costa | Bay Area | East Bay | Central | Rodeo | Yes | Miller Pipeline damaged a 2" plastic gas main with an excavator while doing gas pipeline replacement. Valid USA ticket. Failed to protect subsurface utility | No | Gas Line | Yes | Excavator | Gas | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X206803544 | Dig-In to PG&E Underground | 2nd Party-Contractor | Miller Pipeline | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E Division Gas |  |  | 2nd Party Gas | Yes | 2022-05-17 | 2” | 26 | 20 | N/A | 5 | May | 2022 |  | 978749 | No
18877 | x | x |  |  | 2022-05-18 | May | 5 | 2022 | 77601 |  |  |  | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | MGE Underground damaged a 2" steel gas main with boring equipment while doing electric work. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Boring Equipment | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X126701227 | Dig-In to PG&E Underground | 2nd Party-Contractor | MGE Underground | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E Division Electric |  |  | 2nd Party Gas | Yes | 2022-05-18 | 2” | 65 | 257 | N/A | 5 | May | 2022 |  |  | No
18876 | x |  |  |  | 2022-05-18 | May | 5 | 2022 | 77622 |  |  |  | San Joaquin | Central Valley | Stockton | South | Stockton | Yes | Marvin damaged the wrap on a 1 1/4" steel gas service line with vacuum equipment while doing unknown work. No USA ticket. | Yes | Gas Line | No | Vacuum Equipment | Unknown | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Marvin | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-18 | 1 ¼” |  | 0 | Unknown | 5 | May | 2022 |  |  | No
18875 | x | x | x | x | 2022-05-18 | May | 5 | 2022 | 77665 |  |  | 123633000 | San Mateo | Central Coast | Peninsula | Central | Half Moon Bay | Yes | Marsh Fence & Deck damaged a 1/2" plastic gas service line with a shovel while digging a post hole for a fence. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Marsh Fence & Deck | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-18 | ½” | 30 | 68 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | 377047 | Yes
18874 | x | x | x | x | 2022-05-18 | May | 5 | 2022 | 77614 |  |  | 123628373 | Kern | Central Valley | Kern | South | Ridgecrest | Yes | Lyles Construction damaged a 1 1/4" plastic gas service line with a backhoe while doing gas pipeline replacements. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Backhoe/Trackhoe | Gas | Incorrect Facility Records / Maps | Yes | W133300315 | Dig-In to PG&E Underground | 2nd Party-Contractor | Lyles Construction | Distribution Service |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-05-18 | 1 ¼” | 25 | 94 | N/A | 5 | May | 2022 |  | 981146 | No
18873 | x | x | x | x | 2022-05-18 | May | 5 | 2022 | 77611 |  |  | 123627790 | San Joaquin | Central Valley | Stockton | South | Stockton | Yes | Wagner Mechanical Inc. damaged a 2" plastic gas main with a backhoe while installing a sewer pipe. No USA ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Wagner Mechanical Inc. | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-18 | 2” | 36 | 64 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2022 |  | 507799 | No
18872 | x | x | x | x | 2022-05-18 | May | 5 | 2022 | 77616 |  |  | 123626769 | Sacramento | Northern | Sacramento | North | Rancho Cordova | Yes | Pavement Recycling Systems damaged a 3/4" steel gas service line with a milling machine while doing a grind and pave. No USA ticket. | No | Gas Line | Yes | Milling/Road Grinding | Road Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Pavement Recycling Systems, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-18 | ¾” | 12 | 53 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 5 | May | 2022 |  | 773404 | No
18871 | x | x |  | x | 2022-05-18 | May | 5 | 2022 | 77618 |  |  |  | Marin | Bay Area | North Bay | North | Belvedere | Yes | Gallagher & Company Construction damaged a 1/2" plastic gas service line with a shovel while trying to determine the depth of the foundation. No USA ticket. | No | Gas Line | Yes | Shovel | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Gallagher & Company Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-18 | ½” | 18 | 33 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 5 | May | 2022 |  | 778096 | Yes
18870 | x | x | x | x | 2022-05-18 | May | 5 | 2022 | 77625 |  |  | 123627957 | Napa | Bay Area | North Bay | North | St Helena | Yes | CityBest Construction damaged a 1/2" plastic gas service line with a shovel while building a new accessory dwelling. No USA ticket. | No | Gas Line | Yes | Shovel | Site Development | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | CityBest Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-18 | ½” | 24 | 49 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | 788386 | Yes
18887 | x | x |  | x | 2022-05-19 | May | 5 | 2022 | 77743 |  |  |  | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a skid steer while doing driveway repairs. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Skid Steer | Driveway Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X213400063 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-19 | ½” | 16 | 23 | N/A | 5 | May | 2022 |  | N/A | No
18886 | x | x | x | x | 2022-05-19 | May | 5 | 2022 | 77731 |  |  | 123638923 | San Mateo | Central Coast | Peninsula | Central | South San Francisco | Yes | HCI Solar Company damaged a 1/2" plastic gas service line with a grounding rod while doing a solar install. No USA ticket. | No | Gas Line | Yes | Grounding Rod | Other | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | HCI Solar Company | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-19 | ½” | 30 | 52 | Other | 5 | May | 2022 |  | 1024165 | Yes
18885 | x | x | x | x | 2022-05-19 | May | 5 | 2022 | 77734 |  |  | 123640038 | Monterey | Central Coast | Central Coast | South | Monterey | Yes | Angel Fencing damaged a 1/2" plastic gas service line with a post-hole digger while building a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Angel Fencing | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-19 | ½” | 8 | 16 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | 1027443 | Yes
18884 | x | x |  | x | 2022-05-19 | May | 5 | 2022 | 77727 |  |  |  | Sacramento | Northern | Sacramento | North | Citrus Heights | Yes | ALP Construction and Painting damaged a 1" plastic gas service line with a digging bar while removing a fence post. No USA ticket. | No | Gas Line | Yes | Digging Bar | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | ALP Construction and Painting | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-19 | 1” | 19 | 75 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2022 |  | 997945 | Yes
18883 | x | x | x | x | 2022-05-19 | May | 5 | 2022 | 77742 |  |  | 123642422 | San Mateo | Central Coast | Peninsula | Central | Menlo Park | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while removing dirt from a fence post hole. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-19 | ½” | 28 | 48 | No Knowledge of USA Ticketing Process | 5 | May | 2022 |  | N/A | Yes
18882 | x | x | x | x | 2022-05-19 | May | 5 | 2022 | 77735 |  |  | 123648040 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Teichert Construction damaged a 3/4" steel gas service line with an excavator while installing a water line. Valid USA ticket. Failed to protect subsurface installation | No | Gas Line | Yes | Excavator | Water | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X036302283 | Dig-In to PG&E Underground | 3rd Party-Contractor | Teichert Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-19 | ¾” | 36 | 51 | N/A | 5 | May | 2022 |  | 8 | No
18881 | x | x | x | x | 2022-05-19 | May | 5 | 2022 | 77695 |  |  | 123647759 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Scott Glasco General Engineering damaged a 2" plastic gas service line with an mini-excavator while trenching for electrical conduit. Valid USA ticket. Excavated outside delineated area | No | Gas Line | Yes | Excavator | Electric Work | Excavated Outside Delineated Area | Yes | X209101604 | Dig-In to PG&E Underground | 3rd Party-Contractor | Scott Glasco General Engineering | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-19 | 2” | 36 | 55 | N/A | 5 | May | 2022 |  | 759008 | No
18880 | x | x | x | x | 2022-05-19 | May | 5 | 2022 | 77717 |  |  | 123636795 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Lifescaping Outdoors damaged a 1/2" plastic gas service line with a shovel while building a fence. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Lifescaping Outdoors | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-19 | ½” | 24 | 50 | Unknown | 5 | May | 2022 |  | 1007986 | Yes
18879 | x | x | x | x | 2022-05-19 | May | 5 | 2022 | 77730 |  |  | 123638656 | Yuba | Northern | Sierra | North | Marysville | Yes | Homeowner damaged a 1 1/4" plastic gas service line with an excavator while removing tree stumps. No USA ticket. | No | Gas Line | Yes | Excavator | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-19 | 1 ¼” | 24 | 58 | Believed They Knew Where Underground Utility was From Previous Knowledge | 5 | May | 2022 |  | N/A | No
18878 | x | x |  | x | 2022-05-19 | May | 5 | 2022 | 77716 |  |  |  | Marin | Bay Area | North Bay | North | San Rafael | Yes | SMI Demolition damaged a 3/4" steel gas service line with an excavator while removing a concrete pool. No USA ticket. | No | Gas Line | Yes | Excavator | Building Demolition | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | SMI Demolition Co. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-19 | ¾” | 16 | 37 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 5 | May | 2022 |  | 1008605 | No
18892 | x | x | x | x | 2022-05-20 | May | 5 | 2022 | 77764 |  | 45304906 | 123647756 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Homeowner damaged a 1/2" plastic gas service line inserted into 3/4" steel with a ground ripper while ripping the land they own next to an orchard. No USA ticket. | No | Gas Line | Yes | Farm Equipment | Agriculture | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-20 | ½” | 30 | 89 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | N/A | No
18891 | x | x | x | x | 2022-05-20 | May | 5 | 2022 | 77806 |  |  | 123654494 | Mendocino | Northern | Humboldt | North | Ukiah | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while installing a houseline for gas and electric. No USA ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-20 | ½” | 10 | 49 | Believed They Knew Where Underground Utility was From Previous Knowledge | 5 | May | 2022 |  | N/A | Yes
18890 | x | x | x | x | 2022-05-20 | May | 5 | 2022 | 77769 |  |  | 123650630 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line inserted into 1/2" copper casing with a post-hole digger while digging a post hole for a fence. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Post-Hole Digger | Fencing | Failed to Dig with Care | Yes | X212603261 | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-20 | 1/4” | 24 | 48 | N/A | 5 | May | 2022 |  |  | Yes
18889 | x | x | x | x | 2022-05-20 | May | 5 | 2022 | 77781 |  |  | 123652570 | Kern | Central Valley | Kern | South | Tehachapi | Yes | Halpin Concrete Construction damaged a 1/2" plastic gas service line with a shovel while installing a foundation for a home addition. No USA ticket. | No | Gas Line | Yes | Shovel | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Halpin Concrete Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-20 | ½” | 24 | 69 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2022 |  | 426508 | Yes
18888 | x | x | x | x | 2022-05-20 | May | 5 | 2022 | 77763 |  |  | 123647572 | San Joaquin | Central Valley | Stockton | South | Stockton | Yes | Homeowner damaged a 1" plastic gas service line with an auger while digging a post hole for a fence, Valid USA ticket. Excavated prior to legal excavation start date and time | No | Gas Line | Yes | Auger | Fencing | Excavated Prior to Legal Excavation Start Date and Time | Yes | X213602729 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-20 | 1” | 24 | 87 | N/A | 5 | May | 2022 |  | N/A | No
18894 | x | x | x | x | 2022-05-21 | May | 5 | 2022 | 77825 |  |  | 123660429 | San Mateo | Central Coast | Peninsula | Central | Pacifica | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while upgrading the electrical service at the residence. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | X213893030 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-21 | ½” | 18 | 23 | N/A | 5 | May | 2022 |  | N/A | Yes
18893 | x |  | x |  | 2022-05-21 | May | 5 | 2022 | 77816 |  |  | 123657104 | San Joaquin | Central Valley | Stockton | South | Stockton | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while installing a fence post. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-21 | ½” | 28 | 29 | Unknown | 5 | May | 2022 |  | N/A | Yes
18896 | x | x | x | x | 2022-05-22 | May | 5 | 2022 | 77844 |  |  | 123664359 | San Mateo | Central Coast | Peninsula | Central | Pacifica | Yes | Homeowner damaged a 1/2" plastic gas service line with a garden spade while upgrading electric service. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Other Hand Tools | Electric Work | Failed to Dig with Care | Yes | X213803030 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-22 | ½” | 18 | 40 | N/A | 5 | May | 2022 |  | N/A | Yes
18902 | x | x |  | x | 2022-05-23 | May | 5 | 2022 | 77902 |  |  |  | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Unknown party damaged the coating to a 3/4" steel gas service line. Unknown who caused the damage or what tool was used. Damage occurred when recent curb/sidewalk work was performed. See DIRT documents for more details. | Yes | Gas Line | No | Unknown | Curb/Sidewalk Work | Unknown | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unknown | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-23 | ¾” | 0 | 0 | Unknown | 5 | May | 2022 |  | N/A | No
18901 | x | x | x | x | 2022-05-23 | May | 5 | 2022 | 77888 |  | 45310487 | 123669716 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | VFT LP Property Management damaged a 1/2" plastic gas service line with a post-hole digger while replacing fence posts. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | VFT LP Property Management | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-23 | ½” | 24 | 20 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  |  | Yes
18900 | x | x | x | x | 2022-05-23 | May | 5 | 2022 | 77860 |  |  | 123667198 | Placer | Northern | Sierra | North | Roseville | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a pickaxe while landscaping. No USA ticket. | No | Gas Line | Yes | Pickaxe | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-23 | ½” | 31 | 25 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2022 |  |  | Yes
18899 | x | x |  | x | 2022-05-23 | May | 5 | 2022 | 77898 |  |  |  | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Bailey Fence Company Inc. damaged a 4" plastic gas main with an auger while installing a new metal gate post. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | No | Auger | Fencing | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X211500099 | Dig-In to PG&E Underground | 3rd Party-Contractor | Bailey Fence Company, Inc. | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-23 | 4" | 24 | 0 | N/A | 5 | May | 2022 |  | 498661 | No
18898 | x | x | x | x | 2022-05-23 | May | 5 | 2022 | 77870 |  |  | 123669410 | Santa Clara | Central Coast | De Anza | Central | Cupertino | Yes | Lewis & Tibbits damaged a 1/2" plastic gas service line with an excavator while tying in a new water main. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X130001276 | Dig-In to PG&E Underground | 3rd Party-Contractor | Lewis & Tibbits | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-23 | ½” | 26 | 28 | N/A | 5 | May | 2022 |  | 281666 | No
18897 | x | x |  |  | 2022-05-23 | May | 5 | 2022 | 77901 |  |  |  | Contra Costa | Bay Area | Diablo | South | Danville | Yes | DT Sons Excavating damaged a 2" plastic gas main with an excavator while installing new telecommunication lines. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Excavator | Telecommunications | Facility was not Located or Marked | Yes | X213102770 | Dig-In to PG&E Underground | 3rd Party-Contractor | DT Sons Excavating | Distribution Main |  | Yes | Locator Error - No Mark |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-23 | 2” | 40 | 66 | N/A | 5 | May | 2022 | Bargaining Unit |  | No
18907 | x | x |  | x | 2022-05-24 | May | 5 | 2022 | 77976 |  |  |  | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | JD Jones Construction damaged a 3/4" steel gas service line with a sawzall while preparing to pour concrete for parking spaces. No USA ticket. | No | Gas Line | Yes | Cutting Machine | Site Development | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | JD Jones Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-24 | ¾” | 6 | 36 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 5 | May | 2022 |  | 1054028 | No
18906 | x | x | x | x | 2022-05-24 | May | 5 | 2022 | 77949 |  |  | 123684450 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Trinity Building damaged a 1" plastic gas service line with a shovel while installing electrical to an ADU. Valid USA ticket. Failed to protect subsurface utility | No | Gas Line | Yes | Shovel | Electric Work | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | W213800175 | Dig-In to PG&E Underground | 3rd Party-Contractor | Trinity Building | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-24 | 1” | 28 | 33 | N/A | 5 | May | 2022 |  | 928369 | Yes
18904 | x |  | x |  | 2022-05-24 | May | 5 | 2022 | 77978 |  |  | 123680769 | Sonoma | Northern | Sonoma | North | Healdsburg | Yes | Unknown contractor damaged a 1/2" plastic gas service line with an unknown tool while doing foundation work. No USA ticket. | No | Gas Line | Yes | Unknown | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unknown | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-24 | ½” | 30 | 120 | Unknown | 5 | May | 2022 |  |  | No
18903 | x | x | x | x | 2022-05-24 | May | 5 | 2022 | 77939 |  |  | 123678208 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | J.D. Landscaping damaged a 1 1/4" plastic gas main with a shovel while planting a tree. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | J.D. Landscaping | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-24 | 1 ¼” | 30 | 54 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 5 | May | 2022 |  | 972837 | Yes
18912 | x |  | x | x | 2022-05-25 | May | 5 | 2022 | 78051 |  |  | 123693836 | Stanislaus | Central Valley | Yosemite | South | Oakdale | Yes | United Pavement Maintenance damaged a 2" plastic gas main with an excavator while removing old drain lines. Valid USA ticket. Failed to maintain marks | No | Gas Line | Yes | Excavator | Drainage Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | X213003946 | Dig-In to PG&E Underground | 3rd Party-Contractor | United Pavement Maintenance | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-25 | 2” | 30 | 62 | N/A | 5 | May | 2022 |  | 905503 | No
18909 | x | x |  | x | 2022-05-25 | May | 5 | 2022 | 78039 |  |  |  | Alameda | Bay Area | East Bay | Central | Oakland | Yes | West Valley Construction damaged tracing wires with a backhoe while doing gas service replacements. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | No | Backhoe/Trackhoe | Gas | Incorrect Facility Records / Maps | Yes | X209802288 | Dig-In to PG&E Underground | 2nd Party-Contractor | West Valley Construction | Distribution Main |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-05-25 | 1 ¼” |  | 0 | N/A | 5 | May | 2022 |  | 174968 | No
18908 | x | x | x |  | 2022-05-25 | May | 5 | 2022 | 78011 |  |  | 123687558 | Amador | Central Valley | Stockton | South | Ione | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while digging a fence post hole. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-25 | ½” | 38 | 52 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | N/A | Yes
18919 | x | x | x | x | 2022-05-26 | May | 5 | 2022 | 78079 |  |  | 123697055 | Santa Cruz | Central Coast | Central Coast | South | Capitola | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a post-hole digger while installing a new fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-26 | ½” | 24 | 49 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  |  | Yes
18918 | x | x | x | x | 2022-05-26 | May | 5 | 2022 | 78094 |  |  | 123699634 | Monterey | Central Coast | Central Coast | South | Carmel | Yes | Monterey Peninsula Engineering damaged a 1/2" plastic gas service line with a steel probe while installing water main. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Probing Tool | Water | Failed to Dig with Care | Yes | W210400359 | Dig-In to PG&E Underground | 3rd Party-Contractor | Monterey Peninsula Engineering | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-26 | ½” | 32 | 45 | N/A | 5 | May | 2022 |  | 972425 | Yes
18917 | x | x | x | x | 2022-05-26 | May | 5 | 2022 | 78071 |  |  | 123696949 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | G Family Construction damaged a 1/2" plastic gas service line with a pickaxe while installing electrical conduit. No USA ticket. | No | Gas Line | Yes | Pickaxe | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | G Family Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-26 | ½” | 22 | 44 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 5 | May | 2022 |  | 893848 | Yes
18916 | x |  |  |  | 2022-05-26 | May | 5 | 2022 | 78085 |  |  |  | Contra Costa | Bay Area | Diablo | South | Alamo | Yes | Unknown contractor damaged 1" plastic gas service line with an excavator while trenching doing unknown work. No USA ticket. Contractor had left the scene when DIRT investigator arrived and homeowner would not cooperate with the investigation. | No | Gas Line | Yes | Excavator | Unknown | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unknown | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-26 | 1” | 30 | 46 | Unknown | 5 | May | 2022 |  |  | No
18914 | x |  | x |  | 2022-05-26 | May | 5 | 2022 | 78106 |  |  | 123707284 | Butte | Northern | North Valley | North | Chico | Yes | M V Construction damaged a 2" plastic gas main with a mini-excavator while repairing a sewer line. No USA ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | M V Construction | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-26 | 2” | 38 | 42 | Unknown | 5 | May | 2022 |  |  | No
18913 | x | x | x | x | 2022-05-26 | May | 5 | 2022 | 78118 |  |  | 123703917 | Merced | Central Valley | Yosemite | South | Atwater | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while digging a post hole for a mailbox. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-26 | ½” | 21 | 14 | No Knowledge of USA Ticketing Process | 5 | May | 2022 |  | N/A | Yes
18927 | x |  |  |  | 2022-05-27 | May | 5 | 2022 | 78138 |  |  |  | Butte | Northern | North Valley | North | Oroville | Yes | Grade Tek damaged the wrap on a 6" steel transmission line with a shovel while potholing to find the facility. Valid USA ticket. Failed to dig with care | Yes | Gas Line | No | Shovel | Site Development | Failed to Dig with Care | Yes | X213001436 | Dig-In to PG&E Underground | 3rd Party-Contractor | Grade Tek Inc. | Transmission Line |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-27 | 6" |  | 0 | N/A | 5 | May | 2022 |  |  | Yes
18926 | x | x | x |  | 2022-05-27 | May | 5 | 2022 | 78140 |  |  | 123708248 | Yolo | Northern | Vacaville | North | Woodland | Yes | Argonaut Constructors damaged a 3/4" steel gas service line with a mini-excavator while doing water work. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | No | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X206600084 | Dig-In to PG&E Underground | 3rd Party-Contractor | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-27 | ¾” |  | 0 | N/A | 5 | May | 2022 |  |  | No
18925 | x |  | x |  | 2022-05-27 | May | 5 | 2022 | 78166 |  |  | 123711508 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Trenchless Tech damaged a 1/2" plastic gas service line with boring equipment while installing telecommunication lines. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Boring Equipment | Telecommunications | Incorrect Facility Records / Maps | Yes | X213900546 | Dig-In to PG&E Underground | 3rd Party-Contractor | Trenchless Tech Inc | Distribution Service |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-27 | ½” | 34 | 51 | N/A | 5 | May | 2022 |  |  | No
18924 | x | x | x | x | 2022-05-27 | May | 5 | 2022 | 78150 |  |  | 123710328 | Monterey | Central Coast | Central Coast | South | Pacific Grove | Yes | JDR Construction damaged a 1/2" plastic gas service line with a shovel while installing new gas facilities. Valid USA ticket. Failed to protect subsurface installation | No | Gas Line | Yes | Shovel | Gas | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | W211600325 | Dig-In to PG&E Underground | 3rd Party-Contractor | JDR Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-27 | ½” | 34 | 26 | N/A | 5 | May | 2022 |  | 623631 | Yes
18923 | x | x | x | x | 2022-05-27 | May | 5 | 2022 | 78167 |  |  | 123711085 | Marin | Bay Area | North Bay | North | San Rafael | Yes | J Solis Landscaping damaged a 1/2" plastic gas service line with a claw hammer while removing a koi pond. No USA ticket for Contractor. Homeowner had valid USA ticket with accurate markings. Primary cause was failed to dig with care | No | Gas Line | Yes | Other Hand Tools | Landscaping | Failed to Dig with Care | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | J Solis Landscaping | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-27 | ½” | 18 | 44 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2022 |  | 1083926 | Yes
18922 | x | x | x | x | 2022-05-27 | May | 5 | 2022 | 78168 |  |  | 123711144 | Kern | Central Valley | Kern | South | Bakersfield | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service line with a shovel while installing irrigation. No USA ticket. | No | Gas Line | Yes | Shovel | Irrigation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-27 | ½” | 16 | 15 | No Knowledge of USA Ticketing Process | 5 | May | 2022 |  |  | Yes
18921 | x |  |  |  | 2022-05-27 | May | 5 | 2022 | 78161 |  |  |  | Fresno | Central Valley | Fresno | South | Fowler | Yes | Homeowner damaged a 1" plastic gas service line with a trencher while installing sprinklers. No USA ticket. | No | Gas Line | Yes | Trencher | Irrigation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-27 | 1” | 12 | 48 | Unknown | 5 | May | 2022 |  | N/A | No
18929 | x | x | x | x | 2022-05-29 | May | 5 | 2022 | 78207 |  |  | 123716169 | Sutter | Northern | Sierra | North | Yuba City | Yes | Homeowner damaged a 1" plastic gas service line with an auger while installing a fence. No USA ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-29 | 1” | 20 | 31 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  | N/A | No
18928 | x | x | x | x | 2022-05-29 | May | 5 | 2022 | 78204 |  | 45321166 | 123715989 | Stanislaus | Central Valley | Yosemite | South | Turlock | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while repairing a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-29 | ½” | 24 | 71 | No Knowledge of USA Ticketing Process | 5 | May | 2022 |  | N/A | Yes
18930 | x |  | x |  | 2022-05-30 | May | 5 | 2022 | 78219 |  |  | 123717862 | Contra Costa | Bay Area | Diablo | South | Antioch | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while replacing a fence post. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-30 | ½” | 12 | 49 | Unknown | 5 | May | 2022 |  | N/A | Yes
18940 | x | x | x | x | 2022-05-31 | May | 5 | 2022 | 78285 |  |  | 123724222 | Nevada | Northern | Sierra | North | Nevada City | Yes | H&D Electric damaged a 1/2" plastic gas service line with a trencher while installing electric for light poles. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Trencher | Electric Work | Facility was not Located or Marked | Yes | X209500643 | Dig-In to PG&E Underground | 3rd Party-Contractor | H&D Electric | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-31 | ½” | 20 | 25 | N/A | 5 | May | 2022 | Bargaining Unit | 180154 | No
18939 | x | x |  | x | 2022-05-31 | May | 5 | 2022 | 78261 |  |  |  | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Unlicensed Contractor damaged a 1" plastic gas service line with a stake while repairing some landscaping. No USA ticket. | No | Gas Line | Yes | Stake | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-31 | 1” | 16 | 10 | Knew About USA Ticket Requirement But Chose Not to Call | 5 | May | 2022 |  |  | Yes
18938 | x | x | x |  | 2022-05-31 | May | 5 | 2022 | 78254 |  |  | 123723212 | Santa Clara | Central Coast | San Jose | Central | Morgan Hill | Yes | Garney Construction damaged a 1/2" plastic gas service line with an excavator while performing a water main replacement. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X201101847 | Dig-In to PG&E Underground | 3rd Party-Contractor | Garney Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-31 | ½” | 48 | 105 | N/A | 5 | May | 2022 |  |  | No
18937 | x |  | x |  | 2022-05-31 | May | 5 | 2022 | 78270 |  |  | 123724195 | Fresno | Central Valley | Fresno | South | Fresno | Yes | USA Directional Bore damaged a 1/2" plastic gas service line with a shovel while potholing for marked facility. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Dig with Care | Yes | X214303367 | Dig-In to PG&E Underground | 3rd Party-Contractor | USA Directional Bore | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-31 | ½” | 36 | 46 | N/A | 5 | May | 2022 |  |  | Yes
18936 | x | x | x | x | 2022-05-31 | May | 5 | 2022 | 78253 |  |  | 123721562 | Alameda | Central Coast | Mission | South | San Leandro | Yes | Homeowner damaged a 1/2" plastic gas service line with a pickaxe while removing a tree stump. No USA ticket. | No | Gas Line | Yes | Pickaxe | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-31 | ½” | 16 | 16 | No Knowledge of USA Ticketing Process | 5 | May | 2022 |  | N/A | Yes
18935 | x |  | x |  | 2022-05-31 | May | 5 | 2022 | 78286 |  |  | 123724727 | Fresno | Central Valley | Fresno | South | Clovis | Yes | AC Industries damaged a 1/2" plastic gas service line with an excavator while installing a sewer line. No USA ticket. Primary cause was failure to expose facility. There were marks for another contractor present | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | AC Industries | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-31 | ½” | 30 | 41 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2022 |  |  | No
18934 | x |  | x |  | 2022-05-31 | May | 5 | 2022 | 78302 |  |  | 123726651 | Merced | Central Valley | Yosemite | South | Los Banos | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence gate. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-05-31 | ½” | 24 | 27 | Unknown | 5 | May | 2022 |  | N/A | Yes
18933 | x | x | x | x | 2022-05-31 | May | 5 | 2022 | 78243 |  |  | 123726202 | San Mateo | Central Coast | Peninsula | Central | Burlingame | Yes | Fence Master damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Post-Hole Digger | Fencing | Failed to Dig with Care | Yes | X214503649 | Dig-In to PG&E Underground | 3rd Party-Contractor | Fence Masters | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-31 | ½” | 24 | 16 | N/A | 5 | May | 2022 |  | 1012927 | Yes
18932 | x | x | x | x | 2022-05-31 | May | 5 | 2022 | 78305 |  |  | 123727084 | Santa Clara | Central Coast | De Anza | Central | Los Altos | Yes | AK Construction Enterprises Inc. damaged a 1" plastic gas service line with a mini-excavator while installing new drainage for a house. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Drainage Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X100401598 | Dig-In to PG&E Underground | 3rd Party-Contractor | AK Construction Enterprises Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-05-31 | 1” | 30 | 5 | N/A | 5 | May | 2022 |  | 850864 | No
18949 | x | x | x |  | 2022-06-01 | Jun | 6 | 2022 | 78329 |  |  | 123729219 | Fresno | Central Valley | Fresno | South | Fresno | Yes | PG&E leak survey damaged a 1/2" plastic gas service line with a probe while looking for a grade 1 leak. Valid USA ticket. Excavated prior to marks being placed. PG&E at-fault - Other Error. Please see narrative for full details | No | Gas Line | Yes | Probing Tool | Other | Other | Yes | X215200924 | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Gas | Distribution Service |  | Yes | Other Error |  |  | 2022 Q2 |  |  |  | Yes | Blue | Other |  |  | 1st Party Gas | Yes | 2022-06-01 | ½” | 18 | 0 | N/A | 6 | Jun | 2022 |  |  | Yes
18948 | x | x | x |  | 2022-06-01 | Jun | 6 | 2022 | 78338 |  |  | 123730519 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Leland R. Anthony Fence Contractor damaged a 1/2" plastic gas service line with a post-hole digger while doing a fence replacement. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Leland R. Anthony Fence Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-01 | ½” | 24 | 37 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | Yes
18947 | x | x | x |  | 2022-06-01 | Jun | 6 | 2022 | 78361 |  |  | 123738323 | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Smith Denison Construction damaged a 1 1/4" plastic gas service line with a backhoe while excavating for future gas service installation. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X027303043 | Dig-In to PG&E Underground | 3rd Party-Contractor | Smith Denison Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-01 | 1 ¼” | 36 | 79 | N/A | 6 | Jun | 2022 |  |  | No
18945 | x | x | x |  | 2022-06-01 | Jun | 6 | 2022 | 78319 |  |  | 123728902 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Homeowner damaged a 1/2" plastic gas service line with an axe while removing a tree stump. No USA ticket. | No | Gas Line | Yes | Other Hand Tools | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-01 | ½” | 12 | 17 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
18944 | x | x | x |  | 2022-06-01 | Jun | 6 | 2022 | 78315 |  | 35353337 | 123728446 | Stanislaus | Central Valley | Yosemite | South | Oakdale | Yes | United Pavement Maintenance damaged a 2" plastic gas main with a mini-excavator while doing a sewer line replacement. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X213003946 | Dig-In to PG&E Underground | 3rd Party-Contractor | United Pavement Maintenance | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-01 | 2” | 24 | 84 | N/A | 6 | Jun | 2022 |  |  | No
18955 | x |  |  |  | 2022-06-02 | Jun | 6 | 2022 | 78397 |  |  |  | Butte | Northern | North Valley | North | Chico | Yes | Unknown contractor damaged the wrap on a 2" steel gas main with unknown tool and unknown cause. Unknown if there was a USA ticket | Yes | Gas Line | No | Unknown | Unknown | Inadequate Excavation Practices | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unknown | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-02 | 2” |  | 0 | Other | 6 | Jun | 2022 |  |  | No
18954 | x | x | x |  | 2022-06-02 | Jun | 6 | 2022 | 78403 |  |  | 123740876 | Merced | Central Valley | Yosemite | South | Merced | Yes | Phase One Construction damaged a 1 1/4" plastic gas main with a mini-excavator while doing site development for a new Starbucks. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Excavator | Site Development | Facility Was Not Located or Marked | Yes | X210402270 | Dig-In to PG&E Underground | 3rd Party-Contractor | Phase One Construction | Distribution Main |  | Yes | Locator Error - No Mark |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-02 | 1 ¼” | 36 | 28 | N/A | 6 | Jun | 2022 | Bargaining Unit |  | No
18952 | x | x | x |  | 2022-06-02 | Jun | 6 | 2022 | 78400 |  |  | 123741601 | San Mateo | Central Coast | Peninsula | Central | Atherton | Yes | Saviano Builders damaged a 1/2" steel gas service line with a mini-excavator while installing a new sewer. Valid USA ticket. PG&E at fault - Locator Error - No Marks | No | Gas Line | Yes | Excavator | Sewer | Facility Was Not Located or Marked | Yes | X212602507 | Dig-In to PG&E Underground | 3rd Party-Contractor | Saviano Builders | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-02 | ½” | 9 | 25 | N/A | 6 | Jun | 2022 | Bargaining Unit |  | No
18951 | x | x | x |  | 2022-06-02 | Jun | 6 | 2022 | 78388 |  |  | 123739323 | Merced | Central Valley | Yosemite | South | Merced | Yes | The Lopez Company damaged a 1/2" plastic gas service line with a shovel while installing electric wire. No USA ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | The Lopez Company | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-02 | ½” | 29 | 42 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | Yes
18950 | x | x | x |  | 2022-06-02 | Jun | 6 | 2022 | 78379 |  |  | 123738807 | San Mateo | Central Coast | Peninsula | Central | Atherton | Yes | DPI Inc. damaged a 1" plastic gas service line with a mini-excavator while installing a fire water line. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X211802522 | Dig-In to PG&E Underground | 3rd Party-Contractor | DPI Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-02 | 1” | 27 | 56 | N/A | 6 | Jun | 2022 |  |  | No
18959 | x | x | x |  | 2022-06-03 | Jun | 6 | 2022 | 78450 |  |  | 123751048 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Cardoza’s Pool & Concrete damaged a 3/4" steel gas service line with a stump grinder while removing a stump. No USA ticket. | No | Gas Line | Yes | Stump Grinder | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Cardoza’s Pool & Concrete | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-03 | ¾” | 8 | 43 | Excavator Did Not Believe a USA Ticket was Required | 6 | Jun | 2022 |  |  | No
18958 | x | x | x |  | 2022-06-03 | Jun | 6 | 2022 | 78470 |  |  | 123759130 | Contra Costa | Bay Area | East Bay | Central | Richmond | Yes | Digitek Engineering damaged a 3/4" steel gas service line with boring equipment while installing fiber optic lines. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Boring Equipment | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X21303719 | Dig-In to PG&E Underground | 3rd Party-Contractor | Digitek Engineering | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-03 | ¾” | 19 | 95 | N/A | 6 | Jun | 2022 |  |  | No
18957 | x | x | x |  | 2022-06-03 | Jun | 6 | 2022 | 78464 |  |  | 123753208 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Diamond D Construction damaged a 1" plastic gas service line with a mini-excavator while installing a storm drain. Expired USA ticket | No | Gas Line | Yes | Excavator | Drainage Work | No USA Ticket | No (expired) | X131201251 | Dig-In to PG&E Underground | 3rd Party-Contractor | Diamond D Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-03 | 1” | 22 | 29 | Expired USA ticket | 6 | Jun | 2022 |  |  | No
18964 | x | x |  |  | 2022-06-04 | Jun | 6 | 2022 | 78484 |  |  |  | Butte | Northern | North Valley | North | Oroville | Yes | Blue Iron Foundation and Shoring damaged an 8" gas transmission line with an auger while installing shoring. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | No | Auger | Other | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X213004081 | Dig-In to PG&E Underground | 2nd Party-Contractor | Blue Iron Foundations and Shoring | Transmission Line |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E Division Electric |  |  | 2nd Party Gas | Yes | 2022-06-04 | 8" | 96 | 0 | N/A | 6 | Jun | 2022 |  |  | No
18963 | x | x | x |  | 2022-06-04 | Jun | 6 | 2022 | 78483 |  | 45328527 | 123761755 | Yolo | Northern | Vacaville | North | Woodland | Yes | Homeowner damaged a 1/2" plastic gas service line with an auger while installing a fence. No USA ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-04 | ½” | 25 | 87 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | No
18962 | x | x | x |  | 2022-06-04 | Jun | 6 | 2022 | 78493 |  |  | 123764181 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while installing a fence. No USA ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-04 | ½” | 20 | 47 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
18961 | x | x | x |  | 2022-06-04 | Jun | 6 | 2022 | 78482 |  |  | 123762196 | Contra Costa | Bay Area | Diablo | South | Walnut Creek | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while doing landscaping. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-04 | ½” | 18 | 81 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
18960 | x | x | x |  | 2022-06-04 | Jun | 6 | 2022 | 78488 |  |  | 123763618 | Contra Costa | Bay Area | East Bay | Central | Pinole | Yes | Homeowner damaged a 3/4" steel gas service line with a digging bar while planting vegetables. No USA ticket. | No | Gas Line | Yes | Digging Bar | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-04 | ¾” | 12 | 120 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
18965 | x | x | x |  | 2022-06-05 | Jun | 6 | 2022 | 78502 |  | 45329093 | 123766398 | Santa Clara | Central Coast | De Anza | Central | Sunnyvale | Yes | City of Sunnyvale damaged a 1" plastic gas service line with an asphalt saw cutter while repairing a water leak. Valid USA ticket. Facility embedded in concrete | No | Gas Line | Yes | Cutting Machine | Water | Facility Embedded in Concrete | Yes | X215600037 | Dig-In to PG&E Underground | 3rd Party-Government Entity | City of Sunnyvale | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-06-05 | 1” | 9 | 96 | N/A | 6 | Jun | 2022 |  |  | No
18976 | x | x | x |  | 2022-06-06 | Jun | 6 | 2022 | 78536 |  |  | 123772701 | Merced | Central Valley | Yosemite | South | Atwater | Yes | MBS Engineering Inc. damaged a 2" plastic gas main line with an excavator while doing site development. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Site Development | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X215300232 | Dig-In to PG&E Underground | 3rd Party-Contractor | MBS Engineering Inc. | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-06 | 2” | 55 | 111 | N/A | 6 | Jun | 2022 |  | 990872 | No
18975 | x | x | x |  | 2022-06-06 | Jun | 6 | 2022 | 78546 |  |  | 123773091 | Santa Clara | Central Coast | San Jose | Central | Morgan Hill | Yes | Unlicensed contractor damaged a 1/2" plastic gas service line with a pick bar while installing a new fence. No USA ticket. | No | Gas Line | Yes | Digging Bar | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-06 | ½” | 24 | 49 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | Yes
18973 | x | x | x |  | 2022-06-06 | Jun | 6 | 2022 | 78524 |  | 45330649 | 123773163 | Yolo | Northern | Vacaville | North | Davis | Yes | Monticello Tree Service damaged a 1/2" plastic gas service line with an auger while installing a fence. No USA ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Monticello Tree Service | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-06 | ½” | 24 | 43 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 6 | Jun | 2022 |  |  | No
18972 | x | x | x |  | 2022-06-06 | Jun | 6 | 2022 | 78545 |  |  | 123772697 | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Outdoor Living Gardens (Robs Landscaping) damaged a 1 1/4" plastic inserted into 2" steel gas main with a pneumatic spade. Valid USA ticket. Facility embedded in concrete | No | Gas Line | Yes | Pneumatic Spader | Fencing | Facility Embedded in Concrete | Yes | X214200063 | Dig-In to PG&E Underground | 3rd Party-Contractor | Outdoor Living Gardens | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-06 | 2” | 10 | 128 | N/A | 6 | Jun | 2022 |  | 1027899 | No
18971 | x | x | x |  | 2022-06-06 | Jun | 6 | 2022 | 78538 |  |  | 123772648 | Contra Costa | Bay Area | East Bay | Central | San Pablo | Yes | Bay Cities Paving & Grading with a 1" plastic gas service line with a probe while doing a water main installation. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Probing Tool | Water | Failed to Dig with Care | Yes | X215203121 | Dig-In to PG&E Underground | 3rd Party-Contractor | Bay Cities Paving & Grading | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-06 | 1” | 42 | 158 | N/A | 6 | Jun | 2022 |  | 238650 | Yes
18969 | x | x | x |  | 2022-06-06 | Jun | 6 | 2022 | 78565 |  |  | 123781756 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | Unlicensed contractor damaged a 1" plastic gas service line with a shovel while installing a post. No USA ticket. | No | Gas Line | Yes | Shovel | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-06 | 1” | 24 | 97 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | Yes
18968 | x | x | x |  | 2022-06-06 | Jun | 6 | 2022 | 78558 |  |  | 123775249 | Placer | Northern | Sierra | North | Auburn | Yes | Unlicensed contractor damaged a 1/2" plastic gas service line with a post-hole digger while installing a fence. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Post-Hole Digger | Fencing | Failed to Dig with Care | Yes | X215000053 | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-06 | ½” | 14 | 53 | N/A | 6 | Jun | 2022 |  |  | Yes
18967 | x | x | x |  | 2022-06-06 | Jun | 6 | 2022 | 78531 |  |  | 123771644 | Marin | Bay Area | North Bay | North | San Anselmo | Yes | Alpha Trenchless damaged a 1" plastic gas service line with a jackhammer while replacing a sewer lateral. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Jackhammer | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X214001351 | Dig-In to PG&E Underground | 3rd Party-Contractor | Alpha Trenchless | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-06 | 1” | 21 | 22 | N/A | 6 | Jun | 2022 |  | 1044308 | No
18966 | x | x | x |  | 2022-06-06 | Jun | 6 | 2022 | 78537 |  | 45330503 | 123771153 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Ace Plumbing & Rooter, Inc. damaged a 1" plastic gas service line with a shovel while repairing a sewer line. No USA ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Ace Plumbing & Rooter, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-06 | 1” | 28 | 347 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  | 829071 | Yes
18981 | x | x | x |  | 2022-06-07 | Jun | 6 | 2022 | 78578 |  |  | 123779309 | Monterey | Central Coast | Central Coast | South | Salinas | Yes | Chris Wilson Plumbing damaged a 1/2" plastic gas service line with a steel probe while installing a sewer clean out. No USA ticket. | No | Gas Line | Yes | Probing Tool | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Chris Wilson Plumbing | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-07 | ½” | 24 | 33 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | Yes
18980 | x | x | x |  | 2022-06-07 | Jun | 6 | 2022 | 78589 |  |  | 123780377 | Contra Costa | Bay Area | East Bay | Central | Richmond | Yes | Vulcan Construction and Maintenance damaged a 3/4" steel gas service line with a core cutting machine while installing bollards. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Cutting Machine | Pole/Post Installation | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X215101123 | Dig-In to PG&E Underground | 2nd Party-Contractor | Vulcan Construction and Maintenance | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-06-07 | ¾” | 4 | 44 | N/A | 6 | Jun | 2022 |  | 414892 | No
18978 | x | x | x |  | 2022-06-07 | Jun | 6 | 2022 | 78600 |  |  | 123780578 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | New Image Construction damaged a 3/4" steel gas service line with a skid steer while replacing a driveway. No USA ticket. | No | Gas Line | Yes | Skid Steer | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | New Image Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-07 | ¾” | 10 | 32 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 6 | Jun | 2022 |  |  | No
18987 | x | x | x |  | 2022-06-08 | Jun | 6 | 2022 | 78632 |  |  | 123786965 | Kern | Central Valley | Kern | South | Bakersfield | Yes | AT&T damaged a 1/2" plastic gas service line with a shovel while trying to locate a telecommunications facility. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Dig with Care | Yes | X215600067 | Dig-In to PG&E Underground | 3rd Party-Contractor | AT&T | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-08 | ½” | 37 | 103 | N/A | 6 | Jun | 2022 |  |  | Yes
18986 | x | x |  |  | 2022-06-08 | Jun | 6 | 2022 | 78660 |  |  | 123795355 | San Mateo | Central Coast | Peninsula | Central | San Mateo | Yes | A&B Construction damaged a 1" plastic gas service line with an excavator for a gas line installation. Valid USA ticket. Excavated before legal start time | No | Gas Line | Yes | Excavator | Gas | Excavated Prior to Legal Excavation Start Date and Time | Yes | X122802236 | Dig-In to PG&E Underground | 3rd Party-Contractor | A&B Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-08 | 1” | 26 | 22 | N/A | 6 | Jun | 2022 |  |  | No
18985 | x | x | x |  | 2022-06-08 | Jun | 6 | 2022 | 78645 |  |  | 123789231 | Contra Costa | Bay Area | Diablo | South | Walnut Creek | Yes | Sefnco Communications damaged a 1/2" plastic gas service line with a mini-excavator while removing asphalt. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Road Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | W212600214 | Dig-In to PG&E Underground | 3rd Party-Contractor | Sefnco Communications | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-08 | ½” | 18 | 47 | N/A | 6 | Jun | 2022 |  |  | No
18984 | x | x | x |  | 2022-06-08 | Jun | 6 | 2022 | 78676 |  |  | 123793423 | Marin | Bay Area | North Bay | North | Tiburon | Yes | Homeowner damaged a 1" plastic gas service line with a pickaxe while removing some plants. No USA ticket. | No | Gas Line | Yes | Pickaxe | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-08 | 1” | 16 | 54 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
18983 | x | x | x |  | 2022-06-08 | Jun | 6 | 2022 | 78648 |  |  | 123789001 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Precision Engineering damaged a 1 1/4" plastic gas service line with an excavator while installing shoring as part of a sewer project. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X212300279 | Dig-In to PG&E Underground | 3rd Party-Contractor | Precision Engineering | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-08 | 1 ¼” | 46 | 45 | N/A | 6 | Jun | 2022 |  | 880266 | No
18982 | x | x | x |  | 2022-06-08 | Jun | 6 | 2022 | 78643 |  |  | 123788667 | Contra Costa | Bay Area | Diablo | South | Walnut Creek | Yes | Homeowner damaged a 3/4" steel gas service line with a sawzall while removing tree roots. No USA ticket. | No | Gas Line | Yes | Cutting Machine | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-08 | ¾” | 18 | 140 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 6 | Jun | 2022 |  |  | No
18994 | x | x | x |  | 2022-06-09 | Jun | 6 | 2022 | 78722 |  |  | 123801491 | Solano | Bay Area | North Bay | North | Vallejo | Yes | City of Vallejo Water damaged 1/2" plastic gas service line inserted into 3/4" steel with a backhoe while fixing a water main break. Valid USA ticket. Facility was not yet marked as this was an emergency and an emergency ticket had been called in but locator hadn't arrived yet to mark | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Excavated Prior to Legal Excavation Start Date and Time | Yes | X216001226 | Dig-In to PG&E Underground | 3rd Party-Government Entity | City of Vallejo Water | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-06-09 | ¾” | 6 | 99 | N/A | 6 | Jun | 2022 |  |  | No
18992 | x | x | x |  | 2022-06-09 | Jun | 6 | 2022 | 78710 |  |  | 123801203 | Alameda | Central Coast | Mission | South | Fremont | Yes | Baja Construction Services damaged a 1/2" plastic gas service line with a shovel while installing a new foundation. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Foundation Work | Failed to Dig with Care | Yes | X209500949 | Dig-In to PG&E Underground | 3rd Party-Contractor | Baja Construction Services | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-09 | ½” | 18 | 50 | N/A | 6 | Jun | 2022 |  | 1030428 | Yes
18990 | x | x | x |  | 2022-06-09 | Jun | 6 | 2022 | 78720 |  |  | 123801190 | San Mateo | Central Coast | Peninsula | Central | Burlingame | Yes | Bay Builders & Remodeling damaged a 1/2" plastic gas service line with a skid steer while grading a driveway. No USA ticket. | No | Gas Line | Yes | Skid Steer | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Bay Builders & Remodeling | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-09 | ½” | 18 | 16 | Believed They Knew Where Underground Utility was From Previous Knowledge | 6 | Jun | 2022 |  |  | No
18988 | x | x | x |  | 2022-06-09 | Jun | 6 | 2022 | 78699 |  |  | 123797280 | Alameda | Bay Area | East Bay | Central | Alameda | Yes | West Valley Construction damaged a 1/2" plastic gas service line inserted into 1 1/4" plastic with a PVC wire cutter while cutting the plastic sleeve around the service line. Valid USA ticket. Failed to protect exposed facility | No | Gas Line | Yes | Cutting Machine | Gas | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X203402714 | Dig-In to PG&E Underground | 2nd Party-Contractor | West Valley Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-06-09 | ½” | 16 | 17 | N/A | 6 | Jun | 2022 |  | 174968 | No
19002 | x | x | x |  | 2022-06-10 | Jun | 6 | 2022 | 78770 |  |  | 123819459 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | C&M Plumbing damaged a 1" plastic gas service line with a stake while installing new sewer pipe. No USA ticket. | No | Gas Line | Yes | Stake | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | C&M Plumbing | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-10 | 1” | 14 | 25 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | Yes
18999 | x | x |  |  | 2022-06-10 | Jun | 6 | 2022 | 78762 |  |  |  | Santa Cruz | Central Coast | Central Coast | South | Scotts Valley | Yes | Unlicensed contractor damaged a 1/2" plastic gas service line with a probe while locating an underground water leak. No USA ticket. | No | Gas Line | Yes | Probing Tool | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-10 | ½” | 18 | 93 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | Yes
18998 | x | x | x |  | 2022-06-10 | Jun | 6 | 2022 | 78742 |  |  | 123819990 | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | Cratus Inc. damaged a 1/2" plastic gas service line with an excavator while doing a water main installation. Valid USA ticket. PG&E at-fault - Other Error | No | Gas Line | Yes | Excavator | Water | Other | Yes | X132102328 | Dig-In to PG&E Underground | 3rd Party-Contractor | Cratus Inc | Distribution Service |  | Yes | Other Error |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-10 | ½” | 22 | 38 | N/A | 6 | Jun | 2022 |  |  | No
18996 | x | x | x |  | 2022-06-10 | Jun | 6 | 2022 | 78751 |  |  | 123817831 | Placer | Northern | Sierra | North | Roseville | Yes | Toro Engineering damaged a 2" steel gas stub with an excavator while installing a new water main. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X207701282 | Dig-In to PG&E Underground | 3rd Party-Contractor | Toro Engineering | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-10 | 2” | 40 | 113 | N/A | 6 | Jun | 2022 |  | 817832 | No
19006 | x | x | x |  | 2022-06-11 | Jun | 6 | 2022 | 78800 |  |  | 123825404 | San Mateo | Central Coast | Peninsula | Central | Menlo Park | Yes | Homeowner damaged 1/4" plastic inserted into 3/4" steel gas service line with an electric grinding tool while planting a tree. No USA ticket. | No | Gas Line | Yes | Cutting Machine | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-11 | ¾” | 16 | 148 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | No
19005 | x | x | x |  | 2022-06-11 | Jun | 6 | 2022 | 78791 |  |  | 123823545 | Shasta | Northern | North Valley | North | Redding | Yes | Homeowner damaged a 1/2" plastic gas service line with a hand tool while installing a fence. No USA ticket. | No | Gas Line | Yes | Other Hand Tools | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-11 | ½” | 18 | 28 | Believed They Knew Where Underground Utility was From Previous Knowledge | 6 | Jun | 2022 |  |  | Yes
19004 | x | x | x |  | 2022-06-11 | Jun | 6 | 2022 | 78799 |  |  | 123825534 | Yolo | Northern | Vacaville | North | Woodland | Yes | Unlicensed contractor damaged a 1/2" plastic gas service line with a post-hole digger while installing a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-11 | ½” | 19 | 69 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
19009 | x | x | x |  | 2022-06-12 | Jun | 6 | 2022 | 78813 |  | 45340778 | 123827203 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Unlicensed contractor damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-12 | ½” | 29 | 38 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
19008 | x | x | x |  | 2022-06-12 | Jun | 6 | 2022 | 78808 |  |  | 123826214 | Solano | Northern | Vacaville | North | Vacaville | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while digging fence post holes. Expired USA ticket. Marks were accurate from previous marks. Primary cause was failure to dig with care. | No | Gas Line | Yes | Post-Hole Digger | Fencing | Failed to Dig with Care | No (expired) | X209602444 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-12 | ½” | 30 | 46 | Expired USA ticket | 6 | Jun | 2022 |  |  | Yes
19007 | x | x | x |  | 2022-06-12 | Jun | 6 | 2022 | 78809 |  |  | 123826327 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while digging fence post holes. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-12 | ½” | 17 | 80 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
19017 | x | x | x |  | 2022-06-13 | Jun | 6 | 2022 | 78862 |  |  | 123845532 | Fresno | Central Valley | Fresno | South | San Joaquin | Yes | Viking Construction damaged a 4" gas transmission line with a ripper while grading. Valid USA ticket. Failed to maintain marks | No | Gas Line | Yes | Other Driven Machinery | Blading/Lot Grading | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | X120401214 | Dig-In to PG&E Underground | 3rd Party-Contractor | Viking Construction | Transmission Line |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-13 | 4" |  | 117 | N/A | 6 | Jun | 2022 |  |  | No
19015 | x | x | x |  | 2022-06-13 | Jun | 6 | 2022 | 78868 |  | 45342442 | 123835657 | Yolo | Northern | Vacaville | North | Woodland | Yes | Argonaut Constructors damaged a 1/2" plastic gas service line with a mini-excavator while excavating for a water main replacement. Valid USA ticket. Failed to protect subsurface installation | No | Gas Line | No | Excavator | Water | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X206600084 | Dig-In to PG&E Underground | 3rd Party-Contractor | Argonaut Constructors | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-13 | ½” | 18 |  | N/A | 6 | Jun | 2022 |  | 171432 | No
19014 | x | x | x |  | 2022-06-13 | Jun | 6 | 2022 | 78837 |  |  | 123830906 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | DPI damaged a 2" plastic gas main with a probe while locating the accurately marked gas line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Probing Tool | Sewer | Failed to Dig with Care | Yes | X022603359 | Dig-In to PG&E Underground | 3rd Party-Contractor | DPI | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-13 | 2” | 35 | 34 | N/A | 6 | Jun | 2022 |  |  | Yes
19013 | x | x |  |  | 2022-06-13 | Jun | 6 | 2022 | 78864 |  |  |  | Contra Costa | Bay Area | Diablo | South | Orinda | Yes | Mr Rooter Plumbing damaged a 1/2" copper gas service line with an excavator while digging a bell hole. Valid USA ticket. PG&E at-fault - Locator Error - Mismarked | No | Gas Line | Yes | Excavator | Sewer | Incorrect Information or Marks | Yes | X216100287 | Dig-In to PG&E Underground | 3rd Party-Contractor | Mr Rooter Plumbing | Distribution Service |  | Yes | Locator Error - Mismark |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-13 | ½” | 48 | 54 | N/A | 6 | Jun | 2022 | Contractor |  | No
19012 | x | x | x |  | 2022-06-13 | Jun | 6 | 2022 | 78880 |  |  | 123837940 | Alameda | Central Coast | Mission | South | Fremont | Yes | Unlicensed contractor damaged a 1" plastic gas service line with a shovel while building a new deck. No USA ticket. | No | Gas Line | Yes | Shovel | Other | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-13 | 1” | 13 | 22 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | Yes
19011 | x | x | x |  | 2022-06-13 | Jun | 6 | 2022 | 78861 |  |  | 123834235 | Solano | Northern | Vacaville | North | Dixon | Yes | Dennis and Sons Cement damaged a 1/2" plastic gas service line with a pickaxe while installing a concrete pad. No USA ticket. | No | Gas Line | Yes | Pickaxe | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Dennis and Sons Cement | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-13 | ½” | 12 | 34 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 6 | Jun | 2022 |  |  | Yes
19010 | x | x | x |  | 2022-06-13 | Jun | 6 | 2022 | 78834 |  |  | 123830552 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | KJ Woods Construction damaged a 1/2" plastic gas service line inserted into 3/4" steel gas service line with an excavator while installing a new sewer/storm drain. Valid USA ticket. Failed to protect subsurface installation | No | Gas Line | Yes | Excavator | Sewer | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X118903602 | Dig-In to PG&E Underground | 3rd Party-Contractor | KJ Woods Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-13 | ½” | 30 | 51 | N/A | 6 | Jun | 2022 |  | 701797 | No
19027 | x | x |  |  | 2022-06-14 | Jun | 6 | 2022 | 78950 |  |  |  | Contra Costa | Bay Area | Diablo | South | Alamo | Yes | Quality Landscape Solutions, Inc. damaged a 1" plastic gas service line with a shovel while planting a tree. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Quality Landscape Solutions, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-14 | 1” | 18 | 15 | Excavator Did Not Believe a USA Ticket was Required | 6 | Jun | 2022 |  |  | Yes
19025 | x | x | x |  | 2022-06-14 | Jun | 6 | 2022 | 78917 |  |  | 123840651 | Contra Costa | Bay Area | Diablo | South | Antioch | Yes | Pacific Coast Landscape Management damaged a 1" plastic gas service line with a trencher while installing drainage lines. No USA ticket. | No | Gas Line | Yes | Trencher | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Pacific Coast Landscape Management | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-14 | 1” | 18 | 48 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 6 | Jun | 2022 |  |  | No
19024 | x | x | x |  | 2022-06-14 | Jun | 6 | 2022 | 78910 |  |  | 123839791 | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Benjamin Franklin Plumbing damaged a 1/2" plastic gas service line with a pneumatic spade while doing a sewer lateral replacement. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Pneumatic Spader | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X213801084 | Dig-In to PG&E Underground | 3rd Party-Contractor | Benjamin Franklin Plumbing | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-14 | ½” | 32 | 14 | N/A | 6 | Jun | 2022 |  |  | No
19023 | x | x | x |  | 2022-06-14 | Jun | 6 | 2022 | 78896 |  | 45343062 | 123840814 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Mid-Cal Plumbing damaged a 1/2" plastic gas service line with a shovel while installing pool plumbing. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Other | Failed to Dig with Care | Yes | X215101222 | Dig-In to PG&E Underground | 3rd Party-Contractor | Mid-Cal Plumbing | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-14 | ½” | 18 | 24 | N/A | 6 | Jun | 2022 |  |  | Yes
19022 | x | x | x |  | 2022-06-14 | Jun | 6 | 2022 | 78911 |  |  | 123840188 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Homeowner damaged a 1/2" plastic gas service line with a mini-excavator while digging a trench for a drainage culvert. No USA ticket. | No | Gas Line | Yes | Excavator | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-14 | ½” | 24 | 38 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | No
19021 | x | x | x |  | 2022-06-14 | Jun | 6 | 2022 | 78901 |  |  | 123839780 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | F&A Plumbing & Rooter damaged a 1/2" plastic gas service line with a pickaxe while doing a gas houseline replacement. No USA ticket. | No | Gas Line | Yes | Pickaxe | Gas | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | F&A Plumbing & Rooter | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-14 | ½” | 18 | 30 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | Yes
19020 | x | x | x |  | 2022-06-14 | Jun | 6 | 2022 | 78947 |  |  | 123845019 | Fresno | Central Valley | Fresno | South | Fresno | Yes | PG&E Gas damaged a 2" plastic gas main with a backhoe while installing new gas distribution facilities. Valid USA ticket. Failed to protect subsurface installation | No | Gas Line | Yes | Backhoe/Trackhoe | Gas | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | W201900278 | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Gas | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Blue | PG&E GDGC |  |  | 1st Party Gas | Yes | 2022-06-14 | 2” | 38 | 23 | N/A | 6 | Jun | 2022 |  |  | No
19019 | x | x | x |  | 2022-06-14 | Jun | 6 | 2022 | 78937 |  |  | 123843760 | Sonoma | Northern | Sonoma | North | Sonoma | Yes | Redwood Residential Fence damaged 1" plastic gas service line with a post-hole digger while replacing a fence. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Post-Hole Digger | Fencing | Failed to Dig with Care | Yes | X214300226 | Dig-In to PG&E Underground | 3rd Party-Contractor | Redwood Residential Fence | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-14 | 1” | 36 | 99 | N/A | 6 | Jun | 2022 |  |  | Yes
19018 | x | x | x |  | 2022-06-14 | Jun | 6 | 2022 | 78903 |  |  | 123841748 | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | Unlicensed contractor damaged a 1/2" plastic gas service line with a shovel while replacing a driveway. No USA ticket. | No | Gas Line | Yes | Shovel | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-14 | ½” | 17 | 26 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
19034 | x | x | x |  | 2022-06-15 | Jun | 6 | 2022 | 78995 |  |  | 123850777 | Sacramento | Northern | Sacramento | North | Orangevale | Yes | Sacramento County damaged a 1/2" plastic gas service line with a post-hole digger while reinstalling a stop sign. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Government Entity | Sacramento County | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-06-15 | ½” | 29 | 47 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | Yes
19032 | x | x | x |  | 2022-06-15 | Jun | 6 | 2022 | 78987 |  |  | 123848582 | Sonoma | Northern | Sonoma | North | Petaluma | Yes | Homeowner damaged a 1/2" plastic gas service line with a mini-excavator while installing leach lines. No USA ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-15 | ½” | 46 | 75 | Other | 6 | Jun | 2022 |  |  | No
19031 | x | x | x |  | 2022-06-15 | Jun | 6 | 2022 | 78982 |  |  | 123850391 | Mendocino | Northern | Humboldt | North | Hopland | Yes | Farrell Gas damaged a 1/2" plastic gas service line with a mini-excavator while installing a gas houseline. No USA ticket. | No | Gas Line | Yes | Excavator | Gas | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Farrell Gas | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-15 | ½” | 32 | 115 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | No
19030 | x | x | x |  | 2022-06-15 | Jun | 6 | 2022 | 78980 |  |  | 123853489 | Alameda | Central Coast | Mission | South | Hayward | Yes | Miller Pipeline damaged a 3" steel gas main with an excavator deactivating the main. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X125302735 | Dig-In to PG&E Underground | 2nd Party-Contractor | Miller Pipeline | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-06-15 | 3" | 60 | 79 | N/A | 6 | Jun | 2022 |  | 978749 | No
19029 | x | x | x |  | 2022-06-15 | Jun | 6 | 2022 | 78972 |  | 45343609 | 123847566 | Stanislaus | Central Valley | Yosemite | South | Newman | Yes | Flowrite Inc. damaged a 1/2" plastic gas service line with a backhoe while working on a housing project. Valid USA ticket. PG&E at-fault - Locator Error - No Marks | No | Gas Line | Yes | Backhoe/Trackhoe | Site Development | Facility Was Not Located or Marked | Yes | W214300334 | Dig-In to PG&E Underground | 3rd Party-Contractor | Flowrite Inc. | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-15 | ½” | 12 | 46 | N/A | 6 | Jun | 2022 | Bargaining Unit |  | No
19028 | x | x |  |  | 2022-06-15 | Jun | 6 | 2022 | 78998 |  |  |  | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Homeowner damaged a 1/2" plastic gas service line with a pickaxe while replacing a plant. No USA ticket. | No | Gas Line | Yes | Pickaxe | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-15 | ½” | 14 | 28 | Excavator Did Not Believe a USA Ticket was Required | 6 | Jun | 2022 |  |  | Yes
19043 | x | x | x |  | 2022-06-16 | Jun | 6 | 2022 | 79034 |  |  | 123856115 | Napa | Bay Area | North Bay | North | St Helena | Yes | BKW Concrete damaged a 1/2" plastic gas service line inserted into 3/4" steel gas service line with an excavator while installing a new foundation. No USA ticket. | No | Gas Line | Yes | Excavator | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | BKW Concrete | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-16 | 1” | 6 | 5 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | No
19042 | x | x |  |  | 2022-06-16 | Jun | 6 | 2022 | 79038 |  |  |  | Fresno | Central Valley | Fresno | South | Fresno | Yes | True Greenscapes damaged a 1" plastic purge point with a skid steer while doing landscaping. No USA ticket. | No | Gas Line | Yes | Skid Steer | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | True Greenscapes | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-16 | 1” | 24 | 69 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 6 | Jun | 2022 |  | 986890 | No
19040 | x | x |  |  | 2022-06-16 | Jun | 6 | 2022 | 79064 |  |  |  | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | Villalobos & Associates damaged a 3/4" steel gas service line with a skid steer while grading for a new driveway. No USA ticket. | No | Gas Line | No | Skid Steer | Driveway Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Villalobos & Associates | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-16 | ¾” |  | 0 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 6 | Jun | 2022 |  | 1017098 | No
19039 | x | x | x |  | 2022-06-16 | Jun | 6 | 2022 | 79040 |  |  | 123856827 | Fresno | Central Valley | Fresno | South | Fresno | Yes | City of Fresno damaged a 3/4" steel gas service line with a backhoe while installing a new sewer system. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X213100332 | Dig-In to PG&E Underground | 3rd Party-Government Entity | City of Fresno | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-06-16 | ¾” | 30 | 57 | N/A | 6 | Jun | 2022 |  |  | No
19038 | x | x | x |  | 2022-06-16 | Jun | 6 | 2022 | 79049 |  |  | 123857713 | Stanislaus | Central Valley | Yosemite | South | Oakdale | Yes | Jack Wilson Construction damaged a 1" plastic gas service line with a skid steer while doing fencing work. No USA ticket. | No | Gas Line | Yes | Skid Steer | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Jack Wilson Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-16 | 1” | 30 | 28 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | No
19037 | x | x | x |  | 2022-06-16 | Jun | 6 | 2022 | 79024 |  |  | 123855366 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Pacific Utility Construction damaged a 1/2" plastic gas service line with a shovel while installing telecommunications lines. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Dig with Care | Yes | X213902127 | Dig-In to PG&E Underground | 3rd Party-Contractor | Pacific Utility Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-16 | ½” | 25 | 24 | N/A | 6 | Jun | 2022 |  |  | Yes
19036 | x | x | x |  | 2022-06-16 | Jun | 6 | 2022 | 79018 |  |  | 123854998 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Garney Construction damaged a 3/4" steel gas service line with an excavator while installing a water main. Valid USA ticket. Facility embedded in concrete | No | Gas Line | Yes | Excavator | Water | Facility Embedded in Concrete | Yes | X211701993 | Dig-In to PG&E Underground | 3rd Party-Contractor | Garney Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-16 | ¾” | 12 | 27 | N/A | 6 | Jun | 2022 |  |  | No
19053 | x |  |  |  | 2022-06-17 | Jun | 6 | 2022 | 79083 |  |  |  | Fresno | Central Valley | Fresno | South | Fresno | Yes | Valverde Construction damaged the wrap on 3" steel gas distribution line with an unknown tool doing unknown work. No USA ticket. | Yes | Gas Line | No | Unknown | Unknown | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Valverde Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-17 | 3" |  |  | Other | 6 | Jun | 2022 |  |  | No
19051 | x | x | x |  | 2022-06-17 | Jun | 6 | 2022 | 79104 |  |  | 123866440 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while doing fence post excavation. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-17 | ½” | 24 | 38 | Believed They Knew Where Underground Utility was From Previous Knowledge | 6 | Jun | 2022 |  |  | Yes
19050 | x | x | x |  | 2022-06-17 | Jun | 6 | 2022 | 79113 |  |  | 123884192 | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Unlicensed contractor damaged a 1/2" plastic gas service line inserted 3/4" steel gas service line with a digging bar while building a new fence. No USA ticket. | No | Gas Line | Yes | Digging Bar | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-17 | ½” | 19 | 96 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
19049 | x | x | x |  | 2022-06-17 | Jun | 6 | 2022 | 79087 |  |  | 123866110 | Alameda | Central Coast | Mission | South | Newark | Yes | Juan Rodriguez Landscaping damaged a 1/2" plastic gas service line with a shovel while attempting to locate the facility. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Pole/Post Installation | Failed to Dig with Care | Yes | W215900116 | Dig-In to PG&E Underground | 3rd Party-Contractor | Juan Rodriguez Landscaping | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-17 | ½” | 26 | 20 | N/A | 6 | Jun | 2022 |  |  | Yes
19048 | x | x | x |  | 2022-06-17 | Jun | 6 | 2022 | 79092 |  |  | 123865494 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | MP Nexlevel damaged a 1/2" plastic gas service line with an mini-excavator while installing telecommunications. Expired USA ticket. | No | Gas Line | Yes | Excavator | Telecommunications | No USA Ticket | No (expired) | X212901672 | Dig-In to PG&E Underground | 3rd Party-Contractor | MP Nexlevel | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-17 | ½” | 36 | 23 | Expired USA ticket | 6 | Jun | 2022 |  |  | No
19047 | x | x | x |  | 2022-06-17 | Jun | 6 | 2022 | 79116 |  |  | 123868834 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Homeowner damaged a 1" plastic gas service line with an auger while installing a fence. No USA ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-17 | 1” | 37 | 35 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | No
19046 | x | x | x |  | 2022-06-17 | Jun | 6 | 2022 | 79088 |  | 45346184 | 123864983 | Santa Cruz | Central Coast | Central Coast | South | Scotts Valley | Yes | Santa Cruz Pipe Fitters damaged a 1/2" plastic gas service line with a digging bar while replacing a water service. No USA ticket. | No | Gas Line | Yes | Digging Bar | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Santa Cruz Pipe Fitters | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-17 | ½” | 24 | 45 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | Yes
19045 | x | x | x |  | 2022-06-17 | Jun | 6 | 2022 | 79077 |  |  | 123865760 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | SMUD damaged a 1 1/4" plastic gas service line with an excavator while repairing an electric outage. No USA ticket. | No | Gas Line | Yes | Excavator | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Government Entity | SMUD | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-06-17 | 1 ¼” | 46 | 58 | Asserted They Could Not Wait (Emergency) | 6 | Jun | 2022 |  |  | No
19044 | x | x | x |  | 2022-06-17 | Jun | 6 | 2022 | 79090 |  |  | 123869652 | Marin | Bay Area | North Bay | North | San Rafael | Yes | Homeowner damaged a 3/4" steel gas service line with a bulldozer while clearing a fire road of debris. No USA ticket. | No | Gas Line | Yes | Bulldozer | Other | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-17 | ¾” | 4 | 32 | Excavator Did Not Believe a USA Ticket was Required | 6 | Jun | 2022 |  |  | No
19058 | x | x | x |  | 2022-06-18 | Jun | 6 | 2022 | 79132 |  |  | 123874726 | Sonoma | Northern | Sonoma | North | Sebastopol | Yes | Homeowner damaged a 1" plastic gas service line with a shovel while installing a new gate post. No USA ticket. | No | Gas Line | Yes | Shovel | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-18 | 1” | 28 | 45 | Believed They Knew Where Underground Utility was From Previous Knowledge | 6 | Jun | 2022 |  |  | Yes
19057 | x |  | x |  | 2022-06-18 | Jun | 6 | 2022 | 79124 |  |  | 123872291 | Santa Clara | Central Coast | De Anza | Central | Campbell | Yes | SPV Construction damaged a 3/4" steel gas service line with a skid steer while grading. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Skid Steer | Blading/Lot Grading | Incorrect facility records/maps | Yes | X216601179 | Dig-In to PG&E Underground | 3rd Party-Contractor | SPV Construction | Distribution Service |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-18 | ¾” | 36 | 107 | N/A | 6 | Jun | 2022 |  |  | No
19056 | x | x | x |  | 2022-06-18 | Jun | 6 | 2022 | 79135 |  | 45347435 | 123874458 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while installing pavers. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Landscaping | Failed to Dig with Care | Yes | X213703588 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-18 | ½” | 21 | 33 | N/A | 6 | Jun | 2022 |  |  | Yes
19054 | x |  | x |  | 2022-06-18 | Jun | 6 | 2022 | 79137 |  |  | 123874796 | Santa Clara | Central Coast | De Anza | Central | Los Altos | Yes | AK Construction damaged a 1" plastic gas service line with a skid steer while grading. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Skid Steer | Blading/Lot Grading | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X100401598 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ak Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-18 | 1” | 12 | 42 | N/A | 6 | Jun | 2022 |  |  | No
19064 | x | x | x |  | 2022-06-20 | Jun | 6 | 2022 | 79185 |  |  | 123883123 | Monterey | Central Coast | Central Coast | South | Carmel | Yes | Carroll Strong Builders Inc. damaged a 1/2" plastic gas service line with a shovel while installing a water line. No USA ticket. | No | Gas Line | Yes | Shovel | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Carroll Strong Builders Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-20 | ½” | 24 | 50 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | Yes
19063 | x | x | x |  | 2022-06-20 | Jun | 6 | 2022 | 79178 |  |  | 123882419 | Sacramento | Northern | Sacramento | North | Elk Grove | Yes | Golden State Utility damaged a 1/2" plastic gas service line with boring equipment while doing a telecommunications install. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Boring Equipment | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X211800846 | Dig-In to PG&E Underground | 3rd Party-Contractor | Golden State Utility | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-20 | ½” | 42 | 76 | N/A | 6 | Jun | 2022 |  |  | No
19062 | x | x | x |  | 2022-06-20 | Jun | 6 | 2022 | 79169 |  |  | 123880805 | Sacramento | Northern | Sacramento | North | Folsom | Yes | Homeowner damaged a 2" gas main with an excavator while replacing a sewer line. No USA ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-20 | 2” | 33 | 75 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | No
19061 | x | x | x |  | 2022-06-20 | Jun | 6 | 2022 | 79193 |  |  | 123883414 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Unlicensed contractor damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence post. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-20 | ½” | 32 | 101 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
19060 | x | x |  |  | 2022-06-20 | Jun | 6 | 2022 | 79176 |  |  |  | Contra Costa | Bay Area | Diablo | South | Moraga | Yes | Roto Rooter damaged a 1/2" plastic gas service line with an excavator while repairing a sewer. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X216900110 | Dig-In to PG&E Underground | 3rd Party-Contractor | Roto Rooter | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-20 | ½” | 20 | 48 | N/A | 6 | Jun | 2022 |  |  | No
19059 | x | x | x |  | 2022-06-20 | Jun | 6 | 2022 | 79179 |  |  | 123881974 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Signature Pools and Spa damaged a 1/2" plastic gas service line with a trencher while building a pool. Valid USA ticket. Failed to maintain marks | No | Gas Line | Yes | Trencher | Other | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | X213701711 | Dig-In to PG&E Underground | 3rd Party-Contractor | Signature Pools and Spa | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-20 | ½” | 30 | 41 | N/A | 6 | Jun | 2022 |  |  | No
19073 | x |  |  |  | 2022-06-21 | Jun | 6 | 2022 | 79227 |  |  |  | Santa Clara | Central Coast | San Jose | Central | Morgan Hill | Yes | Garney Construction damaged a 1/2" plastic gas service line with an excavator while doing a water line install. Valid USA ticket. Failed to protect subsurface installation | No | Gas Line | Yes | Excavator | Water | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | W215400153 | Dig-In to PG&E Underground | 3rd Party-Contractor | Garney Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-21 | ½” | 36 | 28 | N/A | 6 | Jun | 2022 |  |  | No
19072 | x | x | x |  | 2022-06-21 | Jun | 6 | 2022 | 79230 |  |  | 123890144 | Marin | Bay Area | North Bay | North | San Anselmo | Yes | Homeowner damaged 2" steel gas main with a auger but attached to excavator while digging pier holes. Valid USA ticket. Excavated outside delineated area | No | Gas Line | Yes | Auger | Pole/Post Installation | Excavated Outside Delineated Area | Yes | W216600149 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-21 | 2” | 24 | 66 | N/A | 6 | Jun | 2022 |  |  | No
19071 | x | x |  |  | 2022-06-21 | Jun | 6 | 2022 | 79244 |  |  |  | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Pacific Parks Landscaping damaged a 1" plastic gas service line with a shovel while installing a water drainage ditch. No USA ticket. | No | Gas Line | Yes | Shovel | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Pacific Parks Landscaping | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-21 | 1” | 27 | 24 | Believed They Knew Where Underground Utility was From Previous Knowledge | 6 | Jun | 2022 |  |  | Yes
19070 | x | x | x |  | 2022-06-21 | Jun | 6 | 2022 | 79235 |  |  | 123889952 | Fresno | Central Valley | Fresno | South | Fresno | Yes | First Priority Electric damaged a 1" plastic gas service line with a digging bar while installing a gas line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Digging Bar | Gas | Failed to Dig with Care | Yes | X216702297 | Dig-In to PG&E Underground | 3rd Party-Contractor | First Priority Electric | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-21 | 1” | 39 | 14 | N/A | 6 | Jun | 2022 |  |  | Yes
19069 | x | x | x |  | 2022-06-21 | Jun | 6 | 2022 | 79200 |  |  | 123885113 | Mendocino | Northern | Humboldt | North | Willits | Yes | Homeowner damaged a 1/2" plastic gas service line with a t-post while installing a fence. No USA ticket. | No | Gas Line | Yes | Other Hand Tools | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-21 | ½” | 14 | 149 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 6 | Jun | 2022 |  |  | Yes
19068 | x | x |  |  | 2022-06-21 | Jun | 6 | 2022 | 79208 |  |  |  | Contra Costa | Bay Area | East Bay | Central | Richmond | Yes | EBMUD damaged a 1/2" plastic gas service line with an excavator while installing a water main. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Water | Incorrect facility records/maps | Yes | W215100147 | Dig-In to PG&E Underground | 3rd Party-Government Entity | EBMUD | Distribution Service |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2022-06-21 | ½” | 46 | 34 | N/A | 6 | Jun | 2022 |  |  | No
19067 | x |  | x |  | 2022-06-21 | Jun | 6 | 2022 | 79239 |  |  | 123890587 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Sebastian Corp damaged a 1" plastic gas service line with a shovel while preparing a foundation. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Foundation Work | Failed to Dig with Care | No (expired) | X211501938 | Dig-In to PG&E Underground | 3rd Party-Contractor | Sebastian Corp | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-21 | 1” | 23 | 17 | Expired USA ticket | 6 | Jun | 2022 |  |  | Yes
19066 | x | x | x |  | 2022-06-21 | Jun | 6 | 2022 | 79219 |  | 45349637 | 123886532 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | United Site Services damaged 1" plastic gas service line with a digging bar while installing an electric power post. Expired USA ticket. Primary cause was no delineations | No | Gas Line | Yes | Digging Bar | Pole/Post Installation | Failed to Delineate Work Site With Required Markings | No (expired) | X213200946 | Dig-In to PG&E Underground | 3rd Party-Contractor | United Site Services | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-21 | 1” | 30 | 64 | Expired USA ticket | 6 | Jun | 2022 |  |  | Yes
19079 | x | x | x |  | 2022-06-22 | Jun | 6 | 2022 | 79270 |  |  | 123896840 | Monterey | Central Coast | Central Coast | South | Carmel | Yes | Unlicensed contractor damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-22 | ½” | 14 | 45 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
19077 | x | x |  |  | 2022-06-22 | Jun | 6 | 2022 | 79318 |  |  |  | Kern | Central Valley | Kern | South | Bakersfield | Yes | Homeowner damaged a 1/2" plastic gas service line with a stake while planting roses. No USA ticket. | No | Gas Line | Yes | Stake | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-22 | ½” | 20 | 35 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
19076 | x | x | x |  | 2022-06-22 | Jun | 6 | 2022 | 79273 |  |  | 123895644 | Butte | Northern | North Valley | North | Paradise | Yes | Homeowner damaged a 1" plastic gas service line with a backhoe while installing a sprinkler system. No USA ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Irrigation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-22 | 1” | 30 | 29 | Believed They Knew Where Underground Utility was From Previous Knowledge | 6 | Jun | 2022 |  |  | No
19075 | x | x | x |  | 2022-06-22 | Jun | 6 | 2022 | 79296 |  |  | 123898787 | Fresno | Central Valley | Fresno | South | Fresno | Yes | West Valley Construction damaged a 3/4" steel gas service line with a 1/2" insert with a backhoe while installing electrical conduit. Valid USA ticket. PG&E at-fault Locator Error - No Marks | No | Gas Line | Yes | Backhoe/Trackhoe | Electric Work | Facility Was Not Located or Marked | Yes | X215100536 | Dig-In to PG&E Underground | 2nd Party-Contractor | West Valley Construction | Distribution Service |  | Yes | Locator Error - No Mark |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E Division Electric |  |  | 2nd Party Gas | Yes | 2022-06-22 | ½” | 21 | 55 | N/A | 6 | Jun | 2022 | Bargaining Unit | 174968 | No
19074 | x | x | x |  | 2022-06-22 | Jun | 6 | 2022 | 79302 |  |  | 123899663 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Marin Home Restorations damaged a 1/2" plastic gas service line with a pickaxe while digging a drainage trench. No USA ticket. | No | Gas Line | Yes | Pickaxe | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Marin Home Restorations | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-22 | ½” | 16 | 30 | Excavator Did Not Believe a USA Ticket was Required | 6 | Jun | 2022 |  |  | Yes
19087 | x | x | x |  | 2022-06-23 | Jun | 6 | 2022 | 79369 |  |  | 123906502 | Placer | Northern | Sierra | North | Granite Bay | Yes | Hawks Electrical damaged a 1" plastic gas service line with an mini-excavator while installing a drainage pipe. No USA ticket. | No | Gas Line | Yes | Excavator | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Hawks Electrical | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-23 | 1” | 30 | 45 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 6 | Jun | 2022 |  | 286815 | No
19086 | x |  | x |  | 2022-06-23 | Jun | 6 | 2022 | 79381 |  |  | 123908950 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Landscaping Development damaged a 1" plastic gas service line with a trencher while installing irrigation lines. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Trencher | Irrigation | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X216501749 | Dig-In to PG&E Underground | 3rd Party-Contractor | Landscaping Development | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-23 | 1” | 18 | 20 | N/A | 6 | Jun | 2022 |  |  | No
19085 | x | x |  |  | 2022-06-23 | Jun | 6 | 2022 | 79353 |  |  |  | Alameda | Bay Area | East Bay | Central | Oakland | Yes | Larrieta Sanitation (LS) Construction damaged a 1/2" plastic gas service line inserted into 3/4" steel with a concrete saw cutter while repairing a sidewalk. No USA ticket but there were accurate markings at the location. Primary cause of incident is facility embedded in concrete | No | Gas Line | Yes | Cutting Machine | Curb/Sidewalk Work | Facility Embedded in Concrete | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Larrieta Sanitation (LS) Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-23 | ½” | 2 | 58 | Didn’t Think They Were Digging Deep Enough to Damage an Underground Utility | 6 | Jun | 2022 |  | 1007540 | No
19084 | x | x | x |  | 2022-06-23 | Jun | 6 | 2022 | 79365 |  |  | 123906248 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Landscape Development damaged a 1" plastic gas service line with an excavator while installing a new storm drain. No USA ticket. | No | Gas Line | Yes | Excavator | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Landscape Development | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-23 | 1” | 32 | 25 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | No
19082 | x | x | x |  | 2022-06-23 | Jun | 6 | 2022 | 79344 |  | 45351756 | 123904031 | Stanislaus | Central Valley | Yosemite | South | Ceres | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while replacing a fence. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-23 | ½” | 23 | 17 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 6 | Jun | 2022 |  |  | Yes
19095 | x | x | x |  | 2022-06-24 | Jun | 6 | 2022 | 79438 |  |  | 123920542 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Michael O'Shaughnessy Construction damaged a 4" plastic gas main with a mini-excavator while connecting a sewer lateral. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X211101577 | Dig-In to PG&E Underground | 3rd Party-Contractor | Michael O'Shaughnessy Construction | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-24 | 4" | 36 | 247 | N/A | 6 | Jun | 2022 |  |  | No
19094 | x | x | x |  | 2022-06-24 | Jun | 6 | 2022 | 79434 |  |  | 123919588 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Esquivel Grading & Paving, Inc. damaged a 2" plastic gas main with a mini-excavator while excavating for a new water main. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X214403057 | Dig-In to PG&E Underground | 3rd Party-Contractor | Esquivel Grading & Paving, Inc. | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-24 | 2” | 28 | 130 | N/A | 6 | Jun | 2022 |  |  | No
19093 | x | x | x |  | 2022-06-24 | Jun | 6 | 2022 | 79432 |  |  | 123916883 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while doing fencing work. No USA ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-24 | ½” | 23 | 11 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
19092 | x | x | x |  | 2022-06-24 | Jun | 6 | 2022 | 79441 |  | 45353118 | 123919582 | Shasta | Northern | North Valley | North | Redding | Yes | Homeowner damaged a 1 1/4" gas main with a post while replacing a mailbox post. No USA ticket. | No | Gas Line | Yes | Other Hand Tools | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2022-06-24 | 1 ¼” | 25 | 59 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
19091 | x | x | x |  | 2022-06-24 | Jun | 6 | 2022 | 79415 |  |  | 123914897 | Alameda | Bay Area | East Bay | Central | Berkeley | Yes | Cratus Inc damaged a 1/2" plastic gas service line with an excavator while doing a water main installation. Valid USA ticket. PG&E at-fault - Locator Error - Mismark | No | Gas Line | Yes | Excavator | Water | Incorrect Information or Marks | Yes | X216800119 | Dig-In to PG&E Underground | 3rd Party-Contractor | Cratus Inc | Distribution Service |  | Yes | Locator Error - Mismark |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-24 | ½” | 42 | 20 | N/A | 6 | Jun | 2022 | Bargaining Unit |  | No
19090 | x |  | x |  | 2022-06-24 | Jun | 6 | 2022 | 79420 |  |  | 123915714 | San Mateo | Bay Area | Peninsula | Central | South San Francisco | Yes | Unlicensed contractor damaged a 1" plastic gas service line with a shovel while repairing a water line. No USA ticket. | No | Gas Line | Yes | Shovel | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-24 | 1” | 32 | 28 | Other | 6 | Jun | 2022 |  |  | Yes
19088 | x |  | x |  | 2022-06-24 | Jun | 6 | 2022 | 79404 |  |  | 123943030 | Santa Clara | Central Coast | De Anza | Central | Mountain View | Yes | Hillenbrand Excavation damaged a 1 1/4" plastic gas service line with a mini-excavator while doing street light work. Expired USA ticket. No markings were visible as ticket expired 2/10. Primary cause is no USA ticket | No | Gas Line | Yes | Excavator | Street Light Work | No USA Ticket | No (expired) | X201300488 | Dig-In to PG&E Underground | 3rd Party-Contractor | Hillenbrand Excavation | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-24 | 1 ¼” | 30 | 52 | Expired USA ticket | 6 | Jun | 2022 |  |  | No
19097 | x | x | x |  | 2022-06-25 | Jun | 6 | 2022 | 79459 |  |  | 123922587 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Precision Electric damaged a 1/2" plastic gas service line with a shovel while replacing the electrical box to a residence. Expired USA ticket. Primary cause of incident was failed to dig with care. | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | No (expired) | X213901352 | Dig-In to PG&E Underground | 3rd Party-Contractor | Precision Electric | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-25 | ½” | 18 | 28 | Expired USA ticket | 6 | Jun | 2022 |  |  | Yes
19096 | x | x | x |  | 2022-06-25 | Jun | 6 | 2022 | 79470 |  |  | 123926214 | Monterey | Central Coast | Central Coast | South | Salinas | Yes | Unlicensed contractor damaged a 1/2" plastic gas service line with a shovel while building a retaining wall. No USA ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-25 | ½” | 30 | 122 | No Knowledge of USA Ticketing Process | 6 | Jun | 2022 |  |  | Yes
19103 | x | x | x |  | 2022-06-27 | Jun | 6 | 2022 | 79540 |  |  | 123938011 | San Mateo | Central Coast | Peninsula | Central | Foster City | Yes | Caccia Plumbing damaged a 1/2" plastic gas service line with a shovel while installing a new sewer lateral. Valid USA ticket. Excavated prior to receiving positive response | No | Gas Line | Yes | Shovel | Sewer | Excavated Prior to Receiving a Positive Response From All Utilities | Yes | X217800830 | Dig-In to PG&E Underground | 3rd Party-Contractor | Caccia Plumbing | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-27 | ½” | 24 | 21 | N/A | 6 | Jun | 2022 |  |  | Yes
19102 | x | x | x |  | 2022-06-27 | Jun | 6 | 2022 | 79514 |  |  | 123934964 | Yolo | Northern | Vacaville | North | Davis | Yes | VE Electric damaged a 1/2" plastic gas service line with a pickaxe while excavating for new electric service. Valid USA ticket. Failed to maintain marks | No | Gas Line | Yes | Pickaxe | Electric Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | X215902598 | Dig-In to PG&E Underground | 3rd Party-Contractor | VE Electric | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-27 | ½” | 30 | 29 | N/A | 6 | Jun | 2022 |  |  | Yes
19101 | x | x | x |  | 2022-06-27 | Jun | 6 | 2022 | 79533 |  |  | 123935933 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Darcy & Harty Construction Inc damaged a 1" plastic gas service line with an excavator while repaving a street. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Road Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X207601952 | Dig-In to PG&E Underground | 3rd Party-Contractor | Darcy & Harty Construction Inc | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-27 | 1” | 14 | 13 | N/A | 6 | Jun | 2022 |  |  | No
19100 | x | x |  |  | 2022-06-27 | Jun | 6 | 2022 | 79531 |  |  |  | Placer | Northern | Sierra | North | Lincoln | Yes | Central Valley Engineering damaged a 1" plastic gas service line with an excavator while installing a new water main. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X214301305 | Dig-In to PG&E Underground | 3rd Party-Contractor | Central Valley Engineering | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-27 | 1” | 108 | 38 | N/A | 6 | Jun | 2022 |  |  | No
19099 | x | x | x |  | 2022-06-27 | Jun | 6 | 2022 | 79523 |  |  | 123934768 | San Joaquin | Central Valley | Stockton | South | Lathrop | Yes | Lawler Excavations Pipeline and Utilities, Inc. damaged a 2" plastic gas main with a backhoe while doing a water pipe installation. Valid USA ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Incorrect facility records/maps | Yes | X217200813 | Dig-In to PG&E Underground | 3rd Party-Contractor | Lawler Excavations Pipeline and Utilities, Inc. | Distribution Main |  | Yes | Records Error |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-27 | 2” | 36 | 54 | N/A | 6 | Jun | 2022 |  |  | No
19098 | x |  | x |  | 2022-06-27 | Jun | 6 | 2022 | 79509 |  |  | 123937468 | Fresno | Central Valley | Fresno | South | Fresno | Yes | West Valley Construction damaged a 1/2" plastic gas service line with backhoe while installing electrical conduit. Valid USA ticket. Failed to protect subsurface installation | No | Gas Line | Yes | Backhoe/Trackhoe | Electric Work | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | X215100536 | Dig-In to PG&E Underground | 2nd Party-Contractor | West Valley Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E Division Electric |  |  | 2nd Party Gas | Yes | 2022-06-27 | ½” | 36 | 77 | N/A | 6 | Jun | 2022 |  | 174968 | No
19109 | x |  |  |  | 2022-06-28 | Jun | 6 | 2022 | 79579 |  |  |  | Sonoma | Central Coast | Sonoma | North | Cotati | Yes | True Value Hardware damaged a 1" plastic gas service line with a shovel while repairing a water line. No USA ticket. | No | Gas Line | Yes | Shovel | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | True Value Hardware | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-28 | 1” | 35 | 147 | Other | 6 | Jun | 2022 |  |  | Yes
19107 | x | x | x |  | 2022-06-28 | Jun | 6 | 2022 | 79562 |  |  | 123939437 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | WWF Contractors Corp damaged a 1" plastic gas service line with a backhoe while installing new gas service. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X216403105 | Dig-In to PG&E Underground | 3rd Party-Contractor | WWF Contractors Corp | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-28 | 1” | 36 | 31 | N/A | 6 | Jun | 2022 |  |  | No
19106 | x | x | x |  | 2022-06-28 | Jun | 6 | 2022 | 79587 |  |  | 123945843 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Doherty Restoration, Inc. damaged a 1" plastic gas service line with pickaxe while excavating a foundation. No USA ticket. | No | Gas Line | Yes | Pickaxe | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Doherty Restoration, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-28 | 1” | 6 | 57 | Excavator Did Not Believe a USA Ticket was Required | 6 | Jun | 2022 |  |  | Yes
19119 | x |  | x |  | 2022-06-29 | Jun | 6 | 2022 | 79662 |  |  | 123958086 | San Benito | Central Coast | Central Coast | South | Hollister | Yes | Robinson & Moretti, Inc damaged a 1 1/4" gas service line with an excavator while working on storm drain. Expired USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Drainage Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No (expired) | W214300168 | Dig-In to PG&E Underground | 3rd Party-Contractor | Robinson & Moretti, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-29 | 1 ¼” | 42 | 38 | Expired USA ticket | 6 | Jun | 2022 |  |  | No
19118 | x | x | x |  | 2022-06-29 | Jun | 6 | 2022 | 79625 |  | 45356708 | 123954076 | Butte | Northern | North Valley | North | Oroville | Yes | Unlicensed contractor damaged a 1/2" plastic gas service line inserted into 1 1/4" steel with a shovel while installing posts. No USA ticket. | No | Gas Line | Yes | Shovel | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-29 | ½” | 16 | 26 | Believed They Knew Where Underground Utility was From Previous Knowledge | 6 | Jun | 2022 |  |  | Yes
19117 | x | x | x |  | 2022-06-29 | Jun | 6 | 2022 | 79659 |  |  | 123959315 | Sacramento | Northern | Sacramento | North | Rio Linda | Yes | The Handy Man damaged a 3/4" steel gas service line with a jackhammer while replacing a fence post. No USA ticket. | No | Gas Line | Yes | Jackhammer | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | The Handy Man | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-29 | ¾” | 24 | 64 | Excavator Did Not Believe a USA Ticket was Required | 6 | Jun | 2022 |  |  | No
19116 | x |  | x |  | 2022-06-29 | Jun | 6 | 2022 | 79630 |  |  | 123954072 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Lyle's Construction damaged a 1/2" plastic gas service line with a shovel while potholing to replace gas services. Valid USA ticket. Failed to maintain marks | No | Gas Line | Yes | Shovel | Gas | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | X209003073 | Dig-In to PG&E Underground | 2nd Party-Contractor | Lyles Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2022-06-29 | ½” | 28 | 36 | N/A | 6 | Jun | 2022 |  | 981146 | Yes
19115 | x | x | x |  | 2022-06-29 | Jun | 6 | 2022 | 79654 |  |  | 123956221 | Contra Costa | Bay Area | Diablo | South | Orinda | Yes | TAK Communications CA, Inc. damaged a 1/2" plastic gas service line with a shovel while installing telecommunication lines. No USA ticket. | No | Gas Line | Yes | Shovel | Telecommunications | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | TAK Communications CA, Inc. | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-29 | ½” | 24 | 56 | Excavator Did Not Believe a USA Ticket was Required | 6 | Jun | 2022 |  |  | Yes
19114 | x | x | x |  | 2022-06-29 | Jun | 6 | 2022 | 79641 |  |  | 123954525 | Yolo | Northern | Vacaville | North | Davis | Yes | Backyard Homes damaged a 1/2" plastic gas service line with a shovel while installing new electric conduit. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | W216100300 | Dig-In to PG&E Underground | 3rd Party-Contractor | Backyard Homes | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-29 | ½” | 26 | 22 | N/A | 6 | Jun | 2022 |  |  | Yes
19113 | x | x | x |  | 2022-06-29 | Jun | 6 | 2022 | 79667 |  |  | 123958640 | Santa Cruz | Central Coast | Central Coast | South | Watsonville | Yes | KJ Woods Construction damaged a 1/2" plastic gas service line with an excavator while installing a sewer main. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X216300159 | Dig-In to PG&E Underground | 3rd Party-Contractor | KJ Woods Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-29 | ½” | 46 | 50 | N/A | 6 | Jun | 2022 |  |  | No
19112 | x | x | x |  | 2022-06-29 | Jun | 6 | 2022 | 79621 |  |  | 123952877 | Marin | Bay Area | North Bay | North | Mill Valley | Yes | Unlicensed contractor damaged a 1/2" plastic gas service line while preparing to install a curb. The damage was to a tracer wire that the contractor grabbed with his hand and pulled out of the ground. While pulling it out it sliced the gas line. No USA ticket. | No | Gas Line | Yes | Other | Curb/Sidewalk Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-29 | ½” | 12 | 39 | Knew About USA Ticket Requirement But Chose Not to Call | 6 | Jun | 2022 |  |  | No
19111 | x | x | x |  | 2022-06-29 | Jun | 6 | 2022 | 79665 |  |  | 123957841 | San Joaquin | Central Valley | Stockton | South | Tracy | Yes | Knife River Construction damaged a 4" plastic gas main with a front loader while installing a sewer lateral. Valid USA ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Front Loader | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | X135500598 | Dig-In to PG&E Underground | 3rd Party-Contractor | Knife River Construction | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-29 | 4" | 28 | 173 | N/A | 6 | Jun | 2022 |  |  | No
19110 | x |  |  |  | 2022-06-29 | Jun | 6 | 2022 | 79640 |  |  |  | Santa Clara | Central Coast | San Jose | Central | Morgan Hill | Yes | Garney Construction damaged a 1/2" plastic gas service line with shovel while installing a new water line. Valid USA ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Water | Failed to Dig with Care | Yes | W215400153 | Dig-In to PG&E Underground | 3rd Party-Contractor | Garney Construction | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-29 | ½” | 42 | 56 | N/A | 6 | Jun | 2022 |  |  | Yes
19124 | x |  |  |  | 2022-06-30 | Jun | 6 | 2022 | 79688 |  |  |  | Sacramento | Northern | Sacramento | North | Citrus Heights | Yes | Rooter Hero Plumbing damaged the wrap on a gas main with unknown tool while doing sewer repairs. No USA ticket. | Yes | Gas Line | No | Unknown | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Rooter Hero Plumbing | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-30 |  |  | 0 | Other | 6 | Jun | 2022 |  |  | No
19123 | x | x | x |  | 2022-06-30 | Jun | 6 | 2022 | 79682 |  |  | 123964666 | Sacramento | Northern | Sacramento | North | Fair Oaks | Yes | HG Tree Service damaged a 3/4" steel gas service line with a stump grinder while removing a tree stump. No USA ticket. | No | Gas Line | Yes | Stump Grinder | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | HG Tree Service | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-30 | ¾” | 10 | 67 | Believed They Knew Where Underground Utility was From Previous Knowledge | 6 | Jun | 2022 |  |  | No
19122 | x | x | x |  | 2022-06-30 | Jun | 6 | 2022 | 79683 |  |  | 123961781 | Sacramento | Northern | Sacramento | North | Folsom | Yes | Pacific Parks Landscaping damaged a 1" plastic gas service line with a mini-excavator while installing a drainage pipe. No USA ticket. | No | Gas Line | Yes | Excavator | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Pacific Parks Landscaping | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-30 | 1” | 19 | 55 | Knew About 811 Process, But Asserted They Didn’t Want to Wait the Required Time for Markings | 6 | Jun | 2022 |  |  | No
19121 | x | x | x |  | 2022-06-30 | Jun | 6 | 2022 | 79712 |  |  | 123967147 | Contra Costa | Bay Area | East Bay | Central | El Cerrito | Yes | Impact Demo & Paver Installation damaged a 1/2" plastic gas service line inserted into 3/4" steel with a mini-excavator while excavating for a new basement. No USA ticket. | No | Gas Line | Yes | Excavator | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Impact Demo & Paver Installation | Distribution Service |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-30 | ½” | 12 | 70 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 6 | Jun | 2022 |  |  | No
19120 | x |  |  |  | 2022-06-30 | Jun | 6 | 2022 | 79687 |  |  |  | Santa Clara | Central Coast | San Jose | Central | Milpitas | Yes | R&R Pacific Construction damaged the wrap on a 2" plastic gas main with a shovel while exposing the gas line. Valid USA ticket. Failed to dig with care | Yes | Gas Line | No | Shovel | Sewer | Failed to Dig with Care | Yes | W207000243 | Dig-In to PG&E Underground | 3rd Party-Contractor | R&R Pacific Construction | Distribution Main |  | No | N/A |  |  | 2022 Q2 |  |  |  | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2022-06-30 | 2” |  | 0 | N/A | 6 | Jun | 2022 |  |  | Yes