## All Years
Utility Name | Circuit | FIPA Form Name | Date | Year | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | FLOC | HFRA | cGIS HFRA | HFTD | Other Companies | Voltage (Volts) | Business Line | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Circuit_Net9 | Notes (Optional): | Region | District Name | District Number | HFRA Tier | Circuit | GIS_Circuit_Notes | Revised TIER | HFTD | CPUC Reportable | Year | Revised Suspected Initiating Event | Revised Equipment /Facility Failure | Month | Jan to Aug
SCE | Harlem Springs | FIPA_2020_0101_2050 | 2020-01-01 | 2020 | 20:50 | 34.1156 | -117.2587 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-4389384E | OH-4389384E | No | Non-HFRA | N | None | 12 | Distribution | Other | Overhead | Yes | 2020-01-01 | 20:50 | Equipment/Facility Failure | Insulator |  |  | Other
SCE | Caliber | FIPA_2020_0103_0711 | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-549798E | OH-549798E | T3 | Tier 3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | Flycatcher | FIPA_2020_0113_0801 | 2020-01-13 | 2020 | 8:01 | 35.6385 | -118.4046 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1316770E | OH-1316770E | T3 | Tier 3 | Y | Frontier Communications | 12 | Distribution | Other | Overhead | Yes | 2020-01-13 | 8:01 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Hub City | FIPA_2020_0131_1357 | 2020-01-31 | 2020 | 13:57 | 33.8947 | -118.2463 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1813245E | OH-1813245E | No | Non-HFRA | N | AT&T Communication | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
SCE | Fields | FIPA_2020_0204_0543 | 2020-02-04 | 2020 | 5:43 | 34.0914 | -117.5222 | Other | Urban | Less Than .25 Acres | Fire Agency | Rancho Cucamonga Fire Department | OH-4894668E | OH-4894668E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-02-04 | 5:43 | Equipment/Facility Failure | Other |  |  | Other
SCE | WALNUT-CORTEZ-MERCED NO. 2 | FIPA_2020_0213_1308 | 2020-02-13 | 2020 | 13:08 | 34.0915 | -117.8815 | Other | Urban | Less Than .25 Acres | Utility |  | OH-1180455E | OH-1180455E | No | Non-HFRA | N | None | 66 | Transmission | Other | Overhead | Yes | 2020-02-13 | 13:08 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Rover | FIPA_2020_0222_0940 | 2020-02-22 | 2020 | 9:40 | 33.9501 | -116.5302 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-GT14877 | OH-GT14877 | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 2020-02-22 | 9:40 | Equipment/Facility Failure | Insulator |  |  | Weather
SCE | Susquehanna | FIPA_2020_0226_2309 | 2020-02-26 | 2020 | 23:09 | 36.3433 | -119.3041 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1245599E | OH-1245599E | No | Non-HFRA | N | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | Caswell | FIPA_2020_0302_0807 | 2020-03-02 | 2020 | 8:07 | 33.8928 | -118.2751 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-2274731E | OH-2274731E | No | Non-HFRA | N | None | 16 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | Coronado | FIPA_2020_0302_1432 | 2020-03-02 | 2020 | 14:32 | 34.0348 | -118.1187 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1951747E | OH-1951747E | No | Non-HFRA | N | AT&T Communication | 16 | Distribution | Conductor | Overhead | Yes | 2020-03-02 | 14:32 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Grazide | FIPA_2020_0303_2053 | 2020-03-03 | 2020 | 20:53 | 34.0005 | -117.9626 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-E18873Y | OH-E18873Y | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Lightning Arrestor | Overhead | No |  |  | Other |  |  |  | Other
SCE | Burr | FIPA_2020_0306_1123 | 2020-03-06 | 2020 | 11:23 | 36.2286 | -119.0648 | Other | Urban | Less Than .25 Acres | Fire Agency | Montebello Fire Department | OH-4512718E | OH-4512718E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-03-06 | 11:23 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | Medusa | FIPA_2020_0306_1705 | 2020-03-06 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-1811355E | OH-1811355E | T2 | Tier 2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Weather
SCE | Macomber | FIPA_2020_0311_0831 | 2020-03-11 | 2020 | 8:31 | 35.9854 | -119.4069 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-2191789E | OH-2191789E | No | Non-HFRA | N | None | 12 | Distribution | Transformer | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Weather
SCE | Rabbit | FIPA_2020_0317_1555 | 2020-03-17 | 2020 | 15:55 | 34.6673 | -116.9388 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-4288653E | OH-4288653E | No | Non-HFRA | N | None | 12 | Distribution | Other | Overhead | Yes | 2020-03-17 | 15:55 | Contact From Object |  | Animal | Electric Facility | Other
SCE | January | FIPA_2020_0319_1200 | 2020-03-19 | 2020 | 12:00 | 33.6074 | -117.9201 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-835718E | OH-835718E | No | Non-HFRA | N | AT&T Communication | 12 | Distribution | Switch | Overhead | No |  |  | Equipment/Facility Failure | Switch |  |  | Other
SCE | Sand Canyon | FIPA_2020_0422_1520 | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-1090802E | OH-1090802E | T3 | Tier 3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | Invention | FIPA_2020_0426_1250 | 2020-04-26 | 2020 | 12:50 | 34.6606 | -118.2366 | Other | Rural | Less Than .25 Acres | Fire Agency | Antelope Valley Fire Department | OH-1309936E | OH-1309936E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-04-26 | 12:50 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Chalfant | FIPA_2020_0427_1519 | 2020-04-27 | 2020 | 15:19 | 37.5304 | -118.3669 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-45770S | OH-45770S | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Lightning Arrestor | Overhead | Yes | 2020-04-27 | 15:18 | Equipment/Facility Failure | Other |  |  | Other
SCE | Townhall | FIPA_2020_0430_0952 | 2020-04-30 | 2020 | 9:52 | 33.9231 | -116.6498 | Other | Urban | Less Than .25 Acres | Fire Agency | Palm Springs Fire Department | OH-2329507E | OH-2329507E | No | Non-HFRA | N | None | 33 | Distribution | Other | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Other
SCE | Quinby | FIPA_2020_0501_2125 | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4339082E | OH-4339082E | T2 | Tier 2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | Waterman | FIPA_2020_0509_0323 | 2020-05-09 | 2020 | 3:23 | 34.1117 | -117.2804 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1629706E | OH-1629706E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-09 | 3:23 | Other |  |  |  | Unknown |  | Wire Down - WtW not suspected
SCE | Oban | FIPA_2020_0510_1513 | 2020-05-10 | 2020 | 15:13 | 34.7049 | -118.1437 | Other | Rural | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-736330E | OH-736330E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-10 | 15:13 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Shade | FIPA_2020_0511_0814 | 2020-05-11 | 2020 | 8:14 | 33.9792 | -118.0533 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-2061964E | OH-2061964E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-11 | 7:32 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Acrobat | FIPA_2020_0517_1735 | 2020-05-17 | 2020 | 17:35 | 34.5757 | -118.1094 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-928508E | OH-928508E | No | Non-HFRA | N | AT&T Communication | 12 | Distribution | Fuse | Overhead | Yes | 2020-05-17 | 17:35 | Equipment/Facility Failure | Fuse |  | Electric Facility | Other
SCE | VALLEY-MAYBERRY-MORENO-VISTA | FIPA_2020_0518_1210 | 2020-05-18 | 2020 | 12:10 | 33.8587 | -117.0197 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | Tier 3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | Homer | FIPA_2020_0521_1520 | 2020-05-21 | 2020 | 15:20 | 36.4138 | -119.0733 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Woodlake Fire Department | OH-475645E | OH-475645E | No | Non-HFRA | N | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-21 | 15:20 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | Sheffield | FIPA_2020_0523_1637 | 2020-05-23 | 2020 | 16:37 | 34.4139 | -119.5262 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4404319E | OH-4404319E | No | Non-HFRA | N | Frontier Communications | 16 | Distribution | Other | Overhead | Yes | 2020-05-23 | 13:11 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Balsam | FIPA_2020_0526_1959 | 2020-05-26 | 2020 | 19:59 | 34.4206 | -117.3107 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-2155313E | OH-2155313E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Transformer | Overhead | Yes | 2020-05-26 | 28:59 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | Kickapoo Trail | FIPA_2020_0526_2239 | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | Tier 3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | SAUGUS-MOORPARK-SANTA SUSANA-TORREY | FIPA_2020_0528_0614 | 2020-05-28 | 2020 | 6:14 | 34.3947 | -118.6824 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | M6-T5 | OH-7019932 | T3 | Tier 3 | Y | None | 66 | Transmission | Other | Overhead | Yes | 2020-05-28 | 6:14 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Zapata | FIPA_2020_0529_1423 | 2020-05-29 | 2020 | 14:23 | 34.1101 | -117.2672 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4003908E | OH-4003908E | No | Non-HFRA | N | None | 12 | Distribution | Other | Overhead | Yes | 2020-05-29 | 14:23 | Other |  |  |  | Unknown
SCE | Agnes | FIPA_2020_0601_1714 | 2020-06-01 | 2020 | 17:14 | 33.8913 | -118.2139 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4371854E | OH-4371854E | No | Non-HFRA | N | AT&T CALIFORNIA | 4.16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Tambourine | FIPA_2020_0602_0754 | 2020-06-02 | 2020 | 7:54 | 34.4923 | -118.6207 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4393756E | OH-4393756E | T3 | Tier 3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | Yes | 2020-06-02 | 7:54 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | TITTLE | FIPA_2020_0602_1109 | 2020-06-02 | 2020 | 11:09 | 33.7349 | -117.9285 | Other | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Department | OH-2145959E | OH-2145959E | No | Non-HFRA | N | AT&T Communication | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | La Mancha | FIPA_2020_0603_1223 | 2020-06-03 | 2020 | 12:23 | 34.1333 | -118.8523 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-1848408E | OH-1848408E | T3 | Tier 3 | Y | None | 16 | Distribution | Other | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | Heavy | FIPA_2020_0603_1957 | 2020-06-03 | 2020 | 19:57 | 35.3849 | -117.7247 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4390703E | OH-4390703E | No | Non-HFRA | N | None | 33 | Distribution | Conductor | Overhead | Yes | 2020-06-03 | 19:57 | Equipment/Facility Failure | Insulator |  |  | Other
SCE | Bonanza | FIPA_2020_0605_1733 | 2020-06-05 | 2020 | 17:33 | 35.7635 | -118.4218 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Kern County Fire Department | OH-4451126E | OH-4451126E | T3 | Tier 3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 2020-06-05 | 17:33 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Yoda | FIPA_2020_0605_1543 | 2020-06-05 | 2020 | 15:43 | 34.6602 | -118.2251 | Other | Urban | 10 - 99 Acres | Unknown |  | OH-K4922Y | OH-K4922Y | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Trumpet | FIPA_2020_0607_0550 | 2020-06-07 | 2020 | 5:50 | 34.4885 | -118.6168 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1871383E | OH-1871383E | T3 | Tier 3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Other
SCE | Calgrove | FIPA_2020_0607_1509 | 2020-06-07 | 2020 | 15:09 | 34.4885 | -118.6168 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4393062E | OH-4393062E | T3 | Tier 3 | Y | AT&T Communication | 16 | Distribution | Conductor | Overhead | Yes | 2020-06-07 | 15:09 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | SAUGUS-MOORPARK-SANTA SUSANA-TORREY | FIPA_2020_0607_2145 | 2020-06-07 | 2020 | 21:45 | 34.3067 | -118.7197 | Vegetation | Urban | .26 - 9.99 Acres | Utility |  | M13-T1 | OH-7018027 | T3 | Tier 3 | Y | None | 66 | Transmission | Other | Overhead | Yes | 2020-07-06 | 21:45 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Lotto | FIPA_2020_0608_1224 | 2020-06-08 | 2020 | 12:24 | 34.494 | -117.5498 | Other | Rural | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-4106577E | OH-4106577E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-08 | 12:24 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Oakwood | FIPA_2020_0609_0925 | 2020-06-09 | 2020 | 9:25 | 34.1594 | -118.0288 | Other | Urban | Less Than .25 Acres | Fire Agency | Arcadia Fire Department | OH-922692E | OH-922692E | T2 | Tier 2 | Y | AT&T Communication | 4.16 | Distribution | Other | Overhead | Yes | 2020-06-09 | 9:25 | Equipment/Facility Failure | Other |  |  | Other
SCE | Bidder | FIPA_2020_0609_2142 | 2020-06-09 | 2020 | 21:42 | 34.4674 | -119.9055 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Santa Barbara Fire Department | OH-219558E | OH-219558E | T3 | Tier 3 | Y | Frontier Communications | 16 | Distribution | Transformer | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
SCE | Borba | FIPA_2020_0609_1240 | 2020-06-09 | 2020 | 12:40 | 33.9975 | -117.6491 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Ontario Fire Department | OH-1463533E | OH-1463533E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Fuse | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Weaver | FIPA_2020_0609_1450 | 2020-06-09 | 2020 | 14:50 | 34.0515 | -118.0263 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-882039E | OH-882039E | No | Non-HFRA | N | AT&T California | 4.16 | Distribution | Conductor | Overhead | Yes | 2020-06-09 | 15:31 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | Estaban | FIPA_2020_0609_1947 | 2020-06-09 | 2020 | 19:47 | 34.2284 | -119.0724 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-2116776E | OH-2116776E | No | Non-HFRA | N | Frontier Communications | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
SCE | Viento | FIPA_2020_0609_1642 | 2020-06-09 | 2020 | 16:42 | 35.1384 | -118.4809 | Other | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4707894E | OH-4707894E | T3 | Tier 3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
SCE | Elmer | FIPA_2020_0610_1700 | 2020-06-10 | 2020 | 17:00 | 34.1444 | -118.0671 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-656697E | OH-656697E | No | Non-HFRA | N | AT&T Communication | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Pole |  |  | Other
SCE | Windt | FIPA_2020_0610_1533 | 2020-06-10 | 2020 | 15:33 | 36.2374 | -119.4928 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-703067E | OH-703067E | No | Non-HFRA | N | AT&T California | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-10 | 15:33 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Shoreline | FIPA_2020_0611_0815 | 2020-06-11 | 2020 | 8:15 | 33.7476 | -118.3804 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1803572E | OH-1803572E | T2 | Tier 2 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-06-11 | 8:15 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Shoreline | FIPA_2020_0611_0815 | 2020-06-11 | 2020 | 8:15 | 33.7476 | -118.3807 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-975271E | OH-975271E | T2 | Tier 2 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-06-11 | 8:15 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | MAGUNDEN-VESTAL NO. 1 | FIPA_2020_0611_1437 | 2020-06-11 | 2020 | 14:37 | 35.7516 | -119.0617 | Other | Rural | Less Than .25 Acres | Unknown |  | M111-T5 | OH-7022567 | No | Non-HFRA | N | None | 220 | Transmission | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Wells | FIPA_2020_0611_1500 | 2020-06-11 | 2020 | 15:00 | 36.3542 | -119.1345 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4594904E | OH-4594904E | No | Non-HFRA | N | None | 12 | Distribution | Switch | Overhead | No |  |  | Equipment/Facility Failure | Switch |  |  | Other
SCE | Standing Rock | FIPA_2020_0611_1552 | 2020-06-11 | 2020 | 15:52 | 34.5547 | -117.1611 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Apple Valley Fire Department | OH-4881038E | OH-4881038E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
SCE | Wing | FIPA_2020_0612_1217 | 2020-06-12 | 2020 | 12:17 | 34.4595 | -117.2738 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Hesperia Fire Department | OH-2156864E | OH-2156864E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Dalmatian | FIPA_2020_0612_1453 | 2020-06-12 | 2020 | 14:53 | 34.0567 | -117.6349 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-4665052E | OH-4665052E | No | Non-HFRA | N | None | 12 | Distribution | Transformer | Overhead | Yes | 2020-06-12 | 13:44 | Unknown |  |  |  | Unknown
SCE | Conestoga | FIPA_2020_0613_1726 | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | Tier 3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Porphyry | FIPA_2020_0613_2006 | 2020-06-13 | 2020 | 20:06 | 33.8473 | -117.5145 | Vegetation | Urban | .26 - 9.99 Acres | Unknown |  | OH-73328S | OH-73328S | T3 | Tier 3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 20:06 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Allegra | FIPA_2020_0613_0950 | 2020-06-13 | 2020 | 9:50 | 34.1462 | -116.2701 | Other | Rural | Less Than .25 Acres | Customer |  | OH-1686040E | OH-1686040E | No | Non-HFRA | N | None | 12 | Distribution | Other | Overhead | Yes | 2020-06-13 | 9:50 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Hughes Lake | FIPA_2020_0614_1625 | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4665728E | OH-4665728E | T2 | Tier 2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Outside Force
SCE | Whipstock | FIPA_2020_0615_1018 | 2020-06-15 | 2020 | 10:18 | 33.9476 | -117.9233 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-X11989E | OH-X11989E | T3 | Tier 3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-15 | 10:18 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Rough | FIPA_2020_0616_1241 | 2020-06-16 | 2020 | 12:41 | 33.8747 | -117.9594 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1222483E | OH-1222483E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-16 | 14:41 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Stack | FIPA_2020_0619_1909 | 2020-06-19 | 2020 | 19:09 | 33.8069 | -116.5468 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-235364S | OH-235364S | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-19 | 19:09 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Larch | FIPA_2020_0620_1454 | 2020-06-20 | 2020 | 14:54 | 34.033 | -117.3992 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Rialto Fire Department | OH-4869738E | OH-4869738E | T2 | Tier 2 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2020-06-20 | 14:54 | Contact From Object |  | Other | Electric Facility | Unknown
SCE | Cabernet | FIPA_2020_0621_1123 | 2020-06-21 | 2020 | 11:23 | 34.1169 | -117.3787 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-261195S | OH-261195S | No | Non-HFRA | N | AT&T CALIFORNIA | 12 | Distribution | Other | Overhead | Yes | 2020-06-21 | 11:23 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Deloro | FIPA_2020_0622_1303 | 2020-06-22 | 2020 | 13:03 | 34.4787 | -117.2143 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-2154977E | OH-2154977E | No | Non-HFRA | N | None | 12 | Distribution | Lightning Arrestor | Overhead | Yes | 2020-06-22 | 13:03 | Equipment/Facility Failure | Lightning Arrestor |  |  | Other
SCE | Lakota | FIPA_2020_0622_0812 | 2020-06-22 | 2020 | 8:12 | 34.5384 | -117.2251 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-2155419E | OH-2155419E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Transformer | Overhead | Yes | 2020-06-22 | 8:12 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | ARROWHEAD-CALECTRIC-DEVIL CANYON-SHANDIN | FIPA_2020_0624_1653 | 2020-06-24 | 2020 | 16:53 | 34.147 | -117.3573 | Vegetation | Urban | .26 - 9.99 Acres | Unknown |  | OH-4138868E | OH-4138868E | T2 | Tier 2 | Y | None | 115 | Transmission | Other | Overhead | Yes | 2020-06-24 | 16:53 | Other |  |  |  | Unknown |  | 3rd Party - Homeless encampment
SCE | Greenwell | FIPA_2020_0624_1539 | 2020-06-24 | 2020 | 15:39 | 34.4205 | -119.6038 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Summerland Fire Department | OH-1868554E | OH-1868554E | No | Non-HFRA | N | None | 33 | Distribution | Fuse | Overhead | Yes | 2020-06-24 | 12:40 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | Jamaica | FIPA_2020_0625_1738 | 2020-06-25 | 2020 | 17:38 | 33.8708 | -118.0084 | Other | Rural | Less Than .25 Acres | Fire Agency | Orange County Fire Department | UG-5194363 | UG-5194363 | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Underground | No |  |  | Other |  |  |  | None
SCE | Grubstake | FIPA_2020_0627_0848 | 2020-06-27 | 2020 | 8:48 | 34.7745 | -118.1491 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4769654E | OH-4769654E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Other | Overhead | Yes | 2020-06-27 | 8:58 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | EAGLE ROCK-ALHAMBRA NO. 1 | FIPA_2020_0630_1830 | 2020-06-30 | 2020 | 18:30 | 34.1316 | -118.1832 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Monrovia Fire Department | OH-4209659E | OH-4209659E | No | Non-HFRA | N | City of Pasadena | 66 | Transmission | Other | Overhead | Yes | 2020-06-30 | 18:30 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Drag | FIPA_2020_0703_1655 | 2020-07-03 | 2020 | 16:55 | 36.0637 | -119.0127 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Porterville FD | OH-1517323E | OH-1517323E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | La Mancha | FIPA_2020_0705_0357 | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  | OH-1848406E | OH-1848406E | T3 | Tier 3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Other
SCE | Capanero | FIPA_2020_0705_1200 | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | Tier 2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Seals | FIPA_2020_0705_1937 | 2020-07-05 | 2020 | 19:37 | 34.5579 | -117.2892 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1601308E | OH-1601308E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 2020-07-05 | 20:44 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Poco | FIPA_2020_0706_0129 | 2020-07-06 | 2020 | 1:29 | 34.8022 | -117.2089 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Barstow Fire Department | OH-1906079E | OH-1906079E | No | Non-HFRA | N | Frontier Communications | 33 | Distribution | Conductor | Overhead | Yes | 2020-07-06 | 1:29 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | Muddy | FIPA_2020_0711_1710 | 2020-07-11 | 2020 | 17:10 | 33.669 | -117.326 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-11131S | OH-11131S | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 2020-07-11 | 17:20 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Nicholas | FIPA_2020_0713_1743 | 2020-07-13 | 2020 | 17:43 | 34.0461 | -118.6533 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-4251442E | OH-4251442E | T3 | Tier 3 | Y | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-07-13 | 17:43 | Equipment/Facility Failure | Conductor |  |  | Human Error
SCE | Helios | FIPA_2020_0714_1539 | 2020-07-14 | 2020 | 15:39 | 34.8652 | -116.6911 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-2236870E | OH-2236870E | No | Non-HFRA | N | None | 12 | Distribution | Other | Overhead | Yes | 2020-07-14 | 15:39 | Equipment/Facility Failure | Transformer |  |  | Outside Force
SCE | Medallion | FIPA_2020_0715_1155 | 2020-07-15 | 2020 | 11:55 | 34.7034 | -118.1598 | Vegetation | Urban | Less Than .25 Acres | Customer |  | OH-1048136E | OH-1048136E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | None
SCE | Knott | FIPA_2020_0719_0944 | 2020-07-19 | 2020 | 9:44 | 33.8504 | -117.9908 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Department | OH-1171929E | OH-1171929E | No | Non-HFRA | N | None | 12 | Distribution | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | COOL WATER-TIEFORT | FIPA_2020_0723_0756 | 2020-07-23 | 2020 | 7:56 | 35.1594 | -116.7588 | Vegetation | Rural | Less Than .25 Acres | Utility |  | OH-A257230E | OH-A257230E | No | Non-HFRA | N | None | 115 | Transmission | Other | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Flycatcher | FIPA_2020_0725_1312 | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | Tier 3 | Y | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Hose | FIPA_2020_0726_1742 | 2020-07-26 | 2020 | 17:42 | 34.0602 | -117.6389 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished |  | OH-2268985E | OH-2268985E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 2020-07-26 | 14:42 | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | Tortuga | FIPA_2020_0726_1709 | 2020-07-26 | 2020 | 17:09 | 33.8198 | -116.491 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-35838S | OH-35838S | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error
SCE | Lasker | FIPA_2020_0726_1250 | 2020-07-26 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4619162E | OH-4619162E | T3 | Tier 3 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
SCE | Russ Boyd | FIPA_2020_0731_1032 | 2020-07-31 | 2020 | 10:32 | 34.5091 | -117.469 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4771427E | OH-4771427E | No | Non-HFRA | N | None | 33 | Distribution | Transformer | Overhead | Yes | 2020-07-31 | 10:32 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Erringer | FIPA_2020_0801_1920 | 2020-08-01 | 2020 | 19:20 | 34.2612 | -118.7754 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1415211E | OH-1415211E | T3 | Tier 3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Thunderbolt | FIPA_2020_0802_1646 | 2020-08-02 | 2020 | 16:46 | 34.6486 | -118.1234 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-955925E | OH-955925E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Weather
SCE | Morongo | FIPA_2020_0803_1033 | 2020-08-03 | 2020 | 10:33 | 34.0758 | -116.5548 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-2107480E | OH-2107480E | T2 | Tier 2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-03 | 19:15 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Airport | FIPA_2020_0804_1834 | 2020-08-04 | 2020 | 18:34 | 34.7007 | -118.133591D | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-622156E | OH-622156E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-04 | 18:30 | Wire-Wire Contact |  |  |  | Weather
SCE | Mercedes | FIPA_2020_0805_2006 | 2020-08-05 | 2020 | 20:06 | 33.7788 | -117.9301 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-970202E | OH-970202E | No | Non-HFRA | N | AT&T CALIFORNIA | 12 | Distribution | Other | Overhead | Yes | 2020-08-05 | 20:06 | Equipment/Facility Failure | Other |  |  | Other
SCE | Morello | FIPA_2020_0809_0853 | 2020-08-09 | 2020 | 8:53 | 33.9348 | 16.994 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-705838E | OH-705838E | T2 | Tier 2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-09 | 8:53 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Mettler | FIPA_2020_0810_1435 | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Utility |  | OH-2093506E | OH-2093506E | T3 | Tier 3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Human Error
SCE | Bing | FIPA_2020_0812_1440 | 2020-08-12 | 2020 | 14:40 | 33.9486 | -116.9696 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Beaumont Fire Department | OH-1996482E | OH-1996482E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | Lyons | FIPA_2020_0813_2148 | 2020-08-13 | 2020 | 21:48 | 34.3687 | -118.5157 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-4103978E | OH-4103978E | T3 | Tier 3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2020-08-13 | 21:48 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Hampshire | FIPA_2020_0815_1902 | 2020-08-15 | 2020 | 19:02 | 34.2159 | -118.8604 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-1296864E | OH-1296864E | T3 | Tier 3 | Y | Frontier Communications | 16 | Distribution | Conductor | Overhead | Yes | 2020-08-15 | 19:01 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Hart | FIPA_2020_0816_1613 | 2020-08-16 | 2020 | 16:13 | 36.3048 | -119.2099 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Farmsville Fire Department | OH-4505923E | OH-4505923E | No | Non-HFRA | N | None | 12 | Distribution | Transformer | Overhead | Yes | 2020-08-16 | 16:13 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | Ravine | FIPA_2020_0818_1600 | 2020-08-18 | 2020 | 16:00 | 34.2148 | -118.197 | Other | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-732723E | OH-732723E | T2 | Tier 2 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Nicholas | FIPA_2020_0818_1647 | 2020-08-18 | 2020 | 16:47 | 34.051 | -118.6476 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-GT111426 | OH-GT111426 | T3 | Tier 3 | Y | Frontier Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Beeline | FIPA_2020_0818_1514 | 2020-08-18 | 2020 | 15:14 | 34.5409 | -117.3653 | Vegetation | Rural | Less Than .25 Acres | Utility |  | OH-4613951E | OH-4613951E | No | Non-HFRA | N | None | 12 | Distribution | Other | Overhead | Yes | 8/18/ | 15:14 | Equipment/Facility Failure | Insulator |  |  | Other
SCE | Olancha | FIPA_2020_0819_1118 | 2020-08-19 | 2020 | 11:18 | 34.5126 | -117.3671 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-263181S | OH-263181S | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-19 | 11:18 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Mandarin | FIPA_2020_0819_0821 | 2020-08-19 | 2020 | 8:21 | 34.1421 | -117.8874 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1034427E | OH-1034427E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-19 | 8:40 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Showdown | FIPA_2020_0823_1739 | 2020-08-23 | 2020 | 17:39 | 34.59 | -118.2032 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4777412E | OH-4777412E | T3 | Tier 3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 2020-08-23 | 17:39 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Lotto | FIPA_2020_0825_1241 | 2020-08-25 | 2020 | 12:41 | 34.4508 | -117.5924 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-4006134E | OH-4006134E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error
SCE | Shiraz | FIPA_2020_0829_1129 | 2020-08-29 | 2020 | 11:29 | 34.1196 | -117.3203 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-704775E | OH-704775E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  | 11:29 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Cafe | FIPA_2020_0831_1712 | 2020-08-31 | 2020 | 17:12 | 33.9387 | -116.4764 | Other | RURAL | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-1556297E | OH-1556297E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
SCE | Oban | FIPA_2020_0904_1801 | 2020-09-04 | 2020 | 18:01 | 34.7039 | -118.1303 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-970804E | OH-970804E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No | 2020-09-04 | 18:01 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Rotec | FIPA_2020_0905_1429 | 2020-09-05 | 2020 | 14:29 | 33.7502 | -117.0329 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Hemet Fire Department | OH-4214288E | OH-4214288E | No | Non-HFRA | N | None | 12 | Distribution | Switch | Overhead | No |  |  | Equipment/Facility Failure | Switch |  |  | Other
SCE | Baldwin | FIPA_2020_0906_1505 | 2020-09-06 | 2020 | 15:05 | 34.1711 | -118.0551 | Other | Urban | Less Than .25 Acres | Fire Agency | Sierra Madre Fire Department | OH-X7926E | OH-X7926E | T2 | Tier 2 | Y | Frontier Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Triumph | FIPA_2020_0906_0233 | 2020-09-06 | 2020 | 2:33 | 34.0892 | -118.1377 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1605216E | OH-1605216E | No | Non-HFRA | N | AT&T CALIFORNIA and TIME WARNER NORTH | 16 | Distribution | Transformer | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Other
SCE | Barbossa | FIPA_2020_0917_0833 | 2020-09-17 | 2020 | 8:33 | 34.0735 | -117.8772 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | West Covina Fire Department | OH-4828324E | OH-4828324E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 2020-09-17 | 8:33 | Contact From Object |  | Other | Electric Facility | Unknown
SCE | Musket | FIPA_2020_0920_0131 | 2020-09-20 | 2020 | 1:31 | 33.9134 | -118.0864 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-2006014E | OH-2096013E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | Flying D | FIPA_2020_0924_1035 | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-1761180E | OH-1761180E | T3 | Tier 3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | Drum | FIPA_2020_0929_1639 | 2020-09-29 | 2020 | 16:39 | 33.9175 | -117.9819 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1509725E | OH-1509725E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Other | Overhead | Yes | 2020-09-29 | 16:39 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | Calgrove | FIPA_2020_1003_1745 | 2020-10-03 | 2020 | 17:45 | 34.3515 | -118.5616 | Vegetation | Rural | Less Than .25 Acres | Customer |  | OH-2101062E | OH-2101062E | T3 | Tier 3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Power | FIPA_2020_1004_1545 | 2020-10-04 | 2020 | 15:45 | 34.1616 | -117.3411 | Vegetation | Urban | Less Than .25 Acres | Customer |  | OH-200686S | OH-200686S | No | Non-HFRA | N | Frontier Communications | 4.16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Cement | FIPA_2020_1015_1832 | 2020-10-15 | 2020 | 18:32 | 34.5792 | -117.359 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Victorville Fire Department | OH-4531653E | OH-4531653E | No | Non-HFRA | N | None | 33 | Distribution | Other | Overhead | Yes | 2020-10-15 | 18:31 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Parcells | FIPA_2020_1015_0112 | 2020-10-15 | 2020 | 1:12 | 34.0618 | -117.7556 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Pomona LACFD | OH-4098618E | OH-4098618E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Other
SCE | Amazon | FIPA_2020_1016_2233 | 2020-10-16 | 2020 | 22:33 | 34.1053 | -117.9485 | Building | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4617757E | OH-4617757E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Transformer | Overhead | Yes | 2020-10-16 | 22:42 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | Deer | FIPA_2020_1019_2358 | 2020-10-19 | 2020 | 23:58 | 35.9769 | -118.9992 | Vegetation | Rural | Less Than .25 Acres | Customer |  | OH-1895627E | OH-1895627E | No | Non-HFRA | N | AT&T California | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | Tlsmith | FIPA_2020_1022_0412 | 2020-10-22 | 2020 | 4:12 | 36.2722 | -119.3164 | Other | Urban | Less Than .25 Acres | Fire Agency | City of Visalia Fire Department | OH-1467831E | OH-1467831E | No | Non-HFRA | N | AT&T California | 12 | Distribution | Transformer | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Human Error
SCE | Catawba | FIPA_2020_1026_1435 | 2020-10-26 | 2020 | 14:35 | 34.107 | -117.4845 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-670473E | OH-670473E | No | Non-HFRA | N | AT&T California | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Weather
SCE | Vicasa | FIPA_2020_1026_1156 | 2020-10-26 | 2020 | 11:56 | 34.0998 | -118.5925 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-795990E | OH-795990E | T3 | Tier 3 | Y | Frontier Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Weather
SCE | Border | FIPA_2020_1026_0332 | 2020-10-26 | 2020 | 3:32 | 33.8763 | -117.5805 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Corona City Fire Department | OH-1790807E | OH-1790807E | No | Non-HFRA | N | AT&T California | 12 | Distribution | Other | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Thelma | FIPA_2020_1029_2322 | 2020-10-29 | 2020 | 23:22 | 33.7843 | -117.8436 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Department | OH-1374367E | OH-1374367E | No | Non-HFRA | N | AT&T California | 12 | Distribution | Other | Overhead | Yes | 2020-10-29 | 23:22 | Equipment/Facility Failure | Other |  |  | Other
SCE | Nashville | FIPA_2020_1031_1534 | 2020-10-31 | 2020 | 15:34 | 34.0255 | -117.0791 | Vegetation | Urban | .26 - 9.99 Acres | Unknown |  | OH-4671710E | OH-4671710E | T2 | Tier 2 | Y | None | 12 | Distribution | Transformer | Overhead | Yes | 2020-10-31 | 15:09 | Equipment/Facility Failure | Transformer |  |  | Human Error
SCE | La Cumbre | FIPA_2020_1105_0545 | 2020-11-05 | 2020 | 5:45 | 34.4177 | -119.7562 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Santa Barbara Fire Department | OH-4199184E | OH-4199184E | No | Non-HFRA | N | Frontier Communications | 4.16 | Distribution | Conductor | Overhead | Yes | 2020-11-05 | 5:45 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Kickapoo Trail | FIPA_2020_1109_0749 | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1941931E | OH-1941931E | T3 | Tier 3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Bidder | FIPA_2020_1109_1816 | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Santa Barbara County Fire Department | OH-2023941E | OH-2023941E | T3 | Tier 3 | Y | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Heers | VIPA_2020_1110_1116 | 2020-11-10 | 2020 | 11:16 | 33.9607 | 117.2489 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Moreno Valley Fire Department | UG-5206035 | UG-5206035 | No | Non-HFRA | N | None | 12 | Distribution | Switch | Underground | Yes | 2020-11-10 | 11:20 | Equipment/Facility Failure | Switch |  |  | Other
SCE | Troy | FIPA_2020_1114_2200 | 2020-11-14 | 2020 | 22:00 | 34.053 | -118.0627 | Building | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1237759E | OH-1237759E | No | Non-HFRA | N | AT&T California | 4.16 | Distribution | Other | Overhead | No |  |  | Unknown |  |  |  | Unknown
SCE | Fingal | FIPA_2020_1118_2047 | 2020-11-18 | 2020 | 20:47 | 33.9028 | -116.7543 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-432067S | OH-432067S | T3 | Tier 3 | Y | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Dusty | FIPA_2020_1118_1509 | 2020-11-18 | 2020 | 15:09 | 34.122 | 117.9774 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Los Angeles Fire Duarte | OH-900297E | OH-900297E | No | Non-HFRA | N | None | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Pole |  |  | Weather
SCE | Kalmia | FIPA_2020_1123_0144 | 2020-11-23 | 2020 | 1:44 | 33.9632 | -118.247 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1933391E | OH-1933391E | No | Non-HFRA | N | AT&T California | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-23 | 1:45 | Contamination |  |  |  | Other
SCE | Hampshire | FIPA_2020_1125_1051 | 2020-11-25 | 2020 | 10:51 | 34.1888 | -118.8689 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura Fire Department | OH-4735343E | OH-4735343E | T3 | Tier 3 | Y | Frontier Communications; AT&T Calfornia | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-25 | 10:15 | Equipment/Facility Failure | Conductor |  |  | Human Error
SCE | Oban | FIPA_2020_1126_1817 | 2020-11-26 | 2020 | 18:17 | 34.7144 | -118.1305 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-306360E | OH-306360E | No | Non-HFRA | N | None | 12 | Distribution | Switch | Overhead | No | 2020-11-26 | 18:17 | Equipment/Facility Failure | Switch |  |  | other
SCE | Vicasa | FIPA_2020_1130_2102 | 2020-11-30 | 2020 | 21:02 | 34.0723 | -118.588 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Los Angeles Fire Department | OH-4535641E | OH-4535641E | T3 | Tier 3 | Y | Verizon Wireless, AT&T Mobility, Frontier Communications, Crown Castle NG West, Inc | 16 | Distribution | Other | Overhead | Yes | 2020-11-30 | 21:02 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | Locksley | FIPA_2020_1130_0812 | 2020-11-30 | 2020 | 8:12 | 34.1279 | -118.0589 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1271478E | OH-1271478E | No | Non-HFRA | N | AT&T California | 16 | Distribution | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Moonwalk | FIPA_2020_1213_2218 | 2020-12-13 | 2020 | 22:18 | 33.68 | -117.9027 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1462050E | OH-1462050E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Pinzon | FIPA_2020_1214_0400 | 2020-12-14 | 2020 | 4:00 | 33.8042 | -118.3617 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Torrance Fire Department | OH-229022E | OH-229022E | T2 | Tier 2 | Y | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-12-14 | 4:05 | Equipment/Facility Failure | Pole |  |  | Other
SCE | Sturgeon | FIPA_2020_1214_1016 | 2020-12-14 | 2020 | 10:16 | 34.0459 | -117.2013 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-817035E | OH-817035E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Abacus | FIPA_2020_1215_1000 | 2020-12-15 | 2020 | 10:00 | 34.1252 | -117.2102 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-1971562E | OH-1971562E | No | Non-HFRA | N | None | 12 | Distribution | Fuse | Overhead | Yes | 2020-12-15 | 9:48 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Cagli | FIPA_2020_1220_0919 | 2020-12-20 | 2020 | 9:19 | 34.1241 | -117.6258 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-2152996E | OH-2152996E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Lightning Arrestor | Overhead | Yes | 2020-12-20 | 9:13 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Carbon | FIPA_2020_1222_1845 | 2020-12-22 | 2020 | 18:45 | 35.0349 | -118.1689 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4072932E | OH-4072932E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-12-22 | 18:51 | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | Rover | FIPA_2020_1223_1426 | 2020-12-23 | 2020 | 14:26 | 33.9718 | -116.5041 | Other | Urban | .26 - 9.99 Acres | Fire Agency | Riverside County Fire Department | OH-4029775E | OH-4029775E | No | Non-HFRA | N | None | 12 | Distribution | Transformer | Overhead | No |  |  | Other |  |  |  | Other
Note on A1: Name of utility reporting the event
Note on D1: Date the event started (Use MM/DD/YY when inputting dates)
Note on F1: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on G1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on H1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on I1: Material involved in the initial fueling of the fire;
Note on J1: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on K1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on L1: Is who suppressed the fire
Note on M1: If the fire was suppressed by a fire agency or agencies, insert the lead agency when one or more agency was involved
Note on N1: Utility’s description of the pole and/or equipment involved.
Note on S1: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on T1: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on V1: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on W1: The equipment involved in the event (overhead, padmounted or subsurface);
Note on X1: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on Y1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on Z1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AA1: The suspected cause of the ignition;
Note on AB1: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on AC1: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AD1: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AE1: Factors that contributed to the ignition;
Note on AG1: An Optional Field, list additional information that could be useful when examining data.
Note on AK1: Marsico, Louis: Pulled on 9/25/19
Note on AA6: A cessation of normal operation

## Sheet1
Utility Name | Circuit | FIPA Form Name | Date | Year | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | FLOC | HFRA | cGIS HFRA | HFTD | Other Companies | Voltage (Volts) | Business Line | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Circuit_Net9 | Notes (Optional):
SCE | Harlem Springs | FIPA_2020_0101_2050 | 1/1/2020 | 2020 | 20:50 | 34.1156 | -117.2587 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-4389384E | OH-4389384E | No | Non-HFRA | N | None | 12 | Distribution | Other | Overhead | Yes | 1/1/2020 | 20:50 | Equipment/Facility Failure | Insulator |  |  | Other
SCE | Caliber | FIPA_2020_0103_0711 | 1/3/2020 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-549798E | OH-549798E | T3 | Tier 3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 1/3/2020 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | Flycatcher | FIPA_2020_0113_0801 | 1/13/2020 | 2020 | 8:01 | 35.6385 | -118.4046 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1316770E | OH-1316770E | T3 | Tier 3 | Y | Frontier Communications | 12 | Distribution | Other | Overhead | Yes | 1/13/2020 | 8:01 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Hub City | FIPA_2020_0131_1357 | 1/31/2020 | 2020 | 13:57 | 33.8947 | -118.2463 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1813245E | OH-1813245E | No | Non-HFRA | N | AT&T Communication | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
SCE | Fields | FIPA_2020_0204_0543 | 2/4/2020 | 2020 | 5:43 | 34.0914 | -117.5222 | Other | Urban | Less Than .25 Acres | Fire Agency | Rancho Cucamonga Fire Department | OH-4894668E | OH-4894668E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 2/4/2020 | 5:43 | Equipment/Facility Failure | Other |  |  | Other
SCE | WALNUT-CORTEZ-MERCED NO. 2 | FIPA_2020_0213_1308 | 2/13/2020 | 2020 | 13:08 | 34.0915 | -117.8815 | Other | Urban | Less Than .25 Acres | Utility |  | OH-1180455E | OH-1180455E | No | Non-HFRA | N | None | 66 | Transmission | Other | Overhead | Yes | 2/13/2020 | 13:08 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Rover | FIPA_2020_0222_0940 | 2/22/2020 | 2020 | 9:40 | 33.9501 | -116.5302 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-GT14877 | OH-GT14877 | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 2/22/2020 | 9:40 | Equipment/Facility Failure | Insulator |  |  | Weather
SCE | Susquehanna | FIPA_2020_0226_2309 | 2/26/2020 | 2020 | 23:09 | 36.3433 | -119.3041 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1245599E | OH-1245599E | No | Non-HFRA | N | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | Caswell | FIPA_2020_0302_0807 | 3/2/2020 | 2020 | 8:07 | 33.8928 | -118.2751 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-2274731E | OH-2274731E | No | Non-HFRA | N | None | 16 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | Coronado | FIPA_2020_0302_1432 | 3/2/2020 | 2020 | 14:32 | 34.0348 | -118.1187 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1951747E | OH-1951747E | No | Non-HFRA | N | AT&T Communication | 16 | Distribution | Conductor | Overhead | Yes | 3/2/2020 | 14:32 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Grazide | FIPA_2020_0303_2053 | 3/3/2020 | 2020 | 20:53 | 34.0005 | -117.9626 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-E18873Y | OH-E18873Y | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Lightning Arrestor | Overhead | No |  |  | Other |  |  |  | Other
SCE | Burr | FIPA_2020_0306_1123 | 3/6/2020 | 2020 | 11:23 | 36.2286 | -119.0648 | Other | Urban | Less Than .25 Acres | Fire Agency | Montebello Fire Department | OH-4512718E | OH-4512718E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 3/6/2020 | 11:23 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | Medusa | FIPA_2020_0306_1705 | 3/6/2020 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-1811355E | OH-1811355E | T2 | Tier 2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Weather
SCE | Macomber | FIPA_2020_0311_0831 | 3/11/2020 | 2020 | 8:31 | 35.9854 | -119.4069 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-2191789E | OH-2191789E | No | Non-HFRA | N | None | 12 | Distribution | Transformer | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Weather
SCE | Rabbit | FIPA_2020_0317_1555 | 3/17/2020 | 2020 | 15:55 | 34.6673 | -116.9388 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-4288653E | OH-4288653E | No | Non-HFRA | N | None | 12 | Distribution | Other | Overhead | Yes | 3/17/2020 | 15:55 | Contact From Object |  | Animal | Electric Facility | Other
SCE | January | FIPA_2020_0319_1200 | 3/19/2020 | 2020 | 12:00 | 33.6074 | -117.9201 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-835718E | OH-835718E | No | Non-HFRA | N | AT&T Communication | 12 | Distribution | Switch | Overhead | No |  |  | Equipment/Facility Failure | Switch |  |  | Other
SCE | Sand Canyon | FIPA_2020_0422_1520 | 4/22/2020 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-1090802E | OH-1090802E | T3 | Tier 3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | Invention | FIPA_2020_0426_1250 | 4/26/2020 | 2020 | 12:50 | 34.6606 | -118.2366 | Other | Rural | Less Than .25 Acres | Fire Agency | Antelope Valley Fire Department | OH-1309936E | OH-1309936E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 4/26/2020 | 12:50 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Chalfant | FIPA_2020_0427_1519 | 4/27/2020 | 2020 | 15:19 | 37.5304 | -118.3669 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-45770S | OH-45770S | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Lightning Arrestor | Overhead | Yes | 4/27/2020 | 15:18 | Equipment/Facility Failure | Other |  |  | Other
SCE | Townhall | FIPA_2020_0430_0952 | 4/30/2020 | 2020 | 9:52 | 33.9231 | -116.6498 | Other | Urban | Less Than .25 Acres | Fire Agency | Palm Springs Fire Department | OH-2329507E | OH-2329507E | No | Non-HFRA | N | None | 33 | Distribution | Other | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Other
SCE | Quinby | FIPA_2020_0501_2125 | 5/1/2020 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4339082E | OH-4339082E | T2 | Tier 2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 5/1/2020 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | Waterman | FIPA_2020_0509_0323 | 5/9/2020 | 2020 | 3:23 | 34.1117 | -117.2804 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1629706E | OH-1629706E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 5/9/2020 | 3:23 | Other |  |  |  | Unknown |  | Wire Down - WtW not suspected
SCE | Oban | FIPA_2020_0510_1513 | 5/10/2020 | 2020 | 15:13 | 34.7049 | -118.1437 | Other | Rural | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-736330E | OH-736330E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 5/10/2020 | 15:13 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Shade | FIPA_2020_0511_0814 | 5/11/2020 | 2020 | 8:14 | 33.9792 | -118.0533 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-2061964E | OH-2061964E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 5/11/2020 | 7:32 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Acrobat | FIPA_2020_0517_1735 | 5/17/2020 | 2020 | 17:35 | 34.5757 | -118.1094 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-928508E | OH-928508E | No | Non-HFRA | N | AT&T Communication | 12 | Distribution | Fuse | Overhead | Yes | 5/17/2020 | 17:35 | Equipment/Facility Failure | Fuse |  | Electric Facility | Other
SCE | VALLEY-MAYBERRY-MORENO-VISTA | FIPA_2020_0518_1210 | 5/18/2020 | 2020 | 12:10 | 33.8587 | -117.0197 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | Tier 3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | Homer | FIPA_2020_0521_1520 | 5/21/2020 | 2020 | 15:20 | 36.4138 | -119.0733 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Woodlake Fire Department | OH-475645E | OH-475645E | No | Non-HFRA | N | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 5/21/2020 | 15:20 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | Sheffield | FIPA_2020_0523_1637 | 5/23/2020 | 2020 | 16:37 | 34.4139 | -119.5262 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4404319E | OH-4404319E | No | Non-HFRA | N | Frontier Communications | 16 | Distribution | Other | Overhead | Yes | 5/23/2020 | 13:11 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Balsam | FIPA_2020_0526_1959 | 5/26/2020 | 2020 | 19:59 | 34.4206 | -117.3107 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-2155313E | OH-2155313E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Transformer | Overhead | Yes | 5/26/2020 | 28:59 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | Kickapoo Trail | FIPA_2020_0526_2239 | 5/26/2020 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | Tier 3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | SAUGUS-MOORPARK-SANTA SUSANA-TORREY | FIPA_2020_0528_0614 | 5/28/2020 | 2020 | 6:14 | 34.3947 | -118.6824 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | M6-T5 | OH-7019932 | T3 | Tier 3 | Y | None | 66 | Transmission | Other | Overhead | Yes | 5/28/2020 | 6:14 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Zapata | FIPA_2020_0529_1423 | 5/29/2020 | 2020 | 14:23 | 34.1101 | -117.2672 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4003908E | OH-4003908E | No | Non-HFRA | N | None | 12 | Distribution | Other | Overhead | Yes | 5/29/2020 | 14:23 | Other |  |  |  | Unknown
SCE | Agnes | FIPA_2020_0601_1714 | 6/1/2020 | 2020 | 17:14 | 33.8913 | -118.2139 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4371854E | OH-4371854E | No | Non-HFRA | N | AT&T CALIFORNIA | 4.16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Tambourine | FIPA_2020_0602_0754 | 6/2/2020 | 2020 | 7:54 | 34.4923 | -118.6207 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4393756E | OH-4393756E | T3 | Tier 3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | Yes | 6/2/2020 | 7:54 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | TITTLE | FIPA_2020_0602_1109 | 6/2/2020 | 2020 | 11:09 | 33.7349 | -117.9285 | Other | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Department | OH-2145959E | OH-2145959E | No | Non-HFRA | N | AT&T Communication | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | La Mancha | FIPA_2020_0603_1223 | 6/3/2020 | 2020 | 12:23 | 34.1333 | -118.8523 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-1848408E | OH-1848408E | T3 | Tier 3 | Y | None | 16 | Distribution | Other | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | Heavy | FIPA_2020_0603_1957 | 6/3/2020 | 2020 | 19:57 | 35.3849 | -117.7247 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4390703E | OH-4390703E | No | Non-HFRA | N | None | 33 | Distribution | Conductor | Overhead | Yes | 6/3/2020 | 19:57 | Equipment/Facility Failure | Insulator |  |  | Other
SCE | Bonanza | FIPA_2020_0605_1733 | 6/5/2020 | 2020 | 17:33 | 35.7635 | -118.4218 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Kern County Fire Department | OH-4451126E | OH-4451126E | T3 | Tier 3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 6/5/2020 | 17:33 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Yoda | FIPA_2020_0605_1543 | 6/5/2020 | 2020 | 15:43 | 34.6602 | -118.2251 | Other | Urban | 10 - 99 Acres | Unknown |  | OH-K4922Y | OH-K4922Y | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Trumpet | FIPA_2020_0607_0550 | 6/7/2020 | 2020 | 5:50 | 34.4885 | -118.6168 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1871383E | OH-1871383E | T3 | Tier 3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Other
SCE | Calgrove | FIPA_2020_0607_1509 | 6/7/2020 | 2020 | 15:09 | 34.4885 | -118.6168 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4393062E | OH-4393062E | T3 | Tier 3 | Y | AT&T Communication | 16 | Distribution | Conductor | Overhead | Yes | 6/7/2020 | 15:09 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | SAUGUS-MOORPARK-SANTA SUSANA-TORREY | FIPA_2020_0607_2145 | 6/7/2020 | 2020 | 21:45 | 34.3067 | -118.7197 | Vegetation | Urban | .26 - 9.99 Acres | Utility |  | M13-T1 | OH-7018027 | T3 | Tier 3 | Y | None | 66 | Transmission | Other | Overhead | Yes | 7/6/2020 | 21:45 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Lotto | FIPA_2020_0608_1224 | 6/8/2020 | 2020 | 12:24 | 34.494 | -117.5498 | Other | Rural | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-4106577E | OH-4106577E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 6/8/2020 | 12:24 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Oakwood | FIPA_2020_0609_0925 | 6/9/2020 | 2020 | 9:25 | 34.1594 | -118.0288 | Other | Urban | Less Than .25 Acres | Fire Agency | Arcadia Fire Department | OH-922692E | OH-922692E | T2 | Tier 2 | Y | AT&T Communication | 4.16 | Distribution | Other | Overhead | Yes | 6/9/2020 | 9:25 | Equipment/Facility Failure | Other |  |  | Other
SCE | Bidder | FIPA_2020_0609_2142 | 6/9/2020 | 2020 | 21:42 | 34.4674 | -119.9055 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Santa Barbara Fire Department | OH-219558E | OH-219558E | T3 | Tier 3 | Y | Frontier Communications | 16 | Distribution | Transformer | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
SCE | Borba | FIPA_2020_0609_1240 | 6/9/2020 | 2020 | 12:40 | 33.9975 | -117.6491 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Ontario Fire Department | OH-1463533E | OH-1463533E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Fuse | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Weaver | FIPA_2020_0609_1450 | 6/9/2020 | 2020 | 14:50 | 34.0515 | -118.0263 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-882039E | OH-882039E | No | Non-HFRA | N | AT&T California | 4.16 | Distribution | Conductor | Overhead | Yes | 6/9/2020 | 15:31 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | Estaban | FIPA_2020_0609_1947 | 6/9/2020 | 2020 | 19:47 | 34.2284 | -119.0724 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-2116776E | OH-2116776E | No | Non-HFRA | N | Frontier Communications | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
SCE | Viento | FIPA_2020_0609_1642 | 6/9/2020 | 2020 | 16:42 | 35.1384 | -118.4809 | Other | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4707894E | OH-4707894E | T3 | Tier 3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
SCE | Elmer | FIPA_2020_0610_1700 | 6/10/2020 | 2020 | 17:00 | 34.1444 | -118.0671 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-656697E | OH-656697E | No | Non-HFRA | N | AT&T Communication | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Pole |  |  | Other
SCE | Windt | FIPA_2020_0610_1533 | 6/10/2020 | 2020 | 15:33 | 36.2374 | -119.4928 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-703067E | OH-703067E | No | Non-HFRA | N | AT&T California | 12 | Distribution | Conductor | Overhead | Yes | 6/10/2020 | 15:33 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Shoreline | FIPA_2020_0611_0815 | 6/11/2020 | 2020 | 8:15 | 33.7476 | -118.3804 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1803572E | OH-1803572E | T2 | Tier 2 | Y | None | 16 | Distribution | Other | Overhead | Yes | 6/11/2020 | 8:15 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Shoreline | FIPA_2020_0611_0815 | 6/11/2020 | 2020 | 8:15 | 33.7476 | -118.3807 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-975271E | OH-975271E | T2 | Tier 2 | Y | None | 16 | Distribution | Other | Overhead | Yes | 6/11/2020 | 8:15 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | MAGUNDEN-VESTAL NO. 1 | FIPA_2020_0611_1437 | 6/11/2020 | 2020 | 14:37 | 35.7516 | -119.0617 | Other | Rural | Less Than .25 Acres | Unknown |  | M111-T5 | OH-7022567 | No | Non-HFRA | N | None | 220 | Transmission | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Wells | FIPA_2020_0611_1500 | 6/11/2020 | 2020 | 15:00 | 36.3542 | -119.1345 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4594904E | OH-4594904E | No | Non-HFRA | N | None | 12 | Distribution | Switch | Overhead | No |  |  | Equipment/Facility Failure | Switch |  |  | Other
SCE | Standing Rock | FIPA_2020_0611_1552 | 6/11/2020 | 2020 | 15:52 | 34.5547 | -117.1611 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Apple Valley Fire Department | OH-4881038E | OH-4881038E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
SCE | Wing | FIPA_2020_0612_1217 | 6/12/2020 | 2020 | 12:17 | 34.4595 | -117.2738 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Hesperia Fire Department | OH-2156864E | OH-2156864E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Dalmatian | FIPA_2020_0612_1453 | 6/12/2020 | 2020 | 14:53 | 34.0567 | -117.6349 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-4665052E | OH-4665052E | No | Non-HFRA | N | None | 12 | Distribution | Transformer | Overhead | Yes | 6/12/2020 | 13:44 | Unknown |  |  |  | Unknown
SCE | Conestoga | FIPA_2020_0613_1726 | 6/13/2020 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | Tier 3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 6/13/2020 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Porphyry | FIPA_2020_0613_2006 | 6/13/2020 | 2020 | 20:06 | 33.8473 | -117.5145 | Vegetation | Urban | .26 - 9.99 Acres | Unknown |  | OH-73328S | OH-73328S | T3 | Tier 3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 6/13/2020 | 20:06 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Allegra | FIPA_2020_0613_0950 | 6/13/2020 | 2020 | 9:50 | 34.1462 | -116.2701 | Other | Rural | Less Than .25 Acres | Customer |  | OH-1686040E | OH-1686040E | No | Non-HFRA | N | None | 12 | Distribution | Other | Overhead | Yes | 6/13/2020 | 9:50 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Hughes Lake | FIPA_2020_0614_1625 | 6/14/2020 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4665728E | OH-4665728E | T2 | Tier 2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 6/14/2020 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Outside Force
SCE | Whipstock | FIPA_2020_0615_1018 | 6/15/2020 | 2020 | 10:18 | 33.9476 | -117.9233 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-X11989E | OH-X11989E | T3 | Tier 3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 6/15/2020 | 10:18 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Rough | FIPA_2020_0616_1241 | 6/16/2020 | 2020 | 12:41 | 33.8747 | -117.9594 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1222483E | OH-1222483E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 6/16/2020 | 14:41 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Stack | FIPA_2020_0619_1909 | 6/19/2020 | 2020 | 19:09 | 33.8069 | -116.5468 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-235364S | OH-235364S | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 6/19/2020 | 19:09 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Larch | FIPA_2020_0620_1454 | 6/20/2020 | 2020 | 14:54 | 34.033 | -117.3992 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Rialto Fire Department | OH-4869738E | OH-4869738E | T2 | Tier 2 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 6/20/2020 | 14:54 | Contact From Object |  | Other | Electric Facility | Unknown
SCE | Cabernet | FIPA_2020_0621_1123 | 6/21/2020 | 2020 | 11:23 | 34.1169 | -117.3787 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-261195S | OH-261195S | No | Non-HFRA | N | AT&T CALIFORNIA | 12 | Distribution | Other | Overhead | Yes | 6/21/2020 | 11:23 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Deloro | FIPA_2020_0622_1303 | 6/22/2020 | 2020 | 13:03 | 34.4787 | -117.2143 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-2154977E | OH-2154977E | No | Non-HFRA | N | None | 12 | Distribution | Lightning Arrestor | Overhead | Yes | 6/22/2020 | 13:03 | Equipment/Facility Failure | Lightning Arrestor |  |  | Other
SCE | Lakota | FIPA_2020_0622_0812 | 6/22/2020 | 2020 | 8:12 | 34.5384 | -117.2251 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-2155419E | OH-2155419E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Transformer | Overhead | Yes | 6/22/2020 | 8:12 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | ARROWHEAD-CALECTRIC-DEVIL CANYON-SHANDIN | FIPA_2020_0624_1653 | 6/24/2020 | 2020 | 16:53 | 34.147 | -117.3573 | Vegetation | Urban | .26 - 9.99 Acres | Unknown |  | OH-4138868E | OH-4138868E | T2 | Tier 2 | Y | None | 115 | Transmission | Other | Overhead | Yes | 6/24/2020 | 16:53 | Other |  |  |  | Unknown |  | 3rd Party - Homeless encampment
SCE | Greenwell | FIPA_2020_0624_1539 | 6/24/2020 | 2020 | 15:39 | 34.4205 | -119.6038 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Summerland Fire Department | OH-1868554E | OH-1868554E | No | Non-HFRA | N | None | 33 | Distribution | Fuse | Overhead | Yes | 6/24/2020 | 12:40 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | Jamaica | FIPA_2020_0625_1738 | 6/25/2020 | 2020 | 17:38 | 33.8708 | -118.0084 | Other | Rural | Less Than .25 Acres | Fire Agency | Orange County Fire Department | UG-5194363 | UG-5194363 | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Underground | No |  |  | Other |  |  |  | None
SCE | Grubstake | FIPA_2020_0627_0848 | 6/27/2020 | 2020 | 8:48 | 34.7745 | -118.1491 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4769654E | OH-4769654E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Other | Overhead | Yes | 6/27/2020 | 8:58 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | EAGLE ROCK-ALHAMBRA NO. 1 | FIPA_2020_0630_1830 | 6/30/2020 | 2020 | 18:30 | 34.1316 | -118.1832 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Monrovia Fire Department | OH-4209659E | OH-4209659E | No | Non-HFRA | N | City of Pasadena | 66 | Transmission | Other | Overhead | Yes | 6/30/2020 | 18:30 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Drag | FIPA_2020_0703_1655 | 7/3/2020 | 2020 | 16:55 | 36.0637 | -119.0127 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Porterville FD | OH-1517323E | OH-1517323E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | La Mancha | FIPA_2020_0705_0357 | 7/5/2020 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  | OH-1848406E | OH-1848406E | T3 | Tier 3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 7/5/2020 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Other
SCE | Capanero | FIPA_2020_0705_1200 | 7/5/2020 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | Tier 2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 7/5/2020 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Seals | FIPA_2020_0705_1937 | 7/5/2020 | 2020 | 19:37 | 34.5579 | -117.2892 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1601308E | OH-1601308E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 7/5/2020 | 20:44 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Poco | FIPA_2020_0706_0129 | 7/6/2020 | 2020 | 1:29 | 34.8022 | -117.2089 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Barstow Fire Department | OH-1906079E | OH-1906079E | No | Non-HFRA | N | Frontier Communications | 33 | Distribution | Conductor | Overhead | Yes | 7/6/2020 | 1:29 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | Muddy | FIPA_2020_0711_1710 | 7/11/2020 | 2020 | 17:10 | 33.669 | -117.326 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-11131S | OH-11131S | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 7/11/2020 | 17:20 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Nicholas | FIPA_2020_0713_1743 | 7/13/2020 | 2020 | 17:43 | 34.0461 | -118.6533 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-4251442E | OH-4251442E | T3 | Tier 3 | Y | None | 16 | Distribution | Conductor | Overhead | Yes | 7/13/2020 | 17:43 | Equipment/Facility Failure | Conductor |  |  | Human Error
SCE | Helios | FIPA_2020_0714_1539 | 7/14/2020 | 2020 | 15:39 | 34.8652 | -116.6911 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-2236870E | OH-2236870E | No | Non-HFRA | N | None | 12 | Distribution | Other | Overhead | Yes | 7/14/2020 | 15:39 | Equipment/Facility Failure | Transformer |  |  | Outside Force
SCE | Medallion | FIPA_2020_0715_1155 | 7/15/2020 | 2020 | 11:55 | 34.7034 | -118.1598 | Vegetation | Urban | Less Than .25 Acres | Customer |  | OH-1048136E | OH-1048136E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | None
SCE | Knott | FIPA_2020_0719_0944 | 7/19/2020 | 2020 | 9:44 | 33.8504 | -117.9908 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Department | OH-1171929E | OH-1171929E | No | Non-HFRA | N | None | 12 | Distribution | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | COOL WATER-TIEFORT | FIPA_2020_0723_0756 | 7/23/2020 | 2020 | 7:56 | 35.1594 | -116.7588 | Vegetation | Rural | Less Than .25 Acres | Utility |  | OH-A257230E | OH-A257230E | No | Non-HFRA | N | None | 115 | Transmission | Other | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Flycatcher | FIPA_2020_0725_1312 | 7/25/2020 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | Tier 3 | Y | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Hose | FIPA_2020_0726_1742 | 7/26/2020 | 2020 | 17:42 | 34.0602 | -117.6389 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished |  | OH-2268985E | OH-2268985E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 7/26/2020 | 14:42 | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | Tortuga | FIPA_2020_0726_1709 | 7/26/2020 | 2020 | 17:09 | 33.8198 | -116.491 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-35838S | OH-35838S | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error
SCE | Lasker | FIPA_2020_0726_1250 | 7/26/2020 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4619162E | OH-4619162E | T3 | Tier 3 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
SCE | Russ Boyd | FIPA_2020_0731_1032 | 7/31/2020 | 2020 | 10:32 | 34.5091 | -117.469 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4771427E | OH-4771427E | No | Non-HFRA | N | None | 33 | Distribution | Transformer | Overhead | Yes | 7/31/2020 | 10:32 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Erringer | FIPA_2020_0801_1920 | 8/1/2020 | 2020 | 19:20 | 34.2612 | -118.7754 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1415211E | OH-1415211E | T3 | Tier 3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Thunderbolt | FIPA_2020_0802_1646 | 8/2/2020 | 2020 | 16:46 | 34.6486 | -118.1234 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-955925E | OH-955925E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Weather
SCE | Morongo | FIPA_2020_0803_1033 | 8/3/2020 | 2020 | 10:33 | 34.0758 | -116.5548 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-2107480E | OH-2107480E | T2 | Tier 2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 8/3/2020 | 19:15 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Airport | FIPA_2020_0804_1834 | 8/4/2020 | 2020 | 18:34 | 34.7007 | -118.133591D | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-622156E | OH-622156E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 8/4/2020 | 18:30 | Wire-Wire Contact |  |  |  | Weather
SCE | Mercedes | FIPA_2020_0805_2006 | 8/5/2020 | 2020 | 20:06 | 33.7788 | -117.9301 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-970202E | OH-970202E | No | Non-HFRA | N | AT&T CALIFORNIA | 12 | Distribution | Other | Overhead | Yes | 8/5/2020 | 20:06 | Equipment/Facility Failure | Other |  |  | Other
SCE | Morello | FIPA_2020_0809_0853 | 8/9/2020 | 2020 | 8:53 | 33.9348 | 16.994 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-705838E | OH-705838E | T2 | Tier 2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 8/9/2020 | 8:53 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Mettler | FIPA_2020_0810_1435 | 8/10/2020 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Utility |  | OH-2093506E | OH-2093506E | T3 | Tier 3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Human Error
SCE | Bing | FIPA_2020_0812_1440 | 8/12/2020 | 2020 | 14:40 | 33.9486 | -116.9696 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Beaumont Fire Department | OH-1996482E | OH-1996482E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | Lyons | FIPA_2020_0813_2148 | 8/13/2020 | 2020 | 21:48 | 34.3687 | -118.5157 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-4103978E | OH-4103978E | T3 | Tier 3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 8/13/2020 | 21:48 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Hampshire | FIPA_2020_0815_1902 | 8/15/2020 | 2020 | 19:02 | 34.2159 | -118.8604 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-1296864E | OH-1296864E | T3 | Tier 3 | Y | Frontier Communications | 16 | Distribution | Conductor | Overhead | Yes | 8/15/2020 | 19:01 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Hart | FIPA_2020_0816_1613 | 8/16/2020 | 2020 | 16:13 | 36.3048 | -119.2099 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Farmsville Fire Department | OH-4505923E | OH-4505923E | No | Non-HFRA | N | None | 12 | Distribution | Transformer | Overhead | Yes | 8/16/2020 | 16:13 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | Ravine | FIPA_2020_0818_1600 | 8/18/2020 | 2020 | 16:00 | 34.2148 | -118.197 | Other | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-732723E | OH-732723E | T2 | Tier 2 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Nicholas | FIPA_2020_0818_1647 | 8/18/2020 | 2020 | 16:47 | 34.051 | -118.6476 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-GT111426 | OH-GT111426 | T3 | Tier 3 | Y | Frontier Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Beeline | FIPA_2020_0818_1514 | 8/18/2020 | 2020 | 15:14 | 34.5409 | -117.3653 | Vegetation | Rural | Less Than .25 Acres | Utility |  | OH-4613951E | OH-4613951E | No | Non-HFRA | N | None | 12 | Distribution | Other | Overhead | Yes | 8/18/ | 15:14 | Equipment/Facility Failure | Insulator |  |  | Other
SCE | Olancha | FIPA_2020_0819_1118 | 8/19/2020 | 2020 | 11:18 | 34.5126 | -117.3671 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-263181S | OH-263181S | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 8/19/2020 | 11:18 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Mandarin | FIPA_2020_0819_0821 | 8/19/2020 | 2020 | 8:21 | 34.1421 | -117.8874 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1034427E | OH-1034427E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 8/19/2020 | 8:40 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Showdown | FIPA_2020_0823_1739 | 8/23/2020 | 2020 | 17:39 | 34.59 | -118.2032 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4777412E | OH-4777412E | T3 | Tier 3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 8/23/2020 | 17:39 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Lotto | FIPA_2020_0825_1241 | 8/25/2020 | 2020 | 12:41 | 34.4508 | -117.5924 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-4006134E | OH-4006134E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error
SCE | Shiraz | FIPA_2020_0829_1129 | 8/29/2020 | 2020 | 11:29 | 34.1196 | -117.3203 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-704775E | OH-704775E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  | 11:29 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Cafe | FIPA_2020_0831_1712 | 8/31/2020 | 2020 | 17:12 | 33.9387 | -116.4764 | Other | RURAL | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-1556297E | OH-1556297E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
SCE | Oban | FIPA_2020_0904_1801 | 9/4/2020 | 2020 | 18:01 | 34.7039 | -118.1303 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-970804E | OH-970804E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No | 9/4/2020 | 18:01 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Rotec | FIPA_2020_0905_1429 | 9/5/2020 | 2020 | 14:29 | 33.7502 | -117.0329 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Hemet Fire Department | OH-4214288E | OH-4214288E | No | Non-HFRA | N | None | 12 | Distribution | Switch | Overhead | No |  |  | Equipment/Facility Failure | Switch |  |  | Other
SCE | Baldwin | FIPA_2020_0906_1505 | 9/6/2020 | 2020 | 15:05 | 34.1711 | -118.0551 | Other | Urban | Less Than .25 Acres | Fire Agency | Sierra Madre Fire Department | OH-X7926E | OH-X7926E | T2 | Tier 2 | Y | Frontier Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Triumph | FIPA_2020_0906_0233 | 9/6/2020 | 2020 | 2:33 | 34.0892 | -118.1377 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1605216E | OH-1605216E | No | Non-HFRA | N | AT&T CALIFORNIA and TIME WARNER NORTH | 16 | Distribution | Transformer | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Other
SCE | Barbossa | FIPA_2020_0917_0833 | 9/17/2020 | 2020 | 8:33 | 34.0735 | -117.8772 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | West Covina Fire Department | OH-4828324E | OH-4828324E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | Yes | 9/17/2020 | 8:33 | Contact From Object |  | Other | Electric Facility | Unknown
SCE | Musket | FIPA_2020_0920_0131 | 9/20/2020 | 2020 | 1:31 | 33.9134 | -118.0864 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-2006014E | OH-2096013E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | Flying D | FIPA_2020_0924_1035 | 9/24/2020 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-1761180E | OH-1761180E | T3 | Tier 3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | Drum | FIPA_2020_0929_1639 | 9/29/2020 | 2020 | 16:39 | 33.9175 | -117.9819 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1509725E | OH-1509725E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Other | Overhead | Yes | 9/29/2020 | 16:39 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | Calgrove | FIPA_2020_1003_1745 | 10/3/2020 | 2020 | 17:45 | 34.3515 | -118.5616 | Vegetation | Rural | Less Than .25 Acres | Customer |  | OH-2101062E | OH-2101062E | T3 | Tier 3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Power | FIPA_2020_1004_1545 | 10/4/2020 | 2020 | 15:45 | 34.1616 | -117.3411 | Vegetation | Urban | Less Than .25 Acres | Customer |  | OH-200686S | OH-200686S | No | Non-HFRA | N | Frontier Communications | 4.16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Cement | FIPA_2020_1015_1832 | 10/15/2020 | 2020 | 18:32 | 34.5792 | -117.359 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Victorville Fire Department | OH-4531653E | OH-4531653E | No | Non-HFRA | N | None | 33 | Distribution | Other | Overhead | Yes | 10/15/2020 | 18:31 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Parcells | FIPA_2020_1015_0112 | 10/15/2020 | 2020 | 1:12 | 34.0618 | -117.7556 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Pomona LACFD | OH-4098618E | OH-4098618E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Other
SCE | Amazon | FIPA_2020_1016_2233 | 10/16/2020 | 2020 | 22:33 | 34.1053 | -117.9485 | Building | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4617757E | OH-4617757E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Transformer | Overhead | Yes | 10/16/2020 | 22:42 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | Deer | FIPA_2020_1019_2358 | 10/19/2020 | 2020 | 23:58 | 35.9769 | -118.9992 | Vegetation | Rural | Less Than .25 Acres | Customer |  | OH-1895627E | OH-1895627E | No | Non-HFRA | N | AT&T California | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | Tlsmith | FIPA_2020_1022_0412 | 10/22/2020 | 2020 | 4:12 | 36.2722 | -119.3164 | Other | Urban | Less Than .25 Acres | Fire Agency | City of Visalia Fire Department | OH-1467831E | OH-1467831E | No | Non-HFRA | N | AT&T California | 12 | Distribution | Transformer | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Human Error
SCE | Catawba | FIPA_2020_1026_1435 | 10/26/2020 | 2020 | 14:35 | 34.107 | -117.4845 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-670473E | OH-670473E | No | Non-HFRA | N | AT&T California | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Weather
SCE | Vicasa | FIPA_2020_1026_1156 | 10/26/2020 | 2020 | 11:56 | 34.0998 | -118.5925 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-795990E | OH-795990E | T3 | Tier 3 | Y | Frontier Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Weather
SCE | Border | FIPA_2020_1026_0332 | 10/26/2020 | 2020 | 3:32 | 33.8763 | -117.5805 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Corona City Fire Department | OH-1790807E | OH-1790807E | No | Non-HFRA | N | AT&T California | 12 | Distribution | Other | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Thelma | FIPA_2020_1029_2322 | 10/29/2020 | 2020 | 23:22 | 33.7843 | -117.8436 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Department | OH-1374367E | OH-1374367E | No | Non-HFRA | N | AT&T California | 12 | Distribution | Other | Overhead | Yes | 10/29/2020 | 23:22 | Equipment/Facility Failure | Other |  |  | Other
SCE | Nashville | FIPA_2020_1031_1534 | 10/31/2020 | 2020 | 15:34 | 34.0255 | -117.0791 | Vegetation | Urban | .26 - 9.99 Acres | Unknown |  | OH-4671710E | OH-4671710E | T2 | Tier 2 | Y | None | 12 | Distribution | Transformer | Overhead | Yes | 10/31/2020 | 15:09 | Equipment/Facility Failure | Transformer |  |  | Human Error
SCE | La Cumbre | FIPA_2020_1105_0545 | 11/5/2020 | 2020 | 5:45 | 34.4177 | -119.7562 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Santa Barbara Fire Department | OH-4199184E | OH-4199184E | No | Non-HFRA | N | Frontier Communications | 4.16 | Distribution | Conductor | Overhead | Yes | 11/5/2020 | 5:45 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Kickapoo Trail | FIPA_2020_1109_0749 | 11/9/2020 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1941931E | OH-1941931E | T3 | Tier 3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 11/9/2020 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | Bidder | FIPA_2020_1109_1816 | 11/9/2020 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Santa Barbara County Fire Department | OH-2023941E | OH-2023941E | T3 | Tier 3 | Y | None | 16 | Distribution | Conductor | Overhead | Yes | 11/9/2020 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Heers | VIPA_2020_1110_1116 | 11/10/2020 | 2020 | 11:16 | 33.9607 | 117.2489 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Moreno Valley Fire Department | UG-5206035 | UG-5206035 | No | Non-HFRA | N | None | 12 | Distribution | Switch | Underground | Yes | 11/10/2020 | 11:20 | Equipment/Facility Failure | Switch |  |  | Other
SCE | Troy | FIPA_2020_1114_2200 | 11/14/2020 | 2020 | 22:00 | 34.053 | -118.0627 | Building | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1237759E | OH-1237759E | No | Non-HFRA | N | AT&T California | 4.16 | Distribution | Other | Overhead | No |  |  | Unknown |  |  |  | Unknown
SCE | Fingal | FIPA_2020_1118_2047 | 11/18/2020 | 2020 | 20:47 | 33.9028 | -116.7543 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-432067S | OH-432067S | T3 | Tier 3 | Y | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Dusty | FIPA_2020_1118_1509 | 11/18/2020 | 2020 | 15:09 | 34.122 | 117.9774 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Los Angeles Fire Duarte | OH-900297E | OH-900297E | No | Non-HFRA | N | None | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Pole |  |  | Weather
SCE | Kalmia | FIPA_2020_1123_0144 | 11/23/2020 | 2020 | 1:44 | 33.9632 | -118.247 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1933391E | OH-1933391E | No | Non-HFRA | N | AT&T California | 16 | Distribution | Conductor | Overhead | Yes | 11/23/2020 | 1:45 | Contamination |  |  |  | Other
SCE | Hampshire | FIPA_2020_1125_1051 | 11/25/2020 | 2020 | 10:51 | 34.1888 | -118.8689 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura Fire Department | OH-4735343E | OH-4735343E | T3 | Tier 3 | Y | Frontier Communications; AT&T Calfornia | 16 | Distribution | Conductor | Overhead | Yes | 11/25/2020 | 10:15 | Equipment/Facility Failure | Conductor |  |  | Human Error
SCE | Oban | FIPA_2020_1126_1817 | 11/26/2020 | 2020 | 18:17 | 34.7144 | -118.1305 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-306360E | OH-306360E | No | Non-HFRA | N | None | 12 | Distribution | Switch | Overhead | No | 11/26/2020 | 18:17 | Equipment/Facility Failure | Switch |  |  | other
SCE | Vicasa | FIPA_2020_1130_2102 | 11/30/2020 | 2020 | 21:02 | 34.0723 | -118.588 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Los Angeles Fire Department | OH-4535641E | OH-4535641E | T3 | Tier 3 | Y | Verizon Wireless, AT&T Mobility, Frontier Communications, Crown Castle NG West, Inc | 16 | Distribution | Other | Overhead | Yes | 11/30/2020 | 21:02 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | Locksley | FIPA_2020_1130_0812 | 11/30/2020 | 2020 | 8:12 | 34.1279 | -118.0589 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1271478E | OH-1271478E | No | Non-HFRA | N | AT&T California | 16 | Distribution | Other | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Moonwalk | FIPA_2020_1213_2218 | 12/13/2020 | 2020 | 22:18 | 33.68 | -117.9027 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1462050E | OH-1462050E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | Pinzon | FIPA_2020_1214_0400 | 12/14/2020 | 2020 | 4:00 | 33.8042 | -118.3617 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Torrance Fire Department | OH-229022E | OH-229022E | T2 | Tier 2 | Y | None | 16 | Distribution | Conductor | Overhead | Yes | 12/14/2020 | 4:05 | Equipment/Facility Failure | Pole |  |  | Other
SCE | Sturgeon | FIPA_2020_1214_1016 | 12/14/2020 | 2020 | 10:16 | 34.0459 | -117.2013 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-817035E | OH-817035E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | Abacus | FIPA_2020_1215_1000 | 12/15/2020 | 2020 | 10:00 | 34.1252 | -117.2102 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-1971562E | OH-1971562E | No | Non-HFRA | N | None | 12 | Distribution | Fuse | Overhead | Yes | 12/15/2020 | 9:48 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Cagli | FIPA_2020_1220_0919 | 12/20/2020 | 2020 | 9:19 | 34.1241 | -117.6258 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-2152996E | OH-2152996E | No | Non-HFRA | N | Frontier Communications | 12 | Distribution | Lightning Arrestor | Overhead | Yes | 12/20/2020 | 9:13 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | Carbon | FIPA_2020_1222_1845 | 12/22/2020 | 2020 | 18:45 | 35.0349 | -118.1689 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4072932E | OH-4072932E | No | Non-HFRA | N | None | 12 | Distribution | Conductor | Overhead | Yes | 12/22/2020 | 18:51 | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | Rover | FIPA_2020_1223_1426 | 12/23/2020 | 2020 | 14:26 | 33.9718 | -116.5041 | Other | Urban | .26 - 9.99 Acres | Fire Agency | Riverside County Fire Department | OH-4029775E | OH-4029775E | No | Non-HFRA | N | None | 12 | Distribution | Transformer | Overhead | No |  |  | Other |  |  |  | Other

## CPUC Drop Downs
Other Companies | Material at Origin | Land Use at Origin | Suppressed by | Equipment Involved With Ignition | Type | Suspected Initiating Event | Contact From Object | Contributing Factor |  | Size | Facility Contacted | Equipment /Facility Failure | HFRA | HFTD | Outage
BVES | Building | Rural | Customer | Capacitor Bank | Padmounted | Contact Between Third Party Facility on Pole and Supply Lines | Animal | Human Error | Yes | Less Than .25 Acres | Communication Facility | Capacitor Bank | T2 | Y | Yes
Kirkwood Meadows | Other | Urban | Fire Agency | Conductor | Overhead | Contact From Object | Balloons | None | No | .26 - 9.99 Acres | Electric Facility | Conductor | T3 | N | No
Liberty Energy | Vegetation |  | Self Extinguished | Fuse | Subsurface | Contamination | Other | Other |  | 10 - 99 Acres | Pole | Fuse | No
PacifiCorp |  |  | Unknown | Lightning Arrestor |  | Equipment/Facility Failure | Vegetation | Outside Force |  | 100 - 299 Acres |  | Insulator | Yes
PG&E |  |  | Utility | Other |  | Normal Operation | Vehicle | Unknown |  | 300 - 999 Acres |  | Lightning Arrestor
SCE |  |  |  | Switch |  | Other |  | Weather |  | 1000 - 4999 Acres |  | Pole
SDG&E |  |  |  | Transformer |  | Unknown |  |  |  | Greater than 5000 Acres |  | Guy/Span Wire
[6 empty] | Vandalism/Theft |  |  |  | Less than three (3) meters of linear travel |  | Other
[6 empty] | Wire-Wire Contact |  |  |  | Structure Only |  | Protective Relay
Crossarm
Recloser
Sectionalizer
Splice/Clamp/Connector
Switch
Transformer
Voltage Regulator
Note on A1: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on B1: Material involved in the initial fueling of the fire;
Note on C1: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on D1: Is who suppressed the fire
Note on E1: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on F1: The equipment involved in the event (overhead, padmounted or subsurface);
Note on G1: The suspected cause of the ignition;
Note on H1: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on I1: Factors that contributed to the ignition;
Note on K1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on L1: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on M1: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on G2: To be used when contact between a supply facility and non-supply facility on a pole occurred. Note: This field does not specify which facility caused the contact, only that the contact occurred.
Note on G3: Use when contact from outside object caused the incidnet.
Note on G4: Should be used when outside contaminates effect the utility's facilities. Examples: Smoke caused a phase to phase arc which resulted in a fire. Dirt and salt allowed tracking on an insultor, which caused a crossarm to catch on fire and then resulted in a vegetation fire.
Note on G5: A cessation of normal operation
Note on G6: To be used when the supply facility operated normally. Example: A fuse oprated and material fell onto vegetation and started a fire.
Note on G9: This field would include those fires started from gunshots that broke electric equipment, attempted theft of copper cable, etc.
Note on G10: To be used when to two or more supply conductors contact each other.