## CPUC Sample Interactive
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations |  |  |  |  | Notes (Optional):
| Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
SCE | 2014-05-29 | 18:00 | 33.9036 | -118.0387 | Other | Urban | Less Than .25 Acres | Fire Agency | Santa Fe Springs | 14051 Marquadt, Santa Fe Springs 1398339E | None | 66kV | Other | Overhead | No |  |  | Unknown |  |  |  | Unknown
SCE | 2014-06-05 | 9:20 | 34.555 | -118.1178 | Other | Rural | Less Than .25 Acres | Fire Agency | LA County | 700 East Ave. S. Palmdale 1103139E | None | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Unknown
SCE | 2014-06-08 | 18:00 | 33.6809 | -117.9487 | Other | Urban | Less Than .25 Acres | Fire Agency | Huntington Beach | 19391, 19381, 19371, Pitcairn, Huntington Beach 1644241E | None | 12kV | Other | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | None
SCE | 2014-06-13 | 13:00 | 35.7151 | -118.5111 | Vegetation | Rural | 1000 - 4999 Acres | Fire Agency | Cal Fire | West of Lake Isabella & South of Hwy 155 | None | 66kV | Other | Overhead | No |  |  | Unknown |  |  |  | Unknown
SCE | 2014-06-18 | 15:00 | 34.1626 | -118.6767 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | LA County | Location of Fire 726730E Calabasas | None | 16kV | Conductor | Overhead | Yes | 2014-06-18 | Unknown | Unknown |  |  |  | Unknown
SCE | 2014-06-23 | 13:15 | Not Provided | -118.7295 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 00 Old Stage, Glennville, CA 93226 | Unknown | 12kV | Conductor | Overhead | Yes | 2014-06-23 | 16:20 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2014-06-27 | 11:06 | 34.6084 | -119.5003 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ventura County | N Ventura Ave | None | 16kV | Conductor | Overhead | Yes | 2014-06-27 | 11:06 | Contact From Object |  | Animal | Electric Facility | Unknown
SCE | 2014-07-03 | 11:30 | 34.4529 | -119.7548 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Fire Department | C/O Foothill and Rose ln OH-4551557E | Phone & Cable | 16kV | Conductor | Overhead | No |  |  | Other |  |  |  | Other
SCE | 2014-07-24 | 13:00 | 33.5444 | -117.1158 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Not provided | 39613 Liefer Rd., Temecula 2150193E | None | 12kV | Lightning Arrestor | Overhead | No |  |  | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown
SCE | 2014-07-27 | 18:00 | 36.0502 | -119.0575 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare County Fire | 1785 W. POPLAR AVE., PORTERVILE S/E CORNER OF PROPERTY AT FENCE LINE 4447887E | Unknown | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2014-07-29 | 8:23 | 34.4529 | -117.1873 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside County | UG-5057024,rouse rd, menifee ca | None | 12kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2014-07-30 | 15:00 | 34.1593 | -117.2908 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | San Bernardino Fire | 3750 MAYFIELD PL SAAN BERDO, 66864e and 1499831e | None | 12kV | Other | Overhead | Yes | 2014-07-30 | 15:00 | Contact From Object |  | Vegetation | Electric Facility | Human Error | Tree trimmer dropped palm frond on wires.
SCE | 2014-07-31 | 16:00 | 33.7928 | -117.2832 | Other | Rural | Less Than .25 Acres | Fire Agency | Perris Fire Department | 22597 FORREST RD, Perris | Phone & Cable | 12kV | Other | Overhead | No |  |  | Unknown |  |  |  | Unknown
SCE | 2014-08-03 | 20:00 | 36.3426 | -119.3757 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Visalia Fire Department | NS of Goshen Ave. 1/4 mile west of Shirk Rd. Visalia,Ca, OH-827508E | None | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Pole | Unknown
SCE | 2014-08-12 | 13:29 | 34.3868 | -119.3145 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ventura County | SANTA ANA BL S/O SANTA ANA RD OAK VIEW | Unknown | 16kV | Conductor | Overhead | Yes | 2014-08-12 | 12:05 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2014-08-16 | 9:00 | 33.7337 | -117.0152 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Hemet Fire Department | 810 S CAWSTON AVE, 4447283e | Phone | 12kV | Other | Overhead | Yes | 2014-08-16 | 9:00 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2014-08-17 | 15:00 | 33.747 | -117.7993 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | OC Fire Authority | 1622 alta vista dr, santa ana, ca | None | 12kV | Transformer | Overhead | Yes | 2014-08-17 | 16:00 | Equipment/Facility Failure | Transformer |  |  | Unknown
SCE | 2014-08-24 | 8:30 | 34.0088 | -117.4022 | Building | Urban | .26 - 9.99 Acres | Fire Agency | Riverside County FD | 5795 Kenwood Pl Pole 207117S | None | 12kV | Other | Overhead | Yes | 2014-08-24 | 8:30 | Other |  |  |  | Unknown
SCE | 2014-08-30 | 15:30 | 34.1709 | -117.2957 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | San Bernardino Fire | 4718 Acacia San Bernadino, 688508H | Phone & Cable | 4kV | Other | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2014-09-05 | 14:00 | 34.0276 | -117.9072 | Other | Urban | Less Than .25 Acres | Fire Agency | West Covina FD | 1829 Greenleaf Dr. West Covina, V5011025 |  | 12kV | Other | Subsurface | Yes | 2014-09-05 | 14:00 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2014-09-06 | 14:00 | 33.878 | -117.5196 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Riverside County | 13462 magnolia ave, corona 748702E | Unknown | 12kV | Conductor | Overhead | Yes | 2014-09-06 | 14:00 | Unknown |  |  |  | Unknown
SCE | 2014-09-08 | 11:55 | 34.56 | -118.0402 | Other | Urban | Less Than .25 Acres | Fire Agency | LA County | 37316 50TH ST EAST PALMDALE, 1184634E | Phone & Cable | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2014-09-15 | 16:00 | 34.174 | -118.0576 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Sierra Madre FD | rear of 630 Sierra Meadows near structure 1271353E | Unknown | 16kV | Other | Overhead | Yes | 2014-09-15 | 15:54 | Contact From Object |  | Balloons | Electric Facility | None
SCE | 2014-09-19 | 23:20 | 34.0383 | -118.872 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | LA County | 32008 PACIFIC COAST HWY MALIBU CA. 90265, 2144754E | Phone & Cable | 16kV | Transformer | Overhead | No |  |  | Contamination |  |  |  | Other
SCE | 2014-10-03 | 15:00 | 34.0469 | -117.9851 | Other | Urban | Less Than .25 Acres | Unknown |  | 1160454e n/e corner of puente and nelson, la puente, ca | Unknown | 12kV | Other | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Unknown
SCE | 2014-10-04 | 16:00 | 34.1652 | -117.3566 | Other | Urban | Less Than .25 Acres | Fire Agency | San Bernardino Fire | 2497 W. 3rd Ave.San Bernardino, pole has no structure # made R/O to x-mfr pole 2121692e | Unknown | 4kV | Other | Overhead | Yes | 2014-10-04 | 16:00 | Unknown |  |  |  | Unknown
SCE | 2014-10-10 | 16:24 | 34.2049 | -118.8747 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Thousand Oaks | 73 TRIANGLE ST THOUSAND OAKS, CA 1540200E | Unknown | 16kV | Conductor | Overhead | Yes | 2014-10-10 | 16:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2014-11-07 | 17:00 | Not Provided | Not Provided | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Redondo Beach Fire Dept | 509 s Lucia redondo beach 90277 - A6932Y | Unknown | 16kV | Conductor | Overhead | Yes | 2014-11-07 | 19:00 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2014-11-10 | Not Provided | Not Provided | Not Provided | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Arcadia Fire Department | R/O School on Santa Anita and Virginia, (FIRST AV PL/W 138' S/O VIRGINIA DR) OH-922691E | None | 4kV | Conductor | Overhead | Yes | 2014-11-10 | Not Provided | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2014-11-13 | 12:00 | 34.4934 | -117.1864 | Building | Urban | Less Than .25 Acres | Fire Agency | Apple Valley Fire Department | 21838 Ottawa 4559358E | Unknown | 12kV | Other | Overhead | No |  |  | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Unknown
SCE | 2014-11-16 | 13:30 | 34.048 | -118.683 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LA County | R/O 23347 PALM CANYON LANE, (N PP 400 N/O MALIBU CREEK CYN RD BEAR SIERRA) OH-386290E | Unknown | 16kV | Conductor | Overhead | Yes | 2014-11-16 | 13:30 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2014-11-17 | 4:30 | 34.3129 | -118.8983 | Other | Rural | Less Than .25 Acres | Fire Agency | Ventura County | 11856 Broadway rd, moorpark, ca, 93021, 1603560E | Unknown | 16kV | Transformer | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Weather
SCE | 2014-11-21 | 4:41 | 34.0891 | -117.3712 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | RIALTO FD | VACANT FIELD; VACNT LOT NEXT N/O 660 S. RIVERSIDE AVE - 1595040E | Unknown | 12kV | Other | Overhead | No |  |  | Other |  |  |  | Weather | Lightning strike.
SCE | 2014-12-02 | 10:00 | 34.1058 | -117.7882 | Other | Urban | Less Than .25 Acres | Fire Agency | La Verne Fire Department | 1025 Bonita Ave., La Verne G24716Y | Phone & Cable | 12kV | Capacitor Bank | Overhead | Yes | 2014-12-02 | 10:00 | Vandalism/Theft |  |  |  | Unknown
SCE | 2014-12-03 | 19:00 | 34.0377 | -117.7596 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Pomona Fire Department | 1852 GARLAND ST, POMONA, OH-1100807E | None | 12kV | Conductor | Overhead | Yes | 2014-12-03 | 19:00 | Equipment/Facility Failure | Conductor |  |  | Weather
SCE | 2014-12-04 | 4:00 | 34.012 | -117.9709 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LA County | Rochlen St. off Kwis private st., SCE Primary pole ( 1046135E & maybe 1046136E & E14291Y ) | Phone & Cable | 12kV | Conductor | Overhead | Yes | 2014-12-04 | 4:00 | Other |  |  |  | Unknown
SCE | 2014-12-05 | 2:52 | 33.9397 | -117.6115 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Chino Fire Department | 1744 Hellman Chino, CA OH-4280000E | None | 12kV | Other | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
SCE | 2014-12-12 | 1:30 | 35.922 | -119.0179 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | 7260 Rd. 248 Terra Bella, CA, 1901852E | None | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Weather
SCE | 2014-12-27 | 8:17 | 34.072 | -117.839 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LA County | covina hills x CALLE FRANCESCA | Phone & Cable | 12kV | Switch | Overhead | Yes |  |  | Contact From Object |  | Animal | Pole | Outside Force
Note on A1: Name of utility reporting the event
Note on X1: An Optional Field, list additional information that could be useful when examining data.
Note on B2: Date the event started (Use MM/DD/YY when inputting dates)
Note on C2: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on D2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on E2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on F2: Material involved in the initial fueling of the fire;
Note on G2: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on H2: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on I2: Is who suppressed the fire
Note on J2: If the fire was suppressed by a fire agency or agencies, insert the lead agency when one or more agency was involved
Note on K2: Utility’s description of the pole and/or equipment involved.
Note on L2: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on M2: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on N2: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on O2: The equipment involved in the event (overhead, padmounted or subsurface);
Note on P2: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on Q2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on R2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on S2: The suspected cause of the ignition;
Note on T2: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on U2: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on V2: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on W2: Factors that contributed to the ignition;

## CPUC Drop Downs
BVES | Building | Rural | Customer | Capacitor Bank | Padmounted | Contact Between Third Party Facility on Pole and Supply Lines | Animal | Human Error | Yes | Less Than .25 Acres | Communication Facility | Capacitor Bank
Kirkwood Meadows | Other | Urban | Fire Agency | Conductor | Overhead | Contact From Object | Balloons | None | No | .26 - 9.99 Acres | Electric Facility | Conductor
Liberty Energy | Vegetation |  | Self Extinguished | Fuse | Subsurface | Contamination | Other | Other |  | 10 - 99 Acres | Pole | Fuse
PacifiCorp |  |  | Unknown | Lightning Arrestor |  | Equipment/Facility Failure | Vegetation | Outside Force |  | 100 - 299 Acres |  | Insulator
PG&E |  |  | Utility | Other |  | Normal Operation | Vehicle | Unknown |  | 300 - 999 Acres |  | Lightning Arrestor
SCE |  |  |  | Switch |  | Other |  | Weather |  | 1000 - 4999 Acres |  | Pole
SDG&E |  |  |  | Transformer |  | Unknown |  |  |  | Greater than 5000 Acres |  | Guy/Span Wire
[6 empty] | Vandalism/Theft |  |  |  | Less than three (3) meters of linear travel |  | Other
[6 empty] | Wire-Wire Contact |  |  |  | Structure Only |  | Protective Relay
Crossarm
Recloser
Sectionalizer
Splice/Clamp/Connector
Switch
Transformer
Voltage Regulator
Note on G2: To be used when contact between a supply facility and non-supply facility on a pole occurred. Note: This field does not specify which facility caused the contact, only that the contact occurred.
Note on G3: Use when contact from outside object caused the incidnet.
Note on G4: Should be used when outside contaminates effect the utility's facilities. Examples: Smoke caused a phase to phase arc which resulted in a fire. Dirt and salt allowed tracking on an insultor, which caused a crossarm to catch on fire and then resulted in a vegetation fire.
Note on G5: A cessation of normal operation
Note on G6: To be used when the supply facility operated normally. Example: A fuse oprated and material fell onto vegetation and started a fire.
Note on G9: This field would include those fires started from gunshots that broke electric equipment, attempted theft of copper cable, etc.
Note on G10: To be used when to two or more supply conductors contact each other.