## Report
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations |  |  |  |  | Notes (Optional):
Utility Name | Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
SCE | 2019-01-23 | 18:57 | 34.2768 | -118.7847 | Vegetation | Urban | Less Than .25 Acres | Utility |  | OH-1831781E | NA | 16kV | Other | Overhead | Yes | 2019-01-23 | 18:57 | Contact From Object |  | Other | Electric Facility | Other
SCE | 2019-02-08 | 18:11 | 34.2793 | -118.7787 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1542332E | AT&T Communications | 12kV | Transformer | Overhead | Yes | 2019-02-08 | 18:11 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2019-03-03 | 14:25 | 33.8666 | -116.5521 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4493741E | NA | 12kV | Conductor | Overhead | Yes | 2019-03-03 | 14:25 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2019-03-16 | 17:58 | 33.6182 | -117.8025 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  | OH-1729510E | NA | 12kV | Conductor | Overhead | Yes | 2019-03-16 | 17:58 | Equipment/Facility Failure | Crossarm |  |  | Unknown
SCE | 2019-03-25 | 10:31 | 33.9906 | -117.8815 | Building | Urban | Less Than .25 Acres | Unknown |  | OH-4668167E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2019-03-25 | 10:31 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2019-03-27 | 14:39 | 34.0823 | -117.9132 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1165772E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2019-03-30 | 19:30 | 34.2244 | -119.1403 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-4551685E | NA | 66kV | Conductor | Overhead | Yes | 2019-11-01 | 11:58 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2019-04-08 | 15:30 | 34.0795 | -118.1516 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Alhambra Fire Department | OH-4090802E | NA | 16kV | Conductor | Overhead | Yes | 2019-04-08 | 15:00 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2019-04-09 | 4:53 | 34.277 | -119.3047 | Vegetation | Urban | Less Than .25 Acres | Utility |  | OH-4754671E | AT&T Communications | 16kV | Capacitor Bank | Overhead | No |  |  | Equipment/Facility Failure | Capacitor Bank |  |  | Weather
SCE | 2019-04-09 | 13:57 | 33.8557 | -116.5577 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-4854654E | NA | 12kV | Conductor | Overhead | Yes | 2019-04-09 | 13:57 | Wire-Wire Contact |  |  |  | Weather
SCE | 2019-04-14 | 13:40 | 34.0174 | -117.9171 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1034259E | NA | 12kV | Conductor | Overhead | Yes | 2019-04-14 | 13:40 | Contact From Object |  | Balloons | Electric Facility | Other
SCE | 2019-04-15 | 7:28 | 34.304 | -118.9417 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | UG-5536403 | NA | 16kV | Other | Padmounted | Yes | 2019-04-15 | 7:28 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2019-04-19 | 14:05 | 34.5113 | -117.3126 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Victorville Fire Department | OH-4615681E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2019-04-21 | 12:08 | 36.3062 | -119.673 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1643672E | AT&T Communications | 12kV | Conductor | Overhead | Yes | 2019-04-21 | 12:08 | Equipment/Facility Failure | Conductor |  |  | Outside Force
SCE | 2019-04-22 | 1:56 | 34.2028 | -118.8508 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-T1883Y | FRONTIER COMMUNICATIONS | 16kV | Switch | Overhead | Yes | 2019-04-22 | 1:56 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2019-04-22 | 17:03 | 34.4143 | -117.2215 | Other | Rural | Less Than .25 Acres | Fire Agency | Apple Valley Fire Department | OH-2155218E | NA | 12kV | Transformer | Overhead | Yes | 2019-04-23 | 17:03 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2019-04-23 | 21:06 | 34.2147 | -117.0973 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1027559E | FRONTIER COMMUNICATIONS | 12kV |  | Overhead | No |  |  | Unknown |  |  |  | Unknown
SCE | 2019-04-25 | 4:08 | 33.9342 | -118.0544 | Building | Urban | Less Than .25 Acres | Unknown |  | OH-1800252E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Human Error
SCE | 2019-04-24 | 9:06 | 34.6748 | -118.2548 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4755152E | NA | 16kV | Switch | Overhead | Yes | 2019-04-24 | 9:06 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2019-04-24 | 12:07 | 34.136 | -116.1815 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1692954E | NA | 25kV | Conductor | Overhead | Yes | 2019-04-24 | 12:07 | Wire-Wire Contact |  |  |  | Other
SCE | 2019-05-02 | 21:16 | 34.4156 | -118.782 | Vegetation | Urban | .26 - 9.99 Acres | Unknown |  | OH-4510190E | NA | 16kV | Conductor | Overhead | Yes | 2019-05-02 | 21:16 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2019-05-04 | 17:14 | 33.8404 | -117.5209 | Building | Urban | Less Than .25 Acres | Self Extinguished |  | OH-72882S | NA | 16kV | Other | Overhead | Yes | 2019-05-04 | 17:14 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2019-05-10 | 7:31 | 34.7328 | -118.1842 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4487590E | NA | 12kV | Switch | Overhead | Yes | 2019-05-10 | 7:31 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2019-05-14 | 18:26 | 33.5912 | -114.6749 | Other | Rural | Less Than .25 Acres | Fire Agency | Blythe Fire Department | OH-4800765E | NA | 33kV | Transformer | Overhead | Yes | 2019-05-14 | 18:26 | Contamination | Transformer | Animal | Electric Facility | Unknown
SCE | 2019-05-21 | 14:48 | 33.856 | -116.5586 | Vegetation | Urban | Less Than .25 Acres | Utility |  | OH-335422S | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2019-05-21 | 14:48 | Wire-Wire Contact |  |  |  | Unknown
SCE | 2019-05-26 | 16:05 | 34.5327 | -117.3005 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-427976S | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2019-05-26 | 14:27 | Wire-Wire Contact |  |  |  | Weather
SCE | 2019-06-01 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-692807E | AT&T Communications | 12kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor | Animal |  | Human Error
SCE | 2019-06-02 | 14:13 | 34.5984 | -117.6847 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-693081E | NA | 12kV | Fuse | Overhead | No |  |  | Contact From Object | Transformer | Other | Electric Facility | Outside Force
SCE | 2019-06-02 | 18:43 | 34.071 | -117.486 | Building | Urban | Less Than .25 Acres | Fire Agency | Fontana Fire Department | OH-872186E | AT&T Communications | 12kV | Conductor | Overhead | Yes | 2019-06-02 | 18:43 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2019-06-05 | 10:34 | 35.9137 | -119.206 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1441940E | NA | 12kV | Transformer | Overhead | Yes | 2019-06-05 | 10:04 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2019-06-06 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Valencia Fire Department | OH-4419830E | NA | 16kV | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error
SCE | 2019-06-06 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1382763E | AT&T Communications | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2019-06-07 | 7:54 | 36.055 | -118.9491 | Other | Rural | Less Than .25 Acres | Fire Agency | Porterville Fire Department | OH-4099154E | AT&T Communications | 12kV | Conductor | Overhead | Yes | 2019-06-07 | 7:54 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2019-06-10 | 15:43 | 34.4684 | -117.4436 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Victorville Fire Department | OH-4185203E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2019-06-10 | 15:43 | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | 2019-06-11 | 16:31 | 34.0555 | -117.8815 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | West Covina Fire Department | OH-1528404E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2019-06-11 | 16:20 | Other |  |  |  | Human Error
SCE | 2019-06-11 | 17:03 | 33.824 | -117.2974 | Vegetation | Rural | Less Than .25 Acres | Utility |  | UG-5060461 | NA | 12kV | Conductor | Padmounted | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error
SCE | 2019-06-13 | 7:05 | 33.8124 | -118.1784 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1621549E | NA | 12kV | Conductor | Overhead | Yes | 2019-06-13 | 9:37 | Wire-Wire Contact |  |  |  | Outside Force
SCE | 2019-06-17 | 11:48 | 36.1813 | -119.3268 | Other | Rural | Less Than .25 Acres | Fire Agency | Tulare Fire Department | OH-1254244E | AT&T Communications | 12kV | Fuse | Overhead | No |  |  | Contact From Object |  | Vehicle | Communication Facility | Outside Force
SCE | 2019-06-18 | 15:04 | 34.0464 | -117.6764 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ontario Fire Department | OH-2194146E | NA | 12kV | Switch | Overhead | Yes | 2019-06-18 | 15:04 | Equipment/Facility Failure | Switch |  |  | Outside Force
SCE | 2019-06-20 | 6:18 | 34.114 | -117.2341 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | CAL Fire | OH-622103E | AT&T Communications | 12kV | Conductor | Overhead | Yes | 2019-06-20 | 6:18 | Equipment/Facility Failure | Insulator |  |  | Other
SCE | 2019-06-20 | 14:08 | 34.2298 | -117.4048 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bern. Fire Department | OH-201371S | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error
SCE | 2019-06-23 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Local Fire Department | OH-4561512E | NA | 12kV | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2019-06-25 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-X314E | LADWP | 16kV | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather
SCE | 2019-06-27 | 9:07 | 36.033 | -119.0973 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-4351620E | NA | 12kV | Conductor | Overhead | Yes | 2019-06-27 | 9:07 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2019-06-27 | 12:18 | 34.8928 | -116.9788 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1793713E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2019-06-27 | 12:18 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2019-07-04 | 1:09 | 36.0633 | -119.1469 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-820741E | AT&T Communications | 120kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error
SCE | 2019-07-06 | 12:47 | 34.5921 | -117.438 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Bern. Fire Department | OH-2043087E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2019-07-06 | 12:47 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2019-07-07 | 6:28 | 36.0991 | -119.429 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Local Fire Department | OH-4761611E | NA | 12kV | Conductor | Overhead | Yes | 2019-07-07 | 6:28 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None
SCE | 2019-07-07 | 6:39 | 34.1469 | -117.89 | Other | Urban | Less Than .25 Acres | Fire Agency | LA County Fire Department | OH-4110272E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2019-07-07 | 6:09 | Contact From Object |  | Animal | Electric Facility | Other
SCE | 2019-07-15 | 22:43 | 34.1087 | -118.0169 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Local Fire Department | OH-4437103E | NA | 16kV | Conductor | Overhead | Yes | 2019-07-15 | 22:43 | Equipment/Facility Failure | Fuse |  |  | None
SCE | 2019-07-18 | 15:50 | 34.1087 | -117.7061 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LA County Fire Department | OH-650528E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | None
SCE | 2019-07-18 | 21:10 | 36.3279 | -119.2576 | Other | Urban | Less Than .25 Acres | Fire Agency | Visalia Fire Department | OH-4537379E | AT&T Communications | 12kV | Fuse | Overhead | No |  |  | Equipment/Facility Failure | Fuse |  |  | Other
SCE | 2019-07-24 | 8:41 | 34.0666 | -117.3362 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1807397E | NA | 12kV | Conductor | Overhead | Yes | 2019-07-24 | 8:41 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2019-07-24 | 22:55 | 33.8231 | -117.5117 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Corona Fire Department | OH-4053793E | AT&T Communications | 33kV | Conductor | Overhead | Yes | 2019-07-24 | 23:38 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None
SCE | 2019-07-31 | 7:34 | 33.5662 | -117.1183 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished |  | OH-4402032E | NA | 33kV | Other | Overhead | Yes | 2019-07-31 | 7:34 | Contact From Object |  | Animal | Electric Facility | Other
SCE | 2019-08-01 | 8:27 | 33.8797 | -118.1728 | Other | Urban | Less Than .25 Acres | Utility |  | OH-1274442E | NA | 12kV | Lightning Arrestor | Overhead | Yes | 2019-08-01 | 8:27 | Contact From Object |  | Animal | Electric Facility | Other
SCE | 2019-08-01 | 19:15 | 34.009 | -118.1499 | Other | Urban | Less Than .25 Acres | Fire Agency | LA County Fire Department | OH-4095391E | NA | 16kV | Other | Subsurface | Yes | 2019-08-01 | 19:15 | Vandalism/Theft |  |  |  | None
SCE | 2019-08-03 | 20:00 | 34.6829 | -118.1439 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | LA County Fire Department | OH-917891E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2019-08-03 | 20:20 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2019-08-04 | 8:04 | 34.8276 | -119.0419 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | U.S.A.F. Fire Department | OH-2014835E | AT&T Communications | 12kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2019-08-05 | 17:49 | 34.1541 | -117.2611 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-1008856E | FRONTIER COMMUNICATIONS | 12kV | Transformer | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Other
SCE | 2019-08-06 | 15:03 | 34.3918 | -118.6596 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Ventura County Fire Department | M6-T1 | NA | 66kV | Other | Overhead | Yes | 2019-08-06 | 12:51 | Contact From Object |  | Animal | Electric Facility | Other
SCE | 2019-08-07 | 11:01 | 34.0527 | -117.5022 | Vegetation | Urban | Less Than .25 Acres | Unknown |  | OH-4027733E | NA | 12kV | Other | Overhead | Yes | 2019-08-07 | 11:01 | Equipment/Facility Failure | Other |  |  | Outside Force
SCE | 2019-08-10 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-4734128E | AT&T Communications | 16kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2019-08-14 | 9:08 | 33.9511 | -118.1181 | Vegetation | Urban | Less Than .25 Acres | Customer |  | OH-4088074E | FRONTIER COMMUNICATIONS | 12kV | Lightning Arrestor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Other
SCE | 2019-08-16 | 3:37 | 34.1068 | -117.7223 | Other | Urban | Less Than .25 Acres | Fire Agency | Local Fire Department | OH-1632606E | NA | 12kV | Other | Subsurface | Yes | 2019-08-16 | 3:37 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2019-08-16 | 8:35 | 34.2053 | -117.3349 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bern. Fire Department | OH-4138882E | NA | 115kV | Other | Overhead | Yes | 2019-08-16 | 8:35 | Contact From Object |  | Animal | Electric Facility | Other
SCE | 2019-08-21 | 6:28 | 34.1571 | -117.3389 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4699294E | NA | 33kV | Conductor | Overhead | Yes | 2019-08-21 | 6:30 | Contact From Object |  | Animal | Electric Facility | Other
SCE | 2019-08-25 | 8:03 | 34.301 | -118.8308 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Local Fire Department | OH-4754475E | NA | 16kV | Lightning Arrestor | Overhead | Yes | 2019-08-25 | 8:03 | Contact From Object |  | Animal | Electric Facility | Other
SCE | 2019-08-25 | 10:54 | 33.7764 | -117.4852 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | CAL Fire | OH-1757390E | NA | 33kV | Conductor | Overhead | Yes | 2019-08-25 | 10:54 | Vandalism/Theft |  |  |  | Other
SCE | 2019-08-26 | 1:28 | 34.8974 | -118.2459 | Other | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-1897202E | NA | 12kV | Conductor | Overhead | Yes | 2019-08-26 | 1:28 | Equipment/Facility Failure | Conductor |  |  | Other
SCE | 2019-08-28 | 6:06 | 36.3052 | -119.2946 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-4531370E | AT&T Communications | 12kV | Conductor | Overhead | Yes | 2019-08-28 | 6:06 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2019-08-30 | 9:30 | 36.1141 | -119.0537 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare Fire Department | OH-4683777E | AT&T Communications | 12kV | Other | Overhead | Yes | 2019-08-31 | 9:30 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2019-08-30 | 13:37 | 33.7788 | -117.2448 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-4405245E | AT&T Communications | 12kV | Switch | Overhead | Yes | 2019-08-30 | 13:37 | Equipment/Facility Failure | Switch |  |  | Other
SCE | 2019-08-30 | 13:37 | 33.774 | -117.2492 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-1824460E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2019-08-30 | 13:37 | Contact From Object |  | Balloons | Electric Facility | Other
SCE | 2019-08-30 | 14:59 | 34.526 | -117.306 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-1738634E | FRONTIER COMMUNICATIONS | 4kV | Conductor | Overhead | Yes | 2019-08-30 | 14:59 | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | 2019-09-02 | 8:49 | 36.0512 | -119.1693 | Other | Rural | Less Than .25 Acres | Fire Agency | Tulare Fire Department | OH-4701102E | Charter Communications | 12kV | Conductor | Overhead | Yes | 2019-09-02 | 9:05 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | 2019-09-02 | 14:02 | 34.7026 | -118.342 | Other | Rural | Less Than .25 Acres | Fire Agency | LA County Fire Department | OH-4782978E | None | 12kV | Conductor | Overhead | Yes | 2019-09-02 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other
SCE | 2019-09-02 | 15:53 | 35.1291 | -118.4345 | Other | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-1702483E | None | 12kV | Conductor | Overhead | Yes | 2019-09-02 | 15:53 | Contamination |  |  |  | Other
SCE | 2019-09-04 | 9:25 | 34.0759 | -117.7656 | Other | Urban | Less Than .25 Acres | Fire Agency | LA County Fire Department | OH-G19316Y | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2019-09-04 | 9:25 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2019-09-04 | 11:41 | 34.5041 | -117.3383 | Other | Rural | Less Than .25 Acres | Fire Agency | Victorville Fire Department | OH-63234S | FRONTIER COMMUNICATIONS | 12kV | Transformer | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Other
SCE | 2019-09-11 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | LA County Fire Department | OH-4424792E | Verizon / AT&T / Crown Castle | 16kV | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error
SCE | 2019-09-12 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Fire Agency | LA County Fire Department | OH-1937264E | None | 16kV | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Unknown
SCE | 2019-09-15 | 12:54 | 36.3349 | -119.5652 | Other | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-2163004E | AT&T Communications | 12kV | Transformer | Overhead | Yes | 2019-09-15 | 12:54 | Contact From Object |  | Vehicle | Electric Facility | Human Error
SCE | 2019-09-18 | 2:27 | 36.3127 | -119.3242 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Visalia Fire Department | OH-1612894E | AT&T Communications | 12kV | Lightning Arrestor | Overhead | No |  |  | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown
SCE | 2019-09-18 | 2:52 | 34.3143 | -117.3793 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4066969E | NA | 12kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Human Error
SCE | 2019-09-19 | 14:28 | 33.7612 | -117.2259 | Other | Urban | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-2315084E | None | 12kV | Conductor | Overhead | Yes | 2019-09-19 | 14:28 | Contact From Object |  | Vehicle | Electric Facility | Human Error
SCE | 2019-09-19 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | Fire Agency | Riverside County Fire Department | OH-2225310E | None | 33kV | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other
SCE | 2019-09-20 | 13:26 | 37.6805 | -118.403 | Other | Rural | Less Than .25 Acres | Fire Agency | Bishop Fire Department | OH-2357410E | None | 12kV | Transformer | Overhead | Yes | 2019-09-20 | 13:26 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | 2019-09-21 | 8:20 | 34.6391 | -118.085 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | U.S.A.F. Fire Department | OH-1001513E | None | 12kV | Conductor | Overhead | Yes | 2019-09-21 | 8:20 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2019-09-21 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | Fire Agency | CAL Fire | OH-4252581E | AT&T Communications | 12kV | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error
SCE | 2019-09-24 | 14:24 | 33.9376 | -116.8199 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-4259608E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Pole |  |  | Other
SCE | 2019-09-24 | 15:45 | 34.0364 | -117.0404 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Yucaipa Fire Department | OH-4369853E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | Yes | 2019-09-24 | 15:45 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2019-09-24 | 20:22 | 34.2949 | -119.2995 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-1359556E | AT&T Communications | 16kV | Conductor | Overhead | Yes | 2019-09-24 | 20:22 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | 2019-10-02 | 9:13 | 34.5284 | -117.3032 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Victorville Fire Department | OH-4615483E | FRONTIER COMMUNICATIONS | 4kV | Transformer | Overhead | Yes | 2019-10-02 | 9:13 | Equipment/Facility Failure | Transformer |  |  | Other
SCE | 2019-10-11 | 8:00 | 34.273 | -119.2818 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-1281245E | NA | 16kV | Conductor | Overhead | Yes | 2019-10-11 | 8:15 | Contact From Object |  | Vegetation | Electric Facility | Weather
SCE | 2019-10-23 | 15:12 | 34.4614 | -119.2805 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-942543E | AT&T Communications | 16kV | Capacitor Bank | Overhead | No |  |  | Other |  |  |  | Human Error
SCE | 2019-10-24 | 17:37 | 34.3591 | -119.4417 | Other | Urban | .26 - 9.99 Acres | Unknown |  | OH-1241752E | AT&T Communications | 16kV | Other | Overhead | No |  |  | Other |  |  |  | Human Error
SCE | 2019-10-29 | 7:05 | 34.1021 | -118.693 | Other | Urban | Less Than .25 Acres | Fire Agency | LA County Fire Department | OH-4451326E | Charter Communications/Verizon Wireless | 16kV | Conductor | Overhead | Yes | 2019-10-29 | 7:05 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Other
SCE | 2019-10-30 | 16:37 | 33.8731 | -118.197 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Long Beach Fire Department | OH-GT16891 | FRONTIER COMMUNICATIONS | 16kV | Conductor | Overhead | Yes | 2019-10-30 | 16:37 | Contact From Object |  | Vegetation | Electric Facility | Weather
SCE | 2019-11-01 | 5:01 | 33.909 | -117.9148 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Fullerton Fire Department | OH-1163172E | AT&T Communications | 12kV | Conductor | Overhead | Yes | 2019-11-01 | 5:01 | Contact From Object |  | Vegetation | Electric Facility | Other
SCE | 2019-11-03 | 10:42 | 34.0927 | -118.1447 | Other | Urban | Less Than .25 Acres | Fire Agency | Montebello Fire Department | OH-1643445E | NA | 66kV | Lightning Arrestor | Overhead | No |  |  | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown
SCE | 2019-11-04 | 6:46 | 33.9001 | -116.8943 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-256824S | NA | 33kV | Conductor | Overhead | Yes | 2019-11-04 | 6:46 | Equipment/Facility Failure | Conductor |  |  | Weather
SCE | 2019-11-12 | 16:44 | 33.8756 | -117.5884 | Other | Urban | Less Than .25 Acres | Fire Agency | Corona Fire Department | OH-1577081E | AT&T Communications | 12kV | Conductor | Overhead | Yes | 2019-11-12 | 16:44 | Contact From Object |  | Animal | Pole | Other
SCE | 2019-11-19 | 8:56 | 36.1552 | -119.2317 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-4037849E | NA | 12kV | Transformer | Overhead | Yes | 2019-11-19 | 8:56 | Contact From Object |  | Animal | Electric Facility | Other
SCE | 2019-11-01 | 11:58 | 34.2804 | -119.1992 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-1604403E | NA | 66kV | Conductor | Overhead | Yes | 2019-11-01 | 11:58 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2019-11-04 | 15:45 | 34.2989 | -119.1891 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-4423100E | NA | 66kV | Conductor | Overhead | Yes | 2019-11-04 | 15:45 | Contamination |  |  |  | Other
SCE | 2019-12-22 | 22:00 | 34.119 | -118.0902 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Gabriel Fire Department | OH-819824E | AT&T Communications | 16kV | Conductor | Overhead | Yes | 2019-12-22 | 22:00 | Equipment/Facility Failure | Insulator |  |  | None
SCE | 2019-07-25 | 18:28 | 34.5834 | -118.0829 | Building | Rural | Less Than .25 Acres | Fire Agency | LA County Fire Department | OH-878158E | AT&T Communications | 12kV | Conductor | Overhead | Yes | 2019-07-25 | 18:29 | Vandalism/Theft |  |  |  | Other
SCE | 2019-04-24 | 16:40 | 37.639134 | -118.858774 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-424080S | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown
SCE | 2019-04-26 | 14:58 | 34.085480 | -117.043836 | Other | Urban | Less Than .25 Acres | Fire Agency | San Bern. Fire Department | OH-2260760E | NA | 33kV | Conductor | Overhead | Yes | 2019-04-26 | 14:58 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2019-05-19 | 16:07 | 34.166717 | -116.38078 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bern. Fire Department | OH-4742005E | Time Warner | 25kV | Conductor | Overhead | Yes | 2019-05-19 | 16:07 | Contact From Object |  | Other | Electric Facility | Unknown
SCE | 2019-06-02 | 0:17 | 36.204627 | -119.088919 | Building | Rural | Less Than .25 Acres | Fire Agency | Lindsay Fire Department | OH-1895676E | NA | 12kV | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Unknown
SCE | 2019-06-22 | 11:19 | 36.050082 | -119.021493 | Vegetation | Rural | Less Than .25 Acres | Unknown |  | OH-1635225E | NA | 12kV | Conductor | Overhead | Yes | 2019-06-22 | 11:19 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2019-07-04 | 10:34 | 35.608053 | -117.679403 | Other | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4177498E | NA | 12kV | Conductor | Overhead | Yes | 2019-07-04 | 10:34 | Wire-Wire Contact |  |  | Electric Facility | Unknown
SCE | 2019-07-23 | 13:22 | 33.722559 | -117.293662 | Other | Urban | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-4403978E | FRONTIER COMMUNICATIONS | 12kV | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown
SCE | 2019-07-26 | 16:45 | 34.652558 | -118.076532 | Other | Rural | Less Than .25 Acres | Fire Agency | LA County Fire Department | OH-4040460E | NA | 12kV | Conductor | Overhead | Yes | 2019-07-26 | 16:45 | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2019-07-27 | 12:02 | 34.493200 | -117.573065 | Other | Rural | Less Than .25 Acres | Unknown |  | OH-2122305E | NA | 12kV | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  | Electric Facility | Unknown
SCE | 2019-09-07 | 17:36 | 33.766729 | -117.22938 | Other | Rural | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-4112261E | NA | 12kV | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown
SCE | 2019-09-24 | 14:50 | 34.157427 | -117.344169 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bern. Fire Department | OH-4809453E | NA | 4kV | Conductor | Overhead | Yes | 2019-09-24 | 14:50 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2019-10-08 | 8:22 | 34.137645 | -118.028901 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Arcadia Fire Department | OH-4757377E | AT&T Communications | 16kV | Conductor | Overhead | Yes | 2019-10-08 | 8:22 | Contact From Object |  | Vegetation | Electric Facility | Unknown
SCE | 2019-11-24 | 11:40 | 33.7412 | -117.1549 | Other | Urban | Less Than .25 Acres | Fire Agency | CAL Fire | M15-T2 | NA | 33kV | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Unknown
SCE | 2019-11-29 | 13:02 | 34.443255 | -119.76964 | Other | Urban | Less Than .25 Acres | Unknown |  | OH-1453784E | Crown Castle | 16kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Unknown
SCE | 2019-06-13 | 12:00 | 36.083424 | -119.023454 | Building | Rural | Less Than .25 Acres | Unknown |  | OH-1687439E | Charter Communications | 12kV | Meter | Overhead | No |  |  | Vandalism/Theft |  |  | Electric Facility | Human Error
SCE | 2019-06-15 | 16:54 | 34.0078 | -117.9515 | Other | Urban | Less Than .25 Acres | Unknown |  | N/A | NA | 66kV | Conductor | Overhead | No |  |  | Contact From Object |  | Balloons | Electric Facility | Other
Note on A1: Name of utility reporting the event Highlights: Green-data is complete and should be reported. Red/Pink-data is incomplete, and unknown if should be reported. Gray-data set should be excluded.
Note on A2: Name of utility reporting the event Highlights: Green-data is complete and should be reported. Red/Pink-data is incomplete, and unknown if should be reported. Gray-data set should be excluded.
Note on B2: Date the event started (Use MM/DD/YY when inputting dates)
Note on C2: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on D2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on E2: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on F2: Material involved in the initial fueling of the fire;
Note on G2: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on H2: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on I2: Is who suppressed the fire
Note on J2: If the fire was suppressed by a fire agency or agencies, insert the lead agency when one or more agency was involved
Note on K2: Utility’s description of the pole and/or equipment involved.
Note on L2: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on M2: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on N2: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on O2: The equipment involved in the event (overhead, padmounted or subsurface);
Note on P2: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on Q2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on R2: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on S2: The suspected cause of the ignition;
Note on T2: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on U2: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on V2: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on W2: Factors that contributed to the ignition;