## OP & Near Hits Data
Columns Removed due to Confidential Nature - Point Description/Locations, Descriptions
Data can be provided to CPUC upon request.
OP/Near Hit? | CAP# | TELVENT Point Name | Division | Date | Inlet MAOP | Max Value | MAOP Value | Pressure Difference | Percent over MAOP | Primary Event Category | HU / EQ | Clearance or Maintenance? | P | Secondary Event Category | Old Event Category | Apparent Cause | Simplified cause (OP Events) | Constrained system | Clearance | Exposure Rank (High/Low) | Exceeded MOP? | Capture Type | Corrective/Future Planned Actions | Region | Group | LP > 14, Trans>MOP+3, HP>MOP | Gas Log Event | HIS Name | Transmission/ Distribution | Year | Month | Specific OP Metric Group | Large/Small OP Event | Clearance number | Study Group | Avoid by lower setpoints | Quarter | At Compr Stn or Storage | Clearance Time Approval Days | Released to operations (Installed) | Report Final Date | Mooney Regs involved (root or contributing causes)? | HU | Borescope/ Debris | RCE | Slam shut activation? | Tranche | LCC | Runs | FLOC | Operating Diagram | Working Reg Setpoints (psig) | Primary OPP Setpoints (psig) | Secondary OPP Setpoints (psig)
OP | 128045607 | YO_PAT_RN20 | Yosemite | 2024-01-12 14:32 | 890 | 61.88 | 60 | 1.88 | 3.133% | Gas Contaminants – Debris | EQ |  | P5 |  |  |  | Regulation failed due to debris in the station piping and equipment. Slam shut activated as intended to prevent further pressure exceedance. Slam shut activation | [5 empty] | • Perform internal inspection and shut in the run. • Borescoped and cleaned lead run. • Monitor setpoints were reduced (to 46 psig) which allow more operating room between MAOP and equipment. • Removed strainer gaskets before returning to service. (And submit MPR for damaged strainer gasket.) | [5 empty] | HP Distribution |  |  |  | Small OP Event |  |  | Yes |  | No | [5 empty] | Yes | No | Yes | Distribution - DREG | Yes | H-14 | #N/A
OP | 128078573 | FAI_PT0002 | Stockton | 2024-01-22 | 365 | 107.4 | 90 | 17.4 | 19.33% | Maintenance Operations Quality | HU | M | P50.2 |  |  |  | Regulation failed to perform as intended - as performing maintenance created a dead end / low flow system that was not gauged. | [5 empty] | • Leak Survey completed on 1/23/24. No leaks found. • Clearance initiated for transmission station (HP-31) outlet pressure reduction to 62 psig (lead) and 58 psig (lag). • GPOM will perform another class A-inspection prior to pressure reduction. • TROP (G4# 80008010) to lower MAOP from 90 psig to 72 psig. | [5 empty] | Transmission |  |  |  | Large OP Event |  |  | Yes |  | No | [5 empty] | No | Yes | No | Transmission - Simple | No | H-14 | #N/A
Near Hit | 128171073 | MiniAT | Kern | 2024-02-12 | 465 | 471.1 | 720 | -248.9 | -34.57% | Failure Equipment | EQ |  | P5 |  |  |  | Meter set backpressure and valve leakage resulted in the pressure increase. Set was originally designed and has an MAOP of 720 psig | [5 empty] | • GPOM reduced pressure to 240 psig. • MAOPE has been engaged to determine of the MAOP is higher than 465 psig on the operating diagram. MAOPE determined the MAOP is 720 psig and will process the paperwork. • FIMP to work with GPOM to lower token relief valve setpoint as needed. | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | No | Transmission - LVC | Yes | H-15 | #N/A
OP | 128198144 | YO_TUR_RT12 | Yosemite | 2024-02-16 | 890 | 60.458 | 60 | 0.458 | 0.7633% | Gas Contaminants - Sulfur | EQ |  | P5 |  |  |  | Regulation failed to control pressure due to sulfur in the station equipment. | [5 empty] | GPOM made area safe, completed class inspection B, and returned station to service. Engineering to review maintenance history for additional maintenance recommendations. | [5 empty] | HP Distribution |  |  |  | Small OP Event |  |  | No |  | No | [5 empty] | No | No | No | Distribution - DREG | No | H-14 | #N/A
Near Hit | 128221263 | FR_FRE_RGS3 | Fresno | 2024-02-15 17:10 | 650 |  |  | 0 | #DIV/0! | Slam Shut Activation | EQ |  | P5 |  |  |  | Slam shut activation | [5 empty] | Investigate the spurious activation Engage GSP to load shift so FGLC has more take away than it currently does. | [5 empty] | HP Distribution |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Distribution - DREG | No | H-14 | #N/A
OP | 128243445 | S2M_PT0029 ; S2M_PT0031; S2M_PT0032; S2M_PT0033 | Sacramento | 2024-03-05 | 412 | 244.8 | 240 | 4.8 | 2% | Maintenance Operations Quality | HU |  | P5 |  |  |  | Technician inadvertently placed wrong valve in local control. | [5 empty] | • GPOM technician immediately recognized the issue and made actions to correct the pressure increase. • Station was returned to safe operation. • GPOM to discuss lesson learned and review clearance procedure before continuing work. | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | No |  | No | [5 empty] | No | No | No | Transmission - Complex | No | H-19 | GT.STAT.COMP.MCDONLDISL
Near Hit | 128352549 | SA_WIN_PT021 | Sacramento | 2024-03-21 | 975 | 111 | 125 | -14 | -11.2% | Slam Shut Activation | EQ |  | P5 |  |  |  | Slam Shut Activation | [5 empty] | • Slam Shut set points were adjusted 127 psig & 132 psig in compliance with 4125P-07. • Team set out a data recorder and will review information once it is picked up. | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - Simple | No | H-14 | #N/A
Near Hit | 128365291 | MI_ERE_ER11 | Yosemite | 2024-03-23 | 175 |  | 60 | -60 | -100% | Slam Shut Activation | EQ |  | P5 |  |  |  | Customer Shutdown | [5 empty] | TRVs installed in 2021 Regulation was replaced in 2022, with slam shuts installed Scheduled to be rebuilt in 2025 | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | H-15 | #N/A
Near Hit | 128466871 | ST_TRA_M001 | Stockton | 2024-04-05 10:34 | 890 |  | 60 | -60 | -100% | Slam Shut Activation | EQ |  | P5 |  |  |  | Customer Shutdown | [5 empty] | mitigation | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | H-15 | #N/A
Near Hit | 128466838 | YO_MAD_RB42 | Yosemite | 2024-04-05 12:01 |  |  |  | 0 | #DIV/0! | Slam Shut Activation | EQ |  | P5 |  |  |  | Slam shut activation | [11 empty] | HP Distribution |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Distribution - DREG | No | H-14 | #N/A
OP | 128617796 | YO_LBN_M003_PT2 | Yosemite | 2024-04-22 | 890 | 540.6 | 500 | 40.6 | 8.12% | Maintenance Operations Quality | HU |  | P5 |  |  |  | Regulation failed to control pressure during maintenance. | [5 empty] | Regulation failed to control pressure during maintenance. | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | No |  | No | [5 empty] | No | No | No | Transmission - LVC | Yes | H-15 | #N/A
Near Hit | 128716023 | YO_ATW_M001 | Yosemite | 2024-05-04 |  |  |  | 0 | #DIV/0! | Slam Shut Activation | EQ |  | P5 |  |  |  | Failure - Equipment | [5 empty] | GPOM to investigate and reset SS 7/10/24 CAPS are submitted for tracking and trending purposes for slam shut activations. To a certain extent they document the number of potential overpressure events that were prevented with installing the equipment, and document the potential end of life for the equipment (if these occur with higher frequency, it could be a malfunction of the equipment). Closed for trending. | [5 empty] | Transmission |  |  |  | Near Hit |  |  | N/A |  | No | [5 empty] | N/A | No | Yes | Transmission - LVC | Yes | H-14 | #N/A
Near Hit | 128726729 | DI_ANT_RA05 | Diablo | 2024-05-07 | 573 |  | 58 | -58 | -100% | Slam Shut Activation | EQ |  | P5 |  |  |  | Moisture identified | [5 empty] | Station was rebuilt, and ss were installed with the new design in 2020. The has requested information about the SS if it was manufactured with the thru hole, and will add to the list if it needs a retrofit. Consider looking at other stations installed/rebuilt in this timeframe to understand if there are more new stations with a similar issue. | [5 empty] | HP Distribution |  |  |  | Near Hit |  |  | N/A |  | No | [5 empty] | N/A | No | Yes | Distribution - DREG | Yes | H-14 | #N/A
Near Hit | 129028216 | ST_ION_M001 | Stockton | 2024-06-05 | 300 |  | 60 | -60 | -100% | Slam Shut Activation | EQ |  | P5 |  |  |  | Customer Shutdown | [5 empty] | GPOM to investigate and reset SS | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | LVC | #N/A
OP | 129054236 | YO_MAD_M003_PT2 | Yosemite | 2024-06-08 | 400 | 418.1 | 400 | 18.1 | 4.525% | Thermal Expansion | EQ |  | P5 |  |  |  | Thermal expansion | [5 empty] | GPOM relieved high-pressure gas and performed a class A inspection. Regulation Engineering to review equipment modifications. MAOP Engineering to review records for a potential MAOP correction. | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | No |  | No | [5 empty] | No | No | No | Transmission - LVC | Yes | LVC | #N/A
Near Hit | 129108449 | N/A | Central Coast | 2024-06-21 | 303 | 60 |  | 60 | #DIV/0! | Failure - Equipment | EQ |  | P5 |  |  |  | Regulation failed to control pressure - bypass valve tampering, rupture disk. | [5 empty] | We treated the restoration like an OP. We rebuilt the farm tap, removed the hard bypass and created a soft bypass. We restored the line, pressure tested the line and leak surveyed upon completion. M&C will tailboard there teams about what happened and the potential problems. Here is where we can learn from this .. If M&C has a question, please call us, we welcome it. Never feel your alone, if your nervous call and we will help, doesn't have to be an emergency. We are your brothers and sisters . If it is near a GPOM asset, but on a distribution side, Gas Control should call both M&C and GPOM . If you arrive on scene, and find that you are near a GPOM asset, please call for our support. Not only because it is ours, but we may have more information on the site that will be useful . If the situation is safe to do so(read, not life or property threatening), allow a GPOM rep to show up and operate the assets, we are all here for each other . If it is an unsafe situation(very rare life threatening situations) that needs immediate action, then the following steps should be taken (never reg set's) o Call GPOM, if we can't arrive in a safe amount of time, we can walk you through all the steps o Ensure proper oq's o Have gas control give proper instructions if applicable o Gauge up, and document and watch pressure o Close the Outlet valve, downstream valve to isolate o Call GPOM, for follow up response . If it looks like it was tampered with, let us know and we will correct it these are the recommendations we came up with. | [5 empty] | Distribution |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | No | Distribution - FTAP | Yes | H-10 | #N/A
OP | 129167598 | YO_MAD_M003_PT2 | Yosemite | 2024-06-28 | 400 | 403.1 | 400 | 3.1 | 0.775% | Thermal Expansion | EQ |  | P5 |  |  |  | Thermal expansion | [5 empty] | GPOM relieved high-pressure gas and performed a class A inspection. Regulation Engineering to review equipment modifications. MAOP Engineering to review records for a potential MAOP correction. | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | No |  | No | [5 empty] | No | No | No | Transmission - LVC | Yes | LVC | #N/A
Near Hit | 129159375 | ST_TRA_M003 | Stockton | 2024-07-02 | 1040 | 60 |  | 60 | #DIV/0! | Slam shut activation | EQ |  | P5 |  |  |  | Slam shut activation | [5 empty] | GPOM to investigate and reset SS 7/10/24 CAPS are submitted for tracking and trending purposes for slam shut activations. To a certain extent they document the number of potential overpressure events that were prevented with installing the equipment, and document the potential end of life for the equipment (if these occur with higher frequency, it could be a malfunction of the equipment). Closed for trending. | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | LVC | #N/A
OP | 129175542 | YO_LBN_M003_PT2 | Yosemite | 2024-07-04 | 890 | 550.03 | 500 | 50.03 | 10.01% | Failure - Equipment | EQ |  | P5 |  |  |  | Regulation Failed to control pressure | [5 empty] | • GPOM technician responded and made area safe. • Leak survey has been scheduled. • PLE reviewing TROP requirements. looking to potentially install a TRV downstream of the primary regulation - PT3 Low Alarm setting was lowered from 77 to 74 psig (its downstream of all equipment, but still results in GPOM callouts during operation). | [5 empty] | Transmission |  |  |  | Large OP Event | 17121 |  | No |  | No | [5 empty] | No | Yes | No | Transmission - LVC | Yes | LVC | #N/A
Near Hit | 129204341 | MI_ERE_ER11 | Yosemite | 2024-07-09 | 175 |  | 60 | -60 | -100% | Slam shut activation | EQ |  | P5 |  |  |  | Customer Shutdown | [5 empty] | GPOM to investigate and reset SS 7/10/24 CAPS are submitted for tracking and trending purposes for slam shut activations. To a certain extent they document the number of potential overpressure events that were prevented with installing the equipment, and document the potential end of life for the equipment (if these occur with higher frequency, it could be a malfunction of the equipment). Closed for trending. | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | LVC | #N/A
Near Hit | 129350132 | ST_ION_M001 | Stockton | 2024-08-06 | 300 |  | 60 | -60 | -100% | Slam shut activation | EQ |  | P5 |  |  |  | Customer Shutdown | [5 empty] | Slam shut tripped around 2:36pm. Pressure trend equipment did not pick up a pressure spike but customer is known for hard stops (tripped slam shut 2 months back). When gpom arrived on site, they could still hear gas flowing and identified the bypass as the source flow. Bypass had 2 valves and reg with slam shut. We had them perform functionality checks on the main run including slam shut seal. All equipment worked as advertised. When performing the inspection on bypass equipment, they found both bypass valves leakby. We had Gpom confirmed the slam shut on the bypass reg sealed when tripped to act as an isolation point until we can replace the bypass valves. The delivery pressure is 20#. MAOP is 300# and H alarm is 135#. Gpom is required to respond to the 135# if activated. Tonight we feel comfortable sending gpom home until we can replace the valves. We spoke with Shane and he agreed with plan tonight. Our next steps will be to hand this off to PLE to get a job together to replace the valves. Hien and I are considering a slam shut set point change to a higher value to reduce unwarranted activations need to understand costumer equipment/piping limitations. Fingers crossed the RE or Gary have this insight. | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | LVC | #N/A
OP | 129372897 | ST_LOD_RL43_PT3 | Stockton | 2024-08-10 | 412 | 60.142 | 60 | 0.142 | 0.2367% | Gas Contaminants - Debris | EQ |  | P5 |  |  |  | Debris (metallic) was found on the regulator diaphragm | [5 empty] | • Rubber goods replaced • Borescope inspection on both runs •Engineering to review lowering the outlet setpoints and alarm setpoints | [5 empty] | Distribution |  |  |  | Small OP Event |  |  | Yes |  | no | [5 empty] | Yes/Yes | No | No | Distribution - DREG | No | H-14 | #N/A
Near Hit | 129406621 | SSD_PT0003 | Sacramento | 2024-08-15 | 975 | 866 | 720 | 146 | 20.28% | Failure - Equipment | EQ |  | P5 |  |  |  | Regulation Failed to control pressure | [5 empty] | NOT AN OP EVENT - Customer Owned and Operated Regulation System | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | No | Transmission - LVC | Yes | LVC | #N/A
OP | 129437051 | AIS5362 | Central Coast | 2024-08-25 | 390 | 131.57 | 130 | 1.57 | 1.208% | Failure - Equipment | EQ |  | P5 |  |  |  | Leak-by on bypass valve during no flow condition | [5 empty] | Internal inspection of regulation equipment Replaced rubber goods Calibrated MiniAT Packed bypass plug valve with grease Lowered LVCR set points | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | No |  | No | [5 empty] | No | No | No | Transmission - LVC | Yes | LVC | #N/A
OP | 129437899 | YO_FRB_M001 | Yosemite | 2024-08-24 | 620 | 60.53 | 60 | 0.53 | 0.8833% | Failure - Equipment | EQ |  | P5 |  |  |  | Regulators could not control pressure during the customer rapid shutoff. | [5 empty] | GPOM technician responded and made area safe. Regulation equipment was internally inspected with rubber components replacement. Regulation Engineering to review equipment for potential setpoint reduction. | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | No |  | No | [5 empty] | No | No | No | Transmission - LVC | Yes | LVC | #N/A
Near Hit | 129490524 | ST_TRA_M001 | Stockton | 2024-09-03 | 890 |  | 60 | -60 | -100% | Slam shut activation | EQ |  | P5 |  |  |  | Customer startup/shutdown | [11 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | LVC | #N/A
Near Hit | 129490527 | ST_TRA_M001 | Stockton | 2024-09-05 | 890 |  | 60 | -60 | -100% | Slam shut activation | EQ |  | P5 |  |  |  | Tech found sulfur in the controller on the primary and replaced pilot | [5 empty] | Tech found sulfur in the controller on the primary and replaced pilot | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | LVC | #N/A
OP | 129544084 | SMS_PT0005 | Sacramento | 2024-09-17 | 800 | 154.4 | 150 | 4.4 | 2.933% | Failure - Equipment | EQ |  | P5.1 |  |  |  | Morning Star operations resulted in an inadvertent pressure increase. | [5 empty] | • GPOM to submit MPR on the broken main spring of the slam shut. The spring will be replaced prior to returning the run to service. • Installing strainer gasket upstream of regulation for debris capture. | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | 1 | #N/A
Near Hit | 129557609 | SA_DVS_RD06 | Sacramento | 2024-09-19 | 792 |  | 60 | -60 | -100% | Slam shut activation | EQ |  | P5 |  |  |  | Slam shut activation | [5 empty] | - New slam shut installed - not clear what caused the issue to the result in ss activation - minimumal load, which caused the PF Monitor come into control -station loading/sp might be fighting eachother | [5 empty] | Distribution |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | Yes | Distribution- DREG | No | H-14 | #N/A
Near Hit | 129614915 | ST_FCP_RM47 | Stockton | 2024-09-14 |  | 55.484 | 60 | -4.516 | -7.527% | Gas Contaminants - Sulfur | EQ |  | P5 |  |  |  | Regulation failed to control pressure due to sulfur in the station equipment. | [5 empty] | GPOM investigated station | [5 empty] | Distribution |  |  |  | Near Hit |  |  | No |  | No | [5 empty] | No | No | No | Distribution - DREG | No | H-14 | #N/A
OP | 129786957 | SI_WMS_M001 | Sierra | 2024-10-26 | 800 | 53.46 | 50 | 3.46 | 6.92% | Failure - Equipment | EQ |  | P50.1 |  |  |  | Wadham Energy operations resulted in an inadvertent pressure increase. | [5 empty] | • GPOM inspected meter set and found no issue. • FIMP/MTCL to check why MAOP alarm was not communicating to Gas Control. • GPOM/PLE to evaluate increase downstream MAOP | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | Yes |  | no | [5 empty] | no | No | Yes | Transmission - LVC | Yes | LVC | #N/A
Near Hit | 129805964 | SI_WMS_M001 | Sierra | 2024-11-12 | 800 | 36 | 50 | -14 | -28% | Slam shut activation | EQ |  | P5 |  |  |  | Slam shut activation | [5 empty] | GPOM investigated station | [5 empty] | Transmission |  |  |  | Near Hit |  |  | no |  | no | [5 empty] | no | No | Yes | Transmission - LVC | Yes | LVC | #N/A
OP | 129807759 | SI_WMS_M001 | Sierra | 2024-11-12 16:12 | 800 | 50.3 | 50 | 0.3 | 0.6% | Failure - Equipment | EQ | [5 empty] | Wadham Energy operations resulted in an inadvertent pressure increase. | [5 empty] | • GPOM inspected meter set and found no issue. • GPOM reduced the slam shut set point to 42 psig. | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | Yes |  | no | [5 empty] | no | No | Yes | Transmission - LVC | Yes | LVC | #N/A
Near Hit | 129808607 | N/A | Kern | 2024-11-12 09:12 | 465 |  |  | 0 | #DIV/0! | 3rd Party - Equipment | HU | [5 empty] | Third-party vandalism | [5 empty] | -station has scheduled rebuild - consider gaurds, and updating the security on site | [5 empty] | Transmission |  |  |  | Near Hit |  |  | No |  | no | [5 empty] | no | No | No | Transmission - | No | H-14 | #N/A
OP | 129847840 | EB_BER_M001 | East Bay | 2024-11-19 | 150 | 132.25 | 99 | 33.25 | 33.59% | Maintenance Operations Quality | HU | [5 empty] | Regulation failed to control while performing maintenance inspection. | [5 empty] | Replaced rubber goods Remove dual long line Establish maintenance during flowing conditions Leak survey | [5 empty] | Transmission |  |  |  | Large OP Event | 17322.02 |  | No |  | no | [5 empty] | no | Yes | No | Transmission - LVC | Yes | LVC | #N/A
OP | 129861503 | `YHB_PT0003 | Yosemite | 2024-11-20 | 1440 | 425.3 | 400 | 25.3 | 6.325% | Clearance Execution | HU | [5 empty] | Valving operations during the clearance execution resulted in creating a bottled section. | [5 empty] | • GPOM isolated the biomethane skid from the customer and performed equipment checks. • Stand-down/Continue to perform steps for the TROP clearance 80267001. | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | No |  | no | [5 empty] | No | No | No | Transmission - Biomethane | No | BIO | #N/A
OP | 129854898 | Gauge pressure | Rio Vista | 2024-11-15 | 795 | 756 | 650 | 106 | 16.31% | Failure - Equipment | EQ | [5 empty] | Potential leakage across a valve into a bottled section. | [5 empty] | • Leak survey is currently scheduled. • Clearance in process to reduce pressure on L-210A and identify the source of gas that caused the overpressure. • There is a planned retirement project for the section of L-210A (R-1594 L-210A MP 0.00-1.36 Retire Pipe). ACE to determine extent of condition | [5 empty] | Transmission |  |  |  | Large OP Event |  |  | No |  | no | [5 empty] | No | Yes | No | Transmission - Complex | No | H-19 | #N/A
OP | 129860288 | KT2_PT0100A | Kern | 2024-11-23 | 867 | 662 | 660 | 2 | 0.303% | Failure - Equipment | EQ | [5 empty] | Electrical failure of station power & K-4 Compressor control panel malfunction resulted in the pressure increase on the suction piping. | [5 empty] | • Local technicians fixed an electrical failure found on P-3. • Topock Station was shut-in until the loss of supply from Kinder Morgan could be resolved. • K-4 remains off until the cause can be evaluated. | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | No |  | Yes | [5 empty] | No | No | No | Transmission - Complex | No | H-19 | #N/A
Near Hit | 129860254 | MI_ERE_ER11 | Yosemite | 2024-11-23 | 175 | 58.38 | 60 | -1.62 | -2.7% | Slam shut activation | EQ |  | P5 |  |  |  | Customer Shutdown | [5 empty] | GPOM crew restored the customer within the hour. | [5 empty] | Transmission |  |  |  | Near hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | LVC | #N/A
Near Hit | 129896275 | YO_HLM_M001 | Yosemite | 2024-12-04 | 400 |  |  | 0 | #DIV/0! | Slam shut activation | EQ |  | P5 |  |  |  | The slam shut may not have full been reset during the return to service efforts. | [5 empty] | Dispatch tech to investigate | [5 empty] | Transmission |  |  |  | Near hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | LVC | #N/A
Near Hit | 130537563 | MI_ERE_ER11 | Yosemite | 2024-12-14 | 175 |  |  | 0 | #DIV/0! | Slam shut activation | EQ |  | P5 |  |  |  | Customer Shutdown | [5 empty] | Dispatch tech to investigate | [5 empty] | Transmission |  |  |  | Near hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | LVC | #N/A
Near Hit | 130537566 | EB_BER_M001 | East Bay | 2024-12-19 | 150 |  |  | 0 | #DIV/0! | Maintenance Operations Quality | HU |  | P5 |  |  |  | Set Points were not returned to updated numbers after maintenance | [5 empty] | CAP# 130533371 has been created to review all 2024 set point clearances executed in EB GPOM, to ensure all associated maintenance documents reflect accurate data. Point will be removed from MiniAT | [5 empty] | Transmission |  |  |  | Near hit |  |  | No |  | No | [5 empty] | No | No | No | Transmission - LVC | Yes | LVC | #N/A
Near Hit | 130541087 | SJ_GIL_M002_PT3 | San Jose | 2024-12-19 | 400 |  |  | 0 | #DIV/0! | Maintenance Operations Quality | HU |  | P5 |  |  |  | Incorrect Operation | [5 empty] | GPOM to conduct investigation & to determine if commissioning guidance is needed in the TIL. | [5 empty] | Transmission |  |  |  | Near hit |  |  | No |  | No | [5 empty] | No | No | No | Transmission - LVC | Yes | 2 | #N/A
Near Hit | 130537601 | MI_ERE_ER11 | Yosemite | 2024-12-24 | 175 |  |  | 0 | #DIV/0! | Slam shut activation | EQ |  | P5 |  |  |  | Customer Shutdown | [5 empty] | Dispatch tech to investigate Gas Trans Event Final Epage on 12-24-24 07:52 hrs. 554 S. Yosemite Ave. OAKDALE . Activation of pipeline safety device- Slam Shut. Customer impact unknown. Slam Shut Activation at CONAGRA, Tech enroute to investigate. Station returned to normal operation. . No additional information to follow. Event Closed pgemapsplus://maps/location?latitude=37.7602880000&longitude=-120.8429050000 | [5 empty] | Transmission |  |  |  | Near hit |  |  | No |  | No | [5 empty] | No | No | Yes | Transmission - LVC | Yes | LVC | GT.STAT.COMP.TOPOCK____
OP | 130540840 | BN2_PT0006 | Tracy District | 2024-12-25 | 890 | 158.46 | 150 | 8.46 | 5.64% | Gas Contaminants - Sulfur | EQ |  | P5 |  |  |  | Tech found sulfur on the controling regulator boot | [5 empty] | Replacement of rubber goods Lowered outlet pressure from 143 psig to 140 psig. Reevaluation of alarm and pressure control set points | [5 empty] | Transmission |  |  |  | Small OP Event |  |  | Yes |  | No | [5 empty] | No | No | No | Transmission | No | 2 | #N/A
OP | 130573931 | NV_RBL_R112_PT3 | North Valley | 2024-12-30 | 911 | 60.98 | 60 | 0.98 | 1.633% | Failure - Equipment | EQ |  | P5 |  |  |  | Pilot vent iced shut | [5 empty] | • Internal inspection of regulation equipment. • Increased pilot vent sizing. | [5 empty] | Distribution |  |  |  | Small OP Event |  |  | No |  | No | [5 empty] | No | Yes | Yes | Distribution - DReg | No | 2 | #N/A
GD.STAT.LPRS.00208
GD.STAT.LPRS.00209
GD.STAT.LPRS.00209
GD.STAT.LPRS.00208
GD.STAT.LPRS.00151
GD.STAT.LPRS.00208
GD.STAT.LPRS.00208
GD.STAT.LPRS.00154
[50 empty] | GT.STAT.COMP.MCDONLDISL |  | 467 | 480
[50 empty] | GT.STAT.LVCR.0000000523 |  | LVC
[50 empty] | GT.STAT.LVCR.0000000105 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Mer\Tif\Gas\REGSTATION\0805204.PDF | 45 | 55
GT.STAT.MISC.HILLSTRPLS_
[50 empty] | GT.STAT.MISC.SPCKLSPLS_ |  | 145 | 155
GT.STAT.LVCR.0000000105
[50 empty] | GT.STAT.LVCR.0000000105 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Mer\Tif\Gas\REGSTATION\0805204.PDF | 45 | 50
[50 empty] | GT.STAT.LVCR.0000000231 |  | 200 | 215
[50 empty] | GT.STAT.LVCR.0000000231 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0810923.pdf
[50 empty] | GD.STAT.DIST.01594 | 385158.pdf | 54 | 58
[50 empty] | GT.STAT.LVCR.0000000232 |  | 150 | 170
[50 empty] | GT.STAT.MISC.SPCKLSPLS_ |  | 130 | 140
[50 empty] | GT.STAT.MISC.SPCKLSPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\085533.pdf
[50 empty] | GT.STAT.MISC.AMADORSTAT | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\085551.pdf
[50 empty] | GT.STAT.MISC.PANOCHPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\284100.pdf
[50 empty] | GT.STAT.MISC.CUMMINGSCK | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\082474.pdf
[50 empty] | GT.STAT.MISC.HILLSTRPLS_ | 282255.pdf
[50 empty] | GT.STAT.MISC.PANOCHPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\284100.pdf
[50 empty] | GT.STAT.MISC.PANOCHPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\284100.pdf
[50 empty] | GT.STAT.MISC.FAIRFIELDS | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\183969.pdf
\\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\081622.pdf
[50 empty] | GT.STAT.MISC.NSACHOLDER | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\382860.pdf
[50 empty] | GD.STAT.DIST.01090 | \\fairfield07\gis\giswebMiscFiles\GasStations\385186.pdf
[50 empty] | GT.STAT.MISC.NSACHOLDER | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\382860.pdf
[50 empty] | GT.STAT.MISC.PANOCHPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\284100.pdf
[50 empty] | GT.STAT.MISC.PANOCHPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\284100.pdf
[50 empty] | GT.STAT.MISC.ANTGSTPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\4807103.pdf
[50 empty] | GT.STAT.MISC.ANTGSTPLS_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\4807103.pdf
[50 empty] | GT.STAT.MISC.LAMONTMTRS | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0806461.pdf
[50 empty] | GT.STAT.MISC.HILLSTRPLS_ | 282255.pdf
[50 empty] | 0 |  | 45 | 50 | 53
[50 empty] | GT.STAT.MISC.HILLSTRPLS_ | 282255.pdf
[50 empty] | GT.STAT.LVCR.0000000258 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0806404.pdf
GD.STAT.DIST.00203
[50 empty] | GT.STAT.LVCR.0000000258 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0806404.pdf
[50 empty] | GT.STAT.LVCR.0000000125 |  | 115 | 125
[50 empty] | GT.STAT.MISC.BYRONTAPRG | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\083679.pdf | 145 | 160
GT.STAT.MISC.ASHLANGARF
[50 empty] | GT.STAT.MISC.RIPONCOGEN; GT.STAT.LVCR.0000000313 |  | 90 | 100 | 115
[50 empty] | GT.STAT.MISC.REDDNGTAP_ | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\183694.pdf
[50 empty] | GT.STAT.LVCR.0000000105 | \\utility.pge.com\projects\metcat\metcatprd-fs01\COMP_PUB\Mer\Tif\Gas\REGSTATION\0805204.PDF | 45 | 50
[50 empty] | GD.STAT.DIST.11140 | 085930.pdf | 54 | 58
GT.STAT.MISC.PANOCHPLS_
[50 empty] | GT.STAT.LVCR.0000000230 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\082445.pdf | 45 | 50
[50 empty] | GT.STAT.LVCR.0000000258 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0806404.pdf | 280 | 310
[50 empty] | 0 |  | 55 | 65
[50 empty] | GT.STAT.LVCR.0000000258 |  | 280 | 310
GD.STAT.DIST.00460
GT.STAT.MISC.KRGTPGEDAG
[50 empty] | GT.STAT.LVCR.0000000230 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\082445.pdf | 80 | 85
GT.STAT.COMP.KETTLEMAN_
GT.STAT.MISC.PANOCHPLS_
[50 empty] | GT.STAT.MISC.HILLSTRPLS_ | 282255.pdf
GT.STAT.MISC.PLS-2A____
[50 empty] | GD.STAT.DIST.00930 |  | SS
[50 empty] | GD.STAT.FTAP.00161 |  | x | x
[50 empty] | GD.STAT.HPRS.10195 | 0804882.pdf | 45 | 50
[50 empty] | 0 |  | 55 | 60
[50 empty] | GD.STAT.DIST.00397 | 0807396.pdf | 53 | 58
[50 empty] | GT.STAT.LVCR.0000000615 |  | 35 | 40
[50 empty] | GT.STAT.LVCR.0000000505 | 0812689.pdf | 120 | 130
[50 empty] | GT.STAT.MISC.HILLSTRPLS_ | 282255.pdf
[50 empty] | GT.STAT.MISC.HLLSTRPLS_ | 282255.pdf | x | x
[50 empty] | GT.STAT.LVCR.0000000685 | 0812720.pdf | 20 | 25
[50 empty] | GT.STAT.LVCR.0000000258 | 0806404.pdf | 280 | 310
[50 empty] | GD.STAT.DIST.00252; GD.STAT.DIST.00241 | 0804616.PDF | x | x
[50 empty] | GT.STAT.MISC.RELIEZREGL | 083692.pdf
[50 empty] | GD.STAT.DIST.00520 | 0806503.PDF | 27 | 29
[50 empty] | GT.STAT.LVCR.0000000251 |  | 225 | 250
[50 empty] | GT.STAT.MISC.FRESNOLOAD | 3808517.pdf | 380 | 395
[50 empty] | GT.STAT.LVCR.0000000251 |  | 225 | 250
[50 empty] | GT.STAT.LVCR.0000000371 | 804741
0
[50 empty] | GD.STAT.DIST.00491 | 809690 | 51 | 56
[50 empty] | GT.STAT.MISC.WLDGSEPLS_ | 0803161.pdf
[50 empty] | GD.STAT.DIST.00687 | 0809232.PDF | 51 | 54 | N/A
[50 empty] | 0 | 0809539.pdf
[50 empty] | 0 |  |  |  | N/A
[50 empty] | GT.STAT.MISC.DIANALRCV_ | 082126.PDF | 230 | 215
[50 empty] | GT.STAT.LVCR.0000000603 | 0812907 | 125 | 130 | 170
[50 empty] | GT.STAT.MISC.LASVNAPLS | 3808137 | 285 | 295 | N/A
[50 empty] | GT.STAT.LVCR.0000000115 | 0809539.pdf | 22 | 34 | 35
[50 empty] | GD.STAT.DIST.11232 - removed? | 0805144.PDF | 30 | 34 | 40
[50 empty] | GT.STAT.LVCR.0000000148 | 0812689.pdf | 45 | 55 | 60
[50 empty] | GT.STAT.LVCR.0000000115 | 0809539.pdf | 22 | 24 | 35
[50 empty] | GT.STAT.LVCR.0000000258 | 0806404 | 338 |  | 390
[50 empty] | GT.STAT.LVCR.0000000505 | 0812689.pdf | 120 | 130 | 137
[50 empty] | GT.STAT.LVCR.0000000115 | 0809539.pdf | 22 | 25 | 30
[50 empty] | GT.STAT.LVCR.0000000109 | 0809533.pdf | 50 | 55 | 57
[50 empty] | 0 | 0809539.pdf
[50 empty] | GD.STAT.DIST.01566 | 0812022.PDF | 20 | 23 | 26
[50 empty] | GT.STAT.LVCR.0000000539 | 0813144 | 280
[50 empty] | GD.STAT.FTAP.04934 |  |  |  | RV
[50 empty] | GD.STAT.DIST.01140 | 0804218.PDF
[50 empty] | GT.STAT.MISC.CONCORDMTR | 0811631.pdf
[50 empty] | GT.STAT.LVCR.0000000170 | 0809592.pdf | 52 | 58
[50 empty] | GD.STAT.DIST.00080 | 0803990.PDF
[50 empty] | GD.STAT.DIST.00024 | 0804102.pdf
[50 empty] | GT.STAT.MISC.TELLISGINR | 0806794.pdf | 220 | 200 | 360
[50 empty] | GD.STAT.DIST.01318 | 0805536.PDF
[50 empty] | GD.STAT.LPRS.00249 | 0805153.PDF
[50 empty] | GD.STAT.DIST.01430 | 0809421.PDF | 50 | 55 | N/A
[50 empty] | GD.STAT.DIST.11205 |  | N/A | N/A
[50 empty] | GD.STAT.DIST.00106 | 0804023.PDF | 31 | 34
[50 empty] | GT.STAT.MISC.HINKLEY_ | 383654.pdf
[50 empty] | GT.STAT.MISC.FRESNOLOAD | 3808517.pdf | N/A | N/A
[50 empty] | GD.STAT.DIST.01164 | 0811598.PDF | 44 | 48
[50 empty] | GT.STAT.LVCR.0000000316 | 0813193.pdf | 110 | 120
GT.STAT.LVCR.0000000152
[50 empty] | GT.STAT.LVCR.0000000125 | 0809549.pdf | 115 | 125 | 140
GD.STAT.DIST.00087
[50 empty] | GT.STAT.LVCR.0000000431 | 0812132.pdf
[50 empty] | GD.STAT.DIST.11139 |  | 54
GD.STAT.LPRS.00272
GT.STAT.LVCR.0000000387
[50 empty] | GD.STAT.DIST.01042 | 0808301.PDF
GD.STAT.LPRS.00075
[50 empty] | GD.STAT.DIST.00702 | 0805154.PDF | 36 | 40 | 37
[50 empty] | GT.STAT.COMP.TOPOCK____ | 383655.pdf
[50 empty] | GD.STAT.LPRS.00179 | 808054 | 8.5" | 10" | 14"
[50 empty] | GT.STAT.MISC.ANTGSTPLS_ | 4807103 | N/A | N/A | N/A
[50 empty] | GT.STAT.LVCR.0000000106 | 809530 | N/A | 130? | 123
[50 empty] | GT.STAT.LVCR.0000000461 | 87572 | 23 | 25 | N/A
[50 empty] | GD.STAT.LPRS.00249 | 805153 | 8.5" | 10"
[50 empty] | GD.STAT.LPRS.00132 | 808913
[50 empty] | GT.STAT.MISC.FIGUERSTAT | 0812779.pdf |  |  | N/A
[50 empty] | GT.STAT.LVCR.0000000633 | 0813627 | 22 | 27 | TBD
[50 empty] | GD.STAT.DIST.00519 | 806502 | 42 | 48 | N/A
[50 empty] | GT.STAT.LVCR.0000000365 | 812805 | 15 | 18 | N/A
[50 empty] | GD.STAT.DIST.00920 |  | 36 | 33 | 42
[50 empty] | GT.STAT.LVCR.0000000125 | 0809549.pdf (pge.com)
[50 empty] | GT.STAT.MISC.HLLSTRPLS_ | 282255
GT.STAT.LVCR.0000000525
GD.STAT.DIST.00160
[50 empty] | GT.STAT.LVCR.0000000633 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0813627.pdf | 20 | 24 | 27
GT.STAT.LVCR.0000000668
[50 empty] | GD.STAT.DIST.11310 | 0814087 (pge.com) | 40 | 58 | 62
[50 empty] | GT.STAT.MISC.ACACIASTRG | 082229.pdf
[50 empty] | GT.STAT.LVCR.0000000435 | 0812916.pdf (pge.com) |  |  | 390
[50 empty] | GD.STAT.DIST.00878 |  | 54 | 58
GD.STAT.DIST.11284
[50 empty] | GT.STAT.MISC.20THMARTIN | 0800151.pdf
[50 empty] | GT.STAT.MISC.PLEASANTCK | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\083596.pdf | 110 | 120 | 129
GT.STAT.LVCR.0000000668
GT.STAT.LVCR.0000000141
GD.STAT.LPRS.00249
GT.STAT.LVCR.0000234
GT.STAT.LVCR.0000000106
GD.STAT.DIST.11201
[50 empty] | GT.STAT.LVCR.0000000611 | \\utility.pge.com\projects\MAOPX\gis\giswebMiscFiles\GasStations\0812909.pdf
GT.STAT.LVCR.0000000651
GD.STAT.FTAP.00075
GT.STAT.LVCR.0000000651
GT.STAT.LVCR.0000000195
[50 empty] | GT.STAT.LVCR.0000000235 |  | 350 | 400
GT.STAT.LVCR.0000000668
GT.STAT.LVCR.0000000611
GD.STAT.DIST.00783
GT.STAT.LVCR.0000000717
[50 empty] | GT.STAT.LVCR.0000000181 | 809603 | 120 | 126
GT.STAT.LVCR.0000000105
GT.STAT.LVCR.0000000141
GT.STAT.LVCR.0000000141
GT.STAT.LVCR.0000000523
[50 empty] | GD.STAT.DIST.01094 |  | 54
GD.STAT.DIST.00799
[50 empty] | GT.STAT.LVCR.0000000115 |  | 22 | 27 | 46
[50 empty] | GT.STAT.LVCR.0000000115 |  | 22 | 27 | 46
[50 empty] | GT.STAT.LVCR.0000000115 |  | 22 | 27 | 42
GT.STAT.MISC.BKRSFDREG_
GT.STAT.LVCR.0000000365
GT.STAT.MISC.CREEDPLS__
GT.STAT.COMP.TOPOCK____
GT.STAT.LVCR.0000000668
GT.STAT.LVCR.0000000149
GT.STAT.LVCR.0000000668
[50 empty] | GT.STAT.LVCR.0000000365 |  | 18 | 21 | 50
GT.STAT.LVCR.0000000572
GT.STAT.LVCR.0000000668
GT.STAT.MISC.NEWMAN
[50 empty] | GD.STAT.DIST.00919 | 807033 | 50 | 55 | 62
Note on N3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See Tab: OP Event Classification
Note on AU3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Slam shut activation - started in 2023
Note on AW3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Low Customer Count - started in 2023
Note on AX3: Singer, Kevin D: N/A - Reg Stations did not contribute to OP Event
Note on E34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 11/7/2024- Date found MAOP Exceeded