## Header
Count of Notification type | Column Labels
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Grand Total
Row Labels
On-Time | 126 | 246 | 941 | 1527 | 1744 | 994 | 117 | 114 | 153 | 111 | 36 | 29 | 6138
Past Due | Column Labels Jan: 44; Column Labels Feb: 80; Column Labels Mar: 226; Column Labels Apr: 217; Column Labels May: 215; Column Labels Jun: 134 | 916
TBC | Column Labels Jul: 55; Column Labels Aug: 52; Column Labels Sep: 138; Column Labels Oct: 172; Column Labels Nov: 180; Column Labels Dec: 103 | 700
Grand Total | 170 | 326 | 1167 | 1744 | 1959 | 1128 | 172 | 166 | 291 | 283 | 216 | 132 | 7754
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | YE
Current % On-Time W/O Projections | 74.12% | 75.46% | 80.63% | 87.56% | 89.03% | 88.12% | 68.02% | 68.67% | 52.58% | 39.22% | 16.67% | 21.97% | 79.16%
Target Percents by Month | 60% | 60% | 60% | 65% | 70% | 75% | 70% | 70% | 75% | 80% | 90% | 90% | 70%
YTD | Jun: 85.89%

## Raw Data
Notification type | Notification No | Technical identification no. | Description | Main work center | Functional Location | Created On | Notification date | Reference date | Open Late | Days | Required End | SOMS DUE Date | Work Type Code | HFTD | XMPT | Priority text | Notification Sytem Status | Notification User Status | Damage Code text | Object Code text | Activity Code text | Order | Order Number Description | MaintActivityType
LC | 127992597 | 004/112 | T2 COLGATE-ALLEGHANY 004/112 RPL POLE | SACTO | ETL.6470.POLE.WOOD | 2024-01-02 | 2024-01-02 | 2024-10-16 | On-Time |  | 2025-01-02 | 2025-01-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35520720 | T2 COLGATE-ALLEGHANY 004/112 RPL POLE | 70Y
LC | 129155112 | 017/151 | T3 MSSRI FLT-GLD HLL#1 17/151 TOUCH | SACTO | ETL.2660.TOWR | 2024-07-02 | 2024-07-02 | 2025-02-21 | Past Due |  | 2025-01-02 | 2025-01-02 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO FRAB NTDE PGEQ BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46460833 | T3 MSSRI FLT-GLD HLL#1 17/151 RPR STRT | ICQ
LC | 127998806 | 000/005 | T2 TOCALOMA TAP_000/005 INS DMPW | LAKEVLLE | ETL.7721.INSL.NCER | 2024-01-03 | 2024-01-03 | 2024-01-03 | Past Due |  | 2025-01-03 | 2025-01-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46271107 | T2 WV TOCALOMA TAP_000/005 INS DMPW | ICW
LC | 129162036 | 015/136 | T3 MSSRI FLT-GLD HLL#1 15/136 TOUCH | SACTO | ETL.2660.TOWR | 2024-07-03 | 2024-07-03 | 2025-03-06 | Past Due |  | 2025-01-03 | 2025-01-03 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO FRAB NTDE PGEQ BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46460012 | T3 MSSRI FLT-GLD HLL#1 15/136 RPR STRT | ICQ
LC | 129162486 | 020/169 | T3 MSSRI FLT-GLD LL #1 20/169 TOUCH | SACTO | ETL.2660.POLE.NWOD | 2024-07-03 | 2024-07-03 | 2025-03-31 | Past Due |  | 2025-01-03 | 2025-01-03 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO FRAB NTDE PGEQ BRIN | No Good/Out of Stdrd | Structure-Steel | Repair | 46460013 | T3 MSSRI FLT-GLD LL #1 20/169 RPR STRS | ICS
LC | 129163907 | 020/166 | T3 MSSRI FLT-GLD LL #1 20/166 TOUCH | SACTO | ETL.2660.POLE.NWOD | 2024-07-03 | 2024-07-03 | 2025-03-31 | Past Due |  | 2025-01-03 | 2025-01-03 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO FRAB NTDE PGEQ BRIN | No Good/Out of Stdrd | Structure-Steel | Repair | 46460014 | T3 MSSRI FLT-GLD LL #1 20/166 RPR STRS | ICS
LC | 128000840 | 008/124 | T2 WV PARDEE #1 8/124 INS DMPW | VICTOR | ETL.8231.INSL.NCER | 2024-01-04 | 2024-01-04 | 2024-07-29 | On-Time |  | 2025-01-04 | 2025-01-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46272126 | T2 WV PARDEE #1 8/124 INS DMPW | ICW
LC | 128001453 | 001/025 | T2 KILARC-DESCHUTES 001/025 GO95 | TABLEMTN | ETL.7300.POLE.WOOD | 2024-01-04 | 2024-01-04 | 2024-12-17 | On-Time |  | 2025-01-04 | 2025-01-04 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35521530 | T2 KILARC-DESCHUTES 001/025 GO95 | 93G
LC | 128001455 | 001/029 | T2 KILARC-DESCHUTES 001/029 GO95 | TABLEMTN | ETL.7300.POLE.WOOD | 2024-01-04 | 2024-01-04 | 2024-12-16 | On-Time |  | 2025-01-04 | 2025-01-04 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35521530 | T2 KILARC-DESCHUTES 001/025 GO95 | 93G
LC | 128001456 | 001/031 | T2 KILARC-DESCHUTES 001/031 GO95 | TABLEMTN | ETL.7300.POLE.WOOD | 2024-01-04 | 2024-01-04 | 2024-12-16 | On-Time |  | 2025-01-04 | 2025-01-04 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35521530 | T2 KILARC-DESCHUTES 001/025 GO95 | 93G
LC | 126523379 | 000/002 | T2 DI MELONES-CURT 0/2L RPL STRW | VICTOR | ETL.2390.POLE.WDPS | 2023-07-07 | 2023-07-05 | 2024-10-28 | On-Time |  | 2025-01-05 | 2025-01-05 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | Rotten | Structure-Wood | Replace | 35514994 | T2 DI MELONES-CURT 0/2L RPL STRW | 70Y
LC | 126523560 | 000/002 | T2 DI MELONES-CURT 0/2C RPL STRW | VICTOR | ETL.2390.POLE.WDPS | 2023-07-07 | 2023-07-05 | 2024-12-09 | On-Time |  | 2025-01-05 | 2025-01-05 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | Rotten | Structure-Wood | Replace | 35514994 | T2 DI MELONES-CURT 0/2L RPL STRW | 70Y
LC | 126523734 | 000/002 | T2 DI MELONES-CURT 0/2R RPL STRW | VICTOR | ETL.2390.POLE.WDPS | 2023-07-07 | 2023-07-05 | 2024-10-28 | On-Time |  | 2025-01-05 | 2025-01-05 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | Rotten | Structure-Wood | Replace | 35514994 | T2 DI MELONES-CURT 0/2L RPL STRW | 70Y
LC | 126527015 | 058/424 | T2 BRDGVLLE-COTTONWD 58/424L RPR OPGW | TABLEMTN | ETL.1110.POLE.STPS | 2023-07-07 | 2023-07-05 | 2025-06-06 | Past Due |  | 2025-01-05 | 2025-01-05 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46088711 | T2 DI BRDGVLLE-COTTONWD 58/424L RPR OPGW | ICS
LC | 126527016 | 058/424 | T2 DI BRDGVLLE-COTTONWD 58/424 RMV VEG | TABLEMTN | ETL.1110.POLE.STPS | 2023-07-07 | 2023-07-05 | 2024-12-09 | On-Time |  | 2025-01-05 | 2025-01-05 | 564 | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH XMPT TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128006907 | 001/032 | T2 HALSEY-PLACER 001/032 RPR GYWW | SACTO | ETL.6990.POLE.NWOD | 2024-01-05 | 2024-01-05 | 2024-12-12 | On-Time |  | 2025-01-05 | 2025-01-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46279755 | T2 HALSEY-PLACER 001/032 RPR GYWW | ICW
LC | 128008086 | 006/006 | T2 HUMBOLDT-MPLE CREEK 06/06 GO95 | EUREKA | ETL.7130.POLE.WOOD | 2024-01-05 | 2024-01-05 | 2024-05-22 | On-Time |  | 2025-01-05 | 2025-01-05 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 31651475 | T2 HUMBOLDT-MAPLE CREEK 6/5 GO95 | 93G
LC | 128008087 | 002/028 | T2 MONTA VISTA-BURNS 02/28 GO95 | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-01-05 | 2024-01-05 | 2025-05-13 | Past Due |  | 2025-01-05 | 2025-01-05 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35528344 | T2 MONTA VISTA-BURNS 02/28 GO95 | 93G
LC | 128011447 | 004/108 | T2 WEIMAR-HALSEY 4/108 GO95 RPL | SACTO | ETL.8340.POLE.WOOD | 2024-01-08 | 2024-01-05 | 2025-03-07 | Past Due |  | 2025-01-05 | 2025-01-05 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35521982 | T2 WEIMAR-HALSEY 4/108 GO95 | 93G
LC | 128011726 | 000/005 | T2 HALSEY-PLACER 000/005 RPL POLE | SACTO | ETL.6990.POLE.WOOD | 2024-01-08 | 2024-01-05 | 2024-12-13 | On-Time |  | 2025-01-05 | 2025-01-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCL COMP OH TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Replace | 35522535 | T2 HALSEY-PLACER 000/005 RPL POLE | 70Y
LC | 128026342 | 001/005 | T2 LAURLS-OTTR 1/5 GO95 CLEAR | MOSSLNDG | ETL.7380.POLE.WOOD | 2024-01-10 | 2024-01-05 | 2024-01-30 | On-Time |  | 2025-01-05 | 2025-01-05 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35526503 | T2 EI LAURLS-OTTR 1/5 GO95 CLEAR | 93G
LC | 129173432 | T086 | T3 WV MDWY-SNTA MRIA (12KV) T86 RPR STRT | PISMOBCH | ETL.9240.TOWR | 2024-07-05 | 2024-07-05 | 2024-07-05 | Past Due |  | 2025-01-05 | 2025-01-05 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB TR3 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46292054 | T3 WV MDWY-SNTA MRIA (12KV) T86 RPR STRT | ICQ
LC | 126591306 | 016/327 | T2 DI CARIBOU-WSTWD 16/327 RPL POLE | TABLEMTN | ETL.6300.POLE.WOOD | 2023-07-14 | 2023-07-06 | 2024-07-29 | On-Time |  | 2025-01-06 | 2025-01-06 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35519122 | T2 EI CARIBOU-WESTWOOD 16/325 RPL POLE | 70Y
LC | 126524335 | 014/001 | T2 EI BRDGVLL GRBRVLL 014/001L RPR GYWW | EUREKA | ETL.6220.POLE.WDPS | 2023-07-07 | 2023-07-07 | 2024-07-13 | On-Time |  | 2025-01-07 | 2025-01-07 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46087893 | T2 EI BRDGVLL GRBRVLL 014/001L RPR GYWW | ICW
LC | 126524786 | 014/004 | T2 EI BRIDGEVILE-GARBRVILE 14/4 RPL PL | EUREKA | ETL.6220.POLE.WOOD | 2023-07-07 | 2023-07-07 | 2024-07-13 | On-Time |  | 2025-01-07 | 2025-01-07 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35504398 | T2 EI BRIDGEVILE-GARBRVILE 14/4 RPL PL | 70Y
LC | 126524982 | 014/003 | T2 EI BRDGVLL GRBRVLL 014/003L RPL POLE | EUREKA | ETL.6220.POLE.WDPS | 2023-07-07 | 2023-07-07 | 2024-07-12 | On-Time |  | 2025-01-07 | 2025-01-07 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35504397 | T2 EI BRDGVLL GRBRVLL 014/003R RPL POLE | 70Y
LC | 126525020 | 014/003 | T2 EI BRDGVLL GRBRVLL 014/003C RPL POLE | EUREKA | ETL.6220.POLE.WDPS | 2023-07-07 | 2023-07-07 | 2024-07-12 | On-Time |  | 2025-01-07 | 2025-01-07 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35504397 | T2 EI BRDGVLL GRBRVLL 014/003R RPL POLE | 70Y
LC | 126525064 | 014/003 | T2 EI BRDGVLL GRBRVLL 014/003R RPL POLE | EUREKA | ETL.6220.POLE.WDPS | 2023-07-07 | 2023-07-07 | 2024-07-12 | On-Time |  | 2025-01-07 | 2025-01-07 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35504397 | T2 EI BRDGVLL GRBRVLL 014/003R RPL POLE | 70Y
LC | 128008926 | 012/052 | T2 MONTA VISTA-JFFERSN #2 12/52 RPL INSS | METCALF | ETL.5230.INSL | 2024-01-07 | 2024-01-07 | 2024-01-08 | On-Time |  | 2025-01-07 | 2025-01-07 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 NTDE | No Good/Out of Stdrd | Insulator-Steel | Replace | 31681166 | T2 MONTA VISTA-JFFERSN #2 12/52 RPL INSS | 93K
LC | 126532087 | 011/013 | T2 BRDGVLLE-GARBERVLLE 11/13 RPL STRW | EUREKA | ETL.6220.POLE.NWOD | 2023-07-08 | 2023-07-08 | 2023-07-08 | Past Due |  | 2025-01-08 | 2025-01-08 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35580152 | T2 EI BRDGVLLE-GARBERVLLE 11/13 RPL STRW | 70Y
LC | 128009256 | 015/110 | T2 DI ELECTRA-BELLOTA 015/110 TOUCH | VICTOR | ETL.4670.TOWR | 2024-01-08 | 2024-01-08 | 2024-01-08 | Past Due |  | 2024-07-08 | 2025-01-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46493454 | T2 ELECTRA-BELLOTA 015/110 TOUCH | ICQ
LC | 128026576 | 016/161 | T2 IGNACIO-ALTO 16/161 ARC FAULT | LAKEVLLE | ETL.7150.POLE.NWOD | 2024-01-10 | 2024-01-08 | 2024-01-08 | Past Due |  | 2025-01-08 | 2025-01-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR2 PRTO FRAB NTDE | Missing | Ground Wire-Tower | Install | 31681250 | AF_06232_IGNACIO-ALTO_016 161_ARC FLT | 93V
LC | 128026662 | A011/250 | T2 SALINAS-LAURELES A11/250 ARC FAULT | MOSSLNDG | ETL.7930.POLE.NWOD | 2024-01-10 | 2024-01-08 | 2024-01-08 | Past Due |  | 2025-01-08 | 2025-01-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR2 PRTO FRAB NTDE | Missing | Ground Wire-Tower | Install | 31681260 | AF_06913_SALINAS-LAUREL_A011 250_ARC FLT | 93V
LC | 128116983 | 004/059 | T2 GREEN VALLEY-PAUL SWEET 4/59 ARC FAUL | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-01-31 | 2024-01-08 | 2024-01-08 | Past Due |  | 2025-01-08 | 2025-01-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR2 PRTO FRAB NTDE | Missing | Ground Wire-Tower | Install | 31682744 | AF_00746_GREEN VALLEY-P SWT_4 059_ARC FT | 93V
LC | 128117154 | 016/225 | T2 VALLEY SPRINGS-CLAY 16/225 ARC FAULT | VICTOR | ETL.8264.POLE.NWOD | 2024-01-31 | 2024-01-08 | 2024-01-08 | Past Due |  | 2025-01-08 | 2025-01-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR2 PRTO FRAB NTDE | Missing | Ground Wire-Tower | Install | 31682784 | AF_07835_VALLEY SPGS-CLAY_16 225_ARC FLT | 93V
LC | 128117156 | 017/245 | VALLEY SPRINGS-CLAY 17/245 ARC FAULT | VICTOR | ETL.8264.POLE.NWOD | 2024-01-31 | 2024-01-08 | 2024-01-08 | Past Due |  | 2025-01-08 | 2025-01-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR2 PRTO FRAB NTDE | Missing | Ground Wire-Tower | Install | 31682785 | AF_05782_VALLEY SPGS-CLAY_17 245_ARC FLT | 93V
LC | 128221331 | 015/282 | T2 FULTON-MOLINO-COTATI 015/282 RLCT GRN | LAKEVLLE | ETL.6910.POLE.WOOD | 2024-02-27 | 2024-01-08 | 2025-01-10 | Past Due |  | 2025-01-08 | 2025-01-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCH COMP OH TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46280520 | T2 FULTON-MOLINO-COTATI 015/282 RLCT GRN | ICW
LC | 129187368 | 025/110 | T3 DI EXCHQR-INDIAN FLAT 25/110 RPR SHLD | FRESNO | ETL.8650.POLE.NWOD | 2024-07-08 | 2024-07-08 | 2024-07-08 | Past Due |  | 2025-01-08 | 2025-01-08 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46280436 | T3 DI EXCHQR-INDIAN FLT 25/110 RPR SHLD | ICS
LC | 129187462 | 026/120 | T3 DI EXCHQUR INDN FLTS 26/120 RPR JUMS | FRESNO | ETL.8650.INSL.NCER | 2024-07-08 | 2024-07-08 | 2024-07-08 | Past Due |  | 2025-01-08 | 2025-01-08 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46280434 | T3 DI EXCHQUR INDN FLTS 26/120 RPR JUMS | ICS
LC | 129187810 | 024/100 | T3 DI EXCHQUR INDN FLTS 24/100 RPR INSS | FRESNO | ETL.8650.INSL.NCER | 2024-07-08 | 2024-07-08 | 2024-07-08 | Past Due |  | 2025-01-08 | 2025-01-08 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46292623 | T3 DI EXCHQUR INDN FLTS 24/100 RPR INSS | ICS
LC | 129187811 | 024/100 | T3 DI EXCHQUR INDN FLTS 24/100 RPR JUMS | FRESNO | ETL.8650.INSL.NCER | 2024-07-08 | 2024-07-08 | 2024-07-08 | Past Due |  | 2025-01-08 | 2025-01-08 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46292624 | T3 DI EXCHQUR INDN FLTS 24/100 RPR JUMS | ICS
LC | 129193219 | 024/097 | T3 DI EXCHEQUER-IDN FLT 24/97 RPR JUMS | FRESNO | ETL.8650.INSL.NCER | 2024-07-09 | 2024-07-08 | 2024-07-08 | Past Due |  | 2025-01-08 | 2025-01-08 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46280433 | T3 DI EXCHEQUER-IDN FLT 24/97 RPR JUMS | ICS
LC | 129224318 | 010/043 | T3 DI MORRO BAY-TMPLTN 10/43 RPL HRDT | PISMOBCH | ETL.5933.TOWR | 2024-07-15 | 2024-07-08 | 2024-09-25 | On-Time |  | 2025-01-08 | 2025-01-08 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46292622 | T3 DI MORRO BAY-TMPLTN 10/43 RPL HRDT | ICQ
LC | 129245248 | 024/093 | T3 DI EXCHQR INDN FLT 24/93 RMV VEG | FRESNO | ETL.8650.POLE.NWOD | 2024-07-19 | 2024-07-08 | 2025-01-06 | On-Time |  | 2025-01-08 | 2025-01-08 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR3 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129245249 | 024/093 | T3 DI EXCHQR INDN FLT 24/93 INSP STRT | FRESNO | ETL.8650.POLE.NWOD | 2024-07-19 | 2024-07-08 | 2024-09-16 | On-Time |  | 2025-01-08 | 2025-01-08 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW NONR FIRE COMP OH TR3 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46322310 | T3 DI EXCHQR INDN FLT 24/93 INSP STRT | ICQ
LC | 129245535 | 027/128 | T3 DI EXCHQR INDN FLT 27/128 RPR JUMS | FRESNO | ETL.8650.INSL.NCER | 2024-07-19 | 2024-07-08 | 2024-07-08 | Past Due |  | 2025-01-08 | 2025-01-08 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46298938 | T3 DI EXCHQR INDN FLT 27/128 RPR JUMS | ICS
LC | 128052669 | 027/006A | T2 PHILO JCT-ELK 27/6A RPL STRW | WILLITS | ETL.7780.POLE.WOOD | 2024-01-18 | 2024-01-09 | 2024-06-07 | On-Time |  | 2025-01-09 | 2025-01-09 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CREW COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35522274 | T2 DI PHLO JT-ELK 27/6B RPL POLE | 70Y
LC | 128052770 | 027/006C | T2 PHILO JCT-ELK 27/6C RPL STRW | WILLITS | ETL.7780.POLE.WOOD | 2024-01-18 | 2024-01-09 | 2024-06-07 | On-Time |  | 2025-01-09 | 2025-01-09 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CREW COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35522274 | T2 DI PHLO JT-ELK 27/6B RPL POLE | 70Y
LC | 129188846 | 009/132 | T3 WV MIDDLE FORK #1 009/132 RPR GRWS | SACTO | ETL.8405.POLE.NWOD | 2024-07-09 | 2024-07-09 | 2024-08-14 | On-Time |  | 2025-01-09 | 2025-01-09 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO FRAB NTDE | No Good/Out of Stdrd | Ground Wire-Steel | Repair | 46305376 | T3 WV MIDDLE FORK #1 009/132 RPR GRWS | ICS
LC | 129189043 | 49 | T3 WV WEIMAR #1 014/191 RPR SWTC | SACTO | ETL.7560.SWIT | 2024-07-09 | 2024-07-09 | 2024-08-14 | On-Time |  | 2025-01-09 | 2025-01-09 | 623 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO | Out of Adjustment | Switch | Repair | 46305377 | T3 WV WEIMAR #1 014/191 RPR SWTC | ICE
LC | 129189751 | 004/005 | T3 DONNELLS-CURTIS 004/005L STUB POLE | VICTOR | ETL.1400.POLE.WDPS | 2024-07-09 | 2024-07-09 | 2024-11-20 | On-Time |  | 2025-01-09 | 2025-01-09 | 586 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW TNT COMP OH FMOB TR3 PRTO FRAB | Rotten | Structure-Wood | Stub | 46281057 | T3 DONNELLS-CURTIS 004/005L STUB POLE | GAR
LC | 129192481 | 006/053 | T3 TIGER CREEK-ELECTRA 006/053 COTTER | VICTOR | ETL.5780.INSL | 2024-07-09 | 2024-07-09 | 2024-10-17 | On-Time |  | 2024-10-09 | 2025-01-09 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO PGEQ DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46280448 | T3 TIGER CREEK-ELECTRA 006/053 COTTER | ICS
LC | 129230181 | 016/445 | T3 DI COLGATE-ALLEGHANY 16/445 RPR SPLW | SACTO | ETL.6470.INSL.NCER | 2024-07-16 | 2024-07-09 | 2024-10-12 | On-Time |  | 2025-01-09 | 2025-01-09 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR | No Good/Out of Stdrd | Splice-Wood | Repair | 46290537 | T3 DI COLGATE-ALLEGHANY 16/445 RPR SPLW | ICW
LC | 129333984 | 000/002B | T3 DI GRIZZLY-BUCKS CREEK 0/2B RPR JUMW | TABLEMTN | ETL.2395.INSL.NCER | 2024-08-05 | 2024-07-09 | 2024-11-13 | On-Time |  | 2025-01-09 | 2025-01-09 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR DURA | No Good/Out of Stdrd | Jumper-Wood | Repair | 46303873 | T3 DI GRIZZLY-BUCKS CREEK 0/2B RPR JUMW | ICW
LC | 129444203 | 003/024 | T3 DI EL DRDO-MSRI FLT #1 3/24 RMV VEG | SACTO | ETL.1530.TOWR | 2024-08-27 | 2024-07-09 | 2025-01-09 | On-Time |  | 2025-01-09 | 2025-01-09 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR3 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128026915 | 020/094 | T2 WV CLLNDR SW ST-MS 20/094 RPL INSS | PISMOBCH | ETL.1210.INSL.NCER | 2024-01-10 | 2024-01-10 | 2024-10-21 | On-Time |  | 2025-01-10 | 2025-01-10 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35585150 | T2 WV CLLNDR SW ST-MS 20/094 RPL INSS | 93K
LC | 128027526 | 036/707 | T2 HAT CREEK #1-WESTWOOD 36/707 GO95 | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-10 | 2024-01-10 | 2024-10-29 | On-Time |  | 2025-01-10 | 2025-01-10 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35524320 | T2 HAT CREEK #1-WESTWOOD 36/707 GO95 | 93G
LC | 129205938 | 006/004 | T3 EI BRDGVLLE-GARBERVILLE 6/4 RPL POLE | EUREKA | ETL.6220.POLE.WOOD | 2024-07-10 | 2024-07-10 | 2024-10-14 | On-Time |  | 2025-01-10 | 2025-01-10 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR3 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35566372 | T3 EI BRDGVLLE-GARBERVILLE 4/0 RPL POLE | 70Y
LC | 126593286 | 008/126 | T2 DI DLTA-MTN GT JCT-MTN 8/126 RPR STRW | TABLEMTN | ETL.6750.POLE.WOOD | 2023-07-14 | 2023-07-11 | 2024-07-17 | On-Time |  | 2025-01-11 | 2025-01-11 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB DURA | No Good/Out of Stdrd | Structure-Wood | Repair | 46092016 | T2 DI DLTA-MTN GT JCT-MTN 8/126 RPR STRW | ICW
LC | 128029794 | 010/220 | T2 COLEMAN-SOUTH 010/220 RPL ANCW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-01-11 | 2024-01-11 | 2024-10-10 | On-Time |  | 2025-01-11 | 2025-01-11 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW REMT SWRK ACCH USA COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35556791 | T2 COLEMAN-SOUTH 010/220 RPL ANCW | 93E
LC | 128030070 | 016/320 | T2 WV SALINAS-LAURELES 16/320 INS DAMP | MOSSLNDG | ETL.7930.INSL.NCER | 2024-01-11 | 2024-01-11 | 2025-04-08 | Past Due |  | 2025-01-11 | 2025-01-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46283534 | T2 WV SALINAS-LAURELES 16/320 INS DAMP | ICW
LC | 128030430 | 011/149 | T2 WV JOLON TAP 11/149 RPL POLE | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-01-11 | 2024-01-11 | 2025-01-18 | Past Due |  | 2025-01-11 | 2025-01-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35584916 | T2 WV JOLON TAP 11/149 RPL POLE | 70Y
LC | 129209928 | 005/005 | T3 DIABLO UNIT #2 005/005 RPR STRT | PISMOBCH | ETL.5950.TOWR | 2024-07-11 | 2024-07-11 | 2024-07-11 | Past Due |  | 2025-01-11 | 2025-01-11 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW CREW ACCH OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46292626 | T3 DIABLO UNIT #2 005/005 RPR STRT | ICQ
LC | 129210338 | 002/001 | T3 EI BRDGVLLE-GARBERVILLE 2/1 RPR GYWW | EUREKA | ETL.6220.POLE.NWOD | 2024-07-11 | 2024-07-11 | 2024-10-09 | On-Time |  | 2025-01-11 | 2025-01-11 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46282843 | T3 EI BRDGVLLE-GARBERVILLE 2/1 RPR GYWW | ICW
LC | 129215226 | 004/096 | T3 DI DRUM-GRSS VLLY-WMR 4/096 RPR ADSS | SACTO | ETL.6760.POLE.NWOD | 2024-07-12 | 2024-07-11 | 2024-08-14 | On-Time |  | 2025-01-11 | 2025-01-11 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46305378 | T3 DI DRUM-GRSS VLLY-WMR 4/096 RPR ADSS | ICW
LC | 129437866 | 000/005C | T3 DI GRIZZLY-BUCKS CREEK 0/5C RPR GYWW | TABLEMTN | ETL.2395.POLE.NWOD | 2024-08-26 | 2024-07-11 | 2024-11-20 | On-Time |  | 2025-01-11 | 2025-01-11 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46328463 | T3 DI GRIZZLY-BUCKS CREEK 0/5C RPR GYWW | ICW
LC | 126570404 | 99 | T2 EI CARIBOU-WESTWOOD 0/4A RPL SWTC | TABLEMTN | ETL.6300.SWIT | 2023-07-12 | 2023-07-12 | 2024-07-28 | On-Time |  | 2025-01-12 | 2025-01-12 | 427T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCH COMP OH FMOB XMPT TR2 PRTO | No Good/Out of Stdrd | Switch-Wood | Replace | 35521271 | T2 EI CARIBOU-WESTWOOD 0/4A RPL SWTC | 93H
LC | 128035114 | 035/682 | T2 HAT CREEK #1-WESTWOOD 35/682 RPL POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-12 | 2024-01-12 | 2024-08-06 | On-Time |  | 2025-01-12 | 2025-01-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR REMT REAR CLR USA COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35524611 | T2 HAT CREEK #1-WESTWOOD 35/682 RPL POLE | 70Y
LC | 128035295 | 025/489 | T2 HAT CREEK #1-WESTWOOD 25/489 RPL POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-12 | 2024-01-12 | 2024-06-18 | On-Time |  | 2025-01-12 | 2025-01-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC REAR ACCH USA COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35524610 | T2 HAT CREEK #1-WESTWOOD 25/489 RPL POLE | 70Y
LC | 129215557 | 004/119A | T3 EI DRM-GRSS VLLY-WMR 4/119A RPR JMPW | SACTO | ETL.6760.POLE.NWOD | 2024-07-12 | 2024-07-12 | 2024-12-19 | On-Time |  | 2025-01-12 | 2025-01-12 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB NTDE | No Good/Out of Stdrd | Jumper-Wood | Repair | 46284253 | T3 EI DRM-GRSS VLLY-WMR 4/119A RPR JMPW | ICW
LC | 129227219 | 018/157 | T3NT EI MSRI FLT-GLD HL#1 18/157 RMV VEG | SACTO | ETL.2660.TOWR | 2024-07-16 | 2024-07-16 | 2025-01-16 | On-Time |  | 2025-01-16 | 2025-01-16 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR3 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129379112 | 005/007 | T3 KONOCTI-EAGLE ROCK 5/7 RMV VEG | WILLITS | ETL.6861.POLE.WOOD | 2024-08-13 | 2024-07-16 | 2024-12-13 | On-Time |  | 2025-01-16 | 2025-01-16 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH TR3 PRTO MBSF FRAB BRIN | Overgrown | Vegetation | Remove
LC | 126604283 | 090/460A | T2 MALIN-ROUND MTN #2 90/460A RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2023-07-17 | 2023-07-17 | 2023-07-17 | Past Due |  | 2025-01-17 | 2025-01-17 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW NONR OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46236031 | T2 MALIN-ROUND MTN #2 90/460A RPR GYWT | ICQ
LC | 128049372 | 030/594 | T2 HT CRK #1-WESTWD 30/594 GO95 RPL | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-17 | 2024-01-17 | 2024-11-06 | On-Time |  | 2025-01-17 | 2025-01-17 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35524491 | T2 HT CRK #1-WESTWD 30/594 GO95 RPL | 93G
LC | 128049500 | 035/680 | T2 HAT CREEK #1-WESTWOOD 035/680 GO95 | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-17 | 2024-01-17 | 2024-10-29 | On-Time |  | 2025-01-17 | 2025-01-17 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35524359 | T2 HAT CREEK #1-WESTWOOD 035/680 GO95 | 93G
LC | 128049501 | 035/688 | T2 HAT CREEK #1-WESTWOOD 035/688 GO95 | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-17 | 2024-01-17 | 2024-10-29 | On-Time |  | 2025-01-17 | 2025-01-17 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35524481 | T2 HAT CREEK #1-WESTWOOD 035/688 GO95 | 93G
LC | 128049803 | 038/743 | T2 HAT CREEK #1-WESTWOOD 038/743 GO95 | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-17 | 2024-01-17 | 2024-12-04 | On-Time |  | 2025-01-17 | 2025-01-17 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35524484 | T2 HAT CREEK #1-WESTWOOD 038/743 GO95 | 93G
LC | 128049804 | 005/105 | T2 HAT CREEK #1-WESTWOOD 005/105 GO95 | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-17 | 2024-01-17 | 2024-11-04 | On-Time |  | 2025-01-17 | 2025-01-17 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35524485 | T2 HAT CREEK #1-WESTWOOD 005/105 GO95 | 93G
LC | 128049805 | 005/106 | T2 HAT CREEK #1-WESTWOOD 005/106 GO95 | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-17 | 2024-01-17 | 2024-11-04 | On-Time |  | 2025-01-17 | 2025-01-17 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35524486 | T2 HAT CREEK #1-WESTWOOD 005/106 GO95 | 93G
LC | 128049896 | 006/135 | T2 KILARC-DESCHUTES 006/135 GO95 | TABLEMTN | ETL.7300.POLE.WOOD | 2024-01-17 | 2024-01-17 | 2024-04-03 | On-Time |  | 2024-07-17 | 2025-01-17 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | Overloaded | GO95 Clear Infract-Wood | Replace | 35524490 | T2 KILARC-DESCHUTES 006/135 GO95 | 93G
LC | 128050592 | 015/349 | T2 DRUM-GRSS VLLY-WEIMR 015/349 GO95 | SACTO | ETL.6760.POLE.WOOD | 2024-01-18 | 2024-01-17 | 2024-12-04 | On-Time |  | 2025-01-17 | 2025-01-17 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35525555 | T2 DRUM-GRSS VLLY-WEIMR 015/349 GO95 | 93G
LC | 129475127 | B017/388 | T3 DI DRM-GRSS VLY-WMAR B17/388 RPR INSW | SACTO | ETL.6760.INSL.NCER | 2024-09-04 | 2024-07-17 | 2024-10-24 | On-Time |  | 2025-01-17 | 2025-01-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46323931 | T3 DI DRM-GRSS VLY-WMAR B17/388 RPR INSW | ICW
LC | 129475451 | B017/388 | T3 DI DRM-GRSS VLY-WMAR B17/388 RPR GYWW | SACTO | ETL.6760.POLE.NWOD | 2024-09-04 | 2024-07-17 | 2024-10-24 | On-Time |  | 2025-01-17 | 2025-01-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46323932 | T3 DI DRM-GRSS VLY-WMAR B17/388 RPR GYWW | ICW
LC | 128052388 | 111/005 | T2 WV HUMBOLDT-BRIDGVLE 111/5L RPL ANCW | EUREKA | ETL.1810.POLE.WDPS | 2024-01-18 | 2024-01-18 | 2025-01-30 | Past Due |  | 2025-01-18 | 2025-01-18 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35597272 | T2 WV HUMBOLDT-BRIDGVLE 111/5L RPL ANCW | 93E
LC | 128052682 | 016/003A | T2 TRINITY-MAPLE CREEKC16/003A INS DMPW | EUREKA | ETL.8170.INSL.NCER | 2024-01-18 | 2024-01-18 | 2024-01-18 | On-Time |  | 2025-01-18 | 2025-01-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46164542 | T2 TRINITY-MAPLE CREEKC16/003B INS DMPW | ICW
LC | 128073413 | 111/005 | T2 WV HUMBOLDT-BRIDGVLE 111/5R RPL GYWW | EUREKA | ETL.1810.POLE.WDPS | 2024-01-23 | 2024-01-18 | 2024-12-11 | On-Time |  | 2025-01-18 | 2025-01-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Replace | 46281458 | T2 WV HUMBOLDT-BRIDGVLE 111/5R RPL GYWW | ICW
LC | 129293083 | B017/386 | T3 DI DRM-GRS VLY-WMR B017/386 RPR GYWW | SACTO | ETL.6760.POLE.WOOD | 2024-07-26 | 2024-07-18 | 2024-10-24 | On-Time |  | 2025-01-18 | 2025-01-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46291823 | T3 DI DRM-GRS VLY-WMR B017/386 RPR GYWW | ICW
LC | 126621606 | 057/001A | T2 HUMBOLDT-TRINITY 57/1A RPL POLE | EUREKA | ETL.1820.POLE.WOOD | 2023-07-19 | 2023-07-19 | 2024-11-10 | On-Time |  | 2025-01-19 | 2025-01-19 | 372 | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW OTHR FIRE COMP OH XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 31656098 | T2 EI HUMBOLDT-TRINITY 57/1C RPL POLE | 70Y
LC | 128067734 | 003/011 | T2 EI VLY SPRGS-CLRS CT 3/11 RPR GYWW | VICTOR | ETL.8220.POLE.WOOD | 2024-01-20 | 2024-01-20 | 2024-09-26 | On-Time |  | 2024-07-20 | 2025-01-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK ACCM COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46253025 | T2 EI VLY SPRNGS-CLVRS CMT_3/11 RPR GYWW | ICW
LC | 128071968 | 011/074 | T2 WV CAYUCOS-CAMBRIA 011/074 RPL DMPS | PISMOBCH | ETL.8560.INSL.NCER | 2024-01-22 | 2024-01-22 | 2025-05-04 | Past Due |  | 2025-01-22 | 2025-01-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Damper-Steel | Replace | 46329624 | T2 WV CAYUCOS-CAMBRIA 011/074 RPL DMPS | ICS
LC | 129280239 | 000/008A | T3 DI GZLY TP (CITY OF SC) 0/8A RPR GYWW | TABLEMTN | ETL.2395.POLE.NWOD | 2024-07-23 | 2024-07-22 | 2024-11-20 | On-Time |  | 2025-01-22 | 2025-01-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46291834 | T3 DI GZLY TP (CITY OF SC) 0/8A RPR GYWW | ICW
LC | 129280281 | 000/008A | T3 DI GZLY TP (CITY OF SC) 0/8A RPR INSW | TABLEMTN | ETL.2395.INSL.NCER | 2024-07-23 | 2024-07-22 | 2025-01-21 | On-Time |  | 2025-01-22 | 2025-01-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46291835 | T3 DI GZLY TP (CITY OF SC) 0/8A RPR INSW | ICW
LC | 129280286 | 000/008C | T3 DI GZLY TP (CITY OF SC) 0/8C RPR GYWW | TABLEMTN | ETL.2395.POLE.NWOD | 2024-07-23 | 2024-07-22 | 2024-11-20 | On-Time |  | 2025-01-22 | 2025-01-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46291836 | T3 DI GZLY TP (CITY OF SC) 0/8C RPR GYWW | ICW
LC | 129293198 | 002/038A | T3 DI GRIZZLY-BUCKS CREEK 2/38A RPR GYWW | TABLEMTN | ETL.2395.POLE.NWOD | 2024-07-26 | 2024-07-22 | 2024-11-22 | On-Time |  | 2024-10-22 | 2025-01-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46291837 | T3 DI GRIZZLY-BUCKS CREEK 2/38A RPR GYWW | ICW
LC | 129293304 | 002/038C | T3 DI GRIZZLY-BUCKS CREEK 2/38C RPR GYWW | TABLEMTN | ETL.2395.POLE.NWOD | 2024-07-26 | 2024-07-22 | 2024-11-27 | On-Time |  | 2024-10-22 | 2025-01-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46291839 | T3 DI GRIZZLY-BUCKS CREEK 2/38C RPR GYWW | ICW
LC | 129293358 | 002/038B | T3 DI GRIZZLY-BUCKS CREEK 2/38B RPR GYWW | TABLEMTN | ETL.2395.POLE.NWOD | 2024-07-26 | 2024-07-22 | 2024-11-22 | On-Time |  | 2024-10-22 | 2025-01-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46291838 | T3 DI GRIZZLY-BUCKS CREEK 2/38B RPR GYWW | ICW
LC | 129334229 | 002/039B | T3 DI GRIZZLY-BUCKS CRK 2/39B RPR INSW | TABLEMTN | ETL.2395.INSL.NCER | 2024-08-05 | 2024-07-22 | 2025-01-21 | On-Time |  | 2025-01-22 | 2025-01-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46303880 | T3 DI GRIZZLY-BUCKS CRK 2/39B RPR INSW | ICW
LC | 129334245 | 001/020B | T3 DI GRIZZLY-BUCKS CRK 1/20B RPR GYWW | TABLEMTN | ETL.2395.POLE.NWOD | 2024-08-05 | 2024-07-22 | 2024-11-21 | On-Time |  | 2025-01-22 | 2025-01-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46303878 | T3 DI GRIZZLY-BUCKS CRK 1/20B RPR GYWW | ICW
LC | 129405335 | 002/017 | T3 MORAGA-OAKLAND #3 2/17 RMV VEG | CONCORD | ETL.2740.TOWR | 2024-08-19 | 2024-07-22 | 2024-10-28 | On-Time |  | 2025-01-22 | 2025-01-22 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH TR3 PRTO MBSF FRAB | Overgrown | Vegetation | Trim
LC | 129407929 | 001/020A | T3 DI GRIZZLY-BUCKS CRK 1/20A RPR GYWW | TABLEMTN | ETL.2395.POLE.NWOD | 2024-08-19 | 2024-07-22 | 2024-11-21 | On-Time |  | 2025-01-22 | 2025-01-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46303877 | T3 DI GRIZZLY-BUCKS CRK 1/20A RPR GYWW | ICW
LC | 129444622 | 002/036A | T3 DI GRIZZLY-BUCKS CREEK 2/36A RPR ANCW | TABLEMTN | ETL.2395.POLE.NWOD | 2024-08-27 | 2024-07-22 | 2025-01-21 | On-Time |  | 2025-01-22 | 2025-01-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46328468 | T3 DI GRIZZLY-BUCKS CREEK 2/36A RPR ANCW | ICW
LC | 129444623 | 002/036A | T3 DI GRIZZLY-BUCKS CREEK 2/36A RPR SHLD | TABLEMTN | ETL.2395.POLE.NWOD | 2024-08-27 | 2024-07-22 | 2025-01-21 | On-Time |  | 2025-01-22 | 2025-01-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Wood | Repair | 46328469 | T3 DI GRIZZLY-BUCKS CREEK 2/36A RPR SHLD | ICW
LC | 129444871 | 001/024B | T3 DI GRIZZLY-BUCKS CREEK 1/24B RPR INSW | TABLEMTN | ETL.2395.INSL.NCER | 2024-08-27 | 2024-07-22 | 2024-11-21 | On-Time |  | 2025-01-22 | 2025-01-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46328472 | T3 DI GRIZZLY-BUCKS CREEK 1/24B RPR INSW | ICW
LC | 128073249 | 053/1035 | T2 HAT CRK #1-WSTWD 53/1035 GO95 | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-23 | 2024-01-23 | 2024-10-02 | On-Time |  | 2025-01-23 | 2025-01-23 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35525995 | T2 DI HAT CRK #1-WSTWD 53/1035 GO95 | 93G
LC | 128073342 | 029/563 | T2 HAT CREEK #1-WESTWD 29/563 GO95 RPL | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-23 | 2024-01-23 | 2024-11-06 | On-Time |  | 2025-01-23 | 2025-01-23 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35526167 | T2 HAT CREEK #1-WESTWD 29/563 GO95 RPL | 93G
LC | 128075383 | 022/015 | T2 HRTLY-CLRLK 22/15 RPL POLE | WILLITS | ETL.7515.POLE.WOOD | 2024-01-23 | 2024-01-23 | 2024-01-23 | Past Due |  | 2025-01-23 | 2025-01-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35568300 | T2 EI HRTLY-CLRLK 22/15 RPL POLE | 70Y
LC | 128077785 | 000/001 | T2 EI CASTAIC TAP _000/001 RPL DMPW | MIDWAY | ETL.9253.INSL.NCER | 2024-01-23 | 2024-01-23 | 2025-01-09 | On-Time |  | 2025-01-23 | 2025-01-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Damper-Wood | Replace | 46297587 | T2 EI CASTAIC TAP _000/001 RPL DMPW | ICW
LC | 129333852 | 001/029A | T3 DI GRIZZLY-BUCKS CRK 1/29A RPR SHLW | TABLEMTN | ETL.2395.POLE.NWOD | 2024-08-05 | 2024-07-23 | 2024-11-22 | On-Time |  | 2025-01-23 | 2025-01-23 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Wood | Repair | 46303874 | T3 DI GRIZZLY-BUCKS CRK 1/29A RPR SHLW | ICW
LC | 128079629 | 020/217 | T2 WV ELK CREEK TAP _020/217 INS DMPW | TABLEMTN | ETL.6921.INSL.NCER | 2024-01-24 | 2024-01-24 | 2024-10-09 | On-Time |  | 2025-01-24 | 2025-01-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46311302 | T2 WV ELK CREEK TAP _020/217 INS DMPW | ICW
LC | 128080808 | 053/003A | T2 TRINITY-MAPLE CREEK 53/3A RPL ANCW | EUREKA | ETL.8170.POLE.NWOD | 2024-01-24 | 2024-01-24 | 2025-06-20 | Past Due |  | 2024-07-24 | 2025-01-24 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35529593 | T2 TRINITY-MAPLE CREEK 53/3A RPL ANCW | 93E
LC | 128081098 | 049/001 | T2 EI HUMBOLDT-TRINITY 49/1R RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-01-24 | 2024-01-24 | 2024-01-23 | On-Time |  | 2025-01-24 | 2025-01-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46096523 | T2 EI HUMBOLDT-TRINITY 49/1L RPR GYWW | ICW
LC | 129348053 | 000/007A | T3 DI GRIZZLY-BUCKS CRK 0/007A RPR GYWW | TABLEMTN | ETL.2395.POLE.NWOD | 2024-08-07 | 2024-07-24 | 2024-11-20 | On-Time |  | 2025-01-24 | 2025-01-24 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46303881 | T3 DI GRIZZLY-BUCKS CRK 0/007A RPR GYWW | ICW
LC | 129444877 | 001/024C | T3 DI GRIZZLY-BUCKS CREEK 1/24C RPR GYWW | TABLEMTN | ETL.2395.POLE.NWOD | 2024-08-27 | 2024-07-24 | 2024-11-22 | On-Time |  | 2025-01-24 | 2025-01-24 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46328473 | T3 DI GRIZZLY-BUCKS CREEK 1/24C RPR GYWW | ICW
LC | 128082799 | 006/118 | T2 EI CARIBOU-WESTWOOD 6/118 RPL DMPW | TABLEMTN | ETL.6300.INSL.NCER | 2024-01-25 | 2024-01-25 | 2024-09-13 | On-Time |  | 2025-01-25 | 2025-01-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK ACCM ACCH COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46291825 | T2NT EI CARIBOU-WESTWOOD 6/118 RPL DMPW | ICW
LC | 128082809 | 006/117 | T2 EI CARIBOU-WESTWOOD 06/117 RPR GYWW | TABLEMTN | ETL.6300.POLE.NWOD | 2024-01-25 | 2024-01-25 | 2024-09-13 | On-Time |  | 2025-01-25 | 2025-01-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46291824 | T2 EI CARIBOU-WESTWOOD 06/117 RPR GYWW | ICW
LC | 128082870 | 006/119 | T2 EI CARIBOU-WESTWOOD 006/119 RPR CNDW | TABLEMTN | ETL.6300.INSL.NCER | 2024-01-25 | 2024-01-25 | 2024-10-18 | On-Time |  | 2025-01-25 | 2025-01-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Conductor-Wood | Repair | 46291826 | T2 EI CARIBOU-WESTWOOD 006/119 RPR CNDW | ICW
LC | 128083322 | 016/132 | T2 EI PIT #1-CTTNWD 016/132 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2024-01-25 | 2024-01-25 | 2025-02-06 | Past Due |  | 2025-01-25 | 2025-01-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46306600 | T2 EI PIT #1-CTTNWD 016/132 BNT STEEL | ICQ
LC | 129287709 | 011/266 | T3 WV DRM-GRSS VLLEY-WMR 11/266 COMPLETE | SACTO | ETL.6760.POLE.NWOD | 2024-07-25 | 2024-07-25 | 2024-08-15 | On-Time |  | 2025-01-25 | 2025-01-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3 PRTO FRAB DURA | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305380 | T3 WV DRM-GRSS VLLEY-WMR 11/266 COMPLETE | ICW
LC | 128086731 | T002/002 | T2 WV TULUCAY-NAPA #1 T02/002 RPL POLE | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-01-26 | 2024-01-26 | 2024-12-05 | On-Time |  | 2025-01-26 | 2025-01-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35568542 | T2 WV TULUCAY-NAPA #1 T02/002 RPL POLE | 70Y
LC | 128089214 | 005/040A | T2 TRINITY-COTTONWD 05/040A RPR GYWW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-01-27 | 2024-01-27 | 2025-01-21 | On-Time |  | 2025-01-27 | 2025-01-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332033 | T2 TRINITY-COTTONWD 05/040A RPR GYWW | ICW
LC | 128096597 | 010/008 | T2 TRINITY-MAPLE CREEK 10/8 GO95 | EUREKA | ETL.8170.POLE.WOOD | 2024-01-29 | 2024-01-29 | 2025-03-19 | Past Due |  | 2025-01-29 | 2025-01-29 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR FIRE COMP OH TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 31657757 | T2 TRINITY-MAPLE CREEK 10/06 GO95 | 93G
LC | 128097652 | 028/214 | T2 EI HIGGINS-BELL 028/214 COTTER | SACTO | ETL.1412.INSL.CERA | 2024-01-29 | 2024-01-29 | 2024-08-21 | On-Time |  | 2024-07-29 | 2025-01-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46178992 | T2 EI HIGGINS-BELL 028/214 COTTER | ICS
LC | 128097884 | 000/001 | T2 WV MELONES-WILSON 000/001 COTTER | VICTOR | ETL.5080.POLE.NWOD | 2024-01-29 | 2024-01-29 | 2025-01-09 | On-Time |  | 2025-01-29 | 2025-01-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | Missing | Hardware-Wood | Install | 46287943 | T2 WV MELONES-WILSON 000/001 COTTER | ICW
LC | 128113971 | 003/029 | T2 DI PIT#1 HT CRK#2 BNY 03/029 RPR ANCW | TABLEMTN | ETL.7040.POLE.WOOD | 2024-01-30 | 2024-01-29 | 2024-04-22 | On-Time |  | 2024-07-29 | 2025-01-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46178993 | T2 DI PIT#1 HT CRK#2 BNY 03/029 RPR ANCW | ICW
LC | 128123217 | 008/184 | T2 DI HMLTN BRNCH CNSTR 08/184 RPR JUMW | TABLEMTN | ETL.7000.INSL.NCER | 2024-02-02 | 2024-01-29 | 2024-07-23 | On-Time |  | 2025-01-29 | 2025-01-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46190731 | T2 DI HMLTN BRNCH CNSTR 08/184 RPR JUMW | ICW
LC | 128123698 | 37 | T2 DI COLGTE PLMRO 13/261 RPR SWTC | TABLEMTN | ETL.6500.SWIT | 2024-02-02 | 2024-01-29 | 2024-08-23 | On-Time |  | 2024-07-29 | 2025-01-29 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | Out of Adjustment | Switch | Repair | 46189708 | T2 DI COLGTE PLMRO 13/261 RPR SWTC | ICE
LC | 128124157 | 000/003 | T2 DI MUSTANG TAP 00/003 RPR JUMW | PISMOBCH | ETL.9091.INSL.NCER | 2024-02-02 | 2024-01-29 | 2024-05-12 | On-Time |  | 2024-07-29 | 2025-01-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46190166 | T2 DI MUSTANG TAP 00/003 RPR JUMW | ICW
LC | 128124216 | 008/188 | T2 DI HMLTN BRNCH CNSTR 08/188 RPR GYWW | TABLEMTN | ETL.7000.POLE.NWOD | 2024-02-02 | 2024-01-29 | 2025-01-14 | On-Time |  | 2025-01-29 | 2025-01-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311134 | T2 DI HMLTN BRNCH CNSTR 08/188 RPR GYWW | ICW
LC | 128124273 | 016/329 | T2 DI COLGTE-PLMRO 16/329 RPR ANCW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-02-02 | 2024-01-29 | 2025-01-28 | On-Time |  | 2025-01-29 | 2025-01-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46382973 | T2 DI COLGTE-PLMRO 16/329 RPR ANCW | ICW
LC | 128138025 | 013/268-GUY | T2 DI CLGTE PLMRO 13/268 RPR GYWW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-02-06 | 2024-01-29 | 2025-01-08 | On-Time |  | 2025-01-29 | 2025-01-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332037 | T2 DI CLGTE PLMRO 13/268 RPR GYWW | ICW
LC | 128138028 | 024/177 | T2 DI TRNTY CTTNWD 24/177L RMV VEG | TABLEMTN | ETL.4040.POLE.STPS | 2024-02-06 | 2024-01-29 | 2025-02-14 | Past Due |  | 2025-01-29 | 2025-01-29 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128143607 | 027/191 | T2 DI TRNTY-COTTONWOOD 27/191 BNT STEEL | TABLEMTN | ETL.4040.TOWR | 2024-02-07 | 2024-01-29 | 2025-02-27 | Past Due |  | 2025-01-29 | 2025-01-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46306602 | T2 DI TRNTY-COTTONWOOD 27/191 BNT STEEL | ICQ
LC | 128102661 | 028/216 | T2 EI HIGGINS-BELL 028/216 RMV VEG | SACTO | ETL.1412.TOWR | 2024-01-30 | 2024-01-30 | 2024-01-30 | Past Due |  | 2025-01-30 | 2025-01-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128103564 | 027/212 | T2 EI HIGGINS-BELL 27/212 RPL INSS | SACTO | ETL.1412.INSL.CERA | 2024-01-30 | 2024-01-30 | 2025-01-22 | On-Time |  | 2025-01-30 | 2025-01-30 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35610004 | T2 EI HIGGINS-BELL 28/213 RPL INSS | 93K
LC | 128103690 | 027/211 | T2 EI HIGGINS-BELL 027/211 RPL INSS | SACTO | ETL.1412.INSL.CERA | 2024-01-30 | 2024-01-30 | 2025-01-24 | On-Time |  | 2025-01-30 | 2025-01-30 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35610003 | T2 EI HIGGINS-BELL 027/211 RPL INSS | 93K
LC | 128103835 | 004/093 | T2 EI CARIBOU-WESTWD 004/093L RPR GYWW | TABLEMTN | ETL.6300.POLE.STPS | 2024-01-30 | 2024-01-30 | 2025-01-06 | On-Time |  | 2025-01-30 | 2025-01-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK ACCL COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332026 | T2 EI CARIBOU-WESTWD 004/093L RPR GYWW | ICW
LC | 128103837 | 004/093 | T2 EI CARIBOU-WESTWD 004/093C RPR GYWW | TABLEMTN | ETL.6300.POLE.STPS | 2024-01-30 | 2024-01-30 | 2025-01-06 | On-Time |  | 2025-01-30 | 2025-01-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK ACCL COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332027 | T2 EI CARIBOU-WESTWD 004/093C RPR GYWW | ICW
LC | 128103958 | 004/093 | T2 EI CARIBOU-WESTWD 004/093R RPR GYWW | TABLEMTN | ETL.6300.POLE.STPS | 2024-01-30 | 2024-01-30 | 2025-01-06 | On-Time |  | 2025-01-30 | 2025-01-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK ACCL COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332028 | T2 EI CARIBOU-WESTWD 004/093R RPR GYWW | ICW
LC | 128104220 | 028/218 | T2 EI HIGGINS-BELL 028/218 COTTER | SACTO | ETL.1412.INSL.CERA | 2024-01-30 | 2024-01-30 | 2025-01-21 | On-Time |  | 2025-01-30 | 2025-01-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300548 | T2 EI HIGGINS-BELL 028/218 COTTER | ICS
LC | 128104389 | 023/002 | T2 EI HARTLEY-CLEARLAKE 23/002 RPL POLE | WILLITS | ETL.7515.POLE.WOOD | 2024-01-30 | 2024-01-30 | 2024-01-30 | Past Due |  | 2025-01-30 | 2025-01-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574585 | T2 EI HARTLEY-CLEARLAKE 23/002 RPL POLE | 70Y
LC | 128104550 | 029/220 | T2 EI HIGGINS-BELL 029/220 COTTER | SACTO | ETL.1412.INSL.CERA | 2024-01-30 | 2024-01-30 | 2025-01-21 | On-Time |  | 2025-01-30 | 2025-01-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300550 | T2 EI HIGGINS-BELL 029/220 COTTER | ICS
LC | 128113467 | 005/098 | T2 EI CARIBOU-WESTWOOD 05/98 RPR GYWW | TABLEMTN | ETL.6300.POLE.NWOD | 2024-01-30 | 2024-01-30 | 2025-01-06 | On-Time |  | 2025-01-30 | 2025-01-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332029 | T2 EI CARIBOU-WESTWOOD 05/98 RPR GYWW | ICW
LC | 128113468 | 005/100 | T2 EI CARIBOU-WESTWOOD 005/100 RPL POLE | TABLEMTN | ETL.6300.POLE.WOOD | 2024-01-30 | 2024-01-30 | 2025-03-07 | Past Due |  | 2025-01-30 | 2025-01-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCH USA COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35556132 | T2 EI CARIBOU-WESTWOOD 005/100 RPL POLE | 70Y
LC | 128113469 | 005/102 | T2 EI CARIB-WESTWD 05/102R RPL POLE | TABLEMTN | ETL.6300.POLE.WDPS | 2024-01-30 | 2024-01-30 | 2025-03-07 | Past Due |  | 2025-01-30 | 2025-01-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCH USA COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35556133 | T2 EI CARIB-WESTWD 05/102R RPL POLE | 70Y
LC | 128113490 | 005/102 | T2 EI CARIB-WESTWD 05/102C RPL POLE | TABLEMTN | ETL.6300.POLE.WDPS | 2024-01-30 | 2024-01-30 | 2025-03-07 | Past Due |  | 2025-01-30 | 2025-01-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP REMT SWRK CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556133 | T2 EI CARIB-WESTWD 05/102R RPL POLE | 70Y
LC | 128113491 | 005/102 | T2 EI CARIB-WESTWD 05/102L RPL POLE | TABLEMTN | ETL.6300.POLE.WDPS | 2024-01-30 | 2024-01-30 | 2025-03-07 | Past Due |  | 2025-01-30 | 2025-01-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556133 | T2 EI CARIB-WESTWD 05/102R RPL POLE | 70Y
LC | 128113595 | 002/059 | T2 EI PINE GROVE TAP 02/059 COTTER | VICTOR | ETL.8351.INSL.CERA | 2024-01-30 | 2024-01-30 | 2024-09-05 | On-Time |  | 2025-01-30 | 2025-01-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP PUBL CITY ACCL ACCM ACCH COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46227584 | T2 EI PINE GROVE TAP 02/059 COTTER | ICW
LC | 128113874 | 000/002 | T2 EI PIT #4 TAP 000/002 RPL DMPS | TABLEMTN | ETL.5432.INSL.CERA | 2024-01-30 | 2024-01-30 | 2025-01-21 | On-Time |  | 2025-01-30 | 2025-01-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Damper-Steel | Replace | 46332030 | T2 EI PIT #4 TAP 000/002 RPL DMPS | ICS
LC | 128114412 | 010/069 | T2 CNTRA CST-LS PSITS 10/69 RPL HNGR | CONCORD | ETL.4510.INSL | 2024-01-31 | 2024-01-30 | 2025-01-23 | On-Time |  | 2025-01-30 | 2025-01-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46286418 | T2 CNTRA CST-LS PSITS 10/69 RPL HRDT | ICQ
LC | 128120536 | 010/069 | T2 EI CNTR CST-LS PSTS 10/69 RPL INSS | CONCORD | ETL.4510.INSL | 2024-02-01 | 2024-01-30 | 2025-01-24 | On-Time |  | 2025-01-30 | 2025-01-30 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575000 | T2 EI CNTR CST-LS PSTS 10/69 RPL INSS | 93K
LC | 128125549 | 029/205 | T2 DI TRNTY CTTNWD 29/205 RPR ANCW | TABLEMTN | ETL.4040.POLE.STPS | 2024-02-02 | 2024-01-30 | 2025-01-21 | On-Time |  | 2025-01-30 | 2025-01-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46328445 | T2 DI TRNTY CTTNWD 29/205 RPR ANCW | ICW
LC | 128133492 | 027/211 | T2 DI MDL FRK GLD HL 27/211 RPR ANCW | SACTO | ETL.5140.POLE.STPS | 2024-02-05 | 2024-01-30 | 2024-04-08 | On-Time |  | 2024-07-30 | 2025-01-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46193245 | T2 DI MDL FRK GLD HL 27/211 RPR ANCW | ICW
LC | 128143281 | 028/199 | T2 DI TRINITY-COTTONWOOD 28/199L RMV VEG | TABLEMTN | ETL.4040.POLE.STPS | 2024-02-07 | 2024-01-30 | 2025-02-14 | Past Due |  | 2025-01-30 | 2025-01-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128143349 | 010/089 | T2 DI EL DR-MSRI FLAT #1 10/89 TOUCH | SACTO | ETL.1530.POLE.NWOD | 2024-02-07 | 2024-01-30 | 2024-01-30 | Past Due |  | 2024-07-30 | 2025-01-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Steel | Repair | 46472279 | T2 DI EL DR-MSRI FLAT #1 10/89 RPR STRS | ICS
LC | 128143394 | 006/106 | T2 DI COLGATE-PALERMO 6/106 RPR GYWW | SACTO | ETL.6500.POLE.NWOD | 2024-02-07 | 2024-01-30 | 2025-01-28 | On-Time |  | 2025-01-30 | 2025-01-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46382974 | T2 DI COLGATE-PALERMO 6/106 RPR GYWW | ICW
LC | 128143460 | 021/167 | T2 DI MDL FK-GLD HILL 21/167 COTTER | SACTO | ETL.5140.INSL.CERA | 2024-02-07 | 2024-01-30 | 2025-01-29 | On-Time |  | 2025-01-30 | 2025-01-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46389169 | T2 DI MDL FK-GLD HILL 21/167 COTTER | ICW
LC | 128143494 | A013/262 | T2 DI COLGATE-PALERMO A13/262 RPR INSW | SACTO | ETL.6500.INSL.NCER | 2024-02-07 | 2024-01-30 | 2024-04-28 | On-Time |  | 2024-07-30 | 2025-01-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46193246 | T2 DI COLGATE-PALERMO A13/262 RPR INSW | ICW
LC | 128148060 | 028/215 | T2 DI MDDLE FORK-GLD HLL 28/215 RPR GYWW | SACTO | ETL.5140.POLE.STPS | 2024-02-08 | 2024-01-30 | 2025-01-29 | On-Time |  | 2025-01-30 | 2025-01-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46389170 | T2 DI MDDLE FORK-GLD HLL 28/215 RPR GYWW | ICW
LC | 128148068 | 050/284 | T2 DI TEMBLOR-SLO-TWR 50/284 RPL INSS | PISMOBCH | ETL.3960.INSL.CERA | 2024-02-08 | 2024-01-30 | 2025-01-30 | On-Time |  | 2025-01-30 | 2025-01-30 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35585152 | T2 DI TEMBLOR-SLO-TWR 50/284 RPL INSS | 93K
LC | 128148155 | 012/228 | T2 DI COLGATE-PALERMO RPR POLE | TABLEMTN | ETL.6500.POLE.WOOD | 2024-02-08 | 2024-01-30 | 2025-01-28 | On-Time |  | 2025-01-30 | 2025-01-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46382975 | T2 DI COLGATE-PALERMO RPR POLE | ICW
LC | 128148271 | 025/198C | T2 DI MDL FK-GLD HILL 25/198C RPR INSW | SACTO | ETL.5140.INSL.NCER | 2024-02-08 | 2024-01-30 | 2025-01-29 | On-Time |  | 2025-01-30 | 2025-01-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46389171 | T2 DI MDL FK-GLD HILL 25/198C RPR INSW | ICW
LC | 128148335 | 009/071 | T2 DI EL DRDO-MSSRI FLT #1 9/71 RPL HRDD | SACTO | ETL.1530.POLE.WOOD | 2024-02-08 | 2024-01-30 | 2025-01-23 | On-Time |  | 2025-01-30 | 2025-01-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46459478 | T2 DI EL DRDO-MSSRI FLT #1 9/71 RPL HRDD | ICW
LC | 128148360 | 009/071 | T2 DI EL DRDO-MSSRI FLT #1 9/71 RMV VEG | SACTO | ETL.1530.POLE.WOOD | 2024-02-08 | 2024-01-30 | 2025-01-23 | On-Time |  | 2025-01-30 | 2025-01-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128148385 | 009/079 | T2 DI EL DRAD-MISSRI FLT#1 9/79 RPL INSW | SACTO | ETL.1530.INSL | 2024-02-08 | 2024-01-30 | 2025-01-23 | On-Time |  | 2025-01-30 | 2025-01-30 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35557740 | T2 DI EL DRAD-MISSRI FLT#1 9/79 RPL INSW | 93I
LC | 126711869 | 084/590 | T2 BRDGVLL-CTTNWD 84/590R RPL STRW | EUREKA | ETL.1110.POLE.WDPS | 2023-07-31 | 2023-07-31 | 2023-07-31 | Past Due |  | 2025-01-31 | 2025-01-31 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW PATR OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35505113 | T2 EI BRIDGEV-COTTONWOOD 84/592 RPL POLE | 70Y
LC | 128115417 | 003/031 | T2 EI PIT #6 TAP_003/031 COTTER | TABLEMTN | ETL.5441.INSL.CERA | 2024-01-31 | 2024-01-31 | 2025-01-21 | On-Time |  | 2025-01-31 | 2025-01-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46332031 | T2 EI PIT #6 TAP_003/031 COTTER | ICW
LC | 128115694 | 007/039 | T2 EI MRR BY-SN LS BSP #2 7/039 RPL INSS | PISMOBCH | ETL.2820.INSL | 2024-01-31 | 2024-01-31 | 2025-01-29 | On-Time |  | 2025-01-31 | 2025-01-31 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCL COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35585153 | T2 EI MRR BY-SN LS BSP #2 7/039 RPL INSS | 93K
LC | 129313569 | 008/132 | T3 ATSCDERO-SN LUIS OBSPO 8/132 RPR ROAD | PISMOBCH | ETL.8490.POLE.NWOD | 2024-07-31 | 2024-07-31 | 2024-08-28 | On-Time |  | 2025-01-31 | 2025-01-31 | 932 | TR3 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR3 PRTO FRAB ETRI | No Good/Out of Stdrd | Road | Repair | 45926543 | T3NT ATASCDRO-SN LS OBSPO 8/138 RMV BRSH | CHS
LC | 129315525 | 002/042 | T3 MIDDLEFORK #1 2/42 RPL POLE | SACTO | ETL.8405.POLE.WOOD | 2024-07-31 | 2024-07-31 | 2024-09-12 | On-Time |  | 2025-01-31 | 2025-01-31 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW TNT COMP OH FMOB TR3 PRTO FRAB | Rotten | Structure-Wood | Replace | 35576469 | T3 MIDDLEFORK #1 2/42 RPL POLE | 70Y
LC | 129324901 | B017/386-GUY | T3 DI ROLLINS TAP B017/386-GUY RPR GYWW | SACTO | ETL.6762.POLE.WOOD | 2024-08-02 | 2024-07-31 | 2024-10-24 | On-Time |  | 2025-01-31 | 2025-01-31 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46303845 | T3 DI ROLLINS TAP B017/386-GUY RPR GYWW | ICW
LC | 128119355 | 002/028 | T2 EI PIT #6 TAP_002/028 RPR CRSW | TABLEMTN | ETL.5441.POLE.STPS | 2024-02-01 | 2024-02-01 | 2025-01-29 | On-Time |  | 2025-02-01 | 2025-02-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46332034 | T2 EI PIT #6 TAP_002/028 RPR CRSW | ICW
LC | 128120195 | A012/268-GUY | T2 EI SALINAS-LAURELES A012/268 RMV VEG | MOSSLNDG | ETL.7930.POLE.WOOD | 2024-02-01 | 2024-02-01 | 2024-02-01 | Past Due |  | 2025-02-01 | 2025-02-01 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128120253 | 012/011 | T2 LOWR LKE-HOMSTKE 12/11 CANCEL | WILLITS | ETL.1481.POLE.WOOD | 2024-02-01 | 2024-02-01 | 2024-02-01 | Past Due |  | 2025-02-01 | 2025-02-01 | 505T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35528612 | T2 LOWR LKE-HOMSTKE 12/11 RPL EMRG | 92E
LC | 128120873 | 008/068 | T2 EI PIT #6 JCT-ROUND MTN 8/68 RPL INSS | TABLEMTN | ETL.5440.INSL | 2024-02-01 | 2024-02-01 | 2025-01-29 | On-Time |  | 2025-02-01 | 2025-02-01 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35571202 | T2 EI PIT #6 JCT-ROUND MTN 8/68 RPL INSS | 93K
LC | 128120892 | 008/068 | T2 EI PIT #6 JCT-RND MTN 8/068 RPL DMPS | TABLEMTN | ETL.5440.INSL | 2024-02-01 | 2024-02-01 | 2025-01-29 | On-Time |  | 2025-02-01 | 2025-02-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB | No Good/Out of Stdrd | Damper-Steel | Replace | 46332035 | T2 EI PIT #6 JCT-RND MTN 8/068 RPL DMPS | ICS
LC | 128148407 | 091/467 | T2 DI MLN-RND MTN #2 091/467 RPR SHLS | TABLEMTN | ETL.6020.TOWR | 2024-02-08 | 2024-02-01 | 2025-01-21 | On-Time |  | 2025-02-01 | 2025-02-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46332038 | T2 DI MLN-RND MTN #2 091/467 RPR SHLS | ICS
LC | 128162466 | 001/039 | T2 DI CTTNWD-BENTON #1 001/039 RPR GYWW | TABLEMTN | ETL.6640.POLE.NWOD | 2024-02-10 | 2024-02-01 | 2024-12-02 | On-Time |  | 2025-02-01 | 2025-02-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332039 | T2 DI CTTNWD-BENTON #1 001/039 RPR GYWW | ICW
LC | 129321632 | 002/016 | T3 MORAGA-OAKLAND #3 2/16 RPR STRT | CONCORD | ETL.2740.TOWR | 2024-08-01 | 2024-08-01 | 2025-06-10 | Past Due |  | 2025-02-01 | 2025-02-01 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46305867 | T3 MORAGA-OAKLAND #3 002/016 RPR STRT | ICQ
LC | 123007336 | 019/223 | T3NT DI IGNACIO-BLNAS #2 19/223 RPR IBWW | LAKEVLLE | ETL.7180.POLE.WOOD | 2022-02-23 | 2022-02-02 | 2023-10-09 | On-Time |  | 2025-02-02 | 2025-02-02 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR3 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 45486086 | T3 DI IGNACIO-BOLINAS #2 19/223 RPR IBWW | ICW
LC | 128125391 | B000/003 | T2 WV FULTON-CALISTOGA B000/003 TOUCH | LAKEVLLE | ETL.6880.POLE.NWOD | 2024-02-02 | 2024-02-02 | 2024-02-02 | Past Due |  | 2024-05-02 | 2025-02-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46505440 | T2 WV FULTON-CALISTOGA B000/003 TOUCH | ICW
LC | 128130016 | 012/230 | T2 VALLY SPRNGS #2 12/230 RPR STRW | VICTOR | ETL.9460.POLE.WOOD | 2024-02-05 | 2024-02-02 | 2024-09-19 | On-Time |  | 2025-02-02 | 2025-02-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46287944 | T2 VALLY SPRNGS #2 12/230 RPR STRW | ICW
LC | 128229128 | 004/008B | T2 LAYTONVILLE-COVELO 04/08B GO95 | WILLITS | ETL.7390.POLE.NWOD | 2024-02-29 | 2024-02-02 | 2025-06-10 | Past Due |  | 2025-02-02 | 2025-02-02 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CREW ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35537444 | T2 LAYTONVILLE-COVELO 04/08B GO95 | 93G
LC | 126733606 | 001/006 | T2 TRINITY-MAPLE CREEK 001/006 RPL ANCW | EUREKA | ETL.8170.POLE.WOOD | 2023-08-03 | 2023-08-03 | 2025-03-18 | Past Due |  | 2025-02-03 | 2025-02-03 | 637T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW CREW REMT COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35525605 | T2 TRINITY-MAPLE CREEK 001/006 RPL ANCW | 93E
LC | 122951949 | 009/052 | T2NT DI PARKWAY-MORAGA 9/52 RPR STRT | CONCORD | ETL.5930.TOWR | 2022-02-09 | 2022-02-05 | 2024-05-14 | On-Time |  | 2025-02-05 | 2025-02-05 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46174169 | T2NT DI PARKWAY-MORAGA 9/52 BNT STEEL | ICQ
LC | 128132160 | 004/040 | T2 MONTA VISTA-BURNS GO95 RPL STRW | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-02-05 | 2024-02-05 | 2025-05-14 | Past Due |  | 2025-02-05 | 2025-02-05 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35573802 | T2 MONTA VISTA-BURNS GO95 RPL STRW | 93G
LC | 128132563 | 037/319 | T2 EI PIT #1-CTTNWD 037/319 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2024-02-05 | 2024-02-05 | 2025-02-06 | Past Due |  | 2025-02-05 | 2025-02-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46306601 | T2 EI PIT #1-CTTNWD 037/319 BNT STEEL | ICQ
LC | 128136006 | 070/354A | T2 WV MLN-RND MTN #2 70/354A RPR SHIELD | TABLEMTN | ETL.6020.TOWR | 2024-02-06 | 2024-02-06 | 2025-01-30 | On-Time |  | 2025-02-06 | 2025-02-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46332036 | T2 WV MLN-RND MTN #2 70/354A RPR SHIELD | ICS
LC | 128136829 | 020/388 | T2 DI HT CRK #1-WESTWD 20/388 GO95 RPL | TABLEMTN | ETL.7030.POLE.WOOD | 2024-02-06 | 2024-02-06 | 2025-05-01 | Past Due |  | 2025-02-06 | 2025-02-06 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH RTNR TR2 PRTO AIR FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35534334 | T2 DI HT CRK #1-WESTWD 20/388 GO95 RPL | 93G
LC | 129335091 | 000/005 | T3 DIABLO-GATES #1 0/5 RPR FOND | PISMOBCH | ETL.5960.TOWR | 2024-08-06 | 2024-08-06 | 2024-08-06 | Past Due |  | 2025-02-06 | 2025-02-06 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46299537 | T3 DIABLO-GATES #1 00/05 RPR FOND | ICQ
LC | 129338334 | 008/118 | T3 MIDDLEFORK #1 8/118 RPL POLE | SACTO | ETL.8405.POLE.WOOD | 2024-08-06 | 2024-08-06 | 2025-01-27 | On-Time |  | 2025-02-06 | 2025-02-06 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW TNT COMP OH FMOB TR3 PRTO FRAB | Rotten | Structure-Wood | Replace | 35571901 | T3 MIDDLEFORK #1 8/118 RPL POLE | 70Y
LC | 122942750 | 000/005 | T3NT EI DIABLO-GATES #1 000/005 RPR STRS | PISMOBCH | ETL.5960.TOWR | 2022-02-07 | 2022-02-07 | 2023-07-26 | On-Time |  | 2025-02-07 | 2025-02-07 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Steel | Repair | 45616660 | T3 EI DIABLO-GATES #1 000/005 RPR STRS | ICS
LC | 128141846 | 004/034 | T2 DIVIDE-VANDENBERG #1 004/034 RPL SPLW | PISMOBCH | ETL.8620.INSL | 2024-02-07 | 2024-02-07 | 2025-01-14 | On-Time |  | 2025-02-07 | 2025-02-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO NTDE PGEQ | No Good/Out of Stdrd | Splice-Wood | Replace | 46329638 | T2 DIVIDE-VANDENBERG #1 004/034 RPL SPLW | ICW
LC | 128142826 | 006/076B | T2 WV JOLON TAP 006/076B RPL POLE | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-02-07 | 2024-02-07 | 2025-01-23 | On-Time |  | 2025-02-07 | 2025-02-07 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573682 | T2 WV JOLON TAP 006/076A RPL POLE | 70Y
LC | 128144626 | 000/009 | T2 EI MCSWAIN TAP 000/009 RPR GYWW | FRESNO | ETL.8991.POLE.WOOD | 2024-02-08 | 2024-02-07 | 2025-02-03 | On-Time |  | 2025-02-07 | 2025-02-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298330 | T2 EI MCSWAIN TAP 000/009 RPR GYWW | ICW
LC | 128168186 | 006/076A | T2 WV JOLON TAP 006/076A RPL POLE | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-02-13 | 2024-02-07 | 2025-01-23 | On-Time |  | 2025-02-07 | 2025-02-07 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573682 | T2 WV JOLON TAP 006/076A RPL POLE | 70Y
LC | 128168189 | 006/076C | T2 WV JOLON TAP 006/076C RPL POLE | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-02-13 | 2024-02-07 | 2025-01-23 | On-Time |  | 2025-02-07 | 2025-02-07 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573682 | T2 WV JOLON TAP 006/076A RPL POLE | 70Y
LC | 128964566 | 001/026 | T3 DSBLA-CNTRVLL 1/26L RPL STRW | TABLEMTN | ETL.6720.POLE.WDPS | 2024-06-01 | 2024-05-07 | 2025-04-18 | Past Due |  | 2025-02-07 | 2025-02-07 | 372T | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35558030 | T3 DI DSBLA-CNTRVLL 001/026L RPL STRW | 70Y
LC | 128964568 | 001/026 | T3 DSBLA-CNTRVLL 1/26R RPL STRW | TABLEMTN | ETL.6720.POLE.WDPS | 2024-06-01 | 2024-05-07 | 2025-04-18 | Past Due |  | 2025-02-07 | 2025-02-07 | 372T | TR3 | YES | E - Schd Compl Yr 0 | Closed | POHW COMP OH XMPT TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35558030 | T3 DI DSBLA-CNTRVLL 001/026L RPL STRW | 70Y
LC | 128964602 | 001/026 | T3 DSBLA-CNTRVLL 1/26C RPL STRW | TABLEMTN | ETL.6720.POLE.WDPS | 2024-06-01 | 2024-05-07 | 2025-04-18 | Past Due |  | 2025-02-07 | 2025-02-07 | 372T | TR3 | YES | E - Schd Compl Yr 0 | Closed | POHW COMP OH XMPT TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35558030 | T3 DI DSBLA-CNTRVLL 001/026L RPL STRW | 70Y
LC | 129406708 | 010/004 | T3 MENDO-WILLITS-FORT BRA 10/4R RPL STRW | WILLITS | ETL.7550.POLE.WDPS | 2024-08-19 | 2024-08-07 | 2025-01-17 | On-Time |  | 2025-02-07 | 2025-02-07 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW CREW COMP OH TR3 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35575356 | T3 MENDO-WILLITS-FORT BRA 10/4L RPL STRW | 70Y
LC | 129406773 | 010/004 | T3 MENDO-WILLITS-FORT BRA 10/4L RPL STRW | WILLITS | ETL.7550.POLE.WDPS | 2024-08-19 | 2024-08-07 | 2025-01-17 | On-Time |  | 2025-02-07 | 2025-02-07 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH TR3 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35575356 | T3 MENDO-WILLITS-FORT BRA 10/4L RPL STRW | 70Y
LC | 129526948 | 011/112 | T3 DI DRUM RIO OSO#2 11/112 INSP FOND | SACTO | ETL.1430.TOWR | 2024-09-12 | 2024-08-07 | 2025-01-30 | On-Time |  | 2025-02-07 | 2025-02-07 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46452801 | T3 DI DRUM RIO OSO#2 11/112 INSP FOND | ICQ
LC | 129526949 | 011/112 | T3 DI DRUM RIO OSO#2 11/112 RPR STRT | SACTO | ETL.1430.TOWR | 2024-09-12 | 2024-08-07 | 2025-01-30 | On-Time |  | 2025-02-07 | 2025-02-07 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381474 | T3 DI DRUM RIO OSO#2 11/112 RPR STRT | ICQ
LC | 123008761 | 059/534 | T2NT DI RND MTN-CTWD #3 59/534 BNT STEEL | TABLEMTN | ETL.5650.TOWR | 2022-02-23 | 2022-02-08 | 2023-06-26 | On-Time |  | 2025-02-08 | 2025-02-08 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45581904 | T2 DI RND MTN-CTTNWD #3 59/534 BNT STEEL | ICQ
LC | 126774727 | 066/001 | T2 HUMBOLDT-TRINITY 66/001L RPL POLE | EUREKA | ETL.1820.POLE.WDPS | 2023-08-08 | 2023-08-08 | 2023-08-08 | Past Due |  | 2025-02-08 | 2025-02-08 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW PATR OH FMOB XMPT TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35530633 | T2 EI HUMBOLDT-TRINITY 66/001L RPL POLE | 70Y
LC | 126872957 | 066/001 | T2 HUMBOLDT-TRINITY 66/001R RPL POLE | EUREKA | ETL.1820.POLE.WDPS | 2023-08-21 | 2023-08-08 | 2023-08-08 | Past Due |  | 2025-02-08 | 2025-02-08 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | POHW PATR OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35530633 | T2 EI HUMBOLDT-TRINITY 66/001L RPL POLE | 70Y
LC | 126872958 | 066/001 | T2 HUMBOLDT-TRINITY 66/001C RPL POLE | EUREKA | ETL.1820.POLE.WDPS | 2023-08-21 | 2023-08-08 | 2023-08-08 | Past Due |  | 2025-02-08 | 2025-02-08 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | POHW PATR OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35530633 | T2 EI HUMBOLDT-TRINITY 66/001L RPL POLE | 70Y
LC | 128144322 | 001/021D | T2 MTN QUARRIES TAP 001/021D RPL MKBL | SACTO | ETL.6991.POLE.WOOD | 2024-02-08 | 2024-02-08 | 2025-03-19 | Past Due |  | 2025-02-08 | 2025-02-08 | 671T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | FAA Lighting-Wood | Replace | 35542519 | T2 MTN QUARRIES TAP 001/021D RPL MKBL | 93P
LC | 128145652 | 008/049 | T2 PARKWAY-MORAGA 008/049 BNT STEEL | CONCORD | ETL.5930.TOWR | 2024-02-08 | 2024-02-08 | 2025-02-06 | On-Time |  | 2025-02-08 | 2025-02-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW REMT COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286419 | T2 PARKWAY-MORAGA 008/049 BNT STEEL | ICQ
LC | 128147886 | 006/011 | T2 VLY SPRNGS-CLVRS CMNT 6/11 GO95 CLEAR | VICTOR | ETL.8220.POLE.WOOD | 2024-02-08 | 2024-02-08 | 2024-09-27 | On-Time |  | 2025-02-08 | 2025-02-08 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35534664 | T2 VLY SPRNGS-CLVRS CMNT 6/11 GO95 CLEAR | 93G
LC | 128147909 | 004/106 | T2 COLGATE-GRSS VLLY 04/106 GO95 CLEAR | SACTO | ETL.6490.POLE.WOOD | 2024-02-08 | 2024-02-08 | 2024-03-09 | On-Time |  | 2025-02-08 | 2025-02-08 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35510451 | T2 COLGATE-GRASS VALLEY 4/104 GO95 CLEAR | 93G
LC | 122985586 | 000/002 | T2NT DI MORRO BAY-MESA 0/2 RPR FOND | PISMOBCH | ETL.5290.TOWR | 2022-02-15 | 2022-02-09 | 2023-08-02 | On-Time |  | 2025-02-09 | 2025-02-09 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCH COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45908257 | T2NT DI MORRO BAY-MESA 0/2 RPR FOND | ICQ
LC | 128150711 | 004/020 | T2 PITTSBURG-EASTSHORE 004/020 RPR FOND | CONCORD | ETL.5462.TOWR | 2024-02-09 | 2024-02-09 | 2025-01-28 | On-Time |  | 2025-02-09 | 2025-02-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW REMT COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46286461 | T2 PITTSBURG-EASTSHORE 004/020 RPR FOND | ICQ
LC | 128151966 | 001/043 | T2 PINE GROVE TAP 001/043 RPR POLE | VICTOR | ETL.8351.POLE.WOOD | 2024-02-09 | 2024-02-09 | 2024-08-13 | On-Time |  | 2025-02-09 | 2025-02-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR REMT SWRK ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46227585 | T2 PINE GROVE TAP 001/043 RPR POLE | ICW
LC | 128152490 | 003/028 | T2 EI HAT CREEK #1-PIT #1 03/28 RPR GYWW | TABLEMTN | ETL.7020.POLE.NWOD | 2024-02-09 | 2024-02-09 | 2024-05-16 | On-Time |  | 2024-08-09 | 2025-02-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46194282 | T2 EI HAT CREEK #1-PIT #1 03/28 RPR GYWW | ICW
LC | 128152492 | 003/030 | T2 EI HAT CREEK #1-PIT #1 03/30 RPR GYWW | TABLEMTN | ETL.7020.POLE.NWOD | 2024-02-09 | 2024-02-09 | 2024-05-16 | On-Time |  | 2024-08-09 | 2025-02-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46194283 | T2 EI HAT CREEK #1-PIT #1 03/30 RPR GYWW | ICW
LC | 128162881 | 008/094 | T2 VEDDER TAP 008/094 GO95 CLEAR | MIDWAY | ETL.2141.POLE.WOOD | 2024-02-10 | 2024-02-10 | 2024-05-01 | On-Time |  | 2025-02-10 | 2025-02-10 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35536714 | T2 VEDDER TAP 008/094 GO95 CLEAR | 70Y
LC | 128162981 | 001/018 | T2 EI PIT #6 1/18L RPR GRWW | TABLEMTN | ETL.5441.POLE.STPS | 2024-02-10 | 2024-02-10 | 2025-01-29 | On-Time |  | 2025-02-10 | 2025-02-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46332060 | T2 EI PIT #6 1/18L RPR GRWW | ICW
LC | 128163032 | 036/266 | T2 EI BELL-PLACER 036/266 COTTER | SACTO | ETL.4395.INSL.CERA | 2024-02-10 | 2024-02-10 | 2025-01-09 | On-Time |  | 2025-02-10 | 2025-02-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46325988 | T2 EI BELL-PLACER 036/266 COTTER | ICS
LC | 128163113 | 001/015 | T2 EI PIT #6 1/15L RPR GRWW | TABLEMTN | ETL.5441.POLE.WDPS | 2024-02-10 | 2024-02-10 | 2025-01-29 | On-Time |  | 2025-02-10 | 2025-02-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46332061 | T2 EI PIT #6 1/15L RPR GRWW | ICW
LC | 122970319 | 006/029 | T2NT EI DIABLO-GATES 6/029 RPR JMPS | PISMOBCH | ETL.5960.INSL.NCER | 2022-02-11 | 2022-02-11 | 2023-11-09 | On-Time |  | 2025-02-11 | 2025-02-11 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO | No Good/Out of Stdrd | Jumper-Steel | Repair | 45592089 | T2 EI DIABLO-GATES 6/029 RPR JMPS | ICS
LC | 128165049 | 001/013 | T2 EI PIT #6 1/13R RPR GYWW | TABLEMTN | ETL.5441.POLE.STPS | 2024-02-12 | 2024-02-12 | 2025-01-29 | On-Time |  | 2025-02-12 | 2025-02-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332062 | T2 EI PIT #6 1/13R RPR GYWW | ICW
LC | 128165350 | 001/013 | T2 EI PIT #6 1/13L RPR GYWW | TABLEMTN | ETL.5441.POLE.STPS | 2024-02-12 | 2024-02-12 | 2025-01-29 | On-Time |  | 2025-02-12 | 2025-02-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332063 | T2 EI PIT #6 1/13L RPR GYWW | ICW
LC | 128165430 | 001/012 | T2 EI PIT #6 TAP 001/012R RPR GYWW | TABLEMTN | ETL.5441.POLE.STPS | 2024-02-12 | 2024-02-12 | 2025-01-29 | On-Time |  | 2025-02-12 | 2025-02-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332064 | T2 EI PIT #6 TAP 001/012R RPR GYWW | ICW
LC | 128165439 | 007/087 | T2 WV VEDDER TAP 007/087 INS DMPW | MIDWAY | ETL.2141.POLE.NWOD | 2024-02-12 | 2024-02-12 | 2024-02-07 | On-Time |  | 2025-02-12 | 2025-02-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46287017 | T2 WV VEDDER TAP 007/087 INS DMPW | ICW
LC | 128165440 | 001/012 | T2 EI PIT #6 TAP 001/012L RPR GYWW | TABLEMTN | ETL.5441.POLE.STPS | 2024-02-12 | 2024-02-12 | 2025-01-29 | On-Time |  | 2025-02-12 | 2025-02-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332065 | T2 EI PIT #6 TAP 001/012L RPR GYWW | ICW
LC | 128165500 | 000/002 | T2 LOWER LAKE-HOMESTAKE 0/2 RPL GYPL | WILLITS | ETL.1481.POLE.WOOD | 2024-02-12 | 2024-02-12 | 2024-10-31 | On-Time |  | 2024-05-12 | 2025-02-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | Rotten | Guy Pole-Wood | Replace | 35574445 | T2 LOWER LAKE-HOMESTAKE 0/2 RPL GUY POLE | 70Y
LC | 128165614 | 47 | T2 DRUM-SPAULDING 008/212 RPR SWTC | SACTO | ETL.6770.SWIT | 2024-02-12 | 2024-02-12 | 2024-06-17 | On-Time |  | 2024-05-12 | 2025-02-12 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH FMOB TR2 PRTO DURA BRIN | Out of Adjustment | Switch | Repair | 46209472 | T2 DRUM-SPAULDING 008/212 RPR SWTC | ICE
LC | 128165983 | 001/011A | T2 EI PIT #6 TAP 01/011A RPR GYWW | TABLEMTN | ETL.5441.POLE.NWOD | 2024-02-12 | 2024-02-12 | 2025-01-21 | On-Time |  | 2025-02-12 | 2025-02-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332066 | T2 EI PIT #6 TAP 01/011A RPR GYWW | ICW
LC | 128166036 | 005/023 | T2 PITTSBURG-EASTSHORE 005/023 REGRADE | CONCORD | ETL.5462.TOWR | 2024-02-12 | 2024-02-12 | 2025-02-03 | On-Time |  | 2025-02-12 | 2025-02-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW REMT COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46286462 | T2 PITTSBURG-EASTSHORE 005/023 REGRADE | ICQ
LC | 128166037 | 001/011C | T2 EI PIT #6 TAP 01/011C RPR GYWW | TABLEMTN | ETL.5441.POLE.NWOD | 2024-02-12 | 2024-02-12 | 2025-01-21 | On-Time |  | 2025-02-12 | 2025-02-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332067 | T2 EI PIT #6 TAP 01/011C RPR GYWW | ICW
LC | 128166111 | 028/231 | T3 WV PIT #1-CTTNWD 28/231 RPR JMPW | TABLEMTN | ETL.5390.INSL.NCER | 2024-02-12 | 2024-02-12 | 2024-11-08 | On-Time |  | 2025-02-12 | 2025-02-12 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB XMPT TR3 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46194300 | T3 WV PIT #1-CTTNWD 28/231 RPR JMPW | ICW
LC | 128166391 | 000/009 | T2 EI PIT #6 TAP 000/09R RPR GYWW | TABLEMTN | ETL.5441.POLE.STPS | 2024-02-12 | 2024-02-12 | 2025-01-29 | On-Time |  | 2025-02-12 | 2025-02-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332068 | T2 EI PIT #6 TAP 000/09R RPR GYWW | ICW
LC | 128166411 | 000/009 | T2 EI PIT #6 TAP 000/09L RPR GYWW | TABLEMTN | ETL.5441.POLE.STPS | 2024-02-12 | 2024-02-12 | 2025-01-29 | On-Time |  | 2025-02-12 | 2025-02-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332069 | T2 EI PIT #6 TAP 000/09L RPR GYWW | ICW
LC | 128167090 | 012/163 | T2 EI WATSONVL-SALINS 12/163 RPR GYWW | MOSSLNDG | ETL.8310.POLE.WOOD | 2024-02-12 | 2024-02-12 | 2025-02-10 | On-Time |  | 2025-02-12 | 2025-02-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391193 | T2 EI WATSONVL-SALINS 12/163 RPR GYWW | ICW
LC | 128167349 | 000/006 | T2 EI PIT #6 TAP 000/06R RPL IBWW | TABLEMTN | ETL.5441.INSL.CERA | 2024-02-12 | 2024-02-12 | 2025-01-29 | On-Time |  | 2025-02-12 | 2025-02-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Replace | 46332070 | T2 EI PIT #6 TAP 000/06R RPL IBWW | ICW
LC | 128167450 | 000/008 | T2 EI PIT #6 TAP 000/08R RPR GYWW | TABLEMTN | ETL.5441.POLE.STPS | 2024-02-12 | 2024-02-12 | 2025-01-29 | On-Time |  | 2025-02-12 | 2025-02-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332071 | T2 EI PIT #6 TAP 000/08R RPR GYWW | ICW
LC | 128167460 | 000/008 | T2 EI PIT #6 TAP 000/08L RPR GYWW | TABLEMTN | ETL.5441.POLE.STPS | 2024-02-12 | 2024-02-12 | 2025-01-29 | On-Time |  | 2025-02-12 | 2025-02-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332072 | T2 EI PIT #6 TAP 000/08L RPR GYWW | ICW
LC | 128168494 | 016/326 | T2 CARIBOU-WESTWOOD 016/326 GO95 RPL | TABLEMTN | ETL.6300.POLE.WOOD | 2024-02-13 | 2024-02-12 | 2025-02-15 | Past Due |  | 2025-02-12 | 2025-02-12 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35535829 | T2 CARIBOU-WESTWOOD 016/326 GO95 RPL | 93G
LC | 129372316 | 001/014 | T3 DI EL DRDO-MISS FLT #1 1/14 RPL INSS | SACTO | ETL.1530.INSL | 2024-08-12 | 2024-08-12 | 2024-09-21 | On-Time |  | 2025-02-12 | 2025-02-12 | 532T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH FMOB TR3 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577306 | T3 DI EL DRDO-MISS FLT #1 1/14 RPL INSS | 93K
LC | 129435118 | 013/144 | T3 IGNACIO-BOLINAS #1 13/144 RPL ANCW | LAKEVLLE | ETL.7140.POLE.WOOD | 2024-08-26 | 2024-08-12 | 2024-08-12 | Past Due |  | 2025-02-12 | 2025-02-12 | 637T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OTHR FIRE ACCL OH TR3 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35533014 | T3 DI IGNACIO-BOLINAS #1 13/144 REFRAME | 93E
LC | 128168863 | 005/025 | T2 PITTSBURG-SAN RAMON 005/025 REGRADE | CONCORD | ETL.5490.TOWR | 2024-02-13 | 2024-02-13 | 2025-01-30 | On-Time |  | 2025-02-13 | 2025-02-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46286463 | T2 PITTSBURG-SAN RAMON 005/025 REGRADE | ICQ
LC | 128169911 | 032/243 | T2 EI HIGGINS-BELL 032/243 COTTER | SACTO | ETL.1412.INSL.CERA | 2024-02-13 | 2024-02-13 | 2025-01-21 | On-Time |  | 2025-02-13 | 2025-02-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300551 | T2 EI HIGGINS-BELL 032/243 COTTER | ICS
LC | 128172977 | 029/197 | T2 DI POE-RIO OSO-RIO OS 29/197 RPL HRDT | TABLEMTN | ETL.5540.TOWR | 2024-02-14 | 2024-02-13 | 2025-01-08 | On-Time |  | 2025-02-13 | 2025-02-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381957 | T2 DI POE-RIO OSO-RIO OS 29/197 RPL HRDT | ICQ
LC | 128183756 | 006/110 | T2 DI COLGATE-PALERMO 06/110 RPR JUMW | SACTO | ETL.6500.INSL.NCER | 2024-02-15 | 2024-02-13 | 2025-03-25 | Past Due |  | 2025-02-13 | 2025-02-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46382976 | T2 DI COLGATE-PALERMO 06/110 RPR JUMW | ICW
LC | 128183771 | 008/148 | T2 DI COLGATE-PALERMO 08/148 RPR GYWW | SACTO | ETL.6500.POLE.NWOD | 2024-02-15 | 2024-02-13 | 2025-02-08 | On-Time |  | 2025-02-13 | 2025-02-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46382977 | T2 DI COLGATE-PALERMO 08/148 RPR GYWW | ICW
LC | 128183776 | 005/093 | T2 DI COLGATE-PALERMO 05/93 RPL STRW | SACTO | ETL.6500.POLE.WOOD | 2024-02-15 | 2024-02-13 | 2025-03-24 | Past Due |  | 2025-02-13 | 2025-02-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557130 | T2 DI COLGATE-PALERMO 05/93 RPL STRW | 70Y
LC | 128183920 | 007/136 | T2 DI COLGATE-PALERMO 07/136 RPR INSW | SACTO | ETL.6500.INSL.CERA | 2024-02-15 | 2024-02-13 | 2025-02-08 | On-Time |  | 2025-02-13 | 2025-02-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator-Wood | Repair | 46382978 | T2 DI COLGATE-PALERMO 07/136 RPR INSW | ICW
LC | 128183922 | 007/136 | T2 DI COLGATE-PALERMO 07/136 RPR GYWW | SACTO | ETL.6500.POLE.NWOD | 2024-02-15 | 2024-02-13 | 2025-02-08 | On-Time |  | 2025-02-13 | 2025-02-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46382979 | T2 DI COLGATE-PALERMO 07/136 RPR GYWW | ICW
LC | 128183927 | 007/136 | T2 DI COLGATE-PALERMO 07/136 RPR ANCW | SACTO | ETL.6500.POLE.NWOD | 2024-02-15 | 2024-02-13 | 2025-02-08 | On-Time |  | 2025-02-13 | 2025-02-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46383042 | T2 DI COLGATE-PALERMO 07/136 RPR ANCW | ICW
LC | 128184866 | 017/249 | T2 DI CLAY-MARTEL 17/249 RPL HRDS | VICTOR | ETL.8250.POLE.NWOD | 2024-02-15 | 2024-02-13 | 2025-04-12 | Past Due |  | 2025-02-13 | 2025-02-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Steel | Replace | 46287945 | +T2 DI CLAY-MARTEL 17/249 RPL HRDS | ICS
LC | 128186710 | 023/170A | T2 DI TRINITY-CTTNWOOD 23/170A RPR ANCW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-02-15 | 2024-02-13 | 2024-06-04 | On-Time |  | 2024-08-13 | 2025-02-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46328447 | T2 DI TRINITY-CTTNWOOD 23/170A RPR ANCW | ICW
LC | 128186711 | 023/170A | T2 DI TRINITY-CTTNWD 23/170A RPR ANCW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-02-15 | 2024-02-13 | 2024-08-17 | On-Time |  | 2025-02-13 | 2025-02-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46306669 | T2 DI TRINITY-CTTNWD 23/170A RPR ANCW | ICW
LC | 128186712 | 023/170B | T2 DI TRINITY-COTTONWD 23/170B RPR ANCW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-02-15 | 2024-02-13 | 2024-08-18 | On-Time |  | 2025-02-13 | 2025-02-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46306663 | T2 DI TRINITY-COTTONWD 23/170B RPR ANCW | ICW
LC | 128186798 | 023/167A | T2 DI TRINITY-COTTONWOOD 23/167A RMV VEG | TABLEMTN | ETL.4040.POLE.NWOD | 2024-02-15 | 2024-02-13 | 2024-11-20 | On-Time |  | 2024-08-13 | 2025-02-13 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128186811 | 055/383 | T2 CARIBOU-TBL MTN 055/383 TOUCH | TABLEMTN | ETL.4440.TOWR | 2024-02-15 | 2024-02-13 | 2024-02-13 | Past Due |  | 2024-08-13 | 2025-02-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491531 | T2 DI CARIBOU-TBL MTN 055/383 TOUCH | ICQ
LC | 128186813 | 054/381 | T2 DI CARIBOU-TBL MTN 054/381 BNT STEEL | TABLEMTN | ETL.4440.TOWR | 2024-02-15 | 2024-02-13 | 2025-01-08 | On-Time |  | 2025-02-13 | 2025-02-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310425 | T2 DI CARIBOU-TBL MTN 054/381 BNT STEEL | ICQ
LC | 128186819 | 055/384 | T2 CARIBOU-TBL MTN 055/384 TOUCH | TABLEMTN | ETL.4440.TOWR | 2024-02-15 | 2024-02-13 | 2024-02-13 | Past Due |  | 2024-08-13 | 2025-02-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491532 | T2 DI CARIBOU-TBL MTN 055/384 TOUCH | ICQ
LC | 128186844 | 005/082 | T2 DI COLGATE-PALERMO 5/82 RPL INSW | SACTO | ETL.6500.INSL.CERA | 2024-02-15 | 2024-02-13 | 2025-04-29 | Past Due |  | 2025-02-13 | 2025-02-13 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35557129 | T2 DI COLGATE-PALERMO 5/082 RPL INSW | 93I
LC | 128186892 | 032/212 | T2 DI POE-RI SO-RIO OS 32/212 TOUCH | TABLEMTN | ETL.5540.TOWR | 2024-02-15 | 2024-02-13 | 2025-02-12 | On-Time |  | 2024-08-13 | 2025-02-13 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46459403 | T2 DI POE-RI SO-RIO OS 32/212 RMV ENCRCH | CHR
LC | 128186968 | 029/443 | T2 DI CLAY-MARTEL 29/443 RPR GYWW | VICTOR | ETL.8250.POLE.NWOD | 2024-02-15 | 2024-02-13 | 2025-04-30 | Past Due |  | 2025-02-13 | 2025-02-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46287947 | +T2 DI CLAY-MARTEL 29/443 RPR GYWW | ICW
LC | 128187041 | 010/201 | T2 DI COLGATE-PALERMO 10/201 RPL INSW | SACTO | ETL.6500.INSL.NCER | 2024-02-15 | 2024-02-13 | 2024-04-20 | On-Time |  | 2025-02-13 | 2025-02-13 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35533888 | T2 DI COLGATE-PALERMO 10/201 RPL INSW | 93I
LC | 128187113 | 054/382 | T2 CARIBOU-TABLE MNTN 54/382 BNT STEL | TABLEMTN | ETL.4440.TOWR | 2024-02-15 | 2024-02-13 | 2024-02-13 | Past Due |  | 2025-02-13 | 2025-02-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310426 | T2 DI CARIBOU-TABLE MNTN 54/382 BNT STEL | ICQ
LC | 128290424 | 013/168 | T2 DI WST PT-VLLY SPRNGS 13/168 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-02-13 | 2024-08-27 | On-Time |  | 2025-02-13 | 2025-02-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46229383 | T2 DI WST PT-VLLY SPRNGS 13/168 RPR GYWW | ICW
LC | 122982442 | 019/078 | T2NT EI DIABLO-MIDWAY #2 19/078 RPR STRT | PISMOBCH | ETL.5970.TOWR | 2022-02-14 | 2022-02-14 | 2023-07-06 | On-Time |  | 2025-02-14 | 2025-02-14 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45616679 | T2 EI DIABLO-MIDWAY #2 19/078 RPR STRT | ICQ
LC | 128172516 | 010/109 | T2 EI ARCO-CHOLAME 010/109L RPR GYWW | MIDWAY | ETL.8440.POLE.STPS | 2024-02-14 | 2024-02-14 | 2025-01-10 | On-Time |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46302307 | T2 EI ARCO-CHOLAME 010/109L RPR GYWW | ICW
LC | 128172541 | 010/109 | T2 EI ARCO-CHOLAME 010/109B RPR GYWW | MIDWAY | ETL.8440.POLE.STPS | 2024-02-14 | 2024-02-14 | 2025-01-10 | On-Time |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46302308 | T2 EI ARCO-CHOLAME 010/109B RPR GYWW | ICW
LC | 128172708 | 002/049 | T2 EI PINE GROVE TAP 2/49 RMV VEG | VICTOR | ETL.8351.POLE.WOOD | 2024-02-14 | 2024-02-14 | 2025-02-17 | Past Due |  | 2025-02-14 | 2025-02-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP PUBL ACCL COMP OH FMOB TR2 PRTO FRAR | Overgrown | Vegetation | Remove
LC | 128172999 | 006/060 | T2 EI DIVIDE-VANDENBERG#1 6/60 RPL INSW | PISMOBCH | ETL.8620.INSL | 2024-02-14 | 2024-02-14 | 2025-01-14 | On-Time |  | 2025-02-14 | 2025-02-14 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573269 | T2 EI DIVIDE-VANDENBERG#1 6/60 RPL INSW | 93I
LC | 128173387 | 015/318 | T2 WV KILARC-DESCHUTES 015/318 RPL ANCW | TABLEMTN | ETL.7300.POLE.NWOD | 2024-02-14 | 2024-02-14 | 2025-01-16 | On-Time |  | 2025-02-14 | 2025-02-14 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573780 | T2 WV KILARC-DESCHUTES 015/318 RPL ANCW | 93E
LC | 128173460 | 003/014 | T2 WV MNT VST-JEFRSN #1 03/14 RPR ATCG | METCALF | ETL.5220.TOWR | 2024-02-14 | 2024-02-14 | 2025-01-07 | On-Time |  | 2025-02-14 | 2025-02-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Anti-Climbing Guard | Structure-Tower | Repair | 46298813 | T2 WV MNT VST-JEFRSN #1 03/14 RPR ATCG | ICQ
LC | 128173464 | 001/012 | T2 EI DINOSAUR POINT TAP 1/12 RPR INSW | FRESNO | ETL.8961.INSL.NCER | 2024-02-14 | 2024-02-14 | 2025-03-17 | Past Due |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT ACCM COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298334 | T2 EI DINOSAUR POINT TAP 1/12 RPR INSW | ICW
LC | 128173465 | 001/012 | T2 EI DINOSAUR POINT TAP 1/12 RPR ANCW | FRESNO | ETL.8961.POLE.NWOD | 2024-02-14 | 2024-02-14 | 2025-03-17 | Past Due |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46298335 | T2 EI DINOSAUR POINT TAP 1/12 RPR ANCW | ICW
LC | 128173986 | 006/057 | T2 EI DIVIDE-VANDENBERG #1 6/57 RPR GRWW | PISMOBCH | ETL.8620.POLE.WOOD | 2024-02-14 | 2024-02-14 | 2025-01-14 | On-Time |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46329641 | T2 EI DIVIDE-VANDENBERG #1 6/57 RPR GRWW | ICW
LC | 128174021 | 006/057 | T2 EI DIVIDE-VANDENBERG #1 6/57 RPL INSW | PISMOBCH | ETL.8620.INSL | 2024-02-14 | 2024-02-14 | 2025-01-14 | On-Time |  | 2025-02-14 | 2025-02-14 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573268 | T2 EI DIVIDE-VANDENBERG #1 6/57 RPL INSW | 93I
LC | 128174215 | 006/054 | T2 EI DIVIDE-VANDENBERG #2 6/54 RPL INSW | PISMOBCH | ETL.8630.INSL | 2024-02-14 | 2024-02-14 | 2025-01-21 | On-Time |  | 2025-02-14 | 2025-02-14 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573302 | T2 EI DIVIDE-VANDENBERG #2 6/54 RPL INSW | 93I
LC | 128174369 | 005/104 | T2 EI CORDELIA #2 TAP 005/104 RPR STRW | SACTO | ETL.8184.POLE.WOOD | 2024-02-14 | 2024-02-14 | 2025-02-03 | On-Time |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337398 | T2 EI CORDELIA #2 TAP 005/104 RPR STRW | ICW
LC | 128174523 | 034/258 | T2 EI HIGGINS-BELL 034/258 RPL INSS | SACTO | ETL.1412.INSL.CERA | 2024-02-14 | 2024-02-14 | 2025-01-24 | On-Time |  | 2025-02-14 | 2025-02-14 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570807 | T2 EI HIGGINS-BELL RPL INSS 9 TWRS | 93K
LC | 128174524 | 034/258 | T2 EI HIGGINS-BELL 034/258 RPL HANGER | SACTO | ETL.1412.INSL.CERA | 2024-02-14 | 2024-02-14 | 2025-01-24 | On-Time |  | 2025-02-14 | 2025-02-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46327637 | T2 EI HIGGINS-BELL 034/258 RPL HANGER | ICQ
LC | 128174804 | 020/285 | T2 CLAY-MARTEL 20/285 RPR IBWW | VICTOR | ETL.8250.INSL.NCER | 2024-02-14 | 2024-02-14 | 2025-04-30 | Past Due |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR SWRK ACCH COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46191094 | +T2 CLAY-MARTEL 20/285 RPR IBWW | ICW
LC | 128186950 | 001/015 | T2 DI CHRISTIE-WLLW PASS 1/15 RPL STRW | CONCORD | ETL.6370.POLE.WOOD | 2024-02-15 | 2024-02-14 | 2025-01-31 | On-Time |  | 2025-02-14 | 2025-02-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573111 | T2 DI CHRISTIE-WLLW PASS 1/15 RPL STRW | 70Y
LC | 128186971 | 020/285 | T2 DI CLAY-MARTEL 020/285 RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-02-15 | 2024-02-14 | 2025-04-30 | Past Due |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46287948 | +T2 DI CLAY-MARTEL 020/285 RPR STRW | ICW
LC | 128188337 | 089/451 | T2 DI MALIN-ROUND MTN#2 89/451 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-02-16 | 2024-02-14 | 2025-02-06 | On-Time |  | 2025-02-14 | 2025-02-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332076 | T2 DI MALIN-ROUND MTN#2 89/451 RPR OPGW | ICS
LC | 128188415 | 027/182 | T2 DI POE RIO OSO 27/182 RPR STRT | TABLEMTN | ETL.5540.TOWR | 2024-02-16 | 2024-02-14 | 2025-02-05 | On-Time |  | 2025-02-14 | 2025-02-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381958 | T2 DI POE RIO OSO 27/182 RPR STRT | ICQ
LC | 128188497 | 088/448 | T2 DI MALIN-ROUND MTN#2 88/448 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-02-16 | 2024-02-14 | 2025-02-06 | On-Time |  | 2025-02-14 | 2025-02-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332077 | T2 DI MALIN-ROUND MTN#2 88/448 RPR OPGW | ICS
LC | 128188736 | 002/023 | T2 DI CHRSTIE WILLOW PS 02/023 RPR GYWW | CONCORD | ETL.6370.POLE.NWOD | 2024-02-16 | 2024-02-14 | 2024-02-22 | On-Time |  | 2024-08-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46199720 | T2 DI CHRSTIE WILLOW PS 02/023 RPR GYWW | ICW
LC | 128188922 | 000/003 | T2 DI CHRISTIE-WILLOW PASS 0/3 RPR GYWW | CONCORD | ETL.6370.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2025-01-23 | On-Time |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286496 | T2 DI CHRISTIE-WILLOW PASS 0/3 RPR GYWW | ICW
LC | 128188970 | 000/003 | T2 DI CHRISTIE-WILLOW PASS 0/3 RPR ANCW | CONCORD | ETL.6370.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2024-05-15 | On-Time |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46203843 | T2 DI CHRISTIE-WILLOW PASS 0/3 RPR ANCW | ICW
LC | 128188979 | 089/454 | T2 DI MALIN RND MTN#2 89/454 RPR INSS | TABLEMTN | ETL.6020.INSL | 2024-02-16 | 2024-02-14 | 2025-02-06 | On-Time |  | 2025-02-14 | 2025-02-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46332078 | T2NT DI MALIN RND MTN#2 89/454 RPR INSS | ICS
LC | 128189016 | 000/007 | T2 DI CHRSTIE WILLOW PS 00/007 RPL POLE | CONCORD | ETL.6370.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2025-01-31 | On-Time |  | 2025-02-14 | 2025-02-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573107 | T2 DI CHRSTIE WILLOW PS 00/007 RPL POLE | 70Y
LC | 128189037 | 000/010 | T2 DI CHRSTIE WILLOW PS 0/10 RPR GYWW | CONCORD | ETL.6370.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2025-03-13 | Past Due |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46447001 | T2 DI CHRSTIE WILLOW PS 0/10 RPR GYWW | ICW
LC | 128189523 | 092/469A | T2 DI MALIN-RND MNTN#2 92/469A RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-02-16 | 2024-02-14 | 2024-04-22 | On-Time |  | 2024-05-14 | 2025-02-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46201101 | T2 DI MALIN-RND MNTN#2 92/469A RPR OPGW | ICS
LC | 128189745 | 000/005 | T2 DI CHRISTIE-WILLOW PSS 0/5 RPR ANCW | CONCORD | ETL.6370.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2025-03-26 | Past Due |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46286497 | T2 DI CHRISTIE-WILLOW PSS 0/5 RPR ANCW | ICW
LC | 128190328 | 003/027 | T2 DI PIT#1-HAT CRK#2-BRNY 3/27 RPL HRDD | TABLEMTN | ETL.7040.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2025-05-21 | Past Due |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46332079 | T2 DI PIT#1-HAT CRK#2-BRNY 3/27 RPL HRDD | ICW
LC | 128190451 | 001/011 | T2 DI CHRISTIE-WILLOW PSS 1/11 RPR GYWW | CONCORD | ETL.6370.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2025-01-23 | On-Time |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286499 | T2 DI CHRISTIE-WILLOW PSS 1/11 RPR GYWW | ICW
LC | 128190458 | 001/011 | T2 DI CHRISTIE-WILLOW PSS 1/11 REFRAME | CONCORD | ETL.6370.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2025-01-29 | On-Time |  | 2025-02-14 | 2025-02-14 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35573109 | T2 DI CHRISTIE-WILLOW PSS 1/11 REFRAME | 93E
LC | 128190561 | 003/034 | T2 DI PIT#1-HAT CRK#2 BURNY 3/34 RMV VEG | TABLEMTN | ETL.7040.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2024-12-05 | On-Time |  | 2025-02-14 | 2025-02-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128190564 | 003/034 | T2 DI PIT#1-HAT CRK#2 BRNY 3/34 RPR ANCW | TABLEMTN | ETL.7040.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2024-04-22 | On-Time |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46236358 | T2 DI PIT#1-HAT CRK#2 BRNY 3/34 RPR ANCW | ICW
LC | 128190626 | 000/009 | T2 DI CHRISTIE-WLLW PASS 0/9 RPR GYWW | CONCORD | ETL.6370.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2025-01-23 | On-Time |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286498 | T2 DI CHRISTIE-WLLW PASS 0/9 RPR GYWW | ICW
LC | 128190993 | 021/293 | T2 DI CLAY-MARTEL 21/293 RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2025-04-30 | Past Due |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46287949 | +T2 DI CLAY-MARTEL 21/293 RPR STRW | ICW
LC | 128191061 | 028/409 | T2 DI CLAY-MARTEL 28/409 RPR GYWW | VICTOR | ETL.8250.POLE.NWOD | 2024-02-16 | 2024-02-14 | 2025-04-30 | Past Due |  | 2025-02-14 | 2025-02-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46287950 | +T2 DI CLAY-MARTEL 28/409 RPR GYWW | ICW
LC | 122984234 | 000/004 | T2NT EI KERCKFF #1-KECKF #2 0/4 RPL INSS | FRESNO | ETL.1880.INSL.CERA | 2022-02-15 | 2022-02-15 | 2023-05-20 | On-Time |  | 2025-02-15 | 2025-02-15 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 31596006 | T2 EI CHOWCHILLA-KERCKHOFF RPL INSS 2TWR | 93K
LC | 128203152 | 014/208 | T2 JOLON TAP 014/208 RPR GYWW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-02-22 | 2024-02-15 | 2025-01-15 | On-Time |  | 2025-02-15 | 2025-02-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391160 | T2 JOLON TAP 014/208 RPR GYWW | ICW
LC | 122989658 | 003/034 | T3NT EI ATASCDERO-CAYUCOS 03/34 REGRADE | PISMOBCH | ETL.8480.POLE.NWOD | 2022-02-16 | 2022-02-16 | 2023-03-06 | On-Time |  | 2025-02-16 | 2025-02-16 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Repair | 45600496 | T3NT EI ATASCDERO-CAYUCOS 03/34 REGRADE | ICW
LC | 128188881 | 009/106 | T2 DRUM-SUMMIT #1 9/106 INS DAMW | SACTO | ETL.1440.INSL.NCER | 2024-02-16 | 2024-02-16 | 2024-07-20 | On-Time |  | 2025-02-16 | 2025-02-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46283617 | T2 DRUM-SUMMIT #1 9/106 INS DAMW | ICW
LC | 128190969 | 031/233 | T2 EI HIGGINS-BELL 031/233 RPL INSS | SACTO | ETL.1412.INSL.CERA | 2024-02-16 | 2024-02-16 | 2025-01-22 | On-Time |  | 2025-02-16 | 2025-02-16 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570807 | T2 EI HIGGINS-BELL RPL INSS 9 TWRS | 93K
LC | 128190990 | 007/059 | T2 EI EL DRDO-MSSR FLT #1 7/59 RPR GYWT | SACTO | ETL.1530.TOWR | 2024-02-16 | 2024-02-16 | 2024-12-30 | On-Time |  | 2025-02-16 | 2025-02-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46327638 | T2 EI EL DRDO-MSSR FLT #1 7/59 RPR GYWT | ICQ
LC | 128191007 | 000/003 | T2 EI MOUNTAIN GATE TAP 000/003 RPR SWTC | TABLEMTN | ETL.7641.POLE.WOOD | 2024-02-16 | 2024-02-16 | 2025-01-07 | On-Time |  | 2025-02-16 | 2025-02-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Switch-Wood | Repair | 46303864 | T2 EI MOUNTAIN GATE TAP 000/003 RPR SWTC | ICW
LC | 128193416 | 000/004 | T2 EI MTN GATE JCT-CASCADE 0/4 RPR SWTC | TABLEMTN | ETL.7640.POLE.WOOD | 2024-02-18 | 2024-02-16 | 2025-01-07 | On-Time |  | 2025-02-16 | 2025-02-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Switch-Wood | Repair | 46303865 | T2 EI MTN GATE JCT-CASCADE 0/4 RPR SWTC | ICW
LC | 128192661 | 033/252 | T2 EI HIGGINS-BELL 033/252 RPL INSS | SACTO | ETL.1412.INSL.CERA | 2024-02-17 | 2024-02-17 | 2025-01-22 | On-Time |  | 2025-02-17 | 2025-02-17 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570807 | T2 EI HIGGINS-BELL RPL INSS 9 TWRS | 93K
LC | 123001097 | 009/040 | T2NT DI DIABLO-GATES #1 009/040 RPR GYWS | PISMOBCH | ETL.5960.TOWR | 2022-02-21 | 2022-02-18 | 2023-07-24 | On-Time |  | 2025-02-18 | 2025-02-18 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45616726 | T2 DI DIABLO-GATES #1 009/040 RPR GYWS | ICS
LC | 126859135 | 048/001A | T2 HUMBOLDT-TRINITY 48/001A RPL STRW | EUREKA | ETL.1820.POLE.NWOD | 2023-08-18 | 2023-08-18 | 2023-08-18 | Past Due |  | 2025-02-18 | 2025-02-18 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35530632 | T2 HUMBOLDT-TRINITY 48/001A RPL STRW | 70Y
LC | 126859351 | 048/001B | T2 HUMBOLDT-TRINITY 48/001B RPL STRW | EUREKA | ETL.1820.POLE.NWOD | 2023-08-18 | 2023-08-18 | 2023-08-18 | Past Due |  | 2025-02-18 | 2025-02-18 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | REGW CREW OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35530632 | T2 HUMBOLDT-TRINITY 48/001A RPL STRW | 70Y
LC | 126859384 | 048/001C | T2 HUMBOLDT-TRINITY 48/001C RPL STRW | EUREKA | ETL.1820.POLE.NWOD | 2023-08-18 | 2023-08-18 | 2023-08-18 | Past Due |  | 2025-02-18 | 2025-02-18 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | REGW CREW OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35530632 | T2 HUMBOLDT-TRINITY 48/001A RPL STRW | 70Y
LC | 128195780 | 011/248 | T2 EI SALINAS-LAURELES 011/248 RPR SWTC | MOSSLNDG | ETL.7930.POLE.NWOD | 2024-02-20 | 2024-02-20 | 2025-01-15 | On-Time |  | 2025-02-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT TRAF SWRK ACCL ACCM ACCH FLAG USA COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Switch-Wood | Repair | 46329984 | T2 EI SALINAS-LAURELES 011/248 RPR SWTC | ICW
LC | 128195972 | 006/053 | T2 EI DIVIDE-VANDENBERG #2 6/53 RPL INSW | PISMOBCH | ETL.8630.INSL | 2024-02-20 | 2024-02-20 | 2025-01-21 | On-Time |  | 2025-02-20 | 2025-02-20 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573300 | T2 EI DIVIDE-VANDENBERG #2 6/53 RPL INSW | 93I
LC | 128196084 | 004/057 | T2 WV JOLON TAP 004/057 INS DAMW | MOSSLNDG | ETL.7321.INSL.NCER | 2024-02-20 | 2024-02-20 | 2025-01-30 | On-Time |  | 2025-02-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46391056 | T2 WV JOLON TAP 004/057 INS DAMW | ICW
LC | 128196743 | 006/051 | T2 EI DIVIDE-VANDENBERG #2 6/51 RPL INSW | PISMOBCH | ETL.8630.INSL | 2024-02-20 | 2024-02-20 | 2025-01-21 | On-Time |  | 2025-02-20 | 2025-02-20 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573278 | T2 EI DIVIDE-VANDENBERG #2 6/51 RPL INSW | 93I
LC | 128196916 | 012/156 | T2 WATSONVILLE-SALINAS 12/156 RPR HRDW | MOSSLNDG | ETL.8310.POLE.WOOD | 2024-02-20 | 2024-02-20 | 2025-02-12 | On-Time |  | 2025-02-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Hardware-Wood | Replace | 46391194 | T2 WATSONVILLE-SALINAS 12/156 RPR HRDW | ICW
LC | 128197121 | 006/049 | T2 EI DIVIDE-VANDENBERG #2 6/49 RPL INSW | PISMOBCH | ETL.8630.INSL | 2024-02-20 | 2024-02-20 | 2025-01-22 | On-Time |  | 2025-02-20 | 2025-02-20 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573277 | T2 EI DIVIDE-VANDENBERG #2 6/49 RPL INSW | 93I
LC | 128197610 | 033/250 | T2 EI HIGGINS-BELL 033/250 RPL INSS | SACTO | ETL.1412.INSL.CERA | 2024-02-20 | 2024-02-20 | 2025-01-23 | On-Time |  | 2025-02-20 | 2025-02-20 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570807 | T2 EI HIGGINS-BELL RPL INSS 9 TWRS | 93K
LC | 128197787 | 087/442 | T2 DI MALIN-ROUND MNT#2 87/442 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-02-20 | 2024-02-20 | 2025-02-08 | On-Time |  | 2025-02-20 | 2025-02-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332081 | T2 DI MALIN-ROUND MNT#2 87/442 RPR OPGW | ICS
LC | 128199751 | 028/196C | T2 DI TRINITY-CTNWD 28/196C RPR ANCW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-02-21 | 2024-02-20 | 2024-07-19 | On-Time |  | 2025-02-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46204597 | T2 DI TRINITY-CTNWD 28/196C RPR ANCW | ICW
LC | 128202203 | 001/025 | T2 DI COTTONWOOD-BENTON #1 1/25 RPR POLE | TABLEMTN | ETL.6640.POLE.WOOD | 2024-02-21 | 2024-02-20 | 2024-12-02 | On-Time |  | 2025-02-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46332401 | T2 DI COTTONWOOD-BENTON #1 1/25 RPR POLE | ICW
LC | 128202208 | 009/115 | T2 DI JOLON TAP 9/115 RMV VEG | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-02-21 | 2024-02-20 | 2024-05-03 | On-Time |  | 2024-08-20 | 2025-02-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE SPCR CNCL OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128202212 | B020/452 | T2 DI DRM-GRSS VLLY-WMR B20/452 RPR POLE | SACTO | ETL.6760.POLE.WOOD | 2024-02-21 | 2024-02-20 | 2025-01-15 | On-Time |  | 2025-02-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46323903 | T2 DI DRM-GRSS VLLY-WMR B20/452 RPR POLE | ICW
LC | 128202235 | 086/439 | T2 DI MLN-RND MTN #2 086/439 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-02-21 | 2024-02-20 | 2025-02-08 | On-Time |  | 2025-02-20 | 2025-02-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332402 | T2 DI MLN-RND MTN #2 086/439 RPR OPGW | ICS
LC | 128202303 | 007/093 | T2 DI JOLON TAP 007/093 RPR STRW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-02-21 | 2024-02-20 | 2025-02-03 | On-Time |  | 2025-02-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46391058 | T2 DI JOLON TAP 007/093 RPR STRW | ICW
LC | 128202304 | 007/093 | T2 DI JOLON TAP 007/093 RMV VEG | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-02-21 | 2024-02-20 | 2024-05-14 | On-Time |  | 2024-08-20 | 2025-02-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128202320 | 086/437 | T2 DI MLN-RND MTN #2 86/437 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-02-21 | 2024-02-20 | 2025-02-09 | On-Time |  | 2025-02-20 | 2025-02-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332403 | T2 DI MLN-RND MTN #2 86/437 RPR OPGW | ICS
LC | 128202390 | 018/257B | T2 DI CLAY-MARTEL 018/257B RPL STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-02-21 | 2024-02-20 | 2025-04-12 | Past Due |  | 2025-02-20 | 2025-02-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573119 | +T2 DI CLAY-MARTEL 018/257B RPL STRW | 70Y
LC | 128202404 | 012/059 | T2 DI MSS LNDG-LS BNS 012/059 RPL INSS | MOSSLNDG | ETL.6040.INSL | 2024-02-21 | 2024-02-20 | 2025-04-14 | Past Due |  | 2025-02-20 | 2025-02-20 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35596168 | T2 DI MSS LNDNG-LS BNS 36/159 RPL INSS | 93K
LC | 128204491 | B024/553 | T2 DI DRUM-GRS VLY-WEMR B24/553 RPR GYWW | SACTO | ETL.6760.POLE.NWOD | 2024-02-22 | 2024-02-20 | 2025-01-15 | On-Time |  | 2025-02-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46323904 | T2 DI DRUM-GRS VLY-WEMR B24/553 RPR GYWW | ICW
LC | 128204495 | B025/577 | T2 DI DRUM GRS VLY WMR B025/577 RPR GYWW | SACTO | ETL.6760.POLE.WOOD | 2024-02-22 | 2024-02-20 | 2024-04-06 | On-Time |  | 2024-05-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46209477 | T2 DI DRUM GRS VLY WMR B025/577 RPR GYWW | ICW
LC | 128204499 | B025/577 | T2 DI DRUM GRS VLY WMR B025/577 RPR ADSS | SACTO | ETL.6760.POLE.WOOD | 2024-02-22 | 2024-02-20 | 2024-04-06 | On-Time |  | 2024-05-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46209478 | T2 DI DRUM GRS VLY WMR B025/577 RPR ADSS | ICW
LC | 128204748 | 000/008 | T2 DI ROLLINS TAP 00/08 RPR ANCW | SACTO | ETL.6762.POLE.NWOD | 2024-02-22 | 2024-02-20 | 2025-02-10 | On-Time |  | 2025-02-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46453054 | T2 DI ROLLINS TAP 00/08 RPR ANCW | ICW
LC | 128205257 | 000/007 | T2 DI ROLLINS TAP 00/07 RPR ANCW | SACTO | ETL.6762.POLE.WOOD | 2024-02-22 | 2024-02-20 | 2024-06-25 | On-Time |  | 2024-08-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46204966 | T2 DI ROLLINS TAP 00/07 RPR ANCW | ICW
LC | 128205460 | 000/013 | T2 DI ROLLINS TAP 00/13 RPR STRW | SACTO | ETL.6762.POLE.WOOD | 2024-02-22 | 2024-02-20 | 2025-02-10 | On-Time |  | 2025-02-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46453055 | T2 DI ROLLINS TAP 00/13 RPR STRW | ICW
LC | 128205590 | 007/094 | T2 DI JOLON TAP 7/94 RMV VEG | MOSSLNDG | ETL.7321.POLE.NWOD | 2024-02-22 | 2024-02-20 | 2024-05-10 | On-Time |  | 2024-08-20 | 2025-02-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128205591 | 007/094 | T2 DI JOLON TAP 7/94 RPR ANCW | MOSSLNDG | ETL.7321.POLE.NWOD | 2024-02-22 | 2024-02-20 | 2024-04-01 | On-Time |  | 2024-08-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46211389 | T2 DI JOLON TAP 7/94 RPR ANCW | ICW
LC | 128205595 | 000/014 | T2 DI JOLON TAP 00/14 RPR ANCW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-02-22 | 2024-02-20 | 2024-04-01 | On-Time |  | 2024-08-20 | 2025-02-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46211390 | T2 DI JOLON TAP 00/14 RPR ANCW | ICW
LC | 128205765 | 008/003 | T2 DI SALINAS-FORT ORD#1 8/3 RPL INSS | MOSSLNDG | ETL.7890.INSL.CERA | 2024-02-22 | 2024-02-20 | 2025-02-21 | Past Due |  | 2025-02-20 | 2025-02-20 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35597473 | T2 DI SALINAS-FORT ORD#1 RPL INSS 3 LSTS | 93K
LC | 128205981 | 087/440 | T2 DI MALIN-ROUND MTN #2 87/440 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-02-22 | 2024-02-20 | 2025-02-08 | On-Time |  | 2025-02-20 | 2025-02-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332082 | T2 DI MALIN-ROUND MTN #2 87/440 RPR OPGW | ICS
LC | 128205989 | 008/004 | T2 DI SALINAS-FORT ORD #2 08/04 RPL INSS | MOSSLNDG | ETL.8423.INSL.NCER | 2024-02-22 | 2024-02-20 | 2025-02-18 | On-Time |  | 2025-02-20 | 2025-02-20 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35597474 | T2 DI SALINAS-FORT ORD #2 RPL INSS 2 LST | 93K
LC | 128206030 | 086/436 | T2 DI MALIN-ROUND MTN #2 86/436 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-02-22 | 2024-02-20 | 2025-02-08 | On-Time |  | 2025-02-20 | 2025-02-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332404 | T2 DI MALIN-ROUND MTN #2 86/436 RPR OPGW | ICS
LC | 128206039 | 086/436 | T2 DI MALIN-ROUND MTN #2 86/436 RPR STRT | TABLEMTN | ETL.6020.TOWR | 2024-02-22 | 2024-02-20 | 2024-02-20 | Past Due |  | 2025-02-20 | 2025-02-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381352 | T2 DI MALIN-ROUND MTN #2 86/436 RPR STRT | ICQ
LC | 130737411 | 001/014 | T3NT EL DRDO-MSSRI FLAT #1 1/14 RPR FOND | SACTO | ETL.1530.TOWR | 2025-01-13 | 2024-08-20 | 2024-08-20 | Past Due |  | 2027-08-20 | 2025-02-20 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR3 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair
LC | 128199712 | 031/234 | T2 EI HIGGINS-BELL 031/234 RPL INSS | SACTO | ETL.1412.INSL.CERA | 2024-02-21 | 2024-02-21 | 2025-01-23 | On-Time |  | 2025-02-21 | 2025-02-21 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570807 | T2 EI HIGGINS-BELL RPL INSS 9 TWRS | 93K
LC | 128199951 | 000/001 | T2 EI GRANITE ROCK TP 00/01 GRND WASH | MOSSLNDG | ETL.8311.INSL.CERA | 2024-02-21 | 2024-02-21 | 2025-04-05 | Past Due |  | 2025-02-21 | 2025-02-21 | 622 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC SWRK COMP OH FMOB TR2 PRTO | Contaminated | Insulator | Ground Wash | 46305515 | T2 EI GRANITE ROCK TP 00/01 GRND WASH | ICD
LC | 128200014 | 031/237 | T2 EI HIGGINS-BELL 031/237 RPL INSS | SACTO | ETL.1412.INSL.CERA | 2024-02-21 | 2024-02-21 | 2025-01-24 | On-Time |  | 2025-02-21 | 2025-02-21 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570807 | T2 EI HIGGINS-BELL RPL INSS 9 TWRS | 93K
LC | 128200070 | 000/003 | T2 EI GRANITE ROCK TP 00/03 GRND WASH | MOSSLNDG | ETL.8311.INSL.CERA | 2024-02-21 | 2024-02-21 | 2025-04-05 | Past Due |  | 2024-08-21 | 2025-02-21 | 622 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC SWRK COMP OH FMOB TR2 PRTO DURA BRIN | Contaminated | Insulator | Ground Wash | 46305516 | T2 EI GRANITE ROCK TP 00/03 GRND WASH | ICD
LC | 128200182 | 000/005 | T2 EI GRANITE ROCK TP 00/05 GRND WASH | MOSSLNDG | ETL.8311.INSL.CERA | 2024-02-21 | 2024-02-21 | 2025-04-05 | Past Due |  | 2025-02-21 | 2025-02-21 | 622 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC SWRK COMP OH FMOB TR2 PRTO | Contaminated | Insulator | Ground Wash | 46305518 | T2 EI GRANITE ROCK TP 00/05 GRND WASH | ICD
LC | 128200415 | 031/238 | T2 EI HIGGINS-BELL 031/238 RPL INSS | SACTO | ETL.1412.INSL.CERA | 2024-02-21 | 2024-02-21 | 2025-01-22 | On-Time |  | 2025-02-21 | 2025-02-21 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570807 | T2 EI HIGGINS-BELL RPL INSS 9 TWRS | 93K
LC | 128200957 | 032/241 | T2 EI HIGGINS-BELL 032/241 RPL INSS | SACTO | ETL.1412.INSL.CERA | 2024-02-21 | 2024-02-21 | 2025-01-22 | On-Time |  | 2025-02-21 | 2025-02-21 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570807 | T2 EI HIGGINS-BELL RPL INSS 9 TWRS | 93K
LC | 128200958 | 032/240 | T2 EI HIGGINS-BELL 032/240 RPL INSS | SACTO | ETL.1412.INSL.CERA | 2024-02-21 | 2024-02-21 | 2025-01-23 | On-Time |  | 2025-02-21 | 2025-02-21 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570807 | T2 EI HIGGINS-BELL RPL INSS 9 TWRS | 93K
LC | 128201446 | 033/246 | T2 EI HIGGINS-BELL 033/246 COTTER | SACTO | ETL.1412.INSL.NCER | 2024-02-21 | 2024-02-21 | 2025-01-21 | On-Time |  | 2025-02-21 | 2025-02-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300556 | T2 EI HIGGINS-BELL 033/246 COTTER | ICS
LC | 128201638 | 002/054 | T2 PINE GROVE TAP 002/054 RMV VEG | VICTOR | ETL.8351.POLE.WOOD | 2024-02-21 | 2024-02-21 | 2025-02-17 | On-Time |  | 2025-02-21 | 2025-02-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAR | Overgrown | Vegetation | Remove
LC | 128202867 | 000/011 | T2 DI ROLLINS TAP-00/11 RPL HRDW | SACTO | ETL.6762.POLE.WOOD | 2024-02-22 | 2024-02-21 | 2025-02-10 | On-Time |  | 2025-02-21 | 2025-02-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46453053 | T2 DI ROLLINS TAP-00/11 RPL HRDW | ICW
LC | 128202931 | 000/011 | T2 DI ROLLINS TAP-00/11 RPR ANCW | SACTO | ETL.6762.POLE.WOOD | 2024-02-22 | 2024-02-21 | 2024-06-28 | On-Time |  | 2024-08-21 | 2025-02-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46209474 | T2 DI ROLLINS TAP-00/11 RPR ANCW | ICW
LC | 128205670 | 010/086 | T2 DI EL DRDO MIS FLT #1 10/86 RPL HRDW | SACTO | ETL.1530.POLE.WOOD | 2024-02-22 | 2024-02-21 | 2025-01-23 | On-Time |  | 2025-02-21 | 2025-02-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46459477 | T2 DI EL DRDO MIS FLT #1 10/86 RPL HRDW | ICW
LC | 128205857 | 038/249 | T2 DI POE-RIO OSO 38/249 RMV VEG | TABLEMTN | ETL.5540.TOWR | 2024-02-22 | 2024-02-21 | 2024-09-18 | On-Time |  | 2025-02-21 | 2025-02-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128206035 | 089/455 | T2 DI MALIN-RND MNTN#2 89/455 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-02-22 | 2024-02-21 | 2025-02-06 | On-Time |  | 2025-02-21 | 2025-02-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332405 | T2 DI MALIN-RND MNTN#2 89/455 RPR OPGW | ICS
LC | 128206118 | 087/445 | T2 DI MALIN-RND MNTN#2 87/445 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-02-22 | 2024-02-21 | 2025-02-08 | On-Time |  | 2025-02-21 | 2025-02-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332406 | T2 DI MALIN-RND MNTN#2 87/445 RPR OPGW | ICS
LC | 128206208 | 090/456 | T2 DI MALIN-RND MNTN#2 90/456 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-02-22 | 2024-02-21 | 2024-04-21 | On-Time |  | 2024-05-21 | 2025-02-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46230822 | T2 DI MALIN-RND MNTN#2 90/456 RPR OPGW | ICS
LC | 128206243 | 008/005 | T2 DI SALINAS-FORT ORD #2 08/05 RPR CONS | MOSSLNDG | ETL.8423.INSL.CERA | 2024-02-22 | 2024-02-21 | 2025-02-19 | On-Time |  | 2025-02-21 | 2025-02-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Steel | Repair | 46391201 | T2 DI SALINAS-FORT ORD #2 08/05 RPR CONS | ICS
LC | 128206311 | 007/090 | T2 DI JOLON TAP 07/90 RMV VEG | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-02-22 | 2024-02-21 | 2024-05-14 | On-Time |  | 2024-08-21 | 2025-02-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128206312 | 007/090 | T2 DI JOLON TAP 07/90 RPR ANCW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-02-22 | 2024-02-21 | 2024-04-01 | On-Time |  | 2024-08-21 | 2025-02-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46211391 | T2 DI JOLON TAP 07/90 RPR ANCW | ICW
LC | 128206314 | 007/090 | T2 DI JOLON TAP 07/90 RPR INSW | MOSSLNDG | ETL.7321.INSL.CERA | 2024-02-22 | 2024-02-21 | 2025-01-15 | On-Time |  | 2025-02-21 | 2025-02-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46391162 | T2 DI JOLON TAP 07/90 RPR INSW | ICW
LC | 128207698 | 001/018 | T2 DI CHRISTIE-FRANKLIN #1 1/18 RPR GYWW | CONCORD | ETL.6350.POLE.NWOD | 2024-02-23 | 2024-02-21 | 2024-07-24 | On-Time |  | 2025-02-21 | 2025-02-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46203842 | T2 DI CHRISTIE-FRANKLIN #1 1/18 RPR GYWW | ICW
LC | 128945091 | 087/443 | T2 DI MLN-RND MNTN#2 87/443 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-05-31 | 2024-02-21 | 2025-02-08 | On-Time |  | 2025-02-21 | 2025-02-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46332445 | T2 DI MLN-RND MNTN#2 87/443 RPR SHLD | ICS
LC | 129418226 | 002/017 | T3 MORAGA-OAKLAND #3 2/17 RPR CRST | CONCORD | ETL.2740.TOWR | 2024-08-21 | 2024-08-21 | 2024-10-03 | On-Time |  | 2024-11-21 | 2025-02-21 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Crossarm-Tower | Repair | 46303644 | T3 MORAGA-OAKLAND #3 2/17 RPR STRT | ICQ
LC | 123006571 | 010/044 | T2NT DI DIABLO-GTS #1 10/44 RPP BOLLARD | PISMOBCH | ETL.5960.TOWR | 2022-02-23 | 2022-02-22 | 2023-07-26 | On-Time |  | 2025-02-22 | 2025-02-22 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45616738 | T2 DI DIABLO-GATES #1 010/44 RPP BOLLARD | ICQ
LC | 123031900 | 050/205 | T2NT DI MIDWAY-WHRLWND 50/205 RPR STRT | MIDWAY | ETL.6030.TOWR | 2022-02-28 | 2022-02-22 | 2023-06-13 | On-Time |  | 2025-02-22 | 2025-02-22 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45616855 | T2 DI MIDWAY-WHIRLWIND 050/205 BNT STEEL | ICQ
LC | 126880697 | 092/000C | T2 HUMBOLDT-TRINITY 92/0C INS ANCHW | EUREKA | ETL.1820.POLE.NWOD | 2023-08-22 | 2023-08-22 | 2025-04-23 | Past Due |  | 2025-02-22 | 2025-02-22 | 637 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW CREW REMT SWRK COMP OH FMOB XMPT TR2 PRTO FRAB | Missing | Anchor-Wood | Install | 31680990 | T2 HUMBOLDT-TRINITY 92/0C STAT HOLD | 93E
LC | 126883585 | 091/000 | T2 HUMBOLDT-TRINITY 091/000R RPL POLE | EUREKA | ETL.1820.POLE.WDPS | 2023-08-22 | 2023-08-22 | 2023-08-22 | Past Due |  | 2025-02-22 | 2025-02-22 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW NONR OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35530634 | T2 HUMBOLDT-TRINITY 091/000R RPL POLE | 70Y
LC | 127044581 | 091/000 | T2 HUMBOLDT-TRINITY 091/000L RPL POLE | EUREKA | ETL.1820.POLE.WDPS | 2023-09-13 | 2023-08-22 | 2023-08-22 | Past Due |  | 2025-02-22 | 2025-02-22 | 372 | TR2 | YES | E - Schd Compl Yr 0 | Open | POHW NONR OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35530634 | T2 HUMBOLDT-TRINITY 091/000R RPL POLE | 70Y
LC | 128203563 | 010/134 | T2 EI WATSONVL-SALINS 10/134 BACKFILL | MOSSLNDG | ETL.8310.POLE.NWOD | 2024-02-22 | 2024-02-22 | 2025-02-12 | On-Time |  | 2025-02-22 | 2025-02-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMC REMT SWRK SPCR ACCL COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Wood | Remove | 46391195 | T2 EI WATSONVL-SALINS 10/134 BACKFILL | ICW
LC | 128204613 | 092/000 | T2 HUMBOLDT-TRINITY 92/0B INS ANCHW | EUREKA | ETL.1820.POLE.NWOD | 2024-02-22 | 2023-08-22 | 2024-11-10 | On-Time |  | 2025-02-22 | 2025-02-22 | 637 | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW CREW REMT SWRK COMP OH FMOB XMPT TR2 PRTO FRAB | Missing | Anchor-Wood | Install | 31680990 | T2 HUMBOLDT-TRINITY 92/0C STAT HOLD | 93E
LC | 128204616 | 092/000A | T2 HUMBOLDT-TRINITY 92/0A INS ANCW | EUREKA | ETL.1820.POLE.NWOD | 2024-02-22 | 2023-08-22 | 2024-11-10 | On-Time |  | 2025-02-22 | 2025-02-22 | 637 | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW CREW REMT SWRK COMP OH FMOB XMPT TR2 PRTO FRAB | Missing | Anchor-Wood | Install | 31680990 | T2 HUMBOLDT-TRINITY 92/0C STAT HOLD | 93E
LC | 128205113 | 008/000 | T2 WV MENDOCINO-HARTLEY 8/0 RPL GYWW | WILLITS | ETL.7510.POLE.NWOD | 2024-02-22 | 2024-02-22 | 2024-02-22 | Past Due |  | 2025-02-22 | 2025-02-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Replace | 46333772 | T2 WV MENDOCINO-HARTLEY 8/0 RPL GYWW | ICW
LC | 128205118 | 001/026 | T2 EI VOLTA-SOUTH 001/026 RPR POLE | TABLEMTN | ETL.8300.POLE.WOOD | 2024-02-22 | 2024-02-22 | 2025-01-14 | On-Time |  | 2025-02-22 | 2025-02-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311141 | T2 EI VOLTA-SOUTH 001/026 RPR POLE | ICW
LC | 128205390 | 003/077 | T2 EI VOLTA-SOUTH 03/77 RPR POLE | TABLEMTN | ETL.8300.POLE.WOOD | 2024-02-22 | 2024-02-22 | 2025-01-13 | On-Time |  | 2025-02-22 | 2025-02-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311140 | T2 EI VOLTA-SOUTH 03/77 RPR POLE | ICW
LC | 128209695 | 024/338-GUY | T2 DI CLAY-MARTEL 24/338-GUY RMV VEG | VICTOR | ETL.8250.POLE.WOOD | 2024-02-23 | 2024-02-22 | 2024-09-11 | On-Time |  | 2025-02-22 | 2025-02-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH VEG TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128215051 | 056/312 | T2 TEMBLOR-SAN LUIS OBISPO 56/312 COTTER | PISMOBCH | ETL.3960.INSL | 2024-02-26 | 2024-02-22 | 2025-02-24 | Past Due |  | 2025-02-22 | 2025-02-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329668 | T2 TEMBLOR-SAN LUIS OBISPO 56/312 COTTER | ICS
LC | 128222575 | 003/072 | T2 PLACER-DEL MAR 003/072 GO95 | SACTO | ETL.7800.POLE.WOOD | 2024-02-28 | 2024-02-22 | 2025-02-17 | On-Time |  | 2025-02-22 | 2025-02-22 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35534403 | T2 PLACER-DEL MAR 003/072 GO95 | 93G
LC | 129423902 | 008/150 | T3 WV FRNCH MDWS-MDDL FRK 8/150 INS DAMW | SACTO | ETL.6870.INSL | 2024-08-22 | 2024-08-22 | 2024-09-13 | On-Time |  | 2025-02-22 | 2025-02-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 NTDE | Missing | Damper-Wood | Install | 46322178 | T3 WV FRNCH MDWS-MDDL FRK 8/150 INS DAMW | ICW
LC | 129424878 | 002/019 | T3 MORAGA-OAKLAND #3 02/19 RPR CRST | CONCORD | ETL.2740.TOWR | 2024-08-22 | 2024-08-22 | 2024-10-03 | On-Time |  | 2024-11-22 | 2025-02-22 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Crossarm-Tower | Repair | 46305602 | T3 MORAGA-OAKLAND #3 02/19 RPR CRST | ICQ
LC | 129444633 | 001/016 | T3 DI GRIZZLY-BUCKS CREEK 01/16 RPR SHLD | TABLEMTN | ETL.2395.POLE.STPS | 2024-08-27 | 2024-08-22 | 2024-11-21 | On-Time |  | 2025-02-22 | 2025-02-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Wood | Repair | 46328470 | T3 DI GRIZZLY-BUCKS CREEK 01/16 RPR SHLD | ICW
LC | 123008392 | 035/141 | T2NT EI DIABLO-MIDWAY#3 35/141 BNT STEEL | PISMOBCH | ETL.5980.TOWR | 2022-02-23 | 2022-02-23 | 2023-07-13 | On-Time |  | 2025-02-23 | 2025-02-23 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45616739 | T2 EI DIABLO-MIDWAY #3 035/141 BNT STEEL | ICQ
LC | 123032040 | 050/202 | T2NT DI MIDWY-WHIRLWIND 50/202 RPR GYWS | MIDWAY | ETL.6030.TOWR | 2022-02-28 | 2022-02-23 | 2023-06-14 | On-Time |  | 2025-02-23 | 2025-02-23 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45617370 | T2 DI MIDWAY-WHIRLWIND 050/202 RPR GYWS | ICS
LC | 128208169 | 007/137 | T2 EI CARIBOU-WESTWOOD 7/137R RPL ANCW | TABLEMTN | ETL.6300.POLE.WDPS | 2024-02-23 | 2024-02-23 | 2025-02-18 | On-Time |  | 2025-02-23 | 2025-02-23 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK ACCH USA COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35556134 | T2 EI CARIBOU-WESTWOOD 7/137R RPL ANCW | 93E
LC | 128209563 | 005/000 | T2 WV MENDCNO-PHLO-HPLND 05/00 RPL STRW | WILLITS | ETL.7520.POLE.NWOD | 2024-02-23 | 2024-02-23 | 2025-01-29 | On-Time |  | 2025-02-23 | 2025-02-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574223 | T2 WV MENDCNO-PHLO-HPLND 05/00 RPL STRW | 70Y
LC | 128213917 | 009/185 | T2 MONTA VISTA-LOS GATOS 9/185 GO95 | METCALF | ETL.7610.POLE.WOOD | 2024-02-26 | 2024-02-23 | 2024-02-23 | Past Due |  | 2025-02-23 | 2025-02-23 | 401 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR2 PRTO FRAR | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35534676 | T2 MNTA VSTA-LS GTS 009/185 GO95 | 93G
LC | 123019465 | 028/409 | T2NT WV CLAY-MARTEL 28/409 RPL SPLW | VICTOR | ETL.8250.INSL.NCER | 2022-02-24 | 2022-02-24 | 2023-06-28 | On-Time |  | 2025-02-24 | 2025-02-24 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2N PRTO NTDE | No Good/Out of Stdrd | Splice-Wood | Replace | 45513996 | T2 WV CLAY-MARTEL 28/409 RPL SPLW | ICW
LC | 126907266 | 061/000A | T2 DI HUMBOLDT-TRNTY 61/0A RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2023-08-24 | 2023-08-24 | 2024-11-09 | On-Time |  | 2025-02-24 | 2025-02-24 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46203484 | T2 DI HUMBOLDT-TRNTY 61/0A RPR GYWW | ICW
LC | 126907341 | 061/000B | T2 DI HUMBOLDT-TRNTY 61/0B RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2023-08-24 | 2023-08-24 | 2024-11-09 | On-Time |  | 2025-02-24 | 2025-02-24 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46203486 | T2 DI HUMBOLDT-TRNTY 61/0B RPR GYWW | ICW
LC | 126953754 | 061/005 | T2 DI HUMBOLDT-TRINITY 61/5 RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2023-08-30 | 2023-08-24 | 2024-11-11 | On-Time |  | 2025-02-24 | 2025-02-24 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46203485 | T2 DI HUMBOLDT-TRINITY 61/5 RPR JUMW | ICW
LC | 128210766 | 001/012 | T2 EI FLINT TAP-115 kV_001/012 RPR JMPW | SACTO | ETL.3341.INSL.CERA | 2024-02-24 | 2024-02-24 | 2025-01-16 | On-Time |  | 2025-02-24 | 2025-02-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Jumper-Wood | Repair | 46324622 | T2 EI FLINT TAP-115 KV_001/012 RPR JMPW | ICW
LC | 128210767 | 001/012 | T2 EI FLINT TAP-115 kV_001/012 RPR GYWW | SACTO | ETL.3341.POLE.WOOD | 2024-02-24 | 2024-02-24 | 2025-01-16 | On-Time |  | 2025-02-24 | 2025-02-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324623 | T2 EI FLINT TAP-115 KV_001/012 RPR GYWW | ICW
LC | 128211051 | 000/005 | T2 EI FLINT TAP 00/005 RPL INSW | SACTO | ETL.3341.INSL.CERA | 2024-02-24 | 2024-02-24 | 2025-01-16 | On-Time |  | 2025-02-24 | 2025-02-24 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35558171 | T2 EI FLINT TAP 00/005 RPL INSW | 93I
LC | 123032150 | 053/474 | T2NT DI RND MTN-COTTONWD 53/474 RPR STRT | TABLEMTN | ETL.5650.TOWR | 2022-02-28 | 2022-02-26 | 2023-07-19 | On-Time |  | 2025-02-26 | 2025-02-26 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45581857 | T2 DI RND MTN-COTTONWD 53/474 BNT STEEL | ICQ
LC | 128212072 | 018/370 | T2 CRIBU-WSTWD 018/370 GO95 | TABLEMTN | ETL.6300.POLE.WOOD | 2024-02-26 | 2024-02-26 | 2025-02-14 | On-Time |  | 2025-02-26 | 2025-02-26 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35533891 | T2 CRIBU-WSTWD 018/370 GO95 | 93G
LC | 128212076 | 018/380 | T2 CRIBU-WSTWD 018/380 GO95 | TABLEMTN | ETL.6300.POLE.NWOD | 2024-02-26 | 2024-02-26 | 2025-02-15 | On-Time |  | 2025-02-26 | 2025-02-26 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35533895 | T2 CRIBU-WSTWD 018/380 GO95 | 93G
LC | 128212077 | 016/338 | T2 CRIBU-WSTWD 016/338 GO95 | TABLEMTN | ETL.6300.POLE.WOOD | 2024-02-26 | 2024-02-26 | 2025-02-14 | On-Time |  | 2025-02-26 | 2025-02-26 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35533876 | T2 CRIBU-WSTWD 016/338 GO95 | 93G
LC | 128212763 | 69 | T2 EI TEJON-LEBEC 7/136 RPR SWITCH | MIDWAY | ETL.9250.SWIT | 2024-02-26 | 2024-02-26 | 2025-03-03 | Past Due |  | 2025-02-26 | 2025-02-26 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Out of Adjustment | Switch | Repair | 46302317 | T2 EI TEJON-LEBEC 7/136 RPR SWTICH | ICE
LC | 128213569 | 015/287 | T2 WV FULTN-MOLINO-COTTI 15/287 INS DMPW | LAKEVLLE | ETL.6910.INSL.NCER | 2024-02-26 | 2024-02-26 | 2025-01-08 | On-Time |  | 2025-02-26 | 2025-02-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46305574 | T2 WV FULTN-MOLINO-COTTI 15/287 INS DMPW | ICW
LC | 128214151 | 005/069 | T2 HAT CREEK #1-PIT #1 005/069 GO95 | TABLEMTN | ETL.7020.POLE.WOOD | 2024-02-26 | 2024-02-26 | 2025-05-07 | Past Due |  | 2025-02-26 | 2025-02-26 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35534116 | T2 HAT CREEK #1-PIT #1 005/069 GO95 | 93G
LC | 128214666 | 025/413 | T2 WV KESWICK-TRINITY 25/413 RPL ANCW | TABLEMTN | ETL.7270.POLE.NWOD | 2024-02-26 | 2024-02-26 | 2025-02-22 | On-Time |  | 2025-02-26 | 2025-02-26 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573707 | T2 WV KESWICK-TRINITY 25/413 RPL ANCW | 93E
LC | 128214758 | 037/217 | T2 DI TEMBLOR LS OBSPO 37/217 RPR STRT | PISMOBCH | ETL.3960.TOWR | 2024-02-26 | 2024-02-26 | 2024-02-26 | Past Due |  | 2025-02-26 | 2025-02-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46303829 | T2 DI TEMBLOR LS OBSPO 37/217 BNT STEEL | ICQ
LC | 128214881 | 037/217 | T2 DI TMBLR SN LS OBSPO 37/217 RMV VEG | PISMOBCH | ETL.3960.TOWR | 2024-02-26 | 2024-02-26 | 2024-12-26 | On-Time |  | 2025-02-26 | 2025-02-26 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128214915 | 002/021 | T2 DI ATSCDR CYCS 2/21 RPL HRDW | PISMOBCH | ETL.8480.POLE.STPS | 2024-02-26 | 2024-02-26 | 2025-02-05 | On-Time |  | 2025-02-26 | 2025-02-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46329634 | T2 DI ATSCDR CYCS 2/21 RPL HRDW | ICW
LC | 128214919 | 002/021 | T2 DI ATSCDR CYCS 2/21 RPR GYWW | PISMOBCH | ETL.8480.POLE.STPS | 2024-02-26 | 2024-02-26 | 2025-02-05 | On-Time |  | 2025-02-26 | 2025-02-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46329635 | T2 DI ATSCDR CYCS 2/21 RPR GYWW | ICW
LC | 128215054 | 008/066 | T2 EI CBRILLO-SNTA YNEZ SS 8/66 RPR GYWW | PISMOBCH | ETL.1200.POLE.NWOD | 2024-02-26 | 2024-02-26 | 2025-02-25 | On-Time |  | 2025-02-26 | 2025-02-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46329101 | T2 EI CBRILLO-SNTA YNEZ SS 8/66 RPR GYWW | ICW
LC | 128215066 | 038/222 | T2 DI TMBLOR-SN LUIS OBSP 38/222 RMV VEG | PISMOBCH | ETL.3960.TOWR | 2024-02-26 | 2024-02-26 | 2024-12-26 | On-Time |  | 2025-02-26 | 2025-02-26 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128215122 | 019/089 | T2 DI MS LNDNG LS BNS 19/89 RPL DAMS | MOSSLNDG | ETL.6040.INSL.CERA | 2024-02-26 | 2024-02-26 | 2025-02-23 | On-Time |  | 2025-02-26 | 2025-02-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Damper-Steel | Replace | 46305507 | T2 DI MS LNDNG LS BNS 19/89 RPL DAMS | ICS
LC | 128215303 | 015/352 | T2 DI DRM-GRS VALY-WEMR 15/352 RPR SWTCH | SACTO | ETL.6760.POLE.WOOD | 2024-02-26 | 2024-02-26 | 2025-01-27 | On-Time |  | 2025-02-26 | 2025-02-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Switch-Wood | Repair | 46323905 | T2 DI DRM-GRS VALY-WEMR 15/352 RPR SWTCH | ICW
LC | 128225465 | 006/007 | T2 DI SLNS-FRT ORD #2 6/7 RMV NEST | MOSSLNDG | ETL.8423.POLE.NWOD | 2024-02-28 | 2024-02-26 | 2025-02-05 | On-Time |  | 2025-02-26 | 2025-02-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46391202 | T2 DI SLNS-FRT ORD #2 6/7 RMV NEST | ICS
LC | 128225511 | 000/012 | T2 DI VALLEY SPRINGS #1 00/12 RPL IBWW | VICTOR | ETL.8210.POLE.WOOD | 2024-02-28 | 2024-02-26 | 2025-01-31 | On-Time |  | 2025-02-26 | 2025-02-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46289521 | T2 DI VALLEY SPRINGS #1 00/12 RPL IBWW | ICW
LC | 128225547 | 004/031B | T2 DI TRINITY-COTTONWOOD 4/31B RPR ANCW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-02-28 | 2024-02-26 | 2025-01-16 | On-Time |  | 2025-02-26 | 2025-02-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46332408 | T2 DI TRINITY-COTTONWOOD 4/31B RPR ANCW | ICW
LC | 128225567 | 018/408 | T2 DI DRUM-GRSS VLY-WMR 18/408 RPR GYWW | SACTO | ETL.6760.POLE.NWOD | 2024-02-28 | 2024-02-26 | 2024-03-29 | On-Time |  | 2024-08-26 | 2025-02-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46210365 | T2 DI DRUM-GRSS VLY-WMR 18/408 RPR GYWW | ICW
LC | 128225598 | 001/020 | T2 DI VALLEY SPRINGS #1 1/20 BACKFILL | VICTOR | ETL.8210.POLE.NWOD | 2024-02-28 | 2024-02-26 | 2025-01-06 | On-Time |  | 2025-02-26 | 2025-02-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46289522 | T2 DI VALLEY SPRINGS #1 1/20 BACKFILL | ICW
LC | 128225630 | 012/059B3 | T2 DI FULTON-PUEBLO 12/059B3 RPR GYWW | LAKEVLLE | ETL.1600.POLE.NWOD | 2024-02-28 | 2024-02-26 | 2025-02-13 | On-Time |  | 2025-02-26 | 2025-02-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46403097 | T2 DI FULTON-PUEBLO 12/059B3 RPR GYWW | ICW
LC | 128225744 | 092/471C | T2 DI MLN-RND MTN #2 92/471C RPR SHLS | TABLEMTN | ETL.6020.TOWR | 2024-02-28 | 2024-02-26 | 2025-01-30 | On-Time |  | 2025-02-26 | 2025-02-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46332409 | T2 DI MLN-RND MTN #2 92/471C RPR SHLS | ICS
LC | 128225747 | 017/399 | T2 DI DRUM-GRSS VLY-WMR 17/399 RMV VEG | SACTO | ETL.6760.POLE.WOOD | 2024-02-28 | 2024-02-26 | 2025-02-01 | On-Time |  | 2025-02-26 | 2025-02-26 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128225748 | 017/399 | T2 DI DRUM-GRSS VLY-WMR 17/399 RPR ANCW | SACTO | ETL.6760.POLE.WOOD | 2024-02-28 | 2024-02-26 | 2025-01-27 | On-Time |  | 2025-02-26 | 2025-02-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46323906 | T2 DI DRUM-GRSS VLY-WMR 17/399 RPR ANCW | ICW
LC | 128225770 | 012/059B1 | T2 DI FULTON-PUEBLO 12/059B1 RPR ANCW | LAKEVLLE | ETL.1600.POLE.NWOD | 2024-02-28 | 2024-02-26 | 2025-02-13 | On-Time |  | 2025-02-26 | 2025-02-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46403096 | T2 DI FULTON-PUEBLO 12/059B1 RPR ANCW | ICW
LC | 128229725 | 007/002 | T2 DI SALINAS-FORT ORD #2 7/2 BNT STEEL | MOSSLNDG | ETL.8423.POLE.NWOD | 2024-02-29 | 2024-02-26 | 2025-01-29 | On-Time |  | 2025-02-26 | 2025-02-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46325950 | T2 DI SALINAS-FORT ORD #2 7/2 BNT STEEL | ICQ
LC | 128229803 | 018/413 | T2 DI DRM GRS VLY-WEMR 18/413 RPR INSW | SACTO | ETL.6760.INSL.NCER | 2024-02-29 | 2024-02-26 | 2025-04-16 | Past Due |  | 2025-02-26 | 2025-02-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator-Wood | Repair | 46323908 | T2 DI DRM GRS VLY-WEMR 18/413 RPR INSW | ICW
LC | 128229920 | 019/090 | T2 DI MS LNDG LS BNOS 19/90 RPR SHLD | MOSSLNDG | ETL.6040.TOWR | 2024-02-29 | 2024-02-26 | 2025-02-12 | On-Time |  | 2025-02-26 | 2025-02-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46305508 | T2 DI MS LNDG LS BNOS 19/90 RPR SHLD | ICS
LC | 129444953 | 000/001A | T3 DI GRIZZLY-BUCKS CREEK 0/1A RPR JUMW | TABLEMTN | ETL.2395.INSL.NCER | 2024-08-27 | 2024-08-26 | 2024-09-09 | On-Time |  | 2025-02-26 | 2025-02-26 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46323232 | T3 DI GRIZZLY-BUCKS CREEK 0/1A RPR JUMW | ICW
LC | 128216677 | 000/004 | T2 EI PIT #6 TAP 000/004 RPL INSS | TABLEMTN | ETL.5441.INSL.CERA | 2024-02-27 | 2024-02-27 | 2025-01-30 | On-Time |  | 2025-02-27 | 2025-02-27 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35571203 | T2 EI PIT #6 TAP RPL INSS 2 TWRS | 93K
LC | 128216912 | 011/233 | T2 CARIBOU-WESTWOOD 11/233 GO95 | TABLEMTN | ETL.6300.POLE.WOOD | 2024-02-27 | 2024-02-27 | 2025-03-12 | Past Due |  | 2025-02-27 | 2025-02-27 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35534216 | T2 CARIBOU-WESTWOOD 11/233 GO95 | 93G
LC | 128217552 | 004/053 | T2 HAT CREEK #1-PIT #1 4/53 GO95 REPLACE | TABLEMTN | ETL.7020.POLE.WOOD | 2024-02-27 | 2024-02-27 | 2025-05-07 | Past Due |  | 2025-02-27 | 2025-02-27 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35534249 | T2 HAT CREEK #1-PIT #1 4/53 GO95 REPLACE | 93G
LC | 128217553 | 004/056 | T2 HAT CREEK #1-PIT #1 4/56 GO95 REPLACE | TABLEMTN | ETL.7020.POLE.WOOD | 2024-02-27 | 2024-02-27 | 2025-05-07 | Past Due |  | 2025-02-27 | 2025-02-27 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35534251 | T2 HAT CREEK #1-PIT #1 4/56 GO95 REPLACE | 93G
LC | 128217956 | 000/001 | T2 EI PIT #6 TAP 00/001 RPL INSS | TABLEMTN | ETL.5441.INSL.CERA | 2024-02-27 | 2024-02-27 | 2025-01-30 | On-Time |  | 2025-02-27 | 2025-02-27 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35571203 | T2 EI PIT #6 TAP RPL INSS 2 TWRS | 93K
LC | 128218452 | 011/258-GUY | T2 SALINAS-LAURELES 11/258G RPL GUY POLE | MOSSLNDG | ETL.7930.POLE.WOOD | 2024-02-27 | 2024-02-27 | 2025-01-16 | On-Time |  | 2025-02-27 | 2025-02-27 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH TR2 PRTO FRAB | Rotten | Guy Pole-Wood | Replace | 35507120 | T2 DI SALINAS-LAURELES 11/258 RPL POLE | 70Y
LC | 128220881 | 012/320 | T2 COLGATE-GRASS VALLEY 012/320 GO95 CLR | SACTO | ETL.6490.POLE.WOOD | 2024-02-27 | 2024-02-27 | 2025-02-27 | On-Time |  | 2025-02-27 | 2025-02-27 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAR NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35536564 | T2 COLGATE-GRASS VALLEY 012/320 GO95 CLR | 93G
LC | 128221005 | 008/167 | T2 WV MNTA VISTA-LS GATOS 8/167 INS DMPW | METCALF | ETL.7610.INSL.NCER | 2024-02-27 | 2024-02-27 | 2025-01-14 | On-Time |  | 2025-02-27 | 2025-02-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46286799 | T2 WV MNTA VISTA-LS GATOS 8/167 INS DMPW | ICW
LC | 128225409 | 014/325 | T2 DI DRUM-GRS VLY-WMR 14/325 RPR JUMW | SACTO | ETL.6760.INSL.NCER | 2024-02-28 | 2024-02-27 | 2024-07-17 | On-Time |  | 2025-02-27 | 2025-02-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR NTDE DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46210363 | T2 DI DRUM-GRS VLY-WMR 14/325 RPR JUMW | ICW
LC | 128225468 | 006/002 | T2 DI SALINAS-FORT ORD #2 6/2 RMV VEG | MOSSLNDG | ETL.8423.POLE.NWOD | 2024-02-28 | 2024-02-27 | 2025-01-09 | On-Time |  | 2025-02-27 | 2025-02-27 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128225469 | 006/002 | T2 DI SLNS-FRT ORD #2 6/2 RPR FOND | MOSSLNDG | ETL.8423.POLE.NWOD | 2024-02-28 | 2024-02-27 | 2025-01-27 | On-Time |  | 2025-02-27 | 2025-02-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46325949 | T2 DI SLNS-FRT ORD #2 6/2 RPR FOND | ICQ
LC | 128225491 | 014/325 | T2 DI DRUM-GRS VLY-WMR 14/325 RPL INSW | SACTO | ETL.6760.INSL.NCER | 2024-02-28 | 2024-02-27 | 2025-01-08 | On-Time |  | 2025-02-27 | 2025-02-27 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35554345 | T2 DI DRUM-GRS VLY-WMR 14/325 RPL INSW | 93I
LC | 128225562 | 021/493 | T2 DI DRUM-GRSS VLY-WMR 21/493 RMV VEG | SACTO | ETL.6760.POLE.WOOD | 2024-02-28 | 2024-02-27 | 2025-03-06 | Past Due |  | 2025-02-27 | 2025-02-27 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128225564 | 021/493 | T2 DI DRM-GRSS VLY-WMR 21/493 RPR ANCW | SACTO | ETL.6760.POLE.WOOD | 2024-02-28 | 2024-02-27 | 2024-06-28 | On-Time |  | 2024-08-27 | 2025-02-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46210364 | T2 DI DRM-GRSS VLY-WMR 21/493 RPR ANCW | ICW
LC | 128225606 | 17 | T2 DI CLAY-MARTEL 18/263 RPR JUMW | VICTOR | ETL.8250.SWIT | 2024-02-28 | 2024-02-27 | 2024-04-19 | On-Time |  | 2024-05-27 | 2025-02-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46219955 | T2 DI CLAY-MARTEL 18/263 RPR JUMW | ICW
LC | 128225607 | 018/263 | T2 DI CLAY-MARTEL 18/263 RPR SWITCH | VICTOR | ETL.8250.POLE.WOOD | 2024-02-28 | 2024-02-27 | 2025-04-12 | Past Due |  | 2025-02-27 | 2025-02-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Switch-Wood | Repair | 46289524 | +T2 DI CLAY-MARTEL 18/263 RPR SWITCH | ICW
LC | 128225634 | 020/278 | T2 DI SISQC-SNTA YNEZ SS 20/278 RPL STRW | PISMOBCH | ETL.3700.POLE.WOOD | 2024-02-28 | 2024-02-27 | 2025-02-18 | On-Time |  | 2025-02-27 | 2025-02-27 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573827 | T2 DI SISQC-SNTA YNEZ SS 20/278 RPL STRW | 70Y
LC | 128225637 | 025/117 | T2 DI TESLA-LOS BANOS #1 25/117 RPR SHLS | VICTOR | ETL.6100.TOWR | 2024-02-28 | 2024-02-27 | 2025-04-25 | Past Due |  | 2025-02-27 | 2025-02-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46289526 | T2 DI TESLA-LOS BANOS #1 25/117 RPR SHLS | ICS
LC | 128225820 | 008/002 | T2 DI SLNS-FRT ORD #1 8/002 RPL INSS | MOSSLNDG | ETL.7890.INSL.CERA | 2024-02-28 | 2024-02-27 | 2025-02-18 | On-Time |  | 2025-02-27 | 2025-02-27 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35597473 | T2 DI SALINAS-FORT ORD#1 RPL INSS 3 LSTS | 93K
LC | 128225825 | 008/002 | T2 DI SLNS-FRT ORD #2 8/002 RPL INSS | MOSSLNDG | ETL.8423.INSL.CERA | 2024-02-28 | 2024-02-27 | 2025-02-18 | On-Time |  | 2025-02-27 | 2025-02-27 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35597474 | T2 DI SALINAS-FORT ORD #2 RPL INSS 2 LST | 93K
LC | 128229359 | 007/012 | T2 DI SALINAS-FORT ORD #2 7/12 RPR FOND | MOSSLNDG | ETL.8423.POLE.NWOD | 2024-02-29 | 2024-02-27 | 2025-04-21 | Past Due |  | 2025-02-27 | 2025-02-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46493245 | T2 DI SALINAS-FORT ORD #2 7/12 RPR FOND | ICQ
LC | 128229589 | 020/477 | T2 DI DRUM-GRSS VLY-WMR 20/477 RPR CRSW | SACTO | ETL.6760.POLE.WOOD | 2024-02-29 | 2024-02-27 | 2025-02-14 | On-Time |  | 2025-02-27 | 2025-02-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46323907 | T2 DI DRUM-GRSS VLY-WMR 20/477 RPR CRSW | ICW
LC | 128229614 | 000/005 | T2 DI MRGA-CASTRO VLLY 0/005 RPR OPGW | CONCORD | ETL.5250.TOWR | 2024-02-29 | 2024-02-27 | 2025-03-14 | Past Due |  | 2025-02-27 | 2025-02-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46286505 | T2 DI MRGA-CASTRO VLLY 0/005 RPR OPGW | ICS
LC | 128229637 | 020/475 | T2 DI DRUM-GRS VLY-WEMR-20/475 RPL STRW | SACTO | ETL.6760.POLE.WOOD | 2024-02-29 | 2024-02-27 | 2025-02-14 | On-Time |  | 2025-02-27 | 2025-02-27 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35554351 | T2 DI DRUM-GRS VLY-WEMR-20/475 RPL STRW | 70Y
LC | 128229831 | 002/027 | T2 DI JOLON TAP 2/27 RPL POLE | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-02-29 | 2024-02-27 | 2025-01-28 | On-Time |  | 2025-02-27 | 2025-02-27 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35558556 | T2 DI JOLON TAP 2/27 RPL POLE | 70Y
LC | 128229862 | 020/476 | T2 DI DRM GRS VLY WMRR 20/476 RPR INSW | SACTO | ETL.6760.INSL.NCER | 2024-02-29 | 2024-02-27 | 2025-02-14 | On-Time |  | 2025-02-27 | 2025-02-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46323909 | T2 DI DRM GRS VLY WMRR 20/476 RPR INSW | ICW
LC | 128229866 | 019/265 | T2 DI SQC SNT YN SW STA 19/265 RPR INSW | PISMOBCH | ETL.3700.INSL.CERA | 2024-02-29 | 2024-02-27 | 2025-02-20 | On-Time |  | 2025-02-27 | 2025-02-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46390356 | T2 DI SQC SNT YN SW STA 19/265 RPR INSW | ICW
LC | 128229890 | 001/019 | T2 DI JOLON TAP 1/19 RPL INSW | MOSSLNDG | ETL.7321.INSL.CERA | 2024-02-29 | 2024-02-27 | 2025-01-28 | On-Time |  | 2025-02-27 | 2025-02-27 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35558554 | T2 DI JOLON TAP 1/19 RPL INSW | 93I
LC | 128229936 | 006/010 | T2 SALINAS-FORT ORD #2 6/10 RPR STRT | MOSSLNDG | ETL.8423.POLE.NWOD | 2024-02-29 | 2024-02-27 | 2024-02-27 | Past Due |  | 2025-02-27 | 2025-02-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46540960 | T2 SALINAS-FORT ORD #2 6/10 RPR STRT | ICQ
LC | 128229946 | 025/115 | T2 DI TESLA LS BNOS#1 25/115 RPR SHLD | VICTOR | ETL.6100.TOWR | 2024-02-29 | 2024-02-27 | 2025-04-25 | Past Due |  | 2025-02-27 | 2025-02-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46289525 | T2 DI TESLA LS BNOS#1 25/115 RPR SHLD | ICS
LC | 128229951 | 019/268 | T2 DI SISQUC-SNTA YNZ SS 19/268 COTR KEY | PISMOBCH | ETL.3700.INSL.CERA | 2024-02-29 | 2024-02-27 | 2025-02-20 | On-Time |  | 2025-02-27 | 2025-02-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46390357 | T2 DI SISQUC-SNTA YNZ SS 19/268 COTR KEY | ICW
LC | 128229953 | 020/275 | T2 DI SISQUC-SNTA YNEZ SS 20/275 RPL STR | PISMOBCH | ETL.3700.POLE.WOOD | 2024-02-29 | 2024-02-27 | 2025-02-18 | On-Time |  | 2025-02-27 | 2025-02-27 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573825 | T2 DI SISQUC-SNTA YNEZ SS 20/275 RPL STR | 70Y
LC | 128229955 | 014/326 | T2 DI DRM-GRS VLY-WEIMR 14/326 RPR INSW | SACTO | ETL.6760.INSL.CERA | 2024-02-29 | 2024-02-27 | 2025-01-09 | On-Time |  | 2025-02-27 | 2025-02-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46323910 | T2 DI DRM-GRS VLY-WEIMR 14/326 RPR INSW | ICW
LC | 128229970 | 014/323 | T2 DI DRM GRS VLY WMR 14/323 RPR INSW | SACTO | ETL.6760.INSL.CERA | 2024-02-29 | 2024-02-27 | 2025-01-08 | On-Time |  | 2025-02-27 | 2025-02-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46323911 | T2 DI DRM GRS VLY WMR 14/323 RPR INSW | ICW
LC | 128230005 | 006/008 | T2 DI SALINAS-FORT ORD #1 6/8 COMPLETE | MOSSLNDG | ETL.7890.INSL.NCER | 2024-02-29 | 2024-02-27 | 2025-02-21 | On-Time |  | 2025-02-27 | 2025-02-27 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35597473 | T2 DI SALINAS-FORT ORD#1 RPL INSS 3 LSTS | 93K
LC | 128247187 | 007/010 | T2 DI SALINAS-FORT ORD #2 7/10 INS HRDT | MOSSLNDG | ETL.8423.POLE.NWOD | 2024-03-06 | 2024-02-27 | 2025-01-27 | On-Time |  | 2025-02-27 | 2025-02-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46404407 | T2 DI SALINAS-FORT ORD #2 7/10 INS HRDT | ICQ
LC | 128254277 | 019/152C | T2 DI MDL FORK GLD HL 19/152C RPR ANCW | SACTO | ETL.5140.POLE.NWOD | 2024-03-08 | 2024-02-27 | 2024-07-29 | On-Time |  | 2025-02-27 | 2025-02-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46305360 | T2 DI MDL FORK GLD HL 19/152C RPR ANCW | ICW
LC | 128254610 | 024/189 | T2 DI MDL FORK-GLD HL 24/189 RPR GYWW | SACTO | ETL.5140.POLE.STPS | 2024-03-08 | 2024-02-27 | 2025-01-30 | On-Time |  | 2025-02-27 | 2025-02-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46389172 | T2 DI MDL FORK-GLD HL 24/189 RPR GYWW | ICW
LC | 128254680 | 004/051 | T2 DI JOLON TAP 4/51 RPL ANCW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-03-08 | 2024-02-27 | 2025-01-30 | On-Time |  | 2025-02-27 | 2025-02-27 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573659 | T2 DI JOLON TAP 4/51 RPL ANCW | 93E
LC | 128256223 | 052/214 | T2 MDWY-WHRLWND 052/214 RPR SHLS | MIDWAY | ETL.6030.TOWR | 2024-03-08 | 2024-02-27 | 2024-02-27 | Past Due |  | 2024-08-27 | 2025-02-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46302342 | T2 DI MDWY-WHRLWND 052/214 RPR SHLS | ICS
LC | 128258226 | 051/210 | T2 DI MIDWAY-WHIRLWIND 51/210 RPR SHLS | MIDWAY | ETL.6030.TOWR | 2024-03-08 | 2024-02-27 | 2025-03-09 | Past Due |  | 2025-02-27 | 2025-02-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46302341 | T2 DI MIDWAY-WHIRLWIND 51/210 RPR SHLS | ICS
LC | 128259052 | 021/172 | T2 DI MIDDLE FRK-GD HL 21/172 RPL HRDW | SACTO | ETL.5140.POLE.STPS | 2024-03-09 | 2024-02-27 | 2025-01-30 | On-Time |  | 2025-02-27 | 2025-02-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46397980 | T2 DI MIDDLE FRK-GD HL 21/172 RPL HRDW | ICW
LC | 129444517 | 002/015 | T3 SOBRANTE-""R"" #1 002/015 INS RPTS | CONCORD | ETL.3770.TOWR | 2024-08-27 | 2024-08-27 | 2024-10-02 | On-Time |  | 2025-02-27 | 2025-02-27 | 530 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMC REMT SWRK SPCR CLR ACCL ACCM ACCH COMP OH FMOB TR3 PRTO FRAB NTDE | Missing | Raptor Guard-Steel | Install | 31709919 | T3 SOBRANTE-""R"" #1 002/015 INS RPTS | 93R
LC | 128223436 | 003/019 | T2 PTSBRG-KRKR-CLMB STL 3/19 RPL HRDT | CONCORD | ETL.3310.INSL | 2024-02-28 | 2024-02-28 | 2025-06-22 | Past Due |  | 2024-08-28 | 2025-02-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB DURA BRIN | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46286465 | T2 EI PTSBRG-KRKR-CLMB STL 3/19 RPL HRDT | ICQ
LC | 128223625 | 014/053 | T2 EI DIABLO-MIDWAY #2 14/53 RPR GYWT | PISMOBCH | ETL.5970.TOWR | 2024-02-28 | 2024-02-28 | 2024-02-28 | Past Due |  | 2025-02-28 | 2025-02-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46391335 | T2 EI DIABLO-MIDWAY #2 14/053 RPR GYWT | ICQ
LC | 128223929 | 000/005 | T2 BUCKS CRK-ROCK CRK-CRESTA 0/5 RPL INS | TABLEMTN | ETL.4430.INSL.NCER | 2024-02-28 | 2024-02-28 | 2025-05-16 | Past Due |  | 2025-02-28 | 2025-02-28 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570410 | T2 BUCKS CRK-ROCK CRK-CRESTA 0/5 RPL INS | 93K
LC | 128224065 | 014/054 | T2 DIABLO-MIDWAY #2 14/54 RPR GYWT | PISMOBCH | ETL.5970.TOWR | 2024-02-28 | 2024-02-28 | 2024-02-28 | Past Due |  | 2025-02-28 | 2025-02-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW ACCM OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46391337 | T2 EI DIABLO-MIDWAY #2 14/54 RPR GYWT | ICQ
LC | 128224153 | 000/009A | T2 EI CRUSHER TAP 000/009A RMV VEG | MOSSLNDG | ETL.6241.POLE.WOOD | 2024-02-28 | 2024-02-28 | 2024-12-27 | On-Time |  | 2025-02-28 | 2025-02-28 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128224676 | 010/070 | T2 EI OLEUM-G #1 010/070 RPL HRDT | CONCORD | ETL.3150.TOWR | 2024-02-28 | 2024-02-28 | 2025-01-29 | On-Time |  | 2025-02-28 | 2025-02-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAR | No Good/Out of Stdrd | Hardware-Tower | Replace | 46286466 | T2 EI OLEUM-G #1 010/070 RPL HRDT | ICQ
LC | 128224754 | 003/095 | T2 EI VOLTA-SOUTH 03/95 RPR GYWW | TABLEMTN | ETL.8300.POLE.WOOD | 2024-02-28 | 2024-02-28 | 2025-01-14 | On-Time |  | 2025-02-28 | 2025-02-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311139 | T2 EI VOLTA-SOUTH 03/95 RPR GYWW | ICW
LC | 128228671 | 000/002 | T2 CHOWCHILLA-KERCKHOFF 000/002 GO95 | FRESNO | ETL.1250.INSL.NCER | 2024-02-29 | 2024-02-28 | 2024-02-28 | Past Due |  | 2029-02-28 | 2025-02-28 | 400 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Tower | To Be Corrected | 35490033 | T2 CHOWCHILLA-KERCKHOFF 000/004 GO95 | 93T
LC | 128229958 | 050/358 | T2 DI CARIBOU-TABLE MNTN 50/358 RPR INSS | TABLEMTN | ETL.4440.INSL.NCER | 2024-02-29 | 2024-02-28 | 2025-01-08 | On-Time |  | 2025-02-28 | 2025-02-28 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46332411 | T2 DI CARIBOU-TABLE MNTN 50/358 RPR INSS | ICS
LC | 128230006 | 011/077 | T2 DI IGNCIO-ALT-SASLT#1 11/77 COMPLETE | LAKEVLLE | ETL.7160.TOWR | 2024-02-29 | 2024-02-28 | 2025-03-26 | Past Due |  | 2025-02-28 | 2025-02-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46289541 | T2 DI IGNCIO-ALT-SASLT#1 11/77 RPR FOND | ICQ
LC | 128230007 | 011/077 | T2 DI IGNC-ALT-SASLIT #1 11/77 COMPLETE | LAKEVLLE | ETL.7160.TOWR | 2024-02-29 | 2024-02-28 | 2025-03-26 | Past Due |  | 2024-08-28 | 2025-02-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485382 | T2 DI IGNC-ALT-SASLIT #1 11/77 TOUCH | ICQ
LC | 128230009 | 011/077 | T2 DI IGNCI-ALTO-SASLT#1 11/77 RPL HRDT | LAKEVLLE | ETL.7160.TOWR | 2024-02-29 | 2024-02-28 | 2025-02-10 | On-Time |  | 2025-02-28 | 2025-02-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289503 | T2 DI IGNCI-ALTO-SASLT#1 11/77 RPL HRDT | ICQ
LC | 128240020 | 000/003A | T2 DI CRUSHER TP 0/3A RPR ANCW | MOSSLNDG | ETL.6241.POLE.WOOD | 2024-03-05 | 2024-02-28 | 2024-06-10 | On-Time |  | 2024-08-24 | 2025-02-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46211394 | T2 DI CRUSHER TP 0/3A RPR ANCW | ICW
LC | 128240022 | 000/010 | T2 CRUSHER TP 0/10 RPR ANCW | MOSSLNDG | ETL.6241.POLE.WDPS | 2024-03-05 | 2024-02-28 | 2024-04-01 | On-Time |  | 2024-08-28 | 2025-02-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE SPCR COMP OH TR2 PRTO FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46211395 | T2 DI CRUSHER TP 0/10 RPR ANCW | ICW
LC | 128240026 | 000/003B | T2 CRUSHER TP 0/3B RMV RPR ANCW | MOSSLNDG | ETL.6241.POLE.WOOD | 2024-03-05 | 2024-02-28 | 2024-06-10 | On-Time |  | 2024-08-28 | 2025-02-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE ACCM COMP OH TR2 PRTO FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46211396 | T2 DI CRUSHER TP 0/3B RMV RPR ANCW | ICW
LC | 128240230 | 000/003C | T2 CRUSHER TAP- 00/03C RPR ANCW | MOSSLNDG | ETL.6241.POLE.WOOD | 2024-03-05 | 2024-02-28 | 2024-06-10 | On-Time |  | 2024-08-28 | 2025-02-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE ACCM COMP OH TR2 PRTO FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46211397 | T2 DI CRUSHER TAP- 00/03C RPR ANCW | ICW
LC | 128254342 | 025/112 | T2 DI FINK SS-WESTLEY 25/112 RPR OPGW | VICTOR | ETL.1384.TOWR | 2024-03-08 | 2024-02-28 | 2025-01-27 | On-Time |  | 2025-02-28 | 2025-02-28 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46289529 | T2 DI FINK SS-WESTLEY 25/112 RPR OPGW | ICS
LC | 128254662 | 026/173 | T2 DI POE RIO OSO 26/173 TOUCH | TABLEMTN | ETL.5540.TOWR | 2024-03-08 | 2024-02-28 | 2025-05-02 | Past Due |  | 2024-08-28 | 2025-02-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491894 | T2 DI POE RIO OSO 26/173 TOUCH | ICQ
LC | 128254840 | 000/004 | T2 DI KANAKA TAP 00/004R RPR GYWW | TABLEMTN | ETL.4223.POLE.STPS | 2024-03-08 | 2024-02-28 | 2024-12-07 | On-Time |  | 2025-02-28 | 2025-02-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332417 | T2 DI KANAKA TAP 00/004R RPR GYWW | ICW
LC | 128256663 | 011/253 | T2 DI SANTA ROSA-CORONA 11/253 RPR GYWW | LAKEVLLE | ETL.4309.POLE.WOOD | 2024-03-08 | 2024-02-28 | 2024-03-25 | On-Time |  | 2025-02-28 | 2025-02-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46213538 | T2 DI SANTA ROSA-CORONA 11/253 RPR GYWW | ICW
LC | 128259087 | 010/245 | T2 DI SANTA ROSA-CORONA 10/245 RPR ANCW | LAKEVLLE | ETL.4309.POLE.WOOD | 2024-03-09 | 2024-02-28 | 2024-03-25 | On-Time |  | 2024-08-28 | 2025-02-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCH COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46213537 | T2 DI SANTA ROSA-CORONA 10/245 RPR ANCW | ICW
LC | 128269258 | 003/019 | T2 PTSBRG-KRKR-CLMB STL 3/19 RPL INSS | CONCORD | ETL.3310.INSL | 2024-03-11 | 2024-02-28 | 2025-06-22 | Past Due |  | 2024-08-28 | 2025-02-28 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575001 | T2 EI PTSBRG-KRKR-CLMB STL 3/19 RPL INSS | 93K
LC | 128293441 | 030/203 | T2 DI POE-RIO OSO 30/203 TOUCH | TABLEMTN | ETL.5540.TOWR | 2024-03-15 | 2024-02-28 | 2025-05-02 | Past Due |  | 2024-08-28 | 2025-02-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46477849 | T2 DI POE-RIO OSO 30/203 TOUCH | ICQ
LC | 128227230 | 004/037A | T2 EI DIVIDE-VNDNBRG #1 4/37A RPR GYWW | PISMOBCH | ETL.8620.POLE.WOOD | 2024-02-29 | 2024-02-29 | 2025-01-13 | On-Time |  | 2025-02-28 | 2025-03-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46329642 | T2 EI DIVIDE-VNDNBRG #1 4/37A RPR GYWW | ICW
LC | 128227280 | 004/037B | T2 EI DIVIDE-VNDNBRG #1 4/37B RPR GYWW | PISMOBCH | ETL.8620.POLE.WOOD | 2024-02-29 | 2024-02-29 | 2024-06-25 | On-Time |  | 2024-08-29 | 2025-03-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46266120 | T2 EI DIVIDE-VNDNBRG #1 4/37B RPR GYWW | ICW
LC | 128227859 | 003/024 | T2 EI DIVIDE-VANDENBERG #2 3/24 RPL INSW | PISMOBCH | ETL.8630.INSL.CERA | 2024-02-29 | 2024-02-29 | 2025-01-23 | On-Time |  | 2025-02-28 | 2025-03-01 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP CLR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573272 | T2 EI DIVIDE-VANDENBERG #2 3/24 RPL INSW | 93I
LC | 128227991 | 003/026 | T2 EI DIVIDE-VNDNBRG #1 3/26 INS DAMW | PISMOBCH | ETL.8620.INSL | 2024-02-29 | 2024-02-29 | 2025-01-13 | On-Time |  | 2025-02-28 | 2025-03-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46329639 | T2 EI DIVIDE-VNDNBRG #1 3/26 INS DAMW | ICW
LC | 128228137 | 003/025 | T2 EI DIVIDE-VNDNBRG #1 3/25 INS DAMW | PISMOBCH | ETL.8620.INSL | 2024-02-29 | 2024-02-29 | 2025-01-13 | On-Time |  | 2025-02-28 | 2025-03-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46329640 | T2 EI DIVIDE-VNDNBRG #1 3/25 INS DAMW | ICW
LC | 128228310 | 003/024 | T2 EI DIVIDE-VANDENBERG #1 3/24 RMV NEST | PISMOBCH | ETL.8620.POLE.WOOD | 2024-02-29 | 2024-02-29 | 2025-01-13 | On-Time |  | 2025-02-28 | 2025-03-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Wood | Remove | 46329643 | T2 EI DIVIDE-VANDENBERG #1 3/24 RMV NEST | ICW
LC | 128228427 | 017/325C | T2 EI SALINAS-LAURELES 17/325C RPL DMPW | MOSSLNDG | ETL.7930.INSL.CERA | 2024-02-29 | 2024-02-29 | 2025-04-09 | Past Due |  | 2025-02-28 | 2025-03-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46329985 | T2 EI SALINAS-LAURELES 17/325C RPL DMPW | ICW
LC | 128228441 | 016/120 | T2 WV CAYUCOS-CAMBRIA 16/120 INS ANCW | PISMOBCH | ETL.8560.POLE.NWOD | 2024-02-29 | 2024-02-29 | 2025-02-24 | On-Time |  | 2025-02-28 | 2025-03-01 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Anchor-Wood | Install | 35572859 | T2 WV CAYUCOS-CAMBRIA 16/120 INS ANCW | 93E
LC | 128228477 | 003/008 | T2 WV FORT BRAGG-ELK 003/008 RPL POLE | WILLITS | ETL.2060.POLE.WOOD | 2024-02-29 | 2024-02-29 | 2025-04-23 | Past Due |  | 2025-02-28 | 2025-03-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573913 | T2 WV FORT BRAGG-ELK 003/008 RPL POLE | 70Y
LC | 128229041 | 007/133 | T2 EI TEJON-LEBEC 007/133 RPR GYWW | MIDWAY | ETL.9250.POLE.NWOD | 2024-02-29 | 2024-02-29 | 2024-09-20 | On-Time |  | 2024-08-29 | 2025-03-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46203077 | T2 EI TEJON-LEBEC 007/133 RPR GYWW | ICW
LC | 128229045 | 005/046 | T2 EI DIVIDE-VANDENBERG #2 5/46 RPL INSW | PISMOBCH | ETL.8630.INSL | 2024-02-29 | 2024-02-29 | 2025-01-22 | On-Time |  | 2025-02-28 | 2025-03-01 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573273 | T2 EI DIVIDE-VANDENBERG #2 5/46 RPL INSW | 93I
LC | 128229136 | 013/288 | T2 WV SALINAS-LAURELES 13/288 INS RPTR | MOSSLNDG | ETL.7930.POLE.NWOD | 2024-02-29 | 2024-02-29 | 2025-04-07 | Past Due |  | 2025-02-28 | 2025-03-01 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Raptor Guard-Wood | Replace | 46329986 | T2 WV SALINAS-LAURELES 13/288 INS RPTR | ICB
LC | 128229328 | 016/328 | T2 CARIBOU-WESTWOOD 16/328 GO95 RPL | TABLEMTN | ETL.6300.POLE.WOOD | 2024-02-29 | 2024-02-29 | 2025-02-15 | On-Time |  | 2025-02-28 | 2025-03-01 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35535827 | T2 CARIBOU-WESTWOOD 16/328 GO95 RPL | 93G
LC | 128233836 | 047/411 | T2 ROUND MTN-COTNWD #3 47/411 RPL INSS | TABLEMTN | ETL.5650.INSL | 2024-03-01 | 2024-03-01 | 2025-03-03 | Past Due |  | 2025-03-01 | 2025-03-01 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW NONR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574240 | T2 ROUND MTN-COTNWD #3 47/411 RPL INSS | 93K
LC | 128233837 | 013/292 | T2 WV SALINAS-LAURELES 13/292 TOUCH | MOSSLNDG | ETL.7930.POLE.NWOD | 2024-03-01 | 2024-03-01 | 2025-06-02 | Past Due |  | 2024-09-01 | 2025-03-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46493109 | T2 WV SALINAS-LAURELES 13/292 TOUCH | ICW
LC | 128233839 | 009/070 | T2 WV ROCK CREEK-POE 9/070 RPL INSS | TABLEMTN | ETL.5630.INSL | 2024-03-01 | 2024-03-01 | 2025-04-27 | Past Due |  | 2025-03-01 | 2025-03-01 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW CREW COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35572041 | T2 ROCK CREEK-POE RPL INSS 5 TWRS | 93K
LC | 128236792 | 001/027 | T2 EI FLINT TAP 001/27 RPL INSW | SACTO | ETL.3341.INSL.NCER | 2024-03-04 | 2024-02-29 | 2025-01-17 | On-Time |  | 2025-02-28 | 2025-03-01 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35558172 | T2 EI FLINT TAP 001/27 RPL INSW | 93I
LC | 128247527 | 009/068 | T2 SLO-CAYUCOS 9/68 RPL INSW | PISMOBCH | ETL.9090.INSL.CERA | 2024-03-06 | 2024-03-01 | 2025-05-06 | Past Due |  | 2025-03-01 | 2025-03-01 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE ACCM COMP OH TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Insulator-Wood | Replace | 35535928 | T2 SLO-CAYUCOS 009/68 INSW | 93I
LC | 123054662 | 027/108 | T3NT DI PTTSBRG-SN MATEO 27/108 RPR INSS | CONCORD | ETL.5463.INSL | 2022-03-04 | 2022-03-02 | 2023-06-20 | On-Time |  | 2025-03-02 | 2025-03-02 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3N PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 45514934 | T3 DI PTTSBRG-SAN MATEO 27/108 RPR INSS | ICS
LC | 123047543 | 001/005 | T2NT EI LAYTONVILLE-CVL 1/5 RPR GYWW | WILLITS | ETL.7390.POLE.NWOD | 2022-03-03 | 2022-03-03 | 2023-05-18 | On-Time |  | 2025-03-03 | 2025-03-03 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45640059 | T2 EI LAYTONVILLE-COVELO 1/5 RPR GYWW | ICW
LC | 123050081 | 052/212 | T2NT EI MIDWAY-WHIRLWD 052/212 RPR STRT | MIDWAY | ETL.6030.TOWR | 2022-03-03 | 2022-03-03 | 2023-06-13 | On-Time |  | 2025-03-03 | 2025-03-03 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 45619010 | T2 EI MIDWAY-WHIRLWIND 052/212 BNT STEEL | ICQ
LC | 123055575 | 039/235 | T2NT DI INDIAN FLAT-YOSEMT 39/235 UNBURY | FRESNO | ETL.1112.POLE.NWOD | 2022-03-05 | 2022-03-03 | 2023-02-15 | On-Time |  | 2025-03-03 | 2025-03-03 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45639847 | T2 DI INDIAN FLAT-YOSEMITE 39/235 UNBURY | ICQ
LC | 126960964 | 013/253 | T2 WV VALLEY SPRINGS #2 013/253 INS DMPW | VICTOR | ETL.9460.INSL.NCER | 2023-08-31 | 2023-08-31 | 2025-03-27 | Past Due |  | 2025-03-03 | 2025-03-03 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB XMPT TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46175763 | T2 WV VALLEY SPRINGS #2 013/253 INS DMPW | ICW
LC | 129141429 | 029/243 | T3 DI PIT #1 COTONWD 29/243 RPR JUMS | TABLEMTN | ETL.5390.INSL.NCER | 2024-06-28 | 2024-05-31 | 2024-11-08 | On-Time |  | 2025-03-03 | 2025-03-03 | 628 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR3 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46273972 | T3 DI PIT #1 COTONWD 29/243 RPR JUMS | ICS
LC | 128236876 | 009/010 | T2 WV FORT BRAGG-ELK 9/010 RPL DMPW | WILLITS | ETL.2060.INSL.CERA | 2024-03-04 | 2024-03-04 | 2025-01-23 | On-Time |  | 2025-03-04 | 2025-03-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46305764 | T2 WV FORT BRAGG-ELK 9/010 RPL DMPW | ICW
LC | 128237848 | 004/047 | T2 EI SNEATH LNE-PACIFICA 04/47 RPL POLE | METCALF | ETL.7575.POLE.WOOD | 2024-03-04 | 2024-03-04 | 2024-03-04 | Past Due |  | 2025-03-04 | 2025-03-04 | 372 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573713 | T2 EI SNEATH LNE-PACIFICA 04/47 RPL POLE | 70Y
LC | 128237858 | 017/327 | T2 EI SALINAS-LAURELES 17/327 RPR DMPW | MOSSLNDG | ETL.7930.INSL | 2024-03-04 | 2024-03-04 | 2025-04-09 | Past Due |  | 2025-03-04 | 2025-03-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Damper-Wood | Replace | 46329987 | T2 EI SALINAS-LAURELES 17/327 RPR DMPW | ICW
LC | 128238024 | 031/595 | T2 HAT CREEK #1-WESTWOOD 031/595 GO95 | TABLEMTN | ETL.7030.POLE.WOOD | 2024-03-04 | 2024-03-04 | 2025-06-16 | Past Due |  | 2025-03-04 | 2025-03-04 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35535440 | T2 HAT CREEK #1-WESTWOOD 031/595 GO95 | 93G
LC | 128238193 | 044/857 | T2 HAT CRK #1-WESTWOOD 44/857 GO95 RPL | TABLEMTN | ETL.7030.POLE.WOOD | 2024-03-04 | 2024-03-04 | 2025-05-28 | Past Due |  | 2025-03-04 | 2025-03-04 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35535362 | T2 HAT CRK #1-WESTWOOD 44/857 GO95 RPL | 93G
LC | 128238254 | 006/010 | T2 SALINAS-FORT ORD #2 6/10 TOUCH | MOSSLNDG | ETL.8423.POLE.NWOD | 2024-03-04 | 2024-03-04 | 2024-03-04 | Past Due |  | 2024-09-04 | 2025-03-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491495 | T2 SALINAS-FORT ORD #2 6/10 TOUCH | ICQ
LC | 128238353 | 004/049 | T2 EI SNEATH LANE-PACFC 4/49 RPL ANCW | METCALF | ETL.7575.POLE.WDPS | 2024-03-04 | 2024-03-04 | 2025-02-10 | On-Time |  | 2025-03-04 | 2025-03-04 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573714 | T2 EI SNEATH LANE-PACFC 4/49 RPL ANCW | 93E
LC | 128238418 | 009/186 | T2 CARIBOU-WESTWOOD 9/186 GO95 RPL | TABLEMTN | ETL.6300.POLE.WOOD | 2024-03-04 | 2024-03-04 | 2025-03-11 | Past Due |  | 2025-03-04 | 2025-03-04 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35535444 | T2 CARIBOU-WESTWOOD 9/186 GO95 RPL | 93G
LC | 128238420 | 004/049 | T2 EI SNEATH LANE-PACFC 4/49 RPL ANCW | METCALF | ETL.7575.POLE.WDPS | 2024-03-04 | 2024-03-04 | 2025-02-10 | On-Time |  | 2025-03-04 | 2025-03-04 | 637 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573714 | T2 EI SNEATH LANE-PACFC 4/49 RPL ANCW | 93E
LC | 128238434 | 004/049 | T2 EI SNEATH LANE-PACFC 4/49 RPL ANCW | METCALF | ETL.7575.POLE.WDPS | 2024-03-04 | 2024-03-04 | 2025-02-10 | On-Time |  | 2025-03-04 | 2025-03-04 | 637 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573714 | T2 EI SNEATH LANE-PACFC 4/49 RPL ANCW | 93E
LC | 128238439 | 049/002 | T2 ELK-GUALALA 49/2 GO95 CLEAR | WILLITS | ETL.8410.POLE.WOOD | 2024-03-04 | 2024-03-04 | 2025-02-06 | On-Time |  | 2025-03-04 | 2025-03-04 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35535930 | T2 ELK-GUALALA 49/2 GO95 CLEAR | 93G
LC | 128238598 | 017/326A | T2 EI SALINAS-LAURELES 17/326A RPL STRW | MOSSLNDG | ETL.7930.POLE.WOOD | 2024-03-04 | 2024-03-04 | 2025-04-09 | Past Due |  | 2025-03-04 | 2025-03-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35576935 | T2 EI SALINAS-LAURELES 17/326A RPL STRW | 70Y
LC | 128238599 | 017/326A | T2 EI SALINAS-LAURELES 17/326A RPR DMPW | MOSSLNDG | ETL.7930.INSL | 2024-03-04 | 2024-03-04 | 2025-04-09 | Past Due |  | 2025-03-04 | 2025-03-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Damper-Wood | Replace | 46329988 | T2 EI SALINAS-LAURELES 17/326A RPR DMPW | ICW
LC | 128238681 | 017/326B | T2 EI SALINAS-LAURELES 17/326B RPL STRW | MOSSLNDG | ETL.7930.POLE.WOOD | 2024-03-04 | 2024-03-04 | 2025-04-09 | Past Due |  | 2025-03-04 | 2025-03-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35576935 | T2 EI SALINAS-LAURELES 17/326A RPL STRW | 70Y
LC | 128244376 | 034/004A | T2 TRINITY-MAPLE CREEK 34/4A RPR JUMP | EUREKA | ETL.8170.INSL.NCER | 2024-03-06 | 2024-03-04 | 2024-09-10 | On-Time |  | 2025-03-04 | 2025-03-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Jumper-Steel | Repair | 46320993 | T2 TRINITY-MAPLE CREEK 34/4A RPR JUMP | ICS
LC | 129470863 | 011/266 | T3 DRUM-GRASS VALLEY-WEIMAR 11/266 GO95 | SACTO | ETL.6760.POLE.NWOD | 2024-09-04 | 2024-09-04 | 2024-09-26 | On-Time |  | 2025-03-04 | 2025-03-04 | 401T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCM COMP OH TR3 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35579182 | T3 DRUM-GRASS VALLEY-WEIMAR 11/266 GO95 | 93G
LC | 128240951 | 027/003 | T2 MAPLE CRK-HPA 27/003 GO95 USAGE | EUREKA | ETL.7490.POLE.WOOD | 2024-03-05 | 2024-03-05 | 2024-03-05 | Past Due |  | 2025-03-05 | 2025-03-05 | 401T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35537945 | T2 MAPLE CREEK-HOOPA 27/003 GO95 | 93G
LC | 128241551 | 000/007 | T2 EI PALERMO-OROVILLE #1 00/07 RPR INSW | TABLEMTN | ETL.7730.INSL.CERA | 2024-03-05 | 2024-03-05 | 2025-01-11 | On-Time |  | 2025-03-05 | 2025-03-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP CLR ACCH COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46332412 | T2 EI PALERMO-OROVILLE #1 00/07 RPR INSW | ICW
LC | 128241688 | 004/103 | T2 EI VOLTA-SOUTH 004/103 RPL POLE | TABLEMTN | ETL.8300.POLE.WOOD | 2024-03-05 | 2024-03-05 | 2025-01-15 | On-Time |  | 2025-03-05 | 2025-03-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35571836 | T2 EI VOLTA-SOUTH 004/103 RPL POLE | 70Y
LC | 128241803 | 004/106 | T2 EI VOLTA-SOUTH 004/106 RPR GYWW | TABLEMTN | ETL.8300.POLE.WOOD | 2024-03-05 | 2024-03-05 | 2025-01-13 | On-Time |  | 2025-03-05 | 2025-03-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311137 | T2 EI VOLTA-SOUTH 004/106 RPR GYWW | ICW
LC | 128242403 | 000/011 | T2 EI PALERMO-OROVILLE #1 00/11 RPL POLE | TABLEMTN | ETL.7730.POLE.WOOD | 2024-03-05 | 2024-03-05 | 2025-02-18 | On-Time |  | 2025-03-05 | 2025-03-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574182 | T2 EI PALERMO-OROVILLE #1 00/11 RPL POLE | 70Y
LC | 128243178 | 014/007 | T2 WV FORT BRAGG-ELK 014/007 RPL POLE | WILLITS | ETL.2060.POLE.WOOD | 2024-03-05 | 2024-03-05 | 2025-01-24 | On-Time |  | 2025-03-05 | 2025-03-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAR | No Good/Out of Stdrd | Structure-Wood | Replace | 35573915 | T2 WV FORT BRAGG-ELK 014/007 RPL POLE | 70Y
LC | 128244329 | 005/086 | T2 EI SISQC-SNTA YNZ S S 5/86 INS DMPW | PISMOBCH | ETL.3700.INSL.CERA | 2024-03-06 | 2024-03-05 | 2025-04-02 | Past Due |  | 2025-03-05 | 2025-03-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK ACCL ACCM ACCH COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46390358 | T2 EI SISQC-SNTA YNZ S S 5/86 INS DMPW | ICW
LC | 128254266 | 014/333 | T2 DI DRUM-GRASS VALLEY 14/33 RPR GYWW | SACTO | ETL.6760.POLE.NWOD | 2024-03-08 | 2024-03-05 | 2024-06-28 | On-Time |  | 2025-03-05 | 2025-03-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46271669 | T2 DI DRUM-GRASS VALLEY 14/33 RPR GYWW | ICW
LC | 128254298 | 080/407 | T2 DI MLN RND MTN#2 8/407 RMV VEG | TABLEMTN | ETL.6020.TOWR | 2024-03-08 | 2024-03-05 | 2024-10-16 | On-Time |  | 2025-03-05 | 2025-03-05 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128254350 | 080/407 | T2 DI MLN RND MTN#2 80/407 UNBURY | TABLEMTN | ETL.6020.TOWR | 2024-03-08 | 2024-03-05 | 2025-02-10 | On-Time |  | 2025-03-05 | 2025-03-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381354 | T2 DI MLN RND MTN#2 80/407 UNBURY | ICQ
LC | 128254377 | 000/010A | T2 DI PEORIA TAP 000/010A RPL HRDW | VICTOR | ETL.2391.POLE.WOOD | 2024-03-08 | 2024-03-05 | 2025-01-15 | On-Time |  | 2025-03-05 | 2025-03-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46289530 | T2 DI PEORIA TAP 000/010A RPL HRDW | ICW
LC | 128254478 | 024/137 | T2 DI TSL SLD MNTC 24/137 RPR GYWW | VICTOR | ETL.4000.POLE.WOOD | 2024-03-08 | 2024-03-05 | 2024-05-05 | On-Time |  | 2024-06-05 | 2025-03-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46219957 | T2 DI TSL SLD MNTC 24/137 RPR GYWW | ICW
LC | 128293411 | 030/143 | T2 DI TRACY-LOS BANOS 30/143 RPR GYWT | VICTOR | ETL.6130.TOWR | 2024-03-15 | 2024-03-05 | 2024-06-17 | On-Time |  | 2024-09-05 | 2025-03-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46236712 | T2 DI TRACY-LOS BANOS 30/143 RPR GYWT | ICQ
LC | 128293621 | 024/111 | T2 DI FINK SS-WESTLEY 24/111 RPL HRDT | VICTOR | ETL.1384.TOWR | 2024-03-15 | 2024-03-05 | 2025-02-27 | On-Time |  | 2025-03-05 | 2025-03-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46401412 | T2 DI FINK SS-WESTLEY 24/111 RPL HRDT | ICQ
LC | 128293711 | 024/111 | T2 DI FINK SS-WESTLEY 24/111 RPR SHLD | VICTOR | ETL.1384.TOWR | 2024-03-15 | 2024-03-05 | 2024-03-05 | Past Due |  | 2025-03-05 | 2025-03-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46299692 | T2 DI FINK SS-WESTLEY 24/111 RPR SHIELD | ICS
LC | 128294205 | 047/193 | T2 DI MIDWAY WHIRLWIND 47/193 RPR GYWT | MIDWAY | ETL.6030.TOWR | 2024-03-15 | 2024-03-05 | 2025-03-05 | On-Time |  | 2025-03-05 | 2025-03-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46292627 | T2 DI MIDWAY WHIRLWIND 47/193 RPR GYWT | ICQ
LC | 128296124 | 047/191 | T2 DI MIDWAY-WHIRLWIND 47/191 RPR FOND | MIDWAY | ETL.6030.TOWR | 2024-03-15 | 2024-03-05 | 2024-05-20 | On-Time |  | 2025-03-05 | 2025-03-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46249890 | T2 DI MIDWAY-WHIRLWIND 47/191 RPR FOND | ICQ
LC | 128303182 | 008/069C | T2 DI TRINITY-COTTONWOOD-08/69C RPR ANCW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-03-18 | 2024-03-05 | 2024-06-23 | On-Time |  | 2024-09-05 | 2025-03-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46217442 | T2 DI TRINITY-COTTONWOOD-08/69C RPR ANCW | ICW
LC | 128303260 | 009/003 | T2 DI MELONES-RACETRACK 09/03 RPR GYWW | VICTOR | ETL.2400.POLE.NWOD | 2024-03-18 | 2024-03-05 | 2025-01-22 | On-Time |  | 2025-03-05 | 2025-03-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46326977 | T2 DI MELONES-RACETRACK 09/03 RPR GYWW | ICW
LC | 128303435 | 000/001 | T2 DI PEORIA TAP 00/01 RPR STRW | VICTOR | ETL.2391.POLE.WOOD | 2024-03-18 | 2024-03-05 | 2025-01-15 | On-Time |  | 2025-03-05 | 2025-03-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46289528 | T2 DI PEORIA TAP 00/01 RPR STRW | ICW
LC | 128303439 | 079/403 | T2 DI MLN RND MTN#2 79/403 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-03-18 | 2024-03-05 | 2025-02-08 | On-Time |  | 2025-03-05 | 2025-03-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332440 | T2 DI MLN RND MTN#2 79/403 RPR OPGW | ICS
LC | 128303475 | 012/277 | T2 DI DRM GRAS VALY WMR 12/277 RPL STRW | SACTO | ETL.6760.POLE.WOOD | 2024-03-18 | 2024-03-05 | 2025-01-31 | On-Time |  | 2025-03-05 | 2025-03-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35554159 | T2 DI DRM GRAS VALY WMR 12/277 RPL STRW | 70Y
LC | 128303548 | 024/138 | T2 DI TSLA SLDO MNTCA 24/138 RPL STRW | VICTOR | ETL.4000.POLE.WOOD | 2024-03-18 | 2024-03-05 | 2025-02-24 | On-Time |  | 2025-03-05 | 2025-03-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573516 | T2 DI TSLA SLDO MNTCA 24/138 RPL STRW | 70Y
LC | 128303559 | B016/380 | T2 DI DRUM-GRS VLY-WMR B16/380 COTTER | SACTO | ETL.6760.POLE.NWOD | 2024-03-18 | 2024-03-05 | 2024-06-28 | On-Time |  | 2024-06-05 | 2025-03-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46216021 | T2 DI DRUM-GRS VLY-WMR B16/380 COTTER | ICW
LC | 128303651 | B016/380 | T2 DI DRUM-GRS VLY-WMR B16/380 RMV VEG | SACTO | ETL.6760.POLE.NWOD | 2024-03-18 | 2024-03-05 | 2025-04-28 | Past Due |  | 2025-03-05 | 2025-03-05 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128303766 | B025/571 | T2 DI DRM GRS VLY WEMR B25/571 RPR ADSS | SACTO | ETL.6760.POLE.WOOD | 2024-03-18 | 2024-03-05 | 2025-01-15 | On-Time |  | 2025-03-05 | 2025-03-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | ADSS - Wood | Repair | 46323919 | T2 DI DRM GRS VLY WEMR B25/571 RPR ADSS | ICW
LC | 128303767 | B025/571 | T2 DI DRM GRS VLY WEMR B25/571 RPR POLE | SACTO | ETL.6760.POLE.WOOD | 2024-03-18 | 2024-03-05 | 2024-06-23 | On-Time |  | 2025-03-05 | 2025-03-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46271177 | T2 DI DRM GRS VLY WEMR B25/571 RPR POLE | ICW
LC | 128304802 | 044/180 | T2 DI MIDWAY WHRLWND 44/180 RPR SHLD | MIDWAY | ETL.6030.TOWR | 2024-03-19 | 2024-03-05 | 2025-03-10 | Past Due |  | 2025-03-05 | 2025-03-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46272330 | T2 DI MIDWAY WHRLWND 44/180 RPR SHLD | ICS
LC | 128307519 | 024/111 | T2 DI TESLA-LS BANOS #1 24/111 RPL HRDT | VICTOR | ETL.6100.TOWR | 2024-03-19 | 2024-03-05 | 2024-06-17 | On-Time |  | 2024-09-05 | 2025-03-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Hardware-Tower | Replace | 46248596 | T2 DI TESLA-LS BANOS #1 24/111 RPL HRDT | ICQ
LC | 128321790 | 080/409 | T2 MALIN RD MTN#2 80/409 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-03-19 | 2024-03-05 | 2025-06-17 | Past Due |  | 2025-03-05 | 2025-03-05 | 93Z | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716778 | T2 DI MLN RD MTN#2 RPL ANCT 10 TWRS | 93Z
LC | 128322117 | 031/145 | T2 DI TRACY-LOS BANS 31/145 RPR FOND | VICTOR | ETL.6130.TOWR | 2024-03-19 | 2024-03-05 | 2025-01-17 | On-Time |  | 2025-03-05 | 2025-03-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46325952 | T2 DI TRACY-LOS BANS 31/145 RPR FOND | ICQ
LC | 128322119 | 031/145 | T2 DI TRACY-LOS BANS 31/145 RPL INSS | VICTOR | ETL.6130.INSL | 2024-03-19 | 2024-03-05 | 2025-02-21 | On-Time |  | 2025-03-05 | 2025-03-05 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35599397 | T0 DI TRACY-LOS BANOS 060/270 RPL INSS | 93K
LC | 128336323 | 049/201 | T2 DI MIDWAY-WHIRLW 49/201 RPR SHLD | MIDWAY | ETL.6030.TOWR | 2024-03-20 | 2024-03-05 | 2025-03-10 | Past Due |  | 2025-03-05 | 2025-03-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46302343 | T2 DI MIDWAY-WHIRLW 49/201 RPR SHLD | ICS
LC | 129479018 | 022/114 | T3 ROUND MTN-TBLE MTN #1 22/114 RPR INSS | TABLEMTN | ETL.6060.INSL | 2024-09-05 | 2024-09-05 | 2024-10-30 | On-Time |  | 2025-03-05 | 2025-03-05 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46332446 | T3 ROUND MTN-TBLE MTN #1 22/114 RPR INSS | ICS
LC | 128244389 | 010/134 | T2 WTSNVLLE-SALINAS 10/134 RPR INSW | MOSSLNDG | ETL.8310.INSL.NCER | 2024-03-06 | 2024-03-06 | 2025-02-12 | On-Time |  | 2025-03-06 | 2025-03-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46391203 | T2 WTSNVLLE-SALINAS 10/134 RPR INSW | ICW
LC | 128245141 | 016/332 | T2 CARIBOU-WESTWOOD 016/332 GO95 RPL | TABLEMTN | ETL.6300.POLE.WOOD | 2024-03-06 | 2024-03-06 | 2025-02-14 | On-Time |  | 2025-03-06 | 2025-03-06 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35535990 | T2 CARIBOU-WESTWOOD 016/332 GO95 RPL | 93G
LC | 128245144 | 016/334 | T2 CARIBOU-WESTWOOD 016/334 GO95 RPL | TABLEMTN | ETL.6300.POLE.WOOD | 2024-03-06 | 2024-03-06 | 2025-02-15 | On-Time |  | 2025-03-06 | 2025-03-06 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35535991 | T2 CARIBOU-WESTWOOD 016/334 GO95 RPL | 93G
LC | 128245476 | 028/490 | T2 WV KESWICK-TRINITY 28/490L RPR ANCW | TABLEMTN | ETL.7270.POLE.STPS | 2024-03-06 | 2024-03-06 | 2025-02-22 | On-Time |  | 2025-03-06 | 2025-03-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Anchor-Wood | Repair | 46311295 | T2 WV KESWICK-TRINITY 28/490L RPR ANCW | ICW
LC | 128246530 | 035/001 | T2 RIO DL JCT-BRDGVLLE 035/001 GO95 RPL | EUREKA | ETL.7850.POLE.WOOD | 2024-03-06 | 2024-03-06 | 2024-03-06 | Past Due |  | 2025-03-06 | 2025-03-06 | 401T | TR2 |  | E - Schd Compl Yr 0 | Open | REGW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35517206 | T2 RIO DELL JCT-BRIDGEVILLE 35/2 GO95 | 93G
LC | 128246744 | 003/013 | T2 SONOMA-PUEBLO 3/13 GO95 CLEAR | LAKEVLLE | ETL.3810.POLE.NWOD | 2024-03-06 | 2024-03-06 | 2024-03-09 | On-Time |  | 2025-03-06 | 2025-03-06 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR FIRE COMP OH TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 31655283 | T2 SONOMA-PUEBLO 003/014 GO95 | 93G
LC | 128246903 | 001/023 | T2 EI FLINT TAP 001/023 COTTER | SACTO | ETL.3341.INSL.NCER | 2024-03-06 | 2024-03-06 | 2024-12-19 | On-Time |  | 2025-03-06 | 2025-03-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46324624 | T2 EI FLINT TAP 001/023 COTTER | ICW
LC | 128247447 | 004/050 | T2 WV MTN GATE JCT-CASCADE 4/50 INS DMPW | TABLEMTN | ETL.7640.INSL.NCER | 2024-03-06 | 2024-03-06 | 2025-01-08 | On-Time |  | 2025-03-06 | 2025-03-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46303866 | T2 WV MTN GATE JCT-CASCADE 4/50 INS DMPW | ICW
LC | 128247712 | 047/001 | T2 WV FORT ROSS-GUALALA 47/1 TOUCH | LAKEVLLE | ETL.6980.POLE.NWOD | 2024-03-06 | 2024-03-06 | 2024-03-06 | Past Due |  | 2024-09-06 | 2025-03-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46493810 | T2 WV FORT ROSS-GUALALA 47/1 TOUCH | ICW
LC | 128249149 | 17 | T2 PARDEE #1 TAP 0/0 RPR SWTCH | VICTOR | ETL.8231.SWIT | 2024-03-07 | 2024-03-06 | 2024-11-14 | On-Time |  | 2025-03-06 | 2025-03-06 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | Out of Adjustment | Switch | Repair | 46298632 | T2 PARDEE #1 TAP 0/0 RPR SWTCH | ICE
LC | 128249213 | 009/125 | T2 VALLEY SPRINGS-CLAY 9/125 RPR GYWW | VICTOR | ETL.8264.POLE.WOOD | 2024-03-07 | 2024-03-06 | 2024-07-17 | On-Time |  | 2025-03-06 | 2025-03-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46219956 | T2 VALLEY SPRINGS-CLAY 9/125 RPR GYWW | ICW
LC | 128249241 | 008/113 | T2 VLLY SPRNGS-CLAY 8/113 RPR GYWW | VICTOR | ETL.8264.POLE.WOOD | 2024-03-07 | 2024-03-06 | 2025-05-09 | Past Due |  | 2025-03-06 | 2025-03-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298635 | T2 VLLY SPRNGS-CLAY 8/113 RPR GYWW | ICW
LC | 128252575 | 024/098 | T2 DI DIABLO-GATES #1 24/98 RPR SHLS | PISMOBCH | ETL.5960.TOWR | 2024-03-07 | 2024-03-06 | 2025-02-10 | On-Time |  | 2025-03-06 | 2025-03-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329565 | T2 DI DIABLO-GATES #1 24/98 RPR SHLS | ICS
LC | 128252741 | 009/040 | T2 DI DIABLO-GATES #1 009/040 RPL INSS | PISMOBCH | ETL.5960.INSL.CERA | 2024-03-07 | 2024-03-06 | 2025-02-03 | On-Time |  | 2025-03-06 | 2025-03-06 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577601 | T2 DI DIABLO-GATES #1 009/040 RPL INSS | 93K
LC | 128252748 | 005/027 | T2 DI DIABLO-GATES #1 005/027 RPL HRDT | PISMOBCH | ETL.5960.TOWR | 2024-03-07 | 2024-03-06 | 2024-05-02 | On-Time |  | 2025-03-06 | 2025-03-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46236823 | T2NT DI DIABLO-GATES #1 005/027 RPL HRDT | ICQ
LC | 128252770 | 015/063 | T2 DBL-GATES #1 015/063 TOUCH | PISMOBCH | ETL.5960.TOWR | 2024-03-07 | 2024-03-06 | 2025-05-21 | Past Due |  | 2024-09-06 | 2025-03-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476141 | T2 DI DBL-GATES #1 015/063 TOUCH | ICQ
LC | 128252783 | 014/059 | T2 DI DIABLO-GATES #1 014/059 RPR SHLS | PISMOBCH | ETL.5960.TOWR | 2024-03-07 | 2024-03-06 | 2025-02-24 | On-Time |  | 2025-03-06 | 2025-03-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329566 | T2 DI DIABLO-GATES #1 014/059 RPR SHLS | ICS
LC | 128254553 | 028/170 | T2 DI TEMBLOR-SLO 28/170 TOUCH | PISMOBCH | ETL.3960.TOWR | 2024-03-08 | 2024-03-06 | 2024-03-06 | Past Due |  | 2024-09-06 | 2025-03-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46489459 | T2 DI TEMBLOR-SLO 28/170 TOUCH | ICQ
LC | 128258229 | 028/171 | T2 DI TEMBLOR-SLO 28/171 TOUCH | PISMOBCH | ETL.3960.TOWR | 2024-03-08 | 2024-03-06 | 2025-03-04 | On-Time |  | 2024-09-06 | 2025-03-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46475658 | T2 DI TEMBLOR-SLO 28/171 TOUCH | ICQ
LC | 128303807 | 028/167 | T2 DI TEMBLOR - SLO 28/167 RPR STRT | PISMOBCH | ETL.3960.TOWR | 2024-03-18 | 2024-03-06 | 2025-01-06 | On-Time |  | 2025-03-06 | 2025-03-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46303830 | T2NT DI TEMBLOR - SLO 28/167 RPR STRT | ICQ
LC | 128304997 | 028/166 | T2 DI TEMBLOR-SL OBISPO 28/166 TOUCH | PISMOBCH | ETL.3960.TOWR | 2024-03-19 | 2024-03-06 | 2025-03-04 | On-Time |  | 2024-09-06 | 2025-03-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46475657 | T2 DI TEMBLOR-SL OBISPO 28/166 TOUCH | ICQ
LC | 128306422 | 012/286 | T2 DI DRUM-GRAS VLY-WMR 12/286 RPR GYWW | SACTO | ETL.6760.POLE.NWOD | 2024-03-19 | 2024-03-06 | 2025-01-31 | On-Time |  | 2025-03-06 | 2025-03-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46323920 | T2 DI DRUM-GRAS VLY-WMR 12/286 RPR GYWW | ICW
LC | 129482843 | 005/139 | T3 DRM-GRS VALLEY-WIMAR 5/139 GO95 | SACTO | ETL.6760.POLE.WOOD | 2024-09-06 | 2024-09-06 | 2024-10-27 | On-Time |  | 2025-03-06 | 2025-03-06 | 401T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCL COMP OH TR3 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35580492 | T3 DRM-GRS VALLEY-WIMAR 5/139 GO95 | 93G
LC | 129485256 | 000/008 | T3 KESWICK-TRINITY 000/008 ATS | TABLEMTN | ETL.7270.POLE.WOOD | 2024-09-06 | 2024-09-06 | 2024-09-12 | On-Time |  | 2025-03-06 | 2025-03-06 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 FRAB | No Good/Out of Stdrd | Conductor-Wood | Repair | 46311194 | T3 KESWICK-TRINITY 000/008 ATS | ICW
LC | 129485513 | B021/484 | T3 DRM-GRS VLY-WMR B021/484 INS ANCW | SACTO | ETL.6760.POLE.WOOD | 2024-09-06 | 2024-09-06 | 2024-11-01 | On-Time |  | 2025-03-06 | 2025-03-06 | 637T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCL COMP OH TR3 PRTO FRAB NTDE | Missing | Anchor-Wood | Install | 35579893 | T3 EI DRM-GRS VLY-WMR B021/484 INS ANCW | 93E
LC | 130854356 | 028/490 | T2 WV KESWICK-TRINITY 28/490R RPR ANCW | TABLEMTN | ETL.7270.POLE.STPS | 2025-02-12 | 2024-03-06 | 2025-02-22 | On-Time |  | 2025-03-06 | 2025-03-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Anchor-Wood | Repair | 46474291 | T2 WV KESWICK-TRINITY 28/490R RPR ANCW | ICW
LC | 130854359 | 028/490 | T2 WV KESWICK-TRINITY 28/490C RPR ANCW | TABLEMTN | ETL.7270.POLE.STPS | 2025-02-12 | 2024-03-06 | 2025-02-22 | On-Time |  | 2025-03-06 | 2025-03-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Anchor-Wood | Repair | 46474292 | T2 WV KESWICK-TRINITY 28/490C RPR ANCW | ICW
LC | 123058024 | T-166 | T2NT EI MIDWAY-SANTA MARIA T-166 RMV VEG | MIDWAY | ETL.9240.TOWR | 2022-03-07 | 2022-03-07 | 2023-12-22 | On-Time |  | 2025-03-07 | 2025-03-07 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO FRAA | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128250013 | 003/075 | T2 EI COLEMAN-CTONWD 03/075 RPR STRW | TABLEMTN | ETL.6430.POLE.WOOD | 2024-03-07 | 2024-03-07 | 2025-03-04 | On-Time |  | 2025-03-07 | 2025-03-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46332413 | T2 EI COLEMAN-CTONWD 03/075 RPR STRW | ICW
LC | 128250816 | 004/050 | T2 EI SNEATH LNE-PCFCA 4/50C RPR GYWW | METCALF | ETL.7575.POLE.STPS | 2024-03-07 | 2024-03-07 | 2025-03-06 | On-Time |  | 2025-03-07 | 2025-03-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286823 | T2 EI SNEATH LNE-PCFCA 4/50C RPR GYWW | ICW
LC | 128250938 | 000/000C | T2 EI HAT CREEK #1-PIT #1 0/0C RPR SWTC | TABLEMTN | ETL.7020.POLE.NWOD | 2024-03-07 | 2024-03-07 | 2025-02-25 | On-Time |  | 2025-03-07 | 2025-03-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Switch-Wood | Repair | 46332414 | T2 EI HAT CREEK #1-PIT #1 0/0C RPR SWTC | ICW
LC | 128251168 | 006/129 | T2 EI CARIBOU-WESTWOOD 06/129 RPR INSW | TABLEMTN | ETL.6300.INSL.CERA | 2024-03-07 | 2024-03-07 | 2025-01-18 | On-Time |  | 2025-03-07 | 2025-03-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46332415 | T2 EI CARIBOU-WESTWOOD 06/129 RPR INSW | ICW
LC | 128251578 | 006/130 | T2 EI CARIBOU-WESTWD 06/130 RPR INSW | TABLEMTN | ETL.6300.INSL.CERA | 2024-03-07 | 2024-03-07 | 2025-01-18 | On-Time |  | 2025-03-07 | 2025-03-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46332416 | T2 EI CARIBOU-WESTWD 06/130 RPR INSW | ICW
LC | 128251996 | 002/017 | T2 EI OLUM-NRTH TWR-CRSTI 2/17 BNT STEEL | CONCORD | ETL.3180.TOWR | 2024-03-07 | 2024-03-07 | 2025-02-08 | On-Time |  | 2025-03-07 | 2025-03-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286467 | T2 EI OLUM-NRTH TWR-CRSTI 2/17 BNT STEEL | ICQ
LC | 128252547 | 018/073 | T2 DI DBLO-MDWAY #2 18/073 TOUCH | PISMOBCH | ETL.5970.TOWR | 2024-03-07 | 2024-03-07 | 2025-02-21 | On-Time |  | 2024-09-07 | 2025-03-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46474212 | T2 DI DBLO-MDWAY #2 18/073 TOUCH | ICQ
LC | 128252607 | 000/004 | T2 DI MRO BAY TPMPLTN 0/4 RPR ADSS | PISMOBCH | ETL.5933.POLE.NWOD | 2024-03-07 | 2024-03-07 | 2024-07-30 | On-Time |  | 2024-06-07 | 2025-03-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Steel | Repair | 46229507 | T2 DI MRO BAY TPMPLTN 0/4 RPR ADSS | ICS
LC | 128252639 | 018/071 | T2 DI DIABLO-MIDWAY #2 18/71 RPR GYWT | PISMOBCH | ETL.5970.TOWR | 2024-03-07 | 2024-03-07 | 2025-01-22 | On-Time |  | 2025-03-07 | 2025-03-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46391421 | T2 DI DIABLO-MIDWAY #2 18/71 RPR GYWT | ICQ
LC | 128252658 | 011/046 | T2 MRRW BAY TPMPLTN 11/46 TOUCH | PISMOBCH | ETL.5933.TOWR | 2024-03-07 | 2024-03-07 | 2024-03-07 | Past Due |  | 2024-09-07 | 2025-03-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476156 | T2 DI MRRW BAY TPMPLTN 11/46 TOUCH | ICQ
LC | 128252701 | 013/054 | T2 DI MRR BAY TPMPLTN 13/54 TOUCH | PISMOBCH | ETL.5933.TOWR | 2024-03-07 | 2024-03-07 | 2025-03-05 | On-Time |  | 2024-09-07 | 2025-03-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46475659 | T2 DI MRR BAY TPMPLTN 13/54 TOUCH | ICQ
LC | 128252705 | 013/050 | T2 DI DBLO MIDWAY #2 13/50 RPL HRDT | PISMOBCH | ETL.5970.TOWR | 2024-03-07 | 2024-03-07 | 2025-03-03 | On-Time |  | 2025-03-07 | 2025-03-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46391336 | T2 DI DBLO MIDWAY #2 13/50 RPL HRDT | ICQ
LC | 128254258 | 022/091 | T2 DI DIABLO-GATES #1 22/91 RPR SHLD | PISMOBCH | ETL.5960.TOWR | 2024-03-08 | 2024-03-07 | 2025-02-10 | On-Time |  | 2025-03-07 | 2025-03-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329567 | T2 DI DIABLO-GATES #1 22/91 RPR SHLD | ICS
LC | 128254996 | 149 | T2 IR SBNTE GZLY CLRMNT #2 0/4 RPR SWTC | CONCORD | ETL.3750.SWIT | 2024-03-08 | 2024-03-07 | 2024-07-23 | On-Time |  | 2025-03-07 | 2025-03-07 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW IR FIRE COMP OH TR2 PRTO | Out of Adjustment | Switch | Repair | 46220587 | T2 IR SBNTE GZLY CLRMNT #2 0/4 RPR SWTC | ICE
LC | 128255066 | 014/053 | T2 DI DIABLO-MIDWAY #2 14/53 RPR SHLS | PISMOBCH | ETL.5970.TOWR | 2024-03-08 | 2024-03-07 | 2025-02-26 | On-Time |  | 2025-03-07 | 2025-03-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329579 | T2 DI DIABLO-MIDWAY #2 14/53 RPR SHLS | ICS
LC | 128268089 | 27 | T2 CW MONTA VISTA-BURNS 01/013 RPR SWTC | MOSSLNDG | ETL.7590.SWIT | 2024-03-10 | 2024-03-07 | 2024-08-04 | On-Time |  | 2024-09-07 | 2025-03-07 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW CLR COMP OH FMOB TR2 PRTO DURA BRIN | Out of Adjustment | Switch | Repair | 46210381 | T2 CW MONTA VISTA-BURNS 01/013 RPR SWTC | ICE
LC | 129404988 | 011/046 | T2 DI MORRO BAY-TMPLTN 11/46 RPR OPGW | PISMOBCH | ETL.5933.TOWR | 2024-08-19 | 2024-03-07 | 2025-03-03 | On-Time |  | 2025-03-07 | 2025-03-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46329550 | T2 DI MORRO BAY-TMPLTN 11/46 RPR OPGW | ICS
LC | 123062961 | 040/162A | T2NT EI DBLO-MIDWAY #3 40/162A RPR GYWS | PISMOBCH | ETL.5980.TOWR | 2022-03-08 | 2022-03-08 | 2023-07-12 | On-Time |  | 2025-03-08 | 2025-03-08 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45619964 | T2 EI DIABLO-MIDWAY #3 40/162A RPR GYWS | ICS
LC | 128254907 | 002/016 | T2 EI OLM-NORTH TWR-CHRST 2/16 BNT STEEL | CONCORD | ETL.3180.TOWR | 2024-03-08 | 2024-03-08 | 2024-11-05 | On-Time |  | 2025-03-08 | 2025-03-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286471 | T2 EI OLM-NORTH TWR-CHRST 2/16 BNT STEEL | ICQ
LC | 128255398 | 008/112 | T2 PARDEE #1 TAP 8/112 RPL INSW | VICTOR | ETL.8231.INSL.NCER | 2024-03-08 | 2024-03-08 | 2024-07-18 | On-Time |  | 2025-03-08 | 2025-03-08 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35558550 | T2 PARDEE #1 TAP 8/112 RPL INSW | 93I
LC | 128255989 | 028/116 | T2 DIABLO-MIDWAY #3 28/116 RPR INSS | PISMOBCH | ETL.5980.INSL.NCER | 2024-03-08 | 2024-03-08 | 2024-11-17 | On-Time |  | 2024-09-08 | 2025-03-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46219909 | T2 DIABLO-MIDWAY #3 28/116 RPR INSS | ICS
LC | 128256057 | 010/129 | T2 WV KESWICK-TRINITY 10/129 RPL STRW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-03-08 | 2024-03-08 | 2025-04-24 | Past Due |  | 2025-03-08 | 2025-03-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573303 | T2 WV KESWICK-TRINITY 10/129 RPL POLE | 70Y
LC | 128257099 | 001/012 | T2NT EI OLM-NRTH TWR-CRSTI 1/12 RPR STRT | CONCORD | ETL.3180.TOWR | 2024-03-08 | 2024-03-08 | 2024-03-08 | Past Due |  | 2027-03-08 | 2025-03-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286470 | T2 EI OLM-NRTH TWR-CRSTI 1/12 BNT STEEL | ICQ
LC | 128257111 | 001/032 | T2 EI PALERMO-OROVILLE #1 1/32 RPL POLE | TABLEMTN | ETL.7730.POLE.WOOD | 2024-03-08 | 2024-03-08 | 2025-02-17 | On-Time |  | 2025-03-08 | 2025-03-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574039 | T2 EI PALERMO-OROVILLE #1 1/32 RPL POLE | 70Y
LC | 128257203 | 016/009 | T2 WV HMBLDT BY-RIO DLL JCT 16/9 REFRAME | EUREKA | ETL.7100.POLE.WOOD | 2024-03-08 | 2024-03-08 | 2024-05-20 | On-Time |  | 2025-03-08 | 2025-03-08 | 637 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 31589213 | T2 DI HMBLDT BY-RIO DL JCT 16/9 RPL ANCW | 93E
LC | 128257370 | 013/050 | T2 DI DIABLO-MIDWAY #3 013/050 COTTER | PISMOBCH | ETL.5980.INSL | 2024-03-08 | 2024-03-08 | 2025-02-26 | On-Time |  | 2025-03-08 | 2025-03-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329587 | T2 DI DIABLO-MIDWAY #3 013/050 COTTER | ICS
LC | 128258001 | 001/010 | T2 EI OLUM-NORTH TOWR-CRST 1/10 RPR FOND | CONCORD | ETL.3180.TOWR | 2024-03-08 | 2024-03-08 | 2025-02-27 | On-Time |  | 2025-03-08 | 2025-03-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46286469 | T2 EI OLUM-NORTH TOWR-CRST 1/10 RPR FOND | ICQ
LC | 128258123 | 000/009 | T2 EI OLEUM-G #2 000/009 BNT STEEL | CONCORD | ETL.3160.INSL.NCER | 2024-03-08 | 2024-03-08 | 2025-04-14 | Past Due |  | 2025-03-08 | 2025-03-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286468 | T2 EI OLEUM-G #1 000/009 BNT STEEL | ICQ
LC | 128281244 | 020/082 | T2 DI DIABLO-MIDWAY #3 20/82 RPL RPTS | PISMOBCH | ETL.5980.TOWR | 2024-03-13 | 2024-03-08 | 2025-02-26 | On-Time |  | 2025-03-08 | 2025-03-08 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46329670 | T2 DI DIABLO-MIDWAY #3 20/82 RPL RPTS | ICB
LC | 128281319 | 018/075 | T2 DIABLO-MIDWAY #3 18/75 TOUCH | PISMOBCH | ETL.5980.TOWR | 2024-03-13 | 2024-03-08 | 2024-03-08 | Past Due |  | 2024-09-08 | 2025-03-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476152 | T2 DI DIABLO-MIDWAY #3 18/75 TOUCH | ICQ
LC | 128281476 | 015/058 | T2 DIABLO-MIDWAY #3 15/58 TOUCH | PISMOBCH | ETL.5980.TOWR | 2024-03-13 | 2024-03-08 | 2024-03-08 | Past Due |  | 2024-09-08 | 2025-03-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472219 | T2 DI DIABLO-MIDWAY #3 15/58 RPR STRT | ICQ
LC | 128281477 | 015/059 | T2 DI DIABLO-MIDWAY #3 15/59 RPR SHLS | PISMOBCH | ETL.5980.TOWR | 2024-03-13 | 2024-03-08 | 2025-02-26 | On-Time |  | 2025-03-08 | 2025-03-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329616 | T2 DI DIABLO-MIDWAY #3 15/59 RPR SHLS | ICS
LC | 128292816 | 013/051 | T2 DI DIABLO-MIDWAY #3 13/51 RPR SHLD | PISMOBCH | ETL.5980.TOWR | 2024-03-15 | 2024-03-08 | 2025-02-26 | On-Time |  | 2025-03-08 | 2025-03-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329617 | T2 DI DIABLO-MIDWAY #3 13/51 RPR SHLS | ICS
LC | 128293020 | 002/018 | T2 DI CHRISTIE-WLLW PSS 2/18R RPR GYWW | CONCORD | ETL.6370.POLE.WDPS | 2024-03-15 | 2024-03-08 | 2025-02-02 | On-Time |  | 2025-03-08 | 2025-03-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286508 | T2 DI CHRISTIE-WLLW PSS 2/18R RPR GYWW | ICW
LC | 128293245 | 004/047 | T2 DI JOLON TAP 4/47 RPR GYWW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-03-15 | 2024-03-08 | 2025-01-23 | On-Time |  | 2025-03-08 | 2025-03-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391163 | T2 DI JOLON TAP 4/47 RPR GYWW | ICW
LC | 128293419 | 022/177C | T2 DI MID FRK-GOLD HILL 22/177C RPR GYWW | SACTO | ETL.5140.POLE.NWOD | 2024-03-15 | 2024-03-08 | 2024-04-08 | On-Time |  | 2024-09-08 | 2025-03-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46215972 | T2 DI MID FRK-GOLD HILL 22/177C RPR GYWW | ICW
LC | 128299570 | 021/166A | T2 DI MID FRK-GOLD HILL 21/166A RPR GYWW | SACTO | ETL.5140.POLE.NWOD | 2024-03-18 | 2024-03-08 | 2024-04-08 | On-Time |  | 2024-09-08 | 2025-03-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46215973 | T2 DI MID FRK-GOLD HILL 21/166A RPR GYWW | ICW
LC | 128303410 | 028/116 | T2 DI DIABLO-MIDWAY #3 28/116 INSP STRT | PISMOBCH | ETL.5980.TOWR | 2024-03-18 | 2024-03-08 | 2024-10-01 | On-Time |  | 2025-03-08 | 2025-03-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Overgrown | Structure-Tower | Inspect | 46327070 | T2 DI DIABLO-MIDWAY #3 28/116 INSP STRT | ICQ
LC | 128303442 | 002/022 | T2 DI CHRISTIE-WILLOW PASS 2/22 RPR GYWW | CONCORD | ETL.6370.POLE.STPS | 2024-03-18 | 2024-03-08 | 2024-05-28 | On-Time |  | 2024-09-08 | 2025-03-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46220486 | T2 DI CHRISTIE-WILLOW PASS 2/22 RPR GYWW | ICW
LC | 128303457 | 019/264 | T2 DI SISQ-STAYSWSTA 19/264 RPR GYWW | PISMOBCH | ETL.3700.POLE.NWOD | 2024-03-18 | 2024-03-08 | 2025-02-20 | On-Time |  | 2025-03-08 | 2025-03-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46390359 | T2 DI SISQ-STAYSWSTA 19/264 RPR GYWW | ICW
LC | 128303459 | 032/495 | T2 CLAY-MARTEL 32/495 RPR GYWW | VICTOR | ETL.8250.POLE.NWOD | 2024-03-18 | 2024-03-08 | 2024-03-08 | Past Due |  | 2029-03-08 | 2025-03-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46326978 | +T2 DI CLAY-MARTEL 32/495 RPR GYWW | ICW
LC | 128303620 | 032/495 | T2 DI CLAY-MARTEL 32/495 GO95 | VICTOR | ETL.8250.POLE.NWOD | 2024-03-18 | 2024-03-08 | 2024-03-08 | Past Due |  | 2025-03-08 | 2025-03-08 | 401T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35573189 | T2 DI CLAY-MARTEL 32/495 GO95 | 93G
LC | 128303823 | 019/451 | T2 DI DRM-GRSS VLLY-WMR 19/451 RPL POLE | SACTO | ETL.6760.POLE.WOOD | 2024-03-18 | 2024-03-08 | 2024-12-03 | On-Time |  | 2025-03-08 | 2025-03-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573453 | T2 DI DRM-GRSS VLLY-WMR 19/451 RPL POLE | 70Y
LC | 128305149 | 022/163 | T2 DI TRINITY-CTTNWD 022/163L RPR ANCW | TABLEMTN | ETL.4040.POLE.STPS | 2024-03-19 | 2024-03-08 | 2024-07-20 | On-Time |  | 2024-09-08 | 2025-03-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46227621 | T2 DI TRINITY-CTTNWD 022/163L RPR ANCW | ICW
LC | 128305261 | 024/173 | T2 DI TRINITY-CTTNWOOD 24/173 RPR ANCW | TABLEMTN | ETL.4040.POLE.STPS | 2024-03-19 | 2024-03-08 | 2025-02-25 | On-Time |  | 2025-03-08 | 2025-03-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46332441 | T2 DI TRINITY-CTTNWOOD 24/173 RPR ANCW | ICW
LC | 128306310 | 005/068 | T2 DI JOLON TAP 005/068 RPL HRDD | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-03-19 | 2024-03-08 | 2025-02-03 | On-Time |  | 2025-03-08 | 2025-03-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46391165 | T2 DI JOLON TAP 005/068 RPL HRDD | ICW
LC | 128335985 | 030/454 | T2 DI CLAY-MARTEL 030/454 RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-03-20 | 2024-03-08 | 2024-03-08 | Past Due |  | 2025-03-08 | 2025-03-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46326979 | +T2 DI CLAY-MARTEL 030/454 RPR STRW | ICW
LC | 128336388 | 013/260 | T2 DI CLGT-PALERMO 013/260 RPL HRDD | SACTO | ETL.6500.POLE.WOOD | 2024-03-20 | 2024-03-08 | 2025-03-03 | On-Time |  | 2025-03-08 | 2025-03-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46383047 | T2 DI CLGT-PALERMO 013/260 RPL HRDD | ICW
LC | 128352966 | 018/085 | T2 DI MOSS LDNG-LS BANS 18/85 TOUCH | MOSSLNDG | ETL.6040.TOWR | 2024-03-22 | 2024-03-08 | 2025-03-10 | Past Due |  | 2024-09-08 | 2025-03-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46475675 | T2 DI MOSS LDNG-LS BANS 18/85 TOUCH | ICQ
LC | 128352967 | 018/085 | T2 DI MOSS LDNG-LS BANS 18/85 RMV VEG | MOSSLNDG | ETL.6040.TOWR | 2024-03-22 | 2024-03-08 | 2025-03-07 | On-Time |  | 2025-03-08 | 2025-03-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128369752 | 022/163 | T2 DI TRINITY-CTTNWD 022/163R RPR ANCW | TABLEMTN | ETL.4040.POLE.STPS | 2024-03-26 | 2024-03-08 | 2024-07-20 | On-Time |  | 2024-09-08 | 2025-03-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46227622 | T2 DI TRINITY-CTTNWD 022/163R RPR ANCW | ICW
LC | 128369754 | 022/163 | T2 DI TRINITY-CTTNWD 022/163C RPR ANCW | TABLEMTN | ETL.4040.POLE.STPS | 2024-03-26 | 2024-03-08 | 2024-07-20 | On-Time |  | 2024-09-08 | 2025-03-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46227624 | T2 DI TRINITY-CTTNWD 022/163C RPR ANCW | ICW
LC | 123086302 | 028/168 | T2NT DI TEMBLOR-SLO 28/168 RPR STRT | PISMOBCH | ETL.3960.TOWR | 2022-03-10 | 2022-03-09 | 2023-07-24 | On-Time |  | 2025-03-09 | 2025-03-09 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45634767 | T2 DI TEMBLOR-SN LS OBSP 28/168 RPR STRT | ICQ
LC | 123087358 | 010/094 | T2NT DI BRDGVLLE-CTTNWD 10/94 RPR ADSS | TABLEMTN | ETL.1110.POLE.WDPS | 2022-03-10 | 2022-03-09 | 2023-08-14 | On-Time |  | 2025-03-09 | 2025-03-09 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45643899 | T2 DI BRDGVLLE-CTTNWD 10/94 RPR ADSS | ICW
LC | 127014069 | A004/103 | T2 WV CSCD-BNTN-DSCHTS A4/103 RPL STRW | TABLEMTN | ETL.6310.POLE.WOOD | 2023-09-09 | 2023-09-09 | 2024-11-15 | On-Time |  | 2025-03-09 | 2025-03-09 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35521772 | T2 CASCADE-BNTN-DSCHTS A4/103 RPL POLE | 70Y
LC | 129493991 | 007/006 | T3 WV KONOCTI-EAGLE ROCK 7/006 INS DMPW | WILLITS | ETL.6861.INSL.NCER | 2024-09-09 | 2024-09-09 | 2024-12-16 | On-Time |  | 2025-03-09 | 2025-03-09 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO NTDE | Missing | Damper-Wood | Install | 46333773 | T3 KONOCTI-EAGLE ROCK 7/006 INS DMPW | ICW
LC | 123092068 | 000/001 | T2NT EI RND MTN-TBLE MTN #1 0/1 RPR FOND | TABLEMTN | ETL.6060.TOWR | 2022-03-11 | 2022-03-10 | 2023-08-28 | On-Time |  | 2025-03-10 | 2025-03-10 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45581907 | T2 EI ROUND MTN-TBLE MTN #1 0/1 RPR FOND | ICQ
LC | 123099865 | 001/032 | T2NT DI JFFRSN-STNFRD 001/032 RPR ADSS | METCALF | ETL.7220.POLE.WOOD | 2022-03-14 | 2022-03-10 | 2024-04-01 | On-Time |  | 2025-03-10 | 2025-03-10 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 46080469 | T2NT DI JFFRSN-STNFRD 001/032 RPR ADSS | ICW
LC | 123145224 | 004/030 | T2NT DI CTTNWD-DELEVAN #1 4/30 RPR FOND | TABLEMTN | ETL.4550.TOWR | 2022-03-17 | 2022-03-10 | 2023-07-13 | On-Time |  | 2025-03-10 | 2025-03-10 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45885314 | T2NT DI CTTNWD-DELEVAN #1 4/30 RPR FOND | ICQ
LC | 123155460 | 011/101 | T2NT DI BRDGVILLE-CTTNWD 11/101 RPR ADSS | TABLEMTN | ETL.1110.POLE.WDPS | 2022-03-19 | 2022-03-10 | 2023-08-05 | On-Time |  | 2025-03-10 | 2025-03-10 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45644087 | T2 DI BRIDGEVILLE-CTTNWD 11/101 RPR ADSS | ICW
LC | 123187115 | 011/105 | T2NT DI BRDGVILLE-CTTNWD 11/105 RPR ADSS | TABLEMTN | ETL.1110.POLE.WDPS | 2022-03-25 | 2022-03-10 | 2023-08-05 | On-Time |  | 2025-03-10 | 2025-03-10 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45644161 | T2 DI BRIDGEVILLE-CTTNWD 11/105 RPR ADSS | ICW
LC | 128268110 | 002/049 | T2 EI HAT CREEK #1-WSTWD 2/49 RPR INSW | TABLEMTN | ETL.7030.INSL.NCER | 2024-03-10 | 2024-03-10 | 2025-02-11 | On-Time |  | 2025-03-10 | 2025-03-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46332418 | T2 EI HAT CREEK #1-WSTWD 2/49 RPR INSW | ICW
LC | 123092925 | 018/082 | T3NT EI MSS LNDING-MTCLF 18/82 BNT STEEL | MOSSLNDG | ETL.6050.TOWR | 2022-03-11 | 2022-03-11 | 2023-07-25 | On-Time |  | 2025-03-11 | 2025-03-11 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45650126 | T3NT EI MSS LNDING-MTCLF 18/82 BNT STEEL | ICQ
LC | 123099254 | 003/015 | T2NT DI MELONES-WILSON 3/15 RPR FOND | VICTOR | ETL.5080.TOWR | 2022-03-14 | 2022-03-11 | 2025-02-26 | On-Time |  | 2025-03-11 | 2025-03-11 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46446184 | T2NT DI MELONES-WILSON 3/15 RPR FOND | ICQ
LC | 123155792 | 004/039 | T2NT DI CBRILLO-SANTA YNEZ 4/39 INS STEP | PISMOBCH | ETL.1200.POLE.NWOD | 2022-03-19 | 2022-03-11 | 2023-08-31 | On-Time |  | 2025-03-11 | 2025-03-11 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB NTDE | Missing | Hardware-Wood | Install | 45592180 | T2NT DI CBRILLO-SANTA YNEZ 4/39 INS STEP | ICW
LC | 128269600 | 000/017 | T2 EI TRINITY-MAPLE CREEK 0/17 RPR POLE | EUREKA | ETL.8170.POLE.WOOD | 2024-03-11 | 2024-03-11 | 2025-03-24 | Past Due |  | 2025-03-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46345682 | T2 EI TRINITY-MAPLE CREEK 0/17 RPR POLE | ICW
LC | 128269621 | 022/096A | T2 EI PTTSBRG-TSLA #1 22/96A RMV NEST | CONCORD | ETL.5510.TOWR | 2024-03-11 | 2024-03-11 | 2024-12-22 | On-Time |  | 2025-03-11 | 2025-03-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT COMP OH FMOB TR2 PRTO FRAB NTDE | Debris/Nest/etc. | Structure-Steel | Remove | 46286511 | T2NT EI PTTSBRG-TSLA #1 22/96A RMV NEST | ICS
LC | 128269681 | 002/027 | T2 EI NARROWS #1 TAP 02/027 REGR STRW | SACTO | ETL.6511.POLE.NWOD | 2024-03-11 | 2024-03-11 | 2025-01-15 | On-Time |  | 2025-03-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC REAR ACCL COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46337397 | T2 EI NARROWS #1 TAP 02/027 REGR STRW | ICW
LC | 128269967 | 005/138 | T2 EI WEIMAR-HALSEY 005/138 RPR GYWW | SACTO | ETL.8340.POLE.NWOD | 2024-03-11 | 2024-03-11 | 2025-01-10 | On-Time |  | 2025-03-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46323912 | T2 EI WEIMAR-HALSEY 005/138 RPR GYWW | ICW
LC | 128270163 | 012/087 | T2 EI VACA-SUISUN 012/087 REGRADE | SACTO | ETL.4070.TOWR | 2024-03-11 | 2024-03-11 | 2024-12-17 | On-Time |  | 2025-03-11 | 2025-03-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD ACCL COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46327639 | T2 EI VACA-SUISUN 012/087 REGRADE | ICQ
LC | 128271781 | 000/021 | T2 EI SMRTVLLE-NICOLAUS #2 0/21 RPR INSW | SACTO | ETL.8000.INSL.NCER | 2024-03-11 | 2024-03-11 | 2025-02-21 | On-Time |  | 2025-03-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310257 | T2 EI SMRTVLLE-NICOLAUS #2 0/21 RPR INSW | ICW
LC | 128271803 | 020/110 | T2NT EI LONE TR-CYTN 20/110 RPL RPTS | CONCORD | ETL.6160.INSL.CERA | 2024-03-11 | 2024-03-11 | 2025-03-11 | On-Time |  | 2027-03-11 | 2025-03-11 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46286509 | T2NT EI LONE TR-CYTN 20/110 RPL RPTS | ICB
LC | 128272021 | 060/298 | T2 EI CORTINA-MENDCN #1 60/298 RMV VEG | WILLITS | ETL.1330.TOWR | 2024-03-11 | 2024-03-11 | 2025-02-06 | On-Time |  | 2025-03-11 | 2025-03-11 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128272053 | 005/097 | T2 CORDELIA #2 005/097 RPL POLE | SACTO | ETL.8184.POLE.WOOD | 2024-03-11 | 2024-03-11 | 2025-02-03 | On-Time |  | 2025-03-11 | 2025-03-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557139 | T2 CORDELIA #2 005/097 RPL POLE | 70Y
LC | 128272352 | 002/036C | T2 EI NARROWS #2 TAP 002/036C RMV VEG | SACTO | ETL.6521.POLE.WOOD | 2024-03-11 | 2024-03-11 | 2025-04-21 | Past Due |  | 2025-03-11 | 2025-03-11 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128272413 | 017/110 | T2 EI CNTR CST-LS PSTS 17/110 RPR FOND | CONCORD | ETL.4510.TOWR | 2024-03-11 | 2024-03-11 | 2025-01-15 | On-Time |  | 2025-03-11 | 2025-03-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46286473 | T2 EI CNTR CST-LS PSTS 17/110 RPR FOND | ICQ
LC | 128272515 | 010/067 | T2 EI OLEUM-G #1 010/067 TOUCH | CONCORD | ETL.3150.TOWR | 2024-03-11 | 2024-03-11 | 2025-05-07 | Past Due |  | 2024-09-11 | 2025-03-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAR NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485723 | T2 EI OLEUM-G #1 010/067 TOUCH | ICQ
LC | 128272540 | 010/067 | T2 EI OLEUM-G #1 010/067 UNBURY | CONCORD | ETL.3150.TOWR | 2024-03-11 | 2024-03-11 | 2025-01-28 | On-Time |  | 2025-03-11 | 2025-03-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAR | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46286472 | T2 EI OLEUM-G #1 010/067 UNBURY | ICQ
LC | 128272545 | 024/185A | T2 EI DRUM-HIGGINS 024/185A RPL HRDT | SACTO | ETL.4393.TOWR | 2024-03-11 | 2024-03-11 | 2024-12-17 | On-Time |  | 2025-03-11 | 2025-03-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Hardware-Tower | Install | 46327680 | T2 EI DRUM-HIGGINS 024/185A RPL HRDT | ICQ
LC | 128272564 | 024/185A | T2 EI DRUM-HIGGINS 024/185A RPL INSS | SACTO | ETL.4393.INSL.CERA | 2024-03-11 | 2024-03-11 | 2025-01-10 | On-Time |  | 2025-03-11 | 2025-03-11 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569577 | T2 EI DRUM-HIGGINS 024/185A RPL INSS | 93K
LC | 128272639 | 002/002 | T2 EI TRINITY-MAPLE CREEK 2/002 RPR STRW | EUREKA | ETL.8170.POLE.WOOD | 2024-03-11 | 2024-03-11 | 2025-03-23 | Past Due |  | 2025-03-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46345683 | T2 EI TRINITY-MAPLE CREEK 2/002 RPR POLE | ICW
LC | 128272652 | 024/186A | T2 EI DRUM-HIGGINS 024/186A RPL HRDS | SACTO | ETL.4393.POLE.NWOD | 2024-03-11 | 2024-03-11 | 2025-01-10 | On-Time |  | 2025-03-11 | 2025-03-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Steel | Replace | 46324626 | T2 EI DRUM-HIGGINS 024/186A RPL HRDS | ICS
LC | 128273371 | 002/000 | T2 EI TRINITY-MAPLE CREEK 2/0 RPL POLE | EUREKA | ETL.8170.POLE.WOOD | 2024-03-11 | 2024-03-11 | 2025-03-23 | Past Due |  | 2025-03-11 | 2025-03-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572241 | T2 EI TRINITY-MAPLE CREEK 2/0 RPL PL | 70Y
LC | 128273666 | 005/057 | T2 EI SNEATH LANE-PACIFICA 5/57 RPL POLE | METCALF | ETL.7575.POLE.WOOD | 2024-03-11 | 2024-03-11 | 2024-10-22 | On-Time |  | 2024-09-11 | 2025-03-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35557753 | T2 EI SNEATH LANE-PACIFICA 5/57 RPL POLE | 70Y
LC | 128273830 | 002/012 | T2 VALY SPRINGS-CAL CEMENT 02/12 GO95 | VICTOR | ETL.8220.POLE.NWOD | 2024-03-11 | 2024-03-11 | 2025-03-07 | On-Time |  | 2025-03-11 | 2025-03-11 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35536894 | T2 VALY SPRINGS-CAL CEMENT 02/12 GO95 | 93G
LC | 128273879 | 025/120 | T2 EI CNTRA CSTA-MRGA #1 25/120 RPR FOND | CONCORD | ETL.5452.TOWR | 2024-03-11 | 2024-03-11 | 2025-01-02 | On-Time |  | 2025-03-11 | 2025-03-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46286474 | T2 EI CNTRA CSTA-MRGA #1 25/120 RPR FOND | ICQ
LC | 128274054 | 060/296 | T2 EI CORTINA-MNDCN #1 60/296 TOUCH | WILLITS | ETL.1330.TOWR | 2024-03-11 | 2024-03-11 | 2025-05-19 | Past Due |  | 2024-09-11 | 2025-03-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472281 | T2 EI CORTINA-MNDCN #1 60/296 RPR STRT | ICQ
LC | 128274055 | 060/295 | T2 EI CORTINA-MENDCN #1 60/295 RMV VEG | WILLITS | ETL.1330.TOWR | 2024-03-11 | 2024-03-11 | 2025-02-19 | On-Time |  | 2025-03-11 | 2025-03-11 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128274056 | 060/296 | T2 EI CORTINA-MENDCN #1 60/296 RMV VEG | WILLITS | ETL.1330.TOWR | 2024-03-11 | 2024-03-11 | 2025-02-19 | On-Time |  | 2025-03-11 | 2025-03-11 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128277181 | 159 | T2 IR SBRNTE-GRIZZLY 0/6 RPR SWTC | CONCORD | ETL.3740.SWIT | 2024-03-12 | 2024-03-11 | 2024-03-11 | Past Due |  | 2025-03-11 | 2025-03-11 | 623 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW IR OH TR2 PRTO | Out of Adjustment | Switch | Repair | 46286512 | T2 IR SBRNTE-GRIZZLY 0/6 RPR SWTC | ICE
LC | 128293717 | 012/085 | T2 DI GREEN VALLEY-LLGS 12/85L RPL HRDW | MOSSLNDG | ETL.1720.POLE.WDPS | 2024-03-15 | 2024-03-11 | 2024-06-05 | On-Time |  | 2024-09-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace | 46218788 | T2 DI GREEN VALLEY-LLGS 12/85L RPL HRDW | ICW
LC | 128303189 | 008/054 | T2 DI METCALF-GREEN VALLEY 8/54 TOUCH | MOSSLNDG | ETL.2540.TOWR | 2024-03-18 | 2024-03-11 | 2025-03-14 | Past Due |  | 2024-09-11 | 2025-03-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46477425 | T2 DI METCALF-GREEN VALLEY 8/54 TOUCH | ICQ
LC | 128303206 | 008/055 | T2 DI METCALF-GREEN VALLEY 8/55 TOUCH | MOSSLNDG | ETL.2540.TOWR | 2024-03-18 | 2024-03-11 | 2025-03-14 | Past Due |  | 2024-06-11 | 2025-03-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46477426 | T2 DI METCALF-GREEN VALLEY 8/55 TOUCH | ICQ
LC | 128303214 | 008/055 | T2 DI METCALF-MORGAN HILL 8/55 RPR INSS | MOSSLNDG | ETL.2570.INSL.NCER | 2024-03-18 | 2024-03-11 | 2025-02-28 | On-Time |  | 2025-03-11 | 2025-03-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46391205 | T2 DI METCALF-MORGAN HILL 8/55 RPR INSS | ICS
LC | 128303481 | 012/085 | T2 DI MTCLF-GRN VLLY 012/085 RPR CRSW | MOSSLNDG | ETL.2540.POLE.NWOD | 2024-03-18 | 2024-03-11 | 2025-02-23 | On-Time |  | 2025-03-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46391206 | T2 DI MTCLF-GRN VLLY 012/085 RPR CRSW | ICW
LC | 128303482 | 012/085 | T2 DI MTCLF-GRN VLLY 012/085 TOUCH | MOSSLNDG | ETL.2540.POLE.NWOD | 2024-03-18 | 2024-03-11 | 2024-03-11 | Past Due |  | 2024-09-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46494095 | T2 DI MTCLF-GRN VLLY 012/085 TOUCH | ICW
LC | 128303605 | 009/177 | T2 DI MNTA VSTA-LS GTS 9/177 RPL STRW | METCALF | ETL.7610.POLE.WOOD | 2024-03-18 | 2024-03-11 | 2024-03-11 | Past Due |  | 2025-03-11 | 2025-03-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574114 | T2 DI MNTA VSTA-LS GTS 9/177 RPL STRW | 70Y
LC | 128303612 | 041/173 | T2 DI TMPLTN-GATES 41/173 TOUCH | PISMOBCH | ETL.5934.TOWR | 2024-03-18 | 2024-03-11 | 2024-03-11 | Past Due |  | 2024-09-11 | 2025-03-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476160 | T2 DI TMPLTN-GATES 41/173 TOUCH | ICQ
LC | 128303759 | 009/057 | T2 METCALF-GREEN VALLEY 9/57 RPL INSS | MOSSLNDG | ETL.2540.INSL.CERA | 2024-03-18 | 2024-03-11 | 2024-03-11 | Past Due |  | 2025-03-11 | 2025-03-11 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35596167 | T2 DI METCALF-GREEN VALLEY 9/57 RPL INSS | 93K
LC | 128303917 | 000/006 | T2 DI IBM HARRY RD#1 TAP 0/6 RPR ADSS | METCALF | ETL.2501.TOWR | 2024-03-18 | 2024-03-11 | 2024-06-10 | On-Time |  | 2024-06-11 | 2025-03-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Steel | Repair | 46216062 | T2 DI IBM HARRY RD#1 TAP 0/6 RPR ADSS | ICS
LC | 128322129 | 006/079 | T2 DI JOLON TAP 6/79 REFRAME | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-03-19 | 2024-03-11 | 2025-01-28 | On-Time |  | 2025-03-11 | 2025-03-11 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35573683 | T2 DI JOLON TAP 6/79 RPL CRSW | 93E
LC | 128335893 | 012/089 | T2 DI GREEN VLY-LLAG 12/89 RPR ANCW | MOSSLNDG | ETL.1720.POLE.WDPS | 2024-03-20 | 2024-03-11 | 2024-04-10 | On-Time |  | 2025-03-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46222754 | T2 DI GREEN VLY-LLAG 12/89 RPR ANCW | ICW
LC | 128335894 | 012/089 | T2 DI GREEN VLY-LLAG 12/89 RPR JUMW | MOSSLNDG | ETL.1720.INSL.CERA | 2024-03-20 | 2024-03-11 | 2024-04-10 | On-Time |  | 2024-06-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46218796 | T2 DI GREEN VLY-LLAG 12/89 RPR JUMW | ICW
LC | 128336200 | 009/178 | T2 DI MONTA VST-LS GTS 9/178 RPL STRW | METCALF | ETL.7610.POLE.WOOD | 2024-03-20 | 2024-03-11 | 2024-03-11 | Past Due |  | 2025-03-11 | 2025-03-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCH OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574115 | T2 DI MONTA VST-LS GTS 9/178 RPL STRW | 70Y
LC | 128336343 | 013/086 | T2 DI MTCLF-GRN VLLY 013/086 RPR GYWW | MOSSLNDG | ETL.2540.POLE.WDPS | 2024-03-20 | 2024-03-11 | 2025-02-23 | On-Time |  | 2025-03-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391211 | T2 DI MTCLF-GRN VLLY 013/086 RPR GYWW | ICW
LC | 128336380 | 009/175 | T2 DI MNTA VSTA-LS GTS 009/175 RPL STRW | METCALF | ETL.7610.POLE.WOOD | 2024-03-20 | 2024-03-11 | 2024-03-11 | Past Due |  | 2025-03-11 | 2025-03-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Structure-Wood | Replace | 35573806 | T2 DI MNTA VSTA-LS GTS 009/175 RPL STRW | 70Y
LC | 128336392 | 009/170 | T2 DI MNTA VSTA LS GTOS 09/170 RPR GYWW | METCALF | ETL.7610.POLE.WOOD | 2024-03-20 | 2024-03-11 | 2025-01-02 | On-Time |  | 2025-03-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCH COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286834 | T2 DI MNTA VSTA LS GTOS 09/170 RPR GYWW | ICW
LC | 128336451 | 006/078 | T2 DI JOLON TAP 6/78 RPLC HRDW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-03-20 | 2024-03-11 | 2025-01-23 | On-Time |  | 2025-03-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46391167 | T2 DI JOLON TAP 6/78 RPLC HRDW | ICW
LC | 128336470 | :010/066 | T2 DI GREEN VLY-LLAGAS 10/66 RPL HRDT | MOSSLNDG | ETL.1720.TOWR | 2024-03-20 | 2024-03-11 | 2025-01-27 | On-Time |  | 2025-03-11 | 2025-03-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46404411 | T2 DI GREEN VLY-LLAGAS 10/66 RPL HRDT | ICQ
LC | 128352940 | 003/025 | T2 DI TRINITY-CTTNWD 3/25L RPR GYWW | TABLEMTN | ETL.4040.POLE.STPS | 2024-03-22 | 2024-03-11 | 2024-07-17 | On-Time |  | 2024-09-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46227559 | T2 DI TRINITY-CTTNWD 3/25L RPR GYWW | ICW
LC | 128353119 | 010/189 | T2 DI MNTA VSTA-LS GTS 10/189 RPR POLE | METCALF | ETL.7610.POLE.WOOD | 2024-03-23 | 2024-03-11 | 2025-01-15 | On-Time |  | 2025-03-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Structure-Wood | Repair | 46286869 | T2 DI MNTA VSTA-LS GTS 10/189 RPR POLE | ICW
LC | 128353128 | 009/183 | T2 DI MNTA VSTA-LS GTS 9/183 RPR INSW | METCALF | ETL.7610.INSL.NCER | 2024-03-23 | 2024-03-11 | 2025-01-15 | On-Time |  | 2025-03-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46286870 | T2 DI MNTA VSTA-LS GTS 9/183 RPR INSW | ICW
LC | 128356779 | 003/023 | T2 DI TRINITY-COTTONWOOD 3/23 RPR WDPKR | TABLEMTN | ETL.4040.POLE.WDPS | 2024-03-25 | 2024-03-11 | 2025-01-16 | On-Time |  | 2025-03-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46332444 | T2 DI TRINITY-COTTONWOOD 3/23 RPR WDPKR | ICW
LC | 128444439 | 003/025 | T2 DI TRINITY-CTTNWD 3/25R RPR GYWW | TABLEMTN | ETL.4040.POLE.STPS | 2024-04-04 | 2024-03-11 | 2024-07-17 | On-Time |  | 2024-09-11 | 2025-03-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46230774 | T2 DI TRINITY-CTTNWD 3/25R RPR GYWW | ICW
LC | 128275774 | 030/008 | T2 DI GOLD HILL #1 30/8 RPR IBWW | VICTOR | ETL.6950.POLE.WOOD | 2024-03-12 | 2024-03-12 | 2025-04-12 | Past Due |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46298636 | T2 DI GOLD HILL #1 30/8 RPR IBWW | ICW
LC | 128276819 | 010/123 | T2 EI CLGTE-SMRTVLLE #2 10/123 RPL POLE | SACTO | ETL.6520.POLE.WOOD | 2024-03-12 | 2024-03-12 | 2025-03-05 | On-Time |  | 2025-03-12 | 2025-03-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557136 | T2 EI CLGTE-SMRTVLLE #2 10/123 RPL POLE | 70Y
LC | 128276917 | 018/098 | T2 LONE TREE-CAYETANO 18/98 RPL INSS | CONCORD | ETL.6160.INSL.CERA | 2024-03-12 | 2024-03-12 | 2024-03-12 | Past Due |  | 2025-03-12 | 2025-03-12 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP REMT NOAC CLR OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575002 | T2 EI LONE TREE-CAYETANO RPL INSS IN 2 T | 93K
LC | 128276944 | 006/155 | T2 DEL MONTE-VIEJO 06/155 RMV VEG | MOSSLNDG | ETL.6710.POLE.WOOD | 2024-03-12 | 2024-03-12 | 2024-12-17 | On-Time |  | 2025-03-12 | 2025-03-12 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW PATR REMT SWRK ACCL CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128277305 | 011/258-GUY | T2 EI SALINAS-LAURELS 11/258-GUY RMV VEG | MOSSLNDG | ETL.7930.POLE.WOOD | 2024-03-12 | 2024-03-12 | 2024-12-18 | On-Time |  | 2025-03-12 | 2025-03-12 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP REMT TRAF ACCL ACCM FLAG COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128277682 | 010/002 | T2 EI PTTER VLLY-MENDOCINO 10/2 RPR GYWW | WILLITS | ETL.7810.POLE.WOOD | 2024-03-12 | 2024-03-12 | 2024-04-04 | On-Time |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46220404 | T2 EI PTTER VLLY-MENDOCINO 10/2 RPR GYWW | ICW
LC | 128277792 | 005/123 | T2 EI WEIMAR-HALSEY 5/123 RMV STEP | SACTO | ETL.8340.POLE.NWOD | 2024-03-12 | 2024-03-12 | 2025-01-10 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46323913 | T2 EI WEIMAR-HALSEY 5/123 RMV STEP | ICW
LC | 128277892 | 010/001 | T2 EI POTTER VLLY-MENDOCINO 10/1 RMV VEG | WILLITS | ETL.7810.POLE.NWOD | 2024-03-12 | 2024-03-12 | 2025-02-07 | On-Time |  | 2025-03-12 | 2025-03-12 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128278105 | 004/079 | T2 EI TEMPLETN-ATSCDRO 4/79 RPL INSW | PISMOBCH | ETL.9410.INSL | 2024-03-12 | 2024-03-12 | 2025-04-03 | Past Due |  | 2025-03-12 | 2025-03-12 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573518 | T2 EI TEMPLETN-ATSCDRO 4/79 RPL INSW | 93I
LC | 128278300 | 059/294 | T2 EI CORTINA-MENDOCNO #1 59/294 RMV VEG | WILLITS | ETL.1330.TOWR | 2024-03-12 | 2024-03-12 | 2025-01-24 | On-Time |  | 2025-03-12 | 2025-03-12 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128278527 | 009/009 | T2 EI PTTR VALLEY-MENDOCINO 9/9 RPR GYWW | WILLITS | ETL.7810.POLE.NWOD | 2024-03-12 | 2024-03-12 | 2024-04-04 | On-Time |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46220403 | T2 EI PTTR VALLEY-MENDOCINO 9/9 RPR GYWW | ICW
LC | 128278683 | 004/080 | T2 EI TEMPLETON-ATASCADERO 4/80 RPR POLE | PISMOBCH | ETL.9410.POLE.WOOD | 2024-03-12 | 2024-03-12 | 2025-04-04 | Past Due |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46329656 | T2 EI TEMPLETON-ATASCADERO 4/80 RPR WDPK | ICW
LC | 128278696 | 038/006 | T2 WV RIO DELL JCT-BRDGVLE 38/6 INS DMPW | EUREKA | ETL.7850.INSL.NCER | 2024-03-12 | 2024-03-12 | 2025-03-07 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46345685 | T2 WV RIO DELL JCT-BRDGVLE 38/6 INS DMPW | ICW
LC | 128278989 | 002/008 | T2 EI HUMBLDT-MAPLE CRK 02/08 RPL INSW | EUREKA | ETL.7130.INSL | 2024-03-12 | 2024-03-12 | 2025-04-04 | Past Due |  | 2025-03-12 | 2025-03-12 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574616 | T2 EI HUMBLDT-MAPLE CRK 02/08 RPL INSW | 93I
LC | 128279177 | 004/103 | T2 EI WEIMAR-HALSEY 004/103 RPR POLE | SACTO | ETL.8340.POLE.WOOD | 2024-03-12 | 2024-03-12 | 2025-03-07 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD SWRK CLR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46475603 | T2 EI WEIMAR-HALSEY 004/103 RPR POLE | ICW
LC | 128279472 | 003/016 | T2 EI TRINITY-MAPLE CREEK 3/016 RPR POLE | EUREKA | ETL.8170.POLE.WOOD | 2024-03-12 | 2024-03-12 | 2025-03-23 | Past Due |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46345684 | T2 EI TRINITY-MAPLE CREEK 3/016 RPR POLE | ICW
LC | 128279560 | 033/004 | T2 EI COALINGA #1-SAN MIGUEL 33/04 HANGR | FRESNO | ETL.8580.INSL.CERA | 2024-03-12 | 2024-03-12 | 2024-10-16 | On-Time |  | 2025-03-12 | 2025-03-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46292628 | T2 EI COALINGA #1-SAN MIGUEL 33/04 HANGR | ICQ
LC | 128280259 | 002/056 | T2 EI WEIMAR-HALSEY 2/056 RPR INSW | SACTO | ETL.8340.INSL | 2024-03-12 | 2024-03-12 | 2025-01-10 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46323914 | T2 EI WEIMAR-HALSEY 2/056 RPR INSW | ICW
LC | 128280270 | 002/056 | T2 EI WEIMAR-HALSEY 2/056 RPR POLE | SACTO | ETL.8340.POLE.WOOD | 2024-03-12 | 2024-03-12 | 2025-01-10 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD TRAF CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46323915 | T2 EI WEIMAR-HALSEY 2/056 RPR POLE | ICW
LC | 128282014 | 029/003 | T2 DI GOLD HILL #1 29/3 RPL POLE | VICTOR | ETL.6950.POLE.WOOD | 2024-03-13 | 2024-03-12 | 2025-04-11 | Past Due |  | 2025-03-12 | 2025-03-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573260 | T2 DI GOLD HILL #1 29/3 RPL POLE | 70Y
LC | 128282287 | 028/009 | T2 DI GOLD HILL #1 28/9 RPL POLE | VICTOR | ETL.6950.POLE.WOOD | 2024-03-13 | 2024-03-12 | 2025-04-10 | Past Due |  | 2025-03-12 | 2025-03-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573239 | T2 DI GOLD HILL #1 28/9 RPL POLE | 70Y
LC | 128282550 | 014/174 | T2 DI WEST PT VLY SPRNGS 14/174 RPL INSW | VICTOR | ETL.8350.INSL.NCER | 2024-03-13 | 2024-03-12 | 2024-08-26 | On-Time |  | 2025-03-12 | 2025-03-12 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35544157 | T2 DI WEST PT VLY SPRNGS 14/174 RPL INSW | 93I
LC | 128282640 | 033/004 | T2 EI COAL #1-SAN MIGUEL 33/4 RPL INSS | PISMOBCH | ETL.8580.INSL.CERA | 2024-03-13 | 2024-03-12 | 2024-10-16 | On-Time |  | 2025-03-12 | 2025-03-12 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35585462 | T2 EI COALNGA #1-SAN MIGEL 31/0 RPL INSS | 93K
LC | 128283251 | 029/008 | T2 DI GOLD HILL #1 29/8 RPL POLE | VICTOR | ETL.6950.POLE.WOOD | 2024-03-13 | 2024-03-12 | 2025-04-11 | Past Due |  | 2025-03-12 | 2025-03-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573262 | T2 DI GOLD HILL #1 29/8 RPL POLE | 70Y
LC | 128283319 | 029/016 | T2 DI GOLD HILL #1 29/16 RPR CNDW | VICTOR | ETL.6950.INSL.NCER | 2024-03-13 | 2024-03-12 | 2025-01-28 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46343529 | T2 DI GOLD HILL #1 29/16 RPR CNDW | ICW
LC | 128283532 | 028/002 | T2 DI GOLD HILL #1 28/2 RPR CNDW | VICTOR | ETL.6950.INSL.CERA | 2024-03-13 | 2024-03-12 | 2025-01-24 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46343530 | T2 DI GOLD HILL #1 28/2 RPR CNDW | ICW
LC | 128283614 | 028/003 | T2 DI GOLD HILL #1 28/3 RPL POLE | VICTOR | ETL.6950.POLE.WOOD | 2024-03-13 | 2024-03-12 | 2025-04-10 | Past Due |  | 2025-03-12 | 2025-03-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573238 | T2 DI GOLD HILL #1 28/3 RPL POLE | 70Y
LC | 128283618 | 029/011 | T2 DI GOLD HILL #1 29/11 RPR STRW | VICTOR | ETL.6950.POLE.WOOD | 2024-03-13 | 2024-03-12 | 2025-01-28 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46298637 | T2 DI GOLD HILL #1 29/11 RPR STRW | ICW
LC | 128283714 | 027/009 | T2 DI GOLD HILL #1 27/9 RPL POLE | VICTOR | ETL.6950.POLE.WOOD | 2024-03-13 | 2024-03-12 | 2025-04-09 | Past Due |  | 2025-03-12 | 2025-03-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Rotten | Structure-Wood | Replace | 35573234 | T2 DI GOLD HILL #1 27/9 RPL POLE | 70Y
LC | 128283896 | 013/163A | T2 DI WEST PT-VLY SPRNG 13/163A RPR INSW | VICTOR | ETL.8350.INSL.NCER | 2024-03-13 | 2024-03-12 | 2024-08-26 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46227586 | T2 DI WEST PT-VLY SPRNG 13/163A RPR INSW | ICW
LC | 128284513 | 005/068 | T2 DI WEST PT-VLY SPRNG 5/68 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-03-13 | 2024-03-12 | 2024-07-17 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46266193 | T2 DI WEST PT-VLY SPRNG 5/68 RPR GYWW | ICW
LC | 128286720 | 014/181 | T2 DI WEST PT VLY SPRNGS 14/181 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2025-01-23 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327517 | T2 DI WEST PT VLY SPRNGS 14/181 RPR GYWW | ICW
LC | 128286726 | 015/198 | T2 DI WEST PT VLY SPRNGS 5/198 REGRADE | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2025-01-29 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46326955 | T2 DI WEST PT VLY SPRNGS 5/198 REGRADE | ICW
LC | 128287022 | 006/078 | T2 DI WEST PT VLY SPRNGS 6/78 RPR POLE | VICTOR | ETL.8350.POLE.WOOD | 2024-03-14 | 2024-03-12 | 2024-08-20 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46227587 | T2 DI WEST PT VLY SPRNGS 6/78 RPR POLE | ICW
LC | 128287024 | 006/078 | T2 DI WEST PT VLY SPRNGS 6/78 GO95 | VICTOR | ETL.8350.POLE.WOOD | 2024-03-14 | 2024-03-12 | 2024-08-20 | On-Time |  | 2025-03-12 | 2025-03-12 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35571167 | T2 DI WEST PT VLY SPRNGS 6/78 GO95 | 93G
LC | 128287027 | 016/207 | T2 DI WEST PT VLY SPRNGS 16/207 RPL HRDD | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2024-08-27 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46227589 | T2 DI WEST PT VLY SPRNGS 16/207 RPL HRDD | ICW
LC | 128287028 | 016/207 | T2 DI WEST PT VLY SPRNGS 16/207 RPR INSW | VICTOR | ETL.8350.INSL.NCER | 2024-03-14 | 2024-03-12 | 2024-08-27 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46227705 | T2 DI WEST PT VLY SPRNGS 16/207 RPR INSW | ICW
LC | 128287085 | 006/079 | T2 DI WEST PT VLY SPRNGS 6/79 RPR STRW | VICTOR | ETL.8350.POLE.WOOD | 2024-03-14 | 2024-03-12 | 2024-08-20 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46227706 | T2 DI WEST PT VLY SPRNGS 6/79 RPR STRW | ICW
LC | 128287088 | 016/213 | T2 WEST PT VLY SPRNGS 16/213 RPR STRW | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2024-03-12 | Past Due |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46477454 | T2 DI WEST PT VLY SPRNGS 16/213 TOUCH | ICW
LC | 128287221 | 016/216 | T2 DI WEST PT VLY SPRNGS 16/216 RPL HRDD | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2025-01-24 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46327613 | T2 DI WEST PT VLY SPRNGS 16/216 RPL HRDD | ICW
LC | 128287613 | 006/077 | T2 DI WEST PT VLY SPRNGS 6/77 RPL POLE | VICTOR | ETL.8350.POLE.WOOD | 2024-03-14 | 2024-03-12 | 2024-08-20 | On-Time |  | 2025-03-12 | 2025-03-12 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35544156 | T2 DI WEST PT VLY SPRNGS 6/75 RPL POLE | 70Y
LC | 128287843 | 013/169 | T2 DI WEST PT VLY SPRNGS 13/169 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2024-08-27 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46227707 | T2 DI WEST PT VLY SPRNGS 13/169 RPR GYWW | ICW
LC | 128288099 | 007/085 | T2 DI WEST PT VLY SPRNGS 7/85 RPL POLE | VICTOR | ETL.8350.POLE.WOOD | 2024-03-14 | 2024-03-12 | 2024-08-23 | On-Time |  | 2025-03-12 | 2025-03-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35545131 | T2 DI WEST PT VLY SPRNGS 7/85 RPL POLE | 70Y
LC | 128288183 | 012/150 | T2 DI WEST PT VLY SPRNGS 12/150 RPR INSW | VICTOR | ETL.8350.INSL.NCER | 2024-03-14 | 2024-03-12 | 2024-08-25 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46229380 | T2 DI WEST PT VLY SPRNGS 12/150 RPR INSW | ICW
LC | 128288187 | 016/214 | T2 DI WEST PT VLY SPRNGS 16/214 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2024-08-27 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46227672 | T2 DI WEST PT VLY SPRNGS 16/214 RPR GYWW | ICW
LC | 128288188 | 016/214 | T2 DI WEST PT VLY SPRNGS 16/214 RPL INSW | VICTOR | ETL.8350.INSL.NCER | 2024-03-14 | 2024-03-12 | 2024-08-27 | On-Time |  | 2024-09-12 | 2025-03-12 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35545133 | T2 DI WEST PT VLY SPRNGS 16/214 RPL INSW | 93I
LC | 128288360 | 015/186 | T2 DI WEST PT VLY SPRNGS 15/186 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2024-08-27 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46219980 | T2 DI WEST PT VLY SPRNGS 15/186 RPR GYWW | ICW
LC | 128288926 | 016/212 | T2 DI WEST PT VLY SPRNGS 16/212 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2025-01-29 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46326956 | T2 DI WEST PT VLY SPRNGS 16/212 RPR GYWW | ICW
LC | 128289450 | 006/075 | T2 DI WEST PT VLY SPRNGS 6/75 RPL POLE | VICTOR | ETL.8350.POLE.WOOD | 2024-03-14 | 2024-03-12 | 2024-08-20 | On-Time |  | 2025-03-12 | 2025-03-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35544156 | T2 DI WEST PT VLY SPRNGS 6/75 RPL POLE | 70Y
LC | 128290054 | 011/142 | T2 DI WST PT VLY SPRGS 11/142 TOUCH | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2024-03-12 | Past Due |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46477455 | T2 DI WST PT VLY SPRGS 11/142 TOUCH | ICW
LC | 128290145 | 009/108 | T2 DI WST PT VLY SPRNGS 9/108 RPL POLE | VICTOR | ETL.8350.POLE.WOOD | 2024-03-14 | 2024-03-12 | 2024-08-21 | On-Time |  | 2024-09-12 | 2025-03-12 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35539027 | T2 DI WST PT VLY SPRNGS 9/108 RPL POLE | 70Y
LC | 128290303 | 009/081 | T2 DI PARADISE-TBL MTN 9/81 RPR JUMS | TABLEMTN | ETL.4316.INSL.NCER | 2024-03-14 | 2024-03-12 | 2024-12-18 | On-Time |  | 2025-03-12 | 2025-03-12 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46311121 | T2 DI PARADISE-TBL MTN 9/81 RPR JUMS | ICS
LC | 128290304 | 009/081 | T2 DI PARADISE-TBL MTN 9/81 RPR INSS | TABLEMTN | ETL.4316.INSL.NCER | 2024-03-14 | 2024-03-12 | 2024-05-18 | On-Time |  | 2024-09-13 | 2025-03-12 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46217443 | T2 DI PARADISE-TBL MTN 9/81 RPR INSS | ICS
LC | 128290378 | 008/096 | T2 DI WST PNT-VLY SPRNGS- 08/96 RPR POLE | VICTOR | ETL.8350.POLE.WOOD | 2024-03-14 | 2024-03-12 | 2024-08-21 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46229381 | T2 DI WST PNT-VLY SPRNGS- 08/96 RPR POLE | ICW
LC | 128290379 | 008/096 | T2 DI WST PNT-VLY SPRNGS- 08/96 RPL HRDD | VICTOR | ETL.8350.POLE.WOOD | 2024-03-14 | 2024-03-12 | 2024-08-21 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46229382 | T2 DI WST PNT-VLY SPRNGS- 08/96 RPL HRDD | ICW
LC | 128290450 | 020/160 | DI T2 PARADISE-TBL MTN 20/160 RPL INSW | TABLEMTN | ETL.4316.INSL.NCER | 2024-03-14 | 2024-03-12 | 2025-02-11 | On-Time |  | 2025-03-12 | 2025-03-12 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574023 | DI T2 PARADISE-TBL MTN 20/160 RPL INSW | 93I
LC | 128290459 | 006/054 | T2 DI PARADISE-TBL MTN 6/54 BNT STEEL | TABLEMTN | ETL.4316.TOWR | 2024-03-14 | 2024-03-12 | 2025-03-07 | On-Time |  | 2025-03-12 | 2025-03-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46311010 | T2 DI PARADISE-TBL MTN 6/54 BNT STEEL | ICQ
LC | 128290520 | 023/181 | T2 DI PRD-TBL MTN 23/181L RMV VEG | TABLEMTN | ETL.4316.POLE.STPS | 2024-03-14 | 2024-03-12 | 2024-05-07 | On-Time |  | 2024-09-12 | 2025-03-12 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128290561 | 013/165 | T2 DI WST PT-VLLY SPRNGS 13/165 RPL HRDW | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2024-08-26 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46229384 | T2 DI WST PT-VLLY SPRNGS 13/165 RPL HRDW | ICW
LC | 128290576 | 006/055BC | T2 DI PARADISE-TBL MTN 06/55BC RPR GYWW | TABLEMTN | ETL.4316.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2025-01-07 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310852 | T2 DI PARADISE-TBL MTN 06/55BC RPR GYWW | ICW
LC | 128290620 | 006/056 | DI T2 PARADISE-TBL MTN 6/56 RPL HRDT | TABLEMTN | ETL.4316.TOWR | 2024-03-14 | 2024-03-12 | 2025-02-04 | On-Time |  | 2025-03-12 | 2025-03-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46311012 | DI T2 PARADISE-TBL MTN 6/56 RPL HRDT | ICQ
LC | 128290621 | 006/056 | T2 DI PARADISE-TABLE MTN 6/56 RPR STRT | TABLEMTN | ETL.4316.TOWR | 2024-03-14 | 2024-03-12 | 2025-03-11 | On-Time |  | 2025-03-12 | 2025-03-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46311013 | T2 DI PARADISE-TABLE MTN 6/56 RPR STRT | ICQ
LC | 128291023 | 006/055BB | T2 DI PARADISE-TBL MTN 06/55BB COTTER | TABLEMTN | ETL.4316.INSL.NCER | 2024-03-14 | 2024-03-12 | 2025-01-07 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310856 | T2 DI PARADISE-TBL MTN 06/55BB COTTER | ICW
LC | 128291057 | 006/055 | T2 DI PARADISE-TBL MTN 6/55 INS HRDT | TABLEMTN | ETL.4316.TOWR | 2024-03-14 | 2024-03-12 | 2025-02-04 | On-Time |  | 2025-03-12 | 2025-03-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Missing | Hardware-Tower | Install | 46311014 | T2 DI PARADISE-TBL MTN 6/55 INS HRDT | ICQ
LC | 128291113 | 012/158 | T2 DI WST PT-VLLY SPRNGS 12/158 RPR STRW | VICTOR | ETL.8350.POLE.WOOD | 2024-03-14 | 2024-03-12 | 2024-08-24 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46229385 | T2 DI WST PT-VLLY SPRNGS 12/158 RPR STRW | ICW
LC | 128291151 | 007/088 | T2 DI WST PT-VLLY SPRNGS 7/088 RPL POLE | VICTOR | ETL.8350.POLE.WOOD | 2024-03-14 | 2024-03-12 | 2024-08-21 | On-Time |  | 2025-03-12 | 2025-03-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35545131 | T2 DI WEST PT VLY SPRNGS 7/85 RPL POLE | 70Y
LC | 128291155 | 013/162 | T2 DI WST PT-VLLY SPRNGS 13/162 RPR INSW | VICTOR | ETL.8350.INSL.NCER | 2024-03-14 | 2024-03-12 | 2024-08-26 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46247643 | T2 DI WST PT-VLLY SPRNGS 13/162 RPR INSW | ICW
LC | 128291156 | 012/151 | T2 DI WT PT-VLLY SPRGS 12/151 TOUCH | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2024-03-12 | Past Due |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46477456 | T2 DI WT PT-VLLY SPRGS 12/151 TOUCH | ICW
LC | 128291158 | 012/160 | T2 DI WST PT-VLLY SPRNGS 12/160 RPR STRW | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2025-01-23 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46327518 | T2 DI WST PT-VLLY SPRNGS 12/160 RPR STRW | ICW
LC | 128291187 | 006/055CC | T2 DI PRADIS-TBL MTN 06/55CC RPR ANCW | TABLEMTN | ETL.4316.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2024-05-18 | On-Time |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46217446 | T2 DI PRADIS-TBL MTN 06/55CC RPR ANCW | ICW
LC | 128291191 | 005/044 | T2 DI PARADISE-TBL MTN 5/44 TOUCH | TABLEMTN | ETL.4316.TOWR | 2024-03-14 | 2024-03-12 | 2024-03-12 | Past Due |  | 2024-09-12 | 2025-03-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478116 | T2 DI PARADISE-TBL MTN 5/44 TOUCH | ICQ
LC | 128291220 | 012/157 | T2 DI WST PT-VLLY SPRNGS 12/157 RPR INSW | VICTOR | ETL.8350.INSL.NCER | 2024-03-14 | 2024-03-12 | 2024-08-24 | On-Time |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46219981 | T2 DI WST PT-VLLY SPRNGS 12/157 RPR INSW | ICW
LC | 128291223 | 015/196 | T2 DI WST PT-VLLY SPRNGS 15/196 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2024-08-26 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46219983 | T2 DI WST PT-VLLY SPRNGS 15/196 RPR ANCW | ICW
LC | 128291225 | 014/179 | T2 DI WST PT-VLY SPRGS 14/179 TOUCH | VICTOR | ETL.8350.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2024-03-12 | Past Due |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46477457 | T2 DI WST PT-VLY SPRGS 14/179 TOUCH | ICW
LC | 128291264 | 006/055CA | T2 DI PRADIS-TBL MTN 6/55CA RPR ANCW | TABLEMTN | ETL.4316.POLE.NWOD | 2024-03-14 | 2024-03-12 | 2024-05-18 | On-Time |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46217445 | T2 DI PRADIS-TBL MTN 6/55CA RPR ANCW | ICW
LC | 128291292 | 006/052 | T2 DI PARADISE-TABLE MTN 6/052 RPR INSS | TABLEMTN | ETL.4316.INSL.NCER | 2024-03-14 | 2024-03-12 | 2025-02-11 | On-Time |  | 2025-03-12 | 2025-03-12 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46311122 | T2 DI PARADISE-TABLE MTN 6/052 RPR INSS | ICS
LC | 128291293 | 005/047 | T2 DI PARADISE-TABLE MTN 5/047 RPR STRT | TABLEMTN | ETL.4316.TOWR | 2024-03-14 | 2024-03-12 | 2025-03-03 | On-Time |  | 2025-03-12 | 2025-03-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46311017 | T2 DI PARADISE-TABLE MTN 5/047 RPR STRT | ICQ
LC | 128291294 | 005/047 | T2 DI PARADISE-TABLE MTN 5/047 RPR FOND | TABLEMTN | ETL.4316.TOWR | 2024-03-14 | 2024-03-12 | 2025-03-03 | On-Time |  | 2025-03-12 | 2025-03-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46311018 | T2 DI PARADISE-TABLE MTN 5/047 RPR FOND | ICQ
LC | 128291299 | 012/156 | T2 DI WST PT-VLLY SPRNGS 12/156 COMPLETE | VICTOR | ETL.8350.INSL.NCER | 2024-03-14 | 2024-03-12 | 2024-08-25 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46229387 | T2 DI WST PT-VLLY SPRNGS 12/156 COTTER | ICW
LC | 128291311 | ;010/092 | T2 DI PARADISE-TBL MTN ;10/92 RPL HRDT | TABLEMTN | ETL.4316.TOWR | 2024-03-14 | 2024-03-12 | 2025-01-29 | On-Time |  | 2025-03-12 | 2025-03-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46311019 | T2 DI PARADISE-TBL MTN ;10/92 RPL HRDT | ICQ
LC | 128291340 | 006/058 | T2 DI PARDIS-TABLE MTN 6/058 TOUCH | TABLEMTN | ETL.4316.TOWR | 2024-03-14 | 2024-03-12 | 2024-03-12 | Past Due |  | 2024-09-12 | 2025-03-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46477848 | T2 DI PARDIS-TABLE MTN 6/058 TOUCH | ICQ
LC | 128291341 | 006/058 | T2 DI PARADISE-TABLE MTN 6/058 RPR STRT | TABLEMTN | ETL.4316.TOWR | 2024-03-14 | 2024-03-12 | 2025-03-06 | On-Time |  | 2025-03-12 | 2025-03-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46311040 | T2 DI PARADISE-TABLE MTN 6/058 RPR STRT | ICQ
LC | 128292835 | 020/161 | T2 DI PARADISE-TABLE MTN 20/161 RPR GYWW | TABLEMTN | ETL.4316.POLE.STPS | 2024-03-15 | 2024-03-12 | 2025-01-07 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310850 | T2 DI PARADISE-TABLE MTN 20/161 RPR GYWW | ICW
LC | 128292839 | 020/165 | T2 DI PARADISE-TBL MTN 20/165C RPR ANCW | TABLEMTN | ETL.4316.POLE.STPS | 2024-03-15 | 2024-03-12 | 2024-05-17 | On-Time |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46217448 | T2 DI PARADISE-TBL MTN 20/165C RPR ANCW | ICW
LC | 128292840 | 020/165 | T2 DI PARADISE-TBL MTN 20/165L RPR ANCW | TABLEMTN | ETL.4316.POLE.STPS | 2024-03-15 | 2024-03-12 | 2024-05-17 | On-Time |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46217449 | T2 DI PARADISE-TBL MTN 20/165L RPR ANCW | ICW
LC | 128292841 | 020/165 | T2 DI PARADISE-TBL MTN 20/165R RPR ANCW | TABLEMTN | ETL.4316.POLE.STPS | 2024-03-15 | 2024-03-12 | 2024-05-17 | On-Time |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46217450 | T2 DI PARADISE-TBL MTN 20/165R RPR ANCW | ICW
LC | 128292952 | 025/196 | T2 DI PARADISE-TBL MT 25/196 RPR INSW | TABLEMTN | ETL.4316.INSL.NCER | 2024-03-15 | 2024-03-12 | 2025-02-11 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310847 | T2 DI PARADISE-TBL MT 25/196 RPR INSW | ICW
LC | 128292956 | 025/196 | T2 DI PARADISE-TBL MT 25/196L RPR ANCW | TABLEMTN | ETL.4316.POLE.STPS | 2024-03-15 | 2024-03-12 | 2024-05-15 | On-Time |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46217456 | T2 DI PARADISE-TBL MT 25/196L RPR ANCW | ICW
LC | 128292957 | 025/196 | T2 DI PARADISE-TBL MT 25/196C RPR ANCW | TABLEMTN | ETL.4316.POLE.STPS | 2024-03-15 | 2024-03-12 | 2024-05-15 | On-Time |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46217457 | T2 DI PARADISE-TBL MT 25/196C RPR ANCW | ICW
LC | 128292958 | 025/196 | T2 DI PARADISE-TBL MT 25/196R RPR ANCW | TABLEMTN | ETL.4316.POLE.STPS | 2024-03-15 | 2024-03-12 | 2024-05-15 | On-Time |  | 2024-09-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46217458 | T2 DI PARADISE-TBL MT 25/196R RPR ANCW | ICW
LC | 128293142 | 012/106 | T2 DI PARADISE-TBL MTN 12/106 RPR STRT | TABLEMTN | ETL.4316.TOWR | 2024-03-15 | 2024-03-12 | 2025-03-06 | On-Time |  | 2025-03-12 | 2025-03-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46311041 | T2 DI PARADISE-TBL MTN 12/106 RPR STRT | ICQ
LC | 128293179 | 008/074 | T2 DI PARADISE-TBL MT 8/74 BNT STEEL | TABLEMTN | ETL.4316.TOWR | 2024-03-15 | 2024-03-12 | 2025-02-05 | On-Time |  | 2025-03-12 | 2025-03-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46311042 | T2 DI PARADISE-TBL MT 8/74 BNT STEEL | ICQ
LC | 128293386 | 024/184 | T2 DI PARADISE-TBL MT 24/184L RPL STRW | TABLEMTN | ETL.4316.POLE.WDPS | 2024-03-15 | 2024-03-12 | 2025-02-11 | On-Time |  | 2025-03-12 | 2025-03-12 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574024 | T2 DI PARADISE-TBL MT 24/184R RPL STRW | 70Y
LC | 128293389 | 024/184 | T2 DI PARADISE-TBL MT 24/184R RPL STRW | TABLEMTN | ETL.4316.POLE.WDPS | 2024-03-15 | 2024-03-12 | 2025-02-11 | On-Time |  | 2025-03-12 | 2025-03-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574024 | T2 DI PARADISE-TBL MT 24/184R RPL STRW | 70Y
LC | 128301738 | 005/066 | T2 DI WEST PT-VLY SPRNGS 5/66 RPR SWTC | VICTOR | ETL.8350.POLE.WOOD | 2024-03-18 | 2024-03-12 | 2024-08-19 | On-Time |  | 2025-03-12 | 2025-03-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Switch-Wood | Repair | 46229388 | T2 DI WEST PT-VLY SPRNGS 5/66 RPR SWTCH | ICW
LC | 129522603 | 006/037 | T3 SBRNT-GRZLY-CLEMNT #2 6/37 RPR FOND | CONCORD | ETL.3750.TOWR | 2024-09-12 | 2024-09-12 | 2024-09-12 | On-Time |  | 2024-12-12 | 2025-03-12 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3 FRAB DURA BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46321015 | T3 SBRNT-GRZLY-CLEMNT #2 6/37 RPR FOND | ICQ
LC | 130833278 | 006/052 | T2 DI PARADISE-TABLE MTN 6/52 HANGER | TABLEMTN | ETL.4316.INSL.NCER | 2025-02-07 | 2024-03-12 | 2025-05-03 | Past Due |  | 2025-03-12 | 2025-03-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46472289 | T2 DI PARADISE-TABLE MTN 6/52 HANGER | ICQ
LC | 128280934 | 001/013 | T2 GRANITE ROCK TAP 1/013 RPL IBWW | MOSSLNDG | ETL.8311.INSL.CERA | 2024-03-13 | 2024-03-13 | 2025-03-08 | On-Time |  | 2025-03-13 | 2025-03-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46305519 | T2 GRANITE ROCK TAP 1/013 RPL IBWW | ICW
LC | 128281227 | 013/070 | T2 EI TESLA-NEWARK #1 13/70 RPR OPGW | CONCORD | ETL.5720.TOWR | 2024-03-13 | 2024-03-13 | 2024-05-11 | On-Time |  | 2024-06-13 | 2025-03-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46220593 | T2 EI TESLA-NEWARK #1 13/70 RPR OPGW | ICS
LC | 128281334 | 008/001 | T2 EI PTTR VLLY-MENDOCINO 8/1 RMV NEST | WILLITS | ETL.7810.POLE.NWOD | 2024-03-13 | 2024-03-13 | 2025-03-11 | On-Time |  | 2025-03-13 | 2025-03-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46403730 | T2 EI PTTR VLLY-MENDOCINO 8/1 RMV NEST | ICS
LC | 128281409 | 008/001 | T2 EI PTTR VLLY-MENDOCINO 8/1 RPR INSS | WILLITS | ETL.7810.INSL.NCER | 2024-03-13 | 2024-03-13 | 2024-04-04 | On-Time |  | 2024-06-13 | 2025-03-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46220208 | T2 EI PTTR VLLY-MENDOCINO 8/1 RPR INSS | ICS
LC | 128281760 | 000/015 | T2 EI CTNWD-PANORAMA 0/15 RPL STRW | TABLEMTN | ETL.1340.POLE.WOOD | 2024-03-13 | 2024-03-13 | 2025-03-13 | On-Time |  | 2025-03-13 | 2025-03-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557667 | T2 EI CTNWD-PANORAMA 0/15 RPL STRW | 70Y
LC | 128281786 | 004/084 | T2 EI TEMPLETON-ATASCADERO 4/84 RPR POLE | PISMOBCH | ETL.9410.POLE.WOOD | 2024-03-13 | 2024-03-13 | 2025-04-03 | Past Due |  | 2025-03-13 | 2025-03-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46329657 | T2 EI TEMPLETON-ATASCADERO 4/84 RPR WDPK | ICW
LC | 128282117 | 012/269 | T2 SALINAS-LAURELES 12/269 CNCL | MOSSLNDG | ETL.7930.POLE.WOOD | 2024-03-13 | 2024-03-13 | 2024-03-13 | Past Due |  | 2025-03-13 | 2025-03-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46329990 | T2 WV SALINAS-LAURELES 12/269 RPL HRDW | ICW
LC | 128282149 | 006/035A | T2 EI JFFERSN-HLSDLE JCT 6/35A RPL ANCW | METCALF | ETL.7190.POLE.WOOD | 2024-03-13 | 2024-03-13 | 2025-02-27 | On-Time |  | 2025-03-13 | 2025-03-13 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAR | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573576 | T2 EI JFFERSN-HLSDLE JCT 6/35A RPL ANCW | 93E
LC | 128282275 | 008/002 | T2 EI PTTR VLLY-MENDOCINO 8/2 RMV NEST | WILLITS | ETL.7810.POLE.NWOD | 2024-03-13 | 2024-03-13 | 2025-03-11 | On-Time |  | 2025-03-13 | 2025-03-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46403731 | T2 EI PTTR VLLY-MENDOCINO 8/2 RMV NEST | ICS
LC | 128282309 | 012/071 | T2 CHRISTIE-SOBRANTE - 115 kV_012/071 | CONCORD | ETL.1260.TOWR | 2024-03-13 | 2024-03-13 | 2024-03-13 | On-Time |  | 2025-03-13 | 2025-03-13 | 539 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH FMOB TR2 PRTO FRAB | Investigate | Non-Routine Patrol | Ground Patrol | 46211362 | T2 CHRISTIE-SOBRANTE - 115 KV_012/071 | BFY
LC | 128282905 | 000/018 | T2 EI PALERMO-OROVILLE #1 00/18 RPR INSW | TABLEMTN | ETL.7730.INSL.NCER | 2024-03-13 | 2024-03-13 | 2025-01-11 | On-Time |  | 2025-03-13 | 2025-03-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD SWRK CLR ACCH COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46332419 | T2 EI PALERMO-OROVILLE #1 00/18 RPR INSW | ICW
LC | 128283042 | 000/017 | T2 EI PALERMO-OROVILLE #1 00/17 RPR STRW | TABLEMTN | ETL.7730.POLE.WOOD | 2024-03-13 | 2024-03-13 | 2025-01-09 | On-Time |  | 2025-03-13 | 2025-03-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46345036 | T2 EI PALERMO-OROVILLE #1 00/17 RPR STRW | ICW
LC | 128283167 | 006/035C | T2 FFRSON-HLSDLE JCT 6/35C RPL STRW | METCALF | ETL.7190.POLE.WOOD | 2024-03-13 | 2024-03-13 | 2024-03-13 | Past Due |  | 2024-09-13 | 2025-03-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAR DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35573578 | T2 EI JEFFERSON-HLSDALE JCT 6/35C RPL PL | 70Y
LC | 128283327 | 005/028 | T2 EI DIABLO-GATES #1 005/028 RMV NEST | PISMOBCH | ETL.5960.TOWR | 2024-03-13 | 2024-03-13 | 2024-05-01 | On-Time |  | 2025-03-13 | 2025-03-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46236832 | T2 EI DIABLO-GATES #1 005/028 RMV NEST | ICS
LC | 128283362 | 005/088 | T2 EI TEMPLETON-ATASCADERO 5/88 RPL POLE | PISMOBCH | ETL.9410.POLE.WOOD | 2024-03-13 | 2024-03-13 | 2025-04-03 | Past Due |  | 2025-03-13 | 2025-03-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573700 | T2 EI TEMPLETON-ATASCADERO 5/88 RPL POLE | 70Y
LC | 128283748 | 002/016 | T2 EI HMBLDT-MAPLE CREEK 02/016 RPL INSW | EUREKA | ETL.7130.INSL.CERA | 2024-03-13 | 2024-03-13 | 2025-04-04 | Past Due |  | 2025-03-13 | 2025-03-13 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574619 | T2 EI HMBLDT-MAPLE CREEK 02/016 RPL INSW | 93I
LC | 128283826 | 007/003 | T2 EI PTTR VLLY-MENDOCINO 7/3 RMV NEST | WILLITS | ETL.7810.POLE.NWOD | 2024-03-13 | 2024-03-13 | 2025-03-11 | On-Time |  | 2025-03-13 | 2025-03-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46403729 | T2 EI PTTR VLLY-MENDOCINO 7/3 RMV NEST | ICS
LC | 128283850 | 007/003 | T2 EI PTTR VLLY-MENDOCINO 7/3 UNBURRY | WILLITS | ETL.7810.POLE.NWOD | 2024-03-13 | 2024-03-13 | 2025-03-13 | On-Time |  | 2025-03-13 | 2025-03-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46290105 | T2 EI PTTR VLLY-MENDOCINO 7/3 UNBURRY | ICQ
LC | 128283940 | 007/002 | T2 EI PTTR VLLY-MENDOCINO 7/2 RPL HRDT | WILLITS | ETL.7810.POLE.NWOD | 2024-03-13 | 2024-03-13 | 2025-03-13 | On-Time |  | 2025-03-13 | 2025-03-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46290104 | T2 EI PTTR VLLY-MENDOCINO 7/2 RPL HRDT | ICQ
LC | 128283942 | 007/002 | T2 EI PTTR VLLY-MENDOCINO 7/2 REGRADE | WILLITS | ETL.7810.POLE.NWOD | 2024-03-13 | 2024-03-13 | 2025-03-13 | On-Time |  | 2025-03-13 | 2025-03-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46290103 | T2 EI PTTR VLLY-MENDOCINO 7/2 REGRADE | ICQ
LC | 128284133 | 004/088 | T2 EI WEIMAR-HALSEY 4/088 COTTER | SACTO | ETL.8340.INSL.NCER | 2024-03-13 | 2024-03-13 | 2025-01-14 | On-Time |  | 2025-03-13 | 2025-03-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46323933 | T2 EI WEIMAR-HALSEY 4/088 COTTER | ICW
LC | 128284212 | 003/083 | T2 EI PLACER-DEL MAR 003/083 RMV VEG | SACTO | ETL.7800.POLE.WOOD | 2024-03-13 | 2024-03-13 | 2025-05-16 | Past Due |  | 2025-03-13 | 2025-03-13 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP WATR CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128284318 | 051/207A | T2 DIABLO-GATES #1 51/207A COMPLETE | PISMOBCH | ETL.5960.TOWR | 2024-03-13 | 2024-03-13 | 2024-05-08 | On-Time |  | 2025-03-13 | 2025-03-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46211464 | T2 DIABLO-GATES #1 51/207A RPR GYWT | ICQ
LC | 128284392 | 004/087 | T2 EI WEIMAR-HALSEY 4/087 RPR POLE | SACTO | ETL.8340.POLE.WOOD | 2024-03-13 | 2024-03-13 | 2025-01-10 | On-Time |  | 2025-03-13 | 2025-03-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46323916 | T2 EI WEIMAR-HALSEY 4/087 RPR POLE | ICW
LC | 128284394 | 011/013 | T2 EI PTTR VLLY-WILLITS 11/013 RPL POLE | WILLITS | ETL.7820.POLE.WOOD | 2024-03-13 | 2024-03-13 | 2025-02-19 | On-Time |  | 2025-03-13 | 2025-03-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573220 | T2 EI PTTR VLLY-WILLITS 11/013 RPL POLE | 70Y
LC | 128284781 | 011/012 | T2 EI PTTR VLLY-WILLITS 11/012 RPL POLE | WILLITS | ETL.7820.POLE.WOOD | 2024-03-13 | 2024-03-13 | 2025-02-19 | On-Time |  | 2025-03-13 | 2025-03-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573199 | T2 EI PTTR VLLY-WILLITS 11/012 RPL POLE | 70Y
LC | 128284823 | 003/082 | T2 EI PLACER-DEL MAR 03/82 RPR INSW | SACTO | ETL.7800.INSL.CERA | 2024-03-13 | 2024-03-13 | 2025-02-18 | On-Time |  | 2025-03-13 | 2025-03-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP TRAF CLR ACCM FLAG COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46323917 | T2 EI PLACER-DEL MAR 03/82 RPR INSW | ICW
LC | 128284826 | 057/280 | T2 EI CRTNA-MNDCNO #1 57/280 RMV VEG | WILLITS | ETL.1330.TOWR | 2024-03-13 | 2024-03-13 | 2024-03-13 | On-Time |  | 2025-03-13 | 2025-03-13 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128284919 | 030/008 | T2 WV GOLD HILL #1_030/008 RPR IBWW | VICTOR | ETL.6950.INSL.NCER | 2024-03-13 | 2024-03-13 | 2025-04-12 | Past Due |  | 2025-03-13 | 2025-03-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46326954 | T2 WV GOLD HILL #1_030/008 RPR IBWW | ICW
LC | 128284927 | 003/083 | T2 EI WEIMAR-HALSEY 3/083 RMV VEG | SACTO | ETL.8340.POLE.NWOD | 2024-03-13 | 2024-03-13 | 2025-04-22 | Past Due |  | 2025-03-13 | 2025-03-13 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128285058 | 001/019 | T2 EI SMARTVLE-NICOLAUS #1 1/19 RPR POLE | SACTO | ETL.7990.POLE.WOOD | 2024-03-13 | 2024-03-13 | 2025-02-12 | On-Time |  | 2025-03-13 | 2025-03-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310258 | T2 EI SMARTVLE-NICOLAUS #1 1/1 RPR POLE | ICW
LC | 128285242 | 006/055D | T2 WV PARADISE-TABLE MTN 6/55D RPR POLE | TABLEMTN | ETL.4316.POLE.NWOD | 2024-03-13 | 2024-03-13 | 2025-01-07 | On-Time |  | 2024-09-13 | 2025-03-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46250588 | T2 WV PARADISE-TABLE MTN 6/55D RPR POLE | ICW
LC | 128285366 | 003/084 | T2 EI COLGATE-GRAS VALLEY 3/084 RPR CNDW | SACTO | ETL.6490.INSL.NCER | 2024-03-13 | 2024-03-13 | 2025-03-01 | On-Time |  | 2025-03-13 | 2025-03-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Conductor-Wood | Repair | 46383043 | T2 EI COLGATE-GRAS VALLEY 3/084 RPR CNDW | ICW
LC | 128286480 | 028/114 | T2 EI DIABLO-MIDWAY #3 28/114 RPR ROAD | PISMOBCH | ETL.5980.TOWR | 2024-03-14 | 2024-03-13 | 2024-03-13 | Past Due |  | 2025-03-13 | 2025-03-13 | 932 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Road | Repair | 45192143 | T3NT DIABLO-MIDWAY #3 006/023 RPR ROAD | CHS
LC | 128290405 | 012/052 | T2 DI MRO BAY-SOLAR SS #1 12/52 TOUCH | PISMOBCH | ETL.5300.TOWR | 2024-03-14 | 2024-03-13 | 2025-03-12 | On-Time |  | 2024-09-13 | 2025-03-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476021 | T2 DI MRO BAY-SOLAR SS #1 12/52 TOUCH | ICQ
LC | 128290907 | 017/073 | T2 DI MORO BAY-SOLSWST #1 17/73 TOUCH | PISMOBCH | ETL.5300.TOWR | 2024-03-14 | 2024-03-13 | 2025-03-12 | On-Time |  | 2024-09-13 | 2025-03-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476022 | T2 DI MORO BAY-SOLSWST #1 17/73 TOUCH | ICQ
LC | 128291256 | 011/047 | T2 DI MR BY SLR SW ST#1 11/47 RPL HRDT | PISMOBCH | ETL.5300.TOWR | 2024-03-14 | 2024-03-13 | 2025-03-10 | On-Time |  | 2025-03-13 | 2025-03-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46400012 | T2 DI MR BY SLR SW ST#1 11/47 RPL HRDT | ICQ
LC | 128291258 | 030/132 | T2 DI MORR BY-SOLAR SW#1 30/132 TOUCH | PISMOBCH | ETL.5300.TOWR | 2024-03-14 | 2024-03-13 | 2025-03-13 | On-Time |  | 2024-09-13 | 2025-03-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476026 | T2 DI MORR BY-SOLAR SW#1 30/132 TOUCH | ICQ
LC | 128291259 | 017/075 | T2 DI MR BY SLR SW ST#1 17/75 RPR INSS | PISMOBCH | ETL.5300.INSL.NCER | 2024-03-14 | 2024-03-13 | 2024-10-19 | On-Time |  | 2024-09-13 | 2025-03-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46229511 | T2 DI MR BY SLR SW ST#1 17/75 RPR INSS | ICS
LC | 128291372 | 035/150 | T2 DI MRRO BY-SLR SW #1 35/150 RPR FOND | PISMOBCH | ETL.5300.TOWR | 2024-03-14 | 2024-03-13 | 2025-03-10 | On-Time |  | 2025-03-13 | 2025-03-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46400013 | T2 DI MRRO BY-SLR SW #1 35/150 RPR FOND | ICQ
LC | 128292863 | 017/074 | T2 DI MORO BY SLR SS #1 17/74 TOUCH | PISMOBCH | ETL.5300.TOWR | 2024-03-15 | 2024-03-13 | 2025-03-12 | On-Time |  | 2024-09-13 | 2025-03-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476024 | T2 DI MORO BY SLR SS #1 17/74 TOUCH | ICQ
LC | 128292877 | 017/076 | T2 DI MRRO BY-SLR SS #1 17/076 RPR INSS | PISMOBCH | ETL.5300.INSL.NCER | 2024-03-15 | 2024-03-13 | 2025-01-02 | On-Time |  | 2025-03-13 | 2025-03-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329541 | T2 DI MRRO BY-SLR SS #1 17/076 RPR INSS | ICS
LC | 128293075 | 007/031 | T2 DI MORRO BY-SLR SW S #1 7/31 RPL INSS | PISMOBCH | ETL.5300.INSL.NCER | 2024-03-15 | 2024-03-13 | 2025-04-10 | Past Due |  | 2025-03-13 | 2025-03-13 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35583345 | T0 EI MORRO BAY-SOLAR SS#1 REP INS 6 LST | 93K
LC | 128293076 | 007/031 | T2 DI MORRO BY-SLR SW S #2 7/31 RPL INSS | PISMOBCH | ETL.5310.INSL.NCER | 2024-03-15 | 2024-03-13 | 2024-03-13 | Past Due |  | 2025-03-13 | 2025-03-13 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577375 | T0 EI MORRO BAY-SOLAR SS#2 42/180 RPLC I | 93K
LC | 128296325 | 010/043 | T2 DI MORRO BAY-SOLAR #1 10/43 TOUCH | PISMOBCH | ETL.5300.TOWR | 2024-03-15 | 2024-03-13 | 2025-03-12 | On-Time |  | 2024-09-13 | 2025-03-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476025 | T2 DI MORRO BAY-SOLAR #1 10/43 TOUCH | ICQ
LC | 128296463 | 000/003A | T2 DI MORRO BAY-SLR #2 0/3A RPR ADSS | PISMOBCH | ETL.5310.POLE.NWOD | 2024-03-15 | 2024-03-13 | 2025-01-02 | On-Time |  | 2025-03-13 | 2025-03-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | ADSS - Steel | Repair | 46329549 | T2 DI MORRO BAY-SLR #2 0/3A RPR ADSS | ICS
LC | 128296464 | 036/155 | T2 DI MORRO BAY-SOLAR #1 36/155 RPR INSS | PISMOBCH | ETL.5300.INSL.NCER | 2024-03-15 | 2024-03-13 | 2025-01-02 | On-Time |  | 2025-03-13 | 2025-03-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329542 | T2 DI MORRO BAY-SOLAR #1 36/155 RPR INSS | ICS
LC | 128296505 | 003/043 | T2 DI PARADISE-TABLE 3/43 RPL INSS | TABLEMTN | ETL.4316.INSL.NCER | 2024-03-15 | 2024-03-13 | 2025-03-20 | Past Due |  | 2025-03-13 | 2025-03-13 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570814 | T2 DI PARADISE-TABLE MTN RPL INSS 4 TSP | 93K
LC | 128296508 | 018/077 | T2 DI MORRO BAY-SOLAR #1 18/77 TOUCH | PISMOBCH | ETL.5300.TOWR | 2024-03-15 | 2024-03-13 | 2025-03-11 | On-Time |  | 2024-09-13 | 2025-03-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476020 | T2 DI MORRO BAY-SOLAR #1 18/77 TOUCH | ICQ
LC | 128296547 | 002/035 | T2 DI PARADISE-BUTTE 2/35 RPL HRDS | TABLEMTN | ETL.4396.POLE.NWOD | 2024-03-15 | 2024-03-13 | 2025-03-10 | On-Time |  | 2025-03-13 | 2025-03-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Steel | Replace | 46300498 | T2 DI PARADISE-BUTTE 2/35 RPL HRDS | ICS
LC | 128296611 | 006/061 | T2 DI PARADISE-BUTTE 6/61 RPL INSS | TABLEMTN | ETL.4396.INSL.NCER | 2024-03-15 | 2024-03-13 | 2025-03-19 | Past Due |  | 2025-03-13 | 2025-03-13 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570812 | T0 DI PRDS PARADISE-BUTTE RPL INSS 5 TSP | 93K
LC | 128296648 | 002/027 | T2 EI GRANITE ROCK TAP 2/27 RPR GYWW | MOSSLNDG | ETL.8311.POLE.WOOD | 2024-03-15 | 2024-03-13 | 2025-03-08 | On-Time |  | 2025-03-13 | 2025-03-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305541 | T2 EI GRANITE ROCK TAP 2/27 RPR GYWW | ICW
LC | 128298378 | 001/023 | T2 DI PARADISE-TABLE MTN 1/23 RPL INSS | TABLEMTN | ETL.4316.INSL.NCER | 2024-03-18 | 2024-03-13 | 2025-02-10 | On-Time |  | 2025-03-13 | 2025-03-13 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570814 | T2 DI PARADISE-TABLE MTN RPL INSS 4 TSP | 93K
LC | 128303658 | 013/124 | T2 DI WOODLEAF-PALERMO 13/124 RPL INSW | TABLEMTN | ETL.4220.INSL.NCER | 2024-03-18 | 2024-03-13 | 2025-03-13 | On-Time |  | 2025-03-13 | 2025-03-13 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35571797 | T2 DI WOODLEAF-PALERMO 13/124 RPL INSW | 93I
LC | 128303928 | 018/195 | T2 DI WDLF PLRM 18/195 RPL INSW | TABLEMTN | ETL.4220.INSL.NCER | 2024-03-18 | 2024-03-13 | 2025-03-13 | On-Time |  | 2025-03-13 | 2025-03-13 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35571792 | T2 DI WDLF PLRM 18/195 RPL INSW | 93I
LC | 128337019 | 078/395C | T2 DI MALN RND MTN #2 78/395C RMV VEG | TABLEMTN | ETL.6020.TOWR | 2024-03-21 | 2024-03-13 | 2024-12-06 | On-Time |  | 2025-03-13 | 2025-03-13 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128337060 | 078/395C | T2 DI MALN RND MTN #2 78/395C UNBURY | TABLEMTN | ETL.6020.TOWR | 2024-03-21 | 2024-03-13 | 2025-02-10 | On-Time |  | 2025-03-13 | 2025-03-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381356 | T2 DI MALN RND MTN #2 78/395C UNBURY | ICQ
LC | 128337122 | 078/396 | T2 DI MLN RND MTN #2 78/396 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-03-21 | 2024-03-13 | 2025-02-08 | On-Time |  | 2025-03-13 | 2025-03-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332442 | T2 DI MLN RND MTN #2 78/396 RPR OPGW | ICS
LC | 128393132 | 078/398A | T2 DI MLN-RND MTN #2 78/398A CNCL | TABLEMTN | ETL.6020.TOWR | 2024-03-29 | 2024-03-13 | 2025-02-11 | On-Time |  | 2025-03-13 | 2025-03-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381358 | T2 DI MLN-RND MTN #2 78/398A RPR GYWT | ICQ
LC | 123097667 | 010/001 | T2NT DI MELONES-CURTIS 10/1 RPL INSW | VICTOR | ETL.2390.INSL.NCER | 2022-03-14 | 2022-03-14 | 2023-10-02 | On-Time |  | 2025-03-14 | 2025-03-14 | 508 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR NTDE | No Good/Out of Stdrd | Insulator-Wood | Replace | 31605029 | T2 DI MELONES-CURTIS 10/1 RPL INSW | 93I
LC | 123097956 | 003/019 | T2NT EI XCHQR-IDN FLT-YSMT 3/19 INS RPTS | FRESNO | ETL.8650.TOWR | 2022-03-14 | 2022-03-14 | 2023-06-20 | On-Time |  | 2025-03-14 | 2025-03-14 | 593 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 45647553 | T2 EI XCHQR-IDN FLT-YSMT 3/19 INS RPTS | ICB
LC | 123152465 | 003/028 | T2NT DI MORAGA-OAKLAND#2 3/28 RPL INSS | CONCORD | ETL.2730.INSL | 2022-03-18 | 2022-03-14 | 2023-04-19 | On-Time |  | 2025-03-14 | 2025-03-14 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 31620103 | DI MORAGA-OAKLAND#2 RPL INSS IN 3/28 | 93K
LC | 123156289 | 002/017 | T3NT DI MRGA-OKLAND #1 02/17 BNT STEEL | CONCORD | ETL.2720.TOWR | 2022-03-19 | 2022-03-14 | 2023-10-12 | On-Time |  | 2025-03-14 | 2025-03-14 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45617016 | T3 DI MORAGA-OAKLAND #1 02/17 BNT STEEL | ICQ
LC | 123162491 | 014/128 | T2NT DI BRIDGEVILL CTNWD 14/128 RPR ADSS | TABLEMTN | ETL.1110.POLE.WDPS | 2022-03-21 | 2022-03-14 | 2023-08-14 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45581881 | T2 DI BRDGVL CTNWD 14/128 RPR ADSS | ICW
LC | 123165418 | 011/256 | T2NT DI SNT RS CRN 11/256 RMV BUTT | LAKEVLLE | ETL.4309.POLE.WOOD | 2022-03-22 | 2022-03-14 | 2023-05-22 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE ACCL COMP OH TR2 PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 45575429 | T2NT DI SNT RS CRN 11/256 RMV BUTT | ICW
LC | 127055457 | 050/001 | T2 WV COTTONWD-HUMBLDT 50/01 INS DMPW | EUREKA | ETL.1820.INSL.NCER | 2023-09-14 | 2023-09-14 | 2025-04-07 | Past Due |  | 2025-03-14 | 2025-03-14 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB XMPT TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46203487 | T2 WV COTTONWD-HUMBLDT 50/01 INS DMPW | ICW
LC | 128286921 | 003/018A | T2 EI TRNITY-MAPLE CREK 03/018A RPL TIED | EUREKA | ETL.8170.INSL.CERA | 2024-03-14 | 2024-03-14 | 2025-03-25 | Past Due |  | 2024-09-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Tie Wire-Wood | Replace | 46345686 | T2 EI TRNITY-MAPLE CREK 03/018A RPL TIED | ICW
LC | 128287075 | 047/291 | T2 EI MADISON-VACA 47/291 RPR STRT | SACTO | ETL.2170.TOWR | 2024-03-14 | 2024-03-14 | 2024-12-17 | On-Time |  | 2025-03-14 | 2025-03-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46327681 | T2 EI MADISON-VACA 47/291 RPR STRT | ICQ
LC | 128287145 | 009/041 | T2 EI DIABLO-GATES #1 009/041 RPL INSS | PISMOBCH | ETL.5960.INSL | 2024-03-14 | 2024-03-14 | 2025-02-03 | On-Time |  | 2025-03-14 | 2025-03-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35585465 | T2 EI DIABLO-GATES #1 009/041 RPL INSS | 93K
LC | 128287246 | 025/405 | T2 KESWICK-TRINITY 025/405 GO95 | TABLEMTN | ETL.7270.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2025-04-17 | Past Due |  | 2025-03-14 | 2025-03-14 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR ACCM COMP OH TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35573702 | T2 KESWICK-TRINITY 025/405 GO95 | 93G
LC | 128287267 | 009/004 | T2 EI POTTER VALLEY-MNDOCINO 9/4 RMV VEG | WILLITS | ETL.7810.POLE.NWOD | 2024-03-14 | 2024-03-14 | 2025-01-29 | On-Time |  | 2025-03-14 | 2025-03-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128287270 | 005/091 | T2 EI TEMPLTON-ATASCADERO 05/091 RMV VEG | PISMOBCH | ETL.9410.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2025-02-17 | On-Time |  | 2025-03-14 | 2025-03-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128287327 | ;002/005 | T2 CARIBOU #2 ;002/005 RPL STRW | TABLEMTN | ETL.6280.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2025-03-04 | On-Time |  | 2025-03-14 | 2025-03-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35612914 | T2 CARIBOU #2 ;002/005 RPL STRW | 70Y
LC | 128287387 | 025/406 | T2 KESWICK-TRINITY 025/406 GO95 | TABLEMTN | ETL.7270.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2025-04-16 | Past Due |  | 2025-03-14 | 2025-03-14 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR ACCM COMP OH TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35573704 | T2 KESWICK-TRINITY 025/406 GO95 | 93G
LC | 128287524 | 001/023 | T2 EI SMARTVLLE-NCOLAUS #1 1/23 RPL STRW | SACTO | ETL.7990.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2025-03-09 | On-Time |  | 2025-03-14 | 2025-03-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572889 | T2 EI SMARTVLLE-NCOLAUS #1 1/23 RPL STRW | 70Y
LC | 128287594 | 002/025 | T2 EI PLACER-GOLD HLL #1 2/25 TOUCH | SACTO | ETL.3340.TOWR | 2024-03-14 | 2024-03-14 | 2024-03-14 | Past Due |  | 2024-09-14 | 2025-03-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP RESD ACCL OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491891 | T2 EI PLACER-GOLD HLL #1 2/25 TOUCH | ICQ
LC | 128287800 | 005/093 | T2 EI TMPLETN-ATASCADERO 5/93 RPL PL | PISMOBCH | ETL.9410.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2025-04-04 | Past Due |  | 2025-03-14 | 2025-03-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573701 | T2 EI TMPLETN-ATASCADERO 5/93 RPL PL | 70Y
LC | 128288000 | 006/014 | T2 EI TRINITY-MAPLE CREK 06/014 CNCL | EUREKA | ETL.8170.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2024-03-14 | Past Due |  | 2025-03-14 | 2025-03-14 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572116 | T2 EI TRINITY-MAPLE CREK 06/014 RPL ANCW | 93E
LC | 128288283 | 009/002 | T2 EI POTTER VALLEY-MENDO 9/2 RPR GYWW | WILLITS | ETL.7810.POLE.NWOD | 2024-03-14 | 2024-03-14 | 2025-03-11 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46403732 | T2 EI POTTER VALLEY-MENDO 9/2 RPR GYWW | ICW
LC | 128288287 | 031/001 | T2 EI COLNGA #1-SN MGL 31/1 RMV ENCRCH | FRESNO | ETL.8580.TOWR | 2024-03-14 | 2024-03-14 | 2024-09-23 | On-Time |  | 2024-09-14 | 2025-03-14 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46232961 | T2NT EI COLNGA #1-SN MGL 31/1 RMV ENCRCH | CHR
LC | 128288487 | 006/011 | T2 EI TRINITY-MPL CRK 006/011L RPR GYWW | EUREKA | ETL.8170.POLE.WDPS | 2024-03-14 | 2024-03-14 | 2025-03-11 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH RTNR FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345687 | T2 EI TRINITY-MPL CRK 006/011L RPR GYWW | ICW
LC | 128288566 | 006/011 | T2 EI TRINITY-MPL CRK 006/011C RPR GUY | EUREKA | ETL.8170.POLE.WDPS | 2024-03-14 | 2024-03-14 | 2025-03-11 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345688 | T2 EI TRINITY-MPL CRK 006/011C RPR GUY | ICW
LC | 128288613 | 000/008 | T2 EI COLEMAN-COTTONWOOD 0/8 RPL STRW | TABLEMTN | ETL.6430.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2025-03-03 | On-Time |  | 2025-03-14 | 2025-03-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556138 | T2 EI COLMAN-COTONWOD 00/008 RPL STRW | 70Y
LC | 128289054 | 000/001 | T2 EI COLEMAN-CTTNWD 0/1 RPL ANCW | TABLEMTN | ETL.6430.POLE.NWOD | 2024-03-14 | 2024-03-14 | 2024-12-05 | On-Time |  | 2025-03-14 | 2025-03-14 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35538561 | T2 EI COLEMAN-COTTONWOOD 0/1 RPL ANCW | 93E
LC | 128289070 | 006/012 | T2 TRINITY-MAPLE CREK 06/012 COMPLETE | EUREKA | ETL.8170.INSL.CERA | 2024-03-14 | 2024-03-14 | 2024-03-14 | Past Due |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Conductor-Wood | Repair | 46512123 | T2 EI TRINITY-MAPLE CREK 06/012 COMPLETE | ICW
LC | 128289156 | 003/028 | T2 EI PLACER-GOLD HILL #1 3/28 TOUCH | SACTO | ETL.3340.TOWR | 2024-03-14 | 2024-03-14 | 2024-03-14 | Past Due |  | 2024-06-14 | 2025-03-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP RESD ACCL OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478202 | T2 EI PLACER-GOLD HILL #1 3/28 TOUCH | ICQ
LC | 128289233 | 000/009 | T2 EI WEIMAR-HALSEY 000/009 COMPLETE | SACTO | ETL.8340.INSL | 2024-03-14 | 2024-03-14 | 2025-03-10 | On-Time |  | 2025-03-14 | 2025-03-14 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP CREW RESD REMT SWRK CLR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35571830 | T2 EI WEIMAR-HALSEY 000/009 RPL INSW | 93I
LC | 128289283 | 000/006 | T2 EI PINE GROVE TAP 00/6 REFRAME | VICTOR | ETL.8351.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2024-08-22 | On-Time |  | 2025-03-14 | 2025-03-14 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35544798 | T2 EI PINE GROVE TAP 00/6 REFRAME | 93E
LC | 128289418 | 000/010 | T2 EI WEIMAR-HALSEY 000/010 RPR GYWW | SACTO | ETL.8340.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2025-02-12 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46323934 | T2NT EI WEIMAR-HALSEY 000/010 RPR GYWW | ICW
LC | 128289473 | 000/004 | T2 EI COLMAN-COTONWOD 00/004 RPR STRW | TABLEMTN | ETL.6430.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2025-03-03 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46332447 | T2 EI COLMAN-COTONWOD 00/004 RPR STRW | ICW
LC | 128289543 | 017/079 | T2 EI PITTSBURG-TESLA #1 17/79 RMV NEST | CONCORD | ETL.5510.TOWR | 2024-03-14 | 2024-03-14 | 2024-12-22 | On-Time |  | 2025-03-14 | 2025-03-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46286513 | T2 EI PITTSBURG-TESLA #1 17/79 RMV NEST | ICS
LC | 128289546 | 027/110 | T2 EI DIABLO-MIDWAY #2 27/110 RPR FOND | PISMOBCH | ETL.5970.TOWR | 2024-03-14 | 2024-03-14 | 2025-01-23 | On-Time |  | 2025-03-14 | 2025-03-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT ACCM COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46391425 | T2NT EI DIABLO-MIDWAY #2 27/110 RPR FOND | ICQ
LC | 128289921 | 003/010 | T2 EI HUMBOLDT-MAPLE CREEK 3/10 RPL INSW | EUREKA | ETL.7130.INSL.CERA | 2024-03-14 | 2024-03-14 | 2025-05-27 | Past Due |  | 2025-03-14 | 2025-03-14 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574648 | T2 EI HUMBOLDT-MAPLE CREEK 3/10 RPL INSW | 93I
LC | 128290027 | 000/014 | T2 EI WEIMAR-HALSEY 00/014 RPR CRSW | SACTO | ETL.8340.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2025-02-11 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46323935 | T2 EI WEIMAR-HALSEY 00/014 RPR CRSW | ICW
LC | 128290192 | 000/010 | T2 EI PINE GROVE TAP 00/10 COTTER | VICTOR | ETL.8351.INSL.CERA | 2024-03-14 | 2024-03-14 | 2024-08-17 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46227674 | T2 EI PINE GROVE TAP 00/10 COTTER | ICW
LC | 128290215 | 002/066 | T2 EI PLACER-DEL MAR 2/66 RMV VEG | SACTO | ETL.7800.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2025-04-22 | Past Due |  | 2025-03-14 | 2025-03-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP NOAC SWRK CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128290254 | 001/022 | T2 EI SMARTVLE-NICLAUS #2 1/022 RPR INSW | SACTO | ETL.8000.INSL.NCER | 2024-03-14 | 2024-03-14 | 2025-02-21 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310259 | T2 EI SMARTVLE-NICLAUS #2 1/022 RPR INSW | ICW
LC | 128290279 | 003/079 | T2 EI COLGATE-GRS VALLEY 03/079 RPL STRW | SACTO | ETL.6490.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2025-03-01 | On-Time |  | 2025-03-14 | 2025-03-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557127 | T2 EI COLGATE-GRS VALLEY 03/079 RPL STRW | 70Y
LC | 128290292 | 003/012 | T2 HUMBOLDT-MAPLE CREEK 3/12 COMPLETE | EUREKA | ETL.7130.INSL.CERA | 2024-03-14 | 2024-03-14 | 2025-05-27 | Past Due |  | 2025-03-14 | 2025-03-14 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574652 | T2 EI HUMBOLDT-MAPLE CREEK 3/12 RPL INSW | 93I
LC | 128290354 | 001/029 | T2 EI SMARTVLE-NICOLAUS #1 1/29 RPR STRW | SACTO | ETL.7990.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2025-02-12 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310341 | T2 EI SMARTVLE-NICOLAUS #1 1/29 RPR STRW | ICW
LC | 128290417 | 014/014 | T2 EI FORT BRAGG-ELK 14/14 RMV VEG | WILLITS | ETL.2060.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2024-12-13 | On-Time |  | 2025-03-14 | 2025-03-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP RESD REMT ACCL COMP OH FMOB TR2 PRTO FRAR | Overgrown | Vegetation | Trim
LC | 128290486 | 031/000 | T2 EI COALNGA #1-SAN MIGEL 31/0 RPL INSS | PISMOBCH | ETL.8580.INSL.CERA | 2024-03-14 | 2024-03-14 | 2025-02-11 | On-Time |  | 2025-03-14 | 2025-03-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35585462 | T2 EI COALNGA #1-SAN MIGEL 31/0 RPL INSS | 93K
LC | 128298432 | 013/052 | T2 DI MORRO BAY-TEMPLTN 13/52 RPR OPGW | PISMOBCH | ETL.5933.TOWR | 2024-03-18 | 2024-03-14 | 2024-07-30 | On-Time |  | 2025-03-14 | 2025-03-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46229514 | T2 DI MORRO BAY-TEMPLTN 13/52 RPR OPGW | ICS
LC | 128301682 | 051/361 | T2 DI CARIBOU-TABLE MTN 51/361 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2024-03-18 | 2024-03-14 | 2025-01-02 | On-Time |  | 2025-03-14 | 2025-03-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46310427 | T2 DI CARIBOU-TABLE MTN 51/361 RPL HRDT | ICQ
LC | 128303277 | 005/070 | T2 DI GREEN VLY-PAUL SWT 5/70 RPL INSW | MOSSLNDG | ETL.1730.INSL.CERA | 2024-03-18 | 2024-03-14 | 2025-03-06 | On-Time |  | 2025-03-14 | 2025-03-14 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573570 | T2 DI GREEN VLY-PAUL SWT 5/70 RPL INSW | 93I
LC | 128303438 | 013/122 | T2 DI WOODLEAF-PALERMO-13/122 TOUCH | TABLEMTN | ETL.4220.POLE.NWOD | 2024-03-18 | 2024-03-14 | 2025-03-13 | On-Time |  | 2024-09-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46486714 | T2 DI WOODLEAF-PALERMO-13/122 TOUCH | ICW
LC | 128303466 | 008/166 | T2 DI CETERVILE-TBL MTN 8/166 INS STEP | TABLEMTN | ETL.6330.POLE.NWOD | 2024-03-18 | 2024-03-14 | 2024-12-04 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46311284 | T2NT DI CETERVILE-TBL MTN 8/166 INS STEP | ICW
LC | 128303583 | 009/078 | T2 DI WOODLEAF-PALERMO 09/78C RPL STRW | TABLEMTN | ETL.4220.POLE.WDPS | 2024-03-18 | 2024-03-14 | 2024-08-21 | On-Time |  | 2025-03-14 | 2025-03-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35540606 | T2 DI WOODLEAF-PALERMO 9/78R RPL STRW | 70Y
LC | 128303584 | 009/078 | T2 DI WOODLEAF-PALERMO 09/78L RPL STRW | TABLEMTN | ETL.4220.POLE.WDPS | 2024-03-18 | 2024-03-14 | 2024-08-21 | On-Time |  | 2025-03-14 | 2025-03-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35540606 | T2 DI WOODLEAF-PALERMO 9/78R RPL STRW | 70Y
LC | 128303609 | 017/348 | T2 DI COLGATE-PLRMO 017/348 RPR ANCW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-03-18 | 2024-03-14 | 2025-02-05 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46383046 | T2 DI COLGATE-PLRMO 017/348 RPR ANCW | ICW
LC | 128303691 | 017/348 | T2 COLGATE-PLRMO 017/348 RPL HRDD | SACTO | ETL.6500.POLE.WOOD | 2024-03-18 | 2024-03-14 | 2024-03-14 | Past Due |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace
LC | 128303760 | 005/067 | T2 DI GREEN VLY-PL SWT 5/67 RPR IBWW | MOSSLNDG | ETL.1730.INSL.NCER | 2024-03-18 | 2024-03-14 | 2024-08-18 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46218793 | T2 DI GREEN VLY-PL SWT 5/67 RPR IBWW | ICW
LC | 128303787 | 004/022 | T2 DI VASONA-METCALF 04/22 RPR STRT | METCALF | ETL.5932.TOWR | 2024-03-18 | 2024-03-14 | 2025-02-27 | On-Time |  | 2025-03-14 | 2025-03-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46298812 | T2 DI VASONA-METCALF 04/22 RPR STRT | ICQ
LC | 128303805 | 008/163 | T2 DI CNTVL-TBL MTN-ORVLE 8/163 RMV ENCR | TABLEMTN | ETL.6330.POLE.NWOD | 2024-03-18 | 2024-03-14 | 2025-02-03 | On-Time |  | 2025-03-14 | 2025-03-14 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Encroachment | Right of Way | Remove | 46459020 | T2 DI CNTVL-TBL MTN-ORVLE 8/163 RMV ENCR | CHR
LC | 128303827 | 008/165 | T2 DI CNTRVL-TBL MTN-ORO 8/165 RPR STRW | TABLEMTN | ETL.6330.POLE.WOOD | 2024-03-18 | 2024-03-14 | 2024-12-04 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311285 | T2 DI CNTRVL-TBL MTN-ORO 8/165 RPR STRW | ICW
LC | 128303874 | 008/156 | T2 DI CNTRVL-TBL MTN-ORVL 8/156 RPR INSW | TABLEMTN | ETL.6330.INSL.NCER | 2024-03-18 | 2024-03-14 | 2024-12-04 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46311286 | T2 DI CNTRVL-TBL MTN-ORVL 8/156 RPR INSW | ICW
LC | 128303997 | 005/104 | T2 DI CNTRVL-TBL MTN-ORVL 5/104 RPR STRW | TABLEMTN | ETL.6330.POLE.WOOD | 2024-03-18 | 2024-03-14 | 2024-12-04 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311289 | T2 DI CNTRVL-TBL MTN-ORVL 5/104 RPR STRW | ICW
LC | 128304016 | 005/051 | T2 DI WOODLEAF-PALERMO 5/51L RPL HRDW | TABLEMTN | ETL.4220.POLE.WDPS | 2024-03-18 | 2024-03-14 | 2025-03-13 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46332452 | T2 DI WOODLEAF-PALERMO 5/51L RPL HRDW | ICW
LC | 128353141 | 004/062 | T2 DI GRN VALLY-PAUL SWT 4/062 RPR CRSW | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-03-23 | 2024-03-14 | 2025-03-06 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46391214 | T2 DI GRN VALLY-PAUL SWT 4/062 RPR CRSW | ICW
LC | 128353142 | 005/049 | T2 DI WOODLEAF-PALERMO 05/49 RMV VEG | TABLEMTN | ETL.4220.POLE.STPS | 2024-03-23 | 2024-03-14 | 2024-08-13 | On-Time |  | 2024-09-14 | 2025-03-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128353143 | 005/049 | T2 DI WOODLEAF-PALERMO 05/49L INSP STRW | TABLEMTN | ETL.4220.POLE.STPS | 2024-03-23 | 2024-03-14 | 2024-08-10 | On-Time |  | 2024-09-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46217460 | T2 DI WOODLEAF-PALERMO 05/49L INSP STRW | ICW
LC | 128353193 | 016/160 | T2 DI WOODLEAF-PALERMO 16/160 RPR ANCW | TABLEMTN | ETL.4220.POLE.WOOD | 2024-03-23 | 2024-03-14 | 2025-01-06 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46332443 | T2 DI WOODLEAF-PALERMO 16/160 RPR ANCW | ICW
LC | 128353194 | 016/160 | T2 DI WOODLEAF-PALERMO 16/160 RMV VEG | TABLEMTN | ETL.4220.POLE.WOOD | 2024-03-23 | 2024-03-14 | 2025-03-13 | On-Time |  | 2025-03-14 | 2025-03-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128353270 | 004/063 | T2 DI GRN VLY-PAUL SWEET 4/63 RPR ANCW | MOSSLNDG | ETL.1730.POLE.WOOD | 2024-03-23 | 2024-03-14 | 2025-03-04 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Anchor-Wood | Repair | 46391215 | T2 DI GRN VLY-PAUL SWEET 4/63 RPR ANCW | ICW
LC | 128353372 | 006/058 | T2 DI WDLF-PALERMO 006/058 RPR ANCW | TABLEMTN | ETL.4220.POLE.WOOD | 2024-03-23 | 2024-03-14 | 2025-03-13 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46332462 | T2 DI WDLF-PALERMO 006/058 RPR ANCW | ICW
LC | 128353388 | 004/043 | T2 DI WOODLEAF-PALERMO 04/43R INSP STRW | TABLEMTN | ETL.4220.POLE.STPS | 2024-03-23 | 2024-03-14 | 2024-08-17 | On-Time |  | 2024-09-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46218248 | T2 DI WOODLEAF-PALERMO 04/43R INSP STRW | ICW
LC | 128353389 | 004/043 | T2 DI WOODLEAF-PALERMO 04/43C INSP STRW | TABLEMTN | ETL.4220.POLE.STPS | 2024-03-23 | 2024-03-14 | 2024-08-17 | On-Time |  | 2024-09-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46217462 | T2 DI WOODLEAF-PALERMO 04/43C INSP STRW | ICW
LC | 128353400 | 004/043 | T2 DI WOODLEAF-PALERMO 04/43 INSP STRW | TABLEMTN | ETL.4220.POLE.STPS | 2024-03-23 | 2024-03-14 | 2024-08-17 | On-Time |  | 2024-09-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46217461 | T2 DI WOODLEAF-PALERMO 04/43 INSP STRW | ICW
LC | 128365607 | 005/049 | T2 DI WOODLEAF-PALERMO 05/49R INSP STRW | TABLEMTN | ETL.4220.POLE.STPS | 2024-03-25 | 2024-03-14 | 2024-08-10 | On-Time |  | 2024-09-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46230761 | T2 DI WOODLEAF-PALERMO 05/49R INSP STRW | ICW
LC | 128365609 | 005/049 | T2 DI WOODLEAF-PALERMO 05/49C INSP STRW | TABLEMTN | ETL.4220.POLE.STPS | 2024-03-25 | 2024-03-14 | 2024-08-10 | On-Time |  | 2024-09-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46230760 | T2 DI WOODLEAF-PALERMO 05/49C INSP STRW | ICW
LC | 128366273 | 006/132 | T2 DI CNTRVL TBL MTN RVLE 6/132 RPL STRW | TABLEMTN | ETL.6330.POLE.WOOD | 2024-03-25 | 2024-03-14 | 2025-02-05 | On-Time |  | 2025-03-14 | 2025-03-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Rotten | Structure-Wood | Replace | 35556137 | T2 DI CNTRVL TBL MTN RVLE 6/132 RPL STRW | 70Y
LC | 128366275 | 005/068B | T2 DI GRN VLY-PL SWT 5/68B RPR GYWW | MOSSLNDG | ETL.1730.POLE.WOOD | 2024-03-25 | 2024-03-14 | 2025-02-07 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391217 | T2 DI GRN VLY-PL SWT 5/68B RPR GYWW | ICW
LC | 128366291 | 012/273 | T2 DI DRUM GRS VLY WMR 12/273 RPR GYWW | SACTO | ETL.6760.POLE.NWOD | 2024-03-25 | 2024-03-14 | 2024-07-19 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCH COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46283618 | T2 DI DRUM GRS VLY WMR 12/273 RPR GYWW | ICW
LC | 128366296 | 012/273 | T2 DI DRUM GRS VLY WMR 12/273 RPR ANCW | SACTO | ETL.6760.POLE.NWOD | 2024-03-25 | 2024-03-14 | 2024-06-26 | On-Time |  | 2024-09-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCH COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46227629 | T2 DI DRUM GRS VLY WMR 12/273 RPR ANCW | ICW
LC | 128366329 | 005/050 | T2 DI WDLF PLMRO 05/050 RPR INSW | TABLEMTN | ETL.4220.INSL.NCER | 2024-03-25 | 2024-03-14 | 2025-03-13 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46332463 | T2 DI WDLF PLMRO 05/050 RPR INSW | ICW
LC | 128366504 | 006/130 | T2 DI CNTRVL-TBL MTN-ORVL 6/130 RPL SPLW | TABLEMTN | ETL.6330.INSL.NCER | 2024-03-25 | 2024-03-14 | 2025-02-05 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Splice-Wood | Replace | 46311287 | T2 DI CNTRVL-TBL MTN-ORVL 6/130 RPL SPLW | ICW
LC | 128366520 | 004/091A | T2 DI CNTRVL TBL MTN ORVL 4/91A RPL SPLW | TABLEMTN | ETL.6330.INSL.NCER | 2024-03-25 | 2024-03-14 | 2024-12-04 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Splice-Wood | Replace | 46311294 | T2 DI CNTRVL TBL MTN ORVL 4/91A RPL SPLW | ICW
LC | 128366573 | 006/072 | T2 DI GRN VLY PAUL SWT 6/72 RPR BOND | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-03-25 | 2024-03-14 | 2025-03-05 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46391222 | T2 DI GRN VLY PAUL SWT 6/72 RPR BOND | ICW
LC | 128366579 | 009/176 | T2 DI CNTRVL TBL MTN ORVL 9/176 TOUCH | TABLEMTN | ETL.6330.POLE.NWOD | 2024-03-25 | 2024-03-14 | 2025-02-03 | On-Time |  | 2024-09-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46485705 | T2 DI CNTRVL TBL MTN ORVL 9/176 TOUCH | ICW
LC | 128366597 | 005/069 | T2 DI GRN VLY-PL SWT 5/69L RPR CRSW | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-03-25 | 2024-03-14 | 2025-03-04 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46391223 | T2 DI GRN VLY-PL SWT 5/69L RPR CRSW | ICW
LC | 128366633 | 006/125 | T2 DI CNTRVL-TBL MTN-ORVL 6/125 REFRAME | TABLEMTN | ETL.6330.POLE.WOOD | 2024-03-25 | 2024-03-14 | 2024-05-22 | On-Time |  | 2025-03-14 | 2025-03-14 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35549298 | T2 DI CNTRVL-TBL MTN-ORVL 6/125 REFRAME | 93E
LC | 128366740 | 004/092 | T2 DI CNTRVL TBL MTN ORVL 4/92 RPL SPLW | TABLEMTN | ETL.6330.INSL.NCER | 2024-03-25 | 2024-03-14 | 2024-12-04 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Splice-Wood | Replace | 46311293 | T2 DI CNTRVL TBL MTN ORVL 4/92 RPL SPLW | ICW
LC | 128366839 | 003/084 | T2 DI CNTRVL TBL MTN ORVL 3/84 RPL SPLW | TABLEMTN | ETL.6330.INSL.NCER | 2024-03-25 | 2024-03-14 | 2024-05-21 | On-Time |  | 2024-09-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Splice-Wood | Replace | 46230820 | T2 DI CNTRVL TBL MTN ORVL 3/84 RPL SPLW | ICW
LC | 128366920 | 009/177 | T2 DI CNTRVL TBL MTN ORVL 9/177 TOUCH | TABLEMTN | ETL.6330.POLE.NWOD | 2024-03-25 | 2024-03-14 | 2025-02-03 | On-Time |  | 2024-09-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46485708 | T2 DI CNTRVL TBL MTN ORVL 9/177 TOUCH | ICW
LC | 128366922 | 007/137 | T2 DI CNTRVL-TBL MTN-ORVL 7/137 RPL STRW | TABLEMTN | ETL.6330.POLE.WOOD | 2024-03-25 | 2024-03-14 | 2025-02-05 | On-Time |  | 2025-03-14 | 2025-03-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556137 | T2 DI CNTRVL TBL MTN RVLE 6/132 RPL STRW | 70Y
LC | 128366984 | 005/111 | T2 DI CNTRVL TBL MTN ORVL 5/111 RPR ANCW | TABLEMTN | ETL.6330.POLE.NWOD | 2024-03-25 | 2024-03-14 | 2024-12-04 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46311288 | T2 DI CNTRVL TBL MTN ORVL 5/111 RPR ANCW | ICW
LC | 128366989 | 005/103 | T2 DI CNTRVL-TB MTN-ORV 5/103L INSP ANCW | TABLEMTN | ETL.6330.POLE.WDPS | 2024-03-25 | 2024-03-14 | 2024-12-04 | On-Time |  | 2025-03-14 | 2025-03-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46311292 | T2 DI CNTRVL-TBL MTN-ORVL 5/103 RMV VEG | ICW
LC | 128367015 | 005/115 | T2 DI CNTRVL TBL MTN ORVL 5/115 RMV VEG | TABLEMTN | ETL.6330.POLE.NWOD | 2024-03-25 | 2024-03-14 | 2025-01-22 | On-Time |  | 2025-03-14 | 2025-03-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128380865 | 027/183 | T2 DI POE-RIO OSO-RIO OSO 27/183 RMV VEG | TABLEMTN | ETL.5540.TOWR | 2024-03-27 | 2024-03-14 | 2025-03-04 | On-Time |  | 2025-03-14 | 2025-03-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 123102994 | 000/004 | T2NT EI RND MTN-TABLE MT #1 0/4 RPR STRT | TABLEMTN | ETL.6060.TOWR | 2022-03-15 | 2022-03-15 | 2023-09-18 | On-Time |  | 2025-03-15 | 2025-03-15 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45235241 | T2 EI RUND MTN-TABLE MTN #1 0/4 RPR STRT | ICQ
LC | 123155237 | 011/090 | T2NT DI TGR CRK VLY SPR 11/90 RMV VEG | VICTOR | ETL.5790.TOWR | 2022-03-19 | 2022-03-15 | 2023-04-26 | On-Time |  | 2025-03-15 | 2025-03-15 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW OTHR FIRE COMP OH TR2N PRTO AIR FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 123185288 | 013/103 | T2NT DI TGR CRK-VLY SPRGS 13/103 BNT STL | VICTOR | ETL.5790.TOWR | 2022-03-24 | 2022-03-15 | 2023-08-07 | On-Time |  | 2025-03-15 | 2025-03-15 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45590789 | T2 DI TGR CRK-VLY SPRNGS 13/103 BNT STL | ICQ
LC | 128293740 | 003/068 | T2 EI PLACER-DEL MAR 3/68 RPR WDPKR | SACTO | ETL.7800.POLE.WOOD | 2024-03-15 | 2024-03-15 | 2025-02-20 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46323918 | T2 EI PLACER-DEL MAR 3/68 RPR WDPKR | ICW
LC | 128293746 | 004/003 | T2 EI POTTER VALLEY-MENDO 4/3 RMV NEST | WILLITS | ETL.7810.POLE.NWOD | 2024-03-15 | 2024-03-15 | 2025-03-11 | On-Time |  | 2025-03-15 | 2025-03-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46403734 | T2 EI POTTER VALLEY-MENDO 4/3 RMV NEST | ICS
LC | 128293940 | 004/004 | T2 EI POTTER VALLEY-MENDO 4/4 RPR FOND | WILLITS | ETL.7810.POLE.NWOD | 2024-03-15 | 2024-03-15 | 2025-03-13 | On-Time |  | 2025-03-15 | 2025-03-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46290107 | T2 EI POTTER VALLEY-MENDO 4/4 RPR FOND | ICQ
LC | 128293941 | 004/004 | T2 EI POTTER VALLEY-MENDO 4/4 RMV NEST | WILLITS | ETL.7810.POLE.NWOD | 2024-03-15 | 2024-03-15 | 2025-03-11 | On-Time |  | 2025-03-15 | 2025-03-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46403735 | T2 EI POTTER VALLEY-MENDO 4/4 RMV NEST | ICS
LC | 128294031 | A003/025 | T2 EI OLM-NRTH TWR-CHRTIE A3/25 RPR FOND | CONCORD | ETL.3180.TOWR | 2024-03-15 | 2024-03-15 | 2025-03-03 | On-Time |  | 2025-03-15 | 2025-03-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46286478 | T2 EI OLM-NRTH TWR-CHRTIE A3/25 RPR FOND | ICQ
LC | 128294137 | 014/245 | T2 ARCO-POLONIO PASS PP 14/245 RPL STRW | MIDWAY | ETL.8450.POLE.WOOD | 2024-03-15 | 2024-03-15 | 2025-04-02 | Past Due |  | 2025-03-15 | 2025-03-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35554107 | T2 EI ARCO-POLONIO PAS P 14/245 RPL POLE | 70Y
LC | 128294248 | 015/062 | T2 EI DIABLO-GATES #1 015/062 RPR SHIELD | PISMOBCH | ETL.5960.TOWR | 2024-03-15 | 2024-03-15 | 2025-02-24 | On-Time |  | 2025-03-15 | 2025-03-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329569 | T2 EI DIABLO-GATES #1 015/062 RPR SHIELD | ICS
LC | 128294449 | 014/248 | T2 EI ARCO-POLONIO PAS P 14/248 RPL POLE | MIDWAY | ETL.8450.POLE.WOOD | 2024-03-15 | 2024-03-15 | 2025-04-07 | Past Due |  | 2025-03-15 | 2025-03-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35554107 | T2 EI ARCO-POLONIO PAS P 14/245 RPL POLE | 70Y
LC | 128294478 | 003/014 | T2 EI HUMBOLDT-MAPLE CREEK 3/14 RPL INSW | EUREKA | ETL.7130.INSL.CERA | 2024-03-15 | 2024-03-15 | 2025-05-28 | Past Due |  | 2025-03-15 | 2025-03-15 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574654 | T2 EI HUMBOLDT-MAPLE CREEK 3/14 RPL INSW | 93I
LC | 128294484 | 007/048 | T2 EI OLEUM-G #1 7/48 COTTER | CONCORD | ETL.3150.INSL | 2024-03-15 | 2024-03-15 | 2025-03-09 | On-Time |  | 2025-03-15 | 2025-03-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC REAR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46286514 | T2 EI OLEUM-G #1 7/48 COTTER | ICS
LC | 128294486 | 003/075 | T2 EI WEIMAR-HALSEY 3/75 RPR INSW | SACTO | ETL.8340.INSL | 2024-03-15 | 2024-03-15 | 2025-03-07 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46323937 | T2 EI WEIMAR-HALSEY 3/75 RPR INSW | ICW
LC | 128294815 | A003/026 | T2 EI OLM-NRTH TWR-CHRTIE A3/26 COMPLETE | CONCORD | ETL.3180.TOWR | 2024-03-15 | 2024-03-15 | 2024-03-20 | On-Time |  | 2024-06-15 | 2025-03-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO CLMB FRAB DURA BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46213535 | T2 EI OLM-NRTH TWR-CHRTIE A3/26 RPR FOND | ICQ
LC | 128294823 | A003/026 | T2 EI OLM-NRTH TR-CHTIE A3/26 RPR STRT | CONCORD | ETL.3180.TOWR | 2024-03-15 | 2024-03-15 | 2025-02-05 | On-Time |  | 2025-03-15 | 2025-03-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286479 | T2 EI OLM-NRTH TR-CHTIE A3/26 RPR STRT | ICQ
LC | 128295154 | 000/002 | T2 SOBRANTE-MORAGA 0/2 RPL POLE | CONCORD | ETL.3742.POLE.WOOD | 2024-03-15 | 2024-03-15 | 2024-03-15 | Past Due |  | 2025-03-15 | 2025-03-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35573711 | T2 EI SOBRANTE-MORAGA 0/2 RPL POLE | 70Y
LC | 128295215 | 005/000 | T2 EI POTTER VALLEY-MENDO 5/0 RMV NEST | WILLITS | ETL.7810.POLE.NWOD | 2024-03-15 | 2024-03-15 | 2025-03-11 | On-Time |  | 2025-03-15 | 2025-03-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46403739 | T2 EI POTTER VALLEY-MENDO 5/0 RMV NEST | ICS
LC | 128295216 | 004/006 | T2 EI POTTER VALLEY-MENDO 4/6 RPR GYWT | WILLITS | ETL.7810.POLE.NWOD | 2024-03-15 | 2024-03-15 | 2025-03-13 | On-Time |  | 2025-03-15 | 2025-03-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46297637 | T2 EI POTTER VALLEY-MENDO 4/6 RPR GYWT | ICQ
LC | 128295309 | 030/000 | T2 EI COLINGA #1-SAN MIGUL 30/0 RPR ANCT | FRESNO | ETL.8580.TOWR | 2024-03-15 | 2024-03-15 | 2025-01-15 | On-Time |  | 2025-03-15 | 2025-03-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW REMT CUSI ACCL COMP OH RTNR FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46292630 | T2 EI COLINGA #1-SAN MIGUL 30/0 RPR ANCT | ICQ
LC | 128295322 | 008/047 | T2 MARTINEZ-SOBRANTE 8/47 RPR CRST | CONCORD | ETL.2270.INSL.CERA | 2024-03-15 | 2024-03-15 | 2024-03-15 | Past Due |  | 2025-03-15 | 2025-03-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Crossarm-Tower | Repair | 46286520 | T2 EI OLM-NRTH TWR-CHRTIE A3/27 RPR STRT | ICQ
LC | 128295404 | 010/068 | T2 EI CNTR CSTA-LS PSTS 10/68 RPR STRT | CONCORD | ETL.4510.TOWR | 2024-03-15 | 2024-03-15 | 2024-08-08 | On-Time |  | 2025-03-15 | 2025-03-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46220487 | T2 EI CNTR CSTA-LS PSTS 10/68 RPR STRT | ICQ
LC | 128295533 | 006/042 | T2 EI OLEUM-G #1 6/42 UNBURY | CONCORD | ETL.3150.TOWR | 2024-03-15 | 2024-03-15 | 2025-01-28 | On-Time |  | 2025-03-15 | 2025-03-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46286476 | T2 EI OLEUM-G #1 6/42 UNBURY | ICQ
LC | 128295609 | 015/260 | T2 EI ARCO-POLNIO PAS PP 15/260 RPL POLE | MIDWAY | ETL.8450.POLE.WOOD | 2024-03-15 | 2024-03-15 | 2025-04-07 | Past Due |  | 2025-03-15 | 2025-03-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35554107 | T2 EI ARCO-POLONIO PAS P 14/245 RPL POLE | 70Y
LC | 128295843 | 010/009 | T2 EI PTTR VLLY-WLLTS 010/009 RPR STRW | WILLITS | ETL.7820.POLE.WOOD | 2024-03-15 | 2024-03-15 | 2025-02-18 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46305766 | T2 EI PTTR VLLY-WLLTS 010/009 RPR STRW | ICW
LC | 128295875 | 011/066 | T2 EI LONE TREE-CAYETAN 11/66 RPL HANGER | CONCORD | ETL.6160.INSL.CERA | 2024-03-15 | 2024-03-15 | 2024-09-17 | On-Time |  | 2025-03-15 | 2025-03-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC CLR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46286477 | T2 EI LONE TREE-CAYETAN 11/66 RPL HANGER | ICQ
LC | 128296302 | 002/061 | T2 EI COLGATE-GRS VALLEY 02/061 COMPLETE | SACTO | ETL.6490.POLE.WOOD | 2024-03-15 | 2024-03-15 | 2025-03-01 | On-Time |  | 2025-03-15 | 2025-03-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572550 | T2 EI COLGATE-GRS VALLEY 02/061 RPL STRW | 70Y
LC | 128296313 | 002/058 | T2 EI COLGATE-GRS VALLEY 02/058 RPL HRDW | SACTO | ETL.6490.POLE.WOOD | 2024-03-15 | 2024-03-15 | 2025-01-15 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46383044 | T2 EI COLGATE-GRS VALLEY 02/058 RPL HRDW | ICW
LC | 128296418 | 001/010 | T2 EI OLEUM-G #1 1/10 RPR STRT | CONCORD | ETL.3150.TOWR | 2024-03-15 | 2024-03-15 | 2025-02-01 | On-Time |  | 2025-03-15 | 2025-03-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286475 | T2 EI OLEUM-G #1 1/10 RPR STRT | ICQ
LC | 128296471 | 004/020 | T2 WV HMBLDT BY-HMBDT #2 4/20 INS DMPS | EUREKA | ETL.7090.INSL.NCER | 2024-03-15 | 2024-03-15 | 2025-03-10 | On-Time |  | 2025-03-15 | 2025-03-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Steel | Install | 46305576 | T2 WV HMBLDT BY-HMBDT #2 4/20 INS DMPS | ICS
LC | 128296473 | 001/034 | T2 EI WEIMAR-HALSEY 1/34 RPR INSW | SACTO | ETL.8340.INSL.NCER | 2024-03-15 | 2024-03-15 | 2025-01-14 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD TRAF CLR ACCH COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46323938 | T2 EI WEIMAR-HALSEY 1/34 RPR INSW | ICW
LC | 128296481 | 003/002 | T2 EI POTTER VALLEY-MENDO 3/2 RPR FOND | WILLITS | ETL.7810.POLE.NWOD | 2024-03-15 | 2024-03-15 | 2025-03-13 | On-Time |  | 2025-03-15 | 2025-03-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46290106 | T2 EI POTTER VALLEY-MENDO 3/2 RPR FOND | ICQ
LC | 128296511 | 002/007 | T2 EI POTTER VALLEY-MENDO 2/7 RMV NEST | WILLITS | ETL.7810.POLE.NWOD | 2024-03-15 | 2024-03-15 | 2025-03-11 | On-Time |  | 2025-03-15 | 2025-03-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46403733 | T2 EI POTTER VALLEY-MENDO 2/7 RMV NEST | ICS
LC | 128297087 | 029/001 | T2 EI COALNGA #1-SAN MIGUL 29/1 RPL HNGR | FRESNO | ETL.8580.INSL.CERA | 2024-03-16 | 2024-03-15 | 2024-10-16 | On-Time |  | 2025-03-15 | 2025-03-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46292629 | T2 EI COALNGA #1-SAN MIGUL 29/1 RPL HNGR | ICQ
LC | 128298516 | 002/004 | T2 MELONES-CURTIS 02/04R RPL POLE | VICTOR | ETL.2390.POLE.WDPS | 2024-03-18 | 2024-03-15 | 2025-05-28 | Past Due |  | 2025-03-15 | 2025-03-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35573694 | T2 MELONES-CURTIS 02/04R RPL POLE | 70Y
LC | 128298517 | 002/004 | T2 MELONES-CURTIS 02/04L RPL POLE | VICTOR | ETL.2390.POLE.WDPS | 2024-03-18 | 2024-03-15 | 2025-05-28 | Past Due |  | 2025-03-15 | 2025-03-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35573694 | T2 MELONES-CURTIS 02/04R RPL POLE | 70Y
LC | 128300770 | 005/054 | T2 DI PARADISE-TABLE MTN 5/54 RPL INSS | TABLEMTN | ETL.4316.INSL.NCER | 2024-03-18 | 2024-03-15 | 2025-02-12 | On-Time |  | 2025-03-15 | 2025-03-15 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570814 | T2 DI PARADISE-TABLE MTN RPL INSS 4 TSP | 93K
LC | 128301733 | 005/109 | T2 DI BRNS-LONE STR#2 5/109 RPR JUMW | MOSSLNDG | ETL.6240.INSL.NCER | 2024-03-18 | 2024-03-15 | 2024-05-20 | On-Time |  | 2024-06-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46218789 | T2 DI BRNS-LONE STR#2 5/109 RPR JUMW | ICW
LC | 128303517 | 004/064 | T2 DI GRN VLY-PAUL SWT 4/64 RPR IBWW | MOSSLNDG | ETL.1730.INSL.NCER | 2024-03-18 | 2024-03-15 | 2025-03-03 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46391207 | T2 DI GRN VLY-PAUL SWT 4/64 RPR IBWW | ICW
LC | 128303580 | 004/064 | T2 DI GRN VLY-PAUL SWT 4/64 RPL HRDD | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-03-18 | 2024-03-15 | 2025-03-03 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46391208 | T2 DI GRN VLY-PAUL SWT 4/64 RPL HRDD | ICW
LC | 128303802 | 007/079 | T2 DI GRN VLY-PAUL SWEET 7/79 RPR GYWW | MOSSLNDG | ETL.1730.POLE.WOOD | 2024-03-18 | 2024-03-15 | 2025-03-04 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAR NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391209 | T2 DI GRN VLY-PAUL SWEET 7/79 RPR GYWW | ICW
LC | 128303803 | 007/079 | T2 DI GRN VLY-PAUL SWEET 7/79 RPR INSW | MOSSLNDG | ETL.1730.INSL.NCER | 2024-03-18 | 2024-03-15 | 2024-08-18 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46218794 | T2 DI GRN VLY-PAUL SWEET 7/79 RPR INSW | ICW
LC | 128304081 | 005/070 | T2 DI BURNS-LONE STAR #1 05/70 RPL HRDW | MOSSLNDG | ETL.6230.POLE.NWOD | 2024-03-18 | 2024-03-15 | 2025-03-07 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB NTDE | Missing | Hardware-Wood | Install | 46391210 | T2 DI BURNS-LONE STAR #1 05/70 RPL HRDW | ICW
LC | 128304082 | 55 | T2 DI BURNS-LONE STAR #1 05/70 RPR SWTC | MOSSLNDG | ETL.6230.SWIT | 2024-03-18 | 2024-03-15 | 2025-03-07 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Switch-Wood | Repair | 46391263 | T2 DI BURNS-LONE STAR #1 05/70 RPR SWTC | ICW
LC | 128319383 | 004/065 | T2 DI GRN VLY-PL SWT 4/65 RPR STRW | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-03-19 | 2024-03-15 | 2025-03-03 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46391212 | T2 DI GRN VLY-PL SWT 4/65 RPR STRW | ICW
LC | 128320606 | 004/065 | T2 DI GRN VLY-PL SWT 4/65 RMV VEG | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-03-19 | 2024-03-15 | 2025-02-25 | On-Time |  | 2025-03-15 | 2025-03-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Overgrown | Vegetation | Remove
LC | 128366136 | 007/078A | T2 DI GRN VLY-PAL SWT 7/78AL RPR STRW | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-03-25 | 2024-03-15 | 2025-03-04 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Structure-Wood | Repair | 46391216 | T2 DI GRN VLY-PAL SWT 7/78AL RPR STRW | ICW
LC | 128366375 | 008/157 | T2 DI MONTA VISTA-LOS GTS 8/157 RMV VEG | METCALF | ETL.7610.POLE.WOOD | 2024-03-25 | 2024-03-15 | 2025-02-12 | On-Time |  | 2025-03-15 | 2025-03-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR CNCL OH TR2 PRTO AIR FRAR | Overgrown | Vegetation | Remove
LC | 128366467 | 004/051 | T2 DI BURNS-LONE STR#1 4/51R RPR GYWW | MOSSLNDG | ETL.6230.POLE.WDPS | 2024-03-25 | 2024-03-15 | 2025-03-08 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391218 | T2 DI BURNS-LONE STR#1 4/51R RPR GYWW | ICW
LC | 128366478 | 006/077 | T2 DI GRN VLY-PAL SWT 6/77 RMV VEG | MOSSLNDG | ETL.1730.POLE.WOOD | 2024-03-25 | 2024-03-15 | 2025-03-11 | On-Time |  | 2025-03-15 | 2025-03-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128366502 | 004/051 | T2 DI BURNS-LONE STR#1 4/51L RMV VEG | MOSSLNDG | ETL.6230.POLE.WDPS | 2024-03-25 | 2024-03-15 | 2024-12-09 | On-Time |  | 2025-03-15 | 2025-03-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128366503 | 004/051 | T2 DI BURNS-LONE STR#1 4/51C RMV VEG | MOSSLNDG | ETL.6230.POLE.WDPS | 2024-03-25 | 2024-03-15 | 2024-12-09 | On-Time |  | 2025-03-15 | 2025-03-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128366506 | 004/051 | T2 DI BURNS-LONE STR#1 4/51L RPR ANCW | MOSSLNDG | ETL.6230.POLE.WDPS | 2024-03-25 | 2024-03-15 | 2025-03-08 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46391219 | T2 DI BURNS-LONE STR#1 4/51L RPR ANCW | ICW
LC | 128366508 | 004/051 | T2 DI BURNS-LONE STR#1 4/51C RPR ANCW | MOSSLNDG | ETL.6230.POLE.WDPS | 2024-03-25 | 2024-03-15 | 2025-03-08 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46391220 | T2 DI BURNS-LONE STR#1 4/51C RPR ANCW | ICW
LC | 128366524 | 004/051 | T2 DI BURNS-LONE STR#1 4/51C RPL HRDW | MOSSLNDG | ETL.6230.POLE.WDPS | 2024-03-25 | 2024-03-15 | 2025-03-08 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46391221 | T2 DI BURNS-LONE STR#1 4/51C RPL HRDW | ICW
LC | 128366614 | 014/095 | T2 DI METCALF-GREEN VLLY 14/95R RPL POLE | MOSSLNDG | ETL.2540.POLE.WDPS | 2024-03-25 | 2024-03-15 | 2025-02-27 | On-Time |  | 2025-03-15 | 2025-03-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574105 | T2 DI METCALF-GREEN VLLY 14/95R RPL POLE | 70Y
LC | 128366617 | 005/070 | T3 DI DESABLA-CENTERVILLE 5/70 RPR IBWW | TABLEMTN | ETL.6720.INSL.NCER | 2024-03-25 | 2024-03-15 | 2025-04-15 | Past Due |  | 2025-03-15 | 2025-03-15 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR3 PRTO AIR NTDE BRIN | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46230794 | T3 DI DESABLA-CENTERVILLE 5/70 RPR IBWW | ICW
LC | 128366808 | 005/063 | T2 DI BURNS-LONE STR#1 5/63 RPR INSW | MOSSLNDG | ETL.6230.INSL.NCER | 2024-03-25 | 2024-03-15 | 2025-03-12 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46391224 | T2 DI BURNS-LONE STR#1 5/63 RPR INSW | ICW
LC | 128366816 | 005/106 | T2 DI BURNS-LONE STAR #2 5/106C RPR GYWW | MOSSLNDG | ETL.6240.POLE.STPS | 2024-03-25 | 2024-03-15 | 2025-03-08 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391225 | T2 DI BURNS-LONE STAR #2 5/106C RPR GYWW | ICW
LC | 128366830 | 005/063 | T2 DI BURNS-LONE STR#1 5/63 RPR CRSW | MOSSLNDG | ETL.6230.POLE.NWOD | 2024-03-25 | 2024-03-15 | 2025-03-12 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46391226 | T2 DI BURNS-LONE STR#1 5/63 RPR CRSW | ICW
LC | 128380364 | 005/110 | T2 DI BURNS-LONE STR#2 5/110 RPR GYWW | MOSSLNDG | ETL.6240.POLE.WOOD | 2024-03-27 | 2024-03-15 | 2025-03-09 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391229 | T2 DI BURNS-LONE STR#2 5/110 RPR GYWW | ICW
LC | 128380561 | 005/110 | T2 DI BURNS-LONE STR#2 5/110 RPR ANCW | MOSSLNDG | ETL.6240.POLE.WOOD | 2024-03-27 | 2024-03-15 | 2024-08-18 | On-Time |  | 2024-09-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46266144 | T2 DI BURNS-LONE STR#2 5/110 RPR ANCW | ICW
LC | 128380601 | 008/162 | T2 DI MNTA VIST LS GTS 8/162 RPR GYWW | METCALF | ETL.7610.POLE.WOOD | 2024-03-27 | 2024-03-15 | 2025-01-02 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286871 | T2 DI MNTA VIST LS GTS 8/162 RPR GYWW | ICW
LC | 128380706 | 007/083 | T2 DI GRN VLY PAUL SWEET 7/83L RMV VEG | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-03-27 | 2024-03-15 | 2025-03-11 | On-Time |  | 2025-03-15 | 2025-03-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128380797 | 015/100 | T2 DI MTCLF GRN VLLY 15/100 RPR STRW | MOSSLNDG | ETL.2540.POLE.WOOD | 2024-03-27 | 2024-03-15 | 2025-02-25 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46391230 | T2 DI MTCLF GRN VLLY 15/100 RPR STRW | ICW
LC | 128380806 | 014/096 | T2 DI METCALF-GRN VLLY 14/96L RPR STRW | MOSSLNDG | ETL.2540.POLE.WDPS | 2024-03-27 | 2024-03-15 | 2025-02-23 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46391228 | T2 DI METCALF-GRN VLLY 14/96L RPR STRW | ICW
LC | 128381292 | 007/080B | T2 GREEN VALLEY-PL 7/80B (R) RMV VEG | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-03-27 | 2024-03-15 | 2025-03-01 | On-Time |  | 2025-03-15 | 2025-03-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | Overgrown | Vegetation | Remove
LC | 128381295 | 007/080 | T2 DI GRN VLY PL SWT 7/80 RPR STRW | MOSSLNDG | ETL.1730.POLE.WOOD | 2024-03-27 | 2024-03-15 | 2025-03-04 | On-Time |  | 2025-03-15 | 2025-03-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Structure-Wood | Repair | 46391232 | T2 DI GRN VLY PL SWT 7/80 RPR STRW | ICW
LC | 128386733 | 007/082 | T2 DI GRN VLLY-PL SWT 7/82 RMV VEG | MOSSLNDG | ETL.1730.POLE.WOOD | 2024-03-28 | 2024-03-15 | 2025-02-24 | On-Time |  | 2025-03-15 | 2025-03-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Trim
LC | 128444515 | 014/095 | T2 DI METCALF-GREEN VLLY 14/95L RPL POLE | MOSSLNDG | ETL.2540.POLE.WDPS | 2024-04-04 | 2024-03-15 | 2025-02-27 | On-Time |  | 2025-03-15 | 2025-03-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574105 | T2 DI METCALF-GREEN VLLY 14/95R RPL POLE | 70Y
LC | 123107471 | 001/003 | T2NT EI MNDCNO-WLTS-FT BRGG 1/3 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2022-03-16 | 2022-03-16 | 2023-06-05 | On-Time |  | 2025-03-16 | 2025-03-16 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45654641 | T2NT EI MNDCNO-WLTS-FT BRGG 1/3 RPR GYWW | ICW
LC | 123108449 | 001/010 | T3NT EI RN MTN-TBL MTN #1 1/10 RPR GYWS | TABLEMTN | ETL.6060.TOWR | 2022-03-16 | 2022-03-16 | 2023-08-16 | On-Time |  | 2025-03-16 | 2025-03-16 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45650907 | T3 EI RND MTN-TBLE MTN #1 1/10 RPR GYWS | ICS
LC | 123108927 | 074/304 | T2NT EI RND MN-TB MTN #1 74/304 RPR STRT | TABLEMTN | ETL.6060.TOWR | 2022-03-16 | 2022-03-16 | 2023-08-03 | On-Time |  | 2025-03-16 | 2025-03-16 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644785 | T2 EI RND MTN-TB MTN #1 74/304 RPR STRT | ICQ
LC | 123110972 | 001/012 | T3NT EI RND MTN-TBLE MTN #1 1/12 BNT STL | TABLEMTN | ETL.6060.TOWR | 2022-03-16 | 2022-03-16 | 2023-08-18 | On-Time |  | 2025-03-16 | 2025-03-16 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45650906 | T3 EI RND MTN-TBLE MTN #1 1/12 BNT STEEL | ICS
LC | 123156276 | 032/266 | T2NT DI BRDGVIL-COTNWD 32/266 RPR ADSS | TABLEMTN | ETL.1110.TOWR | 2022-03-19 | 2022-03-16 | 2023-06-10 | On-Time |  | 2025-03-16 | 2025-03-16 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Steel | Repair | 45644092 | T2 DI BRDGVIL-COTNWD 32/266 RPR ADSS | ICS
LC | 123184410 | 019/175 | T2NT DI BRIDGVLLE-CTTNWD 19/175 RPR ADSS | TABLEMTN | ETL.1110.POLE.WDPS | 2022-03-24 | 2022-03-16 | 2023-08-18 | On-Time |  | 2025-03-16 | 2025-03-16 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45644154 | T2 DI BRIDGEVLLE-COTTNWD 19/175 RPR ADSS | ICW
LC | 123188690 | 006/086 | T2NT DI DVD CBRL #1 6/86 INS FIBER LABEL | PISMOBCH | ETL.1380.POLE.WOOD | 2022-03-25 | 2022-03-16 | 2023-12-06 | On-Time |  | 2025-03-16 | 2025-03-16 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE ACCM COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45599965 | T2 DI DVD CBRL #1 6/86 INS FIBER LABEL | ICW
LC | 123192280 | 012/102 | T2NT DI PIT#1-COTTONWOOD 12/102 RPR STRS | TABLEMTN | ETL.5390.TOWR | 2022-03-25 | 2022-03-16 | 2023-08-24 | On-Time |  | 2025-03-16 | 2025-03-16 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45620079 | T2 DI PIT #1-COTTONWOOD 12/102 RPR STRS | ICQ
LC | 123196364 | 025/222 | T2NT DI BRIDGVILL-CTTNWD 25/222 RPR ADSS | TABLEMTN | ETL.1110.POLE.WDPS | 2022-03-26 | 2022-03-16 | 2023-05-13 | On-Time |  | 2025-03-16 | 2025-03-16 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45644176 | T2 DI BRIDGVILLE-COTTNWD 25/222 RPR ADSS | ICW
LC | 123113107 | 073/299 | T2NT EI RND MTN-TL MTN #2 73/299 BNT ST | TABLEMTN | ETL.6070.TOWR | 2022-03-17 | 2022-03-17 | 2023-08-03 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647753 | T2 EI RND MTN-TBL MTN #2 73/299 BNT ST | ICQ
LC | 123119443 | 002/013 | T3NT EI RND MTN-TABLE MTN#1 2/13 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2022-03-17 | 2022-03-17 | 2023-08-22 | On-Time |  | 2025-03-17 | 2025-03-17 | 564 | TR3N |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR3N PRTO CLMB FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 123143806 | 002/014 | T3NT EI RND MTN-TBL MTN#1 2/14 RPR STRT | TABLEMTN | ETL.6060.TOWR | 2022-03-17 | 2022-03-17 | 2023-08-18 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644373 | T3 EI RND MTN-TABLE MTN#1 2/14 RPR STRT | ICQ
LC | 123144573 | 072/295 | T2NT EI RND MTN-TBL MTN#2 72/295 BNT STL | TABLEMTN | ETL.6070.TOWR | 2022-03-17 | 2022-03-17 | 2024-02-13 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647751 | T2 EI RND MTN-TBL MTN #2 72/295 BNT STL | ICQ
LC | 123145499 | 071/293 | T2NT EI RND MT-TBL MT #1 71/293 BNT STL | TABLEMTN | ETL.6060.TOWR | 2022-03-17 | 2022-03-17 | 2023-07-31 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644536 | T2 EI RND MTN-TABLE MTN #1 71/293 BNT ST | ICQ
LC | 123145866 | 002/016 | T3NT EI RND MTN-TBL MTN#1 2/16 RPR STRT | TABLEMTN | ETL.6060.TOWR | 2022-03-17 | 2022-03-17 | 2023-08-14 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644376 | T3 EI RND MTN-TABLE MTN#1 2/16 RPR STRT | ICQ
LC | 123174158 | 058/532 | T2NT DI PIT #1 CTTNWD 58/532 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2022-03-23 | 2022-03-17 | 2023-09-20 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45581851 | T2 DI PIT #1 CTTNWD 58/532 BNT STEEL | ICQ
LC | 123183620 | 043/371 | T2NT DI RND MTN-CTNWD #3 43/371 RPR STRT | TABLEMTN | ETL.5650.TOWR | 2022-03-24 | 2022-03-17 | 2023-10-16 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648255 | T2 DI RND MTN-CTTNWD #3 43/371 RPR STRT | ICQ
LC | 123184493 | 044/375 | T2NT DI PIT #1-COTTONWD 44/375 INS HRDT | TABLEMTN | ETL.5390.TOWR | 2022-03-24 | 2022-03-17 | 2023-10-16 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Missing | Hardware-Tower | Install | 45639736 | T2 DI PIT #1-COTTONWOOD 44/375 INS HRDT | ICQ
LC | 123184620 | 017/160 | T2NT DI BRDGVLLE-CTTNWD 17/160 INST HRDD | TABLEMTN | ETL.1110.POLE.STPS | 2022-03-24 | 2022-03-17 | 2023-05-09 | On-Time |  | 2025-03-17 | 2025-03-17 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB NTDE | Missing | Hardware-Wood | Install | 45644155 | T2 DI BRDGVLLE-CTTNWD 017/160 INST HRDD | ICW
LC | 123184633 | 017/160 | T2NT DI BRDGVLLE-CTTNWD 17/160 RPR ADSS | TABLEMTN | ETL.1110.POLE.STPS | 2022-03-24 | 2022-03-17 | 2023-05-09 | On-Time |  | 2025-03-17 | 2025-03-17 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45644157 | T2 DI BRDGVLLE-CTTNWD 017/160 RPR ADSS | ICW
LC | 123185575 | 018/067 | T2NT DI EXCR-IDN FT-YSMIT 18/67 RPR STRT | FRESNO | ETL.8650.TOWR | 2022-03-24 | 2022-03-17 | 2023-12-14 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648424 | T2 DI EXCR-INDN FLT-YSMIT 18/67 RPR STRT | ICQ
LC | 123187245 | 043/370 | T2NT DI PIT #1-CTTONWD 43/370 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2022-03-25 | 2022-03-17 | 2023-08-02 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45639733 | DI T2 PIT #1-CTTONWD 43/370 RPR FOND | ICQ
LC | 123197063 | 043/369 | T2NT DI RND MTN-CTTNWD #3 43/369 BNT STL | TABLEMTN | ETL.5650.TOWR | 2022-03-26 | 2022-03-17 | 2023-08-02 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648254 | T2 DI RND MTN-CTTNWD #3 43/369 BNT STEEL | ICQ
LC | 123197158 | 048/421 | T2NT DI RND MTN-CTNWD #3 48/421 RPR STRT | TABLEMTN | ETL.5650.TOWR | 2022-03-26 | 2022-03-17 | 2023-08-01 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45581855 | T2 DI RND MTN-CTTNWD #3 48/421 RPR STRT | ICQ
LC | 123197250 | 018/064 | T2NT DI EXCHQR-IND FLT-YS 18/64 INS STEP | FRESNO | ETL.8650.TOWR | 2022-03-26 | 2022-03-17 | 2023-05-02 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | Missing | Hardware-Tower | Install | 45648433 | T2 DI EXCHQR-INDN FLT-YSM 18/64 INS STEP | ICQ
LC | 123197364 | 052/463 | T2NT DI PT #1 CTNWD 52/463 UNBURY | TABLEMTN | ETL.5390.TOWR | 2022-03-26 | 2022-03-17 | 2023-07-05 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45581346 | T2 DI PT #1 CTNWD 52/463 RPR FOND | ICQ
LC | 123204637 | 019/176 | T2NT DI BRIDGEVLLE-CTNWD 19/176 RPR ADSS | TABLEMTN | ETL.1110.POLE.WDPS | 2022-03-28 | 2022-03-17 | 2023-08-18 | On-Time |  | 2025-03-17 | 2025-03-17 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45644199 | T2 DI BRIDGEVILLE-COTNWD 19/176 RPR ADSS | ICW
LC | 123216768 | 020/185 | T2NT DI BRDGVIL-CTNWD 20/185 RPR ADSS | TABLEMTN | ETL.1110.POLE.WDPS | 2022-03-30 | 2022-03-17 | 2023-06-21 | On-Time |  | 2025-03-17 | 2025-03-17 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45644245 | T2 DI BRDGVIL-CTNWD 20/185 RPR ADSS | ICW
LC | 129544473 | 001/014 | T3 EL DORADO-MSSRI FLT#1 1/14 RPL HANGER | SACTO | ETL.1530.INSL.NCER | 2024-09-17 | 2024-09-17 | 2025-03-16 | On-Time |  | 2025-03-17 | 2025-03-17 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCL COMP OH TR3 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46323217 | T3 EL DORADO-MSSRI FLT#1 1/14 RPL HANGER | ICQ
LC | 129545692 | 005/101 | T3 COLGATE-CHALLENGE 5/101 RMV VEG | SACTO | ETL.6480.POLE.WOOD | 2024-09-17 | 2024-09-17 | 2024-12-12 | On-Time |  | 2024-12-17 | 2025-03-17 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR CNCL OH FMOB TR3 PRTO FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 123150463 | 071/291 | T2NT EI RND MT-TBL MT #2 71/291 BNT STL | TABLEMTN | ETL.6060.TOWR | 2022-03-18 | 2022-03-18 | 2023-07-31 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644531 | T2 EI ROUND MTN-TBLE #2 71/291 RPR STRT | ICQ
LC | 123151552 | 070/289 | T2NT EI RND MTN-TBL MT #1 70/289 BNT STL | TABLEMTN | ETL.6060.TOWR | 2022-03-18 | 2022-03-18 | 2023-08-01 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45617453 | T2 EI ROUND MTN-TBLE #1 70/289 BNT STEEL | ICQ
LC | 123151567 | 070/289 | T2NT EI RND MT-TBL MT #2 70/289 BNT STL | TABLEMTN | ETL.6070.TOWR | 2022-03-18 | 2022-03-18 | 2023-08-01 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45617454 | T2 EI ROUND MTN-TBLE #2 70/289 RPR HRDT | ICQ
LC | 123151612 | 070/289 | T2NT EI RND MT TBL MT #2 70/289 RPR GYWS | TABLEMTN | ETL.6070.TOWR | 2022-03-18 | 2022-03-18 | 2023-09-13 | On-Time |  | 2025-03-18 | 2025-03-18 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45703160 | T2 EI ROUND MTN-TBLE #2 70/289 RPR GYWS | ICS
LC | 123153126 | 003/020 | T3NT EI RND MTN-TBLE MTN #1 3/20 BNT STL | TABLEMTN | ETL.6060.TOWR | 2022-03-18 | 2022-03-18 | 2023-08-18 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644400 | T3 EI ROUND MTN-TBLE MTN #1 3/20 BNT STL | ICQ
LC | 123187455 | 021/078 | T2NT DI XCHQR-INDN FLT 21/78 BNT STEEL | FRESNO | ETL.8650.TOWR | 2022-03-25 | 2022-03-18 | 2023-05-02 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648425 | T2 DI XCHQR-INDN FLT 21/78 BNT STEEL | ICQ
LC | 123188106 | 041/183 | T3NT DI MTCF-MOS LNDNG #1 41/183 RPR FND | MOSSLNDG | ETL.5100.TOWR | 2022-03-25 | 2022-03-18 | 2023-06-27 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45650130 | T3NT DI MTCF-MOS LNDNG #1 41/183 RPR FND | ICQ
LC | 128298522 | 010/062 | T2 LONE TREE CAYENTANO 10/62 RPL HNGR | CONCORD | ETL.6160.INSL.CERA | 2024-03-18 | 2024-03-18 | 2024-03-18 | Past Due |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP REMT SWRK CLR OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46286561 | T2 EI LONE TREE CAYENTANO 10/62 RPL HNGR | ICQ
LC | 128298531 | 009/063 | T2 EI CNTRA CSTA-LS PSTS 9/63 RMV NEST | CONCORD | ETL.4510.TOWR | 2024-03-18 | 2024-03-18 | 2024-12-22 | On-Time |  | 2025-03-18 | 2025-03-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46286560 | T2 EI CNTRA CSTA-LS PSTS 9/63 RMV NEST | ICS
LC | 128298590 | 119 | T2 OLEUM-G #2 7/50 SW#119 RPR SWTC | CONCORD | ETL.3150.SWIT | 2024-03-18 | 2024-03-18 | 2025-03-09 | On-Time |  | 2025-03-18 | 2025-03-18 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR RESD COMP OH FMOB TR2 PRTO | Out of Adjustment | Switch | Repair | 46286565 | T2 OLEUM-G #2 7/50 SW#119 RPR SWTC | ICE
LC | 128298870 | A003/028 | T2 EI OLUM-N TWR-CRSTE A3/28 RPR STRT | CONCORD | ETL.3180.TOWR | 2024-03-18 | 2024-03-18 | 2025-02-05 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46297782 | T2 EI OLUM-N TWR-CRSTE A3/28 RPR STRT | ICQ
LC | 128299060 | 006/128 | T2 EI SMRTVLE-NCLUS #1 6/128 RPR INSW | SACTO | ETL.7990.INSL.NCER | 2024-03-18 | 2024-03-18 | 2025-02-10 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310342 | T2 EI SMRTVLE-NCLUS #1 6/128 RPR INSW | ICW
LC | 128299117 | 006/044 | T2 EI OLEUM-G #1 6/44 BNT STEEL | CONCORD | ETL.3150.TOWR | 2024-03-18 | 2024-03-18 | 2025-02-03 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT REAR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286521 | T2 EI OLEUM-G #1 6/44 BNT STEEL | ICQ
LC | 128299338 | 009/062 | T2 EI CNTRA CSTA-LS PSTS 9/62 RMV NEST | CONCORD | ETL.4510.TOWR | 2024-03-18 | 2024-03-18 | 2024-12-22 | On-Time |  | 2025-03-18 | 2025-03-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46286519 | T2 EI CNTRA CSTA-LS PSTS 9/62 RMV NEST | ICS
LC | 128299638 | 007/045 | T2 EI OLEUM-G #2 7/45 RPR CNDS | CONCORD | ETL.3160.INSL.CERA | 2024-03-18 | 2024-03-18 | 2024-09-03 | On-Time |  | 2024-06-18 | 2025-03-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Conductor-Steel | Repair | 46220498 | T2 EI OLEUM-G #2 7/45 RPR CNDS | ICS
LC | 128299768 | A004/030 | T2 EI OLUM-N TWR-CRSTE A4/30 BNT STEEL | CONCORD | ETL.3180.TOWR | 2024-03-18 | 2024-03-18 | 2025-02-05 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46297784 | T2 EI OLUM-N TWR-CRSTE A4/30 BNT STEEL | ICQ
LC | 128299796 | 023/096 | T2 DIABLO-GATES #1 23/96 TOUCH | PISMOBCH | ETL.5960.TOWR | 2024-03-18 | 2024-03-18 | 2024-03-18 | Past Due |  | 2024-09-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472269 | T2 EI DIABLO-GATES #1 23/96 TOUCH | ICQ
LC | 128299888 | 007/132 | T2 EI SMRTVLE-NCLUS #1 7/132 RPR ANCW | SACTO | ETL.7990.POLE.NWOD | 2024-03-18 | 2024-03-18 | 2025-02-10 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46310344 | T2 EI SMRTVLE-NCLUS #1 7/132 RPR ANCW | ICW
LC | 128299935 | 000/001 | T2 EI CTNWD-PANORAMA 0/1 RPR STRW | TABLEMTN | ETL.1340.POLE.NWOD | 2024-03-18 | 2024-03-18 | 2025-02-27 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46332449 | T2 EI CTNWD-PANORAMA 0/1 RPR STRW | ICW
LC | 128299991 | 000/002 | T2 EI CTNWD-PANORAMA 0/2 COTTER | TABLEMTN | ETL.1340.INSL | 2024-03-18 | 2024-03-18 | 2024-04-22 | On-Time |  | 2024-06-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46218245 | T2 EI CTNWD-PANORAMA 0/2 COTTER | ICW
LC | 128300006 | 000/002 | T2 EI CTNWD-PANORAMA 0/2 RPL STRW | TABLEMTN | ETL.1340.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2025-03-13 | On-Time |  | 2025-03-18 | 2025-03-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35572994 | T2 EI CTNWD-PANORAMA 0/2 RPL STRW | 70Y
LC | 128300022 | 014/073 | T2 CNTRA CSTA-MRGA#1 14/73 RPR FOND | CONCORD | ETL.5452.TOWR | 2024-03-18 | 2024-03-18 | 2024-03-18 | Past Due |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46505478 | T2 CNTRA CSTA-MRGA#1 14/73 RPR FOND | ICQ
LC | 128300080 | 000/003 | T2 EI CTNWD-PANORAMA 0/3 RPR STRW | TABLEMTN | ETL.1340.POLE.NWOD | 2024-03-18 | 2024-03-18 | 2025-03-10 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46332450 | T2 EI CTNWD-PANORAMA 0/3 RPR STRW | ICW
LC | 128300143 | 007/133 | T2 EI BELE AFB(WPA)#2 TAP 7/133 RPR INSS | SACTO | ETL.7971.INSL.NCER | 2024-03-18 | 2024-03-18 | 2025-02-10 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46300499 | T2 EI BELE AFB(WPA)#2 TAP 7/133 RPR INSS | ICW
LC | 128300149 | 002/054 | T2 EI CLGTE-GRASS VALLEY 02/54 COMPLETE | SACTO | ETL.6490.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2025-03-01 | On-Time |  | 2025-03-18 | 2025-03-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557126 | T2 EI CLGTE-GRASS VALLEY 02/054 RPL STRW | 70Y
LC | 128300206 | 000/004 | T2 EI CTNWD-PANORAMA 0/4 RPL STRW | TABLEMTN | ETL.1340.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2025-03-13 | On-Time |  | 2025-03-18 | 2025-03-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557666 | T2 EI CTNWD-PANORAMA 0/4 RPL STRW | 70Y
LC | 128300224 | 080/567 | T2 BRDGVLLE-CTTNWD 80/567 RPL HRDT | EUREKA | ETL.1110.TOWR | 2024-03-18 | 2024-03-18 | 2025-03-11 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46305577 | T2 BRDGVLLE-CTTNWD 80/567 RPL HRDT | ICQ
LC | 128300227 | 005/089 | T2 EI BRIONES TAP 005/089 RPR GYWW | CONCORD | ETL.7055.POLE.NWOD | 2024-03-18 | 2024-03-18 | 2025-03-11 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP CLR ACCL COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286515 | T2 EI BRIONES TAP 005/089 RPR GYWW | ICW
LC | 128300283 | 000/003 | T2 EI AUBERRY TAP 000/003 RMV GYWW | FRESNO | ETL.9331.POLE.NWOD | 2024-03-18 | 2024-03-18 | 2024-09-06 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305276 | T2 EI AUBERRY TAP 000/003 RMV GYWW | ICW
LC | 128300320 | 000/005 | T2 EI CTNWD-PANORAMA 0/5 RPL STRW | TABLEMTN | ETL.1340.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2025-03-13 | On-Time |  | 2025-03-18 | 2025-03-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557666 | T2 EI CTNWD-PANORAMA 0/4 RPL STRW | 70Y
LC | 128300434 | 020/008 | T2 EI RIO DEL JCT-BRDGVLE 20/08 RPL HRDW | EUREKA | ETL.7850.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2025-03-11 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAR | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345690 | T2 EI RIO DEL JCT-BRDGVLE 20/08 RPL HRDW | ICW
LC | 128300619 | 000/006 | T2 EI CTNWD-PANORAMA 0/6 RPR ANCW | TABLEMTN | ETL.1340.POLE.NWOD | 2024-03-18 | 2024-03-18 | 2025-02-27 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46332451 | T2 EI CTNWD-PANORAMA 0/6 RPR ANCW | ICW
LC | 128300728 | 006/121 | T2 EI CORDELIA #2 TAP 6/121 RPR POLE | SACTO | ETL.8184.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2025-02-03 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337396 | T2 EI CORDELIA #2 TAP 6/121 RPR POLE | ICW
LC | 128300937 | 002/057 | T2 EI CLGTE-GRASS VALLEY 02/057 RPL HRDW | SACTO | ETL.6490.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2025-01-15 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46383045 | T2 EI CLGTE-GRASS VALLEY 02/057 RPL HRDW | ICW
LC | 128300998 | 000/020 | T2 EI WEIMAR-HALSEY 0/20 RMV STEP | SACTO | ETL.8340.POLE.NWOD | 2024-03-18 | 2024-03-18 | 2025-02-13 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46323939 | T2 EI WEIMAR-HALSEY 0/20 RMV STEP | ICW
LC | 128301003 | 008/090 | T2 VEDDER TAP 8/90 RPL POLE | MIDWAY | ETL.2141.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2024-04-30 | On-Time |  | 2025-03-18 | 2025-03-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35539651 | T2 VEDDER TAP 7/89 RPL POLE | 70Y
LC | 128301007 | 007/089 | T2 VEDDER TAP 7/89 RPL POLE | MIDWAY | ETL.2141.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2024-04-02 | On-Time |  | 2025-03-18 | 2025-03-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35539651 | T2 VEDDER TAP 7/89 RPL POLE | 70Y
LC | 128301030 | A004/031 | T2 EI OLUM-N TWR-CRSTE A4/31 BNT STEEL | CONCORD | ETL.3180.TOWR | 2024-03-18 | 2024-03-18 | 2025-02-05 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286573 | T2 EI OLUM-N TWR-CRSTE A4/31 BNT STEEL | ICQ
LC | 128301037 | 008/006 | T2 EI TRINITY-MAPLE CREEK 8/006 RPL STRW | EUREKA | ETL.8170.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2025-03-22 | Past Due |  | 2025-03-18 | 2025-03-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572113 | T2 EI TRINITY-MAPLE CREEK 8/006 RPL POLE | 70Y
LC | 128301064 | 008/004 | T2 EI TRINITY-MAPLE CREEK 8/4 RPL INSW | EUREKA | ETL.8170.INSL.CERA | 2024-03-18 | 2024-03-18 | 2025-03-24 | Past Due |  | 2025-03-18 | 2025-03-18 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572112 | T2 EI TRINITY-MAPLE CREEK 8/004 RPL INSW | 93I
LC | 128301170 | A004/032 | T2 EI OLUM-N TWR-CRSTE A4/32 BNT STEEL | CONCORD | ETL.3180.TOWR | 2024-03-18 | 2024-03-18 | 2025-02-07 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286572 | T2 EI OLUM-N TWR-CRSTE A4/32 BNT STEEL | ICQ
LC | 128301683 | 007/137 | T2 EI SMRTVLE-NCLUS #1 7/137 RPR STRW | SACTO | ETL.7990.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2025-02-10 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310345 | T2 EI SMRTVLE-NCLUS #1 7/137 RPR STRW | ICW
LC | 128301713 | 008/055 | T2 EI CNTRA CSTA-LS PSTS 08/55 BNT STEEL | CONCORD | ETL.4510.TOWR | 2024-03-18 | 2024-03-18 | 2025-01-19 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286516 | T2 EI CNTRA CSTA-LS PSTS 08/55 BNT STEEL | ICQ
LC | 128301714 | 008/055 | T2 EI CNTRA CSTA-LS PSTS 08/55 RMV NEST | CONCORD | ETL.4510.TOWR | 2024-03-18 | 2024-03-18 | 2024-12-22 | On-Time |  | 2025-03-18 | 2025-03-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46286518 | T2 EI CNTRA CSTA-LS PSTS 08/55 RMV NEST | ICS
LC | 128301813 | 034/005 | T2 COALINGA #1-SAN MIGUEL 34/00 RPR INSS | PISMOBCH | ETL.8580.INSL.CERA | 2024-03-18 | 2024-03-18 | 2025-02-11 | On-Time |  | 2025-03-18 | 2025-03-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW REMT REAR SWRK ACCM COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329625 | T2 COALINGA #1-SAN MIGUEL 34/00 RPR INSS | ICS
LC | 128302098 | 007/140 | T2 EI SMRTVLLE-NICLAUS #2 7/140 COMPLETE | SACTO | ETL.8000.POLE.NWOD | 2024-03-18 | 2024-03-18 | 2024-08-05 | On-Time |  | 2024-09-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46217628 | T2 EI SMRTVLLE-NICOLAUS #2 7/14 RPR GYWW | ICW
LC | 128302427 | 013/064 | T2 EI CNTRA CSTA-MRGA#1 13/64 RPR FOND | CONCORD | ETL.5452.TOWR | 2024-03-18 | 2024-03-18 | 2025-02-10 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46286563 | T2NT EI CNTRA CSTA-MRGA#1 13/64 RPR FOND | ICQ
LC | 128303190 | 007/138 | T2 EI SMRTVLE-NCLUS #1 7/138 RPR ANCW | SACTO | ETL.7990.POLE.NWOD | 2024-03-18 | 2024-03-18 | 2025-02-10 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46310347 | T2 EI SMRTVLE-NCLUS #1 7/138 RPR ANCW | ICW
LC | 128303236 | 027/005 | T2 EI CLINGA #1-SAN MGUEL 27/005 UNBURY | FRESNO | ETL.8580.TOWR | 2024-03-18 | 2024-03-18 | 2025-01-22 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46292633 | T2 EI CLINGA #1-SAN MGUEL 27/005 UNBURY | ICQ
LC | 128303237 | 027/004 | T2 EI CLINGA #1-SAN MGUEL 27/004 UNBURY | FRESNO | ETL.8580.TOWR | 2024-03-18 | 2024-03-18 | 2025-01-22 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46292632 | T2 EI CLINGA #1-SAN MGUEL 27/004 UNBURY | ICQ
LC | 128303238 | 027/003 | T2 EI CLINGA #1-SAN MGUEL 27/003 UNBURY | FRESNO | ETL.8580.TOWR | 2024-03-18 | 2024-03-18 | 2025-01-22 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46292631 | T2 EI CLINGA #1-SAN MGUEL 27/003 UNBURY | ICQ
LC | 128303248 | 005/026A | T2 EI DIABLO-MESA 5/026A RPL HNGR | PISMOBCH | ETL.4620.INSL.NCER | 2024-03-18 | 2024-03-18 | 2025-03-23 | Past Due |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SPCR ACCH COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46391332 | T2 EI DIABLO-MESA 5/026A RPL HNGR | ICQ
LC | 128303291 | 004/006 | T2 EI HUMBOLDT-MAPLE CREEK 4/06 RPL STRW | EUREKA | ETL.7130.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2025-05-29 | Past Due |  | 2025-03-18 | 2025-03-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574656 | T2 EI HUMBOLDT-MAPLE CREEK 4/06 RPL STRW | 70Y
LC | 128303364 | 001/031 | T2 EI WEIMAR-HALSEY 1/31 RPL STRW | SACTO | ETL.8340.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2025-03-09 | On-Time |  | 2025-03-18 | 2025-03-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35571832 | T2 EI WEIMAR-HALSEY 1/31 RPL STRW | 70Y
LC | 128303496 | 002/010 | T2 EI LOWER LAKE-HOMESTAKE 2/10 COTR KEY | WILLITS | ETL.1481.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2025-03-11 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46333775 | T2 EI LOWER LAKE-HOMESTAKE 2/10 COTR KEY | ICW
LC | 128304120 | 006/048 | T2 DI IGNCO-ALTO-SLTO #1 6/48 RPL INSS | LAKEVLLE | ETL.7160.INSL | 2024-03-18 | 2024-03-18 | 2025-04-26 | Past Due |  | 2025-03-18 | 2025-03-18 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35544694 | T2 DI IGNCO-ALTO-SLTO #1 6/48 RPL INSS. | 93K
LC | 128304574 | 027/016 | T2 DI GOLD HILL #1 027/016 RPL POLE | VICTOR | ETL.6950.POLE.WOOD | 2024-03-19 | 2024-03-18 | 2025-04-09 | Past Due |  | 2025-03-18 | 2025-03-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573236 | T2 DI GOLD HILL #1 027/016 RPL POLE | 70Y
LC | 128318575 | 020/080 | T2 DI PITTSBRG-SAN MATEO 20/80 RMV NEST | CONCORD | ETL.5463.TOWR | 2024-03-19 | 2024-03-18 | 2025-01-15 | On-Time |  | 2025-03-18 | 2025-03-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46286564 | T2 DI PITTSBRG-SAN MATEO 20/80 RMV NEST | ICS
LC | 128322167 | 007/050 | T2 DI IGNC-ALTO-SLT #1 70/50 RMV VEG | LAKEVLLE | ETL.7160.TOWR | 2024-03-19 | 2024-03-18 | 2024-06-28 | On-Time |  | 2025-03-18 | 2025-03-18 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128322210 | 007/050 | T2 DI IGNC-ALTO-SLT #1 70/50 TOUCH | LAKEVLLE | ETL.7160.TOWR | 2024-03-19 | 2024-03-18 | 2025-03-31 | Past Due |  | 2024-09-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485385 | T2 DI IGNC-ALTO-SLT #1 70/50 TOUCH | ICQ
LC | 128353072 | 003/070 | T2 DI CNTRVL-TBL MTN-ORVLE 3/70 RPR IBWW | TABLEMTN | ETL.6330.POLE.WOOD | 2024-03-23 | 2024-03-18 | 2025-02-03 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46311283 | T2 DI CNTRVL-TBL MTN-ORVLE 3/70 RPR IBWW | ICW
LC | 128353074 | 67 | T2 DI CNTRVL-TBL MTN-ORVL 3/70 RPR HRDW | TABLEMTN | ETL.6330.SWIT | 2024-03-23 | 2024-03-18 | 2025-02-03 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | Missing | Hardware-Wood | Install | 46311282 | T2 DI CNTRVL-TBL MTN-ORVL 3/70 RPR HRDW | ICW
LC | 128353076 | 013/057 | T2 DI MRAGA-CSTRO VALLEY 13/57 RPR OPGW | CONCORD | ETL.5250.TOWR | 2024-03-23 | 2024-03-18 | 2024-05-02 | On-Time |  | 2025-03-18 | 2025-03-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46302970 | T2 DI MRAGA-CSTRO VALLEY 13/57 RPR OPGW | ICS
LC | 128353078 | 013/057 | T2 DI MORAGA-CASTRO VLY 13/57 RPR FOND | CONCORD | ETL.5250.TOWR | 2024-03-23 | 2024-03-18 | 2025-01-07 | On-Time |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46286562 | T2NT DI MORAGA-CASTRO VLY 13/57 RPR FOND | ICQ
LC | 128353157 | 013/007 | T2 DI KONOCTI MIDDLETOWN 13/7 RPR INSW | WILLITS | ETL.6380.INSL.NCER | 2024-03-23 | 2024-03-18 | 2024-03-18 | Past Due |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46333778 | T2 DI KONOCTI MIDDLETOWN 13/7 RPR INSW | ICW
LC | 128357138 | 013/057 | T2 DI SAN RAMON-MORAGA 13/57 RPR OPGW | CONCORD | ETL.5250.TOWR | 2024-03-25 | 2024-03-18 | 2024-05-02 | On-Time |  | 2025-03-18 | 2025-03-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46220586 | T2 DI SAN RAMON-MORAGA 13/57 RPR OPGW | ICW
LC | 128380907 | B011/009 | T2 DI FLTN-CALISTOGA B011/009 RPR GYWW | LAKEVLLE | ETL.6880.POLE.NWOD | 2024-03-27 | 2024-03-18 | 2025-02-04 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305578 | T2 DI FLTN-CALISTOGA B011/009 RPR GYWW | ICW
LC | 128381105 | 012/003 | T2 DI KONOCTI-MDDLTN 012/003 RPR STRW | WILLITS | ETL.6380.POLE.WOOD | 2024-03-27 | 2024-03-18 | 2025-03-17 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46333776 | T2 DI KONOCTI-MDDLTN 012/003 RPR STRW | ICW
LC | 128381263 | 109/005 | T2 DI HMBLDT-BRDGVILL 109/5L RPR GYWW | EUREKA | ETL.1810.POLE.STPS | 2024-03-27 | 2024-03-18 | 2025-03-11 | On-Time |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345691 | T2 DI HMBLDT-BRDGVILL 109/5L RPR GYWW | ICW
LC | 128388526 | 005/025 | T2 PITTSBURG-EASTSHORE 5/25 RPL INSS | CONCORD | ETL.5462.INSL | 2024-03-29 | 2024-03-18 | 2024-03-18 | Past Due |  | 2025-03-18 | 2025-03-18 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575003 | T2 DI PITTSBURG-EASTSHORE 5/25 RPL INSS | 93K
LC | 128393409 | 013/003 | T2 DI KNCTI-MDDLTWN 013/003 RPR STRW | WILLITS | ETL.6380.POLE.WOOD | 2024-03-29 | 2024-03-18 | 2024-03-18 | Past Due |  | 2025-03-18 | 2025-03-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46333777 | T2 DI KNCTI-MDDLTWN 013/003 RPR STRW | ICW
LC | 128395512 | 012/013 | T2 KNCTI-MDDLTWN 012/013 RPL STRW | WILLITS | ETL.6380.POLE.WOOD | 2024-03-31 | 2024-03-18 | 2024-03-18 | Past Due |  | 2025-03-18 | 2025-03-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574107 | T2 DI KNCTI-MDDLTWN 012/013 RPL STRW | 70Y
LC | 130957291 | 006/048 | T2 DI IGNCO-ALTO-SLTO #2 6/48 RPR STRT | LAKEVLLE | ETL.7160.TOWR | 2025-03-10 | 2024-03-18 | 2024-03-18 | Past Due |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46485440 | T2 DI IGNCO-ALTO-SLTO #2 6/48 RPR STRT | ICQ
LC | 130957294 | 006/046 | T2 IGNACIO-ALTO-SAUSLTO #2 6/46 RPR STRT | LAKEVLLE | ETL.7170.INSL.NCER | 2025-03-10 | 2024-03-18 | 2024-03-18 | Past Due |  | 2025-03-18 | 2025-03-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46485399 | T2 DI IGNCO-ALT-SLTO #2 6/46 RPR STRT | ICQ
LC | 123189833 | 055/002 | T2NT DI HUMBOLDT-TRINITY 55/2L INS RPTW | EUREKA | ETL.1820.POLE.STPS | 2022-03-25 | 2022-03-19 | 2023-04-08 | On-Time |  | 2025-03-19 | 2025-03-19 | 593 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Raptor Guard-Wood | Replace | 45659245 | T2NT DI HUMBOLDT-TRINITY 55/2L INS RPTW | ICB
LC | 128304348 | 000/010 | T2 WEIMAR #1 0/10 RPR JUMW | SACTO | ETL.7560.INSL.NCER | 2024-03-19 | 2024-03-19 | 2024-09-15 | On-Time |  | 2024-06-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46217631 | T2 WEIMAR #1 000/010 RPR JMPW | ICW
LC | 128304681 | 006/124 | T2 EI CORDELIA #2 TAP 6/124 RMV VEG | SACTO | ETL.8184.POLE.WOOD | 2024-03-19 | 2024-03-19 | 2025-02-27 | On-Time |  | 2025-03-19 | 2025-03-19 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128304716 | 000/002 | T2 EI SMRTVLE-NCLUS #1 0/2 RPR GYWW | SACTO | ETL.7990.POLE.NWOD | 2024-03-19 | 2024-03-19 | 2025-02-12 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310348 | T2 EI SMRTVLE-NCLUS #1 0/2 RPR GYWW | ICW
LC | 128305050 | 042/274A | T2 TRINITY-CTTNWD 42/274A REGRADE | TABLEMTN | ETL.4040.POLE.NWOD | 2024-03-19 | 2024-03-19 | 2025-02-24 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46332453 | T2 TRINITY-CTTNWD 42/274A REGRADE | ICW
LC | 128305101 | 001/016 | T2 EI CTNWD-PANORAMA 1/16 RPR CNDW | TABLEMTN | ETL.1340.INSL.NCER | 2024-03-19 | 2024-03-19 | 2025-03-13 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Conductor-Wood | Repair | 46332454 | T2 EI CTNWD-PANORAMA 1/16 RPR CNDW | ICW
LC | 128305537 | 043/208 | T2NT EI CRTNA-MNDCINO #1 43/208 RMV VEG | WILLITS | ETL.1330.TOWR | 2024-03-19 | 2024-03-19 | 2025-02-25 | On-Time |  | 2027-03-19 | 2025-03-19 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128306153 | 008/011 | T2 EI TRINITY-MAPLE CREEK 8/011 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-03-19 | 2024-03-19 | 2024-10-30 | On-Time |  | 2024-09-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46222542 | T2 EI TRINITY-MAPLE CREEK 8/011 RPR GYWW | ICW
LC | 128306155 | 008/014 | T2 EI TRINITY-MAPLE CREEK 8/014 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-03-19 | 2024-03-19 | 2024-10-30 | On-Time |  | 2024-09-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46222543 | T2 EI TRINITY-MAPLE CREEK 8/014 RPR GYWW | ICW
LC | 128306668 | 007/051 | T2 EI CNTRA CSTA-LS PSTS 7/51 RMV NEST | CONCORD | ETL.4510.TOWR | 2024-03-19 | 2024-03-19 | 2025-01-15 | On-Time |  | 2025-03-19 | 2025-03-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46286566 | T2 EI CNTRA CSTA-LS PSTS 7/51 RMV NEST | ICS
LC | 128307317 | 012/003 | T2 EI PHILO JCT-ELK 12/3 RPR INSW | WILLITS | ETL.7780.INSL.NCER | 2024-03-19 | 2024-03-19 | 2025-03-19 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK ACCL COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46333779 | T2 EI PHILO JCT-ELK 12/3 RPR INSW | ICW
LC | 128307323 | 001/036 | T2 EI COLGATE-GRASS VALEY 1/036 RPL POLE | SACTO | ETL.6490.POLE.WOOD | 2024-03-19 | 2024-03-19 | 2025-02-27 | On-Time |  | 2025-03-19 | 2025-03-19 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557125 | T2 EI COLGATE-GRASS VALEY 1/036 RPL POLE | 70Y
LC | 128307766 | 047/230A | T2 IGNACIO SOBRANTE 47/230A COTTER | CONCORD | ETL.4920.INSL.CERA | 2024-03-19 | 2024-03-19 | 2025-02-17 | On-Time |  | 2025-03-19 | 2025-03-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46403423 | T2 IGNACIO SOBRANTE 47/230A COTTER | ICS
LC | 128308087 | 006/107 | T2 EI BRIONES TAP 6/107 RPL STRW | CONCORD | ETL.7055.POLE.WOOD | 2024-03-19 | 2024-03-19 | 2025-04-20 | Past Due |  | 2025-03-19 | 2025-03-19 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD CLR ACCH USA COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35555499 | T2 EI BRIONES TAP 6/107 RPL STRW | 70Y
LC | 128308418 | 002/044 | T2 EI SMRTVLE-NCLUS #1 2/44 RPR STRW | SACTO | ETL.7990.POLE.WOOD | 2024-03-19 | 2024-03-19 | 2025-02-12 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310350 | T2 EI SMRTVLE-NCLUS #1 2/44 RPR STRW | ICW
LC | 128308419 | 002/044 | T2 EI SMRTVLE-NCLUS #1 2/44 RPR GYWW | SACTO | ETL.7990.POLE.WOOD | 2024-03-19 | 2024-03-19 | 2025-02-12 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310352 | T2 EI SMRTVLE-NCLUS #1 2/44 RPR GYWW | ICW
LC | 128308947 | 005/117 | T2 EI WEIMAR-HALSEY 5/117 RPR WDPK | SACTO | ETL.8340.POLE.WOOD | 2024-03-19 | 2024-03-19 | 2025-01-13 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46324615 | T2 EI WEIMAR-HALSEY 5/117 RPR WDPK | ICW
LC | 128308963 | 005/110 | T2 EI PLACER-DEL MAR 5/110 RPR STRW | SACTO | ETL.7800.POLE.WOOD | 2024-03-19 | 2024-03-19 | 2025-02-19 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD NOAC CLR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46323921 | T2 EI PLACER-DEL MAR 5/110 RPR STRW | ICW
LC | 128309031 | 000/003 | T2 SMRTVLE-NCLUS #2 0/3 RPR INSW | SACTO | ETL.8000.INSL.NCER | 2024-03-19 | 2024-03-19 | 2024-03-19 | Past Due |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310349 | T2 EI SMRTVLE-NCLUS #2 0/3 RPR INSW | ICW
LC | 128309575 | 005/118 | T2 EI WEIMAR-HALSEY 5/118RPR WDPK | SACTO | ETL.8340.POLE.WOOD | 2024-03-19 | 2024-03-19 | 2025-01-13 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46324614 | T2 EI WEIMAR-HALSEY 5/118RPR WDPK | ICW
LC | 128310362 | 005/108 | T2 EI PLACER-DEL MAR 5/108 RPR STRW | SACTO | ETL.7800.POLE.WOOD | 2024-03-19 | 2024-03-19 | 2025-02-20 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP CGI CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46323922 | T2 EI PLACER-DEL MAR 5/108 RPR STRW | ICW
LC | 128311765 | 021/094 | T2 EI MORRO BAY-MESA 21/094 RPR INSS | PISMOBCH | ETL.5290.INSL.NCER | 2024-03-19 | 2024-03-19 | 2025-02-21 | On-Time |  | 2025-03-19 | 2025-03-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329538 | T2 EI MORRO BAY-MESA 21/094 RPR INSS | ICS
LC | 128312001 | 003/066 | T2 EI SMRTVLE-NCLUS #2 3/66 RPR GYWW | SACTO | ETL.8000.POLE.NWOD | 2024-03-19 | 2024-03-19 | 2025-02-21 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310353 | T2 EI SMRTVLE-NCLUS #2 3/66 RPR GYWW | ICW
LC | 128312014 | 000/002 | T2 EI POTER VLEY-MENDOCINO 0/02 UNBURY | WILLITS | ETL.7810.POLE.NWOD | 2024-03-19 | 2024-03-19 | 2025-03-18 | On-Time |  | 2025-03-19 | 2025-03-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAR | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46290119 | T2 EI POTER VLEY-MENDOCINO 0/02 UNBURY | ICQ
LC | 128312158 | 009/003 | T2 EI TRINITY-MAPLE CREEK 9/3 RPL ANCW | EUREKA | ETL.8170.POLE.WOOD | 2024-03-19 | 2024-03-19 | 2025-03-16 | On-Time |  | 2025-03-19 | 2025-03-19 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572111 | T2 EI TRINITY-MAPLE CREEK 9/003 RPL ANCW | 93E
LC | 128312159 | 009/004 | T2 EI TRINITY-MAPLE CREEK 9/4 RPL ANCW | EUREKA | ETL.8170.POLE.WOOD | 2024-03-19 | 2024-03-19 | 2025-03-16 | On-Time |  | 2025-03-19 | 2025-03-19 | 637 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572111 | T2 EI TRINITY-MAPLE CREEK 9/003 RPL ANCW | 93E
LC | 128312183 | 009/003 | T2 EI TRINITY-MAPLE CREEK 9/003 RPR GYWW | EUREKA | ETL.8170.POLE.WOOD | 2024-03-19 | 2024-03-19 | 2024-10-31 | On-Time |  | 2024-09-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46222544 | T2 EI TRINITY-MAPLE CREEK 9/003 RPR GYWW | ICW
LC | 128316138 | 026/003 | T2 EI COALNGA #1-SN MIGUEL 26/03 UNBURY | FRESNO | ETL.8580.TOWR | 2024-03-19 | 2024-03-19 | 2025-01-21 | On-Time |  | 2025-03-19 | 2025-03-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46391141 | T2 EI COALNGA #1-SN MIGUEL 26/03 UNBURY | ICQ
LC | 128316267 | 008/006 | T2 EI HUMBOLDT-MAPLE CREEK 8/6 RPR GYWW | EUREKA | ETL.7130.POLE.NWOD | 2024-03-19 | 2024-03-19 | 2024-03-28 | On-Time |  | 2024-09-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46217268 | T2 EI HUMBOLDT-MAPLE CREEK 8/6 RPR GYWW | ICW
LC | 128317560 | 009/001 | T2 EI HUMBOLDT-MAPLE CREEK 9/1 RPL INSW | EUREKA | ETL.7130.INSL.NCER | 2024-03-19 | 2024-03-19 | 2025-04-03 | Past Due |  | 2025-03-19 | 2025-03-19 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574776 | T2 EI HUMBOLDT-MAPLE CREEK 9/1 RPL INSW | 93I
LC | 128317571 | 003/067 | T2 EI SMRTVLE-NCLUS #2 3/67 RPR GYWW | SACTO | ETL.8000.POLE.NWOD | 2024-03-19 | 2024-03-19 | 2025-02-21 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310354 | T2 EI SMRTVLE-NCLUS #2 3/67 RPR GYWW | ICW
LC | 128320092 | 026/004 | T2 EI COALNGA #1-SN MIGUEL 26/04 COTTER | PISMOBCH | ETL.8580.INSL.CERA | 2024-03-19 | 2024-03-19 | 2025-02-11 | On-Time |  | 2025-03-19 | 2025-03-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329626 | T2 EI COALNGA #1-SN MIGUEL 26/04 COTTER | ICS
LC | 128320605 | 007/048 | T2 EI OLEUM-G #1 7/48 BNT STEEL | CONCORD | ETL.3150.TOWR | 2024-03-19 | 2024-03-19 | 2025-04-18 | Past Due |  | 2025-03-19 | 2025-03-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286571 | T2 EI OLEUM-G #1 7/48 BNT STEEL | ICQ
LC | 128335983 | 008/063 | T2 DI TRINITY-CTTNWD 8/63 TOUCH | TABLEMTN | ETL.4040.POLE.STPS | 2024-03-20 | 2024-03-19 | 2025-02-26 | On-Time |  | 2024-09-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46472108 | T2 DI TRINITY-CTTNWD 8/63 TOUCH | ICW
LC | 128336059 | 078/397 | T2 DI MALIN RND MTN#2 78/397 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-03-20 | 2024-03-19 | 2025-02-09 | On-Time |  | 2025-03-19 | 2025-03-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332457 | T2 DI MALIN RND MTN#2 78/397 RPR OPGW | ICS
LC | 128336253 | 008/010 | T2 DI SALINS FRT ORD#2 8/10 MASTIC | MOSSLNDG | ETL.8423.POLE.NWOD | 2024-03-20 | 2024-03-19 | 2025-03-10 | On-Time |  | 2025-03-19 | 2025-03-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46404410 | T2 DI SALINS FRT ORD#2 8/10 MASTIC | ICQ
LC | 128336256 | 008/010 | T2 DI SALINAS FORT ORD#2 8/10 BNT STEEL | MOSSLNDG | ETL.8423.POLE.NWOD | 2024-03-20 | 2024-03-19 | 2025-05-20 | Past Due |  | 2025-03-19 | 2025-03-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46325953 | T2 DI SALINAS FORT ORD#2 8/10 BNT STEEL | ICQ
LC | 128336385 | 018/429 | T2 DI DRUM-GRS VLY-WMR 18/429 RPR GYWW | SACTO | ETL.6760.POLE.NWOD | 2024-03-20 | 2024-03-19 | 2024-06-28 | On-Time |  | 2024-09-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46217634 | T2 DI DRUM-GRS VLY-WMR 18/429 RPR GYWW | ICW
LC | 128336409 | 019/437 | T2 DI DRUM-GRS VLY-WMR 19/437 RPL INSW | SACTO | ETL.6760.INSL.CERA | 2024-03-20 | 2024-03-19 | 2025-03-11 | On-Time |  | 2025-03-19 | 2025-03-19 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35554350 | T2 DI DRUM-GRS VLY-WMR 19/437 RPL INSW | 93I
LC | 128336437 | 008/064 | T2 DI TRINITY-COTTONWOOD 8/64 RMV DBRS | TABLEMTN | ETL.4040.POLE.STPS | 2024-03-20 | 2024-03-19 | 2025-02-26 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 46332460 | T2 DI TRINITY-COTTONWOOD 8/64 RMV DBRS | ICW
LC | 128353180 | 018/373 | T2 DI COLGATE-PALERMO 18/373 RPL INSW | SACTO | ETL.6500.INSL.NCER | 2024-03-23 | 2024-03-19 | 2024-04-27 | On-Time |  | 2024-09-19 | 2025-03-19 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35540098 | T2 DI COLGATE-PALERMO 18/373 RPL INSW | 93I
LC | 128386619 | 010/217 | T2 DI COTTONWOOD-RB 10/217 RPR STRW | TABLEMTN | ETL.6660.POLE.WOOD | 2024-03-28 | 2024-03-19 | 2025-01-10 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311281 | T2 DI COTTONWOOD-RB 10/217 RPR STRW | ICW
LC | 128387012 | 077/393 | T2 DI MLN-RND MTN #2 77/393 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-03-28 | 2024-03-19 | 2025-02-10 | On-Time |  | 2025-03-19 | 2025-03-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381357 | T2 DI MLN-RND MTN #2 77/393 RPR GYWT | ICQ
LC | 128387066 | 078/398 | T2 DI MLN-RND MTN #2 78/398 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-03-28 | 2024-03-19 | 2025-02-08 | On-Time |  | 2025-03-19 | 2025-03-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332464 | T2 DI MLN-RND MTN #2 78/398 RPR OPGW | ICS
LC | 128387096 | 000/010 | T2 DI VIEJO-MNTRY 000/010 RMV VEG | MOSSLNDG | ETL.8270.POLE.WOOD | 2024-03-28 | 2024-03-19 | 2024-12-17 | On-Time |  | 2025-03-19 | 2025-03-19 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128387098 | 000/010 | T2 DI VIEJO-MNTRY 000/010 RPR ANCW | MOSSLNDG | ETL.8270.POLE.WOOD | 2024-03-28 | 2024-03-19 | 2025-06-09 | Past Due |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46329991 | T2 DI VIEJO-MNTRY 000/010 RPR ANCW | ICW
LC | 128387114 | 000/010 | T2 DI VIEJO-MNTRY 000/010 RPL HRDW | MOSSLNDG | ETL.8270.POLE.WOOD | 2024-03-28 | 2024-03-19 | 2025-06-09 | Past Due |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46329992 | T2 DI VIEJO-MNTRY 000/010 RPL HRDW | ICW
LC | 128387131 | 015/314 | T2 DI COLGATE-PALERMO 15/314 RPL STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-03-28 | 2024-03-19 | 2025-02-06 | On-Time |  | 2025-03-19 | 2025-03-19 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557131 | T2 DI COLGATE-PALERMO 15/314 RPL STRW | 70Y
LC | 128388693 | 000/008 | T2 DI UNION CHMCL TAP 0/008 RMV VEG | CONCORD | ETL.6351.POLE.WOOD | 2024-03-29 | 2024-03-19 | 2024-08-30 | On-Time |  | 2024-09-19 | 2025-03-19 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128388696 | 000/008 | T2 DI UNION CHMCL TAP 0/008 RPR ANCW | CONCORD | ETL.6351.POLE.WOOD | 2024-03-29 | 2024-03-19 | 2024-08-14 | On-Time |  | 2024-09-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46239850 | T2 DI UNION CHMCL TAP 0/008 RPR ANCW | ICW
LC | 128388698 | 55 | T2 DI UNION CHMCL TAP 0/008 RPR SWIW | CONCORD | ETL.6351.SWIT | 2024-03-29 | 2024-03-19 | 2024-11-12 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Switch-Wood | Repair | 46286567 | T2 DI UNION CHMCL TAP 0/008 RPR SWIW | ICW
LC | 128388876 | 015/308 | T2 DI CLGT-PALERMO 15/308 RPR STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-03-29 | 2024-03-19 | 2025-02-05 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46383050 | T2 DI CLGT-PALERMO 15/308 RPR STRW | ICW
LC | 128395219 | 000/001 | T2 DI VIEJO-MONTEREY 0/1 RPR GYWW | MOSSLNDG | ETL.8270.POLE.WOOD | 2024-03-30 | 2024-03-19 | 2024-07-22 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46266149 | T2 DI VIEJO-MONTEREY 0/1 RPR GYWW | ICW
LC | 128395332 | 019/436 | T2 DI DRM-GS VLY-WEMR 19/436 RPL ANCW | SACTO | ETL.6760.POLE.WOOD | 2024-03-30 | 2024-03-19 | 2025-03-11 | On-Time |  | 2025-03-19 | 2025-03-19 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35554349 | T2 DI DRM-GS VLY-WEMR 19/436 RPL ANCW | 93E
LC | 128395342 | 015/301 | T2 DI COLGATE-PALERMO 15/301 RPR CNDW | TABLEMTN | ETL.6500.INSL.CERA | 2024-03-30 | 2024-03-19 | 2025-02-06 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46383051 | T2 DI COLGATE-PALERMO 15/301 RPR CNDW | ICW
LC | 128395497 | 000/008 | T2 VIEJO-MONTEREY 00/08 RPL ANCW | MOSSLNDG | ETL.8270.POLE.WOOD | 2024-03-31 | 2024-03-19 | 2024-03-19 | Past Due |  | 2025-03-19 | 2025-03-19 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35650158 | T2 VIEJO-MONTEREY 00/08 RPL ANCW | 93E
LC | 128395498 | 000/008 | T2 DI VIEJO-MONTEREY 000/008 RPR ANCW | MOSSLNDG | ETL.8270.POLE.WOOD | 2024-03-31 | 2024-03-19 | 2025-06-09 | Past Due |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46329994 | T2 DI VIEJO-MONTEREY 000/008 RPR ANCW | ICW
LC | 128395499 | 000/008 | T2 DI VIEJO-MONTEREY 000/008 RMV VEG | MOSSLNDG | ETL.8270.POLE.WOOD | 2024-03-31 | 2024-03-19 | 2025-01-09 | On-Time |  | 2025-03-19 | 2025-03-19 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128395519 | 000/014 | T2 VIEJO-MONTEREY 000/014 RPL INSW | MOSSLNDG | ETL.8270.INSL.CERA | 2024-03-31 | 2024-03-19 | 2024-03-19 | Past Due |  | 2025-03-19 | 2025-03-19 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573394 | T2 DI VIEJO-MONTEREY 000/014 RPL INSW | 93I
LC | 128395520 | 022/440 | T2 DI CLGT-PALERMO 022/440 RPL STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-03-31 | 2024-03-19 | 2025-02-05 | On-Time |  | 2025-03-19 | 2025-03-19 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557132 | T2 DI CLGT-PALERMO 022/440 RPL STRW | 70Y
LC | 128395526 | 021/424 | T2 DI CLGT-PALERMO 021/424 RPR STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-03-31 | 2024-03-19 | 2025-02-05 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46383052 | T2 DI CLGT-PALERMO 021/424 RPR STRW | ICW
LC | 128395627 | 029/208 | T2 DI TRNTY-CTTNWD 029/208R RPR GYWW | TABLEMTN | ETL.4040.POLE.STPS | 2024-03-31 | 2024-03-19 | 2024-07-19 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46284085 | T2 DI TRNTY-CTTNWD 029/208R RPR GYWW | ICW
LC | 128395643 | 077/394 | T2 DI MLN-RND MTN #2 077/394 RMV VEG | TABLEMTN | ETL.6020.TOWR | 2024-03-31 | 2024-03-19 | 2024-08-13 | On-Time |  | 2025-03-19 | 2025-03-19 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128416338 | 327 | T2 DI TRNTY-CTTNWD 4/36 RPR SWTCH | TABLEMTN | ETL.4040.SWIT | 2024-04-01 | 2024-03-19 | 2025-02-24 | On-Time |  | 2025-03-19 | 2025-03-19 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | Out of Adjustment | Switch | Repair | 46332467 | T2 DI TRNTY-CTTNWD 4/36 RPR SWTCH | ICE
LC | 128416701 | 018/432 | T2 DI DRM-GRS VLY-WMR 18/432 RPR GYWW | SACTO | ETL.6760.POLE.WOOD | 2024-04-01 | 2024-03-19 | 2025-02-26 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324613 | T2 DI DRM-GRS VLY-WMR 18/432 RPR GYWW | ICW
LC | 128430083 | 030/210 | T2 DI TRNTY-CTTNWD 030/210C INSP STRW | TABLEMTN | ETL.4040.POLE.STPS | 2024-04-02 | 2024-03-19 | 2024-09-10 | On-Time |  | 2024-09-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | Overgrown | Structure-Wood | Inspect | 46227625 | T2 DI TRNTY-CTTNWD 030/210C INSP STRW | ICW
LC | 128430089 | 025/178 | T2 DI TRNTY-CTTNWD 025/178R RPR ANCW | TABLEMTN | ETL.4040.POLE.STPS | 2024-04-02 | 2024-03-19 | 2025-02-25 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46332471 | T2 DI TRNTY-CTTNWD 025/178R RPR ANCW | ICW
LC | 128430131 | 025/178 | T2 DI TRNTY-CTTNWD 025/178L RMV VEG | TABLEMTN | ETL.4040.POLE.STPS | 2024-04-02 | 2024-03-19 | 2025-02-14 | On-Time |  | 2025-03-19 | 2025-03-19 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128430133 | 025/178 | T2 DI TRNTY-CTTNWD 025/178L RPR ANCW | TABLEMTN | ETL.4040.POLE.STPS | 2024-04-02 | 2024-03-19 | 2025-02-25 | On-Time |  | 2025-03-19 | 2025-03-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46332472 | T2 DI TRNTY-CTTNWD 025/178L RPR ANCW | ICW
LC | 128323273 | 016/108 | T2 EI NEWARK-LIVERMORE 16/108 RPR ANCW | CONCORD | ETL.7660.POLE.WOOD | 2024-03-20 | 2024-03-20 | 2025-03-11 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD ACCL COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46286741 | T2 EI NEWARK-LIVERMORE 16/108 RPR ANCW | ICW
LC | 128323284 | 004/030 | T2 EI OLEUM-G #2 4/30 COTTER | CONCORD | ETL.3160.INSL | 2024-03-20 | 2024-03-20 | 2025-02-03 | On-Time |  | 2025-03-20 | 2025-03-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46286574 | T2 EI OLEUM-G #2 4/30 COTTER | ICS
LC | 128324170 | 005/101 | T2 EI PLACER-DEL MAR 05/101 RPR HRDW | SACTO | ETL.7800.POLE.WOOD | 2024-03-20 | 2024-03-20 | 2025-02-19 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46323923 | T2 EI PLACER-DEL MAR 05/101 RPR HRDW | ICW
LC | 128324186 | 006/010 | T2 EI TRNTY-MPLE CRK 6/10L RPR GYWW | EUREKA | ETL.8170.POLE.WDPS | 2024-03-20 | 2024-03-20 | 2025-01-24 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345694 | T2 EI TRNTY-MPLE CRK 6/10L RPR GYWW | ICW
LC | 128324350 | 000/007 | T2 EI HMLTN BRNCH-CHSTR 0/7 RPR INSW | TABLEMTN | ETL.7000.INSL.NCER | 2024-03-20 | 2024-03-20 | 2025-03-18 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46311133 | T2 EI HMLTN BRNCH-CHSTR 0/7 RPR INSW | ICW
LC | 128324359 | 009/049 | T2 EI CONTR COST-MORGA#1 9/49 RPR STRT | CONCORD | ETL.5452.TOWR | 2024-03-20 | 2024-03-20 | 2025-01-19 | On-Time |  | 2025-03-20 | 2025-03-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286578 | T2NT EI CONTR COST-MORGA#1 9/49 RPR STRT | ICQ
LC | 128324455 | 015/309 | T2 EI CARIBOU-WESTWOOD 015/309 COMPLETE | TABLEMTN | ETL.6300.POLE.NWOD | 2024-03-20 | 2024-03-20 | 2024-07-29 | On-Time |  | 2024-09-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46233796 | T2 EI CARIBOU-WESTWOOD 015/309 RPR GYWW | ICW
LC | 128324456 | 015/309 | T2 EI CARIBOU-WESTWOOD 015/309 RPL ANCW | TABLEMTN | ETL.6300.POLE.NWOD | 2024-03-20 | 2024-03-20 | 2024-07-29 | On-Time |  | 2025-03-20 | 2025-03-20 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35545653 | T2 EI CARIBOU-WESTWOOD 015/309 RPL ANCW | 93E
LC | 128324573 | 013/103 | T2 EI PIT #3-PIT #1 013/103 RPR STRT | TABLEMTN | ETL.5400.TOWR | 2024-03-20 | 2024-03-20 | 2025-02-10 | On-Time |  | 2025-03-20 | 2025-03-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381959 | T2NT EI PIT #3-PIT #1 013/103 RPR STRT | ICQ
LC | 128324577 | 004/029 | T2 EI OLEUM-G #2 4/29 RPR CNDS | CONCORD | ETL.3160.INSL.CERA | 2024-03-20 | 2024-03-20 | 2025-04-12 | Past Due |  | 2025-03-20 | 2025-03-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH RTNR FMOB TR2 PRTO | No Good/Out of Stdrd | Conductor-Steel | Repair | 46286570 | T2 EI OLEUM-G #2 4/29 RPR CNDS | ICS
LC | 128324616 | 002/059 | T2 EI WEIMAR-HALSEY 2/59 RMV VEG | SACTO | ETL.8340.POLE.WOOD | 2024-03-20 | 2024-03-20 | 2025-02-15 | On-Time |  | 2025-03-20 | 2025-03-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128324618 | 002/059 | T2 EI WEIMAR-HALSEY 2/59 RPL POLE | SACTO | ETL.8340.POLE.WOOD | 2024-03-20 | 2024-03-20 | 2025-03-08 | On-Time |  | 2025-03-20 | 2025-03-20 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35571833 | T2 EI WEIMAR-HALSEY 2/049 RPL STRW | 70Y
LC | 128324653 | 003/066 | T2 EI SMRTVLE-NCLUS #1 3/66 RPR STRW | SACTO | ETL.7990.POLE.WOOD | 2024-03-20 | 2024-03-20 | 2025-02-12 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310356 | T2 EI SMRTVLE-NCLUS #1 3/66 RPR STRW | ICW
LC | 128324768 | 004/028 | T2 EI OLEUM-G #1 4/28 COMPLETE | CONCORD | ETL.3150.TOWR | 2024-03-20 | 2024-03-20 | 2025-03-14 | On-Time |  | 2025-03-20 | 2025-03-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46303556 | T2 EI OLEUM-G #1 4/28 COMPLETE | ICQ
LC | 128324847 | 006/010 | T2 EI TRNTY-MPLE CRK 6/10C RPR GYWW | EUREKA | ETL.8170.POLE.WDPS | 2024-03-20 | 2024-03-20 | 2025-01-24 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345692 | T2 EI TRNTY-MPLE CRK 6/10C RPR GYWW | ICW
LC | 128324848 | 006/010 | T2 EI TRNTY-MPLE CRK 6/10R RPR GYWW | EUREKA | ETL.8170.POLE.WDPS | 2024-03-20 | 2024-03-20 | 2025-01-24 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345693 | T2 EI TRNTY-MPLE CRK 6/10R RPR GYWW | ICW
LC | 128324961 | 004/008 | T2 EI POTTER VALLEY-WLITS 4/8 REGR STRW | WILLITS | ETL.7820.POLE.NWOD | 2024-03-20 | 2024-03-20 | 2025-02-22 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46305769 | T2 EI POTTER VALLEY-WLITS 4/8 REGR STRW | ICW
LC | 128325058 | 011/005 | T2 EI TRINITY-MAPLE CRK 011/005 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-03-20 | 2024-03-20 | 2024-11-01 | On-Time |  | 2024-09-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46219740 | T2 EI TRINITY-MAPLE CRK 011/005 RPR GYWW | ICW
LC | 128325520 | 011/006 | T2 EI TRINITY-MAPLE CRK 11/6 RPL ANCW | EUREKA | ETL.8170.POLE.NWOD | 2024-03-20 | 2024-03-20 | 2025-03-20 | On-Time |  | 2025-03-20 | 2025-03-20 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572109 | T2 EI TRINITY-MAPLE CRK 11/006 RPL ANCW | 93E
LC | 128325715 | 002/049 | T2 EI WEIMAR-HALSEY 2/049 RPL STRW | SACTO | ETL.8340.POLE.WOOD | 2024-03-20 | 2024-03-20 | 2025-03-08 | On-Time |  | 2025-03-20 | 2025-03-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35571833 | T2 EI WEIMAR-HALSEY 2/049 RPL STRW | 70Y
LC | 128325916 | 002/050 | T2 EI WEIMAR-HALSEY 2/050 RPL STRW | SACTO | ETL.8340.POLE.WOOD | 2024-03-20 | 2024-03-20 | 2025-03-08 | On-Time |  | 2025-03-20 | 2025-03-20 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35571833 | T2 EI WEIMAR-HALSEY 2/049 RPL STRW | 70Y
LC | 128326001 | 015/078 | T2 EI VACA-PARKWAY 015/078 TOUCH | SACTO | ETL.5850.TOWR | 2024-03-20 | 2024-03-20 | 2025-02-28 | On-Time |  | 2024-06-20 | 2025-03-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46460820 | T2 EI VACA-PARKWAY 015/078 RPR STRT | ICQ
LC | 128326177 | 000/001 | T2 EI MALACHA TAP 000/001 COTTER | TABLEMTN | ETL.5910.INSL.CERA | 2024-03-20 | 2024-03-20 | 2025-02-17 | On-Time |  | 2025-03-20 | 2025-03-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46332455 | T2 EI MALACHA TAP 000/001 COTTER | ICS
LC | 128326272 | 004/000 | T2 EI POTTER VALLEY-WILLITS 4/0 RPR GYWW | WILLITS | ETL.7820.POLE.NWOD | 2024-03-20 | 2024-03-20 | 2025-02-22 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305768 | T2 EI POTTER VALLEY-WILLITS 4/0 RPR GYWW | ICW
LC | 128326315 | 011/004 | T2 EI TRINITY-MAPLE CRK 11/4 RPL STRW | EUREKA | ETL.8170.POLE.WOOD | 2024-03-20 | 2024-03-20 | 2025-03-20 | On-Time |  | 2025-03-20 | 2025-03-20 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572110 | T2 EI TRINITY-MAPLE CRK 011/002 RPL POLE | 70Y
LC | 128331746 | 002/069 | T2 VOLTA-SOUTH 002/069 RPL SPLW | TABLEMTN | ETL.8300.INSL.NCER | 2024-03-20 | 2024-03-20 | 2025-01-13 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Splice-Wood | Replace | 46311136 | T2 VOLTA-SOUTH 002/069 RPL SPLW | ICW
LC | 128332240 | 008/058 | T2 EI MRAGA-SN LENDRO #3 8/58 RPL DMPS | CONCORD | ETL.2790.INSL | 2024-03-20 | 2024-03-20 | 2025-03-20 | On-Time |  | 2025-03-20 | 2025-03-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Damper-Steel | Replace | 46286577 | T2 EI MRAGA-SN LENDRO #3 8/58 RPL DMPS | ICS
LC | 128334062 | 016/097 | T2 EI NEWARK-LIVERMORE 16/097 RPL STRW | CONCORD | ETL.7660.POLE.WOOD | 2024-03-20 | 2024-03-20 | 2025-04-30 | Past Due |  | 2025-03-20 | 2025-03-20 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35622745 | T2 EI NEWARK-LIVERMORE 16/097 RPL STRW | 70Y
LC | 128334315 | 003/024 | T2 EI OLEUM-G #1 3/24 RPR INSS | CONCORD | ETL.3150.INSL.CERA | 2024-03-20 | 2024-03-20 | 2024-03-20 | Past Due |  | 2025-03-20 | 2025-03-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46539533 | T2 EI OLEUM-G #1 3/24 RPR INSS | ICS
LC | 128334316 | 003/024 | T2 OLEUM-G #2 3/24 RPR INSS | CONCORD | ETL.3160.INSL.CERA | 2024-03-20 | 2024-03-20 | 2025-03-11 | On-Time |  | 2025-03-20 | 2025-03-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297787 | T2 EI OLEUM-G #2 3/24 RPR INSS | ICS
LC | 128335280 | 001/033 | T2 EI PINE GROVE TAP 1/33 RPL TIED | VICTOR | ETL.8351.INSL.CERA | 2024-03-20 | 2024-03-20 | 2024-08-13 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD NOAC SPCR CLR ACCL COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Tie Wire-Wood | Replace | 46229389 | T2 EI PINE GROVE TAP 1/33 RPL TIED | ICW
LC | 128335287 | 004/097 | T2 EI PLACER-DEL MAR 04/097 RPL STRW | SACTO | ETL.7800.POLE.WOOD | 2024-03-20 | 2024-03-20 | 2025-02-19 | On-Time |  | 2025-03-20 | 2025-03-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP CLR ACCM FLAG COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573271 | T2 EI PLACER-DEL MAR 04/097 RPL STRW | 70Y
LC | 128335422 | 003/005 | T2 EI POTTR VLY-WILLTS 03/05 RPR ROAD | WILLITS | ETL.7820.POLE.NWOD | 2024-03-20 | 2024-03-20 | 2024-04-02 | On-Time |  | 2025-03-20 | 2025-03-20 | 932 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Road | Repair | 46216983 | T2 EI POTTR VLY-WILLTS 03/05 RPR ROAD | CHS
LC | 128335594 | 002/049 | T2 EI SMRTVLE-NCLUS #1 2/49 RPR JUMW | SACTO | ETL.7990.INSL.CERA | 2024-03-20 | 2024-03-20 | 2024-08-27 | On-Time |  | 2024-06-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46239900 | T2 EI SMRTVLE-NCLUS #1 2/49 RPR JUMW | ICW
LC | 128335595 | 002/049 | T2 EI SMRTVLE-NCLUS #1 2/49 RPR GYWW | SACTO | ETL.7990.POLE.WOOD | 2024-03-20 | 2024-03-20 | 2024-08-27 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305805 | T2 EI SMRTVLE-NCLUS #1 2/49 RPR GYWW | ICW
LC | 128335597 | 002/050 | T2 EI SMRTVLE-NCLUS #1 2/50 GRND WASH | SACTO | ETL.7990.INSL.NCER | 2024-03-20 | 2024-03-20 | 2025-03-07 | On-Time |  | 2025-03-20 | 2025-03-20 | 622 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | Contaminated | Insulator | Ground Wash | 46310368 | T2 EI SMRTVLE-NCLUS #1 2/50 GRND WASH | ICD
LC | 128335604 | 002/051 | T2 EI SMRTVLE-NCLUS #1 2/51 RPR INSW | SACTO | ETL.7990.INSL.CERA | 2024-03-20 | 2024-03-20 | 2025-03-07 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310355 | T2 EI SMRTVLE-NCLUS #1 2/51 RPR INSW | ICW
LC | 128335618 | 005/001 | T2 EI HUMBOLDT-MAPLE CREEK 5/01 RPR GYWW | EUREKA | ETL.7130.POLE.NWOD | 2024-03-20 | 2024-03-20 | 2024-05-16 | On-Time |  | 2024-09-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46218715 | T2 EI HUMBOLDT-MAPLE CREEK 5/01 RPR GYWW | ICW
LC | 128335652 | 001/033 | T2 EI WEIMAR-HALSEY 1/33 COMPLETE | SACTO | ETL.8340.POLE.WOOD | 2024-03-20 | 2024-03-20 | 2025-03-09 | On-Time |  | 2025-03-20 | 2025-03-20 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35571832 | T2 EI WEIMAR-HALSEY 1/31 RPL STRW | 70Y
LC | 128335801 | 024/161 | T2 IR POE RIO OSO 24/161 RPL INSS | TABLEMTN | ETL.5540.INSL.CERA | 2024-03-20 | 2024-03-20 | 2024-04-24 | On-Time |  | 2024-06-20 | 2025-03-20 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW IR FIRE COMP OH TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35540684 | T2 IR POE RIO OSO 24/161 RPL INSS | 93K
LC | 128335919 | 024/004 | T2 EI COALNGA #1-SN MIGL 24/04 BNT STEEL | FRESNO | ETL.8580.TOWR | 2024-03-20 | 2024-03-20 | 2025-03-21 | Past Due |  | 2025-03-20 | 2025-03-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46292634 | T2 EI COALNGA #1-SN MIGL 24/04 BNT STEEL | ICQ
LC | 128335936 | 009/090 | T2 DI COTTONWD-BENTON#2 9/90 COTTER | TABLEMTN | ETL.6650.INSL.NCER | 2024-03-20 | 2024-03-20 | 2024-04-22 | On-Time |  | 2024-06-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46218246 | T2 DI COTTONWD-BENTON#2 9/90 COTTER | ICW
LC | 128335938 | 009/090 | T2 DI COTTONWD-BENTON#2 9/90L RPL ANCW | TABLEMTN | ETL.6650.POLE.WDPS | 2024-03-20 | 2024-03-20 | 2025-03-18 | On-Time |  | 2025-03-20 | 2025-03-20 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35614902 | T2 DI COTTONWD-BENTON#2 9/90L RPL ANCW | 93E
LC | 128335949 | 006/051 | T2 EI PLACER-GOLD HILL #1 6/51 RPR FOND | SACTO | ETL.3340.TOWR | 2024-03-20 | 2024-03-20 | 2025-01-02 | On-Time |  | 2025-03-20 | 2025-03-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46327682 | T2 EI PLACER-GOLD HILL #1 6/51 RPR FOND | ICQ
LC | 128335951 | 025/000 | T2 EI COALNGA #1-SN MIGUEL 25/0 UNBURY | FRESNO | ETL.8580.TOWR | 2024-03-20 | 2024-03-20 | 2025-01-21 | On-Time |  | 2025-03-20 | 2025-03-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46230801 | T2 EI COALNGA #1-SN MIGUEL 25/0 UNBURY | ICQ
LC | 128336064 | 044/211 | T2 GNACIO-SOBRANTE 44/211 RPL SPCR | CONCORD | ETL.4920.INSL.NCER | 2024-03-20 | 2024-03-20 | 2024-03-20 | Past Due |  | 2025-03-20 | 2025-03-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Spacer-Steel | Replace | 46403452 | T2 EI GNACIO-SOBRANTE 44/211 RPL SPCR | ICS
LC | 128336078 | 003/062 | T2 EI OLEMAN-COTTONWOOD 03/062 RPR STRW | TABLEMTN | ETL.6430.POLE.WOOD | 2024-03-20 | 2024-03-20 | 2025-03-04 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46332458 | T2 EI OLEMAN-COTTONWOOD 03/062 RPR STRW | ICW
LC | 128336092 | 003/063 | T2 EI COLEMAN-COTTONWOOD 03/063 RPR STRW | TABLEMTN | ETL.6430.POLE.WOOD | 2024-03-20 | 2024-03-20 | 2025-03-04 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46332459 | T2 EI COLEMAN-COTTONWOOD 03/063 RPR STRW | ICW
LC | 128336093 | 003/076 | T2 EI COLEMAN-CTTNWD 3/76L RPR STRW | TABLEMTN | ETL.6430.POLE.WDPS | 2024-03-20 | 2024-03-20 | 2024-03-20 | Past Due |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46498599 | T2 EI COLEMAN-CTTNWD 3/76L RPR STRW | ICW
LC | 128336434 | 110/008 | T2 DI HUMBOLDT-BRDGVL 110/8 RPR ADSS | EUREKA | ETL.1810.POLE.STPS | 2024-03-20 | 2024-03-20 | 2024-03-28 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46217267 | T2 DI HUMBOLDT-BRDGVL 110/8 RPR ADSS | ICW
LC | 128336836 | 011/002 | T2 EI TRINITY-MAPLE CRK 011/002 RPL POLE | EUREKA | ETL.8170.POLE.WOOD | 2024-03-21 | 2024-03-20 | 2025-03-23 | Past Due |  | 2025-03-20 | 2025-03-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572110 | T2 EI TRINITY-MAPLE CRK 011/002 RPL POLE | 70Y
LC | 128353187 | 110/002B | T2 DI HUMBOLDT-TRINITY 110/2B RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-03-23 | 2024-03-20 | 2025-03-09 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345699 | T2 DI HUMBOLDT-TRINITY 110/2B RPR GYWW | ICW
LC | 128353188 | 110/002C | T2 DI HUMBOLDT-TRINITY 110/2C RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-03-23 | 2024-03-20 | 2025-03-09 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345700 | T2 DI HUMBOLDT-TRINITY 110/2C RPR GYWW | ICW
LC | 128353277 | 110/002A | T2 DI HUMBOLDT-TRINITY 110/2A RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-03-23 | 2024-03-20 | 2025-03-09 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345698 | T2 DI HUMBOLDT-TRINITY 110/2A RPR GYWW | ICW
LC | 128366220 | 109/000 | T2 DI HMBLDT BRDGVIL 109/000 RPR ANCW | EUREKA | ETL.1810.POLE.WDPS | 2024-03-25 | 2024-03-20 | 2025-03-07 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46345696 | T2 DI HMBLDT BRDGVIL 109/000 RPR ANCW | ICW
LC | 128366221 | 109/000 | T2 DI HMBLDT BRDGVIL 109/000 RPR ADSS | EUREKA | ETL.1810.POLE.WDPS | 2024-03-25 | 2024-03-20 | 2025-03-07 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | ADSS - Wood | Repair | 46345697 | T2 DI HMBLDT BRDGVIL 109/000 RPR ADSS | ICW
LC | 128389157 | 001/011 | T2 DI TRNTY-CTTNWD 001/011L TOUCH | TABLEMTN | ETL.4040.POLE.STPS | 2024-03-29 | 2024-03-20 | 2025-02-24 | On-Time |  | 2024-09-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46472104 | T2 DI TRNTY-CTTNWD 001/011L TOUCH | ICW
LC | 128393608 | 030/209 | T2 DI TRINITY-CTTNWD 030/209L RPR ANCW | TABLEMTN | ETL.4040.POLE.STPS | 2024-03-29 | 2024-03-20 | 2025-02-25 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46332465 | T2 DI TRINITY-CTTNWD 030/209L RPR ANCW | ICW
LC | 128393796 | 031/214 | T2 DI TRINITY-CTTNWD 031/214R RPR ANCW | TABLEMTN | ETL.4040.POLE.STPS | 2024-03-29 | 2024-03-20 | 2024-07-19 | On-Time |  | 2024-09-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46227626 | T2 DI TRINITY-CTTNWD 031/214R RPR ANCW | ICW
LC | 128394090 | 003/006 | T2 DI LWR LK-HMSTK 003/006 RPR IBWW | WILLITS | ETL.1481.INSL.CERA | 2024-03-29 | 2024-03-20 | 2025-03-18 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46333920 | T2 DI LWR LK-HMSTK 003/006 RPR IBWW | ICW
LC | 128394316 | 008/198 | T2 DI CTTNWD-BNTN #1 008/198 RPR STRW | TABLEMTN | ETL.6640.POLE.WOOD | 2024-03-29 | 2024-03-20 | 2024-12-04 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Structure-Wood | Repair | 46332466 | T2 DI CTTNWD-BNTN #1 008/198 RPR STRW | ICW
LC | 128394364 | 008/196 | T2 DI CTTNWD-BNTN #1 008/196 RPL INSW | TABLEMTN | ETL.6640.INSL.NCER | 2024-03-29 | 2024-03-20 | 2025-06-02 | Past Due |  | 2025-03-20 | 2025-03-20 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35557463 | T2 DI CTTNWD-BNTN #1 008/196 RPL INSW | 93I
LC | 128395259 | 003/020 | T2 DI PITTSBURG-CLYTN #3 3/20 RPL INSS | CONCORD | ETL.3290.INSL | 2024-03-30 | 2024-03-20 | 2024-03-20 | Past Due |  | 2025-03-20 | 2025-03-20 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575004 | T2 DI PITTSBURG-CLYTN #3 3/20 RPL INSS | 93K
LC | 128395547 | 008/187 | T2 DI HMLTN BRNCH-CHSTR 8/187 RPL STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-03-31 | 2024-03-20 | 2025-03-22 | Past Due |  | 2025-03-20 | 2025-03-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574584 | T2 DI HMLTN BRNCH-CHSTR 8/187 RPL STRW | 70Y
LC | 128395553 | 108/005 | T2 DI HMBLDT-TRNTY 108/005 RPR INSW | EUREKA | ETL.1820.INSL.NCER | 2024-03-31 | 2024-03-20 | 2025-03-07 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46345695 | T2 DI HMBLDT-TRNTY 108/005 RPR INSW | ICW
LC | 128395604 | 017/249B | T2 DI CLAY-MARTEL 017/249B RPR JUMS | VICTOR | ETL.8250.INSL.NCER | 2024-03-31 | 2024-03-20 | 2025-04-12 | Past Due |  | 2025-03-20 | 2025-03-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46326980 | +T2 DI CLAY-MARTEL 017/249B RPR JUMS | ICS
LC | 128416012 | 110/007 | T2 HMBLDT-BRDGVL 110/7L RPL HRDW | EUREKA | ETL.1810.POLE.STPS | 2024-04-01 | 2024-03-20 | 2024-03-20 | Past Due |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345701 | T2 DI HMBLDT-BRDGVL 110/7L RPL HRDW | ICW
LC | 128416015 | 110/007 | T2 DI HMBLDT-BRDGVL 110/7R RPR ADSS | EUREKA | ETL.1810.POLE.STPS | 2024-04-01 | 2024-03-20 | 2025-03-10 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | ADSS - Wood | Repair | 46345702 | T2 DI HMBLDT-BRDGVL 110/7R RPR ADSS | ICW
LC | 128416273 | 005/026 | T2 DI PITTSBURG-EASTSHORE 5/26 COTTER | CONCORD | ETL.5462.INSL.NCER | 2024-04-01 | 2024-03-20 | 2025-01-21 | On-Time |  | 2025-03-20 | 2025-03-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46286575 | T2 DI PITTSBURG-EASTSHORE 5/26 COTTER | ICS
LC | 128429456 | 110/005 | T2 HUMBOLDTD-BRGVL 110/5 RPR ADSS | EUREKA | ETL.1810.POLE.STPS | 2024-04-02 | 2024-03-20 | 2024-03-20 | Past Due |  | 2024-06-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46221927 | T2 DI HUMBOLDTD-BRGVL 110/5L RPR ADSS | ICW
LC | 128429935 | 035/155 | T2 DI MOSS LANDING-LB 35/155 RPR SHLS | MOSSLNDG | ETL.6040.TOWR | 2024-04-02 | 2024-03-20 | 2025-02-28 | On-Time |  | 2025-03-20 | 2025-03-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46305514 | T2 DI MOSS LANDING-LB 35/155 RPR SHLS | ICS
LC | 128430156 | 035/153 | T2 DI MSS LNDG-LOS BNS 035/153 RPR SHLS | MOSSLNDG | ETL.6040.TOWR | 2024-04-02 | 2024-03-20 | 2025-03-11 | On-Time |  | 2025-03-20 | 2025-03-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46305512 | T2 DI MSS LNDG-LOS BNS 035/153 RPR SHLS | ICS
LC | 128430356 | 009/231 | T2 DI CTTNWD-BNTN #1 009/231 INSP ANCW | TABLEMTN | ETL.6640.POLE.WOOD | 2024-04-02 | 2024-03-20 | 2024-10-10 | On-Time |  | 2024-09-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46237025 | T2 DI CTTNWD-BNTN #1 009/231 RPR ANCW | ICW
LC | 128430359 | 009/231 | T2 DI CTTNWD-BNTN #1 009/231 RMV VEG | TABLEMTN | ETL.6640.POLE.WOOD | 2024-04-02 | 2024-03-20 | 2024-11-20 | On-Time |  | 2024-09-20 | 2025-03-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128444910 | 031/214 | T2 DI TRINITY-CTTNWD 031/214C RPR ANCW | TABLEMTN | ETL.4040.POLE.STPS | 2024-04-04 | 2024-03-20 | 2024-07-19 | On-Time |  | 2024-09-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46230770 | T2 DI TRINITY-CTTNWD 031/214C RPR ANCW | ICW
LC | 128450488 | 031/214 | T2 DI TRINITY-CTTNWD 031/214R RPR ANCW | TABLEMTN | ETL.4040.POLE.STPS | 2024-04-04 | 2024-03-20 | 2024-07-19 | On-Time |  | 2024-09-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46230769 | T2 DI TRINITY-CTTNWD 031/214R RPR ANCW | ICW
LC | 128471074 | 030/209 | T2 DI TRINITY-CTTNWD 030/209R RPR ANCW | TABLEMTN | ETL.4040.POLE.STPS | 2024-04-08 | 2024-03-20 | 2025-02-25 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46332485 | T2 DI TRINITY-CTTNWD 030/209R RPR ANCW | ICW
LC | 128471078 | 030/209 | T2 DI TRINITY-CTTNWD 030/209C RPR ANCW | TABLEMTN | ETL.4040.POLE.STPS | 2024-04-08 | 2024-03-20 | 2025-02-25 | On-Time |  | 2025-03-20 | 2025-03-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46332486 | T2 DI TRINITY-CTTNWD 030/209C RPR ANCW | ICW
LC | 129562970 | 012/007 | T3 WV MONTE RIO-FULTON 012/007 RPL STRW | LAKEVLLE | ETL.7630.POLE.WOOD | 2024-09-20 | 2024-09-20 | 2025-06-05 | Past Due |  | 2025-03-20 | 2025-03-20 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35586175 | T3 WV MONTE RIO-FULTON 012/007 RPL STRW | 70Y
LC | 123162228 | 004/023 | T3NT EI RND MTN-TBL MTN #1 4/23 BNT STL | TABLEMTN | ETL.6060.POLE.NWOD | 2022-03-21 | 2022-03-21 | 2023-08-20 | On-Time |  | 2025-03-21 | 2025-03-21 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644378 | T3 EI RND MTN-TBLE MTN #1 4/23 BNT STEEL | ICQ
LC | 123162451 | 004/024 | T3NT EI RND MTN-TBL MTN #1 4/24 BNT STL | TABLEMTN | ETL.6060.TOWR | 2022-03-21 | 2022-03-21 | 2023-08-19 | On-Time |  | 2025-03-21 | 2025-03-21 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644402 | T3 EI ROND MTN-TBL MTN #1 4/24 BNT STEEL | ICQ
LC | 123196516 | :010/065 | T2NT DI GREEN VLY-LLGS :10/65 BNT STEEL | MOSSLNDG | ETL.1720.TOWR | 2022-03-26 | 2022-03-21 | 2023-06-14 | On-Time |  | 2025-03-21 | 2025-03-21 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45590495 | T2 DI GREEN VALY-LLAGAS :10/65 BNT STEEL | ICQ
LC | 123196632 | 000/005 | T3NT DI MRAGA-SN LNDR #1 0/5 BENT STEEL | CONCORD | ETL.2770.TOWR | 2022-03-26 | 2022-03-21 | 2023-03-27 | On-Time |  | 2025-03-21 | 2025-03-21 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45682455 | T3 DI MORAGA-SN LNDRO #1 0/5 BENT STEEL | ICQ
LC | 123223071 | B003/000 | T3NT DI FLTN CLSTG 3/0 COMPLETE | LAKEVLLE | ETL.6880.POLE.NWOD | 2022-03-31 | 2022-03-21 | 2023-04-25 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 45575461 | T3 DI FLTN CLSTG 3/0 REFILL HOLE | ICW
LC | 128336901 | 006/115 | T2 EI CORDELIA #2 TAP 006/115 INS HRDW | SACTO | ETL.8184.POLE.NWOD | 2024-03-21 | 2024-03-21 | 2025-02-03 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB PGEQ | Missing | Hardware-Wood | Install | 46337395 | T2 EI CORDELIA #2 TAP 006/115 INS HRDW | ICW
LC | 128337444 | 014/003 | T2 EI PHILO JCT-ELK 14/003 RPR STRW | WILLITS | ETL.7780.POLE.WOOD | 2024-03-21 | 2024-03-21 | 2025-03-19 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46333924 | T2 EI PHILO JCT-ELK 14/003 RPR STRW | ICW
LC | 128337457 | 018/082 | T2 EI MORRO BAY-MESA 18/082 RPR FOND | PISMOBCH | ETL.5290.TOWR | 2024-03-21 | 2024-03-21 | 2025-03-11 | On-Time |  | 2025-03-21 | 2025-03-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46476027 | T2 EI MORRO BAY-MESA 18/082 RPR FOND | ICQ
LC | 128337476 | 006/002 | T2 EI HUMBOLDT-MAPLE CRK 6/2L GO95 RPL | EUREKA | ETL.7130.POLE.WDPS | 2024-03-21 | 2024-03-21 | 2025-05-25 | Past Due |  | 2025-03-21 | 2025-03-21 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 31654782 | T2 HUMBOLDT-MAPLE CREEK 6/001 GO95 | 93G
LC | 128337533 | 004/086 | T2 EI PLACER-DEL MAR 4/86 RPL STRW | SACTO | ETL.7800.POLE.NWOD | 2024-03-21 | 2024-03-21 | 2025-02-18 | On-Time |  | 2025-03-21 | 2025-03-21 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573270 | T2 EI PLACER-DEL MAR 4/86 RPL STRW | 70Y
LC | 128337573 | 004/086 | T2 EI PLACER-DEL MAR 4/86 TOUCH | SACTO | ETL.7800.POLE.NWOD | 2024-03-21 | 2024-03-21 | 2025-03-31 | Past Due |  | 2024-09-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46460019 | T2 EI PLACER-DEL MAR 4/86 RPR STRW | ICW
LC | 128337615 | 007/043 | T2 EI VACA-PARKWAY 007/043 RPR INSS | SACTO | ETL.5850.INSL.NCER | 2024-03-21 | 2024-03-21 | 2025-01-24 | On-Time |  | 2025-03-21 | 2025-03-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46324630 | T2 EI VACA-PARKWAY 007/043 RPR INSS | ICS
LC | 128337689 | 005/005 | T2 EI POTTER VLY-MENDOCNO 5/5 RPR STRT | WILLITS | ETL.7810.POLE.NWOD | 2024-03-21 | 2024-03-21 | 2025-03-17 | On-Time |  | 2025-03-21 | 2025-03-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46290176 | T2 EI POTTER VLY-MENDOCNO 5/5 RPR STRT | ICQ
LC | 128337707 | 018/081 | T2 EI MORRO BAY-MESA 18/81 RPL INSS | PISMOBCH | ETL.5290.INSL | 2024-03-21 | 2024-03-21 | 2025-03-17 | On-Time |  | 2024-09-21 | 2025-03-21 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35556422 | T2 EI MORRO BAY-MESA 18/81 RPL INSS | 93K
LC | 128338303 | 006/002 | T2 EI HUMBOLDT-MAPLE CRK 6/2R GO95 RPL | EUREKA | ETL.7130.POLE.WDPS | 2024-03-21 | 2024-03-21 | 2025-05-25 | Past Due |  | 2025-03-21 | 2025-03-21 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 31654782 | T2 HUMBOLDT-MAPLE CREEK 6/001 GO95 | 93G
LC | 128338309 | 003/002 | T2 PTR VLEY-WILLITS 3/2 RPL PL | WILLITS | ETL.7820.POLE.WOOD | 2024-03-21 | 2024-03-21 | 2024-03-21 | Past Due |  | 2025-03-21 | 2025-03-21 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574324 | T2 EI PTR VLEY-WILLITS 3/2 RPL PL | 70Y
LC | 128338349 | 006/000 | T2 EI POTTER VALLEY-MNDCNO 6/0 RPR HRDT | WILLITS | ETL.7810.POLE.NWOD | 2024-03-21 | 2024-03-21 | 2025-03-18 | On-Time |  | 2025-03-21 | 2025-03-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Hardware-Tower | Install | 46290211 | T2 EI POTTER VALLEY-MNDCNO 6/0 RPR HRDT | ICQ
LC | 128338350 | 018/095 | T2 VACA-BAHIA 18/95 RPL INSS | SACTO | ETL.5810.INSL | 2024-03-21 | 2024-03-21 | 2024-11-16 | On-Time |  | 2025-03-21 | 2025-03-21 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35540126 | T2 VACA-BAHIA 18/95 RPL INSS | 93K
LC | 128338357 | 029/139 | T2 EI MNDCINO-REDBUD 29/139 RPR INSS | WILLITS | ETL.2410.INSL.CERA | 2024-03-21 | 2024-03-21 | 2025-03-19 | On-Time |  | 2025-03-21 | 2025-03-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46414247 | T2 EI MNDCINO-REDBUD 29/139 RPR INSS | ICS
LC | 128338400 | 006/000 | T2 EI POTTER VALLEY-MNDCNO 6/0 RPR GYWT | WILLITS | ETL.7810.POLE.NWOD | 2024-03-21 | 2024-03-21 | 2024-04-08 | On-Time |  | 2024-09-21 | 2025-03-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46221882 | T2 EI POTTER VALLEY-MNDCNO 6/0 RPR GYWT | ICQ
LC | 128342025 | 016/067 | T2 EI DIABLO-MIDWAY #3 16/67 RMV BRUSH | PISMOBCH | ETL.5980.TOWR | 2024-03-21 | 2024-03-21 | 2024-10-11 | On-Time |  | 2025-03-21 | 2025-03-21 | 932 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Brush Fuel | Road | Remove | 45192143 | T3NT DIABLO-MIDWAY #3 006/023 RPR ROAD | CHS
LC | 128342232 | 000/001 | T2 WV COLEMAN-RED BLUFF 0/001 RPR INSW | TABLEMTN | ETL.6440.INSL.NCER | 2024-03-21 | 2024-03-21 | 2025-04-21 | Past Due |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46332461 | T2 WV COLEMAN-RED BLUFF 0/001 RPR INSW | ICW
LC | 128342243 | 019/397 | T2 CARIBOU-WESTWOOD 019/397 GO95 | TABLEMTN | ETL.6300.POLE.WOOD | 2024-03-21 | 2024-03-21 | 2025-02-14 | On-Time |  | 2025-03-21 | 2025-03-21 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35539057 | T2 CARIBOU-WESTWOOD 019/397 GO95 | 93G
LC | 128342263 | 001/012 | T2 EI OLEUM-G #1 1/12 RPR FOND | CONCORD | ETL.3150.TOWR | 2024-03-21 | 2024-03-21 | 2025-02-10 | On-Time |  | 2025-03-21 | 2025-03-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46286742 | T2 EI OLEUM-G #1 1/12 RPR FOND | ICQ
LC | 128342364 | 003/000 | T2 EI PTR VLEY-WLTS 03/0 RPR ANCW | WILLITS | ETL.7820.POLE.NWOD | 2024-03-21 | 2024-03-21 | 2025-02-22 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46305773 | T2 EI PTR VLEY-WLTS 03/0 RPR ANCW | ICW
LC | 128342476 | 022/009 | T2 WV FORT BRAGG-ELK 22/009 INS DMPW | WILLITS | ETL.2060.INSL.NCER | 2024-03-21 | 2024-03-21 | 2025-02-27 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46305774 | T2 WV FORT BRAGG-ELK 22/009 INS DMPW | ICW
LC | 128342509 | 002/065 | T2 EI WEIMAR-HALSEY 2/65 RPL POLE | SACTO | ETL.8340.POLE.WOOD | 2024-03-21 | 2024-03-21 | 2025-03-07 | On-Time |  | 2025-03-21 | 2025-03-21 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP RESD REMT SWRK CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35571833 | T2 EI WEIMAR-HALSEY 2/049 RPL STRW | 70Y
LC | 128342845 | 000/011 | T2 EI COLGATE-GRASS VALEY 00/011 COA | SACTO | ETL.6490.POLE.NWOD | 2024-03-21 | 2024-03-21 | 2025-02-11 | On-Time |  | 2025-03-21 | 2025-03-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128343207 | 018/071 | T2 EI DIABLO-MIDWAY #3 18/071 RMV VEG | PISMOBCH | ETL.5980.TOWR | 2024-03-21 | 2024-03-21 | 2025-03-20 | On-Time |  | 2025-03-21 | 2025-03-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128343253 | 002/057 | T2 EI WEIMAR-HALSEY 2/57 RPL POLE | SACTO | ETL.8340.POLE.WOOD | 2024-03-21 | 2024-03-21 | 2025-03-08 | On-Time |  | 2025-03-21 | 2025-03-21 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35571833 | T2 EI WEIMAR-HALSEY 2/049 RPL STRW | 70Y
LC | 128343365 | 002/012 | T3 WV BRIDGEVILLE-GRBRVLL 2/12 INS DMPW | EUREKA | ETL.6220.INSL.NCER | 2024-03-21 | 2024-03-21 | 2025-03-11 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB XMPT TR3 PRTO NTDE BRIN | Missing | Damper-Wood | Install | 46221924 | T3 WV BRIDGEVILLE-GRBRVLL 2/12 INS DMPW | ICW
LC | 128343390 | 000/007 | T2 EI SPLDNG #3-SPLDNG #1 0/7 RPR GYWW | SACTO | ETL.8050.POLE.WOOD | 2024-03-21 | 2024-03-21 | 2025-03-07 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324612 | T2 EI SPLDNG #3-SPLDNG #1 0/7 RPR GYWW | ICW
LC | 128343435 | 000/011 | T2 EI PLACER-DEL MAR 0/11 RMV VEG | SACTO | ETL.7800.POLE.WOOD | 2024-03-21 | 2024-03-21 | 2025-05-16 | Past Due |  | 2025-03-21 | 2025-03-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP NOAC CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128343471 | 038/002 | T2 EI RIO DLL JCT-BRDGVLL 38/2L RPR GYWW | EUREKA | ETL.7850.POLE.STPS | 2024-03-21 | 2024-03-21 | 2025-03-07 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345706 | T2 EI RIO DLL JCT-BRDGVLL 38/2L RPR GYWW | ICW
LC | 128343514 | 007/038 | T2 EI CONTR COST-MORGA#1 7/38 RPR STRT | CONCORD | ETL.5452.TOWR | 2024-03-21 | 2024-03-21 | 2025-01-07 | On-Time |  | 2025-03-21 | 2025-03-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286743 | T2NT EI CONTR COST-MORGA#1 7/38 RPR STRT | ICQ
LC | 128343725 | 039/187 | T2 EI LAKEVLLE SBRNTE #2 39/187 RPR INSS | CONCORD | ETL.4960.INSL | 2024-03-21 | 2024-03-21 | 2025-05-08 | Past Due |  | 2025-03-21 | 2025-03-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46403454 | T2 EI LAKEVLLE SBRNTE #2 39/187 RPR INSS | ICS
LC | 128343771 | 007/037 | T2 EI CONTR COST-MORGA#1 7/37 RPR HRDT | CONCORD | ETL.5452.TOWR | 2024-03-21 | 2024-03-21 | 2025-01-02 | On-Time |  | 2025-03-21 | 2025-03-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46323352 | T2 EI CONTR COST-MORGA#1 7/37 RPR HRDT | ICQ
LC | 128343796 | 011/069 | T2 EI PARKWAY-MORAGA 11/069 RPL INSS | CONCORD | ETL.5930.INSL | 2024-03-21 | 2024-03-21 | 2025-05-18 | Past Due |  | 2025-03-21 | 2025-03-21 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575028 | T2 EI PARKWAY-MORAGA 11/069 RPL INSS | 93K
LC | 128344098 | 039/186 | T2 EI LAKEVLLE-SBRNTE #2 39/186 RPL INSS | CONCORD | ETL.4960.INSL | 2024-03-21 | 2024-03-21 | 2025-05-06 | Past Due |  | 2025-03-21 | 2025-03-21 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35607487 | T2 EI LAKEVLLE-SBRNTE #2 39/186 RPL INSS | 93K
LC | 128344124 | 039/186 | T2 EI IGNACIO-SOBRANTE 39/186 RPR INSS | CONCORD | ETL.4920.INSL.CERA | 2024-03-21 | 2024-03-21 | 2025-02-17 | On-Time |  | 2025-03-21 | 2025-03-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46403453 | T2 EI IGNACIO-SOBRANTE 39/186 RPR INSS | ICS
LC | 128344161 | 008/052 | T2 OLEUM-G #1 8/52 TOUCH | CONCORD | ETL.3150.TOWR | 2024-03-21 | 2024-03-21 | 2024-03-21 | Past Due |  | 2024-06-21 | 2025-03-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46488992 | T2 OLEUM-G #1 8/52 TOUCH | ICQ
LC | 128344240 | 011/012 | T2 EI TRINITY-MAPL CREEK 11/12L RPR GYWW | EUREKA | ETL.8170.POLE.WDPS | 2024-03-21 | 2024-03-21 | 2025-01-20 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345703 | T2 EI TRINITY-MAPL CREEK 11/12L RPR GYWW | ICW
LC | 128344246 | 012/006 | T2 EI TRINITY-MAPLE CREEK 12/6R RPR GYWW | EUREKA | ETL.8170.POLE.WDPS | 2024-03-21 | 2024-03-21 | 2024-11-01 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46222164 | T2 EI TRINITY-MAPLE CREEK 12/6R RPR GYWW | ICW
LC | 128344252 | 012/006 | T2 EI TRINITY-MAPLE CRK 12/6C RPR IBWW | EUREKA | ETL.8170.INSL.NCER | 2024-03-21 | 2024-03-21 | 2025-03-20 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46345704 | T2 EI TRINITY-MAPLE CRK 12/6C RPR IBWW | ICW
LC | 128344334 | 038/002 | T2 EI RIO DLL JCT-BRDGVLL 38/2R RPR GYWW | EUREKA | ETL.7850.POLE.STPS | 2024-03-21 | 2024-03-21 | 2025-03-07 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC ACCL COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345707 | T2 EI RIO DLL JCT-BRDGVLL 38/2R RPR GYWW | ICW
LC | 128344416 | 000/013 | T2 EI SPLDNG #3-SPLDNG #1 0/13 RPL DAMW | SACTO | ETL.8050.INSL.NCER | 2024-03-21 | 2024-03-21 | 2025-03-07 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Damper-Wood | Replace | 46324611 | T2 EI SPLDNG #3-SPLDNG #1 0/13 RPL DAMW | ICW
LC | 128344460 | 000/013 | T2 EI SPLDNG #3-SPLDNG #1 0/13 RPR INSW | SACTO | ETL.8050.INSL.NCER | 2024-03-21 | 2024-03-21 | 2025-03-07 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46324610 | T2 EI SPLDNG #3-SPLDNG #1 0/13 RPR INSW | ICW
LC | 128344533 | 007/056 | T2 EI PLCER-GOLD HILL #1 7/56 RMV NEST | SACTO | ETL.3340.TOWR | 2024-03-21 | 2024-03-21 | 2025-01-30 | On-Time |  | 2025-03-21 | 2025-03-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46300561 | T2NT EI PLCER-GOLD HILL #1 7/56 RMV NEST | ICS
LC | 128344551 | 007/057 | T2 EI PLCER-GOLD HILL #1 7/57 RMV NEST | SACTO | ETL.3340.TOWR | 2024-03-21 | 2024-03-21 | 2025-01-30 | On-Time |  | 2025-03-21 | 2025-03-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD ACCL COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46300562 | T2NT EI PLCER-GOLD HILL #1 7/57 RMV NEST | ICS
LC | 128344640 | 023/003 | T2 EI COALNGA #1-SN MIGUEL 23/3 UNBURY | FRESNO | ETL.8580.TOWR | 2024-03-21 | 2024-03-21 | 2025-01-15 | On-Time |  | 2025-03-21 | 2025-03-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46292635 | T2 EI COALNGA #1-SN MIGUEL 23/3 UNBURY | ICQ
LC | 128344654 | 004/034 | T2 EI PLACER-GOLD HILL #1 4/34 RMV NEST | SACTO | ETL.3340.TOWR | 2024-03-21 | 2024-03-21 | 2025-01-29 | On-Time |  | 2025-03-21 | 2025-03-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC ACCL COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46300563 | T2 EI PLACER-GOLD HILL #1 4/34 RMV NEST | ICS
LC | 128353129 | 110/003C | T2 DI HUMBLDT-TRNTY 110/03C RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-03-23 | 2024-03-21 | 2024-08-14 | On-Time |  | 2024-09-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46219579 | T2 DI HUMBLDT-TRNTY 110/03C RPR GYWW | ICW
LC | 128353131 | 110/003B | T2 DI HUMBLDT-TRNTY 110/03B RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-03-23 | 2024-03-21 | 2024-08-14 | On-Time |  | 2024-09-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46219578 | T2 DI HUMBLDT-TRNTY 110/03B RPR GYWW | ICW
LC | 128353132 | 110/003A | T2 DI HUMBLDT-TRNTY 110/03A RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-03-23 | 2024-03-21 | 2024-08-14 | On-Time |  | 2024-09-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46219577 | T2 DI HUMBLDT-TRNTY 110/03A RPR GYWW | ICW
LC | 128353175 | 001/002 | T2 DI LYTNVLLE-CVLO 001/002 RPR GYWW | WILLITS | ETL.7390.POLE.WOOD | 2024-03-23 | 2024-03-21 | 2025-04-14 | Past Due |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46404152 | T2 DI LYTNVLLE-CVLO 001/002 RPR GYWW | ICW
LC | 128353475 | 000/012 | T2 DI LAYTNVL-COVELO 0/12 RPR GYWW | WILLITS | ETL.7390.POLE.WOOD | 2024-03-23 | 2024-03-21 | 2025-04-14 | Past Due |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46404150 | T2 DI LAYTNVL-COVELO 0/12 RPR GYWW | ICW
LC | 128366362 | ;023/007 | T2 DI KONCTI MDLTWN 23/007 RPR INSW | WILLITS | ETL.6380.INSL.CERA | 2024-03-25 | 2024-03-21 | 2025-03-20 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46498575 | T2 DI KONCTI MDLTWN 23/007 RPR INSW | ICW
LC | 128369141 | 011/069 | T2 EI PARKWAY-MORAGA 11/69 RPL HRDT | CONCORD | ETL.5930.INSL | 2024-03-26 | 2024-03-21 | 2025-05-18 | Past Due |  | 2025-03-21 | 2025-03-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46286744 | T2 EI PARKWAY-MORAGA 11/69 RPL HRDT | ICQ
LC | 128369590 | 018/095 | T2 VACA-BAHIA 18/95 HANGER | SACTO | ETL.5810.INSL | 2024-03-26 | 2024-03-21 | 2024-11-16 | On-Time |  | 2025-03-21 | 2025-03-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46216822 | T2 VACA-BAHIA 18/95 HANGER | ICQ
LC | 128415824 | 010/075 | T2 DI GREEN VALLEY-LLAGAS 10/75 RPL POLE | MOSSLNDG | ETL.1720.POLE.WDPS | 2024-04-01 | 2024-03-21 | 2025-03-20 | On-Time |  | 2025-03-21 | 2025-03-21 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573305 | T2 DI GREEN VALLEY-LLAGAS 10/75 RPL POLE | 70Y
LC | 128416080 | 017/006 | T2 DI KONOCTI-MIDDLET 17/6 RPL HRDW | WILLITS | ETL.6380.POLE.NWOD | 2024-04-01 | 2024-03-21 | 2025-03-17 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46333925 | T2 DI KONOCTI-MIDDLET 17/6 RPL HRDW | ICW
LC | 128416151 | 015/101 | T2 DI MTCALF CRN VLY 15/101L RPL STRW | MOSSLNDG | ETL.2540.POLE.WDPS | 2024-04-01 | 2024-03-21 | 2025-02-26 | On-Time |  | 2025-03-21 | 2025-03-21 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573536 | T2 DI MTCALF CRN VLY 15/101L RPL STRW | 70Y
LC | 128416154 | 015/101 | T2 DI MTCALF CRN VLY 15/101R RPL STRW | MOSSLNDG | ETL.2540.POLE.WDPS | 2024-04-01 | 2024-03-21 | 2025-02-26 | On-Time |  | 2025-03-21 | 2025-03-21 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573536 | T2 DI MTCALF CRN VLY 15/101L RPL STRW | 70Y
LC | 128416172 | 026/004A | T2 DI KONOCTI-MIDDLET 26/4A RPR INSW | WILLITS | ETL.6380.INSL.CERA | 2024-04-01 | 2024-03-21 | 2025-03-20 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46333928 | T2 DI KONOCTI-MIDDLET 26/4A RPR INSW | ICW
LC | 128416281 | 010/074A | T2 DI GREEN VALLEY-LLAGAS 10/74A RMV VEG | MOSSLNDG | ETL.1720.POLE.NWOD | 2024-04-01 | 2024-03-21 | 2025-03-18 | On-Time |  | 2025-03-21 | 2025-03-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128416344 | 015/102 | T2 DI MTCALF CRN VLY 15/102 TOUCH | MOSSLNDG | ETL.2540.POLE.NWOD | 2024-04-01 | 2024-03-21 | 2024-03-21 | Past Due |  | 2024-09-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW ACCL OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46488654 | T2 DI MTCALF CRN VLY 15/102 TOUCH | ICW
LC | 128416385 | :015/008 | T2 DI EAGLE ROCK-CORTINA :15/8 RPL ANCW | WILLITS | ETL.1470.POLE.WOOD | 2024-04-01 | 2024-03-21 | 2025-03-12 | On-Time |  | 2025-03-21 | 2025-03-21 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35557678 | T2 DI EAGLE ROCK-CORTINA :15/8 RPL ANCW | 93E
LC | 128416562 | 018/001 | T2 DI KNCT MDLTWN 18/1 RPR CRSW | WILLITS | ETL.6380.POLE.WOOD | 2024-04-01 | 2024-03-21 | 2025-03-18 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46333926 | T2 DI KNCT MDLTWN 18/1 RPR CRSW | ICW
LC | 128416563 | 018/001 | T2 DI KNCT MDLTWN 18/1 RPR STRW | WILLITS | ETL.6380.POLE.WOOD | 2024-04-01 | 2024-03-21 | 2025-03-18 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46333927 | T2 DI KNCT MDLTWN 18/1 RPR STRW | ICW
LC | 128416843 | 19 | T2 DI CLAY-MARTEL 18/265 RPL SPLW | VICTOR | ETL.8250.SWIT | 2024-04-01 | 2024-03-21 | 2025-06-17 | Past Due |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Splice-Wood | Replace | 46326981 | +T2 DI CLAY-MARTEL 18/265 RPL SPLW | ICW
LC | 128428495 | :014/017 | T2 DI EAGLE ROCK-CORTINA :14/17 COTTER | WILLITS | ETL.1470.INSL.NCER | 2024-04-02 | 2024-03-21 | 2024-09-05 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46305770 | T2 DI EAGLE ROCK-CORTINA :14/17 COTTER | ICW
LC | 128428498 | :014/017 | T2 DI EAGLE ROCK-CORTINA :14/17 RPR IBWW | WILLITS | ETL.1470.INSL.NCER | 2024-04-02 | 2024-03-21 | 2025-03-12 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46305771 | T2 DI EAGLE ROCK-CORTINA :14/17 RPR IBWW | ICW
LC | 128428620 | :014/017 | T2 DI EAGLE ROCK-CORTINA :14/17 RPR CRSW | WILLITS | ETL.1470.POLE.WOOD | 2024-04-02 | 2024-03-21 | 2025-03-12 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46305772 | T2 DI EAGLE ROCK-CORTINA :14/17 RPR CRSW | ICW
LC | 128428624 | 000/010 | T2 DI LYTNVL CVLO 00/010 RPR GYWW | WILLITS | ETL.7390.POLE.WOOD | 2024-04-02 | 2024-03-21 | 2025-04-14 | Past Due |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46404142 | T2 DI LYTNVL CVLO 00/010 RPR GYWW | ICW
LC | 128428627 | 000/010 | T2 DI LYTNVL CVLO 00/010 RPR INSW | WILLITS | ETL.7390.INSL.CERA | 2024-04-02 | 2024-03-21 | 2025-06-10 | Past Due |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46404143 | T2 DI LYTNVL CVLO 00/010 RPR INSW | ICW
LC | 128428628 | 001/000 | T2 DI LYTNVL CVLO 1/0 RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-04-02 | 2024-03-21 | 2024-07-15 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46229231 | T2 DI LYTNVL CVLO 01/000 RPR JUMW | ICW
LC | 128429513 | 019/379 | T2 DI COLGATE-PALERMO 19/379 TOUCH | TABLEMTN | ETL.6500.POLE.NWOD | 2024-04-02 | 2024-03-21 | 2025-05-21 | Past Due |  | 2024-09-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46463545 | T2 DI COLGATE-PALERMO 19/379 RPR STRW | ICW
LC | 128429890 | 018/356 | T2 DI COLGATE-PLMRO 18/356 RPR INSW | TABLEMTN | ETL.6500.INSL.CERA | 2024-04-02 | 2024-03-21 | 2024-08-23 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46265688 | T2 DI COLGATE-PLMRO 18/356 RPR INSW | ICW
LC | 128430024 | 026/007 | T2 DI KNCTI MDDLTWN 026/007 RPL HRDW | WILLITS | ETL.6380.POLE.NWOD | 2024-04-02 | 2024-03-21 | 2025-03-20 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46333929 | T2 DI KNCTI MDDLTWN 026/007 RPL HRDW | ICW
LC | 128430099 | 000/013 | T2 DI LYTNVL CVLO 00/013 RPR IBWW | WILLITS | ETL.7390.INSL.NCER | 2024-04-02 | 2024-03-21 | 2025-04-14 | Past Due |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46404151 | T2 DI LYTNVL CVLO 00/013 RPR IBWW | ICW
LC | 128430247 | 001/012 | T2 MONTA VSTA BRNS 01/012 RPR CRSW | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-04-02 | 2024-03-21 | 2025-05-14 | Past Due |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46391270 | T2 DI MONTA VSTA BRNS 01/012 RPR CRSW | ICW
LC | 128430532 | 024/011 | T2 DI KNCTI MDDLTWN 024/011 RPR ANCW | WILLITS | ETL.6380.POLE.WOOD | 2024-04-02 | 2024-03-21 | 2024-07-22 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46233089 | T2 DI KNCTI MDDLTWN 024/011 RPR ANCW | ICW
LC | 128443078 | 000/004 | T2 DI PERMANENTE #2 TAP 0/4 RPR GYWW | METCALF | ETL.7622.POLE.NWOD | 2024-04-03 | 2024-03-21 | 2025-01-21 | On-Time |  | 2025-03-21 | 2025-03-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286872 | T2 DI PERMANENTE #2 TAP 0/4 RPR GYWW | ICW
LC | 128444360 | 010/075 | T2 DI GREEN VALLEY-LLAGAS 10/75 RPL POLE | MOSSLNDG | ETL.1720.POLE.WDPS | 2024-04-04 | 2024-03-21 | 2025-03-20 | On-Time |  | 2025-03-21 | 2025-03-21 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573305 | T2 DI GREEN VALLEY-LLAGAS 10/75 RPL POLE | 70Y
LC | 128549523 | 006/002 | T2 HUMBOLDT-MAPLE CRK 6/2C GO95 RPL | EUREKA | ETL.7130.POLE.WDPS | 2024-04-16 | 2024-03-21 | 2025-05-25 | Past Due |  | 2025-03-21 | 2025-03-21 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR2 PRTO NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 31654782 | T2 HUMBOLDT-MAPLE CREEK 6/001 GO95 | 93G
LC | 123164557 | 004/026 | T3NT EI RND MTN-TBL MTN #1 4/26 BNT STL | TABLEMTN | ETL.6060.TOWR | 2022-03-22 | 2022-03-22 | 2023-08-19 | On-Time |  | 2025-03-22 | 2025-03-22 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644404 | T3 EI RND MTN-TBLE MTN #1 4/26 BNT STEEL | ICQ
LC | 123164580 | 004/026 | T3NT EI RND MTN-TBLE MTN #1 4/26 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2022-03-22 | 2022-03-22 | 2023-08-22 | On-Time |  | 2025-03-22 | 2025-03-22 | 564 | TR3N |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR3N PRTO CLMB FRAB | Overgrown | Vegetation | Remove
LC | 123165273 | 005/005 | T2NT EI FORT SEWARD TAP 5/5 RMV BUTT | EUREKA | ETL.6222.POLE.NWOD | 2022-03-22 | 2022-03-22 | 2024-01-25 | On-Time |  | 2025-03-22 | 2025-03-22 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 45654199 | T2 EI FORT SEWARD TAP 5/5 RMV BUTT | ICW
LC | 123204021 | 023/134 | T2NT DI STANSLS-MTCA #2 23/134 RPL HRDT | VICTOR | ETL.3820.TOWR | 2022-03-28 | 2022-03-22 | 2023-08-02 | On-Time |  | 2025-03-22 | 2025-03-22 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 45590802 | T2 DI STANSLS-MTCA #2 23/134 RPL HRDT | ICQ
LC | 123223113 | 041/237 | T3NT DI TBLR-SN LS OBSO 41/237 COMPLETE | PISMOBCH | ETL.3960.TOWR | 2022-03-31 | 2022-03-22 | 2023-07-18 | On-Time |  | 2025-03-22 | 2025-03-22 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45638566 | T3 DI TBLOR-SN LS OBSPO 41/237 BNT STEEL | ICQ
LC | 128346029 | 071/360A | T2 MALIN-RND MTN #2 71/360A RPR INSS | TABLEMTN | ETL.6020.INSL.NCER | 2024-03-22 | 2024-03-22 | 2025-02-09 | On-Time |  | 2025-03-22 | 2025-03-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46399503 | T2 MALIN-RND MTN #2 71/360A RPR INSS | ICS
LC | 128346357 | 054/002 | T2 EI ELK-GUALALA 054/002 RPL ANCW | WILLITS | ETL.8410.POLE.WOOD | 2024-03-22 | 2024-03-22 | 2025-03-03 | On-Time |  | 2025-03-22 | 2025-03-22 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573844 | T2 EI ELK-GUALALA 054/002 RPL ANCW | 93E
LC | 128346526 | 008/139 | T2 EI TEMPLETN-ATASCADRO 08/139 TOUCH | PISMOBCH | ETL.9410.POLE.NWOD | 2024-03-22 | 2024-03-22 | 2025-04-04 | Past Due |  | 2024-09-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46488754 | T2 EI TEMPLETN-ATASCADRO 08/139 TOUCH | ICW
LC | 128346760 | 002/020 | T2 EI OLEUM-G #1 2/20 RMV VEG | CONCORD | ETL.3150.TOWR | 2024-03-22 | 2024-03-22 | 2024-12-20 | On-Time |  | 2025-03-22 | 2025-03-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128346946 | 000/003 | T2 CHRISTIE-SOBRANTE 0/3 HANGER | CONCORD | ETL.1260.INSL.CERA | 2024-03-22 | 2024-03-22 | 2025-01-14 | On-Time |  | 2025-03-22 | 2025-03-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46286749 | T2 CHRISTIE-SOBRANTE 0/3 HANGER | ICQ
LC | 128346986 | 008/140 | T2 EI TEMPLETN-ATASCADRO 08/140 RPR STRW | PISMOBCH | ETL.9410.POLE.WOOD | 2024-03-22 | 2024-03-22 | 2025-04-04 | Past Due |  | 2025-03-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46329658 | T2 EI TEMPLETN-ATASCADRO 08/140 RPR STRW | ICW
LC | 128347006 | A003/024 | T2NT EI OLEUM-N TWR-CRSTE A3/24 RPL RPTS | CONCORD | ETL.3180.TOWR | 2024-03-22 | 2024-03-22 | 2025-03-13 | On-Time |  | 2027-03-22 | 2025-03-22 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46286751 | T2NT EI OLEUM-N TWR-CRSTE A3/24 RPL RPTS | ICB
LC | 128350385 | 001/021D | T2 EI MTN QUARRIES TAP 001/021D CNCL | SACTO | ETL.6991.POLE.WOOD | 2024-03-22 | 2024-03-22 | 2024-03-22 | Past Due |  | 2025-03-22 | 2025-03-22 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574702 | T2 EI MTN QUARRIES TAP 001/021D RPL STRW | 70Y
LC | 128350478 | 008/143 | T2 EI TEMPLETN-ATASCADRO 08/143 RPR STRW | PISMOBCH | ETL.9410.POLE.WOOD | 2024-03-22 | 2024-03-22 | 2025-04-04 | Past Due |  | 2025-03-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46329659 | T2 EI TEMPLETN-ATASCADRO 08/143 RPR STRW | ICW
LC | 128350609 | C009/043 | T2 PALERMO-COLGATE C9/43 RMV VEG | TABLEMTN | ETL.5360.TOWR | 2024-03-22 | 2024-03-22 | 2024-03-22 | Past Due |  | 2025-03-22 | 2025-03-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128350648 | 011/260 | T2 WV COLGATE-GRSS VLLEY 11/260 RPL HRDW | SACTO | ETL.6490.POLE.NWOD | 2024-03-22 | 2024-03-22 | 2025-02-21 | On-Time |  | 2025-03-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46457816 | T2 WV COLGATE-GRSS VLLEY 11/260 RPL HRDW | ICW
LC | 128350774 | 039/181 | T2 IGNACIO-SOBRANTE 39/181 RPL INSS | CONCORD | ETL.4920.INSL.CERA | 2024-03-22 | 2024-03-22 | 2024-03-22 | Past Due |  | 2025-03-22 | 2025-03-22 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35608526 | T2 EI IGNACIO-SOBRANTE 39/181 RPL INSS | 93K
LC | 128350877 | 004/020 | T2 WV HUMBLDT BY-HMBLDT #1 4/20 INS DMPT | EUREKA | ETL.1800.INSL.NCER | 2024-03-22 | 2024-03-22 | 2025-03-05 | On-Time |  | 2025-03-22 | 2025-03-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Steel | Install | 46305579 | T2 WV HUMBLDT BY-HMBLDT #1 4/20 INS DMPT | ICS
LC | 128350892 | 017/000 | T2 EI PHILO JCT-ELK 17/000 RPR ANCW | WILLITS | ETL.7780.POLE.WOOD | 2024-03-22 | 2024-03-22 | 2025-02-03 | On-Time |  | 2025-03-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46333931 | T2 EI PHILO JCT-ELK 17/000 RPR ANCW | ICW
LC | 128351011 | 020/001 | T2 EI CLINGA #1-SAN MGUEL 20/001 UNBURY | FRESNO | ETL.8580.TOWR | 2024-03-22 | 2024-03-22 | 2025-03-25 | Past Due |  | 2025-03-22 | 2025-03-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46292636 | T2 EI CLINGA #1-SAN MGUEL 20/001 UNBURY | ICQ
LC | 128351132 | 018/071 | T2 EI DIABLO-MIDWAY #2 18/71 RPR FOND | PISMOBCH | ETL.5970.TOWR | 2024-03-22 | 2024-03-22 | 2025-01-22 | On-Time |  | 2025-03-22 | 2025-03-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46391427 | T2 EI DIABLO-MIDWAY #2 18/71 RPR FOND | ICQ
LC | 128351894 | 018/072 | T2 EI DIABLO-MIDWAY #2 18/72 RPL INSS | PISMOBCH | ETL.5970.INSL.CERA | 2024-03-22 | 2024-03-22 | 2025-03-04 | On-Time |  | 2025-03-22 | 2025-03-22 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35583838 | T0 DI DIABLO-MIDWAY #2 RPL INSS 2 LSTS | 93K
LC | 128351969 | 018/073 | T2 EI DIABLO-MIDWAY #2 18/73 RPR GYWT | PISMOBCH | ETL.5970.TOWR | 2024-03-22 | 2024-03-22 | 2025-01-22 | On-Time |  | 2025-03-22 | 2025-03-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46391428 | T2 EI DIABLO-MIDWAY #2 18/73 RPR GYWT | ICQ
LC | 128352141 | X009/040 | T2 DI DIABLO-MESA X9/040 TOUCH | PISMOBCH | ETL.4620.TOWR | 2024-03-22 | 2024-03-22 | 2025-03-17 | On-Time |  | 2024-09-22 | 2025-03-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476029 | T2 DI DIABLO-MESA X9/040 TOUCH | ICQ
LC | 128352322 | 008/063 | T2 EI PLCER-GOLD HILL #1 8/63 RMV NEST | SACTO | ETL.3340.TOWR | 2024-03-22 | 2024-03-22 | 2025-01-30 | On-Time |  | 2025-03-22 | 2025-03-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD REAR ACCL COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46300564 | T2NT EI PLCER-GOLD HILL #1 8/63 RMV NEST | ICS
LC | 128352468 | 001/032 | T2 EI WEIMAR-HALSEY 1/32 RPR GYWW | SACTO | ETL.8340.POLE.NWOD | 2024-03-22 | 2024-03-22 | 2024-05-20 | On-Time |  | 2024-09-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46252885 | T2 EI WEIMAR-HALSEY 1/32 RPR GYWW | ICW
LC | 128352503 | 001/041 | T2 EI WEIMAR-HALSEY 1/41 COTTER | SACTO | ETL.8340.INSL.NCER | 2024-03-22 | 2024-03-22 | 2024-05-20 | On-Time |  | 2024-09-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD CLR ACCH COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46252882 | T2 EI WEIMAR-HALSEY 1/41 COTTER | ICW
LC | 128352615 | X007/032 | T2 DI DIABLO-MESA X7/32 TOUCH | PISMOBCH | ETL.4620.TOWR | 2024-03-22 | 2024-03-22 | 2025-03-17 | On-Time |  | 2024-09-22 | 2025-03-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476028 | T2 DI DIABLO-MESA X7/32 TOUCH | ICQ
LC | 128352666 | 023/003 | T2 HARTLEY-CLEARLAKE 23/3 GO95 CLEAR | WILLITS | ETL.7515.POLE.WOOD | 2024-03-22 | 2024-03-22 | 2024-03-22 | Past Due |  | 2025-03-22 | 2025-03-22 | 401T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35542601 | T2 HARTLEY-CLEARLAKE 23/003 GO95 | 93G
LC | 128352718 | 001/008 | T2 KANAKA TAP 01/08R RPL POLE | TABLEMTN | ETL.4223.POLE.STPS | 2024-03-22 | 2024-03-22 | 2024-12-07 | On-Time |  | 2024-09-22 | 2025-03-22 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35540817 | T2 KANAKA TAP 01/08 RPL POLES | 70Y
LC | 128352775 | 027/011 | T2 MENDOCINO-WLLTS-FRT BRGG 27/011 GO95 | WILLITS | ETL.7550.POLE.WOOD | 2024-03-22 | 2024-03-22 | 2024-03-22 | Past Due |  | 2025-03-22 | 2025-03-22 | 401T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35543742 | T2 MENDOCINO-WLLTS-FRT BRGG 27/011 GO95 | 93G
LC | 128352779 | 001/008 | T2 KANAKA TAP 01/08C RPL POLE | TABLEMTN | ETL.4223.POLE.STPS | 2024-03-22 | 2024-03-22 | 2024-12-07 | On-Time |  | 2024-09-22 | 2025-03-22 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW NONR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35540817 | T2 KANAKA TAP 01/08 RPL POLES | 70Y
LC | 128352792 | 001/008 | T2 KANAKA TAP 01/08L RPL POLE | TABLEMTN | ETL.4223.POLE.STPS | 2024-03-22 | 2024-03-22 | 2024-12-07 | On-Time |  | 2024-09-22 | 2025-03-22 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW NONR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35540817 | T2 KANAKA TAP 01/08 RPL POLES | 70Y
LC | 128352882 | 001/033 | T2 VOLTA-SOUTH 001/033 RPL ANCW | TABLEMTN | ETL.8300.POLE.WOOD | 2024-03-22 | 2024-03-22 | 2025-01-14 | On-Time |  | 2025-03-22 | 2025-03-22 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586319 | T2 VOLTA-SOUTH 001/033 RPL ANCW | 93E
LC | 128353057 | 017/070 | T2 DI DIABLO-MIDWAY #3 17/70 RMV VEG | PISMOBCH | ETL.5980.TOWR | 2024-03-23 | 2024-03-22 | 2025-02-13 | On-Time |  | 2025-03-22 | 2025-03-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128353115 | 029/117 | T2 DI DIABLO-MIDWAY #2 029/117 RPR FOND | PISMOBCH | ETL.5970.TOWR | 2024-03-23 | 2024-03-22 | 2025-01-23 | On-Time |  | 2025-03-22 | 2025-03-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46391429 | T2 DI DIABLO-MIDWAY #2 029/117 RPR FOND | ICQ
LC | 128353152 | 027/166 | T2 DI TESLA-SLDO-MANTECA 27/166 RPR JUMW | VICTOR | ETL.4000.INSL.NCER | 2024-03-23 | 2024-03-22 | 2024-05-05 | On-Time |  | 2024-06-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46229391 | T2 DI TESLA-SLDO-MANTECA 27/166 RPR JUMW | ICW
LC | 128353182 | 019/274 | T2 DI CLAY- MARTEL 19/274 RPR INSW | VICTOR | ETL.8250.INSL.NCER | 2024-03-23 | 2024-03-22 | 2024-04-11 | On-Time |  | 2024-06-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46218956 | T2 DI CLAY- MARTEL 19/274 RPR INSW | ICW
LC | 128353411 | X006/028 | T2 DI DIABLO-MIDWAY X6/28 TOUCH | PISMOBCH | ETL.4620.TOWR | 2024-03-23 | 2024-03-22 | 2025-03-18 | On-Time |  | 2024-09-22 | 2025-03-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476030 | T2 DI DIABLO-MIDWAY X6/28 TOUCH | ICQ
LC | 128353428 | 031/125 | T2 DI DIABLO-MIDWAY #2 31/125 RPR INSS | PISMOBCH | ETL.5970.INSL.NCER | 2024-03-23 | 2024-03-22 | 2025-03-13 | On-Time |  | 2025-03-22 | 2025-03-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329575 | T2 DI DIABLO-MIDWAY #2 31/125 RPR INSS | ICS
LC | 128353480 | 052/210 | T2 DI DIABLO-GATES #1 52/210 TOUCH | PISMOBCH | ETL.5960.TOWR | 2024-03-23 | 2024-03-22 | 2025-06-04 | Past Due |  | 2024-09-22 | 2025-03-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476162 | T2 DI DIABLO-GATES #1 52/210 TOUCH | ICQ
LC | 128356715 | 043/193 | T2 ROND MTN-TBL MTN#1 43/193 RPR INSS | TABLEMTN | ETL.6060.INSL | 2024-03-25 | 2024-03-22 | 2025-01-30 | On-Time |  | 2025-03-22 | 2025-03-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46306207 | T2 ROND MTN-TBL MTN#1 43/193 RPR INSS | ICS
LC | 128366435 | 001/014 | T2 DI MNTA VSTA BRNS 01/014 RPR ANCW | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-03-25 | 2024-03-22 | 2025-03-18 | On-Time |  | 2025-03-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46391264 | T2 DI MNTA VSTA BRNS 01/014 RPR ANCW | ICW
LC | 128366463 | 032/131 | T2 DI DIABLO- MIDWAY #2 32/131 RPR GYWT | PISMOBCH | ETL.5970.TOWR | 2024-03-25 | 2024-03-22 | 2025-01-23 | On-Time |  | 2025-03-22 | 2025-03-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Replace | 46394442 | T2 DI DIABLO- MIDWAY #2 32/131 RPR GYWT | ICQ
LC | 128366553 | 035/203A | T2 DI INDIAN FLT-YSMTE 35/203A RPR JUMS | FRESNO | ETL.1112.INSL.NCER | 2024-03-25 | 2024-03-22 | 2024-03-22 | Past Due |  | 2025-03-22 | 2025-03-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46298338 | T2 DI INDIAN FLT-YSMTE 35/203A RPR JUMS | ICS
LC | 128366554 | 035/203A | T2 DI EXCHEQUER-INDIAN 35/203A RPR JUMS | FRESNO | ETL.8650.INSL.NCER | 2024-03-25 | 2024-03-22 | 2024-03-22 | Past Due |  | 2025-03-22 | 2025-03-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46298269 | T2 DI EXCHEQUER-INDIAN 35/203A RPR JUMS | ICS
LC | 128366749 | X006/029 | T2 DI MORRO BAY-DIABLO X6/29 RPL INSS | PISMOBCH | ETL.5260.INSL.CERA | 2024-03-25 | 2024-03-22 | 2024-03-22 | Past Due |  | 2025-03-22 | 2025-03-22 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35606487 | T2 DI MORRO BAY-DIABLO X06/29 RPL INSS | 93K
LC | 128368575 | 032/150 | T2 EI TRACY-LOS BANOS 32/150 RPL ZENA | VICTOR | ETL.6130.TOWR | 2024-03-26 | 2024-03-22 | 2025-02-12 | On-Time |  | 2025-03-22 | 2025-03-22 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46299693 | T2 EI TRACY-LOS BANOS 32/150 RPL ZENA | ICB
LC | 128430088 | 024/003 | T2 DI KONOCTI MDLTWN 24/3 RPL ANCW | WILLITS | ETL.6380.POLE.NWOD | 2024-04-02 | 2024-03-22 | 2025-03-20 | On-Time |  | 2025-03-22 | 2025-03-22 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35584567 | T2 DI KONOCTI MDLTWN 24/3 RPL ANCW | 93E
LC | 128430130 | 024/003 | T2 DI KONOCTI MDLTWN 24/3 RPR GYWW | WILLITS | ETL.6380.POLE.NWOD | 2024-04-02 | 2024-03-22 | 2025-02-10 | On-Time |  | 2025-03-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46333932 | T2 DI KONOCTI MDLTWN 24/3 RPR GYWW | ICW
LC | 128430181 | 018/264 | T2 DI CLAY MARTEL 18/264 GO95 | VICTOR | ETL.8250.POLE.WOOD | 2024-04-02 | 2024-03-22 | 2024-03-22 | Past Due |  | 2025-03-22 | 2025-03-22 | 401T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB BRIN | Overloaded | GO95 Clear Infract-Wood | Replace | 35573181 | T2 DI CLAY MARTEL 18/264 GO95 | 93G
LC | 128430182 | 018/264 | T2 DI CLAY MARTEL 18/264 CANCEL | VICTOR | ETL.8250.POLE.WOOD | 2024-04-02 | 2024-03-22 | 2024-03-22 | Past Due |  | 2025-03-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46326982 | +T2 DI CLAY MARTEL 18/264 RPL HRDW | ICW
LC | 128430224 | 001/011 | T2 DI LYTNVL CVLO 1/11 RMV VEG | WILLITS | ETL.7390.POLE.WOOD | 2024-04-02 | 2024-03-22 | 2025-02-26 | On-Time |  | 2025-03-22 | 2025-03-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW SPCR CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128430229 | 001/011 | T2 DI LYTNVL CVLO 1/11 COTTER | WILLITS | ETL.7390.INSL.CERA | 2024-04-02 | 2024-03-22 | 2024-07-18 | On-Time |  | 2025-03-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46229230 | T2 DI LYTNVL CVLO 1/11 COTTER | ICW
LC | 128430307 | 003/016 | T2 MRGA CSTRO VLY 3/16 RPL INSS | CONCORD | ETL.5250.INSL | 2024-04-02 | 2024-03-22 | 2024-03-22 | Past Due |  | 2025-03-22 | 2025-03-22 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575287 | T2 DI MRGA CSTRO VLY RPL INSS IN 2 TWRS. | 93K
LC | 128430324 | 000/015 | T2 DI COLGATE-ALLEGHANY 0/15 RPL ANCW | SACTO | ETL.6470.POLE.WOOD | 2024-04-02 | 2024-03-22 | 2024-06-21 | On-Time |  | 2025-03-22 | 2025-03-22 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35557123 | T2 DI COLGATE-ALLEGHANY 0/15 RPL ANCW | 93E
LC | 128430341 | 003/016 | T2 DI MRGA CSTRO VLY 3/16 TOUCH | CONCORD | ETL.5250.TOWR | 2024-04-02 | 2024-03-22 | 2025-04-28 | Past Due |  | 2024-09-22 | 2025-03-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46488994 | T2 DI MRGA CSTRO VLY 3/16 TOUCH | ICQ
LC | 128430365 | 000/010 | T2 DI MONTA VSTA PRMNTE 00/010 RPR ANCW | METCALF | ETL.7620.POLE.WOOD | 2024-04-02 | 2024-03-22 | 2024-08-22 | On-Time |  | 2024-09-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46235948 | T2 DI MONTA VSTA PRMNTE 00/010 RPR ANCW | ICW
LC | 128430386 | 000/017 | T2 DI COLGATE-ALLEGHANY 0/17 RPR JMPW | SACTO | ETL.6470.INSL.NCER | 2024-04-02 | 2024-03-22 | 2024-06-21 | On-Time |  | 2024-06-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46230697 | T2 DI COLGATE-ALLEGHANY 0/17 RPR JMPW | ICW
LC | 128430490 | 023/003 | T2 DI GRVL LYTONVL 23/003 TOUCH | WILLITS | ETL.8365.POLE.NWOD | 2024-04-02 | 2024-03-22 | 2025-05-09 | Past Due |  | 2024-09-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46507554 | T2 DI GRVL LYTONVL 23/003 TOUCH | ICW
LC | 128443159 | 022/004A | T2 DI KNCTI MDDLTWN 022/004A TOUCH | WILLITS | ETL.6380.POLE.NWOD | 2024-04-03 | 2024-03-22 | 2025-05-19 | Past Due |  | 2024-09-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46507553 | T2 DI KNCTI MDDLTWN 022/004A TOUCH | ICW
LC | 128443267 | 000/011 | T2 DI PERMNTE #1 TAP 0/11 RPL STRW | METCALF | ETL.7621.POLE.WOOD | 2024-04-03 | 2024-03-22 | 2025-01-25 | On-Time |  | 2025-03-22 | 2025-03-22 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573811 | T2 DI PERMNTE #1 TAP 0/11 RPL STRW | 70Y
LC | 128443643 | :017/013 | T2 DI EAGLE ROCK-CRTNA :17/13 RPR STRW | WILLITS | ETL.1470.POLE.WOOD | 2024-04-03 | 2024-03-22 | 2024-09-05 | On-Time |  | 2025-03-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46305775 | T2 DI EAGLE ROCK-CRTNA :17/13 RPR STRW | ICW
LC | 128443760 | 001/010 | T2 DI LAYTONVILLE-COV 1/10 RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-04-03 | 2024-03-22 | 2024-07-15 | On-Time |  | 2025-03-22 | 2025-03-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46229220 | T2 DI LAYTONVILLE-COV 1/10 RPR JUMW | ICW
LC | 123176441 | 066/275 | T2NT EI RND MT-TB MT #1 66/275 BNT STEEL | TABLEMTN | ETL.6060.TOWR | 2022-03-23 | 2022-03-23 | 2023-08-04 | On-Time |  | 2025-03-23 | 2025-03-23 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644514 | T2 EI RND MTN-T MTN #1 66/275 BNT STEEL | ICQ
LC | 123210530 | 015/003 | T2NT DI MNDC-PHL JT-HPLND 15/3 RMV BUTT | WILLITS | ETL.7520.POLE.WOOD | 2022-03-29 | 2022-03-23 | 2023-05-11 | On-Time |  | 2025-03-23 | 2025-03-23 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2N PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 45670908 | T2 DI MNDCN-PHL JCT-HPLND 15/3 RMV BUTT | ICW
LC | 123217049 | 013/127 | T2NT DI UKIAH-HOPLAND 13/127 FILL HOLE | WILLITS | ETL.4050.POLE.NWOD | 2022-03-30 | 2022-03-23 | 2023-03-21 | On-Time |  | 2023-03-23 | 2025-03-23 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Repair | 45487394 | T2NT DI UKIAH-HOPLAND 13/127 FILL HOLE | ICW
LC | 129575186 | 007/063 | T3 ATASCADERO-CAYUCOS 7/63 RPL POLE | PISMOBCH | ETL.8480.POLE.WOOD | 2024-09-23 | 2024-09-23 | 2024-09-23 | Past Due |  | 2025-03-23 | 2025-03-23 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW TNT OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35623923 | T3 ATASCADERO-CAYUCOS 7/63 RPL POLE | 70Y
LC | 129575259 | 006/046 | T3 MORAGA-SAN LEANDRO #1 06/46 BNT STEEL | CONCORD | ETL.2770.TOWR | 2024-09-23 | 2024-09-23 | 2025-01-17 | On-Time |  | 2025-03-23 | 2025-03-23 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46345821 | T3 MORAGA-SAN LEANDRO #1 06/46 BNT STEEL | ICQ
LC | 123188159 | 008/044 | T3NT EI RND MTN-TB MTN #1 08/44 RPR STRT | TABLEMTN | ETL.6060.TOWR | 2022-03-25 | 2022-03-25 | 2023-08-23 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644410 | T3 EI RND MTN-TBLE MTN #1 08/44 RPR STRT | ICQ
LC | 123188364 | 064/269 | T2NT EI RND MTN-TBL MT #2 64/269 BNT STL | TABLEMTN | ETL.6070.TOWR | 2022-03-25 | 2022-03-25 | 2023-08-07 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647742 | T2 EI RND MTN-TBL MT #2 64/269 BNT STEEL | ICQ
LC | 123188591 | 008/045 | T3NT EI RND MTN-TB MTN #1 08/45 RPR STRT | TABLEMTN | ETL.6060.TOWR | 2022-03-25 | 2022-03-25 | 2023-08-23 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644411 | T3 EI RND MTN-TBLE MTN #1 08/45 RPR STRT | ICQ
LC | 123188788 | 064/269 | T2NT EI RND MTN-TBL MT #1 64/269 BNT STL | TABLEMTN | ETL.6060.TOWR | 2022-03-25 | 2022-03-25 | 2023-08-07 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644508 | T2 EI RND MTN-TBL MT #1 64/269 BNT STEEL | ICQ
LC | 123189865 | 008/046 | T3NT EI RND MTN-TB MTN #2 08/46 RPR STRT | TABLEMTN | ETL.6070.TOWR | 2022-03-25 | 2022-03-25 | 2023-07-31 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644879 | T3 EI RND MTN-TBLE MTN #2 08/46 RPR STRT | ICQ
LC | 123192364 | 008/047 | T3NT EI RND MTN-TB MTN #2 08/47 RPR STRT | TABLEMTN | ETL.6070.TOWR | 2022-03-25 | 2022-03-25 | 2023-07-31 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644920 | T3 EI RND MTN-TBLE MTN #2 08/47 RPR STRT | ICQ
LC | 123193215 | 008/048 | T3NT EI RND MTN-TB MTN #2 08/48 RPR STRT | TABLEMTN | ETL.6070.TOWR | 2022-03-25 | 2022-03-25 | 2023-08-16 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644921 | T3 EI RND MTN-TBLE MTN #2 08/48 RPR STRT | ICQ
LC | 123216424 | 054/487 | T2NT DI PIT #1-CTTNWD 54/487 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2022-03-30 | 2022-03-25 | 2023-06-29 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45581848 | T2 DI PIT #1-CTTNWD 54/487 BNT STEEL | ICQ
LC | 123251891 | 022/084 | T2NT DI EXCHQR-DN FT-YSMT 22/84 COMPLETE | FRESNO | ETL.8650.POLE.NWOD | 2022-04-05 | 2022-03-25 | 2023-05-02 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45648500 | T2 DI EXCHQR-IDN FT-YSMIT 22/84 RPR FOND | ICQ
LC | 128357989 | 044/179 | T2 EI DIABLO-MIDWAY #2 44/179 RPR GYWT | PISMOBCH | ETL.5970.TOWR | 2024-03-25 | 2024-03-25 | 2025-03-19 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46394443 | T2 EI DIABLO-MIDWAY #2 44/179 RPR GYWT | ICQ
LC | 128358061 | 020/284 | T2 EI SSQC-SNT YNZ SW ST 20/284 RPL STRW | PISMOBCH | ETL.3700.POLE.WOOD | 2024-03-25 | 2024-03-25 | 2025-02-19 | On-Time |  | 2025-03-25 | 2025-03-25 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573837 | T2 EI SSQC-SNT YNZ SW ST 20/284 RPL STRW | 70Y
LC | 128358589 | 000/007 | T2 PINE GROVE TAP 000/007 RPL HRDW | VICTOR | ETL.8351.POLE.WOOD | 2024-03-25 | 2024-03-25 | 2024-08-22 | On-Time |  | 2025-03-25 | 2025-03-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ | No Good/Out of Stdrd | Hardware-Wood | Replace | 46229392 | T2 PINE GROVE TAP 000/007 RPL HRDW | ICW
LC | 128364817 | 044/183 | T2 EI DIABLO-MIDWAY #2 044/183 COMPLETE | PISMOBCH | ETL.5970.TOWR | 2024-03-25 | 2024-03-25 | 2025-03-19 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46394444 | T2 EI DIABLO-MIDWAY #2 044/183 RPR GYWT | ICQ
LC | 128365172 | 007/040 | T2 EI JFFRSN-HLLSDLE JCT 7/40 RMV VEG | METCALF | ETL.7190.TOWR | 2024-03-25 | 2024-03-25 | 2024-05-09 | On-Time |  | 2025-03-25 | 2025-03-25 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAR | Overgrown | Vegetation | Remove
LC | 128365272 | 020/279 | T2 EI SISQUOC-SNT YNZ SS 20/279 RPL STRW | PISMOBCH | ETL.3700.POLE.WOOD | 2024-03-25 | 2024-03-25 | 2025-02-19 | On-Time |  | 2025-03-25 | 2025-03-25 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP CLR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573830 | T2 EI SISQUOC-SNT YNZ SS 20/279 RPL STRW | 70Y
LC | 128365463 | 045/184 | T2 EI DIABLO-MIDWAY #2 045/184 COMPLETE | PISMOBCH | ETL.5970.TOWR | 2024-03-25 | 2024-03-25 | 2025-03-18 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46394446 | T2 EI DIABLO-MIDWAY #2 045/184 RPR GYWT | ICQ
LC | 128365672 | 001/027 | T2 WV GOLDTREE TAP 001/027 INS DAMW | PISMOBCH | ETL.2821.INSL.NCER | 2024-03-25 | 2024-03-25 | 2025-03-12 | On-Time |  | 2025-03-25 | 2025-03-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46329627 | T2 WV GOLDTREE TAP 001/027 INS DAMW | ICW
LC | 128430467 | 035/150 | T2 DI TEMPLETON GATES 35/150 BNT STEEL | PISMOBCH | ETL.5934.TOWR | 2024-04-02 | 2024-03-25 | 2025-01-07 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46303834 | T2NT DI TEMPLETON GATES 35/150 BNT STEEL | ICQ
LC | 128443192 | 093/474 | T2 DI MALIN-ROUND MTN #2 93/474 UNBURY | TABLEMTN | ETL.6020.TOWR | 2024-04-03 | 2024-03-25 | 2025-01-08 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381364 | T2 DI MALIN-ROUND MTN #2 93/474 UNBURY | ICQ
LC | 128443205 | 048/204 | T2 DI TEMPLETON-GTS-TWR 48/204 RPL HRDT | PISMOBCH | ETL.5934.TOWR | 2024-04-03 | 2024-03-25 | 2025-04-28 | Past Due |  | 2025-03-25 | 2025-03-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46303835 | T2 DI TEMPLETON-GTS-TWR 48/204 RPL HRDT | ICQ
LC | 128443888 | 083/423 | T2 DI MLN-RND MTN #2 83/423 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-03 | 2024-03-25 | 2025-02-11 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381365 | T2 DI MLN-RND MTN #2 83/423 RPR GYWT | ICQ
LC | 128445065 | 049/207 | T2 DI TEMPLETON-GATES 49/207 RPL HRDT | PISMOBCH | ETL.5934.TOWR | 2024-04-04 | 2024-03-25 | 2025-01-08 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46400022 | T2 DI TEMPLETON-GATES 49/207 RPL HRDT | ICQ
LC | 128445526 | 048/204A | T2 DI TEMPLETON-GATES 48/204A RPL HRDT | PISMOBCH | ETL.5934.TOWR | 2024-04-04 | 2024-03-25 | 2025-04-28 | Past Due |  | 2025-03-25 | 2025-03-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46303938 | T2 DI TEMPLETON-GATES 48/204A RPL HRDT | ICQ
LC | 128448443 | 092/472 | T2 DI MALIN-RND MTN #2 92/472 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-04-04 | 2024-03-25 | 2025-01-27 | On-Time |  | 2025-03-25 | 2025-03-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332478 | T2 DI MALIN-RND MTN #2 92/472 RPR OPGW | ICS
LC | 128449767 | 084/426 | T2 DI MALIN RND MTN #2 84/426 RPR FOND | TABLEMTN | ETL.6020.TOWR | 2024-04-04 | 2024-03-25 | 2025-02-11 | On-Time |  | 2025-03-25 | 2025-03-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381368 | T2 DI MALIN RND MTN #2 84/426 RPR FOND | ICQ
LC | 128367887 | 000/018 | T2 QC SMRTVLE-NCLUS #2 0/18 RPL INSW | SACTO | ETL.8000.INSL.NCER | 2024-03-26 | 2024-03-26 | 2025-03-19 | On-Time |  | 2025-03-26 | 2025-03-26 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Replace | 35616446 | T2 QC SMRTVLE-NCLUS #2 0/18 RPL INSW | 93I
LC | 128368782 | 014/064 | T2 EI MORRO BAY-MESA 14/64 RMV NEST | PISMOBCH | ETL.5290.TOWR | 2024-03-26 | 2024-03-26 | 2025-02-21 | On-Time |  | 2025-03-26 | 2025-03-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46329539 | T2 EI MORRO BAY-MESA 14/064 RMV NEST | ICS
LC | 128369388 | 000/001 | T2 EI SPLDNG #3-SPLDNG #1 0/1 INS DAMW | SACTO | ETL.8050.INSL.NCER | 2024-03-26 | 2024-03-26 | 2025-03-07 | On-Time |  | 2025-03-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46324608 | T2 EI SPLDNG #3-SPLDNG #1 0/1 INS DAMW | ICW
LC | 128370666 | 000/008 | T2 WV LAURELES-OTTER 0/8 INS DMPW | MOSSLNDG | ETL.7380.INSL.NCER | 2024-03-26 | 2024-03-26 | 2025-03-23 | On-Time |  | 2025-03-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46391267 | T2 WV LAURELES-OTTER 0/8 INS DMPW | ICW
LC | 128370812 | 000/024 | T2 EI SPLDNG #3-SPLDNG #1 0/24 RPL ANCW | SACTO | ETL.8050.POLE.WOOD | 2024-03-26 | 2024-03-26 | 2025-03-07 | On-Time |  | 2025-03-26 | 2025-03-26 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572885 | T2 EI SPLDNG #3-SPLDNG #1 0/24 RPL ANCW | 93E
LC | 128371248 | 037/006 | T2 EI ELK-GUALALA 037/006L COMPLETE | WILLITS | ETL.8410.POLE.STPS | 2024-03-26 | 2024-03-26 | 2025-03-16 | On-Time |  | 2024-09-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46227602 | T2 EI ELK-GUALALA 037/006L RPR ANCW | ICW
LC | 128371383 | 037/006 | T2 EI ELK-GUALALA 037/006C RPR ANCW | WILLITS | ETL.8410.POLE.STPS | 2024-03-26 | 2024-03-26 | 2025-03-16 | On-Time |  | 2024-09-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46227603 | T2 EI ELK-GUALALA 037/006C RPR ANCW | ICW
LC | 128372214 | 010/055 | T2 EI BAHIA-MORAGA 010/055 RPL INSS | CONCORD | ETL.4340.INSL | 2024-03-26 | 2024-03-26 | 2024-04-21 | On-Time |  | 2025-03-26 | 2025-03-26 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35542748 | T2 EI BAHIA-MORAGA 010/055 RPL INSS | 93K
LC | 128372228 | 007/039 | T2 EI PARKWAY-MORAGA 007/039 RPL INSS | CONCORD | ETL.5930.INSL | 2024-03-26 | 2024-03-26 | 2025-05-19 | Past Due |  | 2025-03-26 | 2025-03-26 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575030 | T2 EI PARKWAY-MORAGA 007/039 RPL INSS | 93K
LC | 128372372 | 018/073 | T2 DIABLO-MIDWAY #3 18/073 TOUCH | PISMOBCH | ETL.5980.TOWR | 2024-03-26 | 2024-03-26 | 2024-03-26 | Past Due |  | 2024-09-26 | 2025-03-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46488929 | T2 EI DIABLO-MIDWAY #3 18/073 TOUCH | ICQ
LC | 128372444 | 008/034 | T2 EI TESLA-METCALF 008/034 INS DAMS | CONCORD | ETL.6110.INSL.NCER | 2024-03-26 | 2024-03-26 | 2025-02-20 | On-Time |  | 2025-03-26 | 2025-03-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Steel | Install | 46286775 | T2 EI TESLA-METCALF 008/034 INS DAMS | ICS
LC | 128373147 | 001/002 | T2 EI POTR VALY-WILTS 01/02 BACKFILL | WILLITS | ETL.7820.POLE.NWOD | 2024-03-27 | 2024-03-26 | 2025-02-18 | On-Time |  | 2025-03-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46308183 | T2NT EI POTR VALY-WILTS 01/02 BACKFILL | ICW
LC | 128373214 | 016/095 | T2 EI NEWARK-LIVERMORE 016/095 RPL ANCW | CONCORD | ETL.7660.POLE.WOOD | 2024-03-27 | 2024-03-26 | 2025-03-23 | On-Time |  | 2025-03-26 | 2025-03-26 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573896 | T2 EI NEWARK-LIVERMORE 016/095 RPL ANCW | 93E
LC | 128380874 | 014/174 | 2 DI ATSCDRO SN LS BSP 14/174 RPL INSS | PISMOBCH | ETL.8490.INSL.NCER | 2024-03-27 | 2024-03-26 | 2025-03-28 | Past Due |  | 2025-03-26 | 2025-03-26 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35576541 | T2 DI ATSCDRO SN LS BSP 14/174 RPL INSS | 93K
LC | 128381100 | 017/000 | T2 DI FULTON-HOPLAND 17/0 RPL STRW | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-03-27 | 2024-03-26 | 2025-03-19 | On-Time |  | 2025-03-26 | 2025-03-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574254 | T2 DI FULTON-HOPLAND 17/0 RPL STRW | 70Y
LC | 128381259 | 005/056 | T2 DI PARADISE-BUTTE 5/56 RPL INSS | TABLEMTN | ETL.4396.INSL.NCER | 2024-03-27 | 2024-03-26 | 2024-07-13 | On-Time |  | 2025-03-26 | 2025-03-26 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35543299 | T2 DI PARADISE-BUTTE RPL INSS 2 TSPS | 93K
LC | 128381270 | 005/056 | T2 DI PARADISE-TBL MTN 5/56 RPL INSS | TABLEMTN | ETL.4316.INSL.NCER | 2024-03-27 | 2024-03-26 | 2024-09-07 | On-Time |  | 2024-06-26 | 2025-03-26 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35531356 | T2 EI PARADISE-TABLE MTN RPL INSS 2 TWRS | 93K
LC | 128381272 | 021/094 | T2 DI MORRO BAY-MESA 21/94 TOUCH | PISMOBCH | ETL.5290.TOWR | 2024-03-27 | 2024-03-26 | 2024-03-26 | Past Due |  | 2024-09-26 | 2025-03-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476147 | T2 DI MORRO BAY-MESA 21/94 TOUCH | ICQ
LC | 128381353 | 000/001 | T2 DI MLNS RACETRACK 0/1 RPL STRW | VICTOR | ETL.2400.POLE.WOOD | 2024-03-27 | 2024-03-26 | 2025-02-26 | On-Time |  | 2025-03-26 | 2025-03-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573698 | T2 DI MLNS RACETRACK 0/1 RPL STRW | 70Y
LC | 128384849 | 037/006 | T2 EI ELK-GUALALA 037/006R RPR ANCW | WILLITS | ETL.8410.POLE.STPS | 2024-03-28 | 2024-03-26 | 2025-03-16 | On-Time |  | 2024-09-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46227604 | T2 EI ELK-GUALALA 037/006R RPR ANCW | ICW
LC | 128386544 | 004/006 | T2 DI LAYTONVLE-COVELO 4/6 RPL STRW | WILLITS | ETL.7390.POLE.WOOD | 2024-03-28 | 2024-03-26 | 2025-06-10 | Past Due |  | 2025-03-26 | 2025-03-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574140 | T2 DI LAYTONVLE-COVELO 4/6 RPL STRW | 70Y
LC | 128386761 | 006/006 | T2 DI LAYTONVILLE-COVEL 6/6 RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-03-28 | 2024-03-26 | 2024-07-19 | On-Time |  | 2025-03-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46229225 | T2 DI LAYTONVILLE-COVEL 6/6 RPR JMPW | ICW
LC | 128386951 | 034/199 | T2 DI TMBLR-SN LS OBSP 34/199 RPR STEEL | PISMOBCH | ETL.3960.TOWR | 2024-03-28 | 2024-03-26 | 2025-03-26 | On-Time |  | 2025-03-26 | 2025-03-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46303837 | T2 DI TMBLR-SN LS OBSP 34/199 RPR STEEL | ICQ
LC | 128386953 | 006/003 | T2 DI LAYTONVILLE-COVELO 6/3 RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-03-28 | 2024-03-26 | 2024-07-10 | On-Time |  | 2025-03-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46229226 | T2 DI LAYTONVILLE-COVELO 6/3 RPR JMPW | ICW
LC | 128393246 | 014/149 | T2 DI IGNACIO-BOLINAS #1 14/149 RPR GYWW | LAKEVLLE | ETL.7140.POLE.NWOD | 2024-03-29 | 2024-03-26 | 2024-09-20 | On-Time |  | 2025-03-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46222552 | T2 DI IGNACIO-BOLINAS #1 14/149 RPR GYWW | ICW
LC | 128415821 | 004/007 | T2 DI LAYTONVILLE-COVELO 4/7 RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-04-01 | 2024-03-26 | 2024-07-15 | On-Time |  | 2025-03-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46229155 | T2 DI LAYTONVILLE-COVELO 4/7 RPR JMPW | ICW
LC | 128416640 | 024/005 | T2 DI FULTON-HOPLAND 24/5 RPR GYWW | LAKEVLLE | ETL.6890.POLE.NWOD | 2024-04-01 | 2024-03-26 | 2024-05-28 | On-Time |  | 2024-06-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46222165 | T2 DI FULTON-HOPLAND 24/5 RPR GYWW | ICW
LC | 128443077 | 021/089 | T2 DI GEYSERS#17 FLTN 21/089 RPR INSS | LAKEVLLE | ETL.4770.INSL.CERA | 2024-04-03 | 2024-03-26 | 2025-04-06 | Past Due |  | 2025-03-26 | 2025-03-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46403457 | T2 DI GEYSERS#17 FLTN 21/089 RPR INSS | ICS
LC | 128443198 | 000/004 | T2 DI MORAGA-CASTRO VLY 0/4 RPR ADSS | CONCORD | ETL.5250.TOWR | 2024-04-03 | 2024-03-26 | 2024-04-30 | On-Time |  | 2024-06-26 | 2025-03-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Steel | Repair | 46222759 | T2 DI MORAGA-CASTRO VLY 0/4 RPR ADSS | ICS
LC | 128443231 | 000/004 | T2 DI MORAGA-CASTRO VLY 0/4 RPR OPGW | CONCORD | ETL.5250.TOWR | 2024-04-03 | 2024-03-26 | 2024-05-20 | On-Time |  | 2024-06-26 | 2025-03-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46227060 | T2 DI MORAGA-CASTRO VLY 0/4 RPR OPGW | ICS
LC | 128443437 | 040/229 | T2 DI TMBLR-SL LS BSP 040/229 TOUCH | PISMOBCH | ETL.3960.TOWR | 2024-04-03 | 2024-03-26 | 2025-03-27 | Past Due |  | 2024-09-26 | 2025-03-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476033 | T2 DI TMBLR-SL LS BSP 040/229 TOUCH | ICQ
LC | 128443439 | 039/171 | T2 DI FULTON-LAKVL 39/171 RPL HRDT | LAKEVLLE | ETL.4950.TOWR | 2024-04-03 | 2024-03-26 | 2025-01-27 | On-Time |  | 2025-03-26 | 2025-03-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289505 | T2 DI FULTON-LAKVL 39/171 RPL HRDT | ICQ
LC | 128443467 | 009/001 | T2 DI FULTON-HOPLAND 9/1 COTR KEY | LAKEVLLE | ETL.6890.INSL.NCER | 2024-04-03 | 2024-03-26 | 2025-01-22 | On-Time |  | 2025-03-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46305580 | T2 DI FULTON-HOPLAND 9/1 COTR KEY | ICW
LC | 128443604 | 004/005 | T2 DI LAYTONVILLE-COV 4/5 RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-04-03 | 2024-03-26 | 2024-07-18 | On-Time |  | 2025-03-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46229159 | T2 DI LAYTONVILLE-COV 4/5 RPR JUMW | ICW
LC | 128443766 | 016/004 | T2 DI FULTON-HOPLAND 16/4 RPR WDPKR | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-04-03 | 2024-03-26 | 2025-03-19 | On-Time |  | 2025-03-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46305581 | T2 DI FULTON-HOPLAND 16/4 RPR WDPKR | ICW
LC | 128447859 | 011/159 | T2 DI ATSCDRO-SL OBSPO 11/159 COMPLETE | PISMOBCH | ETL.8490.TOWR | 2024-04-04 | 2024-03-26 | 2025-03-28 | Past Due |  | 2024-09-26 | 2025-03-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476031 | T2 DI ATSCDRO-SL OBSPO 11/159 TOUCH | ICQ
LC | 128449596 | 039/170 | T2 DI FULTON-LAKEVILLE 39/170 RMV NEST | LAKEVLLE | ETL.4950.TOWR | 2024-04-04 | 2024-03-26 | 2025-02-12 | On-Time |  | 2025-03-26 | 2025-03-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46403458 | T2 DI FULTON-LAKEVILLE 39/170 RMV NEST | ICS
LC | 128457299 | 016/007 | T2 DI HMBLDT BAY-RIO DELL 16/7 TOUCH | EUREKA | ETL.7100.POLE.NWOD | 2024-04-05 | 2024-03-26 | 2025-06-05 | Past Due |  | 2024-09-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46505017 | T2 DI HMBLDT BAY-RIO DELL 16/7 TOUCH | ICW
LC | 128457796 | 035/206 | T2 DI TEMBLOR-SN LS BISP 35/206 COMPLETE | PISMOBCH | ETL.3960.TOWR | 2024-04-05 | 2024-03-26 | 2025-03-27 | Past Due |  | 2025-03-26 | 2025-03-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46303838 | T2 DI TEMBLOR-SN LS BISP 35/206 RPR STRT | ICQ
LC | 128459857 | 005/005 | T2 DI LYTNVLL-CVLO 005/005 RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-04-05 | 2024-03-26 | 2024-07-16 | On-Time |  | 2025-03-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46229158 | T2 DI LYTNVLL-CVLO 005/005 RPR JUMW | ICW
LC | 128460060 | 006/008 | T2 DI LYTNVLL-CVLO 006/008 RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-04-05 | 2024-03-26 | 2024-07-10 | On-Time |  | 2025-03-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46229157 | T2 DI LYTNVLL-CVLO 006/008 RPR JUMW | ICW
LC | 128460063 | 022/092 | T2 DI GEYSERS #12-FLTN 022/092 RMV VEG | LAKEVLLE | ETL.4750.TOWR | 2024-04-05 | 2024-03-26 | 2025-01-16 | On-Time |  | 2025-03-26 | 2025-03-26 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128464690 | 009/000 | T2 DI SALINA-FRT ORD #2 009/000 RPR STRT | MOSSLNDG | ETL.8423.POLE.NWOD | 2024-04-05 | 2024-03-26 | 2025-02-18 | On-Time |  | 2025-03-26 | 2025-03-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46326006 | T2 DI SALINA-FRT ORD #2 009/000 RPR STRT | ICQ
LC | 128464944 | 001/010 | T2 DI KANAKA TAP 1/10 RPL ANCW | TABLEMTN | ETL.4223.POLE.STPS | 2024-04-05 | 2024-03-26 | 2024-12-07 | On-Time |  | 2025-03-26 | 2025-03-26 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573787 | T2 DI KANAKA TAP 1/10 RPL ANCW | 93E
LC | 128465028 | 001/012 | T2 DI KANAKA TAP 1/12R RPR GYWW | TABLEMTN | ETL.4223.POLE.STPS | 2024-04-05 | 2024-03-26 | 2024-12-07 | On-Time |  | 2025-03-26 | 2025-03-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332481 | T2 DI KANAKA TAP 1/12R RPR GYWW | ICW
LC | 128373603 | 000/003 | T2 EI SBRNTE-GRZLY-CLRMNT #2 0/3 COTTER | CONCORD | ETL.3750.INSL.NCER | 2024-03-27 | 2024-03-27 | 2024-12-19 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP CLR ACCL COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46286754 | T2 EI SBRNTE-GRZLY-CLRMNT #2 0/3 COTTER | ICW
LC | 128373676 | 004/076 | T2 TMPLTN-ATASCADERO 04/076 RPR INSW | PISMOBCH | ETL.9410.INSL.NCER | 2024-03-27 | 2024-03-27 | 2025-04-03 | Past Due |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46329655 | T2 TMPLTN-ATASCADERO 04/076 RPR INSW | ICW
LC | 128373950 | 000/005 | T2 EI SBRNT-GRZLY-CLRMNT #2 0/5 RPR ANCW | CONCORD | ETL.3750.POLE.WOOD | 2024-03-27 | 2024-03-27 | 2025-03-16 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REAR ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46286755 | T2 EI SBRNT-GRZLY-CLRMNT #2 0/5 RPR ANCW | ICW
LC | 128375347 | 001/017 | T2 EI CHRISTIE-FRANKLIN#1 1/017 RPR INSW | CONCORD | ETL.6350.INSL.NCER | 2024-03-27 | 2024-03-27 | 2024-07-24 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46222756 | T2 EI CHRISTIE-FRANKLIN#1 1/017 RPR INSW | ICW
LC | 128375414 | 000/006 | T2 EI SBRNT-GRZZLY-CLRMNT#2 0/6 RPR GYWW | CONCORD | ETL.3750.POLE.NWOD | 2024-03-27 | 2024-03-27 | 2024-08-20 | On-Time |  | 2024-09-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REAR CLR ACCM COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46239849 | T2 EI SBRNT-GRZZLY-CLRMNT#2 0/6 RPR GYWW | ICW
LC | 128375577 | 000/007 | T2 EI SBT-GRZLY-CLRMT #2 0/7 RPR GYWW | CONCORD | ETL.3750.POLE.NWOD | 2024-03-27 | 2024-03-27 | 2025-05-03 | Past Due |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REAR CLR ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286756 | T2 EI SBT-GRZLY-CLRMT #2 0/7 RPR GYWW | ICW
LC | 128375719 | 000/008 | T2 EI SBRNT-GRZL-CLRMNT #2 0/08 RPR INSS | CONCORD | ETL.3750.INSL.NCER | 2024-03-27 | 2024-03-27 | 2024-03-27 | Past Due |  | 2025-03-27 | 2025-03-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46286757 | T2 EI SBRNT-GRZL-CLRMNT #2 0/08 RPR INSS | ICS
LC | 128376435 | 007/056 | T2 EI VACA-SUISUN 007/056 RMV VEG | SACTO | ETL.4070.TOWR | 2024-03-27 | 2024-03-27 | 2025-04-23 | Past Due |  | 2025-03-27 | 2025-03-27 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128376473 | 009/176 | T2 VALLEY SPRINGS #1 9/176 GO95 | VICTOR | ETL.8210.POLE.WOOD | 2024-03-27 | 2024-03-27 | 2024-03-27 | Past Due |  | 2025-03-27 | 2025-03-27 | 401T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35542098 | T2 VALLEY SPRINGS #1 9/176 GO95 | 93G
LC | 128377132 | 001/014 | T2 EI CHRISTIE-FRANKLIN#1 1/014 COMPLETE | CONCORD | ETL.6350.POLE.NWOD | 2024-03-27 | 2024-03-27 | 2024-08-06 | On-Time |  | 2024-09-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46234720 | T2 EI CHRISTIE-FRANKLIN#1 1/014 RPR GYWW | ICW
LC | 128377756 | 025/118 | T2 EI EAGLE ROCK-REDBUD 25/118 RPL DMPS | WILLITS | ETL.1480.INSL.CERA | 2024-03-27 | 2024-03-27 | 2025-03-28 | Past Due |  | 2025-03-27 | 2025-03-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Damper-Steel | Replace | 46308187 | T2 EI EAGLE ROCK-REDBUD 25/118 RPL DMPS | ICS
LC | 128377876 | 000/009 | T2 EI SBRNTE-GRZLY-CLMNT#2 0/9 RPR STRT | CONCORD | ETL.3750.TOWR | 2024-03-27 | 2024-03-27 | 2025-03-11 | On-Time |  | 2025-03-27 | 2025-03-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT REAR CLR ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286758 | T2 EI SBRNTE-GRZLY-CLMNT#2 0/9 RPR STRT | ICQ
LC | 128377904 | 000/001B | T2 EI MORAGA-LKWD 000/001B COTTER | CONCORD | ETL.3741.INSL.NCER | 2024-03-27 | 2024-03-27 | 2024-07-11 | On-Time |  | 2025-03-27 | 2025-03-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46239843 | T2 EI MORAGA-LKWD 000/001B COTTER | ICS
LC | 128379680 | 011/081 | T2 EI VACA-SUISUN 011/081 RPL INSS | SACTO | ETL.4070.INSL.CERA | 2024-03-27 | 2024-03-27 | 2025-03-13 | On-Time |  | 2025-03-27 | 2025-03-27 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577313 | T2 EI VACA-SUISUN RPL INSS 2 TWRS | 93K
LC | 128379683 | 001/013 | T2 EI CHRISTIE-FRANKLIN#1 1/013 COMPLETE | CONCORD | ETL.6350.POLE.NWOD | 2024-03-27 | 2024-03-27 | 2024-08-06 | On-Time |  | 2024-09-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46234652 | T2 EI CHRISTIE-FRANKLIN#1 1/013 RPR GYWW | ICW
LC | 128380023 | 000/010 | T2 SBRNT GRZLY CLRMNT 2 0/10 RPR INSS | CONCORD | ETL.3750.INSL | 2024-03-27 | 2024-03-27 | 2024-03-27 | Past Due |  | 2025-03-27 | 2025-03-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP REMT CLR ACCM OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46286759 | T2 EI SBRNT GRZLY CLRMNT 2 0/10 RPR INSS | ICS
LC | 128380032 | 004/033 | T2NT EI SOBRANTE-MORAGA 4/33 RPR FOND | CONCORD | ETL.3742.TOWR | 2024-03-27 | 2024-03-27 | 2025-03-17 | On-Time |  | 2027-03-27 | 2025-03-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46286805 | T2NT EI SOBRANTE-MORAGA 4/33 RPR FOND | ICQ
LC | 128380033 | 004/033 | T2 EI SOBRANTE-MORAGA 4/33 BNT STL | CONCORD | ETL.3742.TOWR | 2024-03-27 | 2024-03-27 | 2025-03-17 | On-Time |  | 2025-03-27 | 2025-03-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286908 | T2 EI SOBRANTE-MORAGA 4/33 BNT STL | ICQ
LC | 128380043 | 004/033 | T2 EI SOBRANTE-MORAGA 4/33 RPL GRWT | CONCORD | ETL.3742.TOWR | 2024-03-27 | 2024-03-27 | 2025-04-02 | Past Due |  | 2025-03-27 | 2025-03-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Ground Wire-Tower | Replace | 46286804 | T2 EI SOBRANTE-MORAGA 4/33 RPL GRWT | ICQ
LC | 128380090 | 000/010 | T2 EI SBRNT GRZLY CLRMNT 2 0/10 RPR STRT | CONCORD | ETL.3750.TOWR | 2024-03-27 | 2024-03-27 | 2025-03-11 | On-Time |  | 2025-03-27 | 2025-03-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286800 | T2 EI SBRNT GRZLY CLRMNT 2 0/10 RPR STRT | ICQ
LC | 128380096 | 000/012 | T2 EI CHRISTIE-FRANKLIN #1 0/12 COMPLETE | CONCORD | ETL.6350.POLE.NWOD | 2024-03-27 | 2024-03-27 | 2024-08-07 | On-Time |  | 2024-09-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46220335 | T2 EI CHRISTIE-FRANKLIN #1 0/12 RPR GYWW | ICW
LC | 128380173 | 004/092 | T2 WEIMAR-HALSEY 004/092 RPL INSW | SACTO | ETL.8340.INSL | 2024-03-27 | 2024-03-27 | 2025-03-10 | On-Time |  | 2025-03-27 | 2025-03-27 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Replace | 35571834 | T2 WEIMAR-HALSEY 004/092 RPL INSW | 93I
LC | 128380233 | 009/162 | T2 TEJON-LEBEC 09/162 RMV BRSH | MIDWAY | ETL.9250.POLE.NWOD | 2024-03-27 | 2024-03-27 | 2025-04-21 | Past Due |  | 2025-03-27 | 2025-03-27 | 932 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | Brush Fuel | Road | Remove | 46452150 | T2 TEJON-LEBEC 09/162 RMV BRSH | CHS
LC | 128380385 | 000/011 | T2 EI SBRNT-GRZL-CLRMNT #2 0/11 RPR STRT | CONCORD | ETL.3750.TOWR | 2024-03-27 | 2024-03-27 | 2025-03-06 | On-Time |  | 2025-03-27 | 2025-03-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD CLR ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286801 | T2 EI SBRNT-GRZL-CLRMNT #2 0/11 RPR STRT | ICQ
LC | 128380417 | 007/038 | T2 EI CORTINA-MENDCIN #1 7/038 RPL ROAD | WILLITS | ETL.1330.TOWR | 2024-03-27 | 2024-03-27 | 2024-05-28 | On-Time |  | 2025-03-27 | 2025-03-27 | 374 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Road | Replace | 31693699 | T2 EI CORTINA-MENDCIN #1 7/038 RPL ROAD | 71Y
LC | 128380424 | 005/028 | T2 EI CORTINA-MENDCN #1 5/28 TOUCH | WILLITS | ETL.1330.TOWR | 2024-03-27 | 2024-03-27 | 2025-04-08 | Past Due |  | 2024-09-27 | 2025-03-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472250 | T2 EI CORTINA-MENDCN #1 5/28 RPR STRT | ICQ
LC | 128380576 | 001/015A | T2 DI MONTA VISTA-BURNS 1/15A RMV VEG | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-03-27 | 2024-03-27 | 2024-05-08 | On-Time |  | 2024-09-27 | 2025-03-27 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE ACCM CNCL OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128380578 | 001/015A | T2 DI MONTA VISTA-BURNS 1/15A RPR ANCW | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-03-27 | 2024-03-27 | 2024-05-22 | On-Time |  | 2024-09-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46235970 | T2 DI MONTA VISTA-BURNS 1/15A RPR ANCW | ICW
LC | 128380582 | 004/030 | T2 EI SOBRANTE-MORAGA 4/30 MASTIC | CONCORD | ETL.3742.TOWR | 2024-03-27 | 2024-03-27 | 2025-03-20 | On-Time |  | 2025-03-27 | 2025-03-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46286803 | T2 EI SOBRANTE-MORAGA 4/30 MASTIC | ICQ
LC | 128380651 | 001/015B | T2 DI MONTA VISTA-BURNS 1/15B RMV VEG | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-03-27 | 2024-03-27 | 2024-05-08 | On-Time |  | 2024-09-27 | 2025-03-27 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE ACCM CNCL OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128380652 | 001/015B | T2 DI MONTA VISTA-BURNS 1/15B RPR ANCW | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-03-27 | 2024-03-27 | 2024-05-22 | On-Time |  | 2024-09-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46235971 | T2 DI MONTA VISTA-BURNS 1/15B RPR ANCW | ICW
LC | 128415899 | 005/002 | T2 DI LAYTONVL COVELO 5/2L RPR GYWW | WILLITS | ETL.7390.POLE.STPS | 2024-04-01 | 2024-03-27 | 2024-07-11 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46278668 | T2 DI LAYTONVL COVELO 5/2L RPR GYWW | ICW
LC | 128419219 | 044/004 | T2 ELK-GUALALA 44/4L RPL ANCW | WILLITS | ETL.8410.POLE.WDPS | 2024-04-02 | 2024-03-27 | 2024-04-25 | On-Time |  | 2025-03-27 | 2025-03-27 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2 PRTO NTDE | No Good/Out of Stdrd | Anchor-Wood | Replace | 35549340 | T2 ELK-GUALALA 44/4L RPL ANCW | 93E
LC | 128430552 | 005/002 | T2 DI LYTNVL CVELO 5/2R RPR GYWW | WILLITS | ETL.7390.POLE.STPS | 2024-04-02 | 2024-03-27 | 2024-07-11 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46278667 | T2 DI LYTNVL CVELO 5/2R RPR GYWW | ICW
LC | 128430556 | 005/002 | T2 DI LYTNVL CVELO 5/2 RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-04-02 | 2024-03-27 | 2024-07-11 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46229224 | T2 DI LYTNVL CVELO 5/2 RPR JUMW | ICW
LC | 128463913 | A001/022 | T2 DI VLLY SPRINGS #1 A001/022 RPR JUMW | VICTOR | ETL.8210.INSL.NCER | 2024-04-05 | 2024-03-27 | 2024-07-09 | On-Time |  | 2024-09-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46229396 | T2 DI VLLY SPRINGS #1 A001/022 RPR JUMW | ICW
LC | 128464069 | 005/058 | T2 DI IGNACIO-BLNS #1 5/058 RPR GYWW | LAKEVLLE | ETL.7140.POLE.NWOD | 2024-04-05 | 2024-03-27 | 2025-02-14 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46403459 | T2NT DI IGNACIO-BLNS #1 5/058 RPR GYWW | ICW
LC | 128464083 | 059/534 | T2 DI PIT #1-COTTONWOOD 59/534 BENT STL | TABLEMTN | ETL.5390.TOWR | 2024-04-05 | 2024-03-27 | 2025-03-13 | On-Time |  | 2025-03-27 | 2025-03-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381502 | T2 DI PIT #1-COTTONWOOD 59/534 BENT STL | ICQ
LC | 128464085 | 059/534 | T2 DI PIT #1-COTTONWOOD 59/534 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-04-05 | 2024-03-27 | 2025-01-06 | On-Time |  | 2025-03-27 | 2025-03-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381503 | T2 DI PIT #1-COTTONWOOD 59/534 RPR FOND | ICQ
LC | 128464131 | 018/258C | T2 DI CLAY-MARTEL 18/258C RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-04-05 | 2024-03-27 | 2025-04-12 | Past Due |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46326983 | +T2 DI CLAY-MARTEL 18/258C RPR STRW | ICW
LC | 128464161 | 058/531 | T2 DI PIT #1-COTTONWOOD 58/531 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-04-05 | 2024-03-27 | 2025-01-06 | On-Time |  | 2025-03-27 | 2025-03-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381504 | T2 DI PIT #1-COTTONWOOD 58/531 RPR FOND | ICQ
LC | 128464258 | 001/019 | T2 DI MNTA VSTA-BRNS 001/019 RPL HRDD | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-04-05 | 2024-03-27 | 2025-03-24 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46391273 | T2 DI MNTA VSTA-BRNS 001/019 RPL HRDD | ICW
LC | 128464434 | 033/516 | T2 DI CLAY-MARTEL 33/516 REFRAME | VICTOR | ETL.8250.POLE.NWOD | 2024-04-05 | 2024-03-27 | 2024-06-13 | On-Time |  | 2024-09-27 | 2025-03-27 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35547095 | T2 DI CLAY-MARTEL 33/516 REFRAME | 93E
LC | 128464436 | 033/516 | T2 DI CLAY-MARTEL 33/516 RPR GYWW | VICTOR | ETL.8250.POLE.NWOD | 2024-04-05 | 2024-03-27 | 2024-06-13 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46238985 | T2 DI CLAY-MARTEL 33/516 RPR GYWW | ICW
LC | 128464494 | 005/001 | T2 DI LAYTONVILLE-COVELO 5/1 RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-04-05 | 2024-03-27 | 2024-07-11 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46229156 | T2 DI LAYTONVILLE-COVELO 5/1 RPR JUMW | ICW
LC | 128464578 | 009/008 | T2 DI FULTON-HOPLAND 9/8 RPR WDPKR | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-04-05 | 2024-03-27 | 2025-03-20 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46305584 | T2 DI FULTON-HOPLAND 9/8 RPR WDPKR | ICW
LC | 128464631 | 009/008 | T2 DI FULTON-HOPLAND 9/8 RPR GYWW | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-04-05 | 2024-03-27 | 2025-01-20 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305583 | T2 DI FULTON-HOPLAND 9/8 RPR GYWW | ICW
LC | 128464900 | 008/005 | T2 DI LWR LAKE-HMSTAKE 8/5 RPL INSW | WILLITS | ETL.1481.INSL.NCER | 2024-04-05 | 2024-03-27 | 2024-09-12 | On-Time |  | 2024-06-27 | 2025-03-27 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35542736 | T2 DI LWR LAKE-HMSTAKE 8/5 RPL INSW | 93I
LC | 128465698 | 022/091 | T2 DI GEYSERS #12-FULTON 22/91 TOUCH | LAKEVLLE | ETL.4750.TOWR | 2024-04-05 | 2024-03-27 | 2025-03-25 | On-Time |  | 2024-09-27 | 2025-03-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485386 | T2 DI GEYSERS #12-FULTON 22/91 TOUCH | ICQ
LC | 128467176 | 007/005 | T2 DI LAYTNVLL-COVELO 7/5 RPL ANCW | WILLITS | ETL.7390.POLE.WOOD | 2024-04-05 | 2024-03-27 | 2025-06-11 | Past Due |  | 2025-03-27 | 2025-03-27 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574143 | T2 DI LAYTNVLL-COVELO 7/5 RPL ANCW | 93E
LC | 128472045 | 044/004 | T2 ELK-GUALALA 44/4C RPL ANCW | WILLITS | ETL.8410.POLE.WDPS | 2024-04-08 | 2024-03-27 | 2024-04-25 | On-Time |  | 2025-03-27 | 2025-03-27 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR FIRE COMP OH TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Anchor-Wood | Replace | 35549340 | T2 ELK-GUALALA 44/4L RPL ANCW | 93E
LC | 128472049 | 044/004 | T2 ELK-GUALALA 44/4R RPL ANCW | WILLITS | ETL.8410.POLE.WDPS | 2024-04-08 | 2024-03-27 | 2024-04-25 | On-Time |  | 2025-03-27 | 2025-03-27 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR FIRE COMP OH TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Anchor-Wood | Replace | 35549340 | T2 ELK-GUALALA 44/4L RPL ANCW | 93E
LC | 128487604 | 004/010 | T2 DI LAYTONVILLE-COVL 4/10L RPR GYWW | WILLITS | ETL.7390.POLE.STPS | 2024-04-08 | 2024-03-27 | 2025-03-28 | Past Due |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46414249 | T2 DI LAYTONVILLE-COVL 4/10L RPR GYWW | ICW
LC | 128489402 | 001/011A | T2 DI KANAKA TAP 01/11A RPR ANCW | TABLEMTN | ETL.4223.POLE.NWOD | 2024-04-08 | 2024-03-27 | 2024-12-07 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46332488 | T2 DI KANAKA TAP 01/11A RPR ANCW | ICW
LC | 128489406 | 001/011A | T2 DI KANAKA TAP 1/11A RPR JUMW | TABLEMTN | ETL.4223.INSL.NCER | 2024-04-08 | 2024-03-27 | 2024-08-15 | On-Time |  | 2024-06-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46237026 | T2 DI KANAKA TAP 01/11A RPR JMPW | ICW
LC | 128490563 | 002/028 | T2 DI MNT VISTA-BURNS 2/28 RPR STRW | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-04-08 | 2024-03-27 | 2025-03-09 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46391274 | T2 DI MNT VISTA-BURNS 2/28 RPR STRW | ICW
LC | 128490567 | 001/011B | T2 DI KANAKA TAP 1/11B RPR JUMW | TABLEMTN | ETL.4223.INSL.NCER | 2024-04-08 | 2024-03-27 | 2024-08-15 | On-Time |  | 2024-06-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46230781 | T2 DI KANAKA TAP 01/11B RPR JMPW | ICW
LC | 128491094 | 001/011C | T2 DI KANAKA TAP 1/11C RPR JUMW | TABLEMTN | ETL.4223.INSL.NCER | 2024-04-08 | 2024-03-27 | 2024-08-15 | On-Time |  | 2024-06-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46230788 | T2 DI KANAKA TAP 01/11C RPR JUMW | ICW
LC | 128492299 | 005/059 | T2 DI IGNACIO-BOLIN #1 5/59 RPR ANCW | LAKEVLLE | ETL.7140.POLE.WOOD | 2024-04-08 | 2024-03-27 | 2025-02-14 | On-Time |  | 2025-03-27 | 2025-03-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46403740 | T2 DI IGNACIO-BOLIN #1 5/59 RPR ANCW | ICW
LC | 128494691 | 059/533 | T2 DI PIT #1-COTTONWOOD 59/533 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-04-09 | 2024-03-27 | 2024-06-17 | On-Time |  | 2024-09-27 | 2025-03-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46256222 | T2 DI PIT #1-COTTONWOOD 59/533 RPR STRT | ICQ
LC | 128494692 | 059/533 | T2 DI PIT #1-COTTONWOOD 59/533 RPR GYWT | TABLEMTN | ETL.5390.TOWR | 2024-04-09 | 2024-03-27 | 2025-02-19 | On-Time |  | 2025-03-27 | 2025-03-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381506 | T2 DI PIT #1-COTTONWOOD 59/533 RPR GYWT | ICQ
LC | 129598581 | 010/005 | T3 MONTE RIO-FULTON 010/005 RPL STRW | LAKEVLLE | ETL.7630.POLE.WOOD | 2024-09-27 | 2024-09-27 | 2025-06-03 | Past Due |  | 2025-03-27 | 2025-03-27 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35586174 | T3 WV MONTE RIO-FULTON 010/005 RPL STRW | 70Y
LC | 123201004 | 009/049 | T3NT EI RND MTN-TBL MT #1 9/49 BNT STEEL | TABLEMTN | ETL.6060.TOWR | 2022-03-28 | 2022-03-28 | 2023-08-19 | On-Time |  | 2025-03-28 | 2025-03-28 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644412 | T3 EI RND MTN-TBLE MTN #1 9/49 BNT STEEL | ICQ
LC | 123203403 | 010/053 | T2NT EI RND MTN-TB MT #2 10/53 BNT STEEL | TABLEMTN | ETL.6070.TOWR | 2022-03-28 | 2022-03-28 | 2023-08-18 | On-Time |  | 2025-03-28 | 2025-03-28 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644925 | T2 EI RND MTN-TBL MTN #2 10/53 BNT STEEL | ICQ
LC | 123203847 | 010/054 | T2NT EI RND MTN-TB MT #1 10/54 BNT STEEL | TABLEMTN | ETL.6060.TOWR | 2022-03-28 | 2022-03-28 | 2023-08-18 | On-Time |  | 2025-03-28 | 2025-03-28 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644413 | T2 EI RND MTN-TBL MTN #1 10/54 BNT STEEL | ICQ
LC | 123204440 | 010/055 | T2NT EI RND MTN-TB MT #2 10/55 BNT STEEL | TABLEMTN | ETL.6070.TOWR | 2022-03-28 | 2022-03-28 | 2023-08-16 | On-Time |  | 2025-03-28 | 2025-03-28 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644927 | T2 EI RND MTN-TBL MTN #2 10/55 BNT STEEL | ICQ
LC | 123222989 | 069/285 | T2NT DI RNDMTN-TBLMTN #2 69/285 BNT STL | TABLEMTN | ETL.6070.TOWR | 2022-03-31 | 2022-03-28 | 2023-12-15 | On-Time |  | 2025-03-28 | 2025-03-28 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647747 | T2 DI RND MTN-TBL MTN #2 69/285 BNT STL | ICQ
LC | 123226059 | T-150 | T2NT DI MIDWAY-SANTA MARIA T-150 RMV VEG | MIDWAY | ETL.9240.TOWR | 2022-04-01 | 2022-03-28 | 2023-12-22 | On-Time |  | 2025-03-28 | 2025-03-28 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH TR2N PRTO AIR FRAA | Overgrown | Vegetation | Remove
LC | 123226597 | 032/267 | T2NT DI BRDGVLLE-CTTNWD 32/267 RPR ADSS | TABLEMTN | ETL.1110.POLE.STPS | 2022-04-01 | 2022-03-28 | 2023-05-11 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45644249 | T2 DI BRDGVLLE-CTTNWD 32/267 RPR ADSS LB | ICW
LC | 123235101 | 004/004 | T2NT DI TRINITY MAPLE CREEK 4/4 RPL SPLW | EUREKA | ETL.8170.INSL.NCER | 2022-04-02 | 2022-03-28 | 2024-02-20 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Splice-Wood | Repair | 45441773 | T2 DI TRNTY MPL CRK 4/4 RPL SPLW | ICW
LC | 123262253 | 032/003 | T2NT DI CLINGA #1-SN MIGL 32/3 RPR STRT | PISMOBCH | ETL.8580.TOWR | 2022-04-07 | 2022-03-28 | 2024-03-14 | On-Time |  | 2025-03-28 | 2025-03-28 | 543 | TR2N | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45638425 | T2 DI CLINGA #1-SN MIGL 32/3 RPR STRT | ICQ
LC | 123275441 | 005/040 | T3NT DI GRN VALLEY-LLAGAS 5/40 COMPLETE | MOSSLNDG | ETL.1720.POLE.WDPS | 2022-04-08 | 2022-03-28 | 2023-04-25 | On-Time |  | 2025-03-28 | 2025-03-28 | 372 | TR3N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE ACCL COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 31610972 | T3 EI GREEN VALLEY-LLAGAS 5/37R RPL POLE | 70Y
LC | 123294992 | 012/004 | T2NT DI MENDOCINO-WLLTS 12/4 RPL SPLW | WILLITS | ETL.7540.INSL.CERA | 2022-04-11 | 2022-03-28 | 2023-10-03 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Splice-Wood | Replace | 45590442 | T2 DI MENDOCINO-WLLTS 12/4 RPL SPLW | ICW
LC | 128383401 | 003/010 | T2 WV MNDCN-PHLO JCT-HPLND 3/10 INS DAMW | WILLITS | ETL.7520.INSL.NCER | 2024-03-28 | 2024-03-28 | 2025-03-05 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46414251 | T2 WV MNDCN-PHLO JCT-HPLND 3/10 INS DAMW | ICW
LC | 128383450 | 041/005 | T2 EI ELK-GUALALA 041/005 RPL STRW | WILLITS | ETL.8410.POLE.WOOD | 2024-03-28 | 2024-03-28 | 2025-06-02 | Past Due |  | 2024-09-28 | 2025-03-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557741 | T2 EI ELK-GUALALA 041/005 RPL STRW | 70Y
LC | 128383478 | 018/075 | T2 EI DIABLO-MIDWAY #2 18/075 RPR GYWT | PISMOBCH | ETL.5970.TOWR | 2024-03-28 | 2024-03-28 | 2024-12-31 | On-Time |  | 2025-03-28 | 2025-03-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46394448 | T2 EI DIABLO-MIDWAY #2 18/075 RPR GYWT | ICQ
LC | 128383562 | 016/161 | T2 EI ARCO-CHOLAME 16/161 RPR GYWW | MIDWAY | ETL.8440.POLE.NWOD | 2024-03-28 | 2024-03-28 | 2024-05-01 | On-Time |  | 2024-09-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46236409 | T2 EI ARCO-CHOLAME 16/161 RPR GYWW | ICW
LC | 128383609 | 020/280 | T2 SSQC-SNT YNZ SW ST 20/280 RPL STRW | PISMOBCH | ETL.3700.POLE.WOOD | 2024-03-28 | 2024-03-28 | 2025-05-07 | Past Due |  | 2025-03-28 | 2025-03-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP PUBL TRAF SWRK CLR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573836 | T2 EI SSQC-SNT YNZ SW ST 20/280 RPL STRW | 70Y
LC | 128384378 | 004/034 | T2 EI VACA-SUISUN 004/034 INS DAMS | SACTO | ETL.4070.INSL.NCER | 2024-03-28 | 2024-03-28 | 2025-03-12 | On-Time |  | 2025-03-28 | 2025-03-28 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Steel | Install | 46324616 | T2 EI VACA-SUISUN 004/034 INS DAMS | ICS
LC | 128384484 | 001/035 | T2 WV KILARC-DESCHUTES 001/035 RPL POLE | TABLEMTN | ETL.7300.POLE.WOOD | 2024-03-28 | 2024-03-28 | 2025-03-10 | On-Time |  | 2025-03-28 | 2025-03-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573768 | T2 WV KILARC-DESCHUTES 001/035 RPL POLE | 70Y
LC | 128384583 | 010/048 | T2 BRENTWOOD-KELSO 10/048 RPR STRT | CONCORD | ETL.4410.TOWR | 2024-03-28 | 2024-03-28 | 2025-03-06 | On-Time |  | 2025-03-28 | 2025-03-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286919 | T2 BRENTWOOD-KELSO 10/048 RPR STRT | ICQ
LC | 128384653 | 015/155 | T2 EI ARCO-CHOLAME 15/155 RMV NEST | MIDWAY | ETL.8440.POLE.NWOD | 2024-03-28 | 2024-03-28 | 2025-01-08 | On-Time |  | 2025-03-28 | 2025-03-28 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46302365 | T2 EI ARCO-CHOLAME 15/155 RMV NEST | ICS
LC | 128384752 | 009/053 | T2 EI SBRNT-STNDRD OIL #2 09/53 RPL INSS | CONCORD | ETL.3790.INSL | 2024-03-28 | 2024-03-28 | 2025-05-20 | Past Due |  | 2025-03-28 | 2025-03-28 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574949 | T0 DI SBRANTE-STNRD OIL #2 016/100 RPL I | 93K
LC | 128385231 | 018/257 | T2 EI SSQC-SNT YNZ SW ST 18/257 RPR GYWW | PISMOBCH | ETL.3700.POLE.NWOD | 2024-03-28 | 2024-03-28 | 2025-02-20 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391101 | T2 EI SSQC-SNT YNZ SW ST 18/257 RPR GYWW | ICW
LC | 128385241 | 001/012 | T2 SOBRANTE-MORAGA 1/12 BENT STL | CONCORD | ETL.3742.TOWR | 2024-03-28 | 2024-03-28 | 2024-03-28 | Past Due |  | 2025-03-28 | 2025-03-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286913 | T2 EI SOBRANTE-MORAGA 1/12 BENT STL | ICQ
LC | 128385291 | 015/152 | T2 EI ARCO-CHOLAME 15/152 RPL STRW | MIDWAY | ETL.8440.POLE.WOOD | 2024-03-28 | 2024-03-28 | 2025-01-10 | On-Time |  | 2025-03-28 | 2025-03-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35554105 | T2 EI ARCO-CHOLAME 15/152 RPL STRW | 70Y
LC | 128385432 | 001/011 | T2 EI SOBRANTE-MORAGA 1/11 RPR STRT | CONCORD | ETL.3742.TOWR | 2024-03-28 | 2024-03-28 | 2025-03-24 | On-Time |  | 2025-03-28 | 2025-03-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46286912 | T2 EI SOBRANTE-MORAGA 1/11 RPR STRT | ICQ
LC | 128385444 | 018/256 | T2 EI SSQC-SNT YNZ SW ST 18/256 RPR GYWW | PISMOBCH | ETL.3700.POLE.NWOD | 2024-03-28 | 2024-03-28 | 2025-02-20 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK ACCL ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391100 | T2 EI SSQC-SNT YNZ SW ST 18/256 RPR GYWW | ICW
LC | 128385757 | 008/050 | T2 EI SBRNT-STNDRD OIL #2 08/50 RPL INSS | CONCORD | ETL.3790.INSL | 2024-03-28 | 2024-03-28 | 2025-05-20 | Past Due |  | 2025-03-28 | 2025-03-28 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574949 | T0 DI SBRANTE-STNRD OIL #2 016/100 RPL I | 93K
LC | 128386006 | 013/006 | T2 EI TRINITY-MAPLE CREEK 13/06 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-03-28 | 2024-03-28 | 2025-01-21 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345709 | T2 EI TRINITY-MAPLE CREEK 13/06 RPR GYWW | ICW
LC | 128386249 | 000/008 | T2 DI COLGATE-PALERMO 0/8 RPR JUMW | SACTO | ETL.6500.INSL.NCER | 2024-03-28 | 2024-03-28 | 2025-03-25 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46383049 | T2 DI COLGATE-PALERMO 0/8 RPR JUMW | ICW
LC | 128386323 | 000/007 | T2 OLEUM-NRTH TWR-CHRSTE 0/7 TOUCH | CONCORD | ETL.3180.TOWR | 2024-03-28 | 2024-03-28 | 2025-05-07 | Past Due |  | 2024-09-28 | 2025-03-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46488995 | T2 OLEUM-NRTH TWR-CHRSTE 0/7 TOUCH | ICQ
LC | 128386413 | 005/057 | T2 DI PARADISE-BUTTE 5/57 RPL INSS | TABLEMTN | ETL.4396.INSL.NCER | 2024-03-28 | 2024-03-28 | 2024-07-13 | On-Time |  | 2025-03-28 | 2025-03-28 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35543299 | T2 DI PARADISE-BUTTE RPL INSS 2 TSPS | 93K
LC | 128387133 | 002/027 | T2 DI MONTA VISTA-BURNS 2/27 TOUCH | MOSSLNDG | ETL.7590.POLE.NWOD | 2024-03-28 | 2024-03-28 | 2025-05-11 | Past Due |  | 2024-09-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Steel | Repair | 46523440 | T2 DI MONTA VISTA-BURNS 2/27 TOUCH | ICW
LC | 128388635 | 004/056 | T2 DI BRNS-LONE STR #1 4/56 RPR ANCW | MOSSLNDG | ETL.6230.POLE.NWOD | 2024-03-29 | 2024-03-28 | 2025-03-13 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46391266 | T2 DI BRNS-LONE STR #1 4/56 RPR ANCW | ICW
LC | 128388637 | 004/056 | T2 DI BRNS-LONE STR #1 4/56 RPR INSW | MOSSLNDG | ETL.6230.INSL.NCER | 2024-03-29 | 2024-03-28 | 2025-03-13 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46391268 | T2 DI BRNS-LONE STR #1 4/56 RPR INSW | ICW
LC | 128394701 | 048/005 | T2 HUMBLDT-TRINITY 48/5C RPL POLE | EUREKA | ETL.1820.POLE.WDPS | 2024-03-30 | 2024-03-28 | 2024-03-28 | Past Due |  | 2025-03-28 | 2025-03-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | REGW PATR OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35542069 | T2 EI HUMBOLDT-TRINITY 48/5L RPL POLE | 70Y
LC | 128416271 | 000/007B | T2 DI KANAKA TP 0/7 RPR JUMW | TABLEMTN | ETL.4223.INSL.NCER | 2024-04-01 | 2024-03-28 | 2024-08-16 | On-Time |  | 2024-06-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46227547 | T2 DI KANAKA TP 0/7 RPR JUMW | ICW
LC | 128466786 | 004/050 | T2 DI BURNS-LONE STAR #1 4/50 RMV VEG | MOSSLNDG | ETL.6230.POLE.WDPS | 2024-04-05 | 2024-03-28 | 2024-05-30 | On-Time |  | 2024-09-28 | 2025-03-28 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128466788 | 004/050 | T2 DI BRNS-LNE STR #1 4/50L RPR ANCW | MOSSLNDG | ETL.6230.POLE.WDPS | 2024-04-05 | 2024-03-28 | 2024-05-22 | On-Time |  | 2024-09-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46235979 | T2 DI BRNS-LNE STR #1 4/50L RPR ANCW | ICW
LC | 128492390 | 004/055 | T2 DI BURNS-LONE STAR#1 4/55 RPL DAMW | MOSSLNDG | ETL.6230.INSL.NCER | 2024-04-08 | 2024-03-28 | 2025-03-13 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46391275 | T2 DI BURNS-LONE STAR#1 4/55 RPL DAMW | ICW
LC | 128492438 | 000/001 | T2 DI COLGATE-SMRVL #1 0/1 RPR GYWW | SACTO | ETL.6510.POLE.NWOD | 2024-04-08 | 2024-03-28 | 2025-01-09 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324606 | T2 DI COLGATE-SMRVL #1 0/1 RPR GYWW | ICW
LC | 128492541 | 017/000 | T2 DI HUMBOLDT BAY-RIO DLL 17/0 RPR GYWW | EUREKA | ETL.7100.POLE.WOOD | 2024-04-08 | 2024-03-28 | 2024-10-16 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46329254 | T2 DI HUMBOLDT BAY-RIO DLL 17/0 RPR GYWW | ICW
LC | 128492542 | 017/000 | T2 DI HUMBOLDT BAY-RIO DEL 17/0 RPR POLE | EUREKA | ETL.7100.POLE.WOOD | 2024-04-08 | 2024-03-28 | 2025-03-13 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46328557 | T2 DI HUMBOLDT BAY-RIO DEL 17/0 RPR POLE | ICW
LC | 128492631 | 000/005 | T2 DI KANAKA TAP 0/5L RPR GYWW | TABLEMTN | ETL.4223.POLE.STPS | 2024-04-08 | 2024-03-28 | 2024-08-15 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46230787 | T2 DI KANAKA TAP 00/05 RPR GYWW | ICW
LC | 128492634 | 000/005 | T2 DI KANAKA TAP 00/05 RMV VEG | TABLEMTN | ETL.4223.POLE.STPS | 2024-04-08 | 2024-03-28 | 2025-05-29 | Past Due |  | 2025-03-28 | 2025-03-28 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | Overgrown | Vegetation | Remove
LC | 128492635 | 000/005 | T2 DI KANAKA TAP 00/05 RPR ANCW | TABLEMTN | ETL.4223.POLE.STPS | 2024-04-08 | 2024-03-28 | 2024-08-15 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46305285 | T2 DI KANAKA TAP 00/05 RPR ANCW | ICW
LC | 128492735 | 012/000A | T2 DI KONOCTI-MIDDLETOWN 12/00A RPR GYWS | WILLITS | ETL.6380.POLE.NWOD | 2024-04-08 | 2024-03-28 | 2025-03-11 | On-Time |  | 2025-03-28 | 2025-03-28 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 46414253 | T2 DI KONOCTI-MIDDLETOWN 12/00A RPR GYWS | ICS
LC | 128493538 | :019/010 | T2 DI EAGLE ROCK-CORTNA :19/10L RPR ANCW | WILLITS | ETL.1470.POLE.STPS | 2024-04-08 | 2024-03-28 | 2025-03-13 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46308189 | T2 DI EAGLE ROCK-CORTNA :19/10L RPR ANCW | ICW
LC | 128493604 | 005/105 | T2 DI BURNS-LONE STAR #2 5/105 RMV VEG | MOSSLNDG | ETL.6240.POLE.STPS | 2024-04-08 | 2024-03-28 | 2024-12-09 | On-Time |  | 2025-03-28 | 2025-03-28 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128493606 | 005/105 | T2 DI BURNS-LONE STAR #2 5/105 RPR GYWW | MOSSLNDG | ETL.6240.POLE.STPS | 2024-04-08 | 2024-03-28 | 2025-03-08 | On-Time |  | 2025-03-28 | 2025-03-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391234 | T2 DI BURNS-LONE STAR #2 5/105 RPR GYWW | ICW
LC | 123207012 | 059/252 | T2NT EI RND MN-TBL MT #2 59/252 BNT STRT | TABLEMTN | ETL.6070.TOWR | 2022-03-29 | 2022-03-29 | 2023-08-22 | On-Time |  | 2025-03-29 | 2025-03-29 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647718 | T2 EI RND MTN-TBL MT #2 59/252 BNT STEEL | ICQ
LC | 123207979 | 055/236 | T2NT EI RND MTN-TB MT #2 55/236 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2022-03-29 | 2022-03-29 | 2023-08-30 | On-Time |  | 2025-03-29 | 2025-03-29 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO CLMB FRAB | Overgrown | Vegetation | Remove
LC | 123208539 | 055/237 | T2NT EI RND MTN-TB MT #2 55/237 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2022-03-29 | 2022-03-29 | 2023-11-27 | On-Time |  | 2025-03-29 | 2025-03-29 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2N PRTO CLMB FRAB | Overgrown | Vegetation | Remove
LC | 123208598 | 055/237 | T2NT EI RND MTN-TB MT #1 55/237 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2022-03-29 | 2022-03-29 | 2023-09-01 | On-Time |  | 2025-03-29 | 2025-03-29 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2N PRTO CLMB FRAB | Overgrown | Vegetation | Remove
LC | 123209475 | 000/004 | T2NT EI SBT-GRZLY-CLRMNT #2 0/4 RPL INSS | CONCORD | ETL.3750.POLE.WOOD | 2022-03-29 | 2022-03-29 | 2023-06-14 | On-Time |  | 2025-03-29 | 2025-03-29 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Insulator-Steel | Replace | 31640243 | T3 DI SBRNT-GRZLY-CLRT#2 A02/14 RPL INSW | 93K
LC | 123227790 | T-142 | T0 T2NT DI MDWY SNT MR T-142 RMV VEGN | MIDWAY | ETL.9240.TOWR | 2022-04-01 | 2022-03-29 | 2023-12-22 | On-Time |  | 2025-03-29 | 2025-03-29 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH PRTO AIR FRAA TER0 | Overgrown | Vegetation | Remove
LC | 123235862 | 027/241 | T2NT DI RND MTN-CTNWD #2 27/241 RPR FND | TABLEMTN | ETL.5640.TOWR | 2022-04-02 | 2022-03-29 | 2023-08-10 | On-Time |  | 2025-03-29 | 2025-03-29 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45648223 | T2NT DI RND MTN-CTNWD #2 27/241 RPR FND | ICQ
LC | 123242920 | 038/333 | T2NT DI RNDMTN- CTTNWD#3 38/333 RPR FOND | TABLEMTN | ETL.5650.TOWR | 2022-04-04 | 2022-03-29 | 2023-08-03 | On-Time |  | 2025-03-29 | 2025-03-29 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45648246 | T2 DI RND MTN- CTTNWD #3 38/333 RPR FOND | ICQ
LC | 123281602 | 042/364 | T2NT DI PIT #1 CTNWD 42/364 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2022-04-09 | 2022-03-29 | 2023-08-02 | On-Time |  | 2025-03-29 | 2025-03-29 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2N PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45639728 | T2 DI PIT #1 CTNWD 42/364 RPR FOND | ICQ
LC | 123298696 | T-155 | T2NT DI MIDWAY-SANTA MARIA T-155 RMV VEG | MIDWAY | ETL.9240.TOWR | 2022-04-11 | 2022-03-29 | 2023-12-22 | On-Time |  | 2025-03-29 | 2025-03-29 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW OTHR FIRE COMP OH TR2N PRTO AIR FRAA | Overgrown | Vegetation | Remove
LC | 123300472 | 011/058 | T2NT DI RND MTN TBL MN #1 11/58 RMV DBRS | TABLEMTN | ETL.6060.TOWR | 2022-04-11 | 2022-03-29 | 2023-08-15 | On-Time |  | 2025-03-29 | 2025-03-29 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2N PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 45698856 | T2 DI RND MTN TBL MTN #1 11/58 RMV DBRW | ICS
LC | 123311154 | 018/001 | T0 T2NT DI CLNG #1 SN MGL 18/1 RPR STRT | FRESNO | ETL.8580.TOWR | 2022-04-12 | 2022-03-29 | 2023-11-22 | On-Time |  | 2025-03-29 | 2025-03-29 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH PRTO AIR FRAA TER0 | No Good/Out of Stdrd | Structure-Tower | Repair | 45639023 | T0 DI CLNG #1 SN MGL 18/1 RPR STRT | ICQ
LC | 127160058 | 003/033 | T2 BRIDGEVILLE-CTTNWD 03/033L TOUCH | TABLEMTN | ETL.1110.POLE.STPS | 2023-09-29 | 2023-09-29 | 2025-05-09 | Past Due |  | 2025-03-29 | 2025-03-29 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB XMPT TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46486711 | T2 BRIDGEVILLE-CTTNWD 03/033L TOUCH | ICW
LC | 128388734 | 017/109-GUYA | T2 EI NWRK-LIVERMRE 017/109-GUY RPR ANCW | CONCORD | ETL.7660.POLE.WOOD | 2024-03-29 | 2024-03-29 | 2024-04-30 | On-Time |  | 2024-09-29 | 2025-03-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46220496 | T2 NEWARK-LIVERMORE_017/109-GUY RPR ANCW | ICW
LC | 128388993 | 007/001 | T2 EI HUMBOLDT-MAPLE CREEK 7/1 RPR CRSW | EUREKA | ETL.7130.POLE.WOOD | 2024-03-29 | 2024-03-29 | 2025-03-27 | On-Time |  | 2025-03-29 | 2025-03-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46345710 | T2 EI HUMBOLDT-MAPLE CREEK 7/1 RPR CRSW | ICW
LC | 128389140 | 004/029 | T2 EI SOBRANTE-MORAGA 4/29 BENT STL | CONCORD | ETL.3742.TOWR | 2024-03-29 | 2024-03-29 | 2025-03-04 | On-Time |  | 2025-03-29 | 2025-03-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287080 | T2 EI SOBRANTE-MORAGA 4/29 BENT STL | ICQ
LC | 128389209 | 013/274 | T2 EI COLEMAN-SOUTH 13/274 RPL STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-03-29 | 2024-03-29 | 2025-03-27 | On-Time |  | 2025-03-29 | 2025-03-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556793 | T2 EI COLEMAN-SOUTH 13/274 RPL STRW | 70Y
LC | 128389241 | 013/276 | T2 EI COLEMAN-SOUTH 13/276 RPL STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-03-29 | 2024-03-29 | 2025-03-27 | On-Time |  | 2025-03-29 | 2025-03-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35572518 | T2 EI COLEMAN-SOUTH 13/276 RPL STRW | 70Y
LC | 128389250 | 013/273 | T2 EI COLEMAN-SOUTH 13/273 RPL STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-03-29 | 2024-03-29 | 2025-03-27 | On-Time |  | 2025-03-29 | 2025-03-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572517 | T2 EI COLEMAN-SOUTH 13/273 RPL STRW | 70Y
LC | 128389486 | 007/002 | T2 EI HUMBOLDT-MAPLE CREEK 7/2 GO95 | EUREKA | ETL.7130.POLE.WOOD | 2024-03-29 | 2024-03-29 | 2025-04-02 | Past Due |  | 2025-03-29 | 2025-03-29 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35574773 | T2 EI HUMBOLDT-MAPLE CREEK 7/2 GO95 | 93G
LC | 128389488 | 007/003 | T2 EI HUMBLDT-MAPLE CREEK 7/3 GO95 CLEAR | EUREKA | ETL.7130.POLE.WOOD | 2024-03-29 | 2024-03-29 | 2025-04-02 | Past Due |  | 2025-03-29 | 2025-03-29 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35574774 | T2 EI HUMBLDT-MAPLE CREEK 7/3 GO95 CLEAR | 93G
LC | 128389516 | 004/031 | T2 EI SOBRANTE-MORAGA 4/31 BENT STL | CONCORD | ETL.3742.TOWR | 2024-03-29 | 2024-03-29 | 2025-03-04 | On-Time |  | 2025-03-29 | 2025-03-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287081 | T2 EI SOBRANTE-MORAGA 4/31 BENT STL | ICQ
LC | 128390687 | 022/004 | T2 EI PHILO JCT-ELK 22/004 RPR STRW | WILLITS | ETL.7780.POLE.WOOD | 2024-03-29 | 2024-03-29 | 2025-01-27 | On-Time |  | 2025-03-29 | 2025-03-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46333934 | T2 EI PHILO JCT-ELK 22/004 RPR STRW | ICW
LC | 128392591 | 012/249 | T2 EI COLEMAN-SOUTH 12/249 RPR GYWW | TABLEMTN | ETL.6450.POLE.NWOD | 2024-03-29 | 2024-03-29 | 2024-05-08 | On-Time |  | 2024-09-29 | 2025-03-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46222495 | T2 EI COLEMAN-SOUTH 12/249 RPR GYWW | ICW
LC | 128392727 | 005/035 | T2 EI SOBRANTE-MORAGA 5/35 BNT STL | CONCORD | ETL.3742.TOWR | 2024-03-29 | 2024-03-29 | 2025-03-04 | On-Time |  | 2025-03-29 | 2025-03-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287082 | T2 EI SOBRANTE-MORAGA 5/35 BNT STL | ICQ
LC | 128393307 | 017/004 | T2 EI TRINITY-MPL CRK 17/4L COMPLETE | EUREKA | ETL.8170.POLE.WDPS | 2024-03-29 | 2024-03-29 | 2025-03-09 | On-Time |  | 2025-03-29 | 2025-03-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345711 | T2 EI TRINITY-MPL CRK 17/4L RPR GYWW | ICW
LC | 128393327 | 019/004 | T2 EI TRINITY-MAPLE CREK 19/004 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-03-29 | 2024-03-29 | 2024-04-30 | On-Time |  | 2025-03-29 | 2025-03-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46229153 | T2 EI TRINITY-MAPLE CREK 19/004 RPR GYWW | ICW
LC | 128393329 | 015/071 | T2 DI MSS LNDG-LS AGLS SS 15/71 COMPLETE | MOSSLNDG | ETL.5340.INSL | 2024-03-29 | 2024-03-29 | 2024-08-11 | On-Time |  | 2024-09-29 | 2025-03-29 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW IR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35545334 | T2 DI MSS LNDG-LS AGLS SS 15/71 RPL INSS | 93K
LC | 128393370 | 017/004 | T2 EI TRNTY-MPL CRK 17/4R COMPLETE | EUREKA | ETL.8170.POLE.WDPS | 2024-03-29 | 2024-03-29 | 2025-03-09 | On-Time |  | 2025-03-29 | 2025-03-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46345712 | T2 EI TRNTY-MPL CRK 17/4R RPR ANCW | ICW
LC | 128393766 | 002/004 | T2 EI TRINITY-MAPLE CREEK 02/04 RPL ANCW | EUREKA | ETL.8170.POLE.WOOD | 2024-03-29 | 2024-03-29 | 2025-03-23 | On-Time |  | 2025-03-29 | 2025-03-29 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572119 | T2 EI TRINITY-MAPLE CREEK 02/04 RPL ANCW | 93E
LC | 128396254 | 001/018 | T2 CHRISTIE-FRANKLIN #1 1/18 COMPLETE | CONCORD | ETL.6350.POLE.NWOD | 2024-04-01 | 2024-03-29 | 2025-03-21 | On-Time |  | 2025-03-29 | 2025-03-29 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573105 | T2 CHRISTIE-FRANKLIN #1 1/18 RPL ANCHOR | 93E
LC | 128510224 | 000/001 | T2 DI SALT SPRNGS-TIGR CRK 0/1 RPL HRDT | VICTOR | ETL.3500.TOWR | 2024-04-10 | 2024-03-29 | 2025-03-26 | On-Time |  | 2025-03-29 | 2025-03-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46404419 | T2 DI SALT SPRNGS-TIGR CRK 0/1 RPL HRDT | ICQ
LC | 128510228 | 000/003 | T2 DI SALT SPRNGS-TIGR CRK 0/3 RPR STRT | VICTOR | ETL.3500.TOWR | 2024-04-10 | 2024-03-29 | 2025-03-26 | On-Time |  | 2025-03-29 | 2025-03-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46326010 | T2 DI SALT SPRNGS-TIGR CRK 0/3 RPR STRT | ICQ
LC | 128573022 | 004/039 | T2 PLACER-GOLD HILL #1 4/39 TOUCH | SACTO | ETL.3340.TOWR | 2024-04-18 | 2024-03-29 | 2025-02-21 | On-Time |  | 2024-09-29 | 2025-03-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46460824 | T2 PLACER-GOLD HILL #1 4/39 RPR STRT | ICQ
LC | 123213314 | 093/476 | T2NT EI MLN-RND MTN #2 93/476 BNT STEEL | TABLEMTN | ETL.6020.TOWR | 2022-03-30 | 2022-03-30 | 2023-08-16 | On-Time |  | 2025-03-30 | 2025-03-30 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45617416 | T2 EI MLN-RND MTN #2 93/476 BNT STEEL | ICQ
LC | 123214812 | 092/472 | T2NT EI MLN-RND MNTN #2 92/472 BNT STEEL | TABLEMTN | ETL.6020.TOWR | 2022-03-30 | 2022-03-30 | 2023-08-16 | On-Time |  | 2025-03-30 | 2025-03-30 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45617415 | T2 EI MLN-RND MNTN #2 92/472 BNT STEEL | ICQ
LC | 123216577 | 092/469 | T2NT EI MLN-RND MTN #2 92/469 BNT STEEL | TABLEMTN | ETL.6020.TOWR | 2022-03-30 | 2022-03-30 | 2023-08-16 | On-Time |  | 2025-03-30 | 2025-03-30 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45617414 | T2 EI MLN-RND MTN #2 92/469 BNT STEEL | ICQ
LC | 123235714 | 022/197 | T2NT DI BRDGVLE-CTNWD 22/197 FIBER LABEL | TABLEMTN | ETL.1110.POLE.WDPS | 2022-04-02 | 2022-03-30 | 2023-06-21 | On-Time |  | 2025-03-30 | 2025-03-30 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45644256 | T2 DI BRDGVLLE-CTTNWD 22/197 FIBER LABEL | ICW
LC | 123262352 | 038/329 | T2NT DI PT #1 CTNWD 38/329 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2022-04-07 | 2022-03-30 | 2023-10-23 | On-Time |  | 2025-03-30 | 2025-03-30 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45639722 | T2 DI PT #1 CTNWD 38/329 BNT STEEL | ICQ
LC | 123301078 | T-160 | T2NT DI MIDWAY-SANTA MARIA T-160 RMV VEG | MIDWAY | ETL.9240.TOWR | 2022-04-11 | 2022-03-30 | 2023-12-22 | On-Time |  | 2025-03-30 | 2025-03-30 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2N PRTO AIR FRAA | Overgrown | Vegetation | Remove
LC | 123220845 | 011/059 | T2NT EI RND MTN-TB MT #1 11/59 BNT STEEL | TABLEMTN | ETL.6060.TOWR | 2022-03-31 | 2022-03-31 | 2023-08-15 | On-Time |  | 2025-03-31 | 2025-03-31 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644414 | T2 EI RND MTN-TBL MTN #1 11/59 BNT STEEL | ICQ
LC | 123221067 | 009/035 | T3NT EI DIABLO-MIDWAY #2 9/35 RPR GYWS | PISMOBCH | ETL.5970.TOWR | 2022-03-31 | 2022-03-31 | 2023-07-05 | On-Time |  | 2025-03-31 | 2025-03-31 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3N PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45638564 | T3 EI DIABLO-MIDWAY #2 9/35 RPR GYWS | ICS
LC | 123221176 | 011/060 | T2NT EI RND MTN-TL MN #1 11/60 BNT STEEL | TABLEMTN | ETL.6060.TOWR | 2022-03-31 | 2022-03-31 | 2023-08-15 | On-Time |  | 2025-03-31 | 2025-03-31 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644415 | T2 EI RND MTN-TBL MTN #1 11/60 BNT STEEL | ICQ
LC | 123221878 | 011/061 | T2NT EI RND MTN-TB MTN #2 11/61 RPR GYWS | TABLEMTN | ETL.6070.TOWR | 2022-03-31 | 2022-03-31 | 2023-08-15 | On-Time |  | 2025-03-31 | 2025-03-31 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45700168 | T2NT EI RND MTN-TB MTN #2 11/61 RPR GYWS | ICS
LC | 123221879 | 011/061 | T2NT EI RND MTN-TL MN #2 11/61 BNT STEEL | TABLEMTN | ETL.6070.TOWR | 2022-03-31 | 2022-03-31 | 2023-08-15 | On-Time |  | 2025-03-31 | 2025-03-31 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647409 | T2 EI RND MTN-TBL MTN #2 11/61 BNT STEEL | ICQ
LC | 123223171 | 011/062 | T2NT EI RND MTN-TL MN #1 11/62 BNT STEEL | TABLEMTN | ETL.6060.TOWR | 2022-03-31 | 2022-03-31 | 2023-08-21 | On-Time |  | 2025-03-31 | 2025-03-31 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644416 | T2 EI RND MTN-TBL MTN #1 11/62 BNT STEEL | ICQ
LC | 123245427 | 002/033 | T2NT DI PARADISE-BUTTE 2/33 RPL INSS | TABLEMTN | ETL.4396.INSL.NCER | 2022-04-05 | 2022-03-31 | 2023-04-24 | On-Time |  | 2025-03-31 | 2025-03-31 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 31616649 | T2 DI PARADISE-BUTTE 2/33 RPL INSS | 93K
LC | 123318835 | 010/139 | T2NT DI DELTA-MTN GATE 10/139 RMV BUTT | TABLEMTN | ETL.6750.POLE.WDPS | 2022-04-13 | 2022-03-31 | 2023-06-21 | On-Time |  | 2025-03-31 | 2025-03-31 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE DURA BRIN | Debris/Nest/etc. | Structure-Wood | Remove | 45681957 | T2NT DI DELTA-MTN GATE 10/139 RMV BUTT | ICW
LC | 123227210 | 012/064 | T2NT EI RND MTN-TL MN #1 12/64 RPR STEEL | TABLEMTN | ETL.6060.TOWR | 2022-04-01 | 2022-04-01 | 2023-08-28 | On-Time |  | 2025-04-01 | 2025-04-01 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644417 | T2 EI RND MTN-TBL MTN #1 12/64 RPR STEEL | ICQ
LC | 123228926 | 016/066 | T2NT EI DBLO-GATES #1 16/66 RPR GYWS | PISMOBCH | ETL.5960.TOWR | 2022-04-01 | 2022-04-01 | 2023-07-28 | On-Time |  | 2025-04-01 | 2025-04-01 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | Missing | Guy Wire-Steel | Install | 45639021 | T2 EI DIABLO-GATES #1 016/066 RPR GYWS | ICS
LC | 123235081 | 011/311 | T3NT EI COLGATE-ALEGHANY 11/311 RPL STRW | SACTO | ETL.6470.POLE.WOOD | 2022-04-02 | 2022-04-01 | 2023-06-22 | On-Time |  | 2025-04-01 | 2025-04-01 | 372 | TR3N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR3N PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 31633458 | T3 DI COLGATE-ALLGHNY 011/293 RPL STRW | 70Y
LC | 123345101 | 065/274 | T2NT DI RND MT TBL MT #1 65/274 RPR FOND | TABLEMTN | ETL.6060.TOWR | 2022-04-16 | 2022-04-01 | 2023-08-08 | On-Time |  | 2025-04-01 | 2025-04-01 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45644512 | T2 DI RND MTN TBL MTN #1 65/274 RPR FOND | ICQ
LC | 128396335 | :012/001 | T2 EGLE RCK-CRTINA :12/1 SW#189 RPR SWTC | WILLITS | ETL.1470.POLE.NWOD | 2024-04-01 | 2024-04-01 | 2024-04-01 | Past Due |  | 2024-10-01 | 2025-04-01 | 623 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 PRTO FRAB DURA BRIN | Out of Adjustment | Switch | Repair | 46227574 | T2 EAGLE ROCK-CORTINA :012/1 RPR SWITCH | ICE
LC | 128397067 | 004/018 | T2 EI MORRO BAY-DIABLO 004/018 RPL INSS | PISMOBCH | ETL.5260.INSL.CERA | 2024-04-01 | 2024-04-01 | 2024-04-01 | Past Due |  | 2025-04-01 | 2025-04-01 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35585694 | T2 EI MORRO BAY-DIABLO 004/018 RPL INSS | 93K
LC | 128397139 | 015/087 | T2 EI MARTINEZ-SOBRANTE 015/087 HANGER | CONCORD | ETL.2270.INSL.CERA | 2024-04-01 | 2024-04-01 | 2025-03-27 | On-Time |  | 2025-04-01 | 2025-04-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46287088 | T2 EI MARTINEZ-SOBRANTE 015/087 HANGER | ICQ
LC | 128397140 | 015/087 | T2 EI CHRISTIE-SOBRANTE 015/087 HANGER | CONCORD | ETL.1260.INSL.CERA | 2024-04-01 | 2024-04-01 | 2025-01-17 | On-Time |  | 2025-04-01 | 2025-04-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46287089 | T2 EI CHRISTIE-SOBRANTE 015/087 HANGER | ICQ
LC | 128398060 | 000/005 | T2 EI CHRISTIE-FRANKLIN#1 0/005 RPR GYWW | CONCORD | ETL.6350.POLE.NWOD | 2024-04-01 | 2024-04-01 | 2025-03-21 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46287083 | T2 EI CHRISTIE-FRANKLIN#1 0/005 RPR GYWW | ICW
LC | 128399272 | 041/009 | T2 EI ELK-GUALALA 041/009 RPL STRW | WILLITS | ETL.8410.POLE.WOOD | 2024-04-01 | 2024-04-01 | 2025-06-02 | Past Due |  | 2025-04-01 | 2025-04-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557742 | T2 EI ELK-GUALALA 041/009 RPL STRW | 70Y
LC | 128403186 | 000/006 | T2 EI CHRISTIE-FRANKLIN#1 0/006 RPR GYWW | CONCORD | ETL.6350.POLE.NWOD | 2024-04-01 | 2024-04-01 | 2024-08-07 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46234721 | T2 EI CHRISTIE-FRANKLIN#1 0/006 RPR GYWW | ICW
LC | 128403660 | 023/108 | T2 EI EAGLE ROCK-CORTINA 23/108 RPR INSS | WILLITS | ETL.1470.INSL.CERA | 2024-04-01 | 2024-04-01 | 2025-03-13 | On-Time |  | 2025-04-01 | 2025-04-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Insulator-Steel | Repair | 46491083 | T2 EI EAGLE ROCK-CORTINA 23/108 RPR INSS | ICS
LC | 128403889 | 005/030 | T2 EI PITTSBURG-CLAYTON #4 5/30 RPR INSS | CONCORD | ETL.3291.INSL | 2024-04-01 | 2024-04-01 | 2025-01-15 | On-Time |  | 2025-04-01 | 2025-04-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46287085 | T2 EI PITTSBURG-CLAYTON #4 5/30 RPR INSS | ICS
LC | 128404071 | 006/032 | T2 EI PTTSBRG-CLYTN #4 6/32 RPR INSS | CONCORD | ETL.3291.INSL | 2024-04-01 | 2024-04-01 | 2025-01-21 | On-Time |  | 2025-04-01 | 2025-04-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46287086 | T2 EI PTTSBRG-CLYTN #4 6/32 RPR INSS | ICS
LC | 128404559 | 016/004 | T2 EI TRINITY-MAPLE CREEK 16/4R RPR GYWW | EUREKA | ETL.8170.POLE.STPS | 2024-04-01 | 2024-04-01 | 2025-03-09 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345715 | T2 EI TRINITY-MAPLE CREEK 16/4R RPR GYWW | ICW
LC | 128405739 | 007/011 | T2 EI CHWCHLL-KRCKHFF 007/011 RPR POLE | FRESNO | ETL.1250.POLE.WOOD | 2024-04-01 | 2024-04-01 | 2025-03-27 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46298275 | T2 EI CHWCHLL-KRCKHFF 007/011 RPR POLE | ICW
LC | 128410172 | 016/131 | T2 EI CARBRY SS-RND MTN 16/131 RPL INSS | TABLEMTN | ETL.5410.INSL | 2024-04-01 | 2024-04-01 | 2025-03-10 | On-Time |  | 2025-04-01 | 2025-04-01 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569571 | T2 EI CARBRY SS-RND MTN RPL INSS 6 TWRS. | 93K
LC | 128410216 | 090/457 | T2 EI MALIN-ROUND MTN #2 90/457 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-01 | 2024-04-01 | 2025-02-12 | On-Time |  | 2025-04-01 | 2025-04-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381359 | T2 EI MALIN-ROUND MTN #2 90/457 RPR GYWT | ICQ
LC | 128410286 | 007/039 | T2 JFFRSN-HLLSDLE JCT 7/39 TOUCH | METCALF | ETL.7190.TOWR | 2024-04-01 | 2024-04-01 | 2025-04-21 | Past Due |  | 2024-10-01 | 2025-04-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAR NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485701 | T2 JFFRSN-HLLSDLE JCT 7/39 TOUCH | ICQ
LC | 128410436 | 012/262 | T2 EI COLEMAN-SOUTH 12/262 COMPLETE | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-01 | 2024-04-01 | 2025-03-24 | On-Time |  | 2025-04-01 | 2025-04-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556794 | T2 EI COLEMAN-SOUTH 12/259 RPL STRW | 70Y
LC | 128410466 | 012/259 | T2 EI COLEMAN-SOUTH 12/259 COMPLETE | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-01 | 2024-04-01 | 2025-03-24 | On-Time |  | 2025-04-01 | 2025-04-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556794 | T2 EI COLEMAN-SOUTH 12/259 RPL STRW | 70Y
LC | 128410617 | 046/002 | T2 EI ELK-GUALALA 046/002 RPL IBWW | WILLITS | ETL.8410.INSL.CERA | 2024-04-01 | 2024-04-01 | 2025-02-06 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Replace | 46308196 | T2 EI ELK-GUALALA 046/002 RPL IBWW | ICW
LC | 128411782 | 014/082 | T2 EI MARTINEZ-SOBRANTE 014/082 HANGER | CONCORD | ETL.2270.INSL | 2024-04-01 | 2024-04-01 | 2025-03-28 | On-Time |  | 2025-04-01 | 2025-04-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46287087 | T2 EI MARTINEZ-SOBRANTE 014/082 HANGER | ICQ
LC | 128413495 | 007/132 | T2 EI CARIBOU-WESTWOOD 07/132 RPR INSW | TABLEMTN | ETL.6300.INSL.NCER | 2024-04-01 | 2024-04-01 | 2024-07-10 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46227545 | T2 EI CARIBOU-WESTWOOD 07/132 RPR INSW | ICW
LC | 128413579 | 003/018 | T2 EI PTTSBRG-CLYTN #3 3/18 RMV NEST | CONCORD | ETL.3290.TOWR | 2024-04-01 | 2024-04-01 | 2025-01-15 | On-Time |  | 2025-04-01 | 2025-04-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46287084 | T2 EI PTTSBRG-CLYTN #3 3/18 RMV NEST | ICS
LC | 128414090 | 016/133 | T2 EI CRBRY SS-RND MTN 16/133 RMV VEG | TABLEMTN | ETL.5410.TOWR | 2024-04-01 | 2024-04-01 | 2025-01-03 | On-Time |  | 2025-04-01 | 2025-04-01 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128415275 | 000/002 | T2 EI JFFRSN-HLLSDLE JCT 0/2 RPL STRW | METCALF | ETL.7190.POLE.WOOD | 2024-04-01 | 2024-04-01 | 2024-04-01 | Past Due |  | 2024-10-01 | 2025-04-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35614429 | T2 EI JFFRSN-HLLSDLE JCT 0/2 RPL STRW | 70Y
LC | 128415393 | 016/134 | T2 EI CRBRY SS-RND MTN 16/134 RPL INSS | TABLEMTN | ETL.5410.INSL | 2024-04-01 | 2024-04-01 | 2025-03-11 | On-Time |  | 2025-04-01 | 2025-04-01 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569571 | T2 EI CARBRY SS-RND MTN RPL INSS 6 TWRS. | 93K
LC | 128415435 | 017/135 | T2 EI CRBRY SS-RND MTN 17/135 RPL INSS | TABLEMTN | ETL.5410.INSL | 2024-04-01 | 2024-04-01 | 2025-03-11 | On-Time |  | 2025-04-01 | 2025-04-01 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP PATR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569571 | T2 EI CARBRY SS-RND MTN RPL INSS 6 TWRS. | 93K
LC | 128415616 | 017/136 | T2 EI CRBRY SS-RND MTN 17/136 RPL INSS | TABLEMTN | ETL.5410.INSL | 2024-04-01 | 2024-04-01 | 2025-03-10 | On-Time |  | 2025-04-01 | 2025-04-01 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569571 | T2 EI CARBRY SS-RND MTN RPL INSS 6 TWRS. | 93K
LC | 128415929 | :017/005 | T2 EI EAGLE ROCK-REDBUD :017/05 RPR INSW | WILLITS | ETL.1480.INSL.NCER | 2024-04-01 | 2024-04-01 | 2025-03-10 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46308190 | T2 EI EAGLE ROCK-REDBUD :017/05 RPR INSW | ICW
LC | 128416021 | 000/002A | T2 POTTER VALLEY-MENDOCINO 0/2A RPR IBWW | WILLITS | ETL.7810.INSL.NCER | 2024-04-01 | 2024-04-01 | 2024-09-03 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46232914 | T2 POTTER VALLEY-MENDOCINO 0/2A RPR IBWW | ICW
LC | 128416355 | 008/043 | T2 EI CORTINA-MENDOCIN #1 8/043 RPL INSS | SACTO | ETL.1330.INSL.CERA | 2024-04-01 | 2024-04-01 | 2025-03-27 | On-Time |  | 2025-04-01 | 2025-04-01 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35603723 | T2 EI CORTINA-MENDOCIN #1 8/043 RPL INSS | 93K
LC | 128416441 | 009/048 | T2 EI CORTINA-MNDCN #1 9/48 RPR STRT | SACTO | ETL.1330.TOWR | 2024-04-01 | 2024-04-01 | 2025-01-17 | On-Time |  | 2025-04-01 | 2025-04-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46290223 | T2 EI CORTINA-MNDCN #1 9/48 RPR STRT | ICQ
LC | 128416450 | 010/049 | T2 EI CORTINA-MENDCINO #1 10/49 UNBURY | SACTO | ETL.1330.TOWR | 2024-04-01 | 2024-04-01 | 2025-01-17 | On-Time |  | 2025-04-01 | 2025-04-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46290239 | T2 EI CORTINA-MENDCINO #1 10/49 UNBURY | ICQ
LC | 128416460 | 009/048 | T2 EI EAGLE ROCK-CORTINA 9/48 RPL DMPS | SACTO | ETL.1470.INSL.CERA | 2024-04-01 | 2024-04-01 | 2025-02-17 | On-Time |  | 2025-04-01 | 2025-04-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Damper-Steel | Replace | 46308194 | T2 EI EAGLE ROCK-CORTINA 9/48 RPL DMPS | ICS
LC | 128416462 | 008/043 | T2 EAGLE ROCK-CORTINA 8/043 RPL INSS | SACTO | ETL.1470.INSL.CERA | 2024-04-01 | 2024-04-01 | 2025-06-02 | Past Due |  | 2025-04-01 | 2025-04-01 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577312 | T2 EI EAGLE ROCK-CORTINA RPL INSS IN 2 T | 93K
LC | 128428515 | 026/161 | T2 DI TESLA-SAL-MANT 26/161 COTTER | VICTOR | ETL.4000.INSL.CERA | 2024-04-02 | 2024-04-01 | 2024-05-05 | On-Time |  | 2024-07-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46229393 | T2 DI TESLA-SAL-MANT 26/161 COTTER | ICW
LC | 128428610 | 026/161 | T2 DI TESLA-SAL-MANT 26/161 RPR GYWW | VICTOR | ETL.4000.POLE.WOOD | 2024-04-02 | 2024-04-01 | 2025-02-26 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46299698 | T2 DI TESLA-SAL-MANT 26/161 RPR GYWW | ICW
LC | 128428619 | 026/161 | T2 DI TESLA-SAL-MANT 26/161 RPL HRDW | VICTOR | ETL.4000.POLE.WOOD | 2024-04-02 | 2024-04-01 | 2025-02-26 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46299699 | T2 DI TESLA-SAL-MANT 26/161 RPL HRDW | ICW
LC | 128428621 | 000/002 | T2 DI LUCERNE#1 TAP 00/002 RMV VEG | WILLITS | ETL.1331.POLE.NWOD | 2024-04-02 | 2024-04-01 | 2025-02-17 | On-Time |  | 2025-04-01 | 2025-04-01 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128428622 | 000/002 | T2 DI LUCERNE#1 TAP 00/002 RPR ANCW | WILLITS | ETL.1331.POLE.NWOD | 2024-04-02 | 2024-04-01 | 2025-03-19 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46414256 | T2 DI LUCERNE#1 TAP 00/002 RPR ANCW | ICW
LC | 128429175 | 026/160 | T2 DI TESLA SLADO MNTCA 26/160 RPR GYWW | VICTOR | ETL.4000.POLE.WOOD | 2024-04-02 | 2024-04-01 | 2025-02-26 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46299700 | T2 DI TESLA SLADO MNTCA 26/160 RPR GYWW | ICW
LC | 128429177 | 026/160 | T2 DI TESLA SLADO MNTCA 26/160 RPL ANCW | VICTOR | ETL.4000.POLE.WOOD | 2024-04-02 | 2024-04-01 | 2025-02-26 | On-Time |  | 2025-04-01 | 2025-04-01 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573517 | T2 DI TESLA SLADO MNTCA 26/160 RPL ANCW | 93E
LC | 128429178 | 026/160 | T2 DI TESLA SLADO MNTCA 26/160 RPR ANMW | VICTOR | ETL.4000.POLE.WOOD | 2024-04-02 | 2024-04-01 | 2025-02-26 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB BRIN | Missing | Animal Guard-Wood | Install | 46455758 | T2 DI TESLA SLADO MNTCA 26/160 RPR ANMW | ICW
LC | 128429179 | 026/160 | T2 DI TESLA SLADO MNTCA 26/160 RPR INSW | VICTOR | ETL.4000.INSL.CERA | 2024-04-02 | 2024-04-01 | 2025-02-26 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46299701 | T2 DI TESLA SLADO MNTCA 26/160 RPR INSW | ICW
LC | 128430007 | 020/007A | T2 DI KNOCTI MDLTWN 20/007A RPR GYWW | WILLITS | ETL.6380.POLE.NWOD | 2024-04-02 | 2024-04-01 | 2025-03-18 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337046 | T2 DI KNOCTI MDLTWN 20/007A RPR GYWW | ICW
LC | 128430325 | 011/004 | T2 MNDCNO HRTLY 11/004 RPR GYWW | WILLITS | ETL.7510.POLE.NWOD | 2024-04-02 | 2024-04-01 | 2024-04-01 | Past Due |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46333937 | T2 DI MNDCNO HRTLY 11/004 RPR GYWW | ICW
LC | 128457326 | 014/082 | T2 EI MARTINEZ-SOBRANTE 014/082 RPL INSS | CONCORD | ETL.2270.INSL | 2024-04-05 | 2024-04-01 | 2025-03-28 | On-Time |  | 2025-04-01 | 2025-04-01 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575033 | T2 EI MARTINEZ-SOBRANTE RPL INSS IN 2 TW | 93K
LC | 128457446 | 015/087 | T2 EI MARTINEZ-SOBRA 15/087 RPL INSS | CONCORD | ETL.2270.INSL.CERA | 2024-04-05 | 2024-04-01 | 2025-03-27 | On-Time |  | 2025-04-01 | 2025-04-01 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575033 | T2 EI MARTINEZ-SOBRANTE RPL INSS IN 2 TW | 93K
LC | 128457530 | 015/087 | T2 EI CHRISTIE SOBRANTE 15/087 RPL INSS | CONCORD | ETL.1260.INSL.CERA | 2024-04-05 | 2024-04-01 | 2025-01-17 | On-Time |  | 2025-04-01 | 2025-04-01 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575034 | T2 EI CHRISTIE SOBRANTE 15/087 RPL INSS | 93K
LC | 128482121 | 000/001 | T2 EI JEFERSN-HILLSDLE JCT 00/01 RMV VEG | METCALF | ETL.7190.POLE.NWOD | 2024-04-08 | 2024-04-01 | 2024-05-09 | On-Time |  | 2025-04-01 | 2025-04-01 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128500311 | 001/018 | T2 DI SLT SPRNGS-TGR CRK 1/18 BENT STL | VICTOR | ETL.3500.TOWR | 2024-04-09 | 2024-04-01 | 2025-03-26 | On-Time |  | 2025-04-01 | 2025-04-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46326007 | T2 DI SLT SPRNGS TGR CRK 1/18 BENT STL | ICQ
LC | 128500356 | 001/012 | T2 DI SLT SPRNGS TGR CRK 1/12 RPL HRDT | VICTOR | ETL.3500.TOWR | 2024-04-09 | 2024-04-01 | 2025-03-26 | On-Time |  | 2025-04-01 | 2025-04-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46416305 | T2 DI SLT SPRNGS TGR CRK 1/12 RPL HRDT | ICQ
LC | 128500504 | 000/009 | T2 DI SLT SPRNGS TGRCRK 0/9 RPR FOND | VICTOR | ETL.3500.TOWR | 2024-04-09 | 2024-04-01 | 2025-03-26 | On-Time |  | 2025-04-01 | 2025-04-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46326009 | T2 DI SLT SPRNGS TGRCRK 0/9 RPR FOND | ICQ
LC | 128500647 | 012/001 | T2 DI MENDCN HARTLEY 12/1L REGRADE | WILLITS | ETL.7510.POLE.STPS | 2024-04-09 | 2024-04-01 | 2025-05-07 | Past Due |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46337044 | T2 DI MENDCN HARTLEY 12/1 REGRADE | ICW
LC | 128500670 | :019/003 | T2 DI EAGLE ROCK CORTINA :19/3 RPR GYWW | WILLITS | ETL.1470.POLE.NWOD | 2024-04-09 | 2024-04-01 | 2025-02-10 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46308193 | T2 DI EAGLE ROCK CORTINA :19/3 RPR GYWW | ICW
LC | 128500690 | 000/001 | T2 DI COLGATE-CHALLENGE 0/1 RPR GYWW | SACTO | ETL.6480.POLE.NWOD | 2024-04-09 | 2024-04-01 | 2024-08-25 | On-Time |  | 2024-10-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46247489 | T2 DI COLGATE-CHALLENGE 0/1 RPR GYWW | ICW
LC | 128500692 | 000/001 | T2 DI COLGATE-CHALLENGE 0/1 RPR JUMW | SACTO | ETL.6480.INSL.NCER | 2024-04-09 | 2024-04-01 | 2024-08-25 | On-Time |  | 2024-07-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46247487 | T2 DI COLGATE-CHALLENGE 0/1 RPR JMPW | ICW
LC | 128510400 | 008/068 | T2 SALT SPRNGS-TGR CRK 8/68 RPR CNDS | VICTOR | ETL.3500.INSL | 2024-04-10 | 2024-04-01 | 2024-04-01 | Past Due |  | 2025-04-01 | 2025-04-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Conductor-Steel | Repair | 46326985 | T2 DI SALT SPRNGS-TGR CRK 8/68 RPR CNDS | ICS
LC | 128510405 | 010/002 | T2 MENDOCINO-HARTLEY 10/2 RPL STRW | WILLITS | ETL.7510.POLE.WOOD | 2024-04-10 | 2024-04-01 | 2024-04-01 | Past Due |  | 2025-04-01 | 2025-04-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW ACCM OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574187 | T2 DI MENDOCINO-HARTLEY 10/2 RPL STRW | 70Y
LC | 128510527 | 003/000 | T2 DI LAYTNVLLE-COVELO 3/0 RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-04-10 | 2024-04-01 | 2024-07-15 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46232913 | T2 DI LAYTNVLLE-COVELO 3/0 RPR JUMW | ICW
LC | 128528886 | 000/001A | T2 DI LUCERNE #1 TAP 0/1A RPR CNDW | WILLITS | ETL.1331.INSL.NCER | 2024-04-11 | 2024-04-01 | 2024-04-01 | Past Due |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46414254 | T2 DI LUCERNE #1 TAP 0/1A RPR CNDW | ICW
LC | 128535207 | 000/002 | T2 DI CLGTE CHLNGE 0/2 RPR JUMW | SACTO | ETL.6480.INSL.NCER | 2024-04-11 | 2024-04-01 | 2024-08-25 | On-Time |  | 2024-07-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46247488 | T2 DI CLGTE CHLNGE 00/002 RPR JUMW | ICW
LC | 128535310 | 011/016 | T2 DI LOWER LAKE-HMSTK 11/16 RPL STRW | WILLITS | ETL.1481.POLE.WOOD | 2024-04-11 | 2024-04-01 | 2025-05-08 | Past Due |  | 2025-04-01 | 2025-04-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574454 | T2 DI LOWER LAKE-HMSTK 11/16 RPL STRW | 70Y
LC | 128535314 | 016/009 | T2 DI LWR LK HMSTK 16/9 RPR JUMW | WILLITS | ETL.1481.INSL.CERA | 2024-04-11 | 2024-04-01 | 2024-04-01 | Past Due |  | 2024-10-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCM OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46236312 | T2 DI LWR LK HMSTK 16/009 RPR JUMW | ICW
LC | 128535503 | 011/006 | T2 DI MNDCNO-HRTLY 11/006 RPR INSW | WILLITS | ETL.7510.INSL.NCER | 2024-04-11 | 2024-04-01 | 2024-04-01 | Past Due |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCM OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46333938 | T2 DI MNDCNO-HRTLY 11/006 RPR INSW | ICW
LC | 128535506 | 004/013 | T2 DI MLNS RCTRCK 04/013 COMPLETE | VICTOR | ETL.2400.INSL.NCER | 2024-04-11 | 2024-04-01 | 2025-02-27 | On-Time |  | 2025-04-01 | 2025-04-01 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35585935 | T2 DI MLNS RCTRCK 04/013 RPL INSW | 93I
LC | 128535587 | 003/007 | T2 DI LYTONVLE CVLO 03/007 RPR CRSW | WILLITS | ETL.7390.POLE.WOOD | 2024-04-11 | 2024-04-01 | 2025-04-14 | Past Due |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46414258 | T2 DI LYTONVLE CVLO 03/007 RPR CRSW | ICW
LC | 128535633 | 010/009 | T2 MNDCNO-HRTLY 10/009 RPR INSW | WILLITS | ETL.7510.INSL.NCER | 2024-04-11 | 2024-04-01 | 2024-04-01 | Past Due |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCM OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46333936 | T2 DI MNDCNO-HRTLY 10/009 RPR INSW | ICW
LC | 128535703 | 015/356 | T2 DI DRM GRS VLY WMR 15/356 RPR CNDW | SACTO | ETL.6760.INSL.CERA | 2024-04-11 | 2024-04-01 | 2024-07-31 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46305363 | T2 DI DRM GRS VLY WMR 15/356 RPR CNDW | ICW
LC | 128535752 | 033/153 | T2 DI TRACY-LOS BANOS-33/153 COMPLETE | VICTOR | ETL.6130.INSL | 2024-04-11 | 2024-04-01 | 2024-08-05 | On-Time |  | 2025-04-01 | 2025-04-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Damper-Steel | Replace | 46232571 | T2 DI TRACY-LOS BANOS-33/153 RPL DAMS | ICS
LC | 128535753 | 033/153 | T2 DI TRACY-LOS BANOS-33/153 WASH INSS | VICTOR | ETL.6130.INSL | 2024-04-11 | 2024-04-01 | 2025-03-25 | On-Time |  | 2025-04-01 | 2025-04-01 | 622 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | Contaminated | Insulator | Ground Wash | 46300276 | T2 DI TRACY-LOS BANOS-33/153 WASH INSS | ICD
LC | 128553762 | 000/002 | T2 LUCERNE#1 TAP 00/002 CANCEL | WILLITS | ETL.1331.INSL.NCER | 2024-04-16 | 2024-04-01 | 2024-04-01 | Past Due |  | 2025-04-01 | 2025-04-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Conductor-Wood | Repair | 46414255 | T2 DI LUCERNE#1 TAP 00/002 RPR CNDW | ICW
LC | 129612502 | 009/077 | T3 MONTA VISTA-BURNS 9/77L RPR ANCW | MOSSLNDG | ETL.7590.POLE.STPS | 2024-10-01 | 2024-10-01 | 2025-03-11 | On-Time |  | 2025-04-01 | 2025-04-01 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB | No Good/Out of Stdrd | ADSS - Wood | Repair | 46345548 | T3 MONTA VISTA-BURNS 9/77L INSP ANCW | ICW
LC | 123236291 | 004/028 | T3NT RND MTN-TBLE MTN #1 4/28 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2022-04-02 | 2022-04-02 | 2023-08-22 | On-Time |  | 2025-04-02 | 2025-04-02 | 564 | TR3N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR3N PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 123261807 | 066/275 | T2NT DI RND MTN TBL MTN 1 66/275 RPR FND | TABLEMTN | ETL.6060.TOWR | 2022-04-07 | 2022-04-02 | 2023-08-04 | On-Time |  | 2025-04-02 | 2025-04-02 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45644516 | T2NT DI RND MTN TBL MTN 1 66/275 RPR FND | ICQ
LC | 123261870 | 066/275 | T2NT DI RND MTN TB MTN 1 66/275 RPR SHLS | TABLEMTN | ETL.6060.TOWR | 2022-04-07 | 2022-04-02 | 2023-02-11 | On-Time |  | 2025-04-02 | 2025-04-02 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire / OPGW-Steel | Repair | 45458656 | T2 DI RND MTN TBL MTN 1 66/275 RPR SHLS | ICS
LC | 128418198 | 101/685 | T2 EI TESLA-NEWARK #2 101/685 RMV VEG | CONCORD | ETL.5354.TOWR | 2024-04-02 | 2024-04-02 | 2024-12-23 | On-Time |  | 2025-04-02 | 2025-04-02 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128418524 | 007/126 | T2 TMPLTN-ATSCDRO 07/126 RPR STRW | PISMOBCH | ETL.9410.POLE.WOOD | 2024-04-02 | 2024-04-02 | 2025-04-03 | Past Due |  | 2025-04-02 | 2025-04-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Structure-Wood | Repair | 46329660 | T2 TMPLTN-ATSCDRO 07/126 RPR STRW | ICW
LC | 128418583 | 011/245 | T2 EI COLEMAN-SOUTH 11/245 RPL STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-02 | 2024-04-02 | 2025-03-26 | On-Time |  | 2025-04-02 | 2025-04-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556792 | T2 EI COLEMAN-SOUTH 11/245 RPL STRW | 70Y
LC | 128418650 | 001/013 | T2 EI OLEUM G #1 001/013 RPR STRT | CONCORD | ETL.3150.TOWR | 2024-04-02 | 2024-04-02 | 2025-02-07 | On-Time |  | 2025-04-02 | 2025-04-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287092 | T2NT EI OLEUM G #1 001/013 RPR STRT | ICQ
LC | 128418786 | 017/141 | T2 EI CRBRY SS-RND MTN 17/141 MASTIC | TABLEMTN | ETL.5410.TOWR | 2024-04-02 | 2024-04-02 | 2025-01-15 | On-Time |  | 2025-04-02 | 2025-04-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46354004 | T2 EI CRBRY SS-RND MTN 17/141 MASTIC | ICQ
LC | 128418851 | 026/115 | T2 EI LOS ESTEROS METCALF 26/115 COTTER | METCALF | ETL.5353.INSL.NCER | 2024-04-02 | 2024-04-02 | 2025-03-07 | On-Time |  | 2025-04-02 | 2025-04-02 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46287098 | T2 EI LOS ESTEROS METCALF 26/115 COTTER | ICS
LC | 128418893 | 089/453 | T2 EI MLN-RND MTN #2 89/453 RPR FOND | TABLEMTN | ETL.6020.TOWR | 2024-04-02 | 2024-04-02 | 2025-02-12 | On-Time |  | 2025-04-02 | 2025-04-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381360 | T2 EI MLN-RND MTN #2 89/453 RPR FOND | ICQ
LC | 128419138 | 001/014 | T2 EI OLEUM-G #1 001/014 RPR STRT | CONCORD | ETL.3150.TOWR | 2024-04-02 | 2024-04-02 | 2025-02-07 | On-Time |  | 2025-04-02 | 2025-04-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287093 | T2NT EI OLEUM-G #1 001/014 RPR STRT | ICQ
LC | 128419487 | 005/034 | T2 EI SBRNT-STD OIL SS #1 5/34 RPL HRDT | CONCORD | ETL.3800.TOWR | 2024-04-02 | 2024-04-02 | 2025-03-10 | On-Time |  | 2025-04-02 | 2025-04-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46287095 | T2 EI SBRNT-STD OIL SS #1 5/34 RPL HRDT | ICQ
LC | 128419875 | 002/017 | T2 EI OLEUM-G #1 002/017 RPR STRT | CONCORD | ETL.3150.TOWR | 2024-04-02 | 2024-04-02 | 2025-02-10 | On-Time |  | 2025-04-02 | 2025-04-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287094 | T2 EI OLEUM-G #1 002/017 RPR STRT | ICQ
LC | 128420186 | 005/114-GUY | T2 EI BRNS-LNE STR #2 5/114-GUY RPL GYPL | MOSSLNDG | ETL.6240.POLE.WOOD | 2024-04-02 | 2024-04-02 | 2025-03-09 | On-Time |  | 2025-04-02 | 2025-04-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP SWRK ACCL ACCM ACCH USA COMP OH FMOB TR2 PRTO FRAB | Rotten | Guy Pole-Wood | Replace | 35572855 | T2 EI BRNS-LNE STR #2 5/114-GUY RPL GYPL | 70Y
LC | 128420461 | 011/236 | T2 EI COLEMAN-SOUTH 11/236 COMPLETE | TABLEMTN | ETL.6450.INSL.NCER | 2024-04-02 | 2024-04-02 | 2025-03-22 | On-Time |  | 2025-04-02 | 2025-04-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46332468 | T2 EI COLEMAN-SOUTH 11/236 RPR INSW | ICW
LC | 128420605 | 018/147 | T2 EI CRBRY SS-RND MTN 18/147 MASTIC | TABLEMTN | ETL.5410.TOWR | 2024-04-02 | 2024-04-02 | 2025-01-15 | On-Time |  | 2025-04-02 | 2025-04-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46354005 | T2 EI CRBRY SS-RND MTN 18/147 MASTIC | ICQ
LC | 128421267 | 088/449 | T2 EI MLN-RND MTN #2 88/449 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-02 | 2024-04-02 | 2025-02-12 | On-Time |  | 2025-04-02 | 2025-04-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381361 | T2 EI MLN-RND MTN #2 88/449 RPR GYWT | ICQ
LC | 128423048 | 004/004 | T2 HUMBOLDT-MAPLE CREEK 04/04 RPR GYWW | EUREKA | ETL.7130.POLE.NWOD | 2024-04-02 | 2024-04-02 | 2025-02-28 | On-Time |  | 2025-04-02 | 2025-04-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345718 | T2 HUMBOLDT-MAPLE CREEK 04/04 RPR GYWW | ICW
LC | 128423733 | 004/005 | T2 HUMBOLDT-MAPLE CREEK 4/5 RPR INSW | EUREKA | ETL.7130.INSL.NCER | 2024-04-02 | 2024-04-02 | 2024-05-29 | On-Time |  | 2024-07-02 | 2025-04-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46238993 | T2 HUMBOLDT-MAPLE CREEK 4/5 RPR INSW | ICW
LC | 128423847 | 007/001 | T2 EI CHOWCHILLA-KERCKHOFF 7/1 RPL POLE | FRESNO | ETL.1250.POLE.WOOD | 2024-04-02 | 2024-04-02 | 2025-03-27 | On-Time |  | 2025-04-02 | 2025-04-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35576153 | T2 EI CHOWCHILLA-KERCKHOFF 7/1 RPL POLE | 70Y
LC | 128423892 | 006/010 | T2 EI CHOWCHILLA-KERCKHOFF 6/10 RPL POLE | FRESNO | ETL.1250.POLE.WOOD | 2024-04-02 | 2024-04-02 | 2025-03-27 | On-Time |  | 2025-04-02 | 2025-04-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35576151 | T2 EI CHOWCHILLA-KERCKHOFF 6/10 RPL POLE | 70Y
LC | 128425228 | 088/447 | T2 EI MLN-RND MTN #2 88/447 RPR FOND | TABLEMTN | ETL.6020.TOWR | 2024-04-02 | 2024-04-02 | 2025-02-12 | On-Time |  | 2025-04-02 | 2025-04-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381362 | T2 EI MLN-RND MTN #2 88/447 RPR FOND | ICQ
LC | 128427463 | 008/039 | T2 EI BRNTWD-KLSO 8/39 RMV NEST | CONCORD | ETL.4410.TOWR | 2024-04-02 | 2024-04-02 | 2025-01-08 | On-Time |  | 2025-04-02 | 2025-04-02 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMC REMT SPCR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46287097 | T2 EI BRNTWD-KLSO 8/39 RMV NEST | ICS
LC | 128428191 | 005/097 | T2 SAN MATEO-HILLSDALE JCT 5/97 GO95 | METCALF | ETL.7950.POLE.WOOD | 2024-04-02 | 2024-04-02 | 2025-05-27 | Past Due |  | 2025-04-02 | 2025-04-02 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAR NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35542095 | T2 SAN MATEO-HILLSDALE JCT 5/97 GO95 | 93G
LC | 128428209 | 005/107 | T2 EI CORDELIA #2 TAP 005/107 RMV VEG | SACTO | ETL.8184.POLE.NWOD | 2024-04-02 | 2024-04-02 | 2025-03-27 | On-Time |  | 2025-04-02 | 2025-04-02 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB PGEQ | Overgrown | Vegetation | Remove
LC | 128428388 | 060/011 | T2 EI ELK-GUALALA 060/011 RPR GYWW | WILLITS | ETL.8410.POLE.WOOD | 2024-04-02 | 2024-04-02 | 2025-03-03 | On-Time |  | 2025-04-02 | 2025-04-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46308200 | T2NT EI ELK-GUALALA 060/011 RPR GYWW | ICW
LC | 128428420 | 063/001 | T2 EI ELK-GUALALA 063/001 RPL ANCW | WILLITS | ETL.8410.POLE.WOOD | 2024-04-02 | 2024-04-02 | 2024-10-04 | On-Time |  | 2024-07-02 | 2025-04-02 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP CREW COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35541733 | T2 EI ELK-GUALALA 063/001 RPL ANCW | 93E
LC | 128429138 | 018/150 | T2 EI CRBRY SS-RND MTN 18/150 RPL INSS | TABLEMTN | ETL.5410.INSL.CERA | 2024-04-02 | 2024-04-02 | 2025-03-11 | On-Time |  | 2025-04-02 | 2025-04-02 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569571 | T2 EI CARBRY SS-RND MTN RPL INSS 6 TWRS. | 93K
LC | 128429902 | 001/022D | T2 DI MTN QUARRIES TP 1/22D RPR GYWW | SACTO | ETL.6991.POLE.WOOD | 2024-04-02 | 2024-04-02 | 2025-03-20 | On-Time |  | 2025-04-02 | 2025-04-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46323924 | T2 DI MTN QUARRIES TP 1/22D RPR GYWW | ICW
LC | 128534987 | 019/001 | T2 DI KNCTI MIDDLETOWN+ 19/1 INS ANCHW | WILLITS | ETL.6380.POLE.NWOD | 2024-04-11 | 2024-04-02 | 2025-03-19 | On-Time |  | 2025-04-02 | 2025-04-02 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Missing | Anchor-Wood | Install | 35611706 | T2 DI KNCTI MIDDLETOWN 19/1 INS ANCHW | 93E
LC | 128535100 | 019/001 | T2 DI KONOCTI MIDDLETOWN+ 19/01 RPR GYWW | WILLITS | ETL.6380.POLE.NWOD | 2024-04-11 | 2024-04-02 | 2025-03-18 | On-Time |  | 2025-04-02 | 2025-04-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46340104 | T2 DI KONOCTI MIDDLETOWN+ 19/01 RPR GYWW | ICW
LC | 128536201 | 009/004 | T2 DI MNDCNO-HRTLY 09/004 RPR IBWW | WILLITS | ETL.7510.INSL.CERA | 2024-04-11 | 2024-04-02 | 2024-04-02 | Past Due |  | 2025-04-02 | 2025-04-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCM OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46339193 | T2 DI MNDCNO-HRTLY 09/004 RPR IBWW | ICW
LC | 128537424 | 026/117 | T2 DI FINK SS-WESTLEY 26/117 RPL HRDT | VICTOR | ETL.1384.TOWR | 2024-04-12 | 2024-04-02 | 2024-11-18 | On-Time |  | 2025-04-02 | 2025-04-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Hardware-Tower | Replace | 46252433 | T2 DI FINK SS-WESTLEY 26/117 RPL HRDT | ICQ
LC | 128538383 | 005/074 | T3 DI DESALBA-CNTRVILLE 5/74 RPR POLE | TABLEMTN | ETL.6720.POLE.WOOD | 2024-04-12 | 2024-04-02 | 2025-04-15 | Past Due |  | 2025-04-02 | 2025-04-02 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46345253 | T3 DI DESALBA-CNTRVILLE 5/74 RPR POLE | ICW
LC | 128433722 | 029/139 | T2 CORTINA-MENDOCINO #1 29/139 TOUCH | WILLITS | ETL.1330.TOWR | 2024-04-03 | 2024-04-03 | 2025-04-07 | Past Due |  | 2024-10-03 | 2025-04-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491081 | T2 CORTINA-MENDOCINO #1 29/139 TOUCH | ICQ
LC | 128433725 | 114/000 | T2 HUMBOLDT-BRDGVLE 114/00 RPR GYWW | EUREKA | ETL.1810.POLE.STPS | 2024-04-03 | 2024-04-03 | 2025-04-02 | On-Time |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345746 | T2 HUMBOLDT-BRDGVLE 114/00 RPR GYWW | ICW
LC | 128433726 | 007/130 | T2 TEMPLETON-ATASCADERO 7/130 RPR POLE | PISMOBCH | ETL.9410.POLE.WOOD | 2024-04-03 | 2024-04-03 | 2025-04-03 | On-Time |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Structure-Wood | Repair | 46329661 | T2 TEMPLETON-ATASCADERO 7/130 RPR POLE | ICW
LC | 128433947 | 007/129 | T2 TEMPLETON-ATASCADERO 7/129 RPR STRW | PISMOBCH | ETL.9410.POLE.WOOD | 2024-04-03 | 2024-04-03 | 2025-04-03 | On-Time |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Structure-Wood | Repair | 46329662 | T2 TEMPLETON-ATASCADERO 7/129 RPR POLE | ICW
LC | 128434018 | 003/020 | T2 EI PITTSBURG-CLAYTON #3 3/20 RMV NEST | CONCORD | ETL.3290.TOWR | 2024-04-03 | 2024-04-03 | 2025-01-15 | On-Time |  | 2025-04-03 | 2025-04-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46287183 | T2 EI PITTSBURG-CLAYTON #3 3/20 RMV NEST | ICS
LC | 128434138 | 059/244 | T2 EI DIABLO-GATES #1 59/244 RPR GYWT | PISMOBCH | ETL.5960.TOWR | 2024-04-03 | 2024-04-03 | 2025-04-03 | On-Time |  | 2025-04-03 | 2025-04-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP ACCM COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46391249 | T2 EI DIABLO-GATES #1 59/244 RPR GYWT | ICQ
LC | 128434360 | 003/020 | T2 EI PITTSBURG-CLAYTON #4 3/20 COTTER | CONCORD | ETL.3291.INSL.NCER | 2024-04-03 | 2024-04-03 | 2024-05-25 | On-Time |  | 2025-04-03 | 2025-04-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46234657 | T2 EI PITTSBURG-CLAYTON #4 3/20 COTTER | ICS
LC | 128435771 | 088/446 | T2 EI MALIN-ROUND MTN #2 88/446 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-03 | 2024-04-03 | 2025-02-12 | On-Time |  | 2025-04-03 | 2025-04-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381363 | T2 EI MALIN-ROUND MTN #2 88/446 RPR GYWT | ICQ
LC | 128435935 | 002/020 | T2 EI OLEUM-G #1 002/020 BNT STEEL | CONCORD | ETL.3150.TOWR | 2024-04-03 | 2024-04-03 | 2025-02-11 | On-Time |  | 2025-04-03 | 2025-04-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287182 | T2 EI OLEUM-G #1 002/020 BNT STEEL | ICQ
LC | 128435956 | 005/110 | T2 EI COLEMAN-SOUTH 5/110 RPL STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-03 | 2024-04-03 | 2025-03-21 | On-Time |  | 2025-04-03 | 2025-04-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556788 | T2 EI COLEMAN-SOUTH 5/110 RPL STRW | 70Y
LC | 128436252 | 009/091 | T2 EI BRDGVLLE-CTTNWD 9/91R RPR CRSW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-03 | 2024-04-03 | 2025-02-07 | On-Time |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46311116 | T2 EI BRDGVLLE-CTTNWD 9/91R RPR CRSW | ICW
LC | 128436646 | 011/115 | T2 EI PIT#5-RND MTN#2 11/115L RPL STRW | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-03 | 2024-04-03 | 2024-06-25 | On-Time |  | 2025-04-03 | 2025-04-03 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35555574 | T2 EI PIT#5-RND MTN#2 11/115R RPL STRW | 70Y
LC | 128436653 | 004/097 | T2 EI COLEMAN-SOUTH 4/97 RMV VEG | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-03 | 2024-04-03 | 2024-05-28 | On-Time |  | 2025-04-03 | 2025-04-03 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128436658 | 005/024 | T2 EI PITTSBURG-SAN MATEO 005/024 COTTER | CONCORD | ETL.5463.INSL | 2024-04-03 | 2024-04-03 | 2024-04-30 | On-Time |  | 2024-07-03 | 2025-04-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46234724 | T2 EI PITTSBURG-SAN MATEO 005/024 COTTER | ICS
LC | 128436659 | 011/115 | T2 EI PIT#5-RND MTN#2 11/115R RPL STRW | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-03 | 2024-04-03 | 2024-06-25 | On-Time |  | 2025-04-03 | 2025-04-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35555574 | T2 EI PIT#5-RND MTN#2 11/115R RPL STRW | 70Y
LC | 128437920 | 011/060 | T2 EI CHRISTIE-SOBRANTE 11/060 INS RPTS | CONCORD | ETL.1260.TOWR | 2024-04-03 | 2024-04-03 | 2025-01-21 | On-Time |  | 2025-04-03 | 2025-04-03 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46287189 | T2 EI CHRISTIE-SOBRANTE 11/060 INS RPTS | ICB
LC | 128438222 | 006/030B | T2 EI PITTSBURG-TESLA #2 6/30B BNT STEEL | CONCORD | ETL.5520.TOWR | 2024-04-03 | 2024-04-03 | 2025-02-05 | On-Time |  | 2025-04-03 | 2025-04-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287186 | T2 EI PITTSBURG-TESLA #2 6/30B BNT STEEL | ICQ
LC | 128438392 | 004/003 | T2 HMBLDT-MPLE CREEK 04/003 RPR GYWW | EUREKA | ETL.7130.POLE.NWOD | 2024-04-03 | 2024-04-03 | 2025-02-28 | On-Time |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345719 | T2 HMBLDT-MPLE CREEK 04/003 RPR GYWW | ICW
LC | 128438437 | 011/059 | T2 EI CHRISTIE-SOBRANTE 11/059 INS RPTS | CONCORD | ETL.1260.TOWR | 2024-04-03 | 2024-04-03 | 2025-01-21 | On-Time |  | 2025-04-03 | 2025-04-03 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46287187 | T2 EI CHRISTIE-SOBRANTE 11/059 INS RPTS | ICB
LC | 128438472 | 051/000 | T2 EI ELK-GUALALA 051/000 RPL ANCW | WILLITS | ETL.8410.POLE.WOOD | 2024-04-03 | 2024-04-03 | 2025-03-24 | On-Time |  | 2025-04-03 | 2025-04-03 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35557743 | T2 EI ELK-GUALALA 051/000 RPL ANCW | 93E
LC | 128438473 | 050/009 | T2 ELK-GUALALA 050/009C RMV VEG | WILLITS | ETL.8410.POLE.WDPS | 2024-04-03 | 2024-04-03 | 2024-04-03 | Past Due |  | 2025-04-03 | 2025-04-03 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128438512 | 004/093 | T2 EI COLEMAN-SOUTH 4/93 RPL STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-03 | 2024-04-03 | 2025-03-25 | On-Time |  | 2025-04-03 | 2025-04-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35556786 | T2 EI COLEMAN-SOUTH 4/93 RPL STRW | 70Y
LC | 128438639 | 007/005 | T2 EI CHOWCHILA-KRCKHF 07/05 RPL STRW | FRESNO | ETL.1250.POLE.WOOD | 2024-04-03 | 2024-04-03 | 2025-03-26 | On-Time |  | 2025-04-03 | 2025-04-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC SWRK COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35576155 | T2 EI CHOWCHILA-KRCKHF 07/05 RPL STRW | 70Y
LC | 128438808 | 001/031-GUY | T2 PLACER-DEL MAR 001/031-GUY RPR GYWW | SACTO | ETL.7800.POLE.WOOD | 2024-04-03 | 2024-04-03 | 2025-02-20 | On-Time |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAR | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46323925 | T2 PLACER-DEL MAR 001/031-GUY RPR GYWW | ICW
LC | 128439512 | 004/089 | T2 EI COLEMAN-SOUTH 4/89 RPL STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-03 | 2024-04-03 | 2025-03-25 | On-Time |  | 2025-04-03 | 2025-04-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35556784 | T2 EI COLEMAN-SOUTH 4/87 RPL STRW | 70Y
LC | 128439612 | 004/088 | T2 EI COLEMAN-SOUTH 4/88 RPR INSW | TABLEMTN | ETL.6450.INSL.CERA | 2024-04-03 | 2024-04-03 | 2025-03-19 | On-Time |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46332473 | T2 EI COLEMAN-SOUTH 4/88 RPR INSW | ICW
LC | 128439687 | 011/065 | T2 EI CHRISTIE-SOBREANTE 11/065 INS RPTS | CONCORD | ETL.1260.TOWR | 2024-04-03 | 2024-04-03 | 2025-01-21 | On-Time |  | 2025-04-03 | 2025-04-03 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46287190 | T2 EI CHRISTIE-SOBREANTE 11/065 INS RPTS | ICB
LC | 128439689 | 011/108 | T2 EI PIT#5-RND MTN#2 11/108L RPL STRW | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-03 | 2024-04-03 | 2025-03-06 | On-Time |  | 2025-04-03 | 2025-04-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35607185 | T2 EI PIT#5-RND MTN#2 11/108L RPL STRW | 70Y
LC | 128439696 | 011/065 | T2 EI CHRISTIE-SOBRANTE 11/065 INS RPTS | CONCORD | ETL.1260.TOWR | 2024-04-03 | 2024-04-03 | 2025-01-21 | On-Time |  | 2025-04-03 | 2025-04-03 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46287191 | T2 EI CHRISTIE-SOBRANTE 11/065 INS RPTS | ICB
LC | 128439700 | 011/108 | T2 EI PIT#5-RND MTN#2 11/108R RPL STRW | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-03 | 2024-04-03 | 2025-03-06 | On-Time |  | 2025-04-03 | 2025-04-03 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35607185 | T2 EI PIT#5-RND MTN#2 11/108L RPL STRW | 70Y
LC | 128439752 | R001/011 | T2 EI CARBERRY SS-RND MTN R01/11 RMV VEG | TABLEMTN | ETL.5410.TOWR | 2024-04-03 | 2024-04-03 | 2025-02-05 | On-Time |  | 2025-04-03 | 2025-04-03 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128439760 | 004/087 | T2 EI COLEMAN-SOUTH 4/87 RPL STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-03 | 2024-04-03 | 2025-03-19 | On-Time |  | 2025-04-03 | 2025-04-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556784 | T2 EI COLEMAN-SOUTH 4/87 RPL STRW | 70Y
LC | 128439832 | 011/113 | T2 EI PIT#5-RND MTN#2 11/1113R RPR GYWW | TABLEMTN | ETL.5430.POLE.STPS | 2024-04-03 | 2024-04-03 | 2025-03-08 | On-Time |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332474 | T2 EI PIT#5-RND MTN#2 11/1113R RPR GYWW | ICW
LC | 128439870 | 010/064 | T2 EI STANSLS-MANTECA #2 10/64 RPR FOND | VICTOR | ETL.3820.TOWR | 2024-04-03 | 2024-04-03 | 2025-03-23 | On-Time |  | 2025-04-03 | 2025-04-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46415877 | T2 EI STANSLS-MANTECA #2 10/64 RPR FOND | ICQ
LC | 128439889 | 011/113 | T2 EI PIT#5-RND MTN#2 11/1113C RPR GYWW | TABLEMTN | ETL.5430.POLE.STPS | 2024-04-03 | 2024-04-03 | 2025-03-08 | On-Time |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332475 | T2 EI PIT#5-RND MTN#2 11/1113C RPR GYWW | ICW
LC | 128440012 | 045/007 | T2 EI ELK-GUALALA 045/007 RPR INSW | WILLITS | ETL.8410.INSL.NCER | 2024-04-03 | 2024-04-03 | 2025-02-06 | On-Time |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46308203 | T2NT EI ELK-GUALALA 045/007 RPR INSW | ICW
LC | 128440074 | 011/113 | T2 EI PIT#5-RND MTN#2 11/1113L RPR GYWW | TABLEMTN | ETL.5430.POLE.STPS | 2024-04-03 | 2024-04-03 | 2025-03-08 | On-Time |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46332476 | T2 EI PIT#5-RND MTN#2 11/1113L RPR GYWW | ICW
LC | 128442617 | 003/024 | T2 EI OLEUM-G #2 003/024 BNT STEEL | CONCORD | ETL.3160.INSL.CERA | 2024-04-03 | 2024-04-03 | 2024-04-03 | Past Due |  | 2025-04-03 | 2025-04-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO CLMB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287184 | T2 EI OLEUM-G #1 003/024 BNT STEEL | ICQ
LC | 128442730 | R000/010 | T2 EI CARBRY SS-RND MTN R00/10 TOUCH | TABLEMTN | ETL.5410.TOWR | 2024-04-03 | 2024-04-03 | 2025-02-26 | On-Time |  | 2024-10-03 | 2025-04-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Structure-Tower | Repair | 46475412 | T2 EI CARBRY SS-RND MTN R00/10 TOUCH | ICQ
LC | 128442817 | 025/002 | T2 EI PHILO JCT-ELK 025/002 INS DMPW | WILLITS | ETL.7780.INSL.CERA | 2024-04-03 | 2024-04-03 | 2025-01-27 | On-Time |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46340107 | T2 EI PHILO JCT-ELK 025/002 INS DMPW | ICW
LC | 128442827 | 031/001 | T2 TRINITY-MAPLE CREEK 31/1C RPL ANCW | EUREKA | ETL.8170.POLE.WDPS | 2024-04-03 | 2024-04-03 | 2024-06-14 | On-Time |  | 2025-04-03 | 2025-04-03 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR FIRE COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35504382 | T2 DI TRINITY-MAPLE CREEK 31/01 RPL ANCW | 93E
LC | 128442829 | 031/001 | T2 TRINITY-MAPLE CREEK 31/1R RPL ANCW | EUREKA | ETL.8170.POLE.WDPS | 2024-04-03 | 2024-04-03 | 2024-06-14 | On-Time |  | 2025-04-03 | 2025-04-03 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR FIRE COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35504382 | T2 DI TRINITY-MAPLE CREEK 31/01 RPL ANCW | 93E
LC | 128442967 | 018/009 | T2 EI TRINITY-MAPLE CREEK 18/09 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-04-03 | 2024-04-03 | 2025-03-01 | On-Time |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345745 | T2 EI TRINITY-MAPLE CREEK 18/09 RPR GYWW | ICW
LC | 128442968 | 018/001 | T2 EI TRINITY-MAPLE CREEK 18/1 RPR STRW | EUREKA | ETL.8170.POLE.WOOD | 2024-04-03 | 2024-04-03 | 2024-04-03 | Past Due |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46345744 | T2 EI TRINITY-MAPLE CREEK 18/01 RPR STRW | ICW
LC | 128442987 | 000/003 | T2NT EI SBRNT-STD OIL SS #1 0/3 MASTIC | CONCORD | ETL.3800.TOWR | 2024-04-03 | 2024-04-03 | 2025-03-11 | On-Time |  | 2027-04-03 | 2025-04-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46287180 | T2NT EI SBRNT-STD OIL SS #1 0/3 MASTIC | ICQ
LC | 128443211 | 000/002 | T2NT EI SBRNT-STD OIL SS #1 0/2 MASTIC | CONCORD | ETL.3800.TOWR | 2024-04-03 | 2024-04-03 | 2025-03-11 | On-Time |  | 2027-04-03 | 2025-04-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46287099 | T2NT EI SBRNT-STD OIL SS #1 0/2 MASTIC | ICQ
LC | 128443243 | 003/017 | T2 TASSAJARA-NEWARK 3/17 RPL INSS | CONCORD | ETL.5920.INSL | 2024-04-03 | 2024-04-03 | 2024-04-03 | Past Due |  | 2025-04-03 | 2025-04-03 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575040 | T2 EI TASSAJARA-NEWARK RPL INSS IN TWR 0 | 93K
LC | 128443255 | 021/082 | T2 EI PITTSBURG-SAN RAMON 21/82 RPL INSS | CONCORD | ETL.5490.INSL | 2024-04-03 | 2024-04-03 | 2025-03-24 | On-Time |  | 2025-04-03 | 2025-04-03 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35618745 | T2 EI PITTSBURG-SAN RAMON 21/82 RPL INSS | 93K
LC | 128443385 | 004/096 | T2 DI CSCDE BNTN DSHTS 04/096 RPL BOND | TABLEMTN | ETL.6310.POLE.WOOD | 2024-04-03 | 2024-04-03 | 2024-11-15 | On-Time |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46332477 | T2 DI CSCDE BNTN DSHTS 04/096 RPL BOND | ICW
LC | 128443386 | 004/096 | T2 DI CSCDE BNTN DSHTS 4/96 RPR JUMW | TABLEMTN | ETL.6310.INSL.NCER | 2024-04-03 | 2024-04-03 | 2024-12-03 | On-Time |  | 2024-07-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46229991 | T2 DI CSCDE BNTN DSHTS 04/96 RPR JUMW | ICW
LC | 128443388 | 013/004 | T2 KNCTI-MDDLETOWN 13/004 RPL INSW | WILLITS | ETL.6380.INSL.NCER | 2024-04-03 | 2024-04-03 | 2024-04-03 | Past Due |  | 2025-04-03 | 2025-04-03 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574108 | T2 DI KNCTI-MDDLETOWN 13/004 RPL INSW | 93I
LC | 128535550 | 012/086 | T2 DI GRN VLY-LLAGS- 12/86 RPR INSW | MOSSLNDG | ETL.1720.INSL.NCER | 2024-04-11 | 2024-04-03 | 2024-05-30 | On-Time |  | 2024-07-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46234712 | T2 DI GRN VLY-LLAGS- 12/86 RPR INSW | ICW
LC | 128535660 | 011/083 | T2 DI GREEN VALEY-LAGAS 11/83L RPR ANCW | MOSSLNDG | ETL.1720.POLE.STPS | 2024-04-11 | 2024-04-03 | 2024-04-03 | Past Due |  | 2025-04-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46283998 | T2 DI GREEN VALEY-LAGAS 11/83L RPR ANCW | ICW
LC | 128539344 | 000/001C | T2 DI IBM HARRY RD #2 TP 0/1C UNBURY | METCALF | ETL.2481.POLE.NWOD | 2024-04-12 | 2024-04-03 | 2025-01-17 | On-Time |  | 2025-04-03 | 2025-04-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46298811 | T2 DI IBM HARRY RD #2 TP 0/1C UNBURY | ICQ
LC | 128539345 | 000/001C | T2 DI IBM HARRY RD #2 TP 0/1C RPR ADSS | METCALF | ETL.2481.POLE.NWOD | 2024-04-12 | 2024-04-03 | 2024-06-10 | On-Time |  | 2024-07-03 | 2025-04-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Steel | Repair | 46229661 | T2 DI IBM HARRY RD #2 TP 0/1C RPR ADSS | ICS
LC | 128539347 | 000/001C | T2 DI IBM HARRY RD #2 TP 0/1C RPL INSS | METCALF | ETL.2481.INSL | 2024-04-12 | 2024-04-03 | 2025-03-15 | On-Time |  | 2025-04-03 | 2025-04-03 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574094 | T2 DI IBM HARRY RD #2 TP 0/1C RPL INSS | 93K
LC | 128541567 | 009/067 | T2 DI GREEN VLY-LLGS 9/67 INST STRW | MOSSLNDG | ETL.1720.POLE.WDPS | 2024-04-12 | 2024-04-03 | 2024-06-03 | On-Time |  | 2024-10-03 | 2025-04-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46236070 | T2 DI GREEN VLY-LLGS 9/67 INST STRW | ICW
LC | 128541899 | 010/009 | T2 DI FULTON-HOPLAND 10/9 RPL STRW | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-04-12 | 2024-04-03 | 2024-04-03 | Past Due |  | 2024-10-03 | 2025-04-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR ACCM OH TR2 PRTO AIR FRAB DURA BRIN | Rotten | Structure-Wood | Replace | 35549294 | T2 DI FULTON-HOPLAND 10/9 RPL STRW | 70Y
LC | 128542168 | :012/082 | T2 DI GREEN VALLEY-LLAGAS 12/82 TOUCH | MOSSLNDG | ETL.1720.TOWR | 2024-04-12 | 2024-04-03 | 2024-04-03 | Past Due |  | 2024-10-03 | 2025-04-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCL OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476001 | T2 DI GREEN VALLEY-LLAGAS 12/82 TOUCH | ICQ
LC | 128542252 | :012/077 | T2 DI GREEN VLY-LLAGAS 12/77 RMV NEST | MOSSLNDG | ETL.1720.TOWR | 2024-04-12 | 2024-04-03 | 2025-02-05 | On-Time |  | 2025-04-03 | 2025-04-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46391166 | T2 DI GREEN VLY-LLAGAS 12/77 RMV NEST | ICS
LC | 128548405 | 000/002 | T2 DI IBM HARRY RD #1 TAP 0/2 RPS ADSS | METCALF | ETL.2501.TOWR | 2024-04-15 | 2024-04-03 | 2025-04-01 | On-Time |  | 2025-04-03 | 2025-04-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | ADSS - Steel | Repair | 46298626 | T2 DI IBM HARRY RD #1 TAP 0/2 RPS ADSS | ICS
LC | 129627797 | 010/243 | T3 DRUM-GRSS VLLY-WMR 10/243 RPL POLE | SACTO | ETL.6760.POLE.WOOD | 2024-10-03 | 2024-10-03 | 2024-11-05 | On-Time |  | 2025-04-03 | 2025-04-03 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW INSP ACCL COMP OH TR3 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35561261 | T3 DI DRM-GRSS VLLY-WMR 10/243 RPL STRW | 70Y
LC | 123239840 | 013/071 | T2NT EI RND MT-TB MTN #2 13/71 BNT STEEL | TABLEMTN | ETL.6070.TOWR | 2022-04-04 | 2022-04-04 | 2023-08-01 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647413 | T2 EI RND MTN-TBL MTN #2 13/71 BNT STEEL | ICQ
LC | 123240772 | 014/073 | T2NT EI RND MT-TB MTN #1 14/73 BNT STEEL | TABLEMTN | ETL.6060.TOWR | 2022-04-04 | 2022-04-04 | 2023-08-01 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644419 | T2 EI RND MTN-TBL MTN #1 14/73 BNT STEEL | ICQ
LC | 123241645 | 014/075 | T2NT EI ROND MT-TB MTN #1 14/75 RPR GYWS | TABLEMTN | ETL.6060.TOWR | 2022-04-04 | 2022-04-04 | 2023-08-02 | On-Time |  | 2025-04-04 | 2025-04-04 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45699100 | T2 EI ROND MTN-TBL MTN #1 14/75 RPR GYWS | ICS
LC | 123332632 | :012/064 | T2NT DI CZY HRS CN-SLS #1 :12/64 BNT STL | MOSSLNDG | ETL.2900.TOWR | 2022-04-14 | 2022-04-04 | 2023-06-23 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45590498 | T2 DI CZY HRS CYN-SLNS #1 :12/64 BNT STL | ICQ
LC | 127194702 | 009/002 | T2 FORT BRAGG-ELK 009/002 GO95 | WILLITS | ETL.2060.POLE.WOOD | 2023-10-04 | 2023-10-04 | 2025-04-24 | Past Due |  | 2025-04-04 | 2025-04-04 | 401 | TR2 | YES | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB XMPT TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 31654427 | EQUET2 FORT BRAGG-ELK 004/007 GO95 CLEAR | 93G
LC | 128444777 | 007/006 | T2 EI HUMBOLDT-MAPLE CREK 07/06 RPL INSW | EUREKA | ETL.7130.INSL.NCER | 2024-04-04 | 2024-04-04 | 2025-04-04 | On-Time |  | 2025-04-04 | 2025-04-04 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574775 | T2 EI HUMBOLDT-MAPLE CREK 07/06 RPL INSW | 93I
LC | 128444785 | 007/006 | T2 EI HUMBOLDT-MAPLE CREK 07/06 RPR GYWW | EUREKA | ETL.7130.POLE.WOOD | 2024-04-04 | 2024-04-04 | 2024-05-23 | On-Time |  | 2024-10-04 | 2025-04-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46232513 | T2 EI HUMBOLDT-MAPLE CREK 07/06 RPR GYWW | ICW
LC | 128444978 | 025/001A | T2 EI PHILO JCT-ELK 025/001A INS DMPW | WILLITS | ETL.7780.INSL.NCER | 2024-04-04 | 2024-04-04 | 2025-01-27 | On-Time |  | 2025-04-04 | 2025-04-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46340213 | T2 EI PHILO JCT-ELK 025/001A INS DMPW | ICW
LC | 128445202 | 007/007 | T2 EI HUMBOLDT-MAPLE CRK 7/7 RPR GYWW | EUREKA | ETL.7130.POLE.NWOD | 2024-04-04 | 2024-04-04 | 2024-05-23 | On-Time |  | 2024-10-04 | 2025-04-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46239981 | T2 EI HUMBOLDT-MAPLE CRK 7/7 RPR GYWW | ICW
LC | 128445545 | R000/006 | T2 EI CRBRY SW STA-RND R000/006 RPL INSW | TABLEMTN | ETL.5410.INSL.CERA | 2024-04-04 | 2024-04-04 | 2025-03-10 | On-Time |  | 2025-04-04 | 2025-04-04 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35611949 | T2 EI CRBRY SW STA-RND R000/006 RPL INSW | 93I
LC | 128447678 | 019/450 | T2 DRM-GRSS VLLY-WEIMAR 19/450 GO95 | SACTO | ETL.6760.POLE.WOOD | 2024-04-04 | 2024-04-04 | 2024-12-03 | On-Time |  | 2025-04-04 | 2025-04-04 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35591682 | DRM-GRSS VLLY-WMAR 19/450 O/L POLE | 93G
LC | 128447710 | 000/005 | T2 WV CRUSHER TAP 0/5 CANCEL | MOSSLNDG | ETL.6241.POLE.WOOD | 2024-04-04 | 2024-04-04 | 2024-04-04 | Past Due |  | 2025-04-04 | 2025-04-04 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35554478 | T2 WV CRUSHER TAP 0/5 REFRAME | 93E
LC | 128448368 | 028/007 | T2 WV MNDCNO-WLTS-FRT BRG 28/7 INS DMPW | WILLITS | ETL.7550.INSL.NCER | 2024-04-04 | 2024-04-04 | 2025-04-03 | On-Time |  | 2025-04-04 | 2025-04-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46308207 | T2 WV MNDCNO-WLTS-FRT BRG 28/7 INS DMPW | ICW
LC | 128448589 | 089/453 | T2 EI MALIN-ROUND MTN #2 89/453 RPR ANCT | TABLEMTN | ETL.6020.TOWR | 2024-04-04 | 2024-04-04 | 2025-02-12 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46381366 | T2 EI MALIN-ROUND MTN #2 89/453 RPR ANCT | ICQ
LC | 128448721 | :008/001 | T2 EI BLT-RVRBNK-MLNS SS :08/01 RPR HRDW | VICTOR | ETL.1070.POLE.NWOD | 2024-04-04 | 2024-04-04 | 2025-04-04 | On-Time |  | 2025-04-04 | 2025-04-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46326957 | T2 EI BLT-RVRBNK-MLNS SS :08/01 RPR HRDW | ICW
LC | 128448733 | 007/048 | T2 OLEUM-""G"" #2 007/048 RPL INSS | CONCORD | ETL.3160.INSL.NCER | 2024-04-04 | 2024-04-04 | 2025-04-12 | Past Due |  | 2025-04-04 | 2025-04-04 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575047 | T2 OLEUM-""G"" #2 RPL INSS IN 2 TWRS. | 93K
LC | 128448848 | 003/082 | T2 EI COLEMAN-SOUTH 3/082 RPL STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-04 | 2024-04-04 | 2025-03-19 | On-Time |  | 2025-04-04 | 2025-04-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556783 | T2 EI COLEMAN-SOUTH 3/082 RPL STRW | 70Y
LC | 128448967 | 087/440 | T2 EI MALIN-ROUND MTN#2 87/440 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-04 | 2024-04-04 | 2025-02-12 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381367 | T2 EI MALIN-ROUND MTN#2 87/440 RPR GYWT | ICQ
LC | 128449780 | 089/452B | T2 EI MALIN-ROUND MTN #2 089/452B UNBURY | TABLEMTN | ETL.6020.TOWR | 2024-04-04 | 2024-04-04 | 2025-02-12 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381369 | T2 EI MALIN-ROUND MTN #2 089/452B UNBURY | ICQ
LC | 128449782 | 007/143 | T2 EI CARIBOU-WESTWOOD 007/143L RPL STRW | TABLEMTN | ETL.6300.POLE.WDPS | 2024-04-04 | 2024-04-04 | 2025-03-10 | On-Time |  | 2025-04-04 | 2025-04-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572142 | T2 EI CARIBOU-WESTWOOD 007/143L RPL STRW | 70Y
LC | 128449783 | 005/042 | T2 PLACER-GOLD HILL #2 5/42 COTTER | SACTO | ETL.4290.INSL.NCER | 2024-04-04 | 2024-04-04 | 2025-01-29 | On-Time |  | 2025-04-04 | 2025-04-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300565 | T2 PLACER-GOLD HILL #2 5/42 COTTER | ICS
LC | 128450335 | 007/143 | T2 EI CARIBOU-WESTWOOD 007/143C RPL STRW | TABLEMTN | ETL.6300.POLE.WDPS | 2024-04-04 | 2024-04-04 | 2025-03-10 | On-Time |  | 2025-04-04 | 2025-04-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572142 | T2 EI CARIBOU-WESTWOOD 007/143L RPL STRW | 70Y
LC | 128451621 | 007/143 | T2 EI CARIBOU-WESTWOOD 007/143R RPL STRW | TABLEMTN | ETL.6300.POLE.WDPS | 2024-04-04 | 2024-04-04 | 2025-03-10 | On-Time |  | 2025-04-04 | 2025-04-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572142 | T2 EI CARIBOU-WESTWOOD 007/143L RPL STRW | 70Y
LC | 128451785 | 086/438 | T2 EI MALIN-ROUND MTN#2 086/438 RPR FOND | TABLEMTN | ETL.6020.TOWR | 2024-04-04 | 2024-04-04 | 2025-02-05 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381372 | T2 EI MALIN-ROUND MTN#2 086/438 RPR FOND | ICQ
LC | 128451954 | 055/495 | T2 DI RND MTN-COTWD #3 55/495 RPL HNGR | TABLEMTN | ETL.5650.INSL.NCER | 2024-04-04 | 2024-04-04 | 2025-03-05 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46310403 | T2 DI RND MTN-COTWD #3 55/495 RPL HNGR | ICQ
LC | 128452039 | 063/004 | T2 EI ELK-GUALALA 63/004 RPR GYWW | WILLITS | ETL.8410.POLE.WOOD | 2024-04-04 | 2024-04-04 | 2025-03-03 | On-Time |  | 2025-04-04 | 2025-04-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46308210 | T2 EI ELK-GUALALA 63/004 RPR GYWW | ICW
LC | 128452045 | 055/495 | T2 DI RND MTN-COTWD #3 55/495 RPR INSS | TABLEMTN | ETL.5650.INSL.NCER | 2024-04-04 | 2024-04-04 | 2025-03-05 | On-Time |  | 2025-04-04 | 2025-04-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46416189 | T2 DI RND MTN-COTWD #3 55/495 RPR INSS | ICS
LC | 128452047 | 055/495 | T2 DI RND MTN-COTWD #3 55/495 RMV VEG | TABLEMTN | ETL.5650.TOWR | 2024-04-04 | 2024-04-04 | 2025-02-07 | On-Time |  | 2025-04-04 | 2025-04-04 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128453912 | 027/220B | T2 EI CARBERY SS-RND MTN 27/220B RMV VEG | TABLEMTN | ETL.5410.TOWR | 2024-04-04 | 2024-04-04 | 2024-11-07 | On-Time |  | 2025-04-04 | 2025-04-04 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128454066 | 025/001B | T2 EI PHILO JCT-ELK 025/001B INS DMPW | WILLITS | ETL.7780.INSL.NCER | 2024-04-04 | 2024-04-04 | 2025-01-27 | On-Time |  | 2025-04-04 | 2025-04-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46340214 | T2 EI PHILO JCT-ELK 025/001B INS DMPW | ICW
LC | 128454124 | 025/001C | T2 EI EI PHILO JCT-ELK 025/001C INS DMPW | WILLITS | ETL.7780.INSL.NCER | 2024-04-04 | 2024-04-04 | 2025-01-27 | On-Time |  | 2025-04-04 | 2025-04-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46340215 | T2 EI EI PHILO JCT-ELK 025/001C INS DMPW | ICW
LC | 128454161 | 018/008 | T2 EI TRINITY-MAPLE CREEK 18/08 RPR GYWW | EUREKA | ETL.8170.POLE.WOOD | 2024-04-04 | 2024-04-04 | 2025-03-01 | On-Time |  | 2025-04-04 | 2025-04-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345747 | T2 EI TRINITY-MAPLE CREEK 18/08 RPR GYWW | ICW
LC | 128454166 | 024/115 | T2 WV MNT VST-CYT SW STA 24/115 INS DMPS | MOSSLNDG | ETL.5090.INSL.NCER | 2024-04-04 | 2024-04-04 | 2025-03-21 | On-Time |  | 2025-04-04 | 2025-04-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Steel | Install | 46391272 | T2 WV MNT VST-CYT SW STA 24/115 INS DMPS | ICS
LC | 128454261 | 003/018 | T2 WV HMBLT BAY-HMBLDT #1 03/18 RPR INSS | EUREKA | ETL.1800.INSL.NCER | 2024-04-04 | 2024-04-04 | 2025-03-03 | On-Time |  | 2025-04-04 | 2025-04-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Insulator-Steel | Repair | 46305587 | T2 WV HMBLT BAY-HMBLDT #1 03/18 RPR INSS | ICS
LC | 128454266 | 014/077 | T2 EI RND MTN-TBL MTN #1 14/077 RPR ANCT | TABLEMTN | ETL.6060.TOWR | 2024-04-04 | 2024-04-04 | 2025-02-18 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46381980 | T2 EI RND MTN-TBL MTN #1 14/077 RPR ANCT | ICQ
LC | 128454267 | 013/069 | T2 EI RND MTN-TBL MTN #1 13/069 RPR ANCT | TABLEMTN | ETL.6060.TOWR | 2024-04-04 | 2024-04-04 | 2025-02-18 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46381982 | T2 EI RND MTN-TBL MTN #1 13/069 RPR ANCT | ICQ
LC | 128454268 | 013/072 | T2 EI RND MTN-TBL MTN #1 13/072 RPR ANCT | TABLEMTN | ETL.6060.TOWR | 2024-04-04 | 2024-04-04 | 2025-02-18 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46381983 | T2 EI RND MTN-TBL MTN #1 13/072 RPR ANCT | ICQ
LC | 128454291 | 025/003 | T2 TRINITY-MAPLE CRK 25/3 GO95 RPL | EUREKA | ETL.8170.POLE.WOOD | 2024-04-04 | 2024-04-04 | 2025-03-31 | On-Time |  | 2025-04-04 | 2025-04-04 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE SPCR ACCL COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35542546 | T2 TRINITY-MAPLE CRK 25/3 RPL O/L POLE | 93G
LC | 128454336 | 013/070 | T2 EI RND MTN-TBL MTN #1 13/070 RPR ANCT | TABLEMTN | ETL.6060.TOWR | 2024-04-04 | 2024-04-04 | 2025-02-18 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46380952 | T2 EI RND MTN-TBL MTN #1 13/070 RPR ANCT | ICQ
LC | 128454338 | 013/070 | T2 EI RND MTN-TBL MT #1 13/70 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-04-04 | 2024-04-04 | 2025-01-22 | On-Time |  | 2025-04-04 | 2025-04-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306208 | T2 EI RND MTN-TBL MT #1 13/70 RMV NEST | ICS
LC | 128454350 | 014/077 | T2 EI RND MTN-TBL MTN #1 14/077 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-04-04 | 2024-04-04 | 2025-01-22 | On-Time |  | 2025-04-04 | 2025-04-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306209 | T2 EI RND MTN-TBL MTN #1 14/077 RMV NEST | ICS
LC | 128454351 | 014/077 | T2 EI RND MTN-TBL MTN #1 14/077 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-04 | 2024-04-04 | 2024-07-01 | On-Time |  | 2025-04-04 | 2025-04-04 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128456925 | 055/495 | T2 DI PIT #1-COTTONWOOD 55/495 RMV VEG | TABLEMTN | ETL.5390.TOWR | 2024-04-05 | 2024-04-04 | 2024-04-04 | Past Due |  | 2025-04-04 | 2025-04-04 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128457082 | 055/495 | T2 DI PIT #1-COTTONWOOD 55/495 RPL HRDT | TABLEMTN | ETL.5390.TOWR | 2024-04-05 | 2024-04-04 | 2024-12-16 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46380953 | T2 DI PIT #1-COTTONWOOD 55/495 RPL HRDT | ICQ
LC | 128457083 | 055/495 | T2 DI PIT #1-COTTONWOOD 55/495 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-04-05 | 2024-04-04 | 2024-04-04 | Past Due |  | 2025-04-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381501 | T2 DI PIT #1-COTTONWOOD 55/495 RPR STRT | ICQ
LC | 128462194 | 054/492 | T2 DI PIT #1-COTTNWD 54/492 RPL HRDT | TABLEMTN | ETL.5390.TOWR | 2024-04-05 | 2024-04-04 | 2024-09-26 | On-Time |  | 2024-10-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Hardware-Tower | Replace | 46256221 | T2 DI PIT #1-COTTONWOOD 54/492 RPL HRDT | ICQ
LC | 128464207 | 034/016 | T2 DI FULTON-HOPLND 34/16 COTTER | LAKEVLLE | ETL.6890.INSL | 2024-04-05 | 2024-04-04 | 2025-03-04 | On-Time |  | 2025-04-04 | 2025-04-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46305591 | T2 DI FULTON-HOPLND 34/16 COTTER | ICW
LC | 128464576 | 005/025 | T2 DI MORRO BAY-TMPLT 5/25 RPR STRT | PISMOBCH | ETL.5933.TOWR | 2024-04-05 | 2024-04-04 | 2025-02-25 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46303920 | T2 DI MORRO BAY-TMPLT 5/25 RPR STRT | ICQ
LC | 128465419 | 022/011 | T2 DI KONOCTI MIDDLETOWN 22/11 RPL STRW | WILLITS | ETL.6380.POLE.WOOD | 2024-04-05 | 2024-04-04 | 2025-03-19 | On-Time |  | 2025-04-04 | 2025-04-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574113 | T2 DI KONOCTI MIDDLETOWN 22/11 RPL STRW | 70Y
LC | 128488248 | 059/536 | T2 DI RND MTN-CTNWD #3 59/536 RPR JUMS | TABLEMTN | ETL.5650.INSL | 2024-04-08 | 2024-04-04 | 2024-08-25 | On-Time |  | 2024-07-04 | 2025-04-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46237145 | T2 DI RND MTN-CTNWD #3 59/536 RPR JMPS | ICS
LC | 128548686 | 012/012 | T2 DI KONOCTI-MIDDLETOWN 12/12 RPR GYWW | WILLITS | ETL.6380.POLE.NWOD | 2024-04-15 | 2024-04-04 | 2025-03-17 | On-Time |  | 2025-04-04 | 2025-04-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46340108 | T2 DI KONOCTI-MIDDLETOWN 12/12 RPR GYWW | ICW
LC | 128548892 | 059/535 | T2 DI ROUND MT-COTT#3 59/535 RPL INSS | TABLEMTN | ETL.5650.INSL | 2024-04-15 | 2024-04-04 | 2025-03-06 | On-Time |  | 2025-04-04 | 2025-04-04 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574240 | T2 ROUND MTN-COTNWD #3 47/411 RPL INSS | 93K
LC | 128548895 | 059/535 | T2 DI ROUND MT-COTT#3 59/535 RPR STRT | TABLEMTN | ETL.5650.TOWR | 2024-04-15 | 2024-04-04 | 2025-02-19 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310406 | T2 DI ROUND MT-COTT#3 59/535 RPR STRT | ICQ
LC | 128548951 | 001/048 | T2 DI CASCADE-B-DESH 1/48 RPR GYWW | TABLEMTN | ETL.6310.POLE.WOOD | 2024-04-15 | 2024-04-04 | 2024-05-15 | On-Time |  | 2025-04-04 | 2025-04-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46249153 | T2 DI CASCADE-B-DESH 1/48 RPR GYWW | ICW
LC | 128548954 | 001/048 | T2 DI CASCADE-B-DESH 1/48 RPL INSW | TABLEMTN | ETL.6310.INSL.NCER | 2024-04-15 | 2024-04-04 | 2025-03-31 | On-Time |  | 2025-04-04 | 2025-04-04 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35556135 | T2 DI CASCADE-B-DESH 1/48 RPL INSW | 93I
LC | 128548991 | 059/535 | T2 DI PIT #1-COTTONWOOD 59/535 BENT STL | TABLEMTN | ETL.5390.TOWR | 2024-04-15 | 2024-04-04 | 2025-03-17 | On-Time |  | 2025-04-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381507 | T2 DI PIT #1-COTTONWOOD 59/535 BENT STL | ICQ
LC | 128549108 | 035/013 | T2 DI FULTON-HOPLAND 35/13 RPR STRW | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-04-15 | 2024-04-04 | 2025-03-19 | On-Time |  | 2025-04-04 | 2025-04-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46305920 | T2 DI FULTON-HOPLAND 35/13 RPR STRW | ICW
LC | 128549232 | 059/536 | T2 DI PIT #1-COTTON 59/536 RPR JUMS | TABLEMTN | ETL.5390.INSL.NCER | 2024-04-15 | 2024-04-04 | 2024-11-05 | On-Time |  | 2024-07-04 | 2025-04-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46247590 | T2 DI PIT#1-COTTON 59/536 RPR JMPS | ICS
LC | 128549280 | 006/062B | T2 IGNACIO-BOLNS#1 6/62B CANCEL | LAKEVLLE | ETL.7140.POLE.WOOD | 2024-04-15 | 2024-04-04 | 2024-04-04 | Past Due |  | 2025-04-04 | 2025-04-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCL OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46403742 | T2 DI IGNACIO-BOLNS#1 6/62B RPR GYWW | ICW
LC | 128549301 | 000/008 | T3 DI DESABLA-CENTERVILLE 0/8 RPL STRW | TABLEMTN | ETL.6720.POLE.WOOD | 2024-04-15 | 2024-04-04 | 2024-11-15 | On-Time |  | 2025-04-04 | 2025-04-04 | 372T | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35553385 | T3 DI DESABLA-CENTERVILLE 0/8 RPL STRW | 70Y
LC | 128551120 | 012/168 | T2 DI ATSCDRO-SLO 12/168 COMPLETE | PISMOBCH | ETL.8490.TOWR | 2024-04-16 | 2024-04-04 | 2025-03-28 | On-Time |  | 2024-10-04 | 2025-04-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476058 | T2 DI ATSCDRO-SLO 12/168 TOUCH | ICQ
LC | 123246273 | 010/045 | T2NT EI DIABLO-GATES #1 010/045 RPR FOND | PISMOBCH | ETL.5960.TOWR | 2022-04-05 | 2022-04-05 | 2023-07-25 | On-Time |  | 2025-04-05 | 2025-04-05 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45639036 | T2 EI DIABLO-GATES #1 010/045 RPR FOND | ICQ
LC | 123246735 | 015/080 | T2NT EI RND MN-TBL MN #1 15/80 RPR GYWS | TABLEMTN | ETL.6060.TOWR | 2022-04-05 | 2022-04-05 | 2023-09-13 | On-Time |  | 2025-04-05 | 2025-04-05 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45699103 | T2 EI RND MTN-TBL MTN #1 15/80 RPR GYWS | ICS
LC | 123247735 | 050/219 | T2NT EI RND MT-TBL MT #2 50/219 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2022-04-05 | 2022-04-05 | 2023-08-02 | On-Time |  | 2025-04-05 | 2025-04-05 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO CLMB FRAB | Overgrown | Vegetation | Remove
LC | 123248561 | 016/082 | T2NT EI RND MT-TBL MT #1 16/82 BNT STEEL | TABLEMTN | ETL.6060.TOWR | 2022-04-05 | 2022-04-05 | 2023-09-13 | On-Time |  | 2025-04-05 | 2025-04-05 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644426 | T2 EI RND MTN-TBL MTN #1 16/82 BNT STEEL | ICQ
LC | 123250193 | 006/029 | T2NT EI DIABLO-GATES #1 006/029 MASTIC | PISMOBCH | ETL.5960.TOWR | 2022-04-05 | 2022-04-05 | 2023-07-17 | On-Time |  | 2025-04-05 | 2025-04-05 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45639037 | T2 EI DIABLO-GATES #1 006/029 MASTIC | ICQ
LC | 123250743 | 016/084 | T2NT EI RND MTN-TBL MN #1 16/84 BNT STL | TABLEMTN | ETL.6060.TOWR | 2022-04-05 | 2022-04-05 | 2023-09-13 | On-Time |  | 2025-04-05 | 2025-04-05 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644428 | T2 EI RND MTN-TBL MTN #1 16/84 BNT STEEL | ICQ
LC | 123251158 | 000/004 | T3NT EI WOODLEAF-PALERMO 0/4 RPR GYWW | TABLEMTN | ETL.4220.POLE.STPS | 2022-04-05 | 2022-04-05 | 2023-04-11 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45681361 | T3NT EI WOODLEAF-PALERMO 0/4 RPR GYWW | ICW
LC | 123251515 | 016/085 | T2NT EI RND MTN-TL MN #1 16/85 BNT STEEL | TABLEMTN | ETL.6060.TOWR | 2022-04-05 | 2022-04-05 | 2023-09-13 | On-Time |  | 2025-04-05 | 2025-04-05 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644431 | T2 EI RND MTN-TBL MTN #1 16/85 BNT STEEL | ICQ
LC | 123317576 | 019/426 | T2NT DI VOLTA-DESCHUTES 19/426 RPL POLE | TABLEMTN | ETL.8290.POLE.WOOD | 2022-04-13 | 2022-04-05 | 2023-05-17 | On-Time |  | 2025-04-05 | 2025-04-05 | 372 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 31635557 | T2 DI VOLTA-DESCHUTES 19/426 RPL POLE | 70Y
LC | 123340578 | 016/004 | T0 T2NT DI COALINGA #1-SAN MIGUEL 16/04 | FRESNO | ETL.8580.TOWR | 2022-04-15 | 2022-04-05 | 2023-06-27 | On-Time |  | 2025-04-05 | 2025-04-05 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH PRTO AIR FRAA TER0 NTDE | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45639142 | DI COALINGA #1-SAN MIGUEL 16/04 RPR FOND | ICQ
LC | 123350789 | 003/009 | T3NT DI BRIDGEVL-GARBERVL 3/9 RPL POLE | EUREKA | ETL.6220.POLE.WOOD | 2022-04-18 | 2022-04-05 | 2024-10-09 | On-Time |  | 2025-04-05 | 2025-04-05 | 372 | TR3 | YES | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH XMPT TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 31604325 | T2 EI BRIDGEVILLE-GARBERVILLE 0/4 RPL PL | 70Y
LC | 128456985 | 012/084 | T2 EI LAS POSITAS-NEWARK 12/84 RPL INSS | CONCORD | ETL.4980.INSL.CERA | 2024-04-05 | 2024-04-05 | 2025-06-05 | Past Due |  | 2025-04-05 | 2025-04-05 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575049 | T2 EI LAS POSITAS-NEWARK 12/84 RPL INSS | 93K
LC | 128457196 | 022/128 | T2 EI STANSLS-MANTECA #2 22/128 COTTER | VICTOR | ETL.3820.INSL.CERA | 2024-04-05 | 2024-04-05 | 2025-03-06 | On-Time |  | 2025-04-05 | 2025-04-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46299704 | T2 EI STANSLS-MANTECA #2 22/128 COTTER | ICS
LC | 128457382 | 088/447 | T2 EI MLN-RND MTN #2 88/447 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-04-05 | 2024-04-05 | 2025-02-08 | On-Time |  | 2025-04-05 | 2025-04-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46332479 | T2 EI MLN-RND MTN #2 88/447 RPR SHLD | ICS
LC | 128457612 | 032/003A | T2 EI PHILO JCT-ELK 032/003A REM VEG | WILLITS | ETL.7780.POLE.WOOD | 2024-04-05 | 2024-04-05 | 2025-03-17 | On-Time |  | 2025-04-05 | 2025-04-05 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128457617 | 001/000 | T2 EI POTTER VALLEY-WILLITS 1/0 RPR ANCW | WILLITS | ETL.7820.POLE.NWOD | 2024-04-05 | 2024-04-05 | 2025-02-18 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46308219 | T2 EI POTTER VALLEY-WILLITS 1/0 RPR ANCW | ICW
LC | 128457688 | 000/002 | T2 WV IONE TAP 000/002 INS DAMW | VICTOR | ETL.8253.INSL.CERA | 2024-04-05 | 2024-04-05 | 2025-03-11 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46299705 | T2 WV IONE TAP 000/002 INS DAMW | ICW
LC | 128457785 | 022/129 | T2 EI STNSLS-MNS SS-RVRBNK 22/129 COTTER | VICTOR | ETL.3840.INSL.NCER | 2024-04-05 | 2024-04-05 | 2024-04-23 | On-Time |  | 2024-10-05 | 2025-04-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46229394 | T2 EI STNSLS-MNS SS-RVRBNK 22/129 COTTER | ICS
LC | 128457838 | 011/187 | T2 WV SURF TAP 11/187 INS DMPS | PISMOBCH | ETL.1381.INSL.NCER | 2024-04-05 | 2024-04-05 | 2025-04-04 | On-Time |  | 2025-04-05 | 2025-04-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Steel | Install | 46329507 | T2 WV SURF TAP 11/187 INS DMPS | ICS
LC | 128459972 | 025/005B | T2 EI PHILO JCT-ELK 025/005B RPL ANCW | WILLITS | ETL.7780.POLE.WOOD | 2024-04-05 | 2024-04-05 | 2025-01-27 | On-Time |  | 2025-04-05 | 2025-04-05 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573420 | T2 EI PHILO JCT-ELK 025/005B RPL ANCW | 93E
LC | 128459977 | 005/026 | T2 WV TULUCAY-VACA 005/026 INS DMPS | SACTO | ETL.5800.INSL | 2024-04-05 | 2024-04-05 | 2025-03-29 | On-Time |  | 2025-04-05 | 2025-04-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Steel | Install | 46324631 | T2 WV TULUCAY-VACA 005/026 INS DMPS | ICS
LC | 128462196 | 021/136 | T2 EI STNSLS-MLNS ST-MNT 21/136 COTTER | VICTOR | ETL.3830.INSL | 2024-04-05 | 2024-04-05 | 2024-04-23 | On-Time |  | 2025-04-05 | 2025-04-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA | No Good/Out of Stdrd | Insulator-Steel | Repair | 46229395 | T2 EI STNSLS-MLNS ST-MNT 21/136 COTTER | ICS
LC | 128462209 | 004/006 | T2 WV MELONES-CURTIS 04/06 RPL HNGR | VICTOR | ETL.2390.INSL.NCER | 2024-04-05 | 2024-04-05 | 2025-05-11 | Past Due |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hanger Plate - Wood | Replace | 46299706 | T2 WV MELONES-CURTIS 04/06 RPL HNGR | ICW
LC | 128462470 | 025/004 | T2 EI PHILO JCT-ELK 025/004 RMV VEG | WILLITS | ETL.7780.POLE.WOOD | 2024-04-05 | 2024-04-05 | 2025-03-27 | On-Time |  | 2025-04-05 | 2025-04-05 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128463973 | 022/130 | T2 EI STNSLS-MNTCA #2 22/130 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-05 | 2024-04-05 | 2025-01-22 | On-Time |  | 2025-04-05 | 2025-04-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46416247 | T2 EI STNSLS-MNTCA #2 22/130 UNBURY | ICQ
LC | 128464187 | 003/027 | T2 OLEUM-N TWR-CHRSTIE 3/27 HANGER | CONCORD | ETL.3180.INSL.NCER | 2024-04-05 | 2024-04-05 | 2024-04-05 | Past Due |  | 2025-04-05 | 2025-04-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46287193 | T2 WV OLEUM-N TWR-CHRSTIE 3/27 HANGER | ICQ
LC | 128464302 | 002/026 | T2 DI CHRISTIE-WILLOW PASS 2/26 RPR INSW | CONCORD | ETL.6370.INSL.NCER | 2024-04-05 | 2024-04-05 | 2025-03-17 | On-Time |  | 2025-04-05 | 2025-04-05 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Out of Adjustment | Switch | Repair | 46525506 | T2 DI CHRISTIE-WILLOW PASS 2/26 RPR INSW | ICE
LC | 128464511 | 007/153 | T2 WV KILARC-DESCHUTES 007/153 INS RPTW | TABLEMTN | ETL.7300.POLE.NWOD | 2024-04-05 | 2024-04-05 | 2024-04-09 | On-Time |  | 2025-04-05 | 2025-04-05 | 672 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Raptor Guard-Wood | Install | 31691981 | T2 WV KILARC-DESCHUTES 007/153 INS RPTW | 93B
LC | 128464816 | 000/001 | T2 EI CHRISTIE-SOBRANTE 0/1 RPR JUMS | CONCORD | ETL.1260.INSL.CERA | 2024-04-05 | 2024-04-05 | 2024-07-15 | On-Time |  | 2025-04-05 | 2025-04-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46234722 | T2 EI CHRISTIE-SOBRANTE 00/01 RPR JMPS | ICS
LC | 128464856 | 027/218 | T2 EI CRBRY SS-ROND MTN 27/218 BNT STEEL | TABLEMTN | ETL.5410.TOWR | 2024-04-05 | 2024-04-05 | 2025-02-19 | On-Time |  | 2025-04-05 | 2025-04-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354006 | T2 EI CRBRY SS-ROND MTN 27/218 BNT STEEL | ICQ
LC | 128465850 | 022/133 | T2 EI STNSLS-MANTEC #2 022/133 RPR STRT | VICTOR | ETL.3820.TOWR | 2024-04-05 | 2024-04-05 | 2025-02-26 | On-Time |  | 2025-04-05 | 2025-04-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416248 | T2 EI STNSLS-MANTEC #2 022/133 BNT STEEL | ICQ
LC | 128465851 | 022/133 | T2 EI STNSLS-MANTEC #2 022/133 RPR FOND | VICTOR | ETL.3820.TOWR | 2024-04-05 | 2024-04-05 | 2025-02-26 | On-Time |  | 2025-04-05 | 2025-04-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416249 | T2 EI STNSLS-MANTEC #2 022/133 UNBURY | ICQ
LC | 128466532 | :016/010 | T2 EI EAGLE ROCK-REDBUD :016/10 RPR INSW | WILLITS | ETL.1480.INSL.NCER | 2024-04-05 | 2024-04-05 | 2025-03-10 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46308211 | T2 EI EAGLE ROCK-REDBUD :016/10 RPR INSW | ICW
LC | 128466584 | 026/213 | T2 EI CARBERY SS-RND MTN 26/213 RPR INSS | TABLEMTN | ETL.5410.INSL.NCER | 2024-04-05 | 2024-04-05 | 2025-03-10 | On-Time |  | 2025-04-05 | 2025-04-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46332482 | T2 EI CARBERY SS-RND MTN 26/213 RPR INSS | ICS
LC | 128466794 | 013/125 | T2 EI BRIDGEVILE-COTONWD 13/125 RPR STRW | TABLEMTN | ETL.1110.POLE.WOOD | 2024-04-05 | 2024-04-05 | 2025-02-07 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311115 | T2 EI BRIDGEVILE-COTONWD 13/125 RPR STRW | ICW
LC | 128466916 | 032/003B | T2 EI PHILO JCT-ELK 032/003B RMV VEG | WILLITS | ETL.7780.POLE.WOOD | 2024-04-05 | 2024-04-05 | 2025-03-17 | On-Time |  | 2025-04-05 | 2025-04-05 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128466930 | 032/000 | T2 EI PHILO JCT-ELK 32/00L COTTER | WILLITS | ETL.7780.POLE.WDPS | 2024-04-05 | 2024-04-05 | 2025-01-29 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46340216 | T2 EI PHILO JCT-ELK 32/00L COTTER | ICW
LC | 128466976 | 014/073 | T2 EI RND MTN-TBL MTN #1 14/073 RPR ANCT | TABLEMTN | ETL.6060.TOWR | 2024-04-05 | 2024-04-05 | 2025-01-22 | On-Time |  | 2025-04-05 | 2025-04-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46380954 | T2 EI RND MTN-TBL MTN #1 14/073 RPR ANCT | ICQ
LC | 128466984 | 014/073 | T2 EI RND MTN-TBL MTN #1 14/073 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-05 | 2024-04-05 | 2024-05-13 | On-Time |  | 2025-04-05 | 2025-04-05 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128467195 | 020/003 | T2 EI TRINTY-MPLE CRK 20/03 RPL SPLW | EUREKA | ETL.8170.INSL.NCER | 2024-04-05 | 2024-04-05 | 2024-04-05 | Past Due |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Splice-Wood | Replace | 46345748 | T2 EI TRINTY-MPLE CRK 20/03 RPL SPLW | ICW
LC | 128467196 | 020/003 | T2 EI TRINTY-MPLE CRK 20/03L RPR GYWW | EUREKA | ETL.8170.POLE.STPS | 2024-04-05 | 2024-04-05 | 2025-03-01 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345749 | T2 EI TRINTY-MPLE CRK 20/03L RPR GYWW | ICW
LC | 128467204 | 022/005 | T2 EI TRINITY-MAPL CREEK 22/5 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-04-05 | 2024-04-05 | 2025-03-01 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345750 | T2NT EI TRINITY-MAPL CREEK 22/5 RPR GYWW | ICW
LC | 128467214 | 020/005 | T2 EI TRINITY-MAPLE CREEK 20/05 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-04-05 | 2024-04-05 | 2024-05-15 | On-Time |  | 2024-10-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46229154 | T2 EI TRINITY-MAPLE CREEK 20/05 RPR GYWW | ICW
LC | 128488468 | 001/001 | T2 DI MNDCNO-WLLTS-FRT BRG 1/1 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-08 | 2024-04-05 | 2025-01-21 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46308224 | T2 DI MNDCNO-WLLTS-FRT BRG 1/1 RPR GYWW | ICW
LC | 128493460 | 005/010 | T2 DI MENDOCINO-WFTBR 5/10 RPR GYWW | WILLITS | ETL.7550.POLE.NWOD | 2024-04-08 | 2024-04-05 | 2025-01-21 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46308226 | T2 DI MENDOCINO-WFTBR 5/10 RPR GYWW | ICW
LC | 128548674 | 004/001 | T2 DI MENDO-WLITS-FRT BRG 04/01 RPR STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-15 | 2024-04-05 | 2025-01-21 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46308225 | T2 DI MENDO-WLITS-FRT BRG 04/01 RPR STRW | ICW
LC | 128549084 | 000/012 | T2 DI MNDCN-WLLTS-FRT BRG 0/12 RPR STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-15 | 2024-04-05 | 2025-03-31 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46308214 | T2 DI MNDCN-WLLTS-FRT BRG 0/12 RPR STRW | ICW
LC | 128549163 | 005/061 | T3 DI DESABLA-CENTERVILLE 5/61 RPL SPLW | TABLEMTN | ETL.6720.INSL.NCER | 2024-04-15 | 2024-04-05 | 2024-11-14 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR3 PRTO AIR NTDE BRIN | No Good/Out of Stdrd | Splice-Wood | Replace | 46247570 | T3 DI DESABLA-CENTERVILLE 5/61 RPL SPLW | ICW
LC | 128549224 | 003/004 | T2 DI POTTER VALLEY-MNDCN 3/4 RMV NEST | WILLITS | ETL.7810.POLE.NWOD | 2024-04-15 | 2024-04-05 | 2025-03-11 | On-Time |  | 2025-04-05 | 2025-04-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46414823 | T2 DI POTTER VALLEY-MNDCN 3/4 RMV NEST | ICS
LC | 128549227 | 003/004 | T2 DI POTTER VALLEY-MNDCN 3/4 RPR FOND | WILLITS | ETL.7810.POLE.NWOD | 2024-04-15 | 2024-04-05 | 2025-03-17 | On-Time |  | 2025-04-05 | 2025-04-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46290143 | T2 DI POTTER VALLEY-MNDCN 3/4 RPR FOND | ICQ
LC | 128555316 | 006/003 | T2 DI MNDCN-WLLTS-FRT BRG 6/3 RPR GYWW | WILLITS | ETL.7550.POLE.NWOD | 2024-04-16 | 2024-04-05 | 2025-01-21 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46308227 | T2 DI MNDCN-WLLTS-FRT BRG 6/3 RPR GYWW | ICW
LC | 128555393 | 006/078 | T2 DI GRN VLY-PAUL SWT 6/78 RPR STRW | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-04-16 | 2024-04-05 | 2025-03-04 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46391236 | T2 DI GRN VLY-PAUL SWT 6/78 RPR STRW | ICW
LC | 128567764 | 006/074 | T2 DI GRN VLY PL SWT 06/074R RPL HRDW | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-04-17 | 2024-04-05 | 2025-03-05 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46391238 | T2 DI GRN VLY PL SWT 06/074R RPL HRDW | ICW
LC | 128567765 | 006/074 | T2 DI GRN VLY PL SWT 06/074L RPL HRDW | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-04-17 | 2024-04-05 | 2025-03-05 | On-Time |  | 2025-04-05 | 2025-04-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46391237 | T2 DI GRN VLY PL SWT 06/074L RPL HRDW | ICW
LC | 131333195 | 003/027 | T2 OLEUM-N TWR-CHRSTIE 3/27 RPL INSS | CONCORD | ETL.3180.INSL.NCER | 2025-06-09 | 2024-04-05 | 2024-04-05 | Past Due |  | 2025-04-05 | 2025-04-05 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Insulator-Steel | Replace
LC | 123339452 | 000/004 | T3NT DI SOBRANTE-"R" #1+ 00/04 RPR STRT | CONCORD | ETL.3770.TOWR | 2022-04-15 | 2022-04-06 | 2023-03-06 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45686285 | T3 DI SOBRANTE-"R" #1+ 00/04 RPR STRT | ICQ
LC | 128468830 | 016/150 | T2 EI BRDGVLLE-CTTNWD 016/150L RPR ADSS | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-06 | 2024-04-06 | 2025-02-07 | On-Time |  | 2025-04-06 | 2025-04-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | ADSS - Wood | Repair | 46311114 | T2 EI BRDGVLLE-CTTNWD 016/150L RPR ADSS | ICW
LC | 128468858 | 023/138 | T2 EI STANISLS-MNTEC #2 023/138 RMV NEST | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2025-03-18 | On-Time |  | 2025-04-06 | 2025-04-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46299708 | T2 EI STANISLS-MNTEC #2 023/138 RMV NEST | ICS
LC | 128468859 | 023/138 | T2 EI STANISLS-MANTECA #2 023/138 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2025-01-23 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416251 | T2 EI STANISLS-MANTECA #2 023/138 UNBURY | ICQ
LC | 128468870 | 023/138 | T2 EI STANISLS-MNTEC #2 23/138 BNT STEEL | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2025-01-23 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416252 | T2 EI STANISLS-MNTEC #2 23/138 BNT STEEL | ICQ
LC | 128468881 | 095/621 | T2 EI NEWARK-VALLECTOS 95/621 RPR STRT | CONCORD | ETL.7670.TOWR | 2024-04-06 | 2024-04-06 | 2025-02-03 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287197 | T2NT EI NEWARK-VALLECTOS 95/621 RPR STRT | ICQ
LC | 128468886 | 009/203 | T2 EI COLEMAN-SOUTH 9/203 RPR GYWW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-06 | 2024-04-06 | 2024-05-09 | On-Time |  | 2024-10-06 | 2025-04-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46229107 | T2 EI COLEMAN-SOUTH 9/203 RPR GYWW | ICW
LC | 128468943 | 024/139 | T2 EI STANISLS-MANTC #2 024/139 RPL HRDT | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2025-01-23 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46416253 | T2 EI STANISLS-MANTC #2 024/139 RPL HRDT | ICQ
LC | 128468949 | 024/139 | T2 EI STANISLS-MANTECA #2 023/139 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2025-01-23 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416254 | T2 EI STANISLS-MANTECA #2 023/139 UNBURY | ICQ
LC | 128469003 | 025/007 | T2 EI PHILO JCT-ELK 025/007 INS DMPW | WILLITS | ETL.7780.INSL.NCER | 2024-04-06 | 2024-04-06 | 2025-01-28 | On-Time |  | 2025-04-06 | 2025-04-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46340217 | T2 EI PHILO JCT-ELK 025/007 INS DMPW | ICW
LC | 128469030 | 095/618 | T2 EI NEWARK-VALLECITOS 095/618 COMPLETE | CONCORD | ETL.7670.INSL.CERA | 2024-04-06 | 2024-04-06 | 2025-03-19 | On-Time |  | 2025-04-06 | 2025-04-06 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP REMT NOAC SWRK CLR ACCM COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577336 | T2 EI NEWARK-VALLECITOS RPL INSS IN 5 TW | 93K
LC | 128469083 | 026/209 | T2 EI CARBRY SS-RND MTN 26/209 BNT STEEL | TABLEMTN | ETL.5410.TOWR | 2024-04-06 | 2024-04-06 | 2025-02-19 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354007 | T2 EI CARBRY SS-RND MTN 26/209 BNT STEEL | ICQ
LC | 128469093 | 003/018A | T2 EI PITTSBURG-MARTINEZ #23/18A COTTER | CONCORD | ETL.3330.INSL.NCER | 2024-04-06 | 2024-04-06 | 2024-07-11 | On-Time |  | 2025-04-06 | 2025-04-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46234658 | T2 EI PITTSBURG-MARTINEZ #23/18A COTTER | ICS
LC | 128469095 | 009/200 | T2 EI COLEMAN-SOUTH 9/200 RPR GYWW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-06 | 2024-04-06 | 2024-05-09 | On-Time |  | 2024-10-06 | 2025-04-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46229105 | T2 EI COLEMAN-SOUTH 9/200 RPR GYWW | ICW
LC | 128469098 | 009/201 | T2 EI COLEMAN-SOUTH 9/201 RPR GYWW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-06 | 2024-04-06 | 2024-05-09 | On-Time |  | 2024-10-06 | 2025-04-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46229106 | T2 EI COLEMAN-SOUTH 9/201 RPR GYWW | ICW
LC | 128469101 | 026/209 | T2 EI CARBERY SS-RND MTN 26/209 RPR FOND | TABLEMTN | ETL.5410.TOWR | 2024-04-06 | 2024-04-06 | 2025-01-15 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46354008 | T2 EI CARBERY SS-RND MTN 26/209 RPR FOND | ICQ
LC | 128469131 | :001/003 | T2 EI BLT-RVRBNK-MLNS SS :01/03 RPR GYWW | VICTOR | ETL.1070.POLE.NWOD | 2024-04-06 | 2024-04-06 | 2025-02-03 | On-Time |  | 2025-04-06 | 2025-04-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327615 | T2 EI BLT-RVRBNK-MLNS SS :01/03 RPR GYWW | ICW
LC | 128469132 | :006/001 | T2 EI BLT-RBK-MLS SS :06/01 RMV VEG | VICTOR | ETL.1070.POLE.WOOD | 2024-04-06 | 2024-04-06 | 2024-06-10 | On-Time |  | 2025-04-06 | 2025-04-06 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128469148 | 015/137 | T2 EI BRDGVLLE-CTTNWD 015/137R RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-06 | 2024-04-06 | 2024-09-04 | On-Time |  | 2025-04-06 | 2025-04-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46309323 | T2 EI BRDGVLLE-CTTNWD 015/137R RPR GYWW | ICW
LC | 128469153 | 013/005B | T2 HUMBOLDT-MAPLE CRK 13/5B INS MKBL | EUREKA | ETL.7130.POLE.NWOD | 2024-04-06 | 2024-04-06 | 2024-04-06 | Past Due |  | 2025-04-06 | 2025-04-06 | 671T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB NTDE | Missing | FAA Lighting-Wood | Install | 35575573 | T2 EI HUMBOLDT-MAPLE CRK 13/5B INS MKBL | 93P
LC | 128469245 | 024/143 | T2 EI STANISLUS-MANTECA #2 24/143 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2025-03-26 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB BRIN | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46493440 | T2 EI STANISLUS-MANTECA #2 24/143 UNBURY | ICQ
LC | 128469248 | 026/207 | T2 EI CARBRY SS-RND MTN 26/207 BNT STEEL | TABLEMTN | ETL.5410.TOWR | 2024-04-06 | 2024-04-06 | 2025-02-12 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354009 | T2 EI CARBRY SS-RND MTN 26/207 BNT STEEL | ICQ
LC | 128469254 | 024/143 | T2 EI STANISLS-MNTEC #2 24/143 BNT STEEL | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2025-03-03 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416255 | T2 EI STANISLS-MNTEC #2 24/143 BNT STEEL | ICQ
LC | 128469277 | 037/176 | T2 EI MENDCNO-REDBD 37/176 COTTER | WILLITS | ETL.2410.INSL.CERA | 2024-04-06 | 2024-04-06 | 2024-12-05 | On-Time |  | 2024-07-06 | 2025-04-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46233085 | T2 EI MENDCNO-REDBD 37/176 COTTER | ICS
LC | 128469298 | 026/207 | T2 EI CARBERY SS-RND MTN 26/207 RPR FOND | TABLEMTN | ETL.5410.TOWR | 2024-04-06 | 2024-04-06 | 2025-02-03 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46354010 | T2 EI CARBERY SS-RND MTN 26/207 RPR FOND | ICQ
LC | 128469329 | 024/142 | T2 EI STANISLS-MNTEC #2 24/142 COMPLETE | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2025-03-03 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416256 | T2 EI STANISLS-MNTEC #2 24/142 BNT STEEL | ICQ
LC | 128469345 | 024/142 | T2 EI STNISLS-MNTC #2 24/142 COMPLETE | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2025-03-03 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416257 | T2 EI STNISLS-MNTC #2 24/142 UNBURY | ICQ
LC | 128469362 | 003/013 | T2 EI MELONES-RACETRACK 03/013 RPR INSW | VICTOR | ETL.2400.INSL.CERA | 2024-04-06 | 2024-04-06 | 2024-05-09 | On-Time |  | 2025-04-06 | 2025-04-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP CLR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46240443 | T2 EI MELONES-RACETRACK 03/013 RPR INSW | ICW
LC | 128469440 | 026/002 | T2 EI PHILO JCT-ELK 026/002 INS DMPW | WILLITS | ETL.7780.INSL.NCER | 2024-04-06 | 2024-04-06 | 2025-01-28 | On-Time |  | 2025-04-06 | 2025-04-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46340218 | T2 EI PHILO JCT-ELK 026/002 INS DMPW | ICW
LC | 128469459 | 017/155 | T2 EI BRDGVLLE-CTTNWD 017/155L RPL STRW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-06 | 2024-04-06 | 2025-04-06 | On-Time |  | 2025-04-06 | 2025-04-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35555555 | T2 EI BRDGVLLE-CTTNWD 017/155L RPL STRW | 70Y
LC | 128469475 | 017/155 | T2 EI BRDGVLLE-CTTNWD 017/155R RPL STRW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-06 | 2024-04-06 | 2025-04-06 | On-Time |  | 2025-04-06 | 2025-04-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35555555 | T2 EI BRDGVLLE-CTTNWD 017/155L RPL STRW | 70Y
LC | 128469477 | 025/145 | T2 EI STANISLAUS-MNTC #2 25/145 RPL HRDT | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2025-03-03 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46416258 | T2 EI STANISLAUS-MNTC #2 25/145 RPL HRDT | ICQ
LC | 128469483 | 025/145 | T2 EI STNISLS-MNTC #2 25/145 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2025-03-03 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416259 | T2 EI STNISLS-MNTC #2 25/145 UNBURY | ICQ
LC | 128469496 | 025/145 | T2 EI STANISLS-MNTEC #2 25/145 BNT STEEL | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2025-03-03 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416280 | T2 EI STANISLS-MNTEC #2 25/145 BNT STEEL | ICQ
LC | 128469521 | 025/146 | T2 EI STANISLAUS-MNTC #2 25/146 RMV NEST | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2025-03-18 | On-Time |  | 2025-04-06 | 2025-04-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46300263 | T2 EI STANISLAUS-MNTC #2 25/146 RMV NEST | ICS
LC | 128469530 | 026/004 | T2 EI PHILO JCT-ELK 026/004L RPL ANCW | WILLITS | ETL.7780.POLE.WDPS | 2024-04-06 | 2024-04-06 | 2025-01-28 | On-Time |  | 2025-04-06 | 2025-04-06 | 637 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573423 | T2 EI PHILO JCT-ELK 026/004R RPL ANCW | 93E
LC | 128469552 | 025/147 | T2 EI STNISLS-MNTC #2 25/147 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2025-03-06 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46416281 | T2 EI STNISLS-MNTC #2 25/147 UNBURY | ICQ
LC | 128469561 | 009/199 | T2 EI COLEMAN-SOUTH 9/199 RPL INSW | TABLEMTN | ETL.6450.INSL.NCER | 2024-04-06 | 2024-04-06 | 2024-10-21 | On-Time |  | 2024-07-06 | 2025-04-06 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35543858 | T2 EI COLEMAN-SOUTH 9/199 RPL INSW | 93I
LC | 128469660 | 026/004 | T2 EI PHILO JCT-ELK 026/004R RPL ANCW | WILLITS | ETL.7780.POLE.WDPS | 2024-04-06 | 2024-04-06 | 2025-01-28 | On-Time |  | 2025-04-06 | 2025-04-06 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573423 | T2 EI PHILO JCT-ELK 026/004R RPL ANCW | 93E
LC | 128469666 | 085/433 | T2 EI MALIN-ROUND MTN#2 085/433 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-04-06 | 2024-04-06 | 2025-02-08 | On-Time |  | 2025-04-06 | 2025-04-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46332484 | T2 EI MALIN-ROUND MTN#2 085/433 RPR OPGW | ICS
LC | 128469794 | 092/599 | T2 EI NEWARK-VALLECITOS 92/599 RPR STRT | CONCORD | ETL.7670.TOWR | 2024-04-06 | 2024-04-06 | 2025-03-18 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287196 | T2 EI NEWARK-VALLECITOS 92/599 RPR STRT | ICQ
LC | 128469795 | 092/599 | T2 EI NEWARK-VALLECITOS 092/599 RPL INSS | CONCORD | ETL.7670.INSL.CERA | 2024-04-06 | 2024-04-06 | 2025-03-18 | On-Time |  | 2025-04-06 | 2025-04-06 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCM COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577336 | T2 EI NEWARK-VALLECITOS RPL INSS IN 5 TW | 93K
LC | 128469919 | 025/001 | T2 EI TRINITY-MAPLE CREEK 25/1L RMV VEG | EUREKA | ETL.8170.POLE.STPS | 2024-04-06 | 2024-04-06 | 2024-11-15 | On-Time |  | 2025-04-06 | 2025-04-06 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128470366 | 025/149 | T2 EI STANISLS-MNTC #2 25/149 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-07 | 2024-04-06 | 2025-03-06 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46416282 | T2 EI STANISLS-MNTC #2 25/149 UNBURY | ICQ
LC | 128470367 | 025/148 | T2 EI STANISLS-MNTC #2 25/148 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-07 | 2024-04-06 | 2025-03-06 | On-Time |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46416283 | T2 EI STANISLS-MNTC #2 25/148 UNBURY | ICQ
LC | 128474568 | 005/033 | T2 MARTINEZ-SOBRANTE 5/33 RPL INSS | CONCORD | ETL.2270.INSL.NCER | 2024-04-08 | 2024-04-06 | 2025-03-28 | On-Time |  | 2025-04-06 | 2025-04-06 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35573072 | T2 MRTNZ-SOBRANTE 5/33 RPL INSS | 93K
LC | 128481053 | 005/035 | T2 OLEUM-MARTINEZ 5/35 RPL INSS | CONCORD | ETL.3170.INSL | 2024-04-08 | 2024-04-06 | 2025-05-09 | Past Due |  | 2025-04-06 | 2025-04-06 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575051 | T2 OLEUM-MARTINEZ 5/35 RPL INSS | 93K
LC | 128481057 | 005/035 | T2 OLEUM-MARTINEZ 5/35 RPL HNGR | CONCORD | ETL.3170.INSL | 2024-04-08 | 2024-04-06 | 2025-05-09 | Past Due |  | 2025-04-06 | 2025-04-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46287195 | T2 OLEUM-MARTINEZ 5/35 RPL HNGR | ICQ
LC | 123357459 | 011/057 | T2NT DI RND MTN-TBL MN #2 11/57 RMV DBRS | TABLEMTN | ETL.6070.TOWR | 2022-04-18 | 2022-04-07 | 2023-08-16 | On-Time |  | 2025-04-07 | 2025-04-07 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 45700167 | T2 DI RND MTN-TBL MTN #2 11/57 RMV DBRS | ICS
LC | 123383076 | 013/001 | T0 T2NT DI COALINGA #1-SAN MGL 13/1 BNT | FRESNO | ETL.8580.TOWR | 2022-04-21 | 2022-04-07 | 2023-11-22 | On-Time |  | 2025-04-07 | 2025-04-07 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH PRTO AIR FRAA TER0 | No Good/Out of Stdrd | Structure-Tower | Repair | 45639145 | T0 DI COALINGA #1-SAN MGL 13/1 BNT STEEL | ICQ
LC | 123390603 | 048/024 | T2NT DI TRINITY-MAPLE CRK 48/24 RMV BUTT | EUREKA | ETL.8170.POLE.WOOD | 2022-04-22 | 2022-04-07 | 2023-06-15 | On-Time |  | 2025-04-07 | 2025-04-07 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 45576187 | T2NT DI TRINITY-MAPLE CRK 48/24 RMV BUTT | ICW
LC | 123400016 | 000/001 | T2NT DI KNGS RVR-SNGR-RDLY 0/1 RPR GYWW | FRESNO | ETL.2030.POLE.NWOD | 2022-04-23 | 2022-04-07 | 2023-05-11 | On-Time |  | 2025-04-07 | 2025-04-07 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45499474 | T2 DI KNGS RVR-SNGR-RDLY 0/1 RPR GYWW | ICW
LC | 123272838 | 017/093 | T2NT EI RND MT-TB MTN #1 17/93 RPR STRT | TABLEMTN | ETL.6060.TOWR | 2022-04-08 | 2022-04-08 | 2023-08-12 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644433 | T2 EI RND MTN-TBL MTN #1 17/93 RPR STRT | ICQ
LC | 123274200 | 018/095 | T2NT EI RND MTN-TB MTN #1 18/95 RPR STRT | TABLEMTN | ETL.6060.TOWR | 2022-04-08 | 2022-04-08 | 2023-08-11 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644435 | T2 EI RND MTN-TB MTN #1 18/95 RPR STRT | ICQ
LC | 123275871 | 019/082 | T2NT EI TESLA-METCALF 019/082 RPR GYWS | METCALF | ETL.6110.TOWR | 2022-04-08 | 2022-04-08 | 2023-04-26 | On-Time |  | 2025-04-08 | 2025-04-08 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45662483 | T2 EI TESLA-METCALF 019/082 RPR GYWS | ICS
LC | 128471638 | ;005/005 | T2 CARIBOU #2 ;005/005 GO95 RPL | TABLEMTN | ETL.6280.POLE.WOOD | 2024-04-08 | 2024-04-08 | 2025-03-04 | On-Time |  | 2025-04-08 | 2025-04-08 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35542626 | T2 CARIBOU #2 ;005/005 GO95 RPL | 93G
LC | 128471786 | 021/127 | T2 EI STLS-MLNS SS-RVBNK 21/127 RPL INSS | VICTOR | ETL.3840.INSL.CERA | 2024-04-08 | 2024-04-08 | 2024-04-08 | Past Due |  | 2025-04-08 | 2025-04-08 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35597758 | T2 EI STLS-MLNS SS-RVBNK 12/127 RPL INSS | 93K
LC | 128471860 | 005/097 | T2 EI SSQC-SNT YNZ SW STA 5/97 RPL INSW | PISMOBCH | ETL.3700.INSL.CERA | 2024-04-08 | 2024-04-08 | 2025-04-03 | On-Time |  | 2025-04-08 | 2025-04-08 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573767 | T2 EI SSQC-SNT YNZ SW STA 5/97 RPL INSW | 93I
LC | 128472351 | 021/126 | T2 EI STNSLS-MNS SS-RVRBNK 21/126 COTTER | VICTOR | ETL.3840.INSL.CERA | 2024-04-08 | 2024-04-08 | 2025-02-03 | On-Time |  | 2025-04-08 | 2025-04-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300265 | T2 EI STNSLS-MNS SS-RVRBNK 21/126 COTTER | ICS
LC | 128472408 | 021/134 | T2 EI STANSLS-MLNS SS-MNTA 21/134 COTTER | VICTOR | ETL.3830.INSL | 2024-04-08 | 2024-04-08 | 2025-02-03 | On-Time |  | 2025-04-08 | 2025-04-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300266 | T2 EI STANSLS-MLNS SS-MNTA 21/134 COTTER | ICS
LC | 128472448 | 005/091 | T2 EI SSQC-SNT YNZ SW STA 5/91 RPL POLE | PISMOBCH | ETL.3700.POLE.WOOD | 2024-04-08 | 2024-04-08 | 2025-02-10 | On-Time |  | 2025-04-08 | 2025-04-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573766 | T2 EI SSQC-SNT YNZ SW STA 5/91 RPL POLE | 70Y
LC | 128472544 | 021/125 | T2 EI STANSLS-MANTECA #2 21/125 RMV NEST | VICTOR | ETL.3820.TOWR | 2024-04-08 | 2024-04-08 | 2024-04-08 | Past Due |  | 2025-04-08 | 2025-04-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46300267 | T2 EI STANSLS-MANTECA #2 21/125 RMV NEST | ICS
LC | 128473168 | 012/264 | T2 EI COLEMAN-SOUTH 12/264 RPR GYWW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-08 | 2024-04-08 | 2024-05-08 | On-Time |  | 2024-10-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46229108 | T2 EI COLEMAN-SOUTH 12/264 RPR GYWW | ICW
LC | 128473192 | 072/524 | T2 EI BRDGVILL-CTTNWD 072/524R RPL POLE | EUREKA | ETL.1110.POLE.WDPS | 2024-04-08 | 2024-04-08 | 2024-04-08 | Past Due |  | 2025-04-08 | 2025-04-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572068 | T2 EI BRDGVLL-CTTNWD 72/523L RPL STRW | 70Y
LC | 128473314 | 021/124 | T2 EI STANSLS-MANTECA #2 21/124 RMV NEST | VICTOR | ETL.3820.TOWR | 2024-04-08 | 2024-04-08 | 2025-03-06 | On-Time |  | 2025-04-08 | 2025-04-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46300269 | T2 EI STANSLS-MANTECA #2 21/124 RMV NEST | ICS
LC | 128473354 | 072/524 | T2 EI BRDGVILL-CTTNWD 072/524L RPL POLE | EUREKA | ETL.1110.POLE.WDPS | 2024-04-08 | 2024-04-08 | 2024-04-08 | Past Due |  | 2025-04-08 | 2025-04-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572068 | T2 EI BRDGVLL-CTTNWD 72/523L RPL STRW | 70Y
LC | 128473495 | 013/002 | T2 EI HUMBOLDT-MAPLE CREEK 13/2 RPL STRW | EUREKA | ETL.7130.POLE.WOOD | 2024-04-08 | 2024-04-08 | 2025-05-29 | Past Due |  | 2025-04-08 | 2025-04-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574778 | T2 EI HUMBOLDT-MAPLE CREEK 13/2 RPL STRW | 70Y
LC | 128473664 | 072/523 | T2 EI BRDGVLL-CTTNWD 72/523L RPL STRW | EUREKA | ETL.1110.POLE.WDPS | 2024-04-08 | 2024-04-08 | 2024-04-08 | Past Due |  | 2025-04-08 | 2025-04-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35572068 | T2 EI BRDGVLL-CTTNWD 72/523L RPL STRW | 70Y
LC | 128473695 | 072/523 | T2 EI BRDGVLL-CTTNWD 72/523R RPL STRW | EUREKA | ETL.1110.POLE.WDPS | 2024-04-08 | 2024-04-08 | 2024-04-08 | Past Due |  | 2025-04-08 | 2025-04-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35572068 | T2 EI BRDGVLL-CTTNWD 72/523L RPL STRW | 70Y
LC | 128473699 | 020/131 | T2 EI STNSLS-MLNS SS-MNTCA 20/131 UNBURY | VICTOR | ETL.3830.TOWR | 2024-04-08 | 2024-04-08 | 2025-03-04 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416291 | T2 EI STNSLS-MLNS SS-MNTCA 20/131 UNBURY | ICQ
LC | 128473712 | 021/123 | T2 EI STNSLS-MNTCA #2 21/123 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-08 | 2024-04-08 | 2025-03-04 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416292 | T2 EI STNSLS-MNTCA #2 21/123 UNBURY | ICQ
LC | 128473730 | 020/131 | T2 EI STNSLS-MLNS SS-MNTCA 20/131 COTTER | VICTOR | ETL.3830.INSL | 2024-04-08 | 2024-04-08 | 2025-02-03 | On-Time |  | 2025-04-08 | 2025-04-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300270 | T2 EI STNSLS-MLNS SS-MNTCA 20/131 COTTER | ICS
LC | 128473757 | 021/123 | T2NT EI STNLS-MNTCA #2 21/123 RPR STRT | VICTOR | ETL.3820.TOWR | 2024-04-08 | 2024-04-08 | 2025-03-04 | On-Time |  | 2027-04-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416293 | T2NT EI STNLS-MNTCA #2 21/123 RPR STRT | ICQ
LC | 128473912 | 010/103 | T2 EI PIT #5-RND MTN #2 10/103 RPL INSS | TABLEMTN | ETL.5430.INSL.CERA | 2024-04-08 | 2024-04-08 | 2025-03-06 | On-Time |  | 2025-04-08 | 2025-04-08 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35571200 | T2 EI PIT #5-RND MTN #2 RPL INSS 2 TWRS | 93K
LC | 128474005 | 072/522 | T2 EI BRDGVLL-CTTNWD 72/522R RPL ANCW | EUREKA | ETL.1110.POLE.STPS | 2024-04-08 | 2024-04-08 | 2025-05-15 | Past Due |  | 2025-04-08 | 2025-04-08 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572066 | T2 EI BRDGVLL-CTTNWD 72/522R RPL ANCW | 93E
LC | 128474063 | 072/522 | T2 EI BRDGVLL-CTTNWD 72/522L RPL ANCW | EUREKA | ETL.1110.POLE.STPS | 2024-04-08 | 2024-04-08 | 2025-05-15 | Past Due |  | 2025-04-08 | 2025-04-08 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572066 | T2 EI BRDGVLL-CTTNWD 72/522R RPL ANCW | 93E
LC | 128474084 | 021/122 | T2 EI STNSLS-MNTCA #2 21/122 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-08 | 2024-04-08 | 2025-01-15 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46416294 | T2 EI STNSLS-MNTCA #2 21/122 UNBURY | ICQ
LC | 128474085 | 021/122 | T2 EI STNSLS-MNTCA #2 21/122 INS DAMS | VICTOR | ETL.3820.INSL.NCER | 2024-04-08 | 2024-04-08 | 2025-04-07 | On-Time |  | 2025-04-08 | 2025-04-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Steel | Install | 46300271 | T2 EI STNSLS-MNTCA #2 21/122 INS DAMS | ICS
LC | 128474102 | 025/202 | T2 EI CARBERRY SS-RND MTN 25/202 RMV VEG | TABLEMTN | ETL.5410.TOWR | 2024-04-08 | 2024-04-08 | 2024-10-30 | On-Time |  | 2025-04-08 | 2025-04-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128474106 | 021/122 | T2 EI STNSLS-MNTCA #2 21/122 RPR CNDW | VICTOR | ETL.3820.INSL.NCER | 2024-04-08 | 2024-04-08 | 2025-04-07 | On-Time |  | 2025-04-08 | 2025-04-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Conductor-Steel | Repair | 46300272 | T2 EI STNSLS-MNTCA #2 21/122 RPR CNDW | ICS
LC | 128474157 | 025/201 | T2 EI CARBERY SS-RND MTN 25/201 RMV VEG | TABLEMTN | ETL.5410.TOWR | 2024-04-08 | 2024-04-08 | 2024-07-11 | On-Time |  | 2025-04-08 | 2025-04-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128474224 | 010/102 | T2 EI PIT #5-RND MTN #2 10/102 RPL INSS | TABLEMTN | ETL.5430.INSL.CERA | 2024-04-08 | 2024-04-08 | 2025-03-06 | On-Time |  | 2025-04-08 | 2025-04-08 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35571200 | T2 EI PIT #5-RND MTN #2 RPL INSS 2 TWRS | 93K
LC | 128474258 | 092/602 | T2 NEWARK-VALLECITOS 092/602 RPL INSS | CONCORD | ETL.7670.INSL.CERA | 2024-04-08 | 2024-04-08 | 2024-04-08 | Past Due |  | 2025-04-08 | 2025-04-08 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP REMT NOAC SWRK CLR ACCM OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577336 | T2 EI NEWARK-VALLECITOS RPL INSS IN 5 TW | 93K
LC | 128474259 | 023/207 | T2 EI BRDGVLLE-CTTNWD 23/207L COMPLETE | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-08 | 2024-04-08 | 2025-02-08 | On-Time |  | 2025-04-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311108 | T2 EI BRDGVLLE-CTTNWD 23/207L RPR GYWW | ICW
LC | 128474296 | 020/129 | T2 STAN-MELONES SS 20/129 TOUCH | VICTOR | ETL.3830.TOWR | 2024-04-08 | 2024-04-08 | 2024-04-08 | Past Due |  | 2024-10-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46477858 | T2 EI STAN-MELONES SS 20/129 TOUCH | ICQ
LC | 128474313 | 022/198 | T2 EI BRDGVLLE-CTTNWD 22/198L RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-08 | 2024-04-08 | 2025-02-17 | On-Time |  | 2025-04-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311113 | T2 EI BRDGVLLE-CTTNWD 22/198L RPR GYWW | ICW
LC | 128474326 | 023/207 | T2 EI BRDGVLLE-CTTNWD 23/207R COMPLETE | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-08 | 2024-04-08 | 2025-02-08 | On-Time |  | 2025-04-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311109 | T2 EI BRDGVLLE-CTTNWD 23/207R RPR GYWW | ICW
LC | 128474340 | 022/198 | T2 EI BRDGVLLE-CTTNWD 22/198R RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-08 | 2024-04-08 | 2025-02-17 | On-Time |  | 2025-04-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311112 | T2 EI BRDGVLLE-CTTNWD 22/198R RPR GYWW | ICW
LC | 128474455 | 010/101 | T2 EI PIT #5 RND MTN #2 10/101L RPL POLE | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-08 | 2024-04-08 | 2025-03-05 | On-Time |  | 2025-04-08 | 2025-04-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35607187 | T2 EI PIT #5 RND MTN #2 10/101L RPL POLE | 70Y
LC | 128474508 | 010/101 | T2 EI PIT #5 RND MTN #2 10/101R RPL POLE | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-08 | 2024-04-08 | 2025-03-05 | On-Time |  | 2025-04-08 | 2025-04-08 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35607187 | T2 EI PIT #5 RND MTN #2 10/101L RPL POLE | 70Y
LC | 128474630 | 020/120 | T2 EI STNSLS-MNTC #2 20/120 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-08 | 2024-04-08 | 2025-03-06 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416296 | T2 EI STNSLS-MNTC #2 20/120 UNBURY | ICQ
LC | 128474658 | 020/128 | T2 STANSLS-MELONES SS MNTCA 20/128 TOUCH | VICTOR | ETL.3830.TOWR | 2024-04-08 | 2024-04-08 | 2024-04-08 | Past Due |  | 2024-10-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46477859 | T2 EI STAN-MELONES SS 20/128 TOUCH | ICQ
LC | 128474679 | 092/604 | T2 EI NEWARK-VALLECITOS 092/604 RPL INSS | CONCORD | ETL.7670.INSL.CERA | 2024-04-08 | 2024-04-08 | 2024-04-08 | Past Due |  | 2025-04-08 | 2025-04-08 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP REMT SWRK CLR ACCM OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577336 | T2 EI NEWARK-VALLECITOS RPL INSS IN 5 TW | 93K
LC | 128475536 | 093/605 | T2 EI NEWARK-VALLECITOS 093/605 RPL INSS | CONCORD | ETL.7670.INSL.CERA | 2024-04-08 | 2024-04-08 | 2024-04-08 | Past Due |  | 2025-04-08 | 2025-04-08 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP REMT SWRK CLR ACCM OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577336 | T2 EI NEWARK-VALLECITOS RPL INSS IN 5 TW | 93K
LC | 128477663 | 009/098 | T2 EI PIT #5 ROUND MTN#2 9/98L RPL STRW | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-08 | 2024-04-08 | 2025-03-04 | On-Time |  | 2025-04-08 | 2025-04-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35607186 | T2 EI PIT #5 ROUND MTN#2 9/98L RPL STRW | 70Y
LC | 128478692 | 009/098 | T2 EI PIT #5 ROUND MTN#2 9/98R RPL STRW | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-08 | 2024-04-08 | 2025-03-04 | On-Time |  | 2025-04-08 | 2025-04-08 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35607186 | T2 EI PIT #5 ROUND MTN#2 9/98L RPL STRW | 70Y
LC | 128479826 | 004/059 | T2 DI GRN VLY-PAUL SWEET 4/59L RMV VEG | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-04-08 | 2024-04-08 | 2024-05-10 | On-Time |  | 2024-10-08 | 2025-04-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128480696 | 009/197 | T2 WV KILARC-DESCHUTES 009/197 RPL STRW | TABLEMTN | ETL.7300.POLE.WOOD | 2024-04-08 | 2024-04-08 | 2025-03-11 | On-Time |  | 2025-04-08 | 2025-04-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573774 | T2 WV KILARC-DESCHUTES 009/197 RPL STRW | 70Y
LC | 128484304 | 024/004 | T2 EI RIO DELL JCT-BRDGVLL 24/4 RPL INSW | EUREKA | ETL.7850.INSL.NCER | 2024-04-08 | 2024-04-08 | 2025-06-13 | Past Due |  | 2025-04-08 | 2025-04-08 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572964 | T2 EI RIO DELL JCT-BRDGVLL 24/4 RPL INSW | 93I
LC | 128484308 | 025/151 | T2 EI STNSLS-MNTCA #2 25/151 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-08 | 2024-04-08 | 2025-03-04 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46416297 | T2 EI STNSLS-MNTCA #2 25/151 UNBURY | ICQ
LC | 128485452 | 025/151 | T2 EI STNSLS-MNTCA #2 25/151 RPR INSS | VICTOR | ETL.3820.INSL.CERA | 2024-04-08 | 2024-04-08 | 2025-04-07 | On-Time |  | 2025-04-08 | 2025-04-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300274 | T2 EI STNSLS-MNTCA #2 25/151 RPR INSS | ICS
LC | 128485722 | 025/159 | T2 EI STANSLS-MLNS SS-MNTA 25/159 UNBURY | VICTOR | ETL.3830.TOWR | 2024-04-08 | 2024-04-08 | 2025-03-04 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416298 | T2 EI STANSLS-MLNS SS-MNTA 25/159 UNBURY | ICQ
LC | 128485725 | 023/202 | T2 EI BRDGVLLE-CTTNWD 23/202R RPR GYWW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-08 | 2024-04-08 | 2024-05-29 | On-Time |  | 2025-04-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46254931 | T2 EI BRDGVLLE-CTTNWD 23/202R RPR GYWW | ICW
LC | 128485726 | 023/203 | T2 EI BRDGVLLE-CTTNWD 23/203R COMPLETE | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-08 | 2024-04-08 | 2025-02-08 | On-Time |  | 2025-04-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311111 | T2 EI BRDGVLLE-CTTNWD 23/203R RPR GYWW | ICW
LC | 128486120 | 023/203 | T2 EI BRDGVLLE-CTTNWD 23/203L COMPLETE | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-08 | 2024-04-08 | 2025-02-08 | On-Time |  | 2025-04-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311110 | T2 EI BRDGVLLE-CTTNWD 23/203L RPR GYWW | ICW
LC | 128488991 | 017/220 | T2 EI WST PNT-VLL SPRNGS 17/220 RPR ANCW | VICTOR | ETL.8350.POLE.NWOD | 2024-04-08 | 2024-04-08 | 2025-01-30 | On-Time |  | 2025-04-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46326958 | T2 EI WST PNT-VLL SPRNGS 17/220 RPR ANCW | ICW
LC | 128493238 | 003/057 | T2 DI GRN VALY-PAUL SWEET 03/57 RPL INSW | MOSSLNDG | ETL.1730.INSL.CERA | 2024-04-08 | 2024-04-08 | 2025-03-07 | On-Time |  | 2025-04-08 | 2025-04-08 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573560 | T2 DI GRN VALY-PAUL SWEET 03/57 RPL INSW | 93I
LC | 128493544 | :016/013 | T2 DI EAGLE ROCK-REDBUD :16/13 COTTER | WILLITS | ETL.1480.INSL.NCER | 2024-04-08 | 2024-04-08 | 2024-12-10 | On-Time |  | 2024-07-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46232916 | T2 DI EAGLE ROCK-REDBUD :16/13 COTTER | ICW
LC | 128493578 | 022/002 | T2 EI COALINGA#1-SN MIGUEL 22/2 RPR FOND | FRESNO | ETL.8580.TOWR | 2024-04-08 | 2024-04-08 | 2025-01-13 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46292638 | T2 EI COALINGA#1-SN MIGUEL 22/2 RPR FOND | ICQ
LC | 128493579 | 022/002 | T2 EI COALINGA#1-SN MIGUEL 22/2 TOUCH | FRESNO | ETL.8580.TOWR | 2024-04-08 | 2024-04-08 | 2025-01-13 | On-Time |  | 2024-10-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46475362 | T2 EI COALINGA#1-SN MIGUEL 22/2 TOUCH | ICQ
LC | 128494215 | 085/430 | T2 EI MALIN-ROUND MTN#2 85/430 UNBURY | TABLEMTN | ETL.6020.TOWR | 2024-04-09 | 2024-04-08 | 2025-02-11 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381370 | T2 EI MALIN-ROUND MTN#2 85/430 UNBURY | ICQ
LC | 128494256 | 085/430 | T2 EI MALIN-ROUND MTN #2 85/430 RPR STRT | TABLEMTN | ETL.6020.TOWR | 2024-04-09 | 2024-04-08 | 2024-04-08 | Past Due |  | 2025-04-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381373 | T2 EI MALIN-ROUND MTN #2 85/430 RPR STRT | ICQ
LC | 128494258 | 085/433 | T2 EI MLIN-ROUND MTN#2 85/433 RPR STRT | TABLEMTN | ETL.6020.TOWR | 2024-04-09 | 2024-04-08 | 2025-02-05 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46380957 | T2 EI MLIN-ROUND MTN#2 85/433 RPR STRT | ICQ
LC | 128494300 | 085/433 | T2 EI MALIN-ROUND MTN #2 85/433 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-09 | 2024-04-08 | 2025-02-05 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46380958 | T2 EI MALIN-ROUND MTN #2 85/433 RPR GYWT | ICQ
LC | 128494301 | 085/432 | T2 EI MALIN-ROUND MTN#2 85/432 UNBURY | TABLEMTN | ETL.6020.TOWR | 2024-04-09 | 2024-04-08 | 2025-02-05 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46380959 | T2 EI MALIN-ROUND MTN#2 85/432 UNBURY | ICQ
LC | 128497556 | 004/050 | T3 DI DESALBA-CNTRVILLE 4/50 RPR JUMW | TABLEMTN | ETL.6720.INSL.CERA | 2024-04-09 | 2024-04-08 | 2025-04-16 | Past Due |  | 2025-04-08 | 2025-04-08 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46230797 | T3 DI DESALBA-CNTRVILLE 4/50 RPR JUMW | ICW
LC | 128548557 | A032/008 | T2 DI FLTN-CALISTOGA A032/008 RPR STRW | LAKEVLLE | ETL.6880.POLE.WOOD | 2024-04-15 | 2024-04-08 | 2025-04-08 | On-Time |  | 2025-04-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Structure-Wood | Repair | 46305926 | T2 DI FLTN-CALISTOGA A032/008 RPR STRW | ICW
LC | 128548805 | 009/184-GUY | T2 MNTA VISTA-LS GATOS 9/184 RPL GYPL | METCALF | ETL.7610.POLE.WOOD | 2024-04-15 | 2024-04-08 | 2024-04-08 | Past Due |  | 2024-07-08 | 2025-04-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB DURA BRIN | Rotten | Guy Pole-Wood | Replace | 35557805 | T2 DI MNTA VSTA-LS GS 9/184-GUY RPL POLE | 70Y
LC | 128549030 | 004/061 | T2 DI WEIMAR #1 4/61 RPL SPLW | SACTO | ETL.7560.INSL.NCER | 2024-04-15 | 2024-04-08 | 2024-09-15 | On-Time |  | 2024-07-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Splice-Wood | Replace | 46247493 | T2 DI WEIMAR #1 004/061 RPL SPLW | ICW
LC | 128549038 | :017/000 | T2 DI EAGLE RCK-REDBUD :017/000 RPR ANCW | WILLITS | ETL.1480.POLE.WOOD | 2024-04-15 | 2024-04-08 | 2025-03-10 | On-Time |  | 2025-04-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46308228 | T2 DI EAGLE RCK-REDBUD :017/000 RPR ANCW | ICW
LC | 128549053 | 002/040 | T2 DI WEIMAR #1 02/40 RPR GYWW | SACTO | ETL.7560.POLE.WOOD | 2024-04-15 | 2024-04-08 | 2024-09-15 | On-Time |  | 2025-04-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310842 | T2 DI WEIMAR #1 02/40 RPR GYWW | ICW
LC | 128555319 | 014/361 | T2 DI CTTNWD-BNTN #1 14/361 RPR GYWW | TABLEMTN | ETL.6640.POLE.NWOD | 2024-04-16 | 2024-04-08 | 2024-12-02 | On-Time |  | 2024-10-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46233794 | T2 DI COTTONWOOD-BTN #1 14/361 RPR GYWW | ICW
LC | 128777667 | 005/117 | T2 PLACER-DEL MAR 5/117 RPR STRW | SACTO | ETL.7800.POLE.WOOD | 2024-05-15 | 2024-04-08 | 2025-02-18 | On-Time |  | 2025-04-08 | 2025-04-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46328496 | T2 PLACER-DEL MAR 5/117 RPR STRW | ICW
LC | 130736920 | 014/057 | T3 PITTSBURG-SAN MATEO 014/057 RPR FOND | CONCORD | ETL.5463.TOWR | 2025-01-13 | 2024-10-08 | 2025-03-05 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46472282 | T3 PITTSBURG-SAN MATEO 014/057 RPR FOND | ICQ
LC | 130736927 | 014/058 | T3 PITTSBURG-SAN MATEO 014/058 RPR FOND | CONCORD | ETL.5463.TOWR | 2025-01-13 | 2024-10-08 | 2025-03-05 | On-Time |  | 2025-04-08 | 2025-04-08 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46472275 | T3 PITTSBURG-SAN MATEO 014/058 RPR FOND | ICQ
LC | 123335142 | 016/005 | T2NT DI FULTON-HOPLAND 16/5 RPR HRDW | LAKEVLLE | ETL.6890.POLE.WOOD | 2022-04-15 | 2022-04-09 | 2023-05-23 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 45571411 | T2 DI FULTON-HOPLAND 16/5 RPR HRDW | ICW
LC | 128494535 | 019/320 | T2 EI ARCO-POLONO PSS PP 19/320 RPR INSW | MIDWAY | ETL.8450.INSL.NCER | 2024-04-09 | 2024-04-09 | 2025-04-04 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46302511 | T2 EI ARCO-POLONO PSS PP 19/320 RPR INSW | ICW
LC | 128494854 | 026/215 | T2 EI CARBERRY SS-RND MTN 26/215 RMV VEG | TABLEMTN | ETL.5410.TOWR | 2024-04-09 | 2024-04-09 | 2025-02-05 | On-Time |  | 2025-04-09 | 2025-04-09 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128497026 | 050/002 | T2 EI FORT ROSS-GUALALA 050/002 RPR GYWW | LAKEVLLE | ETL.6980.POLE.NWOD | 2024-04-09 | 2024-04-09 | 2024-06-25 | On-Time |  | 2024-07-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46239183 | T2 EI FORT ROSS-GUALALA 050/002 RPR GYWW | ICW
LC | 128497128 | 049/001 | T2 EI FORT ROSS-GUALALA 049/001 RPL INSW | LAKEVLLE | ETL.6980.INSL.NCER | 2024-04-09 | 2024-04-09 | 2025-04-07 | On-Time |  | 2025-04-09 | 2025-04-09 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574245 | T2 EI FORT ROSS-GUALALA 049/001 RPL INSW | 93I
LC | 128497257 | 016/205 | T2 EI WST PNT-VLL SPRNGS 16/205 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-04-09 | 2024-04-09 | 2025-01-30 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327519 | T2 EI WST PNT-VLL SPRNGS 16/205 RPR GYWW | ICW
LC | 128497324 | 019/091A | T2 EI VACA-LAKEVILLE #1 19/91A RPL INSS | SACTO | ETL.5840.INSL.CERA | 2024-04-09 | 2024-04-09 | 2025-03-29 | On-Time |  | 2025-04-09 | 2025-04-09 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35608527 | T2 EI VACA-LAKEVILLE #1 19/91A RPL INSS | 93K
LC | 128497361 | 024/215 | T2 EI BRDGVLLE-CTTNWD 24/215L RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-09 | 2024-04-09 | 2025-02-08 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311107 | T2 EI BRDGVLLE-CTTNWD 24/215L RPR GYWW | ICW
LC | 128497362 | 024/215 | T2 EI BRDGVLLE-CTTNWD 24/215R RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-09 | 2024-04-09 | 2025-02-08 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311106 | T2 EI BRDGVLLE-CTTNWD 24/215R RPR GYWW | ICW
LC | 128497466 | :002/009 | T2 EI CARIBOU #2 :2/9 REFRAME | TABLEMTN | ETL.6280.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2025-03-14 | On-Time |  | 2025-04-09 | 2025-04-09 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35556122 | T2 EI CARIBOU #2 :002/009 REFRAME | 93E
LC | 128497626 | 009/096 | T2 EI PIT N 5-RND MTN N 2 9/96L RPR GYWW | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-09 | 2024-04-09 | 2025-03-08 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46454270 | T2 EI PIT N 5-RND MTN N 2 9/96L RPR GYWW | ICW
LC | 128497689 | 009/096 | T2 EI PIT N 5-RND MTN N 2 9/96R RPR GYWW | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-09 | 2024-04-09 | 2025-03-08 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46454274 | T2 EI PIT N 5-RND MTN N 2 9/96R RPR GYWW | ICW
LC | 128497814 | 014/308 | T2 WV KILARC-DESCHUTES 14/308 RPL STRW | TABLEMTN | ETL.7300.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2025-03-11 | On-Time |  | 2025-04-09 | 2025-04-09 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35573778 | T2 WV KILARC-DESCHUTES 14/308 RPL STRW | 70Y
LC | 128497854 | 016/084 | T2 EI RND MTN-TABL MTN #1 16/84 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-09 | 2024-04-09 | 2024-05-13 | On-Time |  | 2025-04-09 | 2025-04-09 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128497864 | 015/079 | T2 EI RND MTN-TABL MTN #1 15/79 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-04-09 | 2024-04-09 | 2025-01-22 | On-Time |  | 2025-04-09 | 2025-04-09 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306210 | T2 EI RND MTN-TABL MTN #1 15/79 RMV NEST | ICS
LC | 128497865 | 015/081 | T2 EI RND MTN-TABL MTN #1 15/81 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-09 | 2024-04-09 | 2024-09-01 | On-Time |  | 2025-04-09 | 2025-04-09 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128497866 | 016/082 | T2 EI RND MTN-TABL MTN #1 16/82 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-09 | 2024-04-09 | 2024-09-10 | On-Time |  | 2025-04-09 | 2025-04-09 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128497880 | 016/083 | T2 EI RND MTN-TBL MTN #1 16/083 RPR ANCT | TABLEMTN | ETL.6060.TOWR | 2024-04-09 | 2024-04-09 | 2025-02-18 | On-Time |  | 2025-04-09 | 2025-04-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46381984 | T2 EI RND MTN-TBL MTN #1 16/083 RPR ANCT | ICQ
LC | 128498020 | 015/330 | T2 WV KILARC-DESCHUTES 015/330 RPL STRW | TABLEMTN | ETL.7300.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2025-03-11 | On-Time |  | 2025-04-09 | 2025-04-09 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573781 | T2 WV KILARC-DESCHUTES 015/330 RPL STRW | 70Y
LC | 128498184 | 024/196 | T2 EI CARBRY SS RND MTN 24/196 RPR FOND | TABLEMTN | ETL.5410.TOWR | 2024-04-09 | 2024-04-09 | 2025-02-03 | On-Time |  | 2025-04-09 | 2025-04-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46354011 | T2 EI CARBRY SS RND MTN 24/196 RPR FOND | ICQ
LC | 128498386 | 004/100 | T2 EI COLEMAN-SOUTH 4/100 RPL STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2025-03-19 | On-Time |  | 2025-04-09 | 2025-04-09 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572513 | T2 EI COLEMAN-SOUTH 4/100 RPL STRW | 70Y
LC | 128498391 | 005/106 | T2 EI COLEMAN-SOUTH 5/106 RPR STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2025-03-25 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46389126 | T2 EI COLEMAN-SOUTH 5/106 RPR STRW | ICW
LC | 128498402 | 005/103 | T2 EI COLEMAN-SOUTH 5/103 RPR STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2025-03-25 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46389127 | T2 EI COLEMAN-SOUTH 5/103 RPR STRW | ICW
LC | 128498959 | ;005/014 | T2 CARIBOU #2 ;005/014 GO95 | TABLEMTN | ETL.6280.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2025-03-04 | On-Time |  | 2025-04-09 | 2025-04-09 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35556127 | T2 CARIBOU #2 ;005/014 GO95 | 93G
LC | 128499064 | 002/024 | T2 EI ELECTRA-BELLOTA 002/024 RPL INSS | VICTOR | ETL.4670.INSL.CERA | 2024-04-09 | 2024-04-09 | 2025-03-21 | On-Time |  | 2025-04-09 | 2025-04-09 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC REAR CLR ACCM COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593221 | T2 EI ELECTRA-BELLOTA 002/024 RPL INSS | 93K
LC | 128499083 | 063/011 | T2 ELK-GUALALA 063/011 RPR STRW | WILLITS | ETL.8410.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2025-03-03 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Structure-Wood | Repair | 46308229 | T2 ELK-GUALALA 063/011 RPR STRW | ICW
LC | 128499171 | 015/204 | T2 EI WST PNT-VLL SPRNGS 15/204 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-04-09 | 2024-04-09 | 2025-02-03 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46326959 | T2 EI WST PNT-VLL SPRNGS 15/204 RPR GYWW | ICW
LC | 128499232 | 008/183 | T2 EI COLEMAN-SOUTH 8/183 RPR GYWW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2024-05-09 | On-Time |  | 2024-10-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46229110 | T2 EI COLEMAN-SOUTH 8/183 RPR GYWW | ICW
LC | 128499390 | 083/424 | T2 EI MALIN-ROUND MTN #2 83/424 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-09 | 2024-04-09 | 2025-02-11 | On-Time |  | 2025-04-09 | 2025-04-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381374 | T2 EI MALIN-ROUND MTN #2 83/424 RPR GYWT | ICQ
LC | 128499484 | 069/499 | T2 BRDGVLLE-CTTNWD 69/499R COMPLETE | EUREKA | ETL.1110.POLE.STPS | 2024-04-09 | 2024-04-09 | 2025-04-07 | On-Time |  | 2025-04-09 | 2025-04-09 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Anchor-Wood | Replace | 35555556 | T2 WV BRDGVLLE-CTTNWD 69/499R RPL ANCW | 93E
LC | 128499498 | 069/499 | T2 WV BRDGVLLE-CTTNWD 69/499L RPL ANCW | EUREKA | ETL.1110.POLE.STPS | 2024-04-09 | 2024-04-09 | 2025-04-07 | On-Time |  | 2025-04-09 | 2025-04-09 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35555556 | T2 WV BRDGVLLE-CTTNWD 69/499R RPL ANCW | 93E
LC | 128499780 | 005/004 | T2 WV LAKEVILLE #1 05/04 INS DAMP | LAKEVLLE | ETL.7360.INSL.NCER | 2024-04-09 | 2024-04-09 | 2025-03-07 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46305927 | T2 WV LAKEVILLE #1 05/04 INS DMPW | ICW
LC | 128499823 | 009/014 | T2 EI CARIBOU-PLUMAS JCT 09/014 RPL POLE | TABLEMTN | ETL.6290.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2025-04-29 | Past Due |  | 2025-04-09 | 2025-04-09 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556130 | T2 EI CARIBOU-PLUMAS JCT 09/014 RPL POLE | 70Y
LC | 128499884 | 024/009 | T2 EI RIO DELL JCT-BRDGVLL 24/9 RPL INSW | EUREKA | ETL.7850.INSL.NCER | 2024-04-09 | 2024-04-09 | 2025-06-11 | Past Due |  | 2025-04-09 | 2025-04-09 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572966 | T2 EI RIO DELL JCT-BRDGVLL 24/9 RPL INSW | 93I
LC | 128499886 | 024/008 | T2 EI RIO DELL JCT-BRDGVLL 24/8 RPL INSW | EUREKA | ETL.7850.INSL.CERA | 2024-04-09 | 2024-04-09 | 2025-06-11 | Past Due |  | 2025-04-09 | 2025-04-09 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572965 | T2 EI RIO DELL JCT-BRDGVLL 24/8 RPL INSW | 93I
LC | 128499920 | 024/010 | T2 EI RIO DLL JCT-BRDGVLL 24/10 GO95 | EUREKA | ETL.7850.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2024-04-09 | Past Due |  | 2025-04-09 | 2025-04-09 | 401T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35572967 | T2 EI RIO DLL JCT-BRDGVLL 24/10 GO95 | 93G
LC | 128499993 | 008/179 | T2 EI COLEMAN-SOUTH 8/179 RPR GYWW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2024-05-09 | On-Time |  | 2024-10-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46229109 | T2 EI COLEMAN-SOUTH 8/179 RPR GYWW | ICW
LC | 128500017 | 008/086 | T2 EI PIT #5-RND MTN #2 8/86 RPL INSS | TABLEMTN | ETL.5430.INSL.NCER | 2024-04-09 | 2024-04-09 | 2025-03-07 | On-Time |  | 2025-04-09 | 2025-04-09 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35611092 | T2 EI PIT #5-RND MTN #2 8/86 RPL INSS | 93K
LC | 128500060 | 008/086 | T2 EI PIT #5-RND MTN #2 8/86R RMV STEP | TABLEMTN | ETL.5430.POLE.STPS | 2024-04-09 | 2024-04-09 | 2025-03-07 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46454275 | T2 EI PIT #5-RND MTN #2 8/86R RMV STEP | ICW
LC | 128500070 | 008/084 | T2 EI PIT #5-RND MTN #2 08/084L RPR GYWW | TABLEMTN | ETL.5430.POLE.STPS | 2024-04-09 | 2024-04-09 | 2025-03-03 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46454276 | T2 EI PIT #5-RND MTN #2 08/084L RPR GYWW | ICW
LC | 128500098 | 022/000 | T2 EI TRINITY-MAPLE CREEK 22/00 RPL ANCW | EUREKA | ETL.8170.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2025-03-21 | On-Time |  | 2025-04-09 | 2025-04-09 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572089 | T2 EI TRINITY-MAPLE CREEK 22/00 RPL ANCW | 93E
LC | 128500118 | 021/008 | T2 EI TRINITY-MAPLE CREEK 21/08 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-04-09 | 2024-04-09 | 2025-02-26 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345755 | T2 EI TRINITY-MAPLE CREEK 21/08 RPR GYWW | ICW
LC | 128500126 | 024/011 | T2 EI RO DELL JCT-BRDGVLL 24/11 RPL INSW | EUREKA | ETL.7850.INSL.NCER | 2024-04-09 | 2024-04-09 | 2025-06-11 | Past Due |  | 2025-04-09 | 2025-04-09 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572968 | T2 EI RO DELL JCT-BRDGVLL 24/11 RPL INSW | 93I
LC | 128500154 | 008/082 | T2 EI PIT #5-RND MTN #2 8/082L RMV STEP | TABLEMTN | ETL.5430.POLE.STPS | 2024-04-09 | 2024-04-09 | 2025-03-03 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46454277 | T2 EI PIT #5-RND MTN #2 8/082L RMV STEP | ICW
LC | 128500189 | 078/397 | T2 EI MALIN-ROUND MTN #2 78/397 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-09 | 2024-04-09 | 2025-02-10 | On-Time |  | 2025-04-09 | 2025-04-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381375 | T2 EI MALIN-ROUND MTN #2 78/397 RPR GYWT | ICQ
LC | 128500192 | 078/399 | T2 MALIN-ROUND MTN #2 78/399 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-04-09 | 2024-04-09 | 2024-04-09 | Past Due |  | 2025-04-09 | 2025-04-09 | 93Z | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716778 | T2 DI MLN RD MTN#2 RPL ANCT 10 TWRS | 93Z
LC | 128500210 | 078/396 | T2 EI MALIN-ROUND MTN #2 78/396 RPR ANCT | TABLEMTN | ETL.6020.TOWR | 2024-04-09 | 2024-04-09 | 2024-06-27 | On-Time |  | 2024-10-09 | 2025-04-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Tower | Repair | 46248632 | T2 EI MALIN-ROUND MTN #2 78/396 RPR ANCT | ICQ
LC | 128500217 | 016/087 | T2 EI RND MTN-TBL MTN #1 16/087 RPR ANCT | TABLEMTN | ETL.6060.TOWR | 2024-04-09 | 2024-04-09 | 2025-02-18 | On-Time |  | 2025-04-09 | 2025-04-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46381985 | T2 EI RND MTN-TBL MTN #1 16/087 RPR ANCT | ICQ
LC | 128500288 | 016/086 | T2 EI RND MTN-TABL MTN #1 16/86 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-04-09 | 2024-04-09 | 2025-01-22 | On-Time |  | 2025-04-09 | 2025-04-09 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306211 | T2 EI RND MTN-TABL MTN #1 16/86 RMV NEST | ICS
LC | 128500296 | 023/191 | T2 EI CARBRY SS-RND MTN 23/191 RPL INSS | TABLEMTN | ETL.5410.INSL | 2024-04-09 | 2024-04-09 | 2024-07-12 | On-Time |  | 2025-04-09 | 2025-04-09 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35559182 | T2 EI CARBRY SS-RND MTN 23/191 RPL INSS | 93K
LC | 128500525 | 044/002 | T2 EI FORT ROSS-GUALALA 44/002 RPR ANCW | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2025-02-07 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46305928 | T2 EI FORT ROSS-GUALALA 44/002 RPR ANCW | ICW
LC | 128509666 | 008/159 | T2 EI CARIBOU-WESTWOOD 08/159 CANCEL | TABLEMTN | ETL.6300.POLE.WOOD | 2024-04-10 | 2024-04-09 | 2025-03-11 | On-Time |  | 2025-04-09 | 2025-04-09 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35555479 | T2 CARIBOU-WESTWOOD 08/159 GO95 | 93G
LC | 128509832 | 008/158 | T2 EI CARIBOU-WESTWOOD 008/158 RPL INSW | TABLEMTN | ETL.6300.INSL | 2024-04-10 | 2024-04-09 | 2025-03-11 | On-Time |  | 2025-04-09 | 2025-04-09 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572147 | T2 EI CARIBOU-WESTWOOD 008/158 RPL INSW | 93I
LC | 128548956 | 040/242 | T2 DI INDIAN FLAT YSMT 40/242 RMV VEG | FRESNO | ETL.1112.POLE.NWOD | 2024-04-15 | 2024-04-09 | 2025-01-06 | On-Time |  | 2025-04-09 | 2025-04-09 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128555629 | 034/138 | T2 DIABLO-MIDWAY #3 34/138 TOUCH | PISMOBCH | ETL.5980.TOWR | 2024-04-16 | 2024-04-09 | 2025-04-07 | On-Time |  | 2024-10-09 | 2025-04-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476036 | T2 DI DIABLO-MDWY #3 34/138 TOUCH | ICQ
LC | 128567988 | 014/061 | T2 DI DIABLO-GATES #1 TOUCH | PISMOBCH | ETL.5960.TOWR | 2024-04-17 | 2024-04-09 | 2025-03-21 | On-Time |  | 2024-10-09 | 2025-04-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46477344 | T2 DI DIABLO-GATES #1 TOUCH | ICQ
LC | 128568294 | 032/129 | T2 DIABLO-GATES #3 32/129 TOUCH | PISMOBCH | ETL.5980.TOWR | 2024-04-17 | 2024-04-09 | 2024-04-09 | Past Due |  | 2024-10-09 | 2025-04-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46488931 | T2 DI DIABLO-GATES #3 32/129 TOUCH | ICQ
LC | 128694945 | 010/165 | T2 EI TEJON-LEBEC 010/165 RPL STRW | MIDWAY | ETL.9250.POLE.WOOD | 2024-05-01 | 2024-04-09 | 2025-02-01 | On-Time |  | 2025-04-09 | 2025-04-09 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573703 | T2 EI TEJON-LEBEC 010/165 RPL STRW | 70Y
LC | 128700432 | 010/166 | T2 EI TEJON-LEBEC 010/166 RPL STRW | MIDWAY | ETL.9250.POLE.WOOD | 2024-05-02 | 2024-04-09 | 2025-02-02 | On-Time |  | 2025-04-09 | 2025-04-09 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573703 | T2 EI TEJON-LEBEC 010/165 RPL STRW | 70Y
LC | 129658209 | 011/092AC | T3 EI TRNTY-CTTNWD 11/92AC RPR GYWW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-10-09 | 2024-10-09 | 2025-02-26 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46471149 | T3 EI TRNTY-CTTNWD 11/92AC RPR GYWW | ICW
LC | 129658245 | 011/092AB | T3 EI TRNTY-CTTNWD 11/92AB RPR GYWW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-10-09 | 2024-10-09 | 2025-02-26 | On-Time |  | 2025-04-09 | 2025-04-09 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46471148 | T3 EI TRNTY-CTTNWD 11/92AB RPR GYWW | ICW
LC | 129658280 | 011/092AA | T3 EI TRNTY-CTTNWD 11/92AA RPL MRKW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-10-09 | 2024-10-09 | 2025-02-26 | On-Time |  | 2025-10-09 | 2025-04-09 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3N PRTO FRAB NTDE | No Good/Out of Stdrd | Marker (i.e. signs)-Wood | Install | 46471147 | T3NT EI TRNTY-CTTNWD 11/92AA RPL MRKW | ICW
LC | 130737456 | 012/051 | T3NT PTSBRG-SN MTEO 012/051 RPR FOND | CONCORD | ETL.5463.TOWR | 2025-01-13 | 2024-10-09 | 2024-10-09 | Past Due |  | 2027-10-09 | 2025-04-09 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR3 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair
LC | 128501949 | 000/014 | T2 SMARTVILLE-NICOLAUS #1 0/14 RPR INSW | SACTO | ETL.7990.INSL.NCER | 2024-04-10 | 2024-04-10 | 2025-03-07 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310358 | T2 SMARTVILLE-NICOLAUS #1 0/14 RPR INSW | ICW
LC | 128509890 | 016/074 | T2 PITTSBURG-TESLA #1 16/74 TOUCH | CONCORD | ETL.5510.TOWR | 2024-04-10 | 2024-04-10 | 2025-04-23 | Past Due |  | 2024-10-10 | 2025-04-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46489042 | T2 PITTSBURG-TESLA #1 16/74 TOUCH | ICQ
LC | 128510109 | 013/056 | T2 TULUCAY-VACA 013/056 TOUCH | SACTO | ETL.5800.TOWR | 2024-04-10 | 2024-04-10 | 2025-03-06 | On-Time |  | 2024-10-10 | 2025-04-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46460822 | T2 TULUCAY-VACA 013/056 RPR STRT | ICQ
LC | 128510239 | 004/033 | T2 EI TGR CRK-VLLY SPRINGS 4/33 RPL INSS | VICTOR | ETL.5790.INSL.CERA | 2024-04-10 | 2024-04-10 | 2025-03-11 | On-Time |  | 2025-04-10 | 2025-04-10 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT CLR ACCM COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593059 | T2 EI TGR CRK-VLLY SPRINGS 4/33 RPL INSS | 93K
LC | 128510294 | 017/092 | T2 EI RND MTN-TBL MTN #2 17/92 RPR FOND | TABLEMTN | ETL.6070.TOWR | 2024-04-10 | 2024-04-10 | 2025-01-22 | On-Time |  | 2025-04-10 | 2025-04-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381986 | T2 EI RND MTN-TBL MTN #2 17/92 RPR FOND | ICQ
LC | 128510321 | 016/277 | T2 EI ARCO-POLNIO PSS PP 16/277 RPL STRW | MIDWAY | ETL.8450.POLE.WOOD | 2024-04-10 | 2024-04-10 | 2025-04-07 | On-Time |  | 2025-04-10 | 2025-04-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35554108 | T2 EI ARCO-POLNIO PSS PP 16/277 RPL STRW | 70Y
LC | 128510437 | 016/278 | T2 EI ARCO-POLONI PSS PP 16/278 RPL INSW | MIDWAY | ETL.8450.INSL.CERA | 2024-04-10 | 2024-04-10 | 2025-04-04 | On-Time |  | 2025-04-10 | 2025-04-10 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35554109 | T2 EI ARCO-POLONI PSS PP 16/278 RPL INSW | 93I
LC | 128510856 | 007/056 | T2 EI BUTT VALY-CARIBOU 7/56 RPR GYWW | TABLEMTN | ETL.1180.POLE.NWOD | 2024-04-10 | 2024-04-10 | 2025-03-27 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337321 | T2 EI BUTT VALY-CARIBOU 7/56 RPR GYWW | ICW
LC | 128511182 | :001/008 | T2 EI CARIBOU #2 (21KV) :001/8 INS DAMW | TABLEMTN | ETL.6280.INSL.CERA | 2024-04-10 | 2024-04-10 | 2025-03-14 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46333918 | T2 EI CARIBOU #2 (21KV) :001/8 INS DAMW | ICW
LC | 128511189 | 006/037 | T2 SOBRANTE-STNDRD OIL #2 06/038 COTTER | CONCORD | ETL.3790.INSL.CERA | 2024-04-10 | 2024-04-10 | 2025-03-26 | On-Time |  | 2025-04-10 | 2025-04-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46287297 | T2 STANISLAUS-MANTECA 06/038 COTTER | ICS
LC | 128511488 | 011/226 | T2 EI COLEMAN-SOUTH 011/226 RPR GYWW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-10 | 2024-04-10 | 2025-03-22 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46389128 | T2 EI COLEMAN-SOUTH 011/226 RPR GYWW | ICW
LC | 128511781 | 009/090 | T2 EI PIT #5-ROUND MTN#2 09/90R RPL STRW | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-10 | 2024-04-10 | 2025-03-05 | On-Time |  | 2025-04-10 | 2025-04-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35607188 | T2 EI PIT #5-ROUND MTN#2 09/90R RPL STRW | 70Y
LC | 128511783 | 009/090 | T2 EI PIT #5-ROUND MTN#2 09/90L RPL STRW | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-10 | 2024-04-10 | 2025-03-05 | On-Time |  | 2025-04-10 | 2025-04-10 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35607188 | T2 EI PIT #5-ROUND MTN#2 09/90R RPL STRW | 70Y
LC | 128511901 | 003/064 | T2 EI COLEMAN-COTTONWOOD 3/064 COMPLETE | TABLEMTN | ETL.6430.POLE.WOOD | 2024-04-10 | 2024-04-10 | 2025-03-28 | On-Time |  | 2025-04-10 | 2025-04-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572511 | T2 EI COLEMAN-COTTONWOOD 3/064 RPL STRW | 70Y
LC | 128512007 | 007/057 | T2 EI BUTTE VLY-CARIBOU 7/57C RPR GYWW | TABLEMTN | ETL.1180.POLE.STPS | 2024-04-10 | 2024-04-10 | 2024-06-03 | On-Time |  | 2024-07-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46255187 | T2 EI BUTTE VLY-CARIBOU 7/57C RPR GYWW | ICW
LC | 128512016 | 000/004 | T2 EI CARIBOU-WESTWOOD 000/004 RPR GYWW | TABLEMTN | ETL.6300.POLE.NWOD | 2024-04-10 | 2024-04-10 | 2024-07-10 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46233792 | T2 EI CARIBOU-WESTWOOD 000/004 RPR GYWW | ICW
LC | 128512075 | 002/016 | T2 EI STNSLS-MNTCA #2 2/16 COTTER | VICTOR | ETL.3820.INSL.CERA | 2024-04-10 | 2024-04-10 | 2025-03-06 | On-Time |  | 2025-04-10 | 2025-04-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300275 | T2 EI STNSLS-MNTCA #2 2/16 COTTER | ICS
LC | 128512432 | 012/087 | T2 MORAGA-LKWD 12/87 CANCEL | CONCORD | ETL.3741.INSL | 2024-04-10 | 2024-04-10 | 2024-04-10 | Past Due |  | 2025-04-10 | 2025-04-10 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575053 | T2 EI MORAGA-LKWD RPL INSS IN 3 TWRS. | 93K
LC | 128512555 | 005/036 | T2 PITTSBURG-CLAYTON #1 5/36 RPL INSS | CONCORD | ETL.3280.INSL | 2024-04-10 | 2024-04-10 | 2024-04-10 | Past Due |  | 2025-04-10 | 2025-04-10 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575052 | T2 EI PITTSBURG-CLAYTON #1 5/36 RPL INSS | 93K
LC | 128512556 | 005/036 | T2 PITTSBURG-CLAYTON #1 5/36 HANGER | CONCORD | ETL.3280.INSL | 2024-04-10 | 2024-04-10 | 2024-04-10 | Past Due |  | 2025-04-10 | 2025-04-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46287290 | T2 EI PITTSBURG-CLAYTON #1 5/36 HANGER | ICQ
LC | 128514989 | 008/088B | T2 EI PIT#5-RND MTN#2 8/88B RPR GYWW | TABLEMTN | ETL.5430.POLE.NWOD | 2024-04-10 | 2024-04-10 | 2024-05-31 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46236145 | T2 EI PIT#5-RND MTN#2 8/88B RPR GYWW | ICW
LC | 128515014 | 008/088A | T2 EI PIT#5-RND MTN#2 8/88A RMV VEG | TABLEMTN | ETL.5430.POLE.NWOD | 2024-04-10 | 2024-04-10 | 2025-02-05 | On-Time |  | 2025-04-10 | 2025-04-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128518829 | 025/001 | T2 RIO DLL JCT-BRDGVLE 25/1 RPL STRW | EUREKA | ETL.7850.POLE.WOOD | 2024-04-10 | 2024-04-10 | 2025-06-10 | Past Due |  | 2025-04-10 | 2025-04-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35573016 | T2 EI RIO DLL JCT-BRDGVLE 25/1 RPL STRW | 70Y
LC | 128518845 | 025/003 | T2 RIO DLL JCT-BRDGVLE 25/3 RPR STRW | EUREKA | ETL.7850.POLE.WOOD | 2024-04-10 | 2024-04-10 | 2024-04-10 | Past Due |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46329200 | T2 EI RIO DLL JCT-BRDGVLE 25/3 RPR STRW | ICW
LC | 128518847 | 025/009 | T2 EI RIO DLL JCT-BRDGVLE 25/9 RPR STRW | EUREKA | ETL.7850.POLE.WOOD | 2024-04-10 | 2024-04-10 | 2025-04-02 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46345756 | T2 EI RIO DLL JCT-BRDGVLE 25/9 RPR STRW | ICW
LC | 128518849 | 025/004 | T2 EI RIO DLL JCT-BRDGVLE 25/4 RPL INSW | EUREKA | ETL.7850.INSL.NCER | 2024-04-10 | 2024-04-10 | 2025-06-12 | Past Due |  | 2025-04-10 | 2025-04-10 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573021 | T2 EI RIO DLL JCT-BRDGVLE 25/4 RPL INSW | 93I
LC | 128518853 | 025/000 | T2 RIO DLL JCT-BRDGVLE 25/0 RPL INSW | EUREKA | ETL.7850.INSL.CERA | 2024-04-10 | 2024-04-10 | 2025-06-10 | Past Due |  | 2025-04-10 | 2025-04-10 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573014 | T2 EI RIO DLL JCT-BRDGVLE 25/0 RPL INSW | 93I
LC | 128518860 | 025/002 | T2 EI RIO DLL JCT-BRGVLE 25/2 ANTI SPLIT | EUREKA | ETL.7850.POLE.WOOD | 2024-04-10 | 2024-04-10 | 2025-06-12 | Past Due |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46328494 | T2 EI RIO DLL JCT-BRGVLE 25/2 ANTI SPLIT | ICW
LC | 128518874 | 85 | T2 DI BURNS-LONE STAR #2 5/115 RPR SWTC | MOSSLNDG | ETL.6240.SWIT | 2024-04-10 | 2024-04-10 | 2025-03-08 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Switch-Wood | Repair | 46391235 | T2 DI BURNS-LONE STAR #2 5/115 RPR SWTC | ICW
LC | 128519070 | 004/037 | T2 EI TGR CRK-VLLY SPRNGS 4/37 RPL INSS | VICTOR | ETL.5790.INSL.CERA | 2024-04-10 | 2024-04-10 | 2025-03-11 | On-Time |  | 2024-10-10 | 2025-04-10 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593059 | T2 EI TGR CRK-VLLY SPRINGS 4/33 RPL INSS | 93K
LC | 128519509 | 008/004 | T2 LAYTONVILLE-WILLITS 8/4 INS DMPW | WILLITS | ETL.8360.INSL.NCER | 2024-04-10 | 2024-04-10 | 2024-04-10 | Past Due |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46414824 | T2 WV LAYTONVILLE-WILLITS 8/4 INS DMPW | ICW
LC | 128519634 | 011/084 | T2 EI MORAGA-LAKEWOOD 11/084 RPR FOND | CONCORD | ETL.3741.TOWR | 2024-04-10 | 2024-04-10 | 2025-01-17 | On-Time |  | 2025-04-10 | 2025-04-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46287343 | T2 EI MORAGA-LAKEWOOD 11/084 RPR FOND | ICQ
LC | 128519669 | 034/279 | T2 EI BRIDGEVILLE-CTTNWD 34/279 RPL GRWW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-10 | 2024-04-10 | 2025-03-23 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46311105 | T2 EI BRIDGEVILLE-CTTNWD 34/279 RPL GRND | ICW
LC | 128519796 | 074/376 | T2 EI MALIN-RND MTN #2 74/376 UNBURY | TABLEMTN | ETL.6020.TOWR | 2024-04-10 | 2024-04-10 | 2025-02-24 | On-Time |  | 2025-04-10 | 2025-04-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381376 | T2 EI MALIN-RND MTN #2 74/376 UNBURY | ICQ
LC | 128519798 | 074/377 | T2 EI MALIN-RND MTN #2 74/377 RPR ANCT | TABLEMTN | ETL.6020.TOWR | 2024-04-10 | 2024-04-10 | 2024-06-27 | On-Time |  | 2024-10-10 | 2025-04-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Tower | Repair | 46257551 | T2 EI MALIN-RND MTN #2 74/377 RPR ANCT | ICQ
LC | 128519838 | 075/380B | T2 EI MALIN-RND MTN #2 75/380B RPR FOND | TABLEMTN | ETL.6020.TOWR | 2024-04-10 | 2024-04-10 | 2025-02-24 | On-Time |  | 2025-04-10 | 2025-04-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381378 | T2 EI MALIN-RND MTN #2 75/380B RPR FOND | ICQ
LC | 128519847 | 077/394 | T2 EI MALIN-ROUND MTN#2 77/394 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-10 | 2024-04-10 | 2025-02-24 | On-Time |  | 2025-04-10 | 2025-04-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381379 | T2 EI MALIN-ROUND MTN#2 77/394 RPR GYWT | ICQ
LC | 128519990 | 017/298 | T2NT EI ARCO-PLNI PSS PP 17/298 RPR CRSW | MIDWAY | ETL.8450.POLE.WOOD | 2024-04-10 | 2024-04-10 | 2025-04-04 | On-Time |  | 2027-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46302512 | T2NT EI ARCO-PLNI PSS PP 17/298 RPR CRSW | ICW
LC | 128520000 | 018/303 | T2NT EI ARCO-POLN PSS PP 18/303 RPR CRSW | MIDWAY | ETL.8450.POLE.WOOD | 2024-04-10 | 2024-04-10 | 2025-04-04 | On-Time |  | 2027-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46302513 | T2NT EI ARCO-POLN PSS PP 18/303 RPR CRSW | ICW
LC | 128520002 | 029/251 | T2 EI RND MTN-CTTNWD #2 29/251 RPR OPGW | TABLEMTN | ETL.5640.TOWR | 2024-04-10 | 2024-04-10 | 2025-03-04 | On-Time |  | 2025-04-10 | 2025-04-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46416190 | T2 EI RND MTN-CTTNWD #2 29/251 RPR OPGW | ICS
LC | 128520051 | 028/246 | T2 EI RND MTN-CTTNWD #2 28/246 RMV VEG | TABLEMTN | ETL.5640.TOWR | 2024-04-10 | 2024-04-10 | 2024-12-04 | On-Time |  | 2025-04-10 | 2025-04-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128520496 | 009/053 | T2 PARKWAY-MORAGA 009/053 TOUCH | CONCORD | ETL.5930.TOWR | 2024-04-11 | 2024-04-10 | 2025-05-08 | Past Due |  | 2024-10-10 | 2025-04-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46489041 | T2 PARKWAY-MORAGA 009/053 TOUCH | ICQ
LC | 128528332 | 005/007 | T2 EI CHOWCHLA-KRCKHFF 5/7 RPL STRW | FRESNO | ETL.1250.POLE.WOOD | 2024-04-11 | 2024-04-10 | 2025-03-26 | On-Time |  | 2025-04-10 | 2025-04-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP REMT ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35554462 | T2 EI CHOWCHLA-KRCKHFF 5/7 RPL STRW | 70Y
LC | 128528357 | 005/008 | T2 EI CHOWCHLLA-KRCKHFF 05/08 RPR STRW | FRESNO | ETL.1250.POLE.WOOD | 2024-04-11 | 2024-04-10 | 2025-03-26 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46298276 | T2 EI CHOWCHLLA-KRCKHFF 05/08 RPR STRW | ICW
LC | 128533336 | 005/098 | T2 EI SSQC-SNT YNZ SW STA 5/98 RPL POLE | PISMOBCH | ETL.3700.POLE.WOOD | 2024-04-11 | 2024-04-10 | 2025-02-10 | On-Time |  | 2025-04-10 | 2025-04-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573770 | T2 EI SSQC-SNT YNZ SW STA 5/98 RPL POLE | 70Y
LC | 128533371 | 005/099 | T2 EI SSQC-SNT YNEZ SW STA 5/99 RPL POLE | PISMOBCH | ETL.3700.POLE.WOOD | 2024-04-11 | 2024-04-10 | 2025-02-10 | On-Time |  | 2025-04-10 | 2025-04-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573771 | T2 EI SSQC-SNT YNEZ SW STA 5/99 RPL POLE | 70Y
LC | 128534900 | 014/001 | T2 DI MENDOCINO-WFTB 14/1 RPL INSW | WILLITS | ETL.7550.INSL.NCER | 2024-04-11 | 2024-04-10 | 2025-04-08 | On-Time |  | 2025-04-10 | 2025-04-10 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574196 | T2 DI MENDOCINO-WFTB 14/1 RPL INSW | 93I
LC | 128534945 | 004/042 | T2 DI MNTA VSTA BRNS 04/042C RPL ANCW | MOSSLNDG | ETL.7590.POLE.STPS | 2024-04-11 | 2024-04-10 | 2025-04-05 | On-Time |  | 2025-04-10 | 2025-04-10 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573804 | T2 DI MNTA VSTA BRNS 04/042 RPL ANCW | 93E
LC | 128535010 | 004/042 | T2 DI MNTA VSTA BRNS 04/042 RMV VEG | MOSSLNDG | ETL.7590.POLE.STPS | 2024-04-11 | 2024-04-10 | 2025-03-20 | On-Time |  | 2025-04-10 | 2025-04-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128535034 | 020/002 | T2 DI MENDOCINO-WFTB 20/2 RPR IBWW | WILLITS | ETL.7550.INSL.NCER | 2024-04-11 | 2024-04-10 | 2025-04-10 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46308238 | T2 DI MENDOCINO-WFTB 20/2 RPR IBWW | ICW
LC | 128535430 | 013/016 | T2 DI MENDOCINO-WFTB 13/16 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-11 | 2024-04-10 | 2025-02-07 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCH COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46308231 | T2 DI MENDOCINO-WFTB 13/16 RPR GYWW | ICW
LC | 128535723 | A000/018 | T2 DI VALLEY SPNGS #1 A0/18 RPR JUMW | VICTOR | ETL.8210.INSL.NCER | 2024-04-11 | 2024-04-10 | 2024-07-09 | On-Time |  | 2024-07-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46232572 | T2 DI VALLEY SPNGS #1 A00/18 RPR JUMW | ICW
LC | 128535762 | 85 | T2 DI MNDCNO-WLTS-FRT BRG :1/2 RPR JUMW | WILLITS | ETL.7550.SWIT | 2024-04-11 | 2024-04-10 | 2025-01-21 | On-Time |  | 2024-07-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46233093 | T2 DI MNDCNO-WLTS-FT BRG :1/002 RPR SWTC | ICW
LC | 128555657 | 036/204 | T2 DI INDIAN FLAT-YSMT 36/204 RPR FOND | FRESNO | ETL.1112.POLE.NWOD | 2024-04-16 | 2024-04-10 | 2024-06-11 | On-Time |  | 2024-10-10 | 2025-04-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46240376 | T2 DI INDIAN FLAT-YSMT 36/204 RPR FOND | ICQ
LC | 128555738 | 004/043 | T2 DI MONTA VISTA-BURNS 4/43 RMV VEG | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-04-16 | 2024-04-10 | 2025-03-20 | On-Time |  | 2025-04-10 | 2025-04-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128555841 | 004/044 | T2 DI MONTA VISTA-BURNS 4/44 RMV VEG | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-04-16 | 2024-04-10 | 2025-03-20 | On-Time |  | 2025-04-10 | 2025-04-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128555844 | 17 | T2 DI PERMANENTE #2 TAP 0/2 RPR SWTC | METCALF | ETL.7622.SWIT | 2024-04-16 | 2024-04-10 | 2025-01-21 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Switch-Wood | Repair | 46286866 | T2 DI PERMANENTE #2 TAP 0/2 RPR SWTC | ICW
LC | 128555847 | :000/012 | T2 DI MNDCN-WLTS-FRT BRG :0/12 TOUCH | WILLITS | ETL.7550.POLE.NWOD | 2024-04-16 | 2024-04-10 | 2025-05-02 | Past Due |  | 2024-10-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAR NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46507555 | T2 DI MNDCN-WLTS-FRT BRG :0/12 TOUCH | ICW
LC | 128555950 | 45 | T2 DI BURNS-LONE STAR #1 5/67 RPR SWTC | MOSSLNDG | ETL.6230.SWIT | 2024-04-16 | 2024-04-10 | 2025-03-07 | On-Time |  | 2025-04-10 | 2025-04-10 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | Out of Adjustment | Switch | Repair | 46391279 | T2 DI BURNS-LONE STAR #1 5/67 RPR SWTC | ICE
LC | 128567757 | 005/002 | T2 DI MNDCNO-PHLO JCT-HPLND 5/2 RPR GYWT | WILLITS | ETL.7520.POLE.NWOD | 2024-04-17 | 2024-04-10 | 2025-03-06 | On-Time |  | 2025-04-10 | 2025-04-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46290144 | T2 DI MNDCNO-PHLO JCT-HPLND 5/2 RPR GYWT | ICQ
LC | 128567941 | 020/001 | T2 MNDO-WLITS-FRT BRG-20/01 RPL STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-17 | 2024-04-10 | 2024-04-10 | Past Due |  | 2025-04-10 | 2025-04-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574300 | T2 DI MNDO-WLITS-FRT BRG-20/01 RPL STRW | 70Y
LC | 128567946 | 040/241 | T2 DI INDN FLT-YSMTE 40/241 RMV VEG | FRESNO | ETL.1112.POLE.NWOD | 2024-04-17 | 2024-04-10 | 2025-01-06 | On-Time |  | 2025-04-10 | 2025-04-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128568191 | 016/105 | T2 DI METCALF-GREEN VLLY 16/105 RPR GYWW | MOSSLNDG | ETL.2540.POLE.STPS | 2024-04-17 | 2024-04-10 | 2025-02-25 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391280 | T2 DI METCALF-GREEN VLLY 16/105 RPR GYWW | ICW
LC | 128577605 | 003/032 | T2 DI MONTA VISTA-BURNS 03/32 RPR GYWW | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-04-18 | 2024-04-10 | 2025-03-25 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391282 | T2 DI MONTA VISTA-BURNS 03/32 RPR GYWW | ICW
LC | 128577735 | 004/037 | T2 DI MONTA VISTA-BURNS 04/37L RPR GYWW | MOSSLNDG | ETL.7590.POLE.STPS | 2024-04-18 | 2024-04-10 | 2025-03-27 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391283 | T2 DI MONTA VISTA-BURNS 04/37L RPR GYWW | ICW
LC | 128577755 | 001/005 | T2 DI MNDCNO-WLTS-FRT BRG 1/5 RPL STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-18 | 2024-04-10 | 2025-04-02 | On-Time |  | 2025-04-10 | 2025-04-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574190 | T2 DI MNDCNO-WLTS-FRT BRG 1/5 RPL STRW | 70Y
LC | 128577882 | 005/107 | T2 DI BURNS-LONE STAR#2 5 5/107 RMV VEG | MOSSLNDG | ETL.6240.POLE.STPS | 2024-04-18 | 2024-04-10 | 2024-10-16 | On-Time |  | 2024-10-10 | 2025-04-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128578176 | 003/029 | T2 DI MONTA VISTA-BURNS 3/29 RPR JUMW | MOSSLNDG | ETL.7590.INSL.NCER | 2024-04-18 | 2024-04-10 | 2024-07-30 | On-Time |  | 2024-07-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46266158 | T2 DI MONTA VISTA-BURNS 03/29 RPR JMPW | ICW
LC | 128578206 | 014/013 | T2 DI MNDO-WLTS-FRT BRG 14/13 RPR ANCW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-18 | 2024-04-10 | 2025-03-31 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46308233 | T2 DI MNDO-WLTS-FRT BRG 14/13 RPR ANCW | ICW
LC | 128578208 | 005/108 | T2 DI BURNS-LONE STAR#2 05/108 RMV VEG | MOSSLNDG | ETL.6240.POLE.NWOD | 2024-04-18 | 2024-04-10 | 2024-10-01 | On-Time |  | 2024-10-10 | 2025-04-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW ACCL CNCL OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128578209 | 005/108 | T2 DI BRNS-LONE STAR#2 5/108 INSPCT STR | MOSSLNDG | ETL.6240.POLE.NWOD | 2024-04-18 | 2024-04-10 | 2024-09-17 | On-Time |  | 2024-10-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46236122 | T2 DI BRNS-LONE STAR#2 5/108 INSPCT STR | ICW
LC | 128578280 | 005/108 | T2 DI BRNS-LONE STAR#2 05/108 RPR GYWW | MOSSLNDG | ETL.6240.POLE.NWOD | 2024-04-18 | 2024-04-10 | 2025-04-05 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391227 | T2 DI BRNS-LONE STAR#2 05/108 RPR GYWW | ICW
LC | 128578286 | 005/108 | T2 DI BRNS-LONE STAR#2 05/108 RPR JMPW | MOSSLNDG | ETL.6240.INSL.NCER | 2024-04-18 | 2024-04-10 | 2024-09-17 | On-Time |  | 2024-07-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH RTNR TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46252187 | T2 DI BRNS-LONE STAR#2 05/108 RPR JMPW | ICW
LC | 128578401 | 005/045 | T2 DI MONTA VISTA-BURNS 5/45R RPR GYWW | MOSSLNDG | ETL.7590.POLE.STPS | 2024-04-18 | 2024-04-10 | 2025-03-24 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391284 | T2 DI MONTA VISTA-BURNS 5/45R RPR GYWW | ICW
LC | 128578522 | 003/036 | T2 DI MONTA VISTA-BURNS 03/36 RMV VEG | MOSSLNDG | ETL.7590.POLE.WDPS | 2024-04-18 | 2024-04-10 | 2024-05-08 | On-Time |  | 2024-10-10 | 2025-04-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128578526 | 003/036 | T2 DI MONTA VISTA-BURNS 3/36C RPL HRDW | MOSSLNDG | ETL.7590.POLE.WDPS | 2024-04-18 | 2024-04-10 | 2025-03-25 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46391285 | T2 DI MONTA VISTA-BURNS 3/36C RPL HRDW | ICW
LC | 128578527 | 003/036 | T2 DI MONTA VISTA-BURNS 03/36R COMPLETE | MOSSLNDG | ETL.7590.POLE.WDPS | 2024-04-18 | 2024-04-10 | 2025-03-25 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391286 | T2 DI MONTA VISTA-BURNS 03/36R RPR GYWW | ICW
LC | 128578528 | 003/036 | T2 DI MONTA VISTA-BURNS 3/36 COTTER | MOSSLNDG | ETL.7590.INSL.CERA | 2024-04-18 | 2024-04-10 | 2025-03-25 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46391287 | T2 DI MONTA VISTA-BURNS 3/36 COTTER | ICW
LC | 128611020 | 016/105 | T2 DI METCALF-GREEN VLLY 16/105 RPR GYWW | MOSSLNDG | ETL.2540.POLE.STPS | 2024-04-22 | 2024-04-10 | 2025-02-25 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391290 | T2 DI METCALF-GREEN VLLY 16/105 RPR GYWW | ICW
LC | 128611021 | 016/105 | T2 DI METCALF-GREEN VLLY 16/105 RPR GYWW | MOSSLNDG | ETL.2540.POLE.STPS | 2024-04-22 | 2024-04-10 | 2025-02-25 | On-Time |  | 2025-04-10 | 2025-04-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391291 | T2 DI METCALF-GREEN VLLY 16/105 RPR GYWW | ICW
LC | 130737417 | 013/052 | T3 PITTSBURG-SAN MATEO 013/052 RPR FOND | CONCORD | ETL.5463.TOWR | 2025-01-13 | 2024-10-10 | 2025-04-10 | On-Time |  | 2025-04-10 | 2025-04-10 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46463767 | T3 PITTSBURG-SAN MATEO 013/052 RPR FOND | ICQ
LC | 130745894 | 013/052 | T3 PITTSBURG-SAN MATEO 13/052 RPR STRT | CONCORD | ETL.5463.TOWR | 2025-01-15 | 2024-10-10 | 2025-04-08 | On-Time |  | 2025-04-10 | 2025-04-10 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46463768 | T3 PITTSBURG-SAN MATEO 13/052 RPR STRT | ICQ
LC | 123296827 | 042/192 | T2NT EI RND MTN-TBL MTN #2 42/192 BNT SL | TABLEMTN | ETL.6070.TOWR | 2022-04-11 | 2022-04-11 | 2023-09-12 | On-Time |  | 2025-04-11 | 2025-04-11 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647707 | T2 EI RND MTN-TBL MTN #2 42/192 BNT STL | ICQ
LC | 123298445 | 019/100 | T2NT EI RND MTN-TB MTN #2 19/100 BNT STL | TABLEMTN | ETL.6070.TOWR | 2022-04-11 | 2022-04-11 | 2023-07-29 | On-Time |  | 2025-04-11 | 2025-04-11 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647418 | T2 EI RND MTN-TBLE MTN #2 19/100 BNT STL | ICQ
LC | 123300071 | 019/099 | T2NT EI RND MTN-TBL MTN #1 19/99 BNT STL | TABLEMTN | ETL.6060.TOWR | 2022-04-11 | 2022-04-11 | 2023-08-21 | On-Time |  | 2025-04-11 | 2025-04-11 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644439 | T2 EI RND MTN-TBL MTN #1 19/99 BNT STEEL | ICQ
LC | 123353099 | 020/125 | T2NT DI MSS LNDG-DLMNT#1 20/125 RPR FOND | MOSSLNDG | ETL.2830.TOWR | 2022-04-18 | 2022-04-11 | 2023-04-04 | On-Time |  | 2023-04-11 | 2025-04-11 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45650137 | T2NT DI MSS LNDG-DLMNT#1 20/125 RPR FOND | ICQ
LC | 123359969 | 001/029 | T3NT DI KESWICK-TRINITY 01/29 RPR GYWW | TABLEMTN | ETL.7270.POLE.WOOD | 2022-04-18 | 2022-04-11 | 2023-05-23 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45729322 | T3 DI KESWICK-TRINITY 01/29 RPR GYWW | ICW
LC | 123440319 | 014/128 | T3NT DI DRM RIO OSO #1 14/128 RPR SPLS | SACTO | ETL.1420.INSL.NCER | 2022-04-27 | 2022-04-11 | 2023-12-07 | On-Time |  | 2025-04-11 | 2025-04-11 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR3N PRTO AIR NTDE | No Good/Out of Stdrd | Splice-Steel | Repair | 45657030 | T3 DI DRM RIO OSO #1 14/128 RPL SPLS | ICS
LC | 123440553 | :009/051 | T3NT DI EGLE RCK-RDBD :009/051 RPR STRT | WILLITS | ETL.1480.TOWR | 2022-04-27 | 2022-04-11 | 2023-08-10 | On-Time |  | 2025-04-11 | 2025-04-11 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644890 | T3 DI EAGLE RCK-RDBD :009/051 RPR STRT | ICQ
LC | 127255240 | 003/026 | T2 PIT #1-COTTONWOOD 3/26 RPR INSS | TABLEMTN | ETL.5390.INSL.NCER | 2023-10-11 | 2023-10-11 | 2024-11-05 | On-Time |  | 2025-04-11 | 2025-04-11 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB XMPT TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46088244 | T2 PIT #1-COTTONWOOD 3/26 RPR INSS | ICS
LC | 128525783 | 001/008 | T2 EI STNLS-MLNS SS-RVBK 1/8 RPR INSS | VICTOR | ETL.3840.INSL.NCER | 2024-04-11 | 2024-04-11 | 2025-03-15 | On-Time |  | 2025-04-11 | 2025-04-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46327610 | T2 EI STNLS-MLNS SS-RVBK 1/8 RPR INSS | ICS
LC | 128525984 | 020/163 | T2NT EI CRBRY SS-RND MTN 20/163 RPR STRT | TABLEMTN | ETL.5410.TOWR | 2024-04-11 | 2024-04-11 | 2025-03-13 | On-Time |  | 2027-04-11 | 2025-04-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354012 | T2NT EI CRBRY SS-RND MTN 20/163 RPR STRT | ICQ
LC | 128526046 | 011/083 | T2 EI MORAGA-LAKEWOOD 11/083 RPR STRT | CONCORD | ETL.3741.TOWR | 2024-04-11 | 2024-04-11 | 2025-03-25 | On-Time |  | 2025-04-11 | 2025-04-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287347 | T2 EI MORAGA-LAKEWOOD 11/083 RPR STRT | ICQ
LC | 128526479 | 001/006 | T2 EI STNLS-MLNS SS-RVBK 1/6 RPR INSS | VICTOR | ETL.3840.INSL.CERA | 2024-04-11 | 2024-04-11 | 2025-03-15 | On-Time |  | 2025-04-11 | 2025-04-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46327500 | T2 EI STNLS-MLNS SS-RVBK 1/6 RPR INSS | ICS
LC | 128528059 | 000/017 | T2 EI CARIBOU-WESTWOOD 00/017R RPL PL | TABLEMTN | ETL.6300.POLE.WDPS | 2024-04-11 | 2024-04-11 | 2025-03-06 | On-Time |  | 2025-04-11 | 2025-04-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572138 | T2 EI CARIBOU-WESTWOOD 00/017R RPL PL | 70Y
LC | 128528060 | 000/017 | T2 EI CARIBOU-WESTWOOD 0/017L RPL PL | TABLEMTN | ETL.6300.POLE.WDPS | 2024-04-11 | 2024-04-11 | 2025-03-06 | On-Time |  | 2025-04-11 | 2025-04-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572138 | T2 EI CARIBOU-WESTWOOD 00/017R RPL PL | 70Y
LC | 128528894 | 005/123 | T2 EI COLEMAN-SOUTH 005/123 RPR POLE | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-11 | 2024-04-11 | 2025-03-22 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46389131 | T2 EI COLEMAN-SOUTH 005/123 RPR POLE | ICW
LC | 128528896 | 006/125 | T2 EI COLEMAN-SOUTH 006/125 RPR POLE | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-11 | 2024-04-11 | 2025-03-22 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46389132 | T2 EI COLEMAN-SOUTH 006/125 RPR POLE | ICW
LC | 128528966 | 000/017 | T2 EI CARIBOU-WESTWOOD 00/017C RPL PL | TABLEMTN | ETL.6300.POLE.WDPS | 2024-04-11 | 2024-04-11 | 2025-03-06 | On-Time |  | 2025-04-11 | 2025-04-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572138 | T2 EI CARIBOU-WESTWOOD 00/017R RPL PL | 70Y
LC | 128529820 | 009/188 | T2 CARIBOU-WESTWOOD 09/188 RPR GYWW | TABLEMTN | ETL.6300.POLE.WOOD | 2024-04-11 | 2024-04-11 | 2024-07-17 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46237048 | T2 CARIBOU-WESTWOOD 09/188 RPR GYWW | ICW
LC | 128531889 | 007/018 | T2 EI CARIBOU-PLUMAS JCT 07/018 RPL INSW | TABLEMTN | ETL.6290.INSL.NCER | 2024-04-11 | 2024-04-11 | 2025-04-29 | Past Due |  | 2025-04-11 | 2025-04-11 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35556129 | T2 EI CARIBOU-PLUMAS JCT 07/018 RPL INSW | 93I
LC | 128531973 | 000/021 | T2 EI CARIBOU-WESTWOOD 0/21C RPR GYWW | TABLEMTN | ETL.6300.POLE.STPS | 2024-04-11 | 2024-04-11 | 2024-07-10 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46239930 | T2 EI CARIBOU-WESTWOOD 0/21C RPR GYWW | ICW
LC | 128531974 | 000/021 | T2 EI CARIBOU-WESTWOOD 0/21 RPR INSW | TABLEMTN | ETL.6300.INSL.NCER | 2024-04-11 | 2024-04-11 | 2025-03-05 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46337291 | T2 EI CARIBOU-WESTWOOD 0/21 RPR INSW | ICW
LC | 128531982 | 000/021 | T2 EI CARIBOU-WESTWOOD 0/21L RPR GYWW | TABLEMTN | ETL.6300.POLE.STPS | 2024-04-11 | 2024-04-11 | 2024-07-10 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46239929 | T2 EI CARIBOU-WESTWOOD 0/21L RPR GYWW | ICW
LC | 128532026 | 000/002 | T2 EI STNSLS-MNTCA #2 0/2 RMV VEG | VICTOR | ETL.3820.TOWR | 2024-04-11 | 2024-04-11 | 2025-01-13 | On-Time |  | 2025-04-11 | 2025-04-11 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128532136 | 000/021 | T2 EI CARIBOU-WESTWD 0/21R RPR GYWW | TABLEMTN | ETL.6300.POLE.STPS | 2024-04-11 | 2024-04-11 | 2024-07-10 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46239928 | T2 EI CARIBOU-WESTWD 00/21R RPR GYWW | ICW
LC | 128532251 | 012/070 | T2 MARTINEZ-SOBRANTE 12/70 RPL INSS | CONCORD | ETL.2270.INSL.CERA | 2024-04-11 | 2024-04-11 | 2025-03-28 | On-Time |  | 2025-04-11 | 2025-04-11 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP PATR COMC REMT NOAC REAR SWRK SPCR CLR ACCL COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575054 | T2 MARTINEZ-SOBRANTE 12/70 RPL INSS | 93K
LC | 128532258 | 012/121 | T2 EI ARCO-CHOLAME 012/121 INS DMPW | MIDWAY | ETL.8440.INSL | 2024-04-11 | 2024-04-11 | 2025-01-08 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | Missing | Damper-Wood | Install | 46302515 | T2 EI ARCO-CHOLAME 012/121 INS DMPW | ICW
LC | 128532684 | 023/116 | T2 EI RND MTN-TBL MTN #2 23/116 RPR ANCT | TABLEMTN | ETL.6070.TOWR | 2024-04-11 | 2024-04-11 | 2025-03-17 | On-Time |  | 2025-04-11 | 2025-04-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46257278 | T2 EI RND MTN-TBL MTN #2 23/116 RPR ANCT | ICQ
LC | 128532685 | 023/116 | T2 EI RND MTN-TBL MTN #2 23/116 RPR FOND | TABLEMTN | ETL.6070.TOWR | 2024-04-11 | 2024-04-11 | 2025-03-17 | On-Time |  | 2025-04-11 | 2025-04-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46310373 | T2 EI RND MTN-TBL MTN #2 23/116 RPR FOND | ICQ
LC | 128533003 | 011/111 | T2 EI ARCO-CHOLAME 011/111 RPR INSW | MIDWAY | ETL.8440.INSL | 2024-04-11 | 2024-04-11 | 2024-05-01 | On-Time |  | 2024-10-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46236408 | T2 EI ARCO-CHOLAME 011/111 RPR INSW | ICW
LC | 128533593 | 023/119 | T2 EI RND MTN-TBL MTN #2 23/119 RPL INSS | TABLEMTN | ETL.6070.INSL | 2024-04-11 | 2024-04-11 | 2025-02-20 | On-Time |  | 2025-04-11 | 2025-04-11 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35611736 | T2 EI RND MTN-TBL MTN #2 23/119 RPL INSS | 93K
LC | 128533728 | 007/153 | T2 EI COLEMAN-SOUTH 007/153 RPR GYWW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-11 | 2024-04-11 | 2025-03-22 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46389133 | T2 EI COLEMAN-SOUTH 007/153 RPR GYWW | ICW
LC | 128534678 | 075/382 | T2 MALIN-ROUND MTN #2 75/382 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-04-11 | 2024-04-11 | 2024-04-11 | Past Due |  | 2025-04-11 | 2025-04-11 | 93Z | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716778 | T2 DI MLN RD MTN#2 RPL ANCT 10 TWRS | 93Z
LC | 128534699 | 036/291 | T2 EI BRDGEVILL-CTTNWD 036/291L RPR GRWW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-11 | 2024-04-11 | 2024-06-03 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46261879 | T2 EI BRDGEVILL-CTTNWD 036/291L RPR GRWW | ICW
LC | 128534722 | 075/382 | T2 EI MALIN-ROUND MTN #2 75/382 RPR FOND | TABLEMTN | ETL.6020.TOWR | 2024-04-11 | 2024-04-11 | 2025-03-19 | On-Time |  | 2025-04-11 | 2025-04-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381380 | T2 EI MALIN-ROUND MTN #2 75/382 RPR FOND | ICQ
LC | 128534723 | 076/389 | T2 EI MALIN-ROUND MTN#2 76/389 RPR FOND | TABLEMTN | ETL.6020.TOWR | 2024-04-11 | 2024-04-11 | 2025-03-19 | On-Time |  | 2025-04-11 | 2025-04-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381381 | T2 EI MALIN-ROUND MTN#2 76/389 RPR FOND | ICQ
LC | 128534732 | 036/290 | T2 EI BRDGEVILL-CTTNWD 036/290L RPR GRWW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-11 | 2024-04-11 | 2025-03-23 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46311103 | T2 EI BRDGEVILL-CTTNWD 036/290L RPR GRWW | ICW
LC | 128534748 | 028/009 | T2 RIO DELL JCT-BRDGVLE 28/9 RPL INSW | EUREKA | ETL.7850.INSL.CERA | 2024-04-11 | 2024-04-11 | 2025-06-14 | Past Due |  | 2025-04-11 | 2025-04-11 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573029 | T2 EI RIO DELL JCT-BRDGVLE 28/9 RPL INSW | 93I
LC | 128534759 | 028/003 | T2 EI RIO DLL JCT-BRDGVLE 28/3 RPL INSW | EUREKA | ETL.7850.INSL.CERA | 2024-04-11 | 2024-04-11 | 2025-06-14 | Past Due |  | 2025-04-11 | 2025-04-11 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573028 | T2 EI RIO DLL JCT-BRDGVLE 28/3 RPL INSW | 93I
LC | 128534762 | 027/134 | T2 EI RND MTN-TBL MTN #1 27/134 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-11 | 2024-04-11 | 2024-11-04 | On-Time |  | 2025-04-11 | 2025-04-11 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128534764 | 027/134 | T2 EI RND MTN-TBL MTN #1 27/134 RPR FOND | TABLEMTN | ETL.6060.TOWR | 2024-04-11 | 2024-04-11 | 2025-03-17 | On-Time |  | 2025-04-11 | 2025-04-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46310375 | T2 EI RND MTN-TBL MTN #1 27/134 RPR FOND | ICQ
LC | 128534780 | 028/002 | T2 EI RIO DLL JCT-BRDGVLE 28/2 RPL STRW | EUREKA | ETL.7850.POLE.WOOD | 2024-04-11 | 2024-04-11 | 2025-06-14 | Past Due |  | 2025-04-11 | 2025-04-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35573027 | T2 EI RIO DLL JCT-BRDGVLE 28/2 RPL STRW | 70Y
LC | 128535042 | 021/174 | T2NT EI CRBRY SS-RND MTN 21/174 RPR STRT | TABLEMTN | ETL.5410.TOWR | 2024-04-11 | 2024-04-11 | 2025-03-13 | On-Time |  | 2027-04-11 | 2025-04-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354013 | T2NT EI CRBRY SS-RND MTN 21/174 RPR STRT | ICQ
LC | 128535060 | 021/175 | T2 EI CRBRY SS-ROUND MTN 21/175 RPR FOND | TABLEMTN | ETL.5410.TOWR | 2024-04-11 | 2024-04-11 | 2025-04-03 | On-Time |  | 2025-04-11 | 2025-04-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46354014 | T2 EI CRBRY SS-ROUND MTN 21/175 RPR FOND | ICQ
LC | 128535061 | 021/176 | T2NT EI CRBRY SS-RND MTN 21/176 RPR STRT | TABLEMTN | ETL.5410.TOWR | 2024-04-11 | 2024-04-11 | 2025-03-13 | On-Time |  | 2027-04-11 | 2025-04-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354015 | T2NT EI CRBRY SS-RND MTN 21/176 RPR STRT | ICQ
LC | 128535156 | 005/063 | T2 EI HAT CREEK #1-PIT #1 5/63 RPL STRW | TABLEMTN | ETL.7020.POLE.WOOD | 2024-04-11 | 2024-04-11 | 2025-05-07 | Past Due |  | 2025-04-11 | 2025-04-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574669 | T2 EI HAT CREEK #1-PIT #1 5/63 RPL STRW | 70Y
LC | 128535212 | 004/097 | T2 DI CSCD-BNTN-DESCHUTES-04/97 RPR JUMW | TABLEMTN | ETL.6310.INSL.NCER | 2024-04-11 | 2024-04-11 | 2024-11-16 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46233791 | T2 DI CSCD-BNTN-DESCHUTES-04/97 RPR JUMW | ICW
LC | 128535254 | 027/002A | T2 EI TRINITY-MAPLE CRK 27/002A RMV VEG | EUREKA | ETL.8170.POLE.WOOD | 2024-04-11 | 2024-04-11 | 2024-10-29 | On-Time |  | 2025-04-11 | 2025-04-11 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128535261 | 025/003A | T2 EI TRINITY-MAPLE CREEK 25/3A COMPLETE | EUREKA | ETL.8170.POLE.WOOD | 2024-04-11 | 2024-04-11 | 2025-03-30 | On-Time |  | 2025-04-11 | 2025-04-11 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35534406 | T2 EI TRINITY-MAPLE CREEK 25/3A RPL STRW | 70Y
LC | 128535270 | 027/002A | T2 EI TRINITY-MAPLE CRK 27/002A RPR GYWW | EUREKA | ETL.8170.POLE.WOOD | 2024-04-11 | 2024-04-11 | 2024-06-19 | On-Time |  | 2024-07-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46232510 | T2 EI TRINITY-MAPLE CRK 27/002A RPR GYWW | ICW
LC | 128535553 | 022/000 | T2 DI MNDCNO-WLLTS-FRT BRG 22/0 RPR JUMW | WILLITS | ETL.7550.INSL.NCER | 2024-04-11 | 2024-04-11 | 2025-04-09 | On-Time |  | 2024-10-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46233086 | T2 DI MENDO-WLTS-FRT BRG-22/00 RPR JUMW | ICW
LC | 128535701 | 020/092 | T2 DI MOSS LANDING-LS BNS 20/92 RPR SHLS | MOSSLNDG | ETL.6040.TOWR | 2024-04-11 | 2024-04-11 | 2025-04-02 | On-Time |  | 2025-04-11 | 2025-04-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46305509 | T2 DI MOSS LANDING-LS BNS 20/92 RPR SHLS | ICS
LC | 128536200 | 076/388 | T2 DI MALIN-RM#2 76/388 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-04-11 | 2024-04-11 | 2025-03-19 | On-Time |  | 2025-04-11 | 2025-04-11 | 93Z | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716778 | T2 DI MLN RD MTN#2 RPL ANCT 10 TWRS | 93Z
LC | 128538509 | 043/283 | T2 DI TRINITY-CTTNWOOD 43/283 RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-04-12 | 2024-04-11 | 2024-08-17 | On-Time |  | 2024-07-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46234426 | T2 DI TRINITY-CTTNWOOD 43/283 RPR JUMW | ICW
LC | 128539252 | 002/013 | T2 DI TRINITY-MAPLE CRK 2/13 RMV VEG | EUREKA | ETL.8170.POLE.NWOD | 2024-04-12 | 2024-04-11 | 2024-10-22 | On-Time |  | 2024-07-11 | 2025-04-11 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128539348 | 021/179 | T2 DI CRAG VIEW-CASCADE 21/179 RPR STRW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-12 | 2024-04-11 | 2025-03-20 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454368 | T2 DI CRAG VIEW-CASCADE 21/179 RPR STRW | ICW
LC | 128539725 | 024/008 | T2 DI MNDCNO-WLTS-FRT BRG 24/8 RPR IBWW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-12 | 2024-04-11 | 2025-04-03 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMC SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46308239 | T2 DI MNDCNO-WLTS-FRT BRG 24/8 RPR IBWW | ICW
LC | 128539726 | 024/008 | T2 DI MNDCNO-WLTS-FRT BRG 24/8 RPR STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-12 | 2024-04-11 | 2025-04-03 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMC SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46308301 | T2 DI MNDCNO-WLTS-FRT BRG 24/8 RPR STRW | ICW
LC | 128541604 | 004/032 | T2 EI OLEUM-G #1 004/032 RMV NEST | CONCORD | ETL.3150.POLE.NWOD | 2024-04-12 | 2024-04-11 | 2025-01-15 | On-Time |  | 2025-04-11 | 2025-04-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46287345 | T2 EI OLEUM-G #1 004/032 RMV NEST | ICS
LC | 128541958 | 022/005 | T2 DI MENDOCINO-WFTB 22/5 RPR CRSW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-12 | 2024-04-11 | 2025-04-10 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCH COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46308300 | T2 DI MENDOCINO-WFTB 22/5 RPR CRSW | ICW
LC | 128577689 | A007/155 | T2 DI CSCD-BTN-DSCHTS A007/155 RPL STRW | TABLEMTN | ETL.6310.POLE.WOOD | 2024-04-18 | 2024-04-11 | 2025-04-07 | On-Time |  | 2025-04-11 | 2025-04-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556136 | T2 DI CSCD-BTN-DSCHTS A007/155 RPL STRW | 70Y
LC | 128577832 | 020/170 | T2 CRAG VW-CSCD 20/170L RPL POLE | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-18 | 2024-04-11 | 2024-04-11 | Past Due |  | 2025-04-11 | 2025-04-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35557672 | T2 DI CRAG VW-CSCD 20/170L RPL POLE | 70Y
LC | 128577833 | 020/170 | T2 CRAG VW-CSCD 20/170R RPL POLE | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-18 | 2024-04-11 | 2024-04-11 | Past Due |  | 2025-04-11 | 2025-04-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35557672 | T2 DI CRAG VW-CSCD 20/170L RPL POLE | 70Y
LC | 128577838 | 047/191 | T2 DI DIABLO-GATES #1 47/191 RPLC HRDT | PISMOBCH | ETL.5960.TOWR | 2024-04-18 | 2024-04-11 | 2025-04-04 | On-Time |  | 2025-04-11 | 2025-04-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46391251 | T2 DI DIABLO-GATES #1 47/191 RPLC HRDT | ICQ
LC | 128577975 | 020/174 | T2 DI CRAG VIEW-CASCADE 20/174R RPR OPGW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-18 | 2024-04-11 | 2025-02-07 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Wood | Repair | 46454370 | T2 DI CRAG VIEW-CASCADE 20/174R RPR OPGW | ICW
LC | 128578135 | 020/091 | T2 DI MOSS LDNG-LS BNS 20/91 RPR SHLS | MOSSLNDG | ETL.6040.TOWR | 2024-04-18 | 2024-04-11 | 2024-07-16 | On-Time |  | 2025-04-11 | 2025-04-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46264435 | T2 DI MOSS LDNG-LS BNS 20/91 RPR SHLS | ICS
LC | 128578189 | 018/087 | T2 DI MOSS LNDNG LS BANOS 18/87 RPR STRT | MOSSLNDG | ETL.6040.TOWR | 2024-04-18 | 2024-04-11 | 2025-01-28 | On-Time |  | 2025-04-11 | 2025-04-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416489 | T2 DI MOSS LNDNG LS BANOS 18/87 RPR STRT | ICQ
LC | 128578359 | 076/387 | T2 DI MALIN-ROUND MTN #2 76/387 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-18 | 2024-04-11 | 2025-03-19 | On-Time |  | 2025-04-11 | 2025-04-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381389 | T2 DI MALIN-ROUND MTN #2 76/387 RPR GYWT | ICQ
LC | 128578496 | 017/080 | T2 DI MOSS LNDNG-LS BANOS 17/80 RPL INSS | MOSSLNDG | ETL.6040.INSL | 2024-04-18 | 2024-04-11 | 2025-02-23 | On-Time |  | 2025-04-11 | 2025-04-11 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35596168 | T2 DI MSS LNDNG-LS BNS 36/159 RPL INSS | 93K
LC | 128578498 | 017/080 | T2 DI MOSS LDNG-LOS BANOS 17/80 RPR SHLS | MOSSLNDG | ETL.6040.TOWR | 2024-04-18 | 2024-04-11 | 2025-02-23 | On-Time |  | 2025-04-11 | 2025-04-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46305506 | T2 DI MOSS LDNG-LOS BANOS 17/80 RPR SHLS | ICS
LC | 128581350 | 021/176 | T2 DI CARG VIEW-CASCADE 021/176 RPR OPGW | TABLEMTN | ETL.1350.POLE.STPS | 2024-04-19 | 2024-04-11 | 2025-02-07 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Wood | Repair | 46454371 | T2 DI CARG VIEW-CASCADE 021/176 RPR OPGW | ICW
LC | 128581615 | 019/166 | T2 DI CRAG VIEW-CASCADE 19/166L TOUCH | TABLEMTN | ETL.1350.POLE.STPS | 2024-04-19 | 2024-04-11 | 2025-06-09 | Past Due |  | 2024-10-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46486716 | T2 DI CRAG VIEW-CASCADE 19/166L TOUCH | ICW
LC | 128582385 | 009/083 | T2 DI BRDGVLL-CTTNWD 009/083 COMPLETE | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-19 | 2024-04-11 | 2025-02-07 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311104 | T2 DI BRDGVLL-CTTNWD 009/083 RPR STRW | ICW
LC | 128583505 | 012/004 | T2 DI KNCTI MDDLTWN 12/004 RPR CRSW | WILLITS | ETL.6380.POLE.WOOD | 2024-04-19 | 2024-04-11 | 2025-03-17 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46340219 | T2 DI KNCTI MDDLTWN 12/004 RPR CRSW | ICW
LC | 128583509 | 012/004 | T2 DI KNCTI-MDDLTWN 12/004 RPR JUMW | WILLITS | ETL.6380.INSL.CERA | 2024-04-19 | 2024-04-11 | 2025-03-17 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46340260 | T2 DI KNCTI-MDDLTWN 12/004 RPR JUMW | ICW
LC | 128584032 | 075/384 | T2 DI MALIN-ROUND MTN #2 75/384 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-04-19 | 2024-04-11 | 2025-02-09 | On-Time |  | 2025-04-11 | 2025-04-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46337581 | T2 DI MALIN-ROUND MTN #2 75/384 RPR OPGW | ICS
LC | 128584139 | 019/165 | T2 CRG VW-CASCADE 019/165L RPL STRW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-11 | 2024-04-11 | Past Due |  | 2025-04-11 | 2025-04-11 | 372 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35557669 | T2 DI CRG VW-CASCADE 019/165R RPL STRW | 70Y
LC | 128584183 | 019/165 | T2 CRG VW-CASCADE 019/165R RPL STRW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-11 | 2024-04-11 | Past Due |  | 2025-04-11 | 2025-04-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35557669 | T2 DI CRG VW-CASCADE 019/165R RPL STRW | 70Y
LC | 128584282 | 047/005 | T2 DI HMBLDT-TRINITY 47/005L RPL ANCW | EUREKA | ETL.1820.POLE.WDPS | 2024-04-19 | 2024-04-11 | 2025-04-07 | On-Time |  | 2025-04-11 | 2025-04-11 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574655 | T2 DI HMBLDT-TRINITY 47/005L RPL ANCW | 93E
LC | 128584388 | 020/168 | T2 DI CRG VW-CASCADE 020/168R RPL STRW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-11 | 2024-04-11 | Past Due |  | 2025-04-11 | 2025-04-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557671 | T2 DI CRG VW-CASCADE 020/168R RPL STRW | 70Y
LC | 128584431 | 020/168 | T2 DI CRG VW-CASCADE 020/168L RPL STRW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-11 | 2024-04-11 | Past Due |  | 2025-04-11 | 2025-04-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557671 | T2 DI CRG VW-CASCADE 020/168R RPL STRW | 70Y
LC | 128622776 | 009/188 | T2 CARIBOU-WESTWOOD 09/188 RPR ANCW | TABLEMTN | ETL.6300.POLE.WOOD | 2024-04-23 | 2024-04-11 | 2024-07-17 | On-Time |  | 2025-04-11 | 2025-04-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46239927 | T2 CARIBOU-WESTWOOD 09/188 RPR ANCW | ICW
LC | 130736956 | 009/039 | T3NT PTTSBRG-SN MTEO 009/039 RPR FOND | CONCORD | ETL.5463.TOWR | 2025-01-13 | 2024-10-11 | 2024-10-11 | Past Due |  | 2027-10-11 | 2025-04-11 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR3 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair
LC | 123303721 | 021/107 | T3NT EI RNDMTN-TBLMTN #2 21/107 BNT STEL | TABLEMTN | ETL.6070.TOWR | 2022-04-12 | 2022-04-12 | 2023-07-29 | On-Time |  | 2025-04-12 | 2025-04-12 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647620 | T3 EI RND MTN-TBL MTN #2 21/107 BNT STEL | ICQ
LC | 123309117 | 021/110 | T3NT EI RND MT-TBL MTN#1 21/110 BNT STEL | TABLEMTN | ETL.6060.TOWR | 2022-04-12 | 2022-04-12 | 2023-07-29 | On-Time |  | 2025-04-12 | 2025-04-12 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644444 | T3 EI RND MTN-TBL MTN #1 21/110 BNT STEL | ICQ
LC | 123311541 | 022/112 | T3NT EI RNDMTN-TBLMTN #2 22/112 RPR GYWS | TABLEMTN | ETL.6070.TOWR | 2022-04-12 | 2022-04-12 | 2023-08-10 | On-Time |  | 2025-04-12 | 2025-04-12 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45702810 | T3 EI RND MTN-TBL MTN #2 22/112 RPR GYWS | ICS
LC | 123313146 | 022/114 | T3NT EI RND MT-TBL MT #1 22/114 RPR GYWS | TABLEMTN | ETL.6060.TOWR | 2022-04-12 | 2022-04-12 | 2023-08-09 | On-Time |  | 2025-04-12 | 2025-04-12 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45699114 | T3 EI RND MTN-TBL MT #1 22/114 RPR GYWS | ICS
LC | 123379293 | 011/203 | T2 DI CLMN RD BLF 11/203 RMV DEBRIS | TABLEMTN | ETL.6440.POLE.NWOD | 2022-04-20 | 2022-04-12 | 2023-06-09 | On-Time |  | 2023-04-12 | 2025-04-12 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 45456247 | T2 DI CLMN RD BLF 11/203 RMV DEBRIS | ICW
LC | 123457803 | 002/065 | T2NT DI VOLTA-SOUTH 2/65 RMV BUTT | TABLEMTN | ETL.8300.POLE.WOOD | 2022-04-29 | 2022-04-12 | 2023-07-20 | On-Time |  | 2025-04-12 | 2025-04-12 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 45456455 | T2NT DI VOLTA-SOUTH 2/65 RMV BUTT | ICW
LC | 123463138 | A016/249 | T2NT DI COLEMN-RED BLFF A16/249 RMV BUTT | TABLEMTN | ETL.6440.POLE.WOOD | 2022-04-30 | 2022-04-12 | 2023-05-17 | On-Time |  | 2025-04-12 | 2025-04-12 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 45456384 | T2NT DI COLEMN-RED BLFF A16/249 RMV BUTT | ICW
LC | 128537097 | 010/078 | T2 EI MORAGA-LAKEWOOD 10/078 RPR SHLD | CONCORD | ETL.3741.TOWR | 2024-04-12 | 2024-04-12 | 2024-10-23 | On-Time |  | 2025-04-12 | 2025-04-12 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46287355 | T2 EI MORAGA-LAKEWOOD 10/078 RPR SHLD | ICS
LC | 128537121 | 010/078 | T2 EI MORAGA-LAKEWOOD 10/078 RPR FOND | CONCORD | ETL.3741.TOWR | 2024-04-12 | 2024-04-12 | 2025-01-14 | On-Time |  | 2025-04-12 | 2025-04-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46287356 | T2 EI MORAGA-LAKEWOOD 10/078 RPR FOND | ICQ
LC | 128537220 | 010/076 | T2 EI MORAGA-LAKEWOOD 10/076 RPR SHLD | CONCORD | ETL.3741.TOWR | 2024-04-12 | 2024-04-12 | 2024-10-23 | On-Time |  | 2025-04-12 | 2025-04-12 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46287353 | T2 EI MORAGA-LAKEWOOD 10/076 RPR SHLD | ICS
LC | 128537519 | 009/071 | T2 EI MORAGA-LAKEWOOD 09/071 RPR FOND | CONCORD | ETL.3741.TOWR | 2024-04-12 | 2024-04-12 | 2025-01-13 | On-Time |  | 2025-04-12 | 2025-04-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46287352 | T2 EI MORAGA-LAKEWOOD 09/071 RPR FOND | ICQ
LC | 128537946 | 034/011 | T2 RIO DELL JCT-BRIDGEVILLE 034/011 GO95 | EUREKA | ETL.7850.POLE.WOOD | 2024-04-12 | 2024-04-12 | 2025-06-17 | Past Due |  | 2025-04-12 | 2025-04-12 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 31652879 | T2 RIO DELL JCT-BRDGVLL 34/10 GO95 | 93G
LC | 128538106 | 021/177 | T2 EI CRBRY SS-RND MTN 21/177 RPR STRT | TABLEMTN | ETL.5410.TOWR | 2024-04-12 | 2024-04-12 | 2025-03-19 | On-Time |  | 2025-04-12 | 2025-04-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354016 | T2 EI CRBRY SS-RND MTN 21/177 RPR STRT | ICQ
LC | 128538120 | 022/178 | T2 EI CRBRY SS-RND MTN 22/178 RPR STRT | TABLEMTN | ETL.5410.TOWR | 2024-04-12 | 2024-04-12 | 2024-11-04 | On-Time |  | 2024-06-12 | 2025-04-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46381066 | T2 EI CRBRY SS-RND MTN 22/178 RPR STRT | ICQ
LC | 128538121 | 021/177 | T2 EI CRBRY SS-RND MTN 21/177 RPR FOND | TABLEMTN | ETL.5410.TOWR | 2024-04-12 | 2024-04-12 | 2025-04-03 | On-Time |  | 2025-04-12 | 2025-04-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46354017 | T2 EI CRBRY SS-RND MTN 21/177 RPR FOND | ICQ
LC | 128538130 | 008/049 | T2 EI STANISLAUS-MANTECA #2 8/49 RMV VEG | VICTOR | ETL.3820.TOWR | 2024-04-12 | 2024-04-12 | 2024-12-30 | On-Time |  | 2025-04-12 | 2025-04-12 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128538206 | 064/267 | T2 EI RND MTN-TBL MTN #2 64/267 RPL INSS | TABLEMTN | ETL.6070.INSL | 2024-04-12 | 2024-04-12 | 2025-02-19 | On-Time |  | 2025-04-12 | 2025-04-12 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574244 | T2 EI RND MTN-TBL MTN #2 RPL INSS 6 TWRS | 93K
LC | 128538263 | 004/009 | T2 FORT BRAGG-ELK 04/09 RPL INSW | WILLITS | ETL.2060.INSL.NCER | 2024-04-12 | 2024-04-12 | 2025-04-21 | Past Due |  | 2025-04-12 | 2025-04-12 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR REMT SWRK CLR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573914 | T2 FORT BRAGG-ELK 04/09 RPL INSW | 93I
LC | 128538470 | 064/268 | T2 EI RND MTN-TBL MTN #2 64/268 RPL INSS | TABLEMTN | ETL.6070.INSL | 2024-04-12 | 2024-04-12 | 2025-02-19 | On-Time |  | 2025-04-12 | 2025-04-12 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574244 | T2 EI RND MTN-TBL MTN #2 RPL INSS 6 TWRS | 93K
LC | 128538589 | 005/063 | T2 EI PT NO.5-RND MTN NO.2 5/63 RPR STR | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-12 | 2024-04-12 | 2025-03-03 | On-Time |  | 2025-04-12 | 2025-04-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454278 | T2 EI PT NO.5-RND MTN NO.2 5/63 RPR STR | ICW
LC | 128538608 | 008/051 | T2 STANISLAUS-MNTEC#2 8/51 RPR STRT | VICTOR | ETL.3820.TOWR | 2024-04-12 | 2024-04-12 | 2024-04-12 | Past Due |  | 2025-04-12 | 2025-04-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46416342 | T2NT EI STANISLAUS-MNTEC#2 8/51 RPR STRT | ICQ
LC | 128538618 | 064/269 | T2 EI RND MTN-TBL MTN #2 64/269 RPL INSS | TABLEMTN | ETL.6070.INSL | 2024-04-12 | 2024-04-12 | 2025-02-19 | On-Time |  | 2025-04-12 | 2025-04-12 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574244 | T2 EI RND MTN-TBL MTN #2 RPL INSS 6 TWRS | 93K
LC | 128538657 | 002/014 | T2 EI WISHON-SN JOAQUN #3 2/14 RPL STRW | FRESNO | ETL.9340.POLE.WOOD | 2024-04-12 | 2024-04-12 | 2025-04-23 | Past Due |  | 2025-04-12 | 2025-04-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35587533 | T2 EI WISHON-SN JOAQUN #3 2/14 RPL STRW | 70Y
LC | 128538773 | 064/270 | T2 EI RND MTN-TBL MTN #2 64/270 RPL INSS | TABLEMTN | ETL.6070.INSL | 2024-04-12 | 2024-04-12 | 2025-02-19 | On-Time |  | 2025-04-12 | 2025-04-12 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574244 | T2 EI RND MTN-TBL MTN #2 RPL INSS 6 TWRS | 93K
LC | 128538774 | 008/002 | T2 SALMON CREEK TAP 8/2 GO95 USAGE | LAKEVLLE | ETL.6981.POLE.WOOD | 2024-04-12 | 2024-04-12 | 2025-04-09 | On-Time |  | 2025-04-12 | 2025-04-12 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35572898 | T2 EI SALMON CREEK TAP 008/002 GO95 | 93G
LC | 128538775 | 008/003 | T2 SALMON CREEK TAP 008/003 RPL POLE | LAKEVLLE | ETL.6981.POLE.WOOD | 2024-04-12 | 2024-04-12 | 2025-04-09 | On-Time |  | 2025-04-12 | 2025-04-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572899 | T2 EI SALMON CREEK TAP 008/003 RPL POLE | 70Y
LC | 128538801 | 005/062 | T2 EI PIT #5-ROUND MTN #2 5/62L RPR STRW | TABLEMTN | ETL.5430.POLE.STPS | 2024-04-12 | 2024-04-12 | 2025-03-03 | On-Time |  | 2025-04-12 | 2025-04-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454279 | T2 EI PIT #5-ROUND MTN #2 5/62L RPR STRW | ICW
LC | 128539317 | 014/075 | T2 VACA-PARKWAY 014/075 RPL DAMS | SACTO | ETL.5850.INSL.NCER | 2024-04-12 | 2024-04-12 | 2025-01-24 | On-Time |  | 2025-04-12 | 2025-04-12 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR REMT ACCH COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Damper-Steel | Replace | 46324632 | T2 VACA-PARKWAY 014/075 RPL DAMS | ICS
LC | 128539529 | 009/069 | T2 EI MORAGA-LAKEWOOD 09/069 RPR STRT | CONCORD | ETL.3741.TOWR | 2024-04-12 | 2024-04-12 | 2025-01-13 | On-Time |  | 2025-04-12 | 2025-04-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287349 | T2 EI MORAGA-LAKEWOOD 09/069 RPR STRT | ICQ
LC | 128539754 | 000/001 | T2 EI KRCKHF-CLVS-SNGR #1 0/1 RPL RPTS | FRESNO | ETL.1890.TOWR | 2024-04-12 | 2024-04-12 | 2025-01-23 | On-Time |  | 2025-04-12 | 2025-04-12 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46292639 | T2NT EI KRCKHF-CLVS-SNGR #1 0/1 RPL RPTS | ICB
LC | 128540341 | 004/021 | T2 SBRNT-SNDRD OL SW ST #1 4/21 TOUCH | CONCORD | ETL.3800.TOWR | 2024-04-12 | 2024-04-12 | 2025-04-28 | Past Due |  | 2024-10-12 | 2025-04-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485734 | T2 SBRNT-SNDRD OL SW ST #1 4/21 TOUCH | ICQ
LC | 128540539 | 004/023 | T2 PITTSBURG-CLAYTON #4 4/23 COTTER | CONCORD | ETL.3291.INSL.NCER | 2024-04-12 | 2024-04-12 | 2024-08-20 | On-Time |  | 2024-07-12 | 2025-04-12 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMC REMT SWRK SPCR CLR ACCL COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46233849 | T2 PITTSBURG-CLAYTON #4 4/23 RPR INSS | ICS
LC | 128540599 | 012/156 | T2 EI WST PNT-VLY SPRNS 12/156 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-04-12 | 2024-04-12 | 2024-08-27 | On-Time |  | 2024-07-12 | 2025-04-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46232573 | T2 EI WST PNT-VLY SPRNS 12/156 RPR GYWW | ICW
LC | 128540657 | 052/256 | T2 EI CORTINA-MNDCNO #1 52/256 BNT STEEL | WILLITS | ETL.1330.TOWR | 2024-04-12 | 2024-04-12 | 2025-03-21 | On-Time |  | 2025-04-12 | 2025-04-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46290152 | T2 EI CORTINA-MNDCNO #1 52/256 BNT STEEL | ICQ
LC | 128540658 | 053/260 | T2 EI CRTNA-MENDCNO #1 53/260 RPR FOND | WILLITS | ETL.1330.TOWR | 2024-04-12 | 2024-04-12 | 2025-03-21 | On-Time |  | 2025-04-12 | 2025-04-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46290153 | T2 EI CRTNA-MENDCNO #1 53/260 RPR FOND | ICQ
LC | 128540778 | 038/307 | T2 EI CTNWD-HUMBOLDT 38/307R RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-12 | 2024-04-12 | 2025-02-17 | On-Time |  | 2025-04-12 | 2025-04-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311102 | T2 EI CTNWD-HUMBOLDT 38/307R RPR GYWW | ICW
LC | 128540885 | 038/307 | T2 EI CTNWD-HUMBOLDT 38/307L RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-12 | 2024-04-12 | 2025-02-17 | On-Time |  | 2025-04-12 | 2025-04-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311101 | T2 EI CTNWD-HUMBOLDT 38/307L RPR GYWW | ICW
LC | 128540981 | 029/001 | T2 RIO DELL JCT-BRDGVLE 29/1 RPL INSW | EUREKA | ETL.7850.INSL.CERA | 2024-04-12 | 2024-04-12 | 2025-06-14 | Past Due |  | 2025-04-12 | 2025-04-12 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573030 | T2 EI RIO DELL JCT-BRDGVLE 29/1 RPL INSW | 93I
LC | 128541468 | 002/061 | T2 EI COLEMAN-SOUTH 002/061 RPL POLE | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-12 | 2024-04-12 | 2025-03-24 | On-Time |  | 2025-04-12 | 2025-04-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556781 | T2 EI COLEMAN-SOUTH 002/061 RPL POLE | 70Y
LC | 128541530 | 002/063 | T2 EI COLEMAN-SOUTH 002/063 RPL POLE | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-12 | 2024-04-12 | 2025-03-24 | On-Time |  | 2025-04-12 | 2025-04-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556781 | T2 EI COLEMAN-SOUTH 002/061 RPL POLE | 70Y
LC | 128541587 | 029/142 | T2 EI RND MTN-TBL MTN #1 29/142 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-04-12 | 2024-04-12 | 2025-01-28 | On-Time |  | 2025-04-12 | 2025-04-12 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306212 | T2 EI RND MTN-TBL MTN #1 29/142 RMV NEST | ICS
LC | 128541589 | 030/145 | T2 EI RND MTN-TBL MTN #1 30/145 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-12 | 2024-04-12 | 2024-11-20 | On-Time |  | 2025-04-12 | 2025-04-12 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128541640 | 029/144 | T2 EI RND MTN-TBL MTN #1 29/144 RPL INSS | TABLEMTN | ETL.6060.INSL | 2024-04-12 | 2024-04-12 | 2025-01-28 | On-Time |  | 2025-04-12 | 2025-04-12 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | Missing | Insulator-Steel | Install | 35569940 | T2 EI RND MTN-TBL MTN #1 RPL INSS 9 TWRS | 93K
LC | 128541887 | 083/424 | T2 EI MALIN-ROUND MTN #2 83/424 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-04-12 | 2024-04-12 | 2025-04-07 | On-Time |  | 2025-04-12 | 2025-04-12 | 93Z | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716778 | T2 DI MLN RD MTN#2 RPL ANCT 10 TWRS | 93Z
LC | 128541908 | 026/003 | T2 EI TRINITY-MAPLE CRK 26/03 RPL HRDD | EUREKA | ETL.8170.POLE.WOOD | 2024-04-12 | 2024-04-12 | 2025-04-12 | On-Time |  | 2025-04-12 | 2025-04-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Hardware-Wood | Install | 46345757 | T2 EI TRINITY-MAPLE CRK 26/03 RPL HRDD | ICW
LC | 128541909 | 026/000 | T2 EI TRINITY-MAPLE CRK 26/0 GO95 RPL | EUREKA | ETL.8170.POLE.WOOD | 2024-04-12 | 2024-04-12 | 2024-08-20 | On-Time |  | 2025-04-12 | 2025-04-12 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35545655 | T2 EI TRINITY-MAPLE CRK 26/0 GO95 | 93G
LC | 128541946 | 004/027 | T2 EI FULTON-IGNACIO #1 4/27 RMV VEG | LAKEVLLE | ETL.4680.TOWR | 2024-04-12 | 2024-04-12 | 2025-01-16 | On-Time |  | 2025-04-12 | 2025-04-12 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128542215 | 013/100 | T2 EI SLT SPRNG-TGR CRK 13/100 MASTIC | VICTOR | ETL.3500.TOWR | 2024-04-12 | 2024-04-12 | 2025-03-27 | On-Time |  | 2025-04-12 | 2025-04-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416346 | T2 EI SLT SPRNG-TGR CRK 13/100 MASTIC | ICQ
LC | 128544117 | 004/058 | T2 MANVILLE TAP 4/58R RPR GYWW | PISMOBCH | ETL.1372.POLE.WDPS | 2024-04-14 | 2024-04-12 | 2024-04-25 | On-Time |  | 2024-07-12 | 2025-04-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46233831 | T2 MANVILLE TAP 4/58R RPR GYWW | ICW
LC | 128544118 | 004/058 | T2 MANVILLE TAP 4/58C RPR GYWW | PISMOBCH | ETL.1372.POLE.WDPS | 2024-04-14 | 2024-04-12 | 2024-04-25 | On-Time |  | 2024-07-12 | 2025-04-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46233832 | T2 MANVILLE TAP 4/58C RPR GYWW | ICW
LC | 128544152 | 004/058 | T2 MANVILLE TAP 4/58L RPR GYWW | PISMOBCH | ETL.1372.POLE.STPS | 2024-04-14 | 2024-04-12 | 2024-04-25 | On-Time |  | 2024-07-12 | 2025-04-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46233833 | T2 MANVILLE TAP 4/58L RPR GYWW | ICW
LC | 123317783 | 023/118 | T2NT EI RND MT-TBL MT #2 23/118 RPR GYWS | TABLEMTN | ETL.6070.TOWR | 2022-04-13 | 2022-04-13 | 2023-08-10 | On-Time |  | 2025-04-13 | 2025-04-13 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45702817 | T2 EI RND MTN-TBL MTN #2 23/118 RPR GYWS | ICS
LC | 123318028 | 023/119 | T2NT EI RD MN-TBL MTN #1 23/119 RPR GYWS | TABLEMTN | ETL.6060.TOWR | 2022-04-13 | 2022-04-13 | 2023-08-10 | On-Time |  | 2025-04-13 | 2025-04-13 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45699116 | T2 EI RND MTN-TBL MTN #1 23/119 RPR GYWS | ICS
LC | 123360121 | 000/007 | T2NT DI KRCKHOFF#1-KRCKHF#2 0/7 RPL INSS | FRESNO | ETL.1880.INSL.CERA | 2022-04-18 | 2022-04-13 | 2023-05-20 | On-Time |  | 2025-04-13 | 2025-04-13 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 31602178 | T2 DI KRCKHOFF#1-KRCKHOFF#2 RPL INSS 2TW | 93K
LC | 123374457 | 012/049 | T2NT DI TSLA-MTCLF 12/49 UNBURY | METCALF | ETL.6110.TOWR | 2022-04-20 | 2022-04-13 | 2023-04-13 | On-Time |  | 2025-04-13 | 2025-04-13 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCH COMP OH TR2N AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45728044 | T2NT DI TSLA-MTCLF 12/49 UNBURY | ICQ
LC | 123380985 | 001/008 | T2NT DI KRCKHFF-CLVS-SNGR#1 1/8 INS HRDT | FRESNO | ETL.1890.TOWR | 2022-04-20 | 2022-04-13 | 2023-01-31 | On-Time |  | 2023-04-13 | 2025-04-13 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | Missing | Hardware-Tower | Install | 45655284 | T2NT DI KRCKHFF-CLVS-SNGR#1 1/8 INS HRDT | ICQ
LC | 123466784 | 000/002 | T3NT DI BRUNSWICK #2 TAP 0/2 RPR INSS | SACTO | ETL.1431.INSL.NCER | 2022-04-30 | 2022-04-13 | 2023-06-15 | On-Time |  | 2025-04-13 | 2025-04-13 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR NTDE | No Good/Out of Stdrd | Insulator-Steel | Repair | 45647485 | T3 DI BRUNSWICK #2 TAP 0/2 RPR INSS | ICS
LC | 123466910 | 000/005 | T3NT DI MISSION POWER TAP 0/005 RPR GYWW | LAKEVLLE | ETL.1651.POLE.NWOD | 2022-04-30 | 2022-04-13 | 2023-09-01 | On-Time |  | 2025-04-13 | 2025-04-13 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45575606 | T3 DI MISSION POWER TAP 000/005 RPR GYWW | ICW
LC | 128542778 | 015/153 | T2 ARCO-CHOLAME 15/153 RPR INSW | MIDWAY | ETL.8440.INSL | 2024-04-13 | 2024-04-13 | 2025-01-08 | On-Time |  | 2025-04-13 | 2025-04-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46302516 | T2 ARCO-CHOLAME 15/153 RPR INSW | ICW
LC | 123360120 | 005/044 | T3NT DI SBRNTE-GRZLY-CLRMT 5/44 RPR STRT | CONCORD | ETL.3740.TOWR | 2022-04-18 | 2022-04-14 | 2023-05-01 | On-Time |  | 2025-04-14 | 2025-04-14 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Steel | Repair | 45513128 | T3 DI SBRNTE-GRZZLY-CLRMT 05/44 RPR STRT | ICS
LC | 123367493 | 016/097 | T2NT DI MOSS LAND-DL MNT #1 16/97 MASTIC | MOSSLNDG | ETL.2830.TOWR | 2022-04-19 | 2022-04-14 | 2023-04-04 | On-Time |  | 2023-04-14 | 2025-04-14 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45650140 | T2NT DI MOSS LAND-DL MNT #1 16/97 MASTIC | ICQ
LC | 123380285 | 000/001 | T2NT DI KRCKHFF#1-KRCKF#2 0/1 UNBURY CMT | FRESNO | ETL.1880.TOWR | 2022-04-20 | 2022-04-14 | 2023-01-03 | On-Time |  | 2025-04-14 | 2025-04-14 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45616292 | T2 DI KRCKHFF#1-KRCKHFF#2 0/1 UNBURY | ICQ
LC | 123464610 | 017/099 | T2NT DI MS LNDNG-DEL MNT #1 17/99 MASTIC | MOSSLNDG | ETL.2830.TOWR | 2022-04-30 | 2022-04-14 | 2024-09-18 | On-Time |  | 2025-04-14 | 2025-04-14 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46141201 | T2NT DI MS LNDNG-DEL MNT #1 17/99 MASTIC | ICQ
LC | 123478538 | 022/198 | T2NT DI BRIDGE-COTTON 22/198 RPR ADSS | TABLEMTN | ETL.1110.POLE.STPS | 2022-05-02 | 2022-04-14 | 2024-01-17 | On-Time |  | 2025-04-14 | 2025-04-14 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45763378 | T2NT DI BRIDGE-COTTON 22/198 RPR ADSS | ICW
LC | 123478740 | 022/195 | T2NT DI BRIDGE-COTTON 22/195 RPR ADSS | TABLEMTN | ETL.1110.POLE.STPS | 2022-05-02 | 2022-04-14 | 2023-09-04 | On-Time |  | 2025-04-14 | 2025-04-14 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 46046551 | T2NT DI BRIDGE-COTTON 22/195 RPR ADSS | ICW
LC | 123480306 | 030/255 | T3NT DI RND MTN-CTTWD #3 30/255 BNT STL | TABLEMTN | ETL.5650.TOWR | 2022-05-02 | 2022-04-14 | 2023-07-17 | On-Time |  | 2025-04-14 | 2025-04-14 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648236 | T3 DI ROUND MTN-CTTNWD #3 30/255 BNT STL | ICQ
LC | 128543974 | 012/070 | T2 CHRISTIE-SOBRANTE 12/70 TOUCH | CONCORD | ETL.1260.TOWR | 2024-04-14 | 2024-04-14 | 2025-04-30 | Past Due |  | 2024-10-14 | 2025-04-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46489044 | T2 CHRISTIE-SOBRANTE 12/70 TOUCH | ICQ
LC | 128544078 | 028/134 | T2 CORTINA-MNDCN #1 28/134 TOUCH | WILLITS | ETL.1330.TOWR | 2024-04-14 | 2024-04-14 | 2025-04-07 | On-Time |  | 2024-10-14 | 2025-04-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472248 | T2 CORTINA-MNDCN #1 28/134 RPR STRT | ICQ
LC | 128544109 | 028/136 | T2 CORTINA-MNDCNO #1 28/136 TOUCH | WILLITS | ETL.1330.TOWR | 2024-04-14 | 2024-04-14 | 2025-04-07 | On-Time |  | 2024-10-14 | 2025-04-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46493185 | T2 CORTINA-MNDCNO #1 28/136 TOUCH | ICQ
LC | 129684092 | 013/052 | T3 PITTSBURG-EASTSHORE 13/52 RPL INSS | CONCORD | ETL.5462.INSL | 2024-10-14 | 2024-10-14 | 2024-10-14 | Past Due |  | 2025-04-14 | 2025-04-14 | 532 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35559807 | T3 DI PITTSBURG-EASTSHORE RPL INSS IN 3 | 93K
LC | 129687080 | 008/112 | T3 MIDDLE FORK #1 008/112 CGI LAND | SACTO | ETL.8405.POLE.WOOD | 2024-10-14 | 2024-10-14 | 2024-10-14 | Past Due |  | 2025-01-14 | 2025-04-14 | 625 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW TNT CGI OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 129687081 | 008/113 | T3 MIDDLE FORK #1 008/113 CGI LAND | SACTO | ETL.8405.POLE.WOOD | 2024-10-14 | 2024-10-14 | 2024-10-14 | Past Due |  | 2025-01-14 | 2025-04-14 | 625 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW TNT CGI OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 123341672 | 023/128 | T3NT BAHIA-MORAGA 023/128 RPL INSS | CONCORD | ETL.4340.INSL.NCER | 2022-04-15 | 2022-04-15 | 2024-04-27 | On-Time |  | 2025-04-15 | 2025-04-15 | 532 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB XMPT TR3 PRTO NTDE | No Good/Out of Stdrd | Insulator-Steel | Replace | 31626482 | T3 BAHIA-MORAGA 023/128 RPL INSS | 93K
LC | 123370615 | :014/074 | T2NT DI CZY HRSE CNYN-SLS 14/74 RPR STRT | MOSSLNDG | ETL.2900.TOWR | 2022-04-19 | 2022-04-15 | 2023-06-28 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45590581 | T2 DI CRZY HRSE CNYN-SLNS 14/74 RPR STRT | ICQ
LC | 123371800 | 001/013 | T2NT DI BALCH-SANGER 1/13 COMPLETE | FRESNO | ETL.1050.TOWR | 2022-04-19 | 2022-04-15 | 2023-05-15 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45616520 | T2 DI BALCH-SANGER 1/13 BENT STEEL | ICQ
LC | 123391182 | :014/076 | T2NT DI CZY HRS-CYN SLS :14/76 BNT STEEL | MOSSLNDG | ETL.2900.TOWR | 2022-04-22 | 2022-04-15 | 2023-06-28 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45590586 | T2 DI CZY HRS-CYN SLS :14/76 BNT STEEL | ICQ
LC | 123451958 | 032/269 | T3NT DI PIT #1-COTTONWD 032/269 UNBURY | TABLEMTN | ETL.5390.TOWR | 2022-04-28 | 2022-04-15 | 2023-07-12 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB NTDE | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45639705 | T3 DI PIT #1-COTTONWOOD 032/269 REGRADE | ICQ
LC | 123484326 | 031/262 | T3NT DI RND MTN-CTWD #3 31/262 COMPLETE | TABLEMTN | ETL.5650.TOWR | 2022-05-03 | 2022-04-15 | 2023-07-12 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648238 | T3 DI RND MTN-CTTNWD #3 31/262 BNT STEEL | ICQ
LC | 123491150 | 012/113 | T3NT DI DRUM-RIO OSO#1 12/113 BENT STEEL | SACTO | ETL.1420.TOWR | 2022-05-03 | 2022-04-15 | 2023-07-05 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45599996 | T3 DI DRUM-RIO OSO#1 12/113 BENT STEEL | ICQ
LC | 123491264 | 030/250 | T3NT DI RND MTN-CTTNWD #3 30/250 BNT STL | TABLEMTN | ETL.5650.TOWR | 2022-05-03 | 2022-04-15 | 2023-07-17 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648235 | T3 DI RND MTN-CTTNWD #3 30/250 BNT STEEL | ICQ
LC | 123492770 | 053/400 | T2NT DI BRDGVLLE-CTTNWD 53/400 BNT STEEL | TABLEMTN | ETL.1110.TOWR | 2022-05-04 | 2022-04-15 | 2023-08-11 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45582375 | T2 DI BRDGVLLE-CTTNWD 53/400 BENT STEEL | ICQ
LC | 128544408 | 023/002 | T2 PHILO JCT-ELK 023/002 WASH INSW | WILLITS | ETL.7780.INSL.CERA | 2024-04-15 | 2024-04-15 | 2024-05-22 | On-Time |  | 2025-04-15 | 2025-04-15 | 622 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | Contaminated | Insulator | Ground Wash | 46250767 | T2 PHILO JCT-ELK 023/002 WASH INSW | ICD
LC | 128544453 | 035/292 | T2 KILARC-VOLTA 60KV TIE 35/292 RPL DMPS | TABLEMTN | ETL.7310.INSL.CERA | 2024-04-15 | 2024-04-15 | 2025-02-17 | On-Time |  | 2025-04-15 | 2025-04-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Damper-Steel | Replace | 46452761 | T2 KILARC-VOLTA 60KV TIE 35/292 RPL DMPS | ICS
LC | 128544690 | 001/002 | T2 POTTER VALLEY-WILLITS 1/2 RPR GYWW | WILLITS | ETL.7820.POLE.NWOD | 2024-04-15 | 2024-04-15 | 2025-02-18 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46308302 | T2 POTTER VALLEY-WILLITS 1/2 RPR GYWW | ICW
LC | 128545131 | 014/085 | T2NT EI STNISLAUS-MNTEC#2 14/85 RPR STRT | VICTOR | ETL.3820.TOWR | 2024-04-15 | 2024-04-15 | 2025-03-19 | On-Time |  | 2027-04-15 | 2025-04-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416347 | T2NT EI STNISLAUS-MNTEC#2 14/85 RPR STRT | ICQ
LC | 128545133 | 014/085 | T2 EI STANISLAUS-MANTEC#2 14/85 RPR FOND | VICTOR | ETL.3820.TOWR | 2024-04-15 | 2024-04-15 | 2025-03-19 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46416348 | T2 EI STANISLAUS-MANTEC#2 14/85 RPR FOND | ICQ
LC | 128545351 | 006/007 | T2 EI SALMON CREEK TAP 06/007 RPL INSW | LAKEVLLE | ETL.6981.INSL | 2024-04-15 | 2024-04-15 | 2025-04-10 | On-Time |  | 2025-04-15 | 2025-04-15 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572897 | T2 EI SALMON CREEK TAP 06/007 RPL INSW | 93I
LC | 128545432 | 014/086 | T2 EI STNISLAUS-MNTEC#2 14/86 RPR FOND | VICTOR | ETL.3820.TOWR | 2024-04-15 | 2024-04-15 | 2025-03-19 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46416349 | T2 EI STNISLAUS-MNTEC#2 14/86 RPR FOND | ICQ
LC | 128545454 | 018/133 | T2 WV CAYUCOS-CAMBRIA 18/133 INS GYWW | PISMOBCH | ETL.8560.POLE.STPS | 2024-04-15 | 2024-04-15 | 2025-02-21 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | Missing | Guy Wire-Wood | Install | 46391106 | T2 WV CAYUCOS-CAMBRIA 18/133 INS GYWW | ICW
LC | 128545483 | 005/045 | T2 EI TGR CRK-VLLY SPRNGS 5/45 RPL INSS | VICTOR | ETL.5790.INSL.CERA | 2024-04-15 | 2024-04-15 | 2025-03-11 | On-Time |  | 2025-04-15 | 2025-04-15 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593059 | T2 EI TGR CRK-VLLY SPRINGS 4/33 RPL INSS | 93K
LC | 128545624 | 015/087 | T2 EI STNISLAUS-MNTEC#2 15/87 RPR FOND | VICTOR | ETL.3820.TOWR | 2024-04-15 | 2024-04-15 | 2025-03-19 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46416350 | T2 EI STNISLAUS-MNTEC#2 15/87 RPR FOND | ICQ
LC | 128545682 | 006/006 | T2 EI SALMON CREEK TAP 06/006 RPL INSW | LAKEVLLE | ETL.6981.INSL | 2024-04-15 | 2024-04-15 | 2025-04-10 | On-Time |  | 2025-04-15 | 2025-04-15 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572896 | T2 EI SALMON CREEK TAP 06/006 RPL INSW | 93I
LC | 128545727 | 002/019 | T2 OLEUM- G #1 2/019 RPL INSS | CONCORD | ETL.3150.INSL.CERA | 2024-04-15 | 2024-04-15 | 2025-04-15 | On-Time |  | 2025-04-15 | 2025-04-15 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575048 | T2 OLEUM- G #1 2/019 RPL INSS. | 93K
LC | 128545842 | 015/088 | T2NT EI STNISLAUS-MNTEC#2 15/88 RPR FOND | VICTOR | ETL.3820.TOWR | 2024-04-15 | 2024-04-15 | 2025-03-19 | On-Time |  | 2027-04-15 | 2025-04-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46416352 | T2NT EI STNISLAUS-MNTEC#2 15/88 RPR FOND | ICQ
LC | 128546039 | 005/044 | T2 EI TGR CRK-VLLY SPRNGS 5/44 RPL INSS | VICTOR | ETL.5790.INSL.CERA | 2024-04-15 | 2024-04-15 | 2025-03-11 | On-Time |  | 2025-04-15 | 2025-04-15 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593059 | T2 EI TGR CRK-VLLY SPRINGS 4/33 RPL INSS | 93K
LC | 128546057 | 007/019 | T2 EI BRCBRG JCT-MRPSA TAP 7/19 RPR ANCW | FRESNO | ETL.8651.POLE.WOOD | 2024-04-15 | 2024-04-15 | 2025-03-29 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46298279 | T2 EI BRCBRG JCT-MRPSA TAP 7/19 RPR ANCW | ICW
LC | 128546113 | 005/044 | T2 EI ELECTRA-BELLOTA 5/44 RPL INSS | VICTOR | ETL.4670.INSL.CERA | 2024-04-15 | 2024-04-15 | 2025-03-18 | On-Time |  | 2025-04-15 | 2025-04-15 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593221 | T2 EI ELECTRA-BELLOTA 002/024 RPL INSS | 93K
LC | 128546125 | ;000/032 | T2 EI CARIBOU #2 ;000/032 RPR JMPW | TABLEMTN | ETL.6280.INSL.NCER | 2024-04-15 | 2024-04-15 | 2025-04-08 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Jumper-Wood | Repair | 46337202 | T2 EI CARIBOU #2 ;000/032 RPR JMPW | ICW
LC | 128546133 | ;002/023 | T2 EI CARIBOU #2 ;2/23 RPL HRDD | TABLEMTN | ETL.6280.POLE.NWOD | 2024-04-15 | 2024-04-15 | 2025-03-06 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46337203 | T2 EI CARIBOU #2 ;002/023 RPL HRDD | ICW
LC | 128546137 | ;001/014 | T2 EI CARIBOU #2 ;01/14 RPR GYWW | TABLEMTN | ETL.6280.POLE.STPS | 2024-04-15 | 2024-04-15 | 2024-07-16 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46283007 | T2 EI CARIBOU #2 ;01/14 RPR GYWW | ICW
LC | 128546411 | 012/148 | T2 EI W PNT-VLLY SPRNG 12/148 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-04-15 | 2024-04-15 | 2025-02-07 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327600 | T2 EI W PNT-VLLY SPRNG 12/148 RPR GYWW | ICW
LC | 128546562 | 005/043 | T2 EI TGR CRK-VLLY SPRNGS 5/43 RPL INSS | VICTOR | ETL.5790.INSL.CERA | 2024-04-15 | 2024-04-15 | 2025-03-11 | On-Time |  | 2025-04-15 | 2025-04-15 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593059 | T2 EI TGR CRK-VLLY SPRINGS 4/33 RPL INSS | 93K
LC | 128546570 | 005/043 | T2 EI ELECTRA-BELLOTA 5/43 RPL INSS | VICTOR | ETL.4670.INSL.CERA | 2024-04-15 | 2024-04-15 | 2025-03-18 | On-Time |  | 2025-04-15 | 2025-04-15 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593221 | T2 EI ELECTRA-BELLOTA 002/024 RPL INSS | 93K
LC | 128546872 | 006/108 | T2 EI SSQC-SANTA YNEZ SS 6/108 RPL STRW | PISMOBCH | ETL.3700.INSL.CERA | 2024-04-15 | 2024-04-15 | 2025-02-11 | On-Time |  | 2025-04-15 | 2025-04-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35573777 | T2 EI SSQC-SANTA YNEZ SS 6/108 RPL INSW | 70Y
LC | 128546936 | 005/042 | T2 EI TGR CRK-VLLY SPRNGS 5/42 RPL INSS | VICTOR | ETL.5790.INSL.CERA | 2024-04-15 | 2024-04-15 | 2025-03-11 | On-Time |  | 2025-04-15 | 2025-04-15 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593059 | T2 EI TGR CRK-VLLY SPRINGS 4/33 RPL INSS | 93K
LC | 128546937 | 005/042 | T2 EI ELECTRA-BELLOTA 5/42 RPL INSS | VICTOR | ETL.4670.INSL.CERA | 2024-04-15 | 2024-04-15 | 2025-03-18 | On-Time |  | 2025-04-15 | 2025-04-15 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593221 | T2 EI ELECTRA-BELLOTA 002/024 RPL INSS | 93K
LC | 128547047 | 017/347 | T2 COLGATE-PALERMO 17/347 GO95 | SACTO | ETL.6500.POLE.WOOD | 2024-04-15 | 2024-04-15 | 2025-05-23 | Past Due |  | 2025-04-15 | 2025-04-15 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35548512 | T2 COLGATE-PALERMO 17/347 GO95 | 93G
LC | 128547122 | 005/041 | T2 EI TGR CRK-VLLY SPRNGS 5/41 RPL INSS | VICTOR | ETL.5790.INSL.CERA | 2024-04-15 | 2024-04-15 | 2025-03-11 | On-Time |  | 2025-04-15 | 2025-04-15 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593059 | T2 EI TGR CRK-VLLY SPRINGS 4/33 RPL INSS | 93K
LC | 128547173 | 022/004 | T2 BRDGVLE-GRBRVILLE 22/04 RPL STRW | EUREKA | ETL.6220.POLE.WOOD | 2024-04-15 | 2024-04-15 | 2024-04-15 | Past Due |  | 2025-04-15 | 2025-04-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572120 | T2 EI BRDGVLE-GRBRVILLE 22/04 RPL STRW | 70Y
LC | 128547340 | 011/116 | T2 PIT #5-ROUND MTN #2 11/116 COTTER | TABLEMTN | ETL.5430.INSL.NCER | 2024-04-15 | 2024-04-15 | 2025-03-08 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46454321 | T2 PIT #5-ROUND MTN #2 11/116 COTTER | ICW
LC | 128547445 | 007/012 | T2 EI BRCBRG JCT-MRPSA TAP 7/12 RPR ANCW | FRESNO | ETL.8651.POLE.WOOD | 2024-04-15 | 2024-04-15 | 2024-09-04 | On-Time |  | 2024-10-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46234445 | T2 EI BRCBRG JCT-MRPSA TAP 7/12 RPR ANCW | ICW
LC | 128547484 | 005/040 | T2 EI TGR CRK-VLLY SPRNGS 5/40 RPL INSS | VICTOR | ETL.5790.INSL.NCER | 2024-04-15 | 2024-04-15 | 2025-03-11 | On-Time |  | 2024-10-15 | 2025-04-15 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593059 | T2 EI TGR CRK-VLLY SPRINGS 4/33 RPL INSS | 93K
LC | 128547520 | 039/000 | T2 EI FORT ROSS-GUALALA 39/00 RPR INSW | LAKEVLLE | ETL.6980.INSL.NCER | 2024-04-15 | 2024-04-15 | 2025-03-21 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46305931 | T2 EI FORT ROSS-GUALALA 39/00 RPR INSW | ICW
LC | 128548033 | 010/082 | T2 EI SLT SPRNGS-TGR CRK 10/82 RPR FOND | VICTOR | ETL.3500.TOWR | 2024-04-15 | 2024-04-15 | 2025-03-27 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416354 | T2 EI SLT SPRNGS-TGR CRK 10/82 RPR FOND | ICQ
LC | 128548205 | 037/003 | T2 EI FORT ROSS-GUALALA 37/003 RPR ANCW | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-04-15 | 2024-04-15 | 2025-02-07 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46305930 | T2 EI FORT ROSS-GUALALA 37/003 RPR ANCW | ICW
LC | 128548237 | 000/001C | T2 ELECTRA-BELLOTA 0/1C COMPLETE | VICTOR | ETL.4670.POLE.NWOD | 2024-04-15 | 2024-04-15 | 2025-03-17 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REAR ACCL COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46416355 | T2 EI ELECTRA-BELLOTA 0/1C RPR GYWT | ICQ
LC | 128548339 | 030/001 | T2 EI RIO DLL JCT-BRDGVLLE 30/1 RPR POLE | EUREKA | ETL.7850.POLE.WOOD | 2024-04-15 | 2024-04-15 | 2025-04-02 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46345758 | T2 EI RIO DLL JCT-BRDGVLLE 30/1 RPR POLE | ICW
LC | 128548362 | 031/152 | T2 EI RND MTN-TBL MN #1 31/152 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-15 | 2024-04-15 | 2024-11-20 | On-Time |  | 2025-04-15 | 2025-04-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128548369 | 082/419B | T2 EI MALIN-ROUND MTN#2 82/419B RPR INSS | TABLEMTN | ETL.6020.INSL.NCER | 2024-04-15 | 2024-04-15 | 2024-08-27 | On-Time |  | 2025-04-15 | 2025-04-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46299479 | T2 EI MALIN-ROUND MTN#2 82/419B RPR INSS | ICS
LC | 128548390 | 030/001 | T2 EI RIO DLL JCT-BRDGVLLE 30/1 RPL INSW | EUREKA | ETL.7850.INSL.CERA | 2024-04-15 | 2024-04-15 | 2025-06-15 | Past Due |  | 2025-04-15 | 2025-04-15 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573035 | T2 EI RIO DLL JCT-BRDGVLLE 30/1 RPL INSW | 93I
LC | 128548391 | 030/000 | T2 EI RIO DLL JCT-BRDGVLLE 30/0 RPL INSW | EUREKA | ETL.7850.INSL.CERA | 2024-04-15 | 2024-04-15 | 2025-06-15 | Past Due |  | 2025-04-15 | 2025-04-15 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573032 | T2 EI RIO DLL JCT-BRDGVLLE 30/0 RPL INSW | 93I
LC | 128548393 | 030/002 | T2 RIO DLL JCT-BRDGVLLE 30/2 RPR STRW | EUREKA | ETL.7850.POLE.WOOD | 2024-04-15 | 2024-04-15 | 2024-04-15 | Past Due |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair
LC | 128548460 | 021/005 | T2 BRDGVLE-GRBRVILLE 21/005 RPL INSW | EUREKA | ETL.6220.INSL.CERA | 2024-04-15 | 2024-04-15 | 2024-04-15 | Past Due |  | 2025-04-15 | 2025-04-15 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572079 | T2 EI BRDGVLE-GRBRVILLE 21/005 RPL INSW | 93I
LC | 128548546 | 058/425D | T2 EI BRDGEVLE-CTWD 58/425D PRP FOND | EUREKA | ETL.1110.POLE.NWOD | 2024-04-15 | 2024-04-15 | 2025-02-27 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46289232 | T2 EI BRDGEVLE-CTWD 58/425D PRP FOND | ICQ
LC | 128548634 | 007/001 | T2 SALMON CREEK TAP 07/001 RPR INSW | LAKEVLLE | ETL.6981.INSL | 2024-04-15 | 2024-04-15 | 2025-04-09 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46305929 | T2 EI SALMON CREEK TAP 07/001 RPR INSW | ICW
LC | 128548639 | 016/164 | T2 RND MNTAIN-COTTONWOOD #2 16/164 TOUCH | TABLEMTN | ETL.5640.TOWR | 2024-04-15 | 2024-04-15 | 2024-04-15 | Past Due |  | 2024-10-15 | 2025-04-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491895 | T2 EI RND MTN-CTTNWD #2 16/164 TOUCH | ICQ
LC | 128548652 | 016/163 | T2 EI RND MTN-CTTNWD #2 16/163 TOUCH | TABLEMTN | ETL.5640.TOWR | 2024-04-15 | 2024-04-15 | 2025-03-08 | On-Time |  | 2024-10-15 | 2025-04-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478118 | T2 EI RND MTN-CTTNWD #2 16/163 TOUCH | ICQ
LC | 128548695 | 017/011 | T2 EI TRINITY-MAPLE CREEK 17/11 RPR STRW | EUREKA | ETL.8170.POLE.WOOD | 2024-04-15 | 2024-04-15 | 2024-04-15 | Past Due |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46493391 | T2 EI TRINITY-MAPLE CREEK 17/11 RPR STRW | ICW
LC | 128548696 | 017/007 | T2 EI TRINITY-MAPLE CREEK 17/7 RPR POLE | EUREKA | ETL.8170.POLE.WOOD | 2024-04-15 | 2024-04-15 | 2024-04-15 | Past Due |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46493390 | T2 EI TRINITY-MAPLE CREEK 17/7 RPR POLE | ICW
LC | 128549307 | 012/119 | T2 EI PIT #5-ROUND MTN #2 12/119 COTTER | TABLEMTN | ETL.5430.INSL.CERA | 2024-04-15 | 2024-04-15 | 2025-03-07 | On-Time |  | 2025-04-15 | 2025-04-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46443293 | T2 EI PIT #5-ROUND MTN #2 12/119 COTTER | ICS
LC | 128550691 | 022/003 | T2 DI MDCNO WLTS FT BRG 22/03 RPR GYWW | WILLITS | ETL.7550.POLE.NWOD | 2024-04-16 | 2024-04-15 | 2025-02-07 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46308303 | T2 DI MDCNO WLTS FT BRG 22/03 RPR GYWW | ICW
LC | 128550838 | 006/113 | T2 EI SSQUOC-SNTA YNZ SS 6/113 RPL POLE | PISMOBCH | ETL.3700.POLE.WOOD | 2024-04-16 | 2024-04-15 | 2025-02-12 | On-Time |  | 2025-04-15 | 2025-04-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35573779 | T2 EI SSQUOC-SNTA YNZ SS 6/113 RPL POLE | 70Y
LC | 128577811 | 033/191 | T2 DI TEMBLOR-SLO 33/191 COTTER | PISMOBCH | ETL.3960.INSL.CERA | 2024-04-18 | 2024-04-15 | 2024-07-24 | On-Time |  | 2025-04-15 | 2025-04-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46250306 | T2 DI TEMBLOR-SLO 33/191 COTTER | ICS
LC | 128581366 | 039/160 | T2 DI DIABLO-MWY #2 39/160 RPR SHLS | PISMOBCH | ETL.5970.TOWR | 2024-04-19 | 2024-04-15 | 2025-04-11 | On-Time |  | 2025-04-15 | 2025-04-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329580 | T2 DI DIABLO-MWY #2 39/160 RPR SHLS | ICS
LC | 128581675 | 047/233 | T2 DI MALIN-RD MTN#2 47/233 RPR SPCR | TABLEMTN | ETL.6020.INSL.CERA | 2024-04-19 | 2024-04-15 | 2025-02-09 | On-Time |  | 2025-04-15 | 2025-04-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46337580 | T2 DI MALIN-RD MTN#2 47/233 RPR SPCR | ICS
LC | 128581722 | 047/233 | T2 DI MALIN-RD MTN#2 47/233 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-04-19 | 2024-04-15 | 2025-03-24 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381024 | T2 DI MALIN-RD MTN#2 47/233 RPR FOND | ICQ
LC | 128581870 | 009/092 | T2 DI PIT#5RND MTN#1 09/092 RPL INSW | TABLEMTN | ETL.5420.INSL.CERA | 2024-04-19 | 2024-04-15 | 2025-04-09 | On-Time |  | 2025-04-15 | 2025-04-15 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35614927 | T2 DI PIT#5RND MTN#1 09/092 RPL INSW | 93I
LC | 128582268 | 030/010 | T2 DI FLTN HPLND 30/010 RPL STRW | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-04-19 | 2024-04-15 | 2025-03-20 | On-Time |  | 2025-04-15 | 2025-04-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574257 | T2 DI FLTN HPLND 30/010 RPL STRW | 70Y
LC | 128582307 | 017/147 | T2 DI CRAG VIEW-CASCADE 17/147 RPR OPGW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-15 | 2025-03-21 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Wood | Repair | 46454324 | T2 DI CRAG VIEW-CASCADE 17/147 RPR OPGW | ICW
LC | 128582309 | 017/147 | T2 DI CRAG VIEW-CASCADE 17/147R RPR STRW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-15 | 2024-05-15 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46240013 | T2 DI CRAG VIEW-CASCADE 17/147R RPR STRW | ICW
LC | 128582344 | 017/147 | T2 DI CRAG VIEW-CASCADE 17/147L RPR STRW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-15 | 2025-03-21 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454325 | T2 DI CRAG VIEW-CASCADE 17/147L RPR STRW | ICW
LC | 128582655 | 011/267 | T2 DI SANTA ROSA-CORN 11/267 TOUCH | LAKEVLLE | ETL.4309.POLE.NWOD | 2024-04-19 | 2024-04-15 | 2025-06-23 | Past Due |  | 2024-10-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46505447 | T2 DI SANTA ROSA-CORN 11/267 TOUCH | ICW
LC | 128582713 | 017/143 | T2 DI CRAG VIEW-CASCADE 17/143 RPR OPGW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-15 | 2025-03-21 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Wood | Repair | 46454327 | T2 DI CRAG VIEW-CASCADE 17/143 RPR OPGW | ICW
LC | 128582821 | 017/142 | T2 DI CRAG VW-CASC 17/142R RPR OPGW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-15 | 2025-03-21 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | OPGW - Wood | Repair | 46454328 | T2 DI CRAG VW-CASC 17/142R RPR OPGW | ICW
LC | 128583006 | 022/004 | T2 DI MNDCNO-WLLTS-FRT BRG 22/4 RPR JUMW | WILLITS | ETL.7550.INSL.NCER | 2024-04-19 | 2024-04-15 | 2025-04-10 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46239217 | T2 DI MNDCNO-WLLTS-FRT BRG 22/4 RPR JUMW | ICW
LC | 128583065 | 019/164 | T2 DI CRAG VW-CASC 19/164R RPR OPGW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-15 | 2025-03-21 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Wood | Repair | 46454330 | T2 DI CRAG VW-CASC 19/164R RPR OPGW | ICW
LC | 128583289 | 015/131 | T2 DI CRAG VIEW-CASCADE 15/131 RPR OPGW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-15 | 2025-01-21 | On-Time |  | 2025-04-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Wood | Repair | 46454372 | T2 DI CRAG VIEW-CASCADE 15/131 RPR OPGW | ICW
LC | 128583822 | 062/312 | T2 DI MALIN-RND MNTN #2 62/312 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-19 | 2024-04-15 | 2025-03-25 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381390 | T2 DI MALIN-RND MNTN #2 62/312 RPR GYWT | ICQ
LC | 128584171 | 005/086 | T2 DI CNTERVILLE-TABLE MTN 5/86 RPR GYWW | TABLEMTN | ETL.6320.POLE.NWOD | 2024-04-19 | 2024-04-15 | 2024-05-14 | On-Time |  | 2024-10-15 | 2025-04-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46240003 | T2 DI CNTERVILLE-TABLE MTN 5/86 RPR GYWW | ICW
LC | 128584711 | 048/238 | T2 DI MALIN-RND MNTIN #2 48/238 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-04-19 | 2024-04-15 | 2025-03-21 | On-Time |  | 2025-04-15 | 2025-04-15 | 93Z | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716724 | T2 EI MALIN-RND MTN #2 RPL ANCT 7 TWRS | 93Z
LC | 128584862 | 047/235 | T2 DI MALIN-RND MTN#2 47/235 RMV VEG | TABLEMTN | ETL.6020.TOWR | 2024-04-19 | 2024-04-15 | 2024-10-29 | On-Time |  | 2024-10-15 | 2025-04-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128584865 | 040/162 | T2 DI DIABLO-MWY #3 40/162 RPL HRDT | PISMOBCH | ETL.5980.TOWR | 2024-04-19 | 2024-04-15 | 2025-04-04 | On-Time |  | 2025-04-15 | 2025-04-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46396364 | T2 DI DIABLO-MWY #3 40/162 RPL HRDT | ICQ
LC | 123344062 | 021/093 | T2NT EI MRR BY-MS 21/93 RPR FOND | PISMOBCH | ETL.5290.TOWR | 2022-04-16 | 2022-04-16 | 2023-07-12 | On-Time |  | 2025-04-16 | 2025-04-16 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45639652 | T2 EI MRR BY-MS 21/93 RPR FOND | ICQ
LC | 128549893 | 004/037 | T2 EI UKIAH-HPLND-CLVRDL 04/37 RPR GYWW | WILLITS | ETL.4050.POLE.WOOD | 2024-04-16 | 2024-04-16 | 2024-12-23 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46414826 | T2 EI UKIAH-HPLND-CLVRDL 04/37 RPR GYWW | ICW
LC | 128550771 | 000/009 | T2 PLACER-GOLD HILL #1 00/09 TOUCH | SACTO | ETL.3340.TOWR | 2024-04-16 | 2024-04-16 | 2025-02-25 | On-Time |  | 2024-10-16 | 2025-04-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46460018 | T2 PLACER-GOLD HILL #1 00/09 RPR STRT | ICQ
LC | 128550967 | 005/037 | T2 EI VALLEY SPRNGS-BLLOTA 5/37 RPL INSS | VICTOR | ETL.5860.INSL.CERA | 2024-04-16 | 2024-04-16 | 2025-03-24 | On-Time |  | 2025-04-16 | 2025-04-16 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593222 | T2 EI VLY SPRNGS-BELLTA 04/28 RPL INSS | 93K
LC | 128551148 | 065/002 | T2 WV HUMBOLDT-TRINITY 65/002 RPL ANCW | EUREKA | ETL.1820.POLE.WDPS | 2024-04-16 | 2024-04-16 | 2025-04-09 | On-Time |  | 2025-04-16 | 2025-04-16 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574772 | T2 WV COTTONWD-HUMBOLDT 65/002 RPL ANCW | 93E
LC | 128551426 | 016/007 | T2 EI OAKHURST TAP 016/007 RPR GYWW | FRESNO | ETL.1252.POLE.NWOD | 2024-04-16 | 2024-04-16 | 2025-03-03 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298282 | T2 EI OAKHURST TAP 016/007 RPR GYWW | ICW
LC | 128552024 | 016/005 | T2 EI OAKHURST TAP 016/005 RPR INSW | FRESNO | ETL.1252.INSL.NCER | 2024-04-16 | 2024-04-16 | 2025-03-04 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298283 | T2 EI OAKHURST TAP 016/005 RPR INSW | ICW
LC | 128553342 | 034/165 | T2 CORTINA-MNDCN #1 34/165 RMV NEST | WILLITS | ETL.1330.TOWR | 2024-04-16 | 2024-04-16 | 2024-04-16 | Past Due |  | 2025-04-16 | 2025-04-16 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46414830 | T2 EI CORTINA-MNDCN #1 34/165 RMV NEST | ICS
LC | 128554230 | 045/355 | T2 BRIDGEVILL-CTTNWD 45/355L COMPLETE | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-16 | 2024-04-16 | 2025-04-07 | On-Time |  | 2025-04-16 | 2025-04-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46351477 | T2 EI BRIDGEVILL-CTTNWD 45/355L RPR GYWT | ICQ
LC | 128554384 | 011/163 | T2 EI SSQC-SANTA YNEZ SS 11/163 RPL POLE | PISMOBCH | ETL.3700.POLE.WOOD | 2024-04-16 | 2024-04-16 | 2025-04-02 | On-Time |  | 2025-04-16 | 2025-04-16 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCL ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573786 | T2 EI SSQC-SANTA YNEZ SS 11/163 RPL POLE | 70Y
LC | 128554410 | 011/162 | T2 EI SSQC-SANTA YNEZ SS 11/162 RPL POLE | PISMOBCH | ETL.3700.POLE.WOOD | 2024-04-16 | 2024-04-16 | 2025-04-03 | On-Time |  | 2025-04-16 | 2025-04-16 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35573785 | T2 EI SSQC-SANTA YNEZ SS 11/162 RPL POLE | 70Y
LC | 128554494 | 033/006 | T2 EI FORT ROSS-GUALALA 033/006 RMV VEG | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-04-16 | 2024-04-16 | 2025-02-03 | On-Time |  | 2025-04-16 | 2025-04-16 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128554613 | 033/004 | T2 EI FORT ROSS-GUALALA 033/004 COTTER | LAKEVLLE | ETL.6980.INSL.NCER | 2024-04-16 | 2024-04-16 | 2025-03-03 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46305932 | T2 EI FORT ROSS-GUALALA 033/004 COTTER | ICW
LC | 128554651 | 029/566 | T2 HAT CREEK #1-WESTWOOD 029/566 GO95 | TABLEMTN | ETL.7030.POLE.WOOD | 2024-04-16 | 2024-04-16 | 2025-04-15 | On-Time |  | 2025-04-16 | 2025-04-16 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35574768 | T2 HAT CREEK #1-WESTWOOD 029/566 GO95 | 93G
LC | 128554655 | 029/572 | T2 HAT CREEK #1-WESTWOOD 029/572 GO95 | TABLEMTN | ETL.7030.POLE.WOOD | 2024-04-16 | 2024-04-16 | 2025-04-15 | On-Time |  | 2025-04-16 | 2025-04-16 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCM COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35574769 | T2 HAT CREEK #1-WESTWOOD 029/572 GO95 | 93G
LC | 128555033 | 062/313 | T2NT EI MALIN-RND MTN #2 62/313 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-16 | 2024-04-16 | 2025-03-25 | On-Time |  | 2027-04-16 | 2025-04-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381382 | T2NT EI MALIN-RND MTN #2 62/313 RPR GYWT | ICQ
LC | 128555034 | 063/314 | T2 MALIN-RND MTN #2 063/314 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-04-16 | 2024-04-16 | 2025-03-25 | On-Time |  | 2025-04-16 | 2025-04-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381383 | T2 EI MALIN-RND MTN #2 063/314 RPR GYWT | ICQ
LC | 128555036 | 063/315 | T2 MALIN-RND MTN #2 063/315 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-04-16 | 2024-04-16 | 2025-03-25 | On-Time |  | 2025-04-16 | 2025-04-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381384 | T2 EI MALIN-RND MTN #2 063/315 RPR GYWT | ICQ
LC | 128555038 | 061/304 | T2 EI MALIN-ROUND MTN #2 61/304 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-16 | 2024-04-16 | 2025-03-25 | On-Time |  | 2025-04-16 | 2025-04-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381385 | T2 EI MALIN-ROUND MTN #2 61/304 RPR GYWT | ICQ
LC | 128555040 | 061/307 | T2NT EI MALIN-RND MTN #2 61/307 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-16 | 2024-04-16 | 2025-03-25 | On-Time |  | 2027-04-16 | 2025-04-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381386 | T2NT EI MALIN-RND MTN #2 61/307 RPR GYWT | ICQ
LC | 128555049 | 033/005 | T2 EI FORT ROSS-GUALALA 033/005 RMV VEG | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-04-16 | 2024-04-16 | 2025-02-03 | On-Time |  | 2025-04-16 | 2025-04-16 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128555050 | 062/311 | T2NT EI MALIN-RND MTN #2 62/311 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-16 | 2024-04-16 | 2025-03-25 | On-Time |  | 2027-04-16 | 2025-04-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381387 | T2NT EI MALIN-RND MTN #2 62/311 RPR GYWT | ICQ
LC | 128555364 | 030/011 | T2 EI RIO DLL JCT-BRDGVLE 30/11 RPL HRDW | EUREKA | ETL.7850.POLE.WOOD | 2024-04-16 | 2024-04-16 | 2025-04-02 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345763 | T2 EI RIO DLL JCT-BRDGVLE 30/11 RPL HRDW | ICW
LC | 128555368 | 031/000 | T2 RIO DLL JCT-BRDGVLLE 31/0 RPL INSW | EUREKA | ETL.7850.INSL.CERA | 2024-04-16 | 2024-04-16 | 2025-06-15 | Past Due |  | 2025-04-16 | 2025-04-16 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573037 | T2 EI RIO DLL JCT-BRDGVLLE 31/0 RPL INSW | 93I
LC | 128555370 | 030/004 | T2 EI RIO DLL JCT-BRDGVLLE 30/4 RMV VEG | EUREKA | ETL.7850.POLE.WOOD | 2024-04-16 | 2024-04-16 | 2025-02-19 | On-Time |  | 2025-04-16 | 2025-04-16 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128555933 | 015/133 | T2 DI CRAG VIEW-CASCADE -15/133L COTTER | TABLEMTN | ETL.1350.INSL.NCER | 2024-04-16 | 2024-04-16 | 2025-01-21 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46454369 | T2 DI CRAG VIEW-CASCADE -15/133L COTTER | ICW
LC | 128556270 | 007/004 | T2 BRCBRG JCT-MRPSA TAP 7/4 COMPLETE | FRESNO | ETL.8651.POLE.WOOD | 2024-04-17 | 2024-04-16 | 2025-03-29 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46298284 | T2 EI BRCBRG JCT-MRPSA TAP 7/4 RPR POLE | ICW
LC | 128556281 | 007/001 | T2 EI BRCBRG JCT-MRPSA TAP 7/1 RPR INSW | FRESNO | ETL.8651.INSL.NCER | 2024-04-17 | 2024-04-16 | 2024-09-04 | On-Time |  | 2024-07-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46234446 | T2 EI BRCBRG JCT-MRPSA TAP 7/1 RPR INSW | ICW
LC | 128567881 | 000/007 | T2 DI LAYTONVILLE-COVEL 0/7 RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-04-17 | 2024-04-16 | 2024-07-10 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46236401 | T2 DI LAYTONVILLE-COVEL 0/7 RPR JUMW | ICW
LC | 128568046 | 003/020 | T2 DI TRINITY-MPLE CREEK 3/20L RPR ANCW | EUREKA | ETL.8170.POLE.WDPS | 2024-04-17 | 2024-04-16 | 2025-02-24 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46345760 | T2 DI TRINITY-MPLE CREEK 3/20L RPR ANCW | ICW
LC | 128568047 | 003/020 | T2 DI TRINITY-MPLE CREEK 3/20C RPR ANCW | EUREKA | ETL.8170.POLE.WDPS | 2024-04-17 | 2024-04-16 | 2025-02-24 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46345761 | T2 DI TRINITY-MPLE CREEK 3/20C RPR ANCW | ICW
LC | 128568048 | 003/020 | T2 DI TRINITY-MPLE CREEK 3/20R RPR ANCW | EUREKA | ETL.8170.POLE.WDPS | 2024-04-17 | 2024-04-16 | 2025-02-24 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46345762 | T2 DI TRINITY-MPLE CREEK 3/20R RPR ANCW | ICW
LC | 128568054 | 023/005 | T2 DI GRBRVIL-LAYTNVIL 23/05 RPR JUMW | WILLITS | ETL.8365.INSL.CERA | 2024-04-17 | 2024-04-16 | 2024-08-13 | On-Time |  | 2024-07-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46236311 | T2 DI GRBRVIL-LAYTNVIL 23/05 RPR JUMW | ICW
LC | 128568056 | 023/005 | T2 DI GRBRVIL-LAYTNVIL 23/05 RPR GYWW | WILLITS | ETL.8365.POLE.WOOD | 2024-04-17 | 2024-04-16 | 2025-02-06 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46414827 | T2 DI GRBRVIL-LAYTNVIL 23/05 RPR GYWW | ICW
LC | 128577564 | 027/006 | T2 DI GRBRRVL LYTNVLE 27/6 RPR JUMW | WILLITS | ETL.8365.INSL.NCER | 2024-04-18 | 2024-04-16 | 2024-08-15 | On-Time |  | 2024-07-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46236405 | T2 DI GRBRRVL LYTNVLE 27/6 RPR JUMW | ICW
LC | 128577567 | 002/026 | T2 DI PIT #3-PIT #1 02/26 RPR JUMS | TABLEMTN | ETL.5400.INSL.NCER | 2024-04-18 | 2024-04-16 | 2024-08-23 | On-Time |  | 2025-04-16 | 2025-04-16 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46237042 | T2 DI PIT #3-PIT #1 /26 RPR JUMS | ICS
LC | 128577724 | 000/031 | T2 DI SPLDNG SUMMIT 0/31 RPL INSW | SACTO | ETL.8060.INSL.NCER | 2024-04-18 | 2024-04-16 | 2024-06-21 | On-Time |  | 2024-10-16 | 2025-04-16 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35547771 | T2 DI SPAULDING-SMMT 0/22 RPL INSW | 93I
LC | 128577727 | 000/025 | T2 DI SPLDNG SUMMIT 0/25 RPL INSW | SACTO | ETL.8060.INSL.NCER | 2024-04-18 | 2024-04-16 | 2024-06-27 | On-Time |  | 2024-10-16 | 2025-04-16 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35547771 | T2 DI SPAULDING-SMMT 0/22 RPL INSW | 93I
LC | 128577921 | 000/013 | T2 DI SPLDNG SUMMIT 0/13 RPR JUMW | SACTO | ETL.8060.INSL.NCER | 2024-04-18 | 2024-04-16 | 2024-06-22 | On-Time |  | 2024-10-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262106 | T2 DI SPLDNG SUMMIT 0/13 RPR JUMW | ICW
LC | 128577926 | 005/003 | T2 DI LYTNVLE COVELO 5/3 RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-04-18 | 2024-04-16 | 2024-07-11 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46236404 | T2 DI LYTNVLE COVELO 5/3 RPR JUMW | ICW
LC | 128577928 | 023/151 | T2 DI POE-RIO OSO 23/151 RPR JUMS | TABLEMTN | ETL.5540.INSL.CERA | 2024-04-18 | 2024-04-16 | 2024-09-17 | On-Time |  | 2024-07-16 | 2025-04-16 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46249483 | T2 DI POE-RIO OSO 23/151 RPR JUMS | ICS
LC | 128577929 | 023/151 | T2 DI POE-RIO OSO 23/151 COTTER | TABLEMTN | ETL.5540.INSL.CERA | 2024-04-18 | 2024-04-16 | 2025-04-03 | On-Time |  | 2025-04-16 | 2025-04-16 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46383934 | T2 DI POE-RIO OSO 23/151 COTTER | ICS
LC | 128578193 | 025/000 | T2 DI GARBERVILLE-LAYT 25/0 RPL STRW | WILLITS | ETL.8365.POLE.WOOD | 2024-04-18 | 2024-04-16 | 2025-04-16 | On-Time |  | 2025-04-16 | 2025-04-16 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574279 | T2 DI GARBERVILLE-LAYT 25/0 RPL STRW | 70Y
LC | 128578387 | 010/077 | T2 DI ROCK CREEK POE 10/77 RPR JUMS | TABLEMTN | ETL.5630.INSL.NCER | 2024-04-18 | 2024-04-16 | 2024-07-24 | On-Time |  | 2025-04-16 | 2025-04-16 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46257392 | T2 DI ROCK CREEK POE 10/77 RPR JUMS | ICS
LC | 128578388 | 010/077 | T2 ROCK CREEK POE 10/77 COMPLETE | TABLEMTN | ETL.5630.TOWR | 2024-04-18 | 2024-04-16 | 2025-04-04 | On-Time |  | 2025-04-16 | 2025-04-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381987 | T2 DI ROCK CREEK POE 10/77 RPL HRDT | ICQ
LC | 128578521 | 000/020 | T2 DI SPAULDING-SUMMIT 0/20 COTTER | SACTO | ETL.8060.POLE.NWOD | 2024-04-18 | 2024-04-16 | 2024-06-22 | On-Time |  | 2024-07-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262107 | T2 DI SPAULDING-SUMMIT 0/20 COTTER | ICW
LC | 128582018 | 028/005 | T2 DI GARBERVILLE-LALYT 28/5 RPR GYWW | WILLITS | ETL.8365.POLE.WOOD | 2024-04-19 | 2024-04-16 | 2025-03-06 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46414829 | T2 DI GARBERVILLE-LALYT 28/5 RPR GYWW | ICW
LC | 128582214 | 025/010 | T2 DI MNDCNO-WLTS-FRT BRG 25/10 RPR JUMW | WILLITS | ETL.7550.INSL.NCER | 2024-04-19 | 2024-04-16 | 2025-04-03 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46239214 | T2 DI MNOCINO-WLLITS-FRT 25/10 RPR JUMW | ICW
LC | 128582216 | 025/010 | T2 DI MNOCINO-WLLITS-FRT 25/10 RPR GYWW | WILLITS | ETL.7550.POLE.NWOD | 2024-04-19 | 2024-04-16 | 2024-10-09 | On-Time |  | 2024-07-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46239213 | T2 DI MNOCINO-WLLITS-FRT 25/10 RPR GYWW | ICW
LC | 128582383 | 031/260 | T2 DI BRDGVL CTTNWD 31/260 RPR IBWW | TABLEMTN | ETL.1110.INSL.CERA | 2024-04-19 | 2024-04-16 | 2024-05-30 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46254928 | T2 DI BRDGVL CTTNWD 31/260 RPR IBWW | ICW
LC | 128582386 | 031/260 | T2 DI BRDGVL CTTNWD 31/260 RPL INSW | TABLEMTN | ETL.1110.INSL.CERA | 2024-04-19 | 2024-04-16 | 2025-04-06 | On-Time |  | 2025-04-16 | 2025-04-16 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35555557 | T2 DI BRDGVL CTTNWD 31/260 RPL INSW | 93I
LC | 128582387 | 031/260 | T2 DI BRDGVL CTTNWD 31/260 RPR ADSS | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-19 | 2024-04-16 | 2024-05-30 | On-Time |  | 2024-07-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46237035 | T2 DI BRDGVL CTTNWD 31/260 RPR ADSS | ICW
LC | 128582674 | 027/009 | T2 DI MNDCNO-WLTS-FRT BRG 27/9 RPR GYWW | WILLITS | ETL.7550.POLE.NWOD | 2024-04-19 | 2024-04-16 | 2024-10-09 | On-Time |  | 2024-07-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46239211 | T2 DI MNDCNO-WLTS-FRT BRG 27/9 RPR GYWW | ICW
LC | 128582679 | 030/257 | T2 DI BRIDGEVILL CTTNWD 30/257R RPL HRDW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-19 | 2024-04-16 | 2025-04-06 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Missing | Hardware-Wood | Install | 46311100 | T2 DI BRIDGEVILL CTTNWD 30/257R RPL HRDW | ICW
LC | 128582695 | 018/154A | T2 DI CRAG VIEW-CASCADE 18/154A RPR GYWW | TABLEMTN | ETL.1350.POLE.NWOD | 2024-04-19 | 2024-04-16 | 2025-03-19 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46454326 | T2 DI CRAG VIEW-CASCADE 18/154A RPR GYWW | ICW
LC | 128582837 | 025/009 | T2 DI MNDNO-WLTS-FRT BRG 25/009 RPR IBWW | WILLITS | ETL.7550.INSL.NCER | 2024-04-19 | 2024-04-16 | 2025-04-03 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46310105 | T2 DI MNDNO-WLTS-FRT BRG 25/009 RPR IBWW | ICW
LC | 128582839 | 025/009 | T2 DI MNDNO-WLTS FRT BRG 25/009 RPL INSW | WILLITS | ETL.7550.INSL.NCER | 2024-04-19 | 2024-04-16 | 2025-04-03 | On-Time |  | 2025-04-16 | 2025-04-16 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574700 | T2 DI MNDNO-WLTS FRT BRG 25/009 RPL INSW | 93I
LC | 128582901 | 025/009 | T2 DI MNDNO-WLTS-FRT BRG 25/009 RPL ANCW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-19 | 2024-04-16 | 2025-04-03 | On-Time |  | 2025-04-16 | 2025-04-16 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574701 | T2 DI MNDNO-WLTS-FRT BRG 25/009 RPL ANCW | 93E
LC | 128583185 | 018/158 | T2 DI CRAG VW CSCDE 18/158 RPR ANCW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-16 | 2025-03-21 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46454331 | T2 DI CRAG VW CSCDE 18/158 RPR ANCW | ICW
LC | 128583245 | 018/158 | T2 DI CRAG VW CSCDE 18/158 RPR STRW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-16 | 2025-03-21 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454332 | T2 DI CRAG VW CSCDE 18/158 RPR STRW | ICW
LC | 128583284 | 018/158 | T2 DI CRAG VW CSCDE 18/158 RPR OPGW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-16 | 2025-03-21 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | OPGW - Wood | Repair | 46454333 | T2 DI CRAG VW CSCDE 18/158 RPR OPGW | ICW
LC | 128583805 | 054/304 | T2 DI TEMBLOR-SLO 54/304 COMPLETE | PISMOBCH | ETL.3960.TOWR | 2024-04-19 | 2024-04-16 | 2025-03-24 | On-Time |  | 2025-04-16 | 2025-04-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46303928 | T2 DI TEMBLOR-SLO 54/304 BENT STL | ICQ
LC | 128584012 | 055/308 | T2 DI TEMBLOR-SLO 55/308 RPL INSS | PISMOBCH | ETL.3960.INSL.CERA | 2024-04-19 | 2024-04-16 | 2025-01-31 | On-Time |  | 2025-04-16 | 2025-04-16 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35585152 | T2 DI TEMBLOR-SLO-TWR 50/284 RPL INSS | 93K
LC | 128584056 | 000/032 | T2 DI SPAULDING-SUMMIT 0/32 RPL INSW | SACTO | ETL.8060.INSL.NCER | 2024-04-19 | 2024-04-16 | 2024-06-21 | On-Time |  | 2024-07-18 | 2025-04-16 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35547771 | T2 DI SPAULDING-SMMT 0/22 RPL INSW | 93I
LC | 128584113 | 003/026 | T2 DI PIT #1-COTTONWOOD 3/26 RPR JUMS | TABLEMTN | ETL.5390.INSL.NCER | 2024-04-19 | 2024-04-16 | 2024-11-05 | On-Time |  | 2024-07-16 | 2025-04-16 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46240001 | T2 DI PIT #1-COTTONWOOD 3/26 RPR JUMS | ICS
LC | 128584131 | 015/130 | T2 DI CRAG VIEW-CASCADE 15/130 RPR OPGW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-19 | 2024-04-16 | 2025-03-21 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Wood | Repair | 46454334 | T2 DI CRAG VIEW-CASCADE 15/130 RPR OPGW | ICW
LC | 128584187 | 021/008 | T2 DI MNDNO-WLTS-FRT BRG 21/008 RPR JUMW | WILLITS | ETL.7550.INSL.NCER | 2024-04-19 | 2024-04-16 | 2025-04-10 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46308699 | T2 DI MNDNO-WLTS-FRT BRG 21/008 RPR JUMW | ICW
LC | 128584244 | 025/003 | T2 DI MNDNO-WLTS-FRT BRG 25/003 RPR STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-19 | 2024-04-16 | 2025-04-03 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310103 | T2 DI MNDNO-WLTS-FRT BRG 25/003 RPR STRW | ICW
LC | 128584283 | 032/189 | T2 DI TMBLR SN LS OBSPO 32/189 RMV NEST | PISMOBCH | ETL.3960.TOWR | 2024-04-19 | 2024-04-16 | 2025-01-30 | On-Time |  | 2025-04-16 | 2025-04-16 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46329534 | T2 DI TMBLR SN LS OBSPO 32/189 RMV NEST | ICS
LC | 128584317 | 023/001 | T2 MNDCNO-WLLTS-FRT BRG 23/1 RPL ANCW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-19 | 2024-04-16 | 2024-04-16 | Past Due |  | 2025-04-16 | 2025-04-16 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574301 | T2 DI MNDCNO-WLLTS-FRT BRG 23/1 RPL ANCW | 93E
LC | 128584399 | 000/022 | T2 DI SPAULDING-SMMT 0/22 RPL INSW | SACTO | ETL.8060.INSL.NCER | 2024-04-19 | 2024-04-16 | 2024-06-22 | On-Time |  | 2024-07-18 | 2025-04-16 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35547771 | T2 DI SPAULDING-SMMT 0/22 RPL INSW | 93I
LC | 128584476 | 017/149 | T2 DI CRAG VW CSCDE 17/149 RPR STRW | TABLEMTN | ETL.1350.POLE.STPS | 2024-04-19 | 2024-04-16 | 2024-09-06 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311384 | T2 DI CRAG VW CSCDE 17/149 RPR STRW | ICW
LC | 128584513 | 025/005 | T2 DI MENDOCINO-WLLS-FT BG 25/5 RPR JUMW | WILLITS | ETL.7550.INSL.NCER | 2024-04-19 | 2024-04-16 | 2025-04-03 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46310104 | T2 DI MENDOCINO-WLLS-FT BG 25/5 RPR JUMW | ICW
LC | 128584537 | 017/149 | T2 DI CRAG VW CSCDE 17/149 RPR OPGW | TABLEMTN | ETL.1350.POLE.STPS | 2024-04-19 | 2024-04-16 | 2024-09-06 | On-Time |  | 2024-10-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Wood | Repair | 46249645 | T2 DI CRAG VW CSCDE 17/149 RPR OPGW | ICW
LC | 128584721 | 002/011 | T2 DI LYTNVLLE-COVELO 002/011C RPR GYWW | WILLITS | ETL.7390.POLE.STPS | 2024-04-19 | 2024-04-16 | 2024-07-17 | On-Time |  | 2024-07-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46238955 | T2 DI LYTNVLLE-COVELO 002/011C RPR GYWW | ICW
LC | 128584722 | 002/011 | T2 DI LYTNVLLE-COVELO 002/011L RPR GYWW | WILLITS | ETL.7390.POLE.STPS | 2024-04-19 | 2024-04-16 | 2025-04-14 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46414825 | T2 DI LYTNVLLE-COVELO 002/011L RPR GYWW | ICW
LC | 128584761 | 024/000 | T2 DI GRBVIL LYTNVIL 24/000 RPR STRW | WILLITS | ETL.8365.POLE.WOOD | 2024-04-19 | 2024-04-16 | 2025-04-12 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46414828 | T2 DI GRBVIL LYTNVIL 24/000 RPR STRW | ICW
LC | 128584804 | 023/006 | T2 DI GRBVIL LYTNVIL 23/006 RPR JUMW | WILLITS | ETL.8365.INSL.NCER | 2024-04-19 | 2024-04-16 | 2024-08-13 | On-Time |  | 2024-07-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46238956 | T2 DI GRBVIL LYTNVIL 23/006 RPR JUMW | ICW
LC | 128585072 | 019/009 | T2 DI MNDNO WLTS FRT BRG 19/009 NRP | WILLITS | ETL.7550.POLE.WOOD | 2024-04-19 | 2024-04-16 | 2024-10-18 | On-Time |  | 2024-10-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH CTMN TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46246708 | T2 DI MNDNO WLTS FRT BRG 19/009 RPR ANCW | ICW
LC | 128585100 | 003/027 | T2 DI PIT #1 COTTONWOOD 03/027 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-04-19 | 2024-04-16 | 2025-03-25 | On-Time |  | 2025-04-16 | 2025-04-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381508 | T2 DI PIT #1 COTTONWOOD 03/027 RPR STRT | ICQ
LC | 128585106 | 015/134 | T2 DI CRAG VW CSCDE 15/134 RPR RPR GYWW | TABLEMTN | ETL.1350.POLE.STPS | 2024-04-19 | 2024-04-16 | 2025-01-17 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46454373 | T2 DI CRAG VW CSCDE 15/134 RPR RPR GYWW | ICW
LC | 128585107 | 015/134 | T2 DI CRAG VW CSCDE 15/134 RPR RPR GYWW | TABLEMTN | ETL.1350.POLE.STPS | 2024-04-19 | 2024-04-16 | 2025-01-17 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46454374 | T2 DI CRAG VW CSCDE 15/134 RPR RPR GYWW | ICW
LC | 128585153 | 025/011 | T2 DI MNNO-WLTS-FRT BRG 25/11 RPR GYWW | WILLITS | ETL.7550.POLE.NWOD | 2024-04-19 | 2024-04-16 | 2024-10-09 | On-Time |  | 2024-10-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46239212 | T2 DI MNDNO-WLTS-FRT BRG 25/011 RPR GYWW | ICW
LC | 128585299 | 023/006 | T2 DI MNDCNO-WLTS-FRT BRG 23/6L RPR GYWW | WILLITS | ETL.7550.POLE.STPS | 2024-04-19 | 2024-04-16 | 2025-03-04 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310100 | T2 DI MNDCNO-WLTS-FRT BRG 23/6L RPR GYWW | ICW
LC | 128585330 | 023/006 | T2 DI MNDCNO-WLTS-FRT BRG 23/6C RPR GYWW | WILLITS | ETL.7550.POLE.STPS | 2024-04-19 | 2024-04-16 | 2025-03-04 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310101 | T2 DI MNDCNO-WLTS-FRT BRG 23/6C RPR GYWW | ICW
LC | 128585331 | 023/006 | T2 DI MNDCNO-WLTS-FRT BRG 23/6R RPR GYWW | WILLITS | ETL.7550.POLE.STPS | 2024-04-19 | 2024-04-16 | 2025-03-04 | On-Time |  | 2025-04-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310102 | T2 DI MNDCNO-WLTS-FRT BRG 23/6R RPR GYWW | ICW
LC | 128585473 | 028/002 | T2 DI GRBRVLL-LYTNVLLE 28/2 RPR JUMW | WILLITS | ETL.8365.INSL.NCER | 2024-04-19 | 2024-04-16 | 2024-08-15 | On-Time |  | 2024-07-16 | 2025-04-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46238957 | T2 DI GRBRVLL-LYTNVLLE 28/2 RPR JUMW | ICW
LC | 128708574 | 007/003A | T2 DI LAYTONVILLE-COVL 7/3A RPL INSW | WILLITS | ETL.7390.INSL.NCER | 2024-05-03 | 2024-04-16 | 2025-06-11 | Past Due |  | 2024-07-16 | 2025-04-16 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35647707 | T2 DI LAYTONVILLE-COVL 7/3A RPL INSW | 93I
LC | 127294055 | 010/143 | T2 DI DT-MTN GT JCT-MTN 10/143R RPL STRW | TABLEMTN | ETL.6750.POLE.WDPS | 2023-10-17 | 2023-10-17 | 2024-12-10 | On-Time |  | 2025-04-17 | 2025-04-17 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH XMPT TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Replace | 35491299 | T2 DI DLTA-MTN GATE 10/142 RPL POLE | 70Y
LC | 128556633 | 019/111 | T2 EI STANISLUS-MANTECA #2 19/111 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-17 | 2024-04-17 | 2025-04-08 | On-Time |  | 2025-04-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416358 | T2 EI STNSLS-MNTC #2 19/111 UNBURY | ICQ
LC | 128556859 | 019/119 | T2 EI STNLS-MLNS SW SM #1 19/119 UNBURY | VICTOR | ETL.3830.TOWR | 2024-04-17 | 2024-04-17 | 2025-04-08 | On-Time |  | 2025-04-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416359 | T2 EI STNLS-MLNS SW SM #1 19/119 UNBURY | ICQ
LC | 128556893 | 010/129 | T2 EI WST PNT-VLY SPRNGS 10/129 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-04-17 | 2024-04-17 | 2025-02-07 | On-Time |  | 2025-04-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327501 | T2 EI WST PNT-VLY SPRNGS 10/129 RPR GYWW | ICW
LC | 128558505 | 019/113 | T2 EI STNSLS-MNTC #2 19/113 RMV NEST | VICTOR | ETL.3820.TOWR | 2024-04-17 | 2024-04-17 | 2025-03-18 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Debris/Nest/etc. | Structure-Steel | Remove | 46300278 | T2 EI STNSLS-MNTC #2 19/113 RMV NEST | ICS
LC | 128559976 | 072/295 | T2 EI RND MTN-TABLE MTN #1 72/295 COTTER | TABLEMTN | ETL.6060.INSL | 2024-04-17 | 2024-04-17 | 2025-01-22 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46306213 | T2 EI RND MTN-TABLE MTN #2 72/295 COTTER | ICS
LC | 128560965 | 004/024 | T2 EI METCALF-HICKS 1 & 2 4/24 RPR FOND | METCALF | ETL.4317.TOWR | 2024-04-17 | 2024-04-17 | 2025-01-06 | On-Time |  | 2025-04-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46298837 | T2 EI METCALF-HICKS 1 & 2 4/24 RPR FOND | ICQ
LC | 128560977 | 067/278 | T2 EI RND MTN-TBLE MTN #1 67/278 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-17 | 2024-04-17 | 2025-01-22 | On-Time |  | 2025-04-17 | 2025-04-17 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128561004 | 019/110 | T2 EI STANISLAUS-MNTECA #2 19/110 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-17 | 2024-04-17 | 2025-04-08 | On-Time |  | 2025-04-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416482 | T2 EI STANISLAUS-MNTECA #2 19/110 UNBURY | ICQ
LC | 128561033 | 067/279 | T2 EI RND MTN-TBLE MTN #1 67/279 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-17 | 2024-04-17 | 2025-01-22 | On-Time |  | 2025-04-17 | 2025-04-17 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128561242 | 017/253 | T2 EI SQC-SNT YNZ SW ST 17/253 RPR GYWW | PISMOBCH | ETL.3700.POLE.NWOD | 2024-04-17 | 2024-04-17 | 2024-09-04 | On-Time |  | 2024-07-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46255913 | T2 EI SQC-SNT YNZ SW ST 17/253 RPR GYWW | ICW
LC | 128561516 | 002/025 | T2 WV MONTA VISTA-BURNS 02/25 INS GYWW | MOSSLNDG | ETL.7590.POLE.NWOD | 2024-04-17 | 2024-04-17 | 2025-05-12 | Past Due |  | 2024-10-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Missing | Guy Wire-Wood | Install | 46236129 | T2 WV MONTA VISTA-BURNS 02/25 INS GYWW | ICW
LC | 128563878 | 067/280 | T2 EI RND MTN-TBLE MTN #1 67/280 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-17 | 2024-04-17 | 2024-10-22 | On-Time |  | 2025-04-17 | 2025-04-17 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128563897 | 067/280 | T2 EI RD MTN-TBLE MTN #1 67/280 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-04-17 | 2024-04-17 | 2025-01-22 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306214 | T2 EI RD MTN-TBLE MTN #1 67/280 RMV NEST | ICS
LC | 128563974 | 034/009 | T2 EI FORT ROSS-GUALALA 34/9 COMPLETE | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-04-17 | 2024-04-17 | 2025-03-21 | On-Time |  | 2025-04-17 | 2025-04-17 | 637 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35574056 | T2 EI FORT ROSS-GUALALA 34/9 REFRAME | 93E
LC | 128564274 | 010/133 | T2 WST PNT-VLY SPRNGS 10/133 TOUCH | VICTOR | ETL.8350.POLE.NWOD | 2024-04-17 | 2024-04-17 | 2024-04-17 | Past Due |  | 2024-10-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46477458 | T2 WST PNT-VLY SPRNGS 10/133 TOUCH | ICW
LC | 128564734 | 000/000 | T2 EI CHOWCHILLA-KERCKHOFF 0/0 RPR FOND | FRESNO | ETL.1250.POLE.NWOD | 2024-04-17 | 2024-04-17 | 2024-06-14 | On-Time |  | 2024-10-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC COMP OH FMOB TR2 PRTO FRAB DURA BRIN | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46240371 | T2 EI CHOWCHILLA-KERCKHOFF 0/0 RPR FOND | ICQ
LC | 128564964 | 000/000 | T2 EI CHOWCHILLA-KERCKHOFF 0/0 COMPLETE | FRESNO | ETL.1250.INSL.NCER | 2024-04-17 | 2024-04-17 | 2025-03-25 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Jumper-Steel | Repair | 46298272 | T2 EI CHOWCHILLA-KERCKHOFF 0/0 RPR JUMS | ICS
LC | 128565105 | 000/000 | T2 EI CHOWCHILLA-KERCKHFF 0/0 RPR STRT | FRESNO | ETL.1250.POLE.NWOD | 2024-04-17 | 2024-04-17 | 2025-05-23 | Past Due |  | 2025-04-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC COMP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46292640 | T2NT EI CHOWCHILLA-KERCKHFF 0/0 RPR STRT | ICQ
LC | 128565547 | 067/281 | T2 EI RND MTN-TBLE MTN #1 67/281 COA | TABLEMTN | ETL.6060.TOWR | 2024-04-17 | 2024-04-17 | 2025-01-22 | On-Time |  | 2025-04-17 | 2025-04-17 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128566672 | 002/053 | T2 EI CARIBOU-WESTWOOD 003/053 RPR GYWW | TABLEMTN | ETL.6300.POLE.NWOD | 2024-04-17 | 2024-04-17 | 2024-07-09 | On-Time |  | 2024-07-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46237043 | T2 EI CARIBOU-WESTWOOD 003/053 RPR GYWW | ICW
LC | 128566738 | 018/103 | T2 EI STNISLUS-MNTECA #2 18/103 COMPLETE | VICTOR | ETL.3820.TOWR | 2024-04-17 | 2024-04-17 | 2025-03-18 | On-Time |  | 2025-04-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416485 | T2 EI STNISLUS-MNTECA #2 18/103 RPR STRT | ICQ
LC | 128566790 | 018/103 | T2 EI STNISLUS-MNTECA #2 18/103 COMPLETE | VICTOR | ETL.3820.TOWR | 2024-04-17 | 2024-04-17 | 2025-03-18 | On-Time |  | 2025-04-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416486 | T2 EI STNISLUS-MNTECA #2 18/103 UNBURY | ICQ
LC | 128566845 | 006/011 | T2 EI BRCBRG JCT-MRPSA TAP 6/11 RPR INSW | FRESNO | ETL.8651.INSL.NCER | 2024-04-17 | 2024-04-17 | 2025-03-29 | On-Time |  | 2025-04-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298261 | T2 EI BRCBRG JCT-MRPSA TAP 6/11 RPR INSW | ICW
LC | 128566860 | 006/009 | T2 EI BRCBRG JCT-MRPSA TAP 6/9 COMPLETE | FRESNO | ETL.8651.INSL.NCER | 2024-04-17 | 2024-04-17 | 2025-03-29 | On-Time |  | 2025-04-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298285 | T2 EI BRCBRG JCT-MRPSA TAP 6/9 RPR INSW | ICW
LC | 128566945 | 017/110 | T2 EI STLS MLNS MNTC #1 17/110 RPL HNGR | VICTOR | ETL.3830.INSL | 2024-04-17 | 2024-04-17 | 2025-04-15 | On-Time |  | 2025-04-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46401413 | T2 EI STLS MLNS MNTC #1 17/110 RPL HNGR | ICQ
LC | 128566980 | 017/110 | T2 EI STLS MLNS MNTC #1 17/110 RPL INSS | VICTOR | ETL.3830.INSL | 2024-04-17 | 2024-04-17 | 2025-04-15 | On-Time |  | 2025-04-17 | 2025-04-17 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35599720 | T2 EI STLS MLNS MNTC #1 17/110 RPL INSS | 93K
LC | 128566986 | 011/160 | T2 EI SSQC-SNTA YNZ SS 11/160R RMV VEG | PISMOBCH | ETL.3700.POLE.WDPS | 2024-04-17 | 2024-04-17 | 2025-02-12 | On-Time |  | 2025-04-17 | 2025-04-17 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP REMT SWRK ACCL CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128567046 | 018/104 | T2 EI STANISLUS-MNTCA #2 18/104 COMPLETE | VICTOR | ETL.3820.TOWR | 2024-04-17 | 2024-04-17 | 2025-03-18 | On-Time |  | 2025-04-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416487 | T2 EI STANISLUS-MNTECA #2 18/104 UNBURY | ICQ
LC | 128567065 | 018/104 | T2 EI STNISLAUS-MNTCA #2 18/104 COMPLETE | VICTOR | ETL.3820.TOWR | 2024-04-17 | 2024-04-17 | 2025-03-18 | On-Time |  | 2025-04-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416488 | T2 EI STNISLAUS-MNTCA #2 18/104 RPR STRT | ICQ
LC | 128567127 | 013/099 | T2 EI WISHON-COPPERMINE 13/099 RMV VEG | FRESNO | ETL.9330.TOWR | 2024-04-17 | 2024-04-17 | 2025-03-07 | On-Time |  | 2025-04-17 | 2025-04-17 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128567267 | 014/006 | T2 EI OAKHURST TAP 014/006 RMV ENCR | FRESNO | ETL.1252.POLE.NWOD | 2024-04-17 | 2024-04-17 | 2025-03-03 | On-Time |  | 2025-04-17 | 2025-04-17 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Encroachment | Right of Way | Remove | 46343242 | T2 EI OAKHURST TAP 014/006 RMV ENCR | CHR
LC | 128567392 | 006/102 | T2 EI SISQUOC-SANTA YNEZ 6/102 RPL INSW | PISMOBCH | ETL.3700.INSL.CERA | 2024-04-17 | 2024-04-17 | 2025-04-04 | On-Time |  | 2025-04-17 | 2025-04-17 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573773 | T2 EI SISQUOC-SANTA YNEZ 6/102 RPL INSW | 93I
LC | 128567461 | 006/107 | T2 EI SSQUOC-SNTA YNZ SS 6/107 RPL POLE | PISMOBCH | ETL.3700.POLE.WOOD | 2024-04-17 | 2024-04-17 | 2025-02-11 | On-Time |  | 2025-04-17 | 2025-04-17 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573775 | T2 EI SSQUOC-SNTA YNZ SS 6/107 RPL POLE | 70Y
LC | 128567622 | 000/009 | T2 EI COLEMAN-SOUTH 0/09 RPR INSW | TABLEMTN | ETL.6450.INSL.NCER | 2024-04-17 | 2024-04-17 | 2025-03-21 | On-Time |  | 2025-04-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46389134 | T2 EI COLEMAN-SOUTH 0/09 RPR INSW | ICW
LC | 128567655 | 013/009 | T2 EI TRINITY-MAPLE CREEK 13/9 RPR CNDW | EUREKA | ETL.8170.INSL.NCER | 2024-04-17 | 2024-04-17 | 2025-03-21 | On-Time |  | 2025-04-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Conductor-Wood | Repair | 46345764 | T2 EI TRINITY-MAPLE CREEK 13/9 RPR CNDW | ICW
LC | 128567662 | 013/009 | T2 EI TRINITY-MAPLE CREEK 13/9 RPL ANCW | EUREKA | ETL.8170.POLE.WOOD | 2024-04-17 | 2024-04-17 | 2025-03-21 | On-Time |  | 2025-04-17 | 2025-04-17 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572108 | T2 EI TRINITY-MAPLE CREEK 13/9 RPL ANCW | 93E
LC | 128567699 | 004/005 | T2 SALMON CREEK TAP 04/005 RPL STRW | LAKEVLLE | ETL.6981.POLE.WOOD | 2024-04-17 | 2024-04-17 | 2024-04-17 | Past Due |  | 2025-04-17 | 2025-04-17 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAR | No Good/Out of Stdrd | Structure-Wood | Replace | 35572895 | T2 EI SALMON CREEK TAP 04/005 RPL STRW | 70Y
LC | 128567709 | 048/239 | T2 MALIN-ROUND MTN #2 48/239 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-04-17 | 2024-04-17 | 2025-03-24 | On-Time |  | 2025-04-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381021 | T2 EI MALIN-ROUND MTN #2 48/239 RPR GYWW | ICQ
LC | 128567791 | 048/241 | T2 EI MALIN-ROUND MTN #2 48/241 RPR ANCT | TABLEMTN | ETL.6020.TOWR | 2024-04-17 | 2024-04-17 | 2024-07-08 | On-Time |  | 2024-10-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Tower | Repair | 46248636 | T2 EI MALIN-ROUND MTN #2 48/241 RPR ANCT | ICQ
LC | 128567861 | 032/005 | T2 EI HMBLDT BY-BRDGLE 32/5L RPR GYWW | EUREKA | ETL.7850.POLE.STPS | 2024-04-17 | 2024-04-17 | 2025-03-25 | On-Time |  | 2025-04-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345765 | T2 EI HMBLDT BY-BRDGLE 32/5L RPR GYWW | ICW
LC | 128567905 | 003/026 | T2 EI MORAGA-OAKLAND #2 3/026 COTTER | CONCORD | ETL.2730.INSL.NCER | 2024-04-17 | 2024-04-17 | 2025-01-26 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46287357 | T2 EI MORAGA-OAKLAND #2 3/026 COTTER | ICS
LC | 128567906 | 003/027 | T2 EI MORAGA-OAKLAND #1 3/027 RPR STRT | CONCORD | ETL.2720.TOWR | 2024-04-17 | 2024-04-17 | 2025-01-17 | On-Time |  | 2025-04-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287405 | T2 EI MORAGA-OAKLAND #1 3/027 RPR STRT | ICQ
LC | 128567974 | 015/155 | T2 EI RND MTN-CTTNWD #2 15/155 RPR OPGW | TABLEMTN | ETL.5640.TOWR | 2024-04-17 | 2024-04-17 | 2025-02-25 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46416191 | T2 EI RND MTN-CTTNWD #2 15/155 RPR OPGW | ICS
LC | 128568017 | 041/323 | T2 EI BRDGEVLE-CTTNWD 41/323R RPL HRDW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-17 | 2024-04-17 | 2025-04-06 | On-Time |  | 2025-04-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46311099 | T2 EI BRDGEVLE-CTTNWD 41/323R RPL HRDW | ICW
LC | 128568064 | 041/323 | T2 EI BRDGEVLE-CTTNWD 41/323L RPL HRDW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-17 | 2024-04-17 | 2025-04-06 | On-Time |  | 2025-04-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46311098 | T2 EI BRDGEVLE-CTTNWD 41/323L RPL HRDW | ICW
LC | 128569929 | 010/119 | T2 EI WST PNT-VLY SPRNGS 10/119 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-04-18 | 2024-04-17 | 2024-08-25 | On-Time |  | 2025-04-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46292342 | T2 EI WST PNT-VLY SPRNGS 10/119 RPR GYWW | ICW
LC | 128569964 | 009/113 | T2 EI WST PNT-VLY SPRNGS 09/113 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-04-18 | 2024-04-17 | 2025-02-12 | On-Time |  | 2025-04-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327612 | T2 EI WST PNT-VLY SPRNGS 09/113 RPR GYWW | ICW
LC | 128570000 | 009/113 | T2 EI WST PNT-VLY SPRNGS 09/113 RPL ANCW | VICTOR | ETL.8350.POLE.NWOD | 2024-04-18 | 2024-04-17 | 2025-04-13 | On-Time |  | 2025-04-17 | 2025-04-17 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573392 | T2 EI WST PNT-VLY SPRNGS 09/113 RPL ANCW | 93E
LC | 128577636 | 028/175 | T2 DI HELMS-GREGG #1 28/175 RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-04-18 | 2024-04-17 | 2025-03-24 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298225 | T2 DI HELMS-GREGG #1 28/175 RPR SHLD | ICS
LC | 128577836 | 027/177 | T2 DI POE-RIO OSO 27/177 RPR INSS | TABLEMTN | ETL.5540.INSL.CERA | 2024-04-18 | 2024-04-17 | 2024-04-24 | On-Time |  | 2024-07-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46232600 | T2 DI POE-RIO OSO 27/177 RPR INSS | ICS
LC | 128581470 | 003/033 | T2 DI MNTA VSTA BRNS 3/33L RPR GYWW | MOSSLNDG | ETL.7590.POLE.WDPS | 2024-04-19 | 2024-04-17 | 2025-03-26 | On-Time |  | 2025-04-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391288 | T2 DI MNTA VSTA BRNS 3/33L RPR GYWW | ICW
LC | 128581503 | 021/147 | T2 DI HELMS GREGG#1 21/147 RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-04-19 | 2024-04-17 | 2025-03-25 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298226 | T2 DI HELMS GREGG#1 21/147 RPR SHLS | ICS
LC | 128581550 | 021/147 | T2 DI HELMS GREGG#1 21/147 RPR INSS | FRESNO | ETL.4870.INSL.CERA | 2024-04-19 | 2024-04-17 | 2024-05-22 | On-Time |  | 2024-07-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46234447 | T2 DI HELMS GREGG#1 21/147 RPR INSS | ICS
LC | 128582093 | 009/054 | T2 BALCH-SANGER 9/54 RPR STRT | FRESNO | ETL.1050.TOWR | 2024-04-19 | 2024-04-17 | 2024-04-17 | Past Due |  | 2024-10-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46240370 | T2 DI BALCH-SANGER 009/054 RPR STRT | ICQ
LC | 128583365 | 029/011 | T2 DI MNDO-WLLTS-FRT BRG 29/11 RPR IBWW | WILLITS | ETL.7550.INSL.NCER | 2024-04-19 | 2024-04-17 | 2025-04-03 | On-Time |  | 2025-04-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46310106 | T2 DI MNDO-WLLTS-FRT BRG 29/11 RPR IBWW | ICW
LC | 128583552 | 010/126 | T2 DI KESWICK-TRINITY 10/126 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-04-19 | 2024-04-17 | 2025-04-24 | Past Due |  | 2024-07-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311296 | T2 DI KESWICK-TRINITY 10/126 RPR JUMW | ICW
LC | 128583553 | 010/126 | T2 DI KESWICK-TRINITY 10/126 CANCEL | TABLEMTN | ETL.7270.POLE.WOOD | 2024-04-19 | 2024-04-17 | 2024-11-22 | On-Time |  | 2025-04-17 | 2025-04-17 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128584000 | 011/062 | T2 DI BALCH-SANGER 011/062 COTTER | FRESNO | ETL.1050.INSL.CERA | 2024-04-19 | 2024-04-17 | 2025-03-12 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46298228 | T2 DI BALCH-SANGER 011/062 RPR INSS | ICS
LC | 128584030 | 011/062 | T2 DI BALCH-SANGER 11/62 RPR JUMS | FRESNO | ETL.1050.INSL.CERA | 2024-04-19 | 2024-04-17 | 2025-03-12 | On-Time |  | 2024-07-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46234450 | T2 DI BALCH-SANGER 011/062 RPR JUMS | ICS
LC | 128584058 | 031/184 | T2 DI HELMS-GREGG #1 31/184 RPR INSS | FRESNO | ETL.4870.INSL.CERA | 2024-04-19 | 2024-04-17 | 2025-03-24 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46298229 | T2 DI HELMS-GREGG #1 31/184 RPR INSS | ICS
LC | 128584320 | 010/125 | T2 DI KESWICK-TRINITY 10/125 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-04-19 | 2024-04-17 | 2025-04-24 | Past Due |  | 2024-07-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311297 | T2 DI KESWICK-TRINITY 10/125 RPR JUMW | ICW
LC | 128584937 | 029/178 | T2 DI HELMS-GREGG #1 29/178 RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-04-19 | 2024-04-17 | 2025-03-24 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298230 | T2 DI HELMS-GREGG #1 29/178 RPR SHLD | ICS
LC | 128585111 | 027/172 | T2 DI HELMS-GREGG #1 27/172 RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-04-19 | 2024-04-17 | 2025-03-24 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298232 | T2 DI HELMS-GREGG #1 27/172 RPR SHLD | ICS
LC | 128585249 | 007/097 | T2 DI KSWCK TRNTY 07/097 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-04-19 | 2024-04-17 | 2024-09-12 | On-Time |  | 2024-07-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251623 | T2 DI KSWCK TRNTY 07/097 RPR JUMW | ICW
LC | 128585253 | 030/181 | T2 DI HELMS-GREGG #1 30/181 RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-04-19 | 2024-04-17 | 2025-03-24 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298234 | T2 DI HELMS-GREGG #1 30/181 RPR SHLD | ICS
LC | 128585375 | 009/057 | T2 DI KNGS RVR-SNGR RDLY 9/57 RPL INSS | FRESNO | ETL.2030.INSL.CERA | 2024-04-19 | 2024-04-17 | 2025-03-11 | On-Time |  | 2025-04-17 | 2025-04-17 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35573905 | T2 DI KNGS RVR-SNGR RDLY 9/57 RPL INSS | 93K
LC | 128585411 | 032/188 | T2 DI HELMS-GREGG #1 032/188 RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-04-19 | 2024-04-17 | 2025-03-24 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298235 | T2 DI HELMS-GREGG #1 032/188 RPR SHLD | ICS
LC | 128585456 | 007/100 | T2 DI KESWICK-TRIN 7/100 CANCEL | TABLEMTN | ETL.7270.POLE.NWOD | 2024-04-19 | 2024-04-17 | 2024-12-19 | On-Time |  | 2025-04-17 | 2025-04-17 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128585458 | 007/100 | T2 DI KESWICK-TRINITY 7/100 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-04-19 | 2024-04-17 | 2024-09-10 | On-Time |  | 2024-07-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251624 | T2 DI KESWICK-TRINITY 7/100 RPR JUMW | ICW
LC | 128585810 | 000/006 | T2 DI KERCKHOFF#1-KFF#2 0/6 COTTER | FRESNO | ETL.1880.INSL.NCER | 2024-04-19 | 2024-04-17 | 2024-08-19 | On-Time |  | 2024-10-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46236411 | T2 DI KERCKHOFF#1-KFF#2 0/6 RPR INSS | ICS
LC | 128585818 | 008/107 | T2 DI KESWICK-TIRN 8/107 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-04-19 | 2024-04-17 | 2024-09-10 | On-Time |  | 2024-07-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251625 | T2 DI KESWICK-TIRN 8/107 RPR JUMW | ICW
LC | 128588112 | 000/006 | T2 DI SPAULDING-SUMMIT 0/6 CNCL | SACTO | ETL.8060.POLE.WOOD | 2024-04-19 | 2024-04-17 | 2024-04-17 | Past Due |  | 2025-04-17 | 2025-04-17 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572863 | T2 DI SPAULDING-SUMMIT 0/6 RPL ANCW | 93E
LC | 128589385 | 030/182 | T2 DI HELMS-GREGG #1 030/182 RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-04-19 | 2024-04-17 | 2025-03-24 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298237 | T2 DI HELMS-GREGG #1 030/182 RPR SHLD | ICS
LC | 128590850 | 028/176 | T2 DI HELMS-GREGG #1 028/176 RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-04-19 | 2024-04-17 | 2025-03-24 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298239 | T2 DI HELMS-GREGG #1 028/176 RPR SHLD | ICS
LC | 128590855 | 026/164 | T2 DI HELMS-GREGG #1 026/164 RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-04-19 | 2024-04-17 | 2025-03-24 | On-Time |  | 2025-04-17 | 2025-04-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298260 | T2 DI HELMS-GREGG #1 026/164 RPR SHLD | ICS
LC | 128593367 | 023/153 | T2 DI POE-RIO OSO 023/153 RPR STRT | TABLEMTN | ETL.5540.TOWR | 2024-04-19 | 2024-04-17 | 2025-01-22 | On-Time |  | 2025-04-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381989 | T2 DI POE-RIO OSO 023/153 RPR STRT | ICQ
LC | 128593663 | 000/002 | T2 DI SPAULDING-SMMT 0/2 RPR JUMW | SACTO | ETL.8060.INSL.NCER | 2024-04-19 | 2024-04-17 | 2024-06-22 | On-Time |  | 2024-07-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262105 | T2 DI SPAULDING-SMMT 0/2 RPR JUMW | ICW
LC | 128599309 | 009/056 | T2 DI BALCH-SANGER 009/056 RPR STRT | FRESNO | ETL.1050.TOWR | 2024-04-19 | 2024-04-17 | 2024-04-29 | On-Time |  | 2024-07-18 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46234565 | T2 DI BALCH-SANGER 009/056 RPR STRT | ICQ
LC | 128600350 | 000/012 | T2 DI SPAULDING-SUMMIT 0/12 RPR GYWW | SACTO | ETL.8060.POLE.WOOD | 2024-04-19 | 2024-04-17 | 2024-06-22 | On-Time |  | 2025-04-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46268819 | T2 DI SPAULDING-SUMMIT 0/12 RPR GYWW | ICW
LC | 128600354 | 012/065B | T2 DI BALCH SANGER 12/065B RPR GYWT | FRESNO | ETL.1050.POLE.NWOD | 2024-04-19 | 2024-04-17 | 2025-01-15 | On-Time |  | 2025-04-17 | 2025-04-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46292643 | T2 DI BALCH SANGER 12/065B RPR GYWT | ICQ
LC | 128618042 | 008/104 | T2 DI KESWICK-TRINITY 8/104 RPR INSW | TABLEMTN | ETL.7270.INSL.NCER | 2024-04-22 | 2024-04-17 | 2025-04-08 | On-Time |  | 2025-04-17 | 2025-04-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46491241 | T2 DI KESWICK-TRINITY 8/104 RPR INSW | ICW
LC | 123360525 | 018/096 | T2NT EI RND MTN-TBL MTN #2 18/96 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2022-04-19 | 2022-04-18 | 2023-08-22 | On-Time |  | 2025-04-18 | 2025-04-18 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2N PRTO CLMB FRAB | Overgrown | Vegetation | Remove
LC | 123440476 | 004/093 | T2NT DI CNTRVL-TB MT-ORVL 4/93 RPL STRW | TABLEMTN | ETL.6330.POLE.WOOD | 2022-04-27 | 2022-04-18 | 2024-05-21 | On-Time |  | 2025-04-18 | 2025-04-18 | 372 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Replace | 31638627 | T2NT DI CNTRVL-TB MT-ORVL 4/93 RPL STRW | 70Y
LC | 123472941 | 040/341 | T2NT DI RND MTN-CTTNWD#3 40/341 RPR STRT | TABLEMTN | ETL.5650.TOWR | 2022-05-02 | 2022-04-18 | 2023-08-03 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648250 | T2 DI RND MTN-CTTNWD #3 40/341 BNT STEEL | ICQ
LC | 123500268 | R002/020 | T2NT DI RND MTN-CTTNWD #3 R2/20 BNT STEL | TABLEMTN | ETL.5650.TOWR | 2022-05-04 | 2022-04-18 | 2023-07-10 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45581906 | T2 DI RND MTN-CTTNWD #3 R2/20 BNT STEEL | ICQ
LC | 123520921 | 006/131 | T2NT DI CNTRVL-TBLMTN-ORV 6/131 RPL STRW | TABLEMTN | ETL.6330.POLE.WOOD | 2022-05-05 | 2022-04-18 | 2023-07-20 | On-Time |  | 2025-04-18 | 2025-04-18 | 372 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 31634715 | T3 DI CENTER-TABLE MTN 3/63 RPL PL | 70Y
LC | 128571129 | 014/005C | T2 EI OAKHURST TAP 014/005C RPR INSW | FRESNO | ETL.1252.INSL.NCER | 2024-04-18 | 2024-04-18 | 2025-02-27 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298262 | T2 EI OAKHURST TAP 014/005C RPR INSW | ICW
LC | 128571242 | 006/039 | T2 EI KRCKHF-CLVIS-SNGR #1 6/39 MASTIC | FRESNO | ETL.1890.TOWR | 2024-04-18 | 2024-04-18 | 2025-01-23 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46292644 | T2NT EI KRCKHF-CLVIS-SNGR #1 6/39 MASTIC | ICQ
LC | 128571317 | 000/005 | T2 EI LOS ESTEROS-METCALF 0/5 COTTER | METCALF | ETL.5353.INSL | 2024-04-18 | 2024-04-18 | 2025-03-26 | On-Time |  | 2025-04-18 | 2025-04-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46286777 | T2 EI LOS ESTEROS-METCALF 0/5 COTTER | ICS
LC | 128571391 | 011/101 | T2 EI BRDGVLE-CTNWD 11/101 RMV VEG | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-18 | 2024-04-18 | 2024-05-14 | On-Time |  | 2025-04-18 | 2025-04-18 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128571830 | 006/141 | T2 WV KILARC-DESCHUTES 6/141 INS DMPW | TABLEMTN | ETL.7300.INSL.NCER | 2024-04-18 | 2024-04-18 | 2025-03-22 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46306216 | T2 WV KILARC-DESCHUTES 6/141 INS DMPW | ICW
LC | 128571897 | 007/163 | T2 WV KILARC-DESCHUTES 7/163 INS DMPW | TABLEMTN | ETL.7300.INSL.NCER | 2024-04-18 | 2024-04-18 | 2025-03-22 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46306217 | T2 WV KILARC-DESCHUTES 7/163 INS DMPW | ICW
LC | 128571935 | 007/164 | T2 WV KILARC-DESCHUTES 7/164 INS DMPW | TABLEMTN | ETL.7300.INSL.NCER | 2024-04-18 | 2024-04-18 | 2025-03-22 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46306218 | T2 WV KILARC-DESCHUTES 7/164 INS DMPW | ICW
LC | 128571939 | 010/088 | T2 EI UKIAH-HPLND-CLVRDL 10/088 RPR GYWW | WILLITS | ETL.4050.POLE.NWOD | 2024-04-18 | 2024-04-18 | 2025-02-12 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46414831 | T2 EI UKIAH-HPLND-CLVRDL 10/088 RPR GYWW | ICW
LC | 128572013 | 016/001 | T2 EI DUNLAP TAP 016/001 RPR INSW | FRESNO | ETL.9061.INSL.NCER | 2024-04-18 | 2024-04-18 | 2025-03-21 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298263 | T2 EI DUNLAP TAP 016/001 RPR INSW | ICW
LC | 128572018 | 014/000 | T2 EI OAKHURST TAP 014/000 RPR GYWW | FRESNO | ETL.1252.POLE.NWOD | 2024-04-18 | 2024-04-18 | 2025-03-03 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298264 | T2 EI OAKHURST TAP 014/000 RPR GYWW | ICW
LC | 128572370 | 017/001 | T2 EI EXCHEQUER-MARIPOSA 17/001 RPL DMPW | FRESNO | ETL.8640.INSL.NCER | 2024-04-18 | 2024-04-18 | 2025-04-16 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Damper-Wood | Replace | 46298265 | T2 EI EXCHEQUER-MARIPOSA 17/001 RPL DMPW | ICW
LC | 128572809 | 001/033 | T2 EI CARIBOU-WESTWOOD 1/033 RPR GYWW | TABLEMTN | ETL.6300.POLE.NWOD | 2024-04-18 | 2024-04-18 | 2024-07-09 | On-Time |  | 2024-07-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46237044 | T2 EI CARIBOU-WESTWOOD 1/033 RPR GYWW | ICW
LC | 128572959 | 021/003 | T2 BRDGVLL-GRBRVLL 21/3 RPR INSS | EUREKA | ETL.6220.INSL.NCER | 2024-04-18 | 2024-04-18 | 2024-04-18 | Past Due |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46345766 | T2 EI BRDGVLL-GRBRVLL 21/3 RPR INSS | ICW
LC | 128573079 | 305 | T2 SLO-OCEANO 19/122A RPR SWTC | PISMOBCH | ETL.3530.SWIT | 2024-04-18 | 2024-04-18 | 2024-04-18 | Past Due |  | 2024-07-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Switch-Wood | Repair | 46329629 | T2 EI SAN LUIS OBSP-OCN 19/122A RPR SWTC | ICW
LC | 128574284 | 000/019 | T2 EI COLEMAN-SOUTH 0/19 RPR GYWW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-18 | 2024-04-18 | 2025-03-21 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46389135 | T2 EI COLEMAN-SOUTH 0/19 RPR GYWW | ICW
LC | 128575770 | 069/286 | T2 EI RD MTN-TBLE MTN #1 69/286 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-04-18 | 2024-04-18 | 2025-01-22 | On-Time |  | 2025-04-18 | 2025-04-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306219 | T2 EI RD MTN-TBLE MTN #1 69/286 RMV NEST | ICS
LC | 128575871 | 000/010 | T2 FRUITLAND TAP 000/010 GO95 | EUREKA | ETL.6221.POLE.WOOD | 2024-04-18 | 2024-04-18 | 2025-05-12 | Past Due |  | 2025-04-18 | 2025-04-18 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35547681 | T2 FRUITLAND TAP 000/010 GO95 | 93G
LC | 128575875 | 033/004 | T2 PHILO JCT-ELK 033/004 GO95 | WILLITS | ETL.7780.POLE.WOOD | 2024-04-18 | 2024-04-18 | 2025-01-30 | On-Time |  | 2025-04-18 | 2025-04-18 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35547682 | T2 PHILO JCT-ELK 033/004 GO95 | 93G
LC | 128575894 | 003/058 | T2 EI CARIBOU-WESTWOOD 003/058 RPR GYWW | TABLEMTN | ETL.6300.POLE.NWOD | 2024-04-18 | 2024-04-18 | 2024-07-09 | On-Time |  | 2024-07-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46237045 | T2 EI CARIBOU-WESTWOOD 003/058 RPR GYWW | ICW
LC | 128576028 | 003/059 | T2 EI CARIBOU-WESTWOOD 003/059 RPR GYWW | TABLEMTN | ETL.6300.POLE.NWOD | 2024-04-18 | 2024-04-18 | 2024-09-11 | On-Time |  | 2024-07-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46237046 | T2 EI CARIBOU-WESTWOOD 003/059 RPR GYWW | ICW
LC | 128576075 | 053/399 | T2 EI BRDGVLLE-CTTNWD 053/399R RPR FOND | EUREKA | ETL.1110.POLE.STPS | 2024-04-18 | 2024-04-18 | 2025-03-09 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46289233 | T2 EI BRDGVLLE-CTTNWD 053/399R RPR FOND | ICQ
LC | 128576097 | 034/142 | T2 EI TESLA-METCALF 34/142 RPR INSS | METCALF | ETL.6110.INSL.NCER | 2024-04-18 | 2024-04-18 | 2025-04-07 | On-Time |  | 2025-04-18 | 2025-04-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46286778 | T2 EI TESLA-METCALF 34/142 RPR INSS | ICS
LC | 128576103 | 003/059 | T2 EI CARIBOU-WESTWOOD 003/059 RPR ANCW | TABLEMTN | ETL.6300.POLE.NWOD | 2024-04-18 | 2024-04-18 | 2024-10-19 | On-Time |  | 2024-07-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46479298 | T2 EI CARIBOU-WESTWOOD 003/059 RPR ANCW | ICW
LC | 128576216 | 015/015 | T2 EI EXCHEQUER-MARIPOSA 15/015 RPR CNDW | FRESNO | ETL.8640.INSL.NCER | 2024-04-18 | 2024-04-18 | 2025-04-16 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Conductor-Wood | Repair | 46298266 | T2 EI EXCHEQUER-MARIPOSA 15/015 RPR CNDW | ICW
LC | 128576349 | 015/013 | T2 EI DUNLAP TAP 015/013 COMPLETE | FRESNO | ETL.9061.POLE.WOOD | 2024-04-18 | 2024-04-18 | 2025-03-21 | On-Time |  | 2025-04-18 | 2025-04-18 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT ACCH COMP OH FMOB TR2 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35573197 | T2 EI DUNLAP TAP 015/013 RPL POLE | 93I
LC | 128576919 | 003/061 | T2 EI CARIBOU-WESTWOOD 3/061 RPR ANCW | TABLEMTN | ETL.6300.POLE.NWOD | 2024-04-18 | 2024-04-18 | 2024-07-09 | On-Time |  | 2024-10-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46237049 | T2 EI CARIBOU-WESTWOOD 3/061 RPR ANCW | ICW
LC | 128577366 | 022/207 | T2 RND MTN-CTTNWD #2 22/207 TOUCH | TABLEMTN | ETL.5640.TOWR | 2024-04-18 | 2024-04-18 | 2024-04-18 | Past Due |  | 2024-10-18 | 2025-04-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478119 | T2 RND MTN-CTTNWD #2 22/207 TOUCH | ICQ
LC | 128577503 | 015/010 | T2 EI EXCHEQUER-MARIPSA 15/10 RPR GYWW | FRESNO | ETL.8640.POLE.NWOD | 2024-04-18 | 2024-04-18 | 2025-04-16 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298267 | T2 EI EXCHEQUER-MARIPSA 15/10 RPR GYWW | ICW
LC | 128577534 | 001/029 | T2 EI COLEMAN-SOUTH 1/29 COMPLETE | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-18 | 2024-04-18 | 2025-03-21 | On-Time |  | 2025-04-18 | 2025-04-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556480 | T2 EI COLEMAN-SOUTH 1/29 RPL STRW | 70Y
LC | 128577670 | 026/008 | T2 RIO DLL JCT-BRDGVLLE 26/8 RPL STRW | EUREKA | ETL.7850.POLE.WOOD | 2024-04-18 | 2024-04-18 | 2025-06-13 | Past Due |  | 2025-04-18 | 2025-04-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573025 | T2 EI RIO DLL JCT-BRDGVLLE 26/8 RPL STRW | 70Y
LC | 128577683 | 000/006 | T2 EI LOS ESTEROS-METCALF 0/6 COMPLETE | METCALF | ETL.5353.INSL | 2024-04-18 | 2024-04-18 | 2025-03-27 | On-Time |  | 2025-04-18 | 2025-04-18 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574629 | T2 EI LOS ESTEROS-METCALF RPL INSS IN 7 | 93K
LC | 128577744 | 007/127 | T2 TEMPLETON-TSCDR 07/127 RPR STRW | PISMOBCH | ETL.9410.POLE.WOOD | 2024-04-18 | 2024-04-18 | 2025-04-04 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46329663 | T2 TEMPLETON-TSCDR 07/127 RPR STRW | ICW
LC | 128577808 | 050/252 | T2 EI MALIN-ROUND MTN #2 51/252 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-04-18 | 2024-04-18 | 2025-02-10 | On-Time |  | 2025-04-18 | 2025-04-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46337457 | T2 EI MALIN-ROUND MTN #2 51/252 RPR SHLD | ICS
LC | 128577839 | 014/008 | T2 EI TRINITY-MAPLE CREEK 14/8 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-04-18 | 2024-04-18 | 2025-04-15 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46493392 | T2 EI TRINITY-MAPLE CREEK 14/8 RPR GYWW | ICW
LC | 128577850 | 052/258 | T2 MLN-RUND MTN #2 052/258 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-04-18 | 2024-04-18 | 2025-03-26 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381023 | T2 EI MLN-RUND MTN #2 052/258 RPR GYWT | ICQ
LC | 128580828 | 005/012 | T2 EI BRCBRG JCT-MRPSA TAP 5/12 RPR INSW | FRESNO | ETL.8651.INSL.NCER | 2024-04-19 | 2024-04-18 | 2025-03-28 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298268 | T2 EI BRCBRG JCT-MRPSA TAP 5/12 RPR INSW | ICW
LC | 128580881 | 009/107 | T2 EI WST PNT-VLY SPRNGS 09/107 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-04-19 | 2024-04-18 | 2025-02-12 | On-Time |  | 2025-04-18 | 2025-04-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327502 | T2 EI WST PNT-VLY SPRNGS 09/107 RPR GYWW | ICW
LC | 128581054 | 009/079 | T2 EI SLT SPRNGS-TGR CRK 9/79 BNT STEEL | VICTOR | ETL.3500.TOWR | 2024-04-19 | 2024-04-18 | 2025-03-27 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416490 | T2 EI SLT SPRNGS-TGR CRK 9/79 BNT STEEL | ICQ
LC | 128581063 | 009/073 | T2 SALT SPRINGS-TIGER CREK 9/73 RPR INSS | VICTOR | ETL.3500.INSL.NCER | 2024-04-19 | 2024-04-18 | 2024-04-18 | Past Due |  | 2025-04-18 | 2025-04-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46326986 | T2 EI SLT SPRINGS-TGR CRK 9/73 RPR INSS | ICS
LC | 128584912 | 052/261 | T2 DI MNLN RND MTN#2 52/261 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-04-19 | 2024-04-18 | 2024-05-09 | On-Time |  | 2024-07-18 | 2025-04-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46240046 | T2 DI MNLN RND MTN#2 52/261 RPR OPGW | ICS
LC | 128585407 | 059/240 | T2 DI DIABLO-GATES #1 59/240 RPR SHLD | PISMOBCH | ETL.5960.TOWR | 2024-04-19 | 2024-04-18 | 2025-02-19 | On-Time |  | 2025-04-18 | 2025-04-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329571 | T2 DI DIABLO-GATES #1 59/240 RPR SHLD | ICS
LC | 128617988 | 049/245 | T2 DI MLN-RND MTN #2 49/245 RMV VEG | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-18 | 2024-04-25 | On-Time |  | 2025-04-18 | 2025-04-18 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128618125 | 051/254 | T2 MALIN-ROUND MTN #2 51/254 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-18 | 2024-04-18 | Past Due |  | 2025-04-18 | 2025-04-18 | 93Z | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716724 | T2 EI MALIN-RND MTN #2 RPL ANCT 7 TWRS | 93Z
LC | 128618530 | 055/272 | T2 MALIN-RND MTN #2 55/272 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-18 | 2025-03-24 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381393 | T2 DI MALIN-RND MTN #2 55/272 RPR GYWT | ICQ
LC | 128618616 | 050/249 | T2 DI MALIN RND MTN #2 50/249 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-18 | 2025-03-26 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381027 | T2 DI MALIN RND MTN #2 50/249 RPR GYWT | ICQ
LC | 128618855 | 044/181 | T2 DI DIABLO-MIDWAY #2 44/181 RPR SHLS | PISMOBCH | ETL.5970.TOWR | 2024-04-22 | 2024-04-18 | 2025-04-11 | On-Time |  | 2025-04-18 | 2025-04-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46248670 | T2 DI DIABLO-MIDWAY #2 44/181 RPR SHLS | ICS
LC | 128618890 | 049/246 | T2 MALIN-ROUND MTN #2 49/246 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-18 | 2025-03-26 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381030 | T2 DI MALIN-ROUND MTN #2 49/246 RPR GYWT | ICQ
LC | 128618900 | 048/241 | T2 DI MLIN RND MTN #2 48/241 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-18 | 2025-02-10 | On-Time |  | 2025-04-18 | 2025-04-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46337586 | T2 DI MLIN RND MTN #2 48/241 RPR OPGW | ICS
LC | 128618901 | 048/241 | T2 DI MLIN RND MTN #2 48/241 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-18 | 2025-02-10 | On-Time |  | 2025-04-18 | 2025-04-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46337587 | T2 DI MLIN RND MTN #2 48/241 RPR SHLD | ICS
LC | 128618904 | 053/262 | T2 DI MLIN RND MTN #2 53/262 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-18 | 2025-03-24 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381395 | T2 DI MLIN RND MTN #2 53/262 RPR GYWT | ICQ
LC | 128618954 | 052/259 | T2 DI MLIN-ROUND MTN #2 52/259 RPR SHLS | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-18 | 2025-02-10 | On-Time |  | 2025-04-18 | 2025-04-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338190 | T2 DI MLIN-ROUND MTN #2 52/259 RPR SHLS | ICS
LC | 128618976 | 055/274 | T2 DI MALIN-ROUND MTN #2 55/274 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-18 | 2024-08-29 | On-Time |  | 2025-04-18 | 2025-04-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46250307 | T2 DI MALIN-ROUND MTN #2 55/274 RPR SHLD | ICS
LC | 128619013 | 035/144 | T2 DI DIABLO-MIDWAY #3 35/144 INSP STRT | PISMOBCH | ETL.5980.TOWR | 2024-04-22 | 2024-04-18 | 2024-10-23 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327073 | T2 DI DIABLO-MIDWAY #3 35/144 INSP STRT | ICQ
LC | 128619018 | 033/136 | T2 DI DIABLO-MIDWAY #3 33/136 INSP STRT | PISMOBCH | ETL.5980.TOWR | 2024-04-22 | 2024-04-18 | 2024-10-01 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327071 | T2 DI DIABLO-MIDWAY #3 33/136 INSP STRT | ICQ
LC | 128619033 | 037/151 | T2 DI DIABLO-MIDWAY #2 37/151 INSP STRT | PISMOBCH | ETL.5970.TOWR | 2024-04-22 | 2024-04-18 | 2024-10-23 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327074 | T2 DI DIABLO-MIDWAY #2 37/151 INSP STRT | ICQ
LC | 128619038 | 050/250 | T2 DI MALIN-ROUND MTN #2 50/250 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-18 | 2025-03-26 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381031 | T2 DI MALIN-ROUND MTN #2 50/250 RPR GYWT | ICQ
LC | 129704279 | 003/022 | T3 CASTRO VALLEY-NWARK 3/22 TOUCH | CONCORD | ETL.4450.TOWR | 2024-10-18 | 2024-10-18 | 2025-04-08 | On-Time |  | 2025-04-18 | 2025-04-18 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46489059 | T3 CASTRO VALLEY-NWARK 3/22 TOUCH | ICQ
LC | 123368404 | 027/135 | T2NT EI RND MT-TBLE MT #1 27/135 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2022-04-19 | 2022-04-19 | 2023-08-22 | On-Time |  | 2025-04-19 | 2025-04-19 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO FRAB | Overgrown | Vegetation | Trim
LC | 123369234 | 027/134 | T2NT EI RND MT-TBLE MT #1 27/168 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2022-04-19 | 2022-04-19 | 2023-08-23 | On-Time |  | 2025-04-19 | 2025-04-19 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO FRAB | Overgrown | Vegetation | Trim
LC | 123467606 | 040/341 | T2NT DI PIT#1-COTTONWD 40/341 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2022-04-30 | 2022-04-19 | 2023-08-03 | On-Time |  | 2025-04-19 | 2025-04-19 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45639725 | T2 DI PIT #1-COTTONWOOD 40/341 BNT STEEL | ICQ
LC | 123491599 | 000/003B | T3NT DI UKH-HPLND-CLVRDL 0/3B RPL HRDW | WILLITS | ETL.4050.POLE.WOOD | 2022-05-03 | 2022-04-19 | 2023-10-20 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 45593093 | T3 DI UKIAH-HOPLND-CLVRDL 0/03B RPL HRDW | ICW
LC | 128581952 | 007/085 | T2 VEDDER TAP 07/85C RPL POLE | MIDWAY | ETL.2141.POLE.WDPS | 2024-04-19 | 2024-04-19 | 2024-04-29 | On-Time |  | 2024-07-19 | 2025-04-19 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35536714 | T2 VEDDER TAP 008/094 GO95 CLEAR | 70Y
LC | 128581971 | 007/085 | T2 VEDDER TAP 07/85R RPL POLE | MIDWAY | ETL.2141.POLE.WDPS | 2024-04-19 | 2024-04-19 | 2024-04-29 | On-Time |  | 2024-07-19 | 2025-04-19 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35536714 | T2 VEDDER TAP 008/094 GO95 CLEAR | 70Y
LC | 128581972 | 006/075 | T2 VEDDER TAP 06/75 RPL POLE | MIDWAY | ETL.2141.POLE.WOOD | 2024-04-19 | 2024-04-19 | 2024-04-30 | On-Time |  | 2024-07-19 | 2025-04-19 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35536714 | T2 VEDDER TAP 008/094 GO95 CLEAR | 70Y
LC | 128581973 | 007/085 | T2 VEDDER TAP 07/85L RPL POLE | MIDWAY | ETL.2141.POLE.WDPS | 2024-04-19 | 2024-04-19 | 2024-04-29 | On-Time |  | 2024-07-19 | 2025-04-19 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35536714 | T2 VEDDER TAP 008/094 GO95 CLEAR | 70Y
LC | 128582274 | 013/003 | T2 EI OAKHURST TAP 013/003 RPR GYWW | FRESNO | ETL.1252.POLE.NWOD | 2024-04-19 | 2024-04-19 | 2025-02-27 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298189 | T2 EI OAKHURST TAP 013/003 RPR GYWW | ICW
LC | 128582317 | 025/153 | T2 EI TSLA-SALDO-MNTECA 26/165 RPR GYWW | VICTOR | ETL.4000.POLE.WOOD | 2024-04-19 | 2024-04-19 | 2025-02-25 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46325890 | T2 EI TSLA-SALDO-MNTECA 26/165 RPR GYWW | ICW
LC | 128582617 | 004/027 | T2 WV BALCH-SANGER 004/027 INS DAMS | FRESNO | ETL.1050.INSL.NCER | 2024-04-19 | 2024-04-19 | 2025-05-12 | Past Due |  | 2025-04-19 | 2025-04-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Steel | Install | 46298227 | T2 WV BALCH-SANGER 004/027 INS DAMS | ICS
LC | 128582892 | 012/010 | T2 EI OAKHURST TAP 012/010 RPR INSW | FRESNO | ETL.1252.INSL.NCER | 2024-04-19 | 2024-04-19 | 2024-10-30 | On-Time |  | 2024-07-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46239780 | T2 EI OAKHURST TAP 012/010 RPR INSW | ICW
LC | 128582932 | 004/025 | T2 METCALF-HICKS 1 & 2 4/25 RMV VEG | METCALF | ETL.4317.TOWR | 2024-04-19 | 2024-04-19 | 2025-05-23 | Past Due |  | 2025-04-19 | 2025-04-19 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128582949 | 022/195 | T2 EI BRDGEVLE-COTNWD 22/195L RPL ANCW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-19 | 2024-04-19 | 2025-03-22 | On-Time |  | 2025-04-19 | 2025-04-19 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Anchor-Wood | Replace | 35604404 | T2 EI BRDGEVLE-COTNWD 22/195L RPL ANCW | 93E
LC | 128582988 | 063/264 | T2 EI RND MTN-TBL MTN #1 63/264 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-19 | 2024-04-19 | 2024-06-25 | On-Time |  | 2025-04-19 | 2025-04-19 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128583016 | 063/267 | T2 EI RND MTN-TBL MTN #1 63/267 RPL INSS | TABLEMTN | ETL.6060.INSL | 2024-04-19 | 2024-04-19 | 2025-01-22 | On-Time |  | 2025-04-19 | 2025-04-19 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | Missing | Insulator-Steel | Install | 35569940 | T2 EI RND MTN-TBL MTN #1 RPL INSS 9 TWRS | 93K
LC | 128583040 | 063/266 | T2 EI RND MTN-TBL MTN #1 63/266 RPL INSS | TABLEMTN | ETL.6060.INSL | 2024-04-19 | 2024-04-19 | 2025-01-22 | On-Time |  | 2025-04-19 | 2025-04-19 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | Missing | Insulator-Steel | Install | 35569940 | T2 EI RND MTN-TBL MTN #1 RPL INSS 9 TWRS | 93K
LC | 128583072 | 063/263 | T2 EI RD MTN-TBL MTN #1 63/263 RPL INSS | TABLEMTN | ETL.6060.INSL | 2024-04-19 | 2024-04-19 | 2025-01-24 | On-Time |  | 2025-04-19 | 2025-04-19 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35606768 | T2 EI RD MTN-TBL MTN #1 63/263 RPL INSS | 93K
LC | 128583206 | 074/305 | T2 EI RND MTN-TBL MTN #2 74/305 MASTIC | TABLEMTN | ETL.6070.TOWR | 2024-04-19 | 2024-04-19 | 2025-01-29 | On-Time |  | 2025-04-19 | 2025-04-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46310379 | T2NT EI RND MTN-TBL MTN #2 74/305 MASTIC | ICQ
LC | 128583259 | 069/285 | T2 EI RD MTN-TBLE MTN #1 69/286 RPR STRT | TABLEMTN | ETL.6060.TOWR | 2024-04-19 | 2024-04-19 | 2025-03-10 | On-Time |  | 2025-04-19 | 2025-04-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310378 | T2 EI RD MTN-TBLE MTN #1 69/286 RPR STRT | ICQ
LC | 128583316 | 012/156 | T2 WV KESWICK-TRINITY 12/156 INS DAMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-04-19 | 2024-04-19 | 2025-03-31 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46311277 | T2 WV KESWICK-TRINITY 12/156 INS DAMW | ICW
LC | 128583470 | 000/001 | T2 CHRISTIE-FRANKLIN #1 0/001 RPL STRW | CONCORD | ETL.6350.POLE.WOOD | 2024-04-19 | 2024-04-19 | 2025-06-06 | Past Due |  | 2025-04-19 | 2025-04-19 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | Rotten | Structure-Wood | Replace | 35573103 | T2 CHRISTIE-FRANKLIN #1 0/001 RPL STRW | 70Y
LC | 128583730 | 45 | T2 EI IONE TAP 000/001 RPR SWITCH | VICTOR | ETL.8253.SWIT | 2024-04-19 | 2024-04-19 | 2025-03-11 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK ACCM ACCH COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Switch-Wood | Repair | 46325891 | T2 EI IONE TAP 000/001 RPR SWITCH | ICW
LC | 128584071 | 016/121 | T2 EI ELECTRA-BELLT 16/121 RMV DBRS CNDS | VICTOR | ETL.4670.INSL | 2024-04-19 | 2024-04-19 | 2025-03-20 | On-Time |  | 2025-04-19 | 2025-04-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD REAR CLR ACCL COMP OH FMOB TR2 PRTO NTDE | Debris/Nest/etc. | Conductor-Steel | Remove | 46326987 | T2 EI ELECTRA-BELLT 16/121 RMV DBRS CNDS | ICS
LC | 128584152 | 017/154 | T2 EI CTNWD-HMBLDT NO. 2 17/154 RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-19 | 2024-04-19 | 2025-02-06 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311097 | T2 EI CTNWD-HMBLDT NO. 2 17/154 RPR GYWW | ICW
LC | 128584153 | 017/154 | T2 EI CTNWD-HMBLDT NO. 2 17/154 RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-19 | 2024-04-19 | 2025-02-06 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311096 | T2 EI CTNWD-HMBLDT NO. 2 17/154 RPR GYWW | ICW
LC | 128584456 | 014/016 | T2 EI EXCHEQUER-MARIPOSA 14/16 RPR ANCW | FRESNO | ETL.8640.POLE.NWOD | 2024-04-19 | 2024-04-19 | 2024-08-02 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46298190 | T2 EI EXCHEQUER-MARIPOSA 14/16 RPR ANCW | ICW
LC | 128584465 | 035/009 | T2 EI FORT ROSS-GUALALA 035/009 RPR ANCW | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-04-19 | 2024-04-19 | 2024-06-10 | On-Time |  | 2024-10-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46239675 | T2 EI FORT ROSS-GUALALA 035/009 RPR ANCW | ICW
LC | 128584633 | 035/004 | T2 EI FORT ROSS-GUALALA 035/004 COMPLETE | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-04-19 | 2024-04-19 | 2025-03-21 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46305933 | T2 EI FORT ROSS-GUALALA 035/004 RPR STRW | ICW
LC | 128584662 | 065/272 | T2 EI RND MTN-TBL MTN #1 65/272 RPR ANCT | TABLEMTN | ETL.6060.TOWR | 2024-04-19 | 2024-04-19 | 2024-06-13 | On-Time |  | 2024-10-19 | 2025-04-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Tower | Repair | 46248665 | T2 EI RND MTN-TBL MTN #1 65/272 RPR ANCT | ICQ
LC | 128584663 | 064/268 | T2 EI RND MTN-TBL MTN #1 64/268 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-19 | 2024-04-19 | 2025-04-23 | Past Due |  | 2025-04-19 | 2025-04-19 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128584673 | 064/268 | T2 EI RND MTN-TBL MTN #1 64/268 RPL INSS | TABLEMTN | ETL.6060.INSL | 2024-04-19 | 2024-04-19 | 2025-01-22 | On-Time |  | 2025-04-19 | 2025-04-19 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | Missing | Insulator-Steel | Install | 35569940 | T2 EI RND MTN-TBL MTN #1 RPL INSS 9 TWRS | 93K
LC | 128584674 | 064/270 | T2 EI RND MTN-TBL MTN #1 64/270 RPL INSS | TABLEMTN | ETL.6060.INSL | 2024-04-19 | 2024-04-19 | 2025-01-23 | On-Time |  | 2025-04-19 | 2025-04-19 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | Missing | Insulator-Steel | Install | 35569940 | T2 EI RND MTN-TBL MTN #1 RPL INSS 9 TWRS | 93K
LC | 128584680 | 065/272 | T2 EI RND MTN-TBL MTN #1 65/272 RPL INSS | TABLEMTN | ETL.6060.INSL | 2024-04-19 | 2024-04-19 | 2025-01-25 | On-Time |  | 2025-04-19 | 2025-04-19 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | Missing | Insulator-Steel | Install | 35569940 | T2 EI RND MTN-TBL MTN #1 RPL INSS 9 TWRS | 93K
LC | 128584899 | 011/089 | T2 EI TGR CRK-VLY SPRNG 11/89 TOUCH | VICTOR | ETL.5790.TOWR | 2024-04-19 | 2024-04-19 | 2025-02-11 | On-Time |  | 2024-10-19 | 2025-04-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472914 | T2 EI TGR CRK-VLY SPRNG 11/89 TOUCH | ICQ
LC | 128584993 | 014/013 | T2 EI EXCHEQUER-MARIPOSA 14/13 TOUCH | FRESNO | ETL.8640.POLE.NWOD | 2024-04-19 | 2024-04-19 | 2025-04-16 | On-Time |  | 2024-10-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SPCR ACCM ACCH COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46494029 | T2 EI EXCHEQUER-MARIPOSA 14/13 TOUCH | ICW
LC | 128584999 | 016/120 | T2 WV CAYUCOS-CAMBRIA 16/120 RPR INSW | PISMOBCH | ETL.8560.INSL.NCER | 2024-04-19 | 2024-04-19 | 2025-02-27 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Insulator-Wood | Repair | 46391107 | T2 WV CAYUCOS-CAMBRIA 16/120 RPR INSW | ICW
LC | 128585014 | 047/234 | T2 EI MALIN-RND MTN #2 47/234 RMV NEST | TABLEMTN | ETL.6020.TOWR | 2024-04-19 | 2024-04-19 | 2025-02-09 | On-Time |  | 2025-04-19 | 2025-04-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46337583 | T2 EI MALIN-RND MTN #2 47/234 RMV NEST | ICS
LC | 128585098 | 033/008 | T2 EI RIO DLL JCT-BRDGVLLE 33/8 RPR GYWW | EUREKA | ETL.7850.POLE.NWOD | 2024-04-19 | 2024-04-19 | 2025-04-15 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345767 | T2 EI RIO DLL JCT-BRDGVLLE 33/8 RPR GYWW | ICW
LC | 128585120 | 034/001 | T2 RIO DLL JCT-BRDGVLLE 34/1 RPR STRW | EUREKA | ETL.7850.POLE.WOOD | 2024-04-19 | 2024-04-19 | 2024-04-19 | Past Due |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46545340 | T2 RIO DLL JCT-BRDGVLLE 34/1 RPR STRW | ICW
LC | 128585124 | 034/009 | T2 EI RIO DLL JCT-BRDGVLLE 34/9 RPL STRW | EUREKA | ETL.7850.POLE.WOOD | 2024-04-19 | 2024-04-19 | 2025-06-17 | Past Due |  | 2025-04-19 | 2025-04-19 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573191 | T2 EI RIO DLL JCT-BRDGVLLE 34/9 RPL STRW | 70Y
LC | 128585131 | 033/010 | T2 RIO DLL JCT-BRDGVLE 33/10 RPL INSW | EUREKA | ETL.7850.INSL.CERA | 2024-04-19 | 2024-04-19 | 2025-06-20 | Past Due |  | 2025-04-19 | 2025-04-19 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573123 | T2 EI RIO DLL JCT-BRDGVLE 33/10 RPL INSW | 93I
LC | 128585175 | 028/113 | T2 DI DIABLO-MIDWAY #2 28/113 RPR SHLS | PISMOBCH | ETL.5970.TOWR | 2024-04-19 | 2024-04-19 | 2025-04-12 | On-Time |  | 2025-04-19 | 2025-04-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329583 | T2 DI DIABLO-MIDWAY #2 28/113 RPR SHLS | ICS
LC | 128585265 | 026/159 | T2 EI TSLA-SALDO-MNTECA 26/159 RPR GYWW | VICTOR | ETL.4000.POLE.WOOD | 2024-04-19 | 2024-04-19 | 2025-02-25 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46325892 | T2 EI TSLA-SALDO-MNTECA 26/159 RPR GYWW | ICW
LC | 128585367 | 009/086 | T2 EI UKIAH HPLND CLVRDLE 9/86R BACKFILL | WILLITS | ETL.4050.POLE.STPS | 2024-04-19 | 2024-04-19 | 2025-02-12 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46414832 | T2 EI UKIAH HPLND CLVRDLE 9/86R BACKFILL | ICW
LC | 128585381 | 009/086 | T2 EI UKIAH-HOPLND-CLVRDL 9/86L BACKFILL | WILLITS | ETL.4050.POLE.STPS | 2024-04-19 | 2024-04-19 | 2025-02-12 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46414833 | T2 EI UKIAH-HOPLND-CLVRDL 9/86L BACKFILL | ICW
LC | 128588626 | 007/003A | T2 EI DUNLAP TAP 007/003A RMV VEG | FRESNO | ETL.9061.POLE.NWOD | 2024-04-19 | 2024-04-19 | 2025-05-05 | Past Due |  | 2025-04-19 | 2025-04-19 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128607628 | 008/067 | T2 EI SLT SPRNGS-TGR CRK 8/67 BNT STEEL | VICTOR | ETL.3500.TOWR | 2024-04-20 | 2024-04-19 | 2025-03-27 | On-Time |  | 2025-04-19 | 2025-04-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416492 | T2 EI SLT SPRNGS-TGR CRK 8/67 BNT STEEL | ICQ
LC | 128607671 | 008/066 | T2 EI SLT SPRNGS-TGR CRK 8/66 BNT STEEL | VICTOR | ETL.3500.TOWR | 2024-04-20 | 2024-04-19 | 2025-03-27 | On-Time |  | 2025-04-19 | 2025-04-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416493 | T2 EI SLT SPRNGS-TGR CRK 8/66 BNT STEEL | ICQ
LC | 128607672 | 008/070 | T2 SLT SPRINGS-TIGR CRK 8/70 CANCEL | VICTOR | ETL.3500.INSL | 2024-04-20 | 2024-04-19 | 2024-04-19 | Past Due |  | 2025-04-19 | 2025-04-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46326989 | T2 EI SLT SPRINGS-TIGR CRK 8/70 RPR INSS | ICS
LC | 128608152 | 004/023 | T2 EI METCALF-EL PATIO #1 04/23 RPR FOND | METCALF | ETL.2500.TOWR | 2024-04-20 | 2024-04-19 | 2025-02-26 | On-Time |  | 2025-04-19 | 2025-04-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46298835 | T2 EI METCALF-EL PATIO #1 04/23 RPR FOND | ICQ
LC | 128617833 | 053/265 | T2 MALIN-ROUND MTN #2 53/265 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-19 | 2025-03-24 | On-Time |  | 2025-04-19 | 2025-04-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381392 | T2 DI MALIN-ROUND MTN #2 53/265 RPR GYWT | ICQ
LC | 128618064 | 027/109 | T2 DI DIABLO-MDWY #2 027/109 RPR SHLS | PISMOBCH | ETL.5970.TOWR | 2024-04-22 | 2024-04-19 | 2024-05-22 | On-Time |  | 2025-04-19 | 2025-04-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46249436 | T2 DI DIABLO-MDWY #2 027/109 RPR SHLS | ICS
LC | 128618196 | 041/167 | T2 DI DIABLO-MDWY #3 041/167 INSP STRT | PISMOBCH | ETL.5980.TOWR | 2024-04-22 | 2024-04-19 | 2024-10-24 | On-Time |  | 2025-04-19 | 2025-04-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327075 | T2 DI DIABLO-MDWY #3 041/167 INSP STRT | ICQ
LC | 128618197 | 041/167 | T2 DI DIABLO-MIDWAY #3 41/167 RPR SHLD | PISMOBCH | ETL.5980.TOWR | 2024-04-22 | 2024-04-19 | 2025-04-11 | On-Time |  | 2025-04-19 | 2025-04-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329622 | T2 DI DIABLO-MDWY #3 041/167 RPR SHLS | ICS
LC | 128618228 | 027/108B | T2 DI DIABLO-MIDWAY #2 27/108B RPR INSS | PISMOBCH | ETL.5970.INSL.NCER | 2024-04-22 | 2024-04-19 | 2025-04-12 | On-Time |  | 2025-04-19 | 2025-04-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329577 | T2 DI DIABLO-MIDWAY #2 27/108B RPR INSS | ICS
LC | 128618288 | 013/051 | T2 DIABLO-MIDWAY #2 13/51 TOUCH | PISMOBCH | ETL.5970.TOWR | 2024-04-22 | 2024-04-19 | 2025-05-13 | Past Due |  | 2024-10-19 | 2025-04-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476143 | T2 DI DIABLO-MIDWAY #2 13/51 TOUCH | ICQ
LC | 128618525 | 091/464 | T2 DI MALIN-RND MNTN #2 91/464 RPR INSS | TABLEMTN | ETL.6020.INSL.NCER | 2024-04-22 | 2024-04-19 | 2025-02-05 | On-Time |  | 2025-04-19 | 2025-04-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46337585 | T2 DI MALIN-RND MNTN #2 91/464 RPR INSS | ICS
LC | 128618605 | 009/111B | T2 DI DRUM-SMMT #1 9/111B RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-04-22 | 2024-04-19 | 2024-05-23 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46254545 | T2 DI DRUM-SMMT #1 9/111B RPR GYWW | ICW
LC | 128618692 | 055/276 | T2 DI MALIN-RND MNTN #2 55/276 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-19 | 2024-05-10 | On-Time |  | 2024-07-19 | 2025-04-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46240047 | T2 DI MALIN-RND MNTN #2 55/276 RPR OPGW | ICS
LC | 128618699 | 055/276 | T2 DI MALIN-RND MNTN #2 55/276 RPR SHLS | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-19 | 2024-05-10 | On-Time |  | 2025-04-19 | 2025-04-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46240048 | T2 DI MALIN-RND MNTN #2 55/276 RPR SHLS | ICS
LC | 128618701 | 027/455 | T2 DI KESWICK-TRINITY 027/455 GO95 | TABLEMTN | ETL.7270.POLE.WOOD | 2024-04-22 | 2024-04-19 | 2025-04-17 | On-Time |  | 2025-04-19 | 2025-04-19 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35573712 | T2 DI KESWICK-TRINITY 027/455 GO95 | 93G
LC | 128618813 | 028/489 | T2 DI KESWICK-TRINITY 28/489 RPR STRW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-04-22 | 2024-04-19 | 2025-04-02 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46493104 | T2 DI KESWICK-TRINITY 28/489 RPR STRW | ICW
LC | 128618969 | 007/087A | T2 DI DRUM-SUMMIT #2 7/87A COMPLETE | SACTO | ETL.1450.POLE.NWOD | 2024-04-22 | 2024-04-19 | 2024-05-16 | On-Time |  | 2024-10-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46252816 | T2 DI DRUM-SUMMIT #2 7/87A COMPLETE | ICW
LC | 128698798 | 007/081C | T2 DI DRUM-SMMT#2 7/81C INSP STRW | SACTO | ETL.1450.POLE.NWOD | 2024-05-01 | 2024-04-19 | 2024-06-16 | On-Time |  | 2025-04-19 | 2025-04-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46265836 | T2 DI DRUM-SMMT#2 7/81C INSP STRW | ICW
LC | 123373399 | 088/446 | T2NT EI MALIN-RND MTN #2 88/446 BENT STL | TABLEMTN | ETL.6020.TOWR | 2022-04-20 | 2022-04-20 | 2023-08-22 | On-Time |  | 2025-04-20 | 2025-04-20 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45617406 | T2 EI MALIN-ROUND MTN #2 88/446 BENT STL | ICQ
LC | 123377820 | 086/435 | T2NT EI MLIN-RUND MTN #2 86/435 BENT STL | TABLEMTN | ETL.6020.TOWR | 2022-04-20 | 2022-04-20 | 2023-08-22 | On-Time |  | 2025-04-20 | 2025-04-20 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45616944 | T2 EI MALIN-ROUND MTN #2 86/435 BENT STL | ICQ
LC | 123397310 | 014/397 | T3NT DI CLGATE-ALLEGHANY 14/397 RPL SPLW | SACTO | ETL.6470.INSL.NCER | 2022-04-22 | 2022-04-20 | 2023-06-05 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR3N PRTO AIR | No Good/Out of Stdrd | Splice-Wood | Replace | 45686127 | T3 DI COLGATE-ALLEGHANY 14/397 RPL SPLW | ICW
LC | 123405147 | 015/094 | T2NT DI STNSLS-MNTCA#2 015/094 BNT STEEL | VICTOR | ETL.3820.TOWR | 2022-04-25 | 2022-04-20 | 2024-11-26 | On-Time |  | 2025-04-20 | 2025-04-20 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB SR23 | No Good/Out of Stdrd | Structure-Tower | Repair | 46134699 | T2NT DI STNSLS-MNTCA#2 015/094 BNT STEEL | ICQ
LC | 123459621 | 004/038 | T2NT DI PT #3 CRBRY SS 4/38 RPL SPLS | TABLEMTN | ETL.5450.INSL.NCER | 2022-04-29 | 2022-04-20 | 2023-12-09 | On-Time |  | 2025-04-20 | 2025-04-20 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Splice-Steel | Replace | 45277070 | T2 DI PT #3 CRBRY SS 4/38 RPL SPLS | ICS
LC | 123561811 | 000/011 | T2NT DI WSHN CPRMN 0/11 RPR FOND CMPLT | FRESNO | ETL.9330.TOWR | 2022-05-10 | 2022-04-20 | 2023-01-04 | On-Time |  | 2025-04-20 | 2025-04-20 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2N PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45617045 | T2 DI WSHN CPRMN 0/11 RPR FOND | ICQ
LC | 128607620 | 054/010 | T2 FORT ROSS-GUALALA 054/010 CANCEL | LAKEVLLE | ETL.6980.INSL.NCER | 2024-04-20 | 2024-04-20 | 2024-04-20 | Past Due |  | 2025-04-20 | 2025-04-20 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Replace | 35564468 | T2 FORT ROSS-GUALALA 054/010 RPL INSW | 93I
LC | 128608036 | 007/132 | T2 CARIBOU-WESTWD 7/132 RPR INSW | TABLEMTN | ETL.6300.INSL.NCER | 2024-04-20 | 2024-04-20 | 2024-07-10 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46237047 | T2 CARIBOU-WESTWD 07/132 RPR INSW | ICW
LC | 128608053 | 009/086 | T2 EI BRIDGEVILLE-CTTNWD 9/86L RPL POLE | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-20 | 2024-04-20 | 2025-04-06 | On-Time |  | 2025-04-20 | 2025-04-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35555552 | T2 EI BRIDGEVILLE-CTTNWD 9/86L RPL POLE | 70Y
LC | 128608055 | 009/086 | T2 EI BRIDGEVILLE-CTTNWD 9/86R RPL POLE | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-20 | 2024-04-20 | 2025-04-06 | On-Time |  | 2025-04-20 | 2025-04-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35555552 | T2 EI BRIDGEVILLE-CTTNWD 9/86L RPL POLE | 70Y
LC | 128608164 | 036/003 | T2 EI FORT ROSS-GUALALA 036/003 COMPLETE | LAKEVLLE | ETL.6980.INSL.NCER | 2024-04-20 | 2024-04-20 | 2025-03-21 | On-Time |  | 2025-04-20 | 2025-04-20 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574057 | T2 EI FORT ROSS-GUALALA 036/003 RPL INSW | 93I
LC | 128608227 | 014/010 | T2 EXCHEQUER-MARIPOSA 14/10 RPR CNDW | FRESNO | ETL.8640.INSL.NCER | 2024-04-20 | 2024-04-20 | 2025-04-15 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SPCR ACCH COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Conductor-Wood | Repair | 46298191 | T2 EI EXCHEQUER-MARIPOSA 14/10 RPR CNDW | ICW
LC | 128608266 | 014/009 | T2 EI EXCHEQUER-MARIPOSA 14/09 RPR STRW | FRESNO | ETL.8640.POLE.NWOD | 2024-04-20 | 2024-04-20 | 2025-04-15 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46298192 | T2 EI EXCHEQUER-MARIPOSA 14/09 RPR STRW | ICW
LC | 128608298 | 037/000 | T2 EI FORT ROSS-GUALALA 037/000 GO95 | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-04-20 | 2024-04-20 | 2025-04-19 | On-Time |  | 2025-04-20 | 2025-04-20 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35574058 | T2 EI FORT ROSS-GUALALA 037/000 GO95 | 93G
LC | 128608389 | 014/007 | T2 EI EXCHEQUER-MARIPOSA 14/07 RPL INSW | FRESNO | ETL.8640.INSL.NCER | 2024-04-20 | 2024-04-20 | 2025-04-15 | On-Time |  | 2025-04-20 | 2025-04-20 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SPCR ACCH COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573230 | T2 EI EXCHEQUER-MARIPOSA 14/07 RPL INSW | 93I
LC | 128608432 | 019/010 | T2 BRIDGEVILLE-GARBRVILLE 19/10 RPR INSW | EUREKA | ETL.6220.INSL.NCER | 2024-04-20 | 2024-04-20 | 2024-04-20 | Past Due |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46345768 | T2 EI BRDGVLL-GRBRVLL 19/10 RPR INSW | ICW
LC | 128609082 | 011/057 | T2 EI RND MTN-TBL MTN #1 11/57 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-20 | 2024-04-20 | 2024-05-24 | On-Time |  | 2025-04-20 | 2025-04-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128609083 | 010/055 | T2 EI RND MTN-TBL MTN #1 10/55 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-04-20 | 2024-04-20 | 2024-07-01 | On-Time |  | 2025-04-20 | 2025-04-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128609097 | 011/057 | T2 EI RND MTN-TBL MTN #1 11/57 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-04-20 | 2024-04-20 | 2025-01-28 | On-Time |  | 2025-04-20 | 2025-04-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306281 | T2 EI RND MTN-TBL MTN #1 11/57 RMV NEST | ICS
LC | 128609107 | 006/051 | T2 EI SLT SPRINGS-TIGR CRK 6/51 COTTER | VICTOR | ETL.3500.INSL.NCER | 2024-04-20 | 2024-04-20 | 2024-07-21 | On-Time |  | 2025-04-20 | 2025-04-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC SWRK COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46236474 | T2 EI SLT SPRINGS-TIGR CRK 6/51 COTTER | ICS
LC | 128609155 | 034/006 | T2 RIO DLL JCT-BRDGVLLE 34/6 RPL STRW | EUREKA | ETL.7850.POLE.WOOD | 2024-04-20 | 2024-04-20 | 2024-04-20 | Past Due |  | 2025-04-20 | 2025-04-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573188 | T2 EI RIO DLL JCT-BRDGVLLE 34/6 RPL STRW | 70Y
LC | 128609156 | 035/001 | T2 EI RIO DLL JCT-BRDGVLLE 35/01 RMV VEG | EUREKA | ETL.7850.POLE.WOOD | 2024-04-20 | 2024-04-20 | 2025-04-15 | On-Time |  | 2025-04-20 | 2025-04-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128609177 | 035/000 | T2 EI RIO DLL JCT-BRDGVLLE 35/0 RPL STRW | EUREKA | ETL.7850.POLE.WOOD | 2024-04-20 | 2024-04-20 | 2025-06-17 | Past Due |  | 2025-04-20 | 2025-04-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573193 | T2 EI RIO DLL JCT-BRDGVLLE 35/0 RPL STRW | 70Y
LC | 128609191 | 054/267 | T2 EI MALIN-ROUND MTN #2 54/267 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-04-20 | 2024-04-20 | 2025-02-10 | On-Time |  | 2025-04-20 | 2025-04-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46337584 | T2 EI MALIN-ROUND MTN #2 54/267 RPR SHLD | ICS
LC | 128609236 | 045/222 | T2 EI CORTINA-MNDCNO #1 045/222 RPR FOND | WILLITS | ETL.1330.TOWR | 2024-04-20 | 2024-04-20 | 2025-03-21 | On-Time |  | 2025-04-20 | 2025-04-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46290154 | T2 EI CORTINA-MNDCNO #1 045/222 RPR FOND | ICQ
LC | 128609248 | 014/001 | T2NT EXCHEQUER-MARIPOSA 14/1 RPR ROAD | FRESNO | ETL.8640.POLE.NWOD | 2024-04-20 | 2024-04-20 | 2025-04-22 | Past Due |  | 2027-04-20 | 2025-04-20 | 932 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP OTHR REMT SPCR ACCH COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Road | Repair | 46388866 | T2NT EXCHEQUER-MARIPOSA 14/1 RPR ROAD | CHS
LC | 128609260 | 017/159 | T2 EI BRIDGEVIL-CTTNW 17/159L RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-20 | 2024-04-20 | 2025-02-07 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311094 | T2 EI BRIDGEVIL-CTTNW 17/159L RPR GYWW | ICW
LC | 128609272 | 017/159 | T2 EI BRIDGEVIL-CTTNW 17/159R RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-20 | 2024-04-20 | 2025-02-07 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311093 | T2 EI BRIDGEVIL-CTTNW 17/159R RPR GYWW | ICW
LC | 128609282 | 004/029 | T2 EI KRCKHF-CLVS-SNGR #1 4/29 RMV VEG | FRESNO | ETL.1890.TOWR | 2024-04-20 | 2024-04-20 | 2025-03-26 | On-Time |  | 2025-04-20 | 2025-04-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128609302 | 011/079 | T2 EI WISHON-COPPERMINE 11/79 TOUCH | FRESNO | ETL.9330.TOWR | 2024-04-20 | 2024-04-20 | 2025-04-02 | On-Time |  | 2024-07-20 | 2025-04-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46477345 | T2 EI WISHON-COPPERMINE 11/79 TOUCH | ICQ
LC | 128609366 | 009/004 | T2 EI DUNLAP TAP 009/004 RPR GYWW | FRESNO | ETL.9061.POLE.NWOD | 2024-04-20 | 2024-04-20 | 2025-03-21 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298194 | T2 EI DUNLAP TAP 009/004 RPR GYWW | ICW
LC | 128609384 | 045/220 | T2 CORTINA-MNDCINO #1 45/220 RMV NEST | WILLITS | ETL.1330.TOWR | 2024-04-20 | 2024-04-20 | 2024-04-20 | Past Due |  | 2025-04-20 | 2025-04-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46414839 | T2 EI CORTINA-MNDCINO #1 45/220 RMV NEST | ICS
LC | 128609407 | 013/016 | T2 EI EXCHEQUER-MARIPOSA 13/16 RPL INSW | FRESNO | ETL.8640.INSL.NCER | 2024-04-20 | 2024-04-20 | 2025-04-15 | On-Time |  | 2025-04-20 | 2025-04-20 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573229 | T2 EI EXCHEQUER-MARIPOSA 13/16 RPL INSW | 93I
LC | 128609414 | 004/022 | T2 EI VACA-LAKEVILLE #1 4/22 RMV NEST | SACTO | ETL.5840.TOWR | 2024-04-20 | 2024-04-20 | 2025-02-04 | On-Time |  | 2025-04-20 | 2025-04-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46403743 | T2 EI VACA-LAKEVILLE #1 4/22 RMV NEST | ICS
LC | 128609422 | 004/023 | T2 EI VACA-LAKEVILLE #1 4/23 RMV NEST | SACTO | ETL.5840.TOWR | 2024-04-20 | 2024-04-20 | 2025-02-04 | On-Time |  | 2025-04-20 | 2025-04-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46403744 | T2 EI VACA-LAKEVILLE #1 4/23 RMV NEST | ICS
LC | 128609463 | 027/111 | T2 EI TESLA-METCALF 27/11 RPR FOND | METCALF | ETL.6110.TOWR | 2024-04-20 | 2024-04-20 | 2025-02-24 | On-Time |  | 2025-04-20 | 2025-04-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46298834 | T2 EI TESLA-METCALF 27/11 RPR FOND | ICQ
LC | 128609471 | 006/131 | T2 EI COLEMAN-SOUTH 6/131 RPR INSW | TABLEMTN | ETL.6450.INSL.CERA | 2024-04-20 | 2024-04-20 | 2025-03-22 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Insulator-Wood | Repair | 46389136 | T2 EI COLEMAN-SOUTH 6/131 RPR INSW | ICW
LC | 128609477 | 004/053 | T2 EI PIT #5-ROUND MTN #2 4/053 RPR JUMW | TABLEMTN | ETL.5430.INSL.NCER | 2024-04-20 | 2024-04-20 | 2025-03-03 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Jumper-Wood | Repair | 46454335 | T2 EI PIT #5-ROUND MTN #2 4/053 RPR JUMW | ICW
LC | 128609482 | 002/047 | T2 EI COLEMAN-SOUTH 2/47 RPL STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-20 | 2024-04-20 | 2025-03-21 | On-Time |  | 2025-04-20 | 2025-04-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556780 | T2 EI COLEMAN-SOUTH 2/47 RPL STRW | 70Y
LC | 128609490 | 002/051 | T2 EI COLEMAN-SOUTH 2/51 RPR INSW | TABLEMTN | ETL.6450.INSL.CERA | 2024-04-20 | 2024-04-20 | 2025-03-24 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46389137 | T2 EI COLEMAN-SOUTH 2/51 RPR INSW | ICW
LC | 128609507 | 006/073 | T2 EI WST PNT-VLLY SPRNGS 6/073 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-04-20 | 2024-04-20 | 2025-02-06 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327601 | T2 EI WST PNT-VLLY SPRNGS 6/073 RPR GYWW | ICW
LC | 128609550 | 027/000 | T2 EI TRINITY-MAPLE CREEK 27/0R COMPLETE | EUREKA | ETL.8170.POLE.WDPS | 2024-04-20 | 2024-04-20 | 2025-04-13 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345770 | T2 EI TRINITY-MAPLE CREEK 27/0R RPR GYWW | ICW
LC | 128609564 | 026/008 | T2 EI TRINITY-MAPLE CREEK 26/8 COMPLETE | EUREKA | ETL.8170.POLE.WDPS | 2024-04-20 | 2024-04-20 | 2025-04-12 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46345769 | T2 EI TRINITY-MAPLE CREEK 26/8 RPR ANCW | ICW
LC | 128609570 | 007/084 | T2 EI WST PNT-VLY SPRNGS 07/84 RPR GYWW | VICTOR | ETL.8350.POLE.NWOD | 2024-04-20 | 2024-04-20 | 2025-02-06 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327503 | T2 EI WST PNT-VLY SPRNGS 07/84 RPR GYWW | ICW
LC | 128609579 | 018/133 | T2 EI ELECTRA-BELLOTA 018/133 RMV NEST | VICTOR | ETL.4670.TOWR | 2024-04-20 | 2024-04-20 | 2025-01-31 | On-Time |  | 2025-04-20 | 2025-04-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP NOAC REAR ACCL COMP OH FMOB TR2 PRTO FRAB NTDE | Debris/Nest/etc. | Structure-Steel | Remove | 46325893 | T2 EI ELECTRA-BELLOTA 018/133 RMV NEST | ICS
LC | 128609602 | 046/227 | T2 CORTINA-MNDCIN #1 046/227 RMV NEST | WILLITS | ETL.1330.TOWR | 2024-04-20 | 2024-04-20 | 2024-04-20 | Past Due |  | 2025-04-20 | 2025-04-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP ACCL OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46414840 | T2 EI CORTINA-MNDCIN #1 046/227 RMV NEST | ICS
LC | 128609670 | 018/128 | T2 EI ELECTRA-BELLOTA 018/128 RPL INSS | VICTOR | ETL.4670.INSL | 2024-04-20 | 2024-04-20 | 2025-03-20 | On-Time |  | 2025-04-20 | 2025-04-20 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP REMT CUSI CLR ACCM COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593221 | T2 EI ELECTRA-BELLOTA 002/024 RPL INSS | 93K
LC | 128610886 | 005/045 | T2 EI SLT SPRNGS-TIGER CRK 5/45 REGRADE | VICTOR | ETL.3500.TOWR | 2024-04-22 | 2024-04-20 | 2025-03-27 | On-Time |  | 2025-04-20 | 2025-04-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46416494 | T2 EI SLT SPRNGS-TIGER CRK 5/45 REGRADE | ICQ
LC | 128611162 | 024/187 | T2 DI PRDSE TBLE MTN 24/187 RPL HRDD | TABLEMTN | ETL.4316.POLE.STPS | 2024-04-22 | 2024-04-20 | 2025-02-11 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46310846 | T2 DI PRDSE TBLE MTN 24/187 RPL HRDD | ICW
LC | 128611168 | 024/187 | T2 DI PRDSE TBLE MTN 24/187 INSP ANCW | TABLEMTN | ETL.4316.POLE.STPS | 2024-04-22 | 2024-04-20 | 2024-09-09 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46310845 | T2 DI PRDSE TBLE MTN 24/187 INSP ANCW | ICW
LC | 128612391 | 027/110 | T2 DI DIABLO-MIDWAY #2 27/110 INSP STRS | PISMOBCH | ETL.5970.TOWR | 2024-04-22 | 2024-04-20 | 2024-10-01 | On-Time |  | 2025-04-20 | 2025-04-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327076 | T2 DI DIABLO-MIDWAY #2 27/110 INSP STRS | ICQ
LC | 128612392 | 027/110 | T2 DI DIABLO-MIDWAY #2 27/110 RPR SHLS | PISMOBCH | ETL.5970.TOWR | 2024-04-22 | 2024-04-20 | 2024-05-22 | On-Time |  | 2025-04-20 | 2025-04-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46249437 | T2 DI DIABLO-MIDWAY #2 27/110 RPR SHLS | ICS
LC | 128617839 | 021/114G | T2 DI BALCH-SANGER 21/114G RMV NEST | FRESNO | ETL.1050.POLE.NWOD | 2024-04-22 | 2024-04-20 | 2024-09-18 | On-Time |  | 2025-04-20 | 2025-04-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB BRIN | Debris/Nest/etc. | Structure-Steel | Remove | 46250432 | T2 DI BALCH-SANGER 21/114G RMV NEST | ICS
LC | 128617985 | 001/011 | T2 DI KRCKHF #1-KRCKHF #2 1/11 UNBURY | FRESNO | ETL.1880.TOWR | 2024-04-22 | 2024-04-20 | 2025-01-23 | On-Time |  | 2025-04-20 | 2025-04-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46292649 | T2 DI KRCKHF #1-KRCKHF #2 1/11 UNBURY | ICQ
LC | 128618279 | 004/046 | T3 DI DESABLA-CNTRVIL 04/46 RPL POLE | TABLEMTN | ETL.6720.POLE.WOOD | 2024-04-22 | 2024-04-20 | 2024-11-19 | On-Time |  | 2025-04-20 | 2025-04-20 | 372T | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35549289 | T3 DI DESABLA-CNTRVIL 04/46 RPL PL | 70Y
LC | 128618341 | 016/089 | T2 DI BALCH-SANGER 16/89 RPR INSS | FRESNO | ETL.1050.INSL.CERA | 2024-04-22 | 2024-04-20 | 2025-03-12 | On-Time |  | 2025-04-20 | 2025-04-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46298185 | T2 DI BALCH-SANGER 16/89 RPR INSS | ICS
LC | 128618580 | 112/002C | T2 DI HUMBOLDT-TRINITY 112/2C TOUCH | EUREKA | ETL.1820.POLE.NWOD | 2024-04-22 | 2024-04-20 | 2025-06-03 | Past Due |  | 2024-10-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46505100 | T2 DI HUMBOLDT-TRINITY 112/2C TOUCH | ICW
LC | 128618714 | 013/067 | T2 DI BALCH-SANGER 13/67 RPR INSS | FRESNO | ETL.1050.INSL.NCER | 2024-04-22 | 2024-04-20 | 2025-03-12 | On-Time |  | 2025-04-20 | 2025-04-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46298186 | T2 DI BALCH-SANGER 13/67 RPR INSS | ICS
LC | 128618843 | 114/000 | T2 HUMBOLDT-BRDGVLLE 114/0L TOUCH | EUREKA | ETL.1810.POLE.STPS | 2024-04-22 | 2024-04-20 | 2024-04-20 | Past Due |  | 2024-10-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46505102 | T2 DI HUMBOLDT-BRDGVLLE 114/0L TOUCH | ICW
LC | 128618878 | 012/104 | T2 DI CRAG VIEW-CASCADE 12/104L RPR OPGW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-22 | 2024-04-20 | 2024-09-07 | On-Time |  | 2024-07-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Wood | Repair | 46249642 | T2 DI CRAG VIEW-CASCADE 12/104L RPR OPGW | ICW
LC | 128618932 | 012/104 | T2 DI CRAG VIEW-CSCD 12/104C RPR WDPKR | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-22 | 2024-04-20 | 2024-09-07 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311387 | T2 DI CRAG VIEW-CSCD 12/104C RPR WDPKR | ICW
LC | 128618937 | 012/104 | T2 DI CRAG VIEW-CSCD 12/104C RPR GYWW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-04-22 | 2024-04-20 | 2024-09-07 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311388 | T2 DI CRAG VIEW-CSCD 12/104C RPR GYWW | ICW
LC | 128618973 | 021/002 | T2 DI MNDCNO-WLTS-FRT BRG 21/2 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-22 | 2024-04-20 | 2024-10-09 | On-Time |  | 2024-07-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46239210 | T2 DI MNDCNO-WLTS-FRT BRG 21/2 RPR GYWW | ICW
LC | 128618986 | 001/009 | T2 DI KERCKHOFF#1-KCKHF#2 1/9 UNBURY | FRESNO | ETL.1880.TOWR | 2024-04-22 | 2024-04-20 | 2025-01-23 | On-Time |  | 2025-04-20 | 2025-04-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46399425 | T2 DI KERCKHOFF#1-KCKHF#2 1/9 UNBURY | ICQ
LC | 128618989 | 001/009 | T2 DI KERCKHOFF#1-KCKHF#2 1/9 RPL HRDT | FRESNO | ETL.1880.TOWR | 2024-04-22 | 2024-04-20 | 2025-01-23 | On-Time |  | 2025-04-20 | 2025-04-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46292647 | T2 DI KERCKHOFF#1-KCKHF#2 1/9 RPL HRDT | ICQ
LC | 128619020 | 001/009 | T2 DI KERCKHOFF#1-KCKHF#2 1/9 BNT STEEL | FRESNO | ETL.1880.TOWR | 2024-04-22 | 2024-04-20 | 2025-01-23 | On-Time |  | 2025-04-20 | 2025-04-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46292648 | T2 DI KERCKHOFF#1-KCKHF#2 1/9 BNT STEEL | ICQ
LC | 128628765 | 035/284 | T2 DI BRIDGEVILLE-COT 35/284 RPR GRWW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-23 | 2024-04-20 | 2025-03-23 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46311091 | T2 DI BRIDGEVILLE-COT 35/284 RPR GRWW | ICW
LC | 128628834 | 035/142 | T2 DI DIABLO-MWY #3 35/142 COA | PISMOBCH | ETL.5980.TOWR | 2024-04-23 | 2024-04-20 | 2025-02-12 | On-Time |  | 2025-04-20 | 2025-04-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128628835 | 035/142 | T2 DI DIABLO-MWY #3 35/142 INSP STRT | PISMOBCH | ETL.5980.TOWR | 2024-04-23 | 2024-04-20 | 2024-10-23 | On-Time |  | 2025-04-20 | 2025-04-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327077 | T2 DI DIABLO-MWY #3 35/142 INSP STRT | ICQ
LC | 128628839 | 033/268 | T2 DI BRIDGEVIL-CTTNWD 33/268L RPL STRW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-23 | 2024-04-20 | 2025-04-07 | On-Time |  | 2025-04-20 | 2025-04-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35572065 | T2 DI BRIDGEVIL-CTTNWD 33/268C RPL STRW | 70Y
LC | 128662375 | 025/008 | T2 DI GRBRVLL-LYTNVLL 25/008 RPR GYWW | WILLITS | ETL.8365.POLE.WOOD | 2024-04-26 | 2024-04-20 | 2025-02-06 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46414836 | T2 DI GRBRVLL-LYTNVLL 25/008 RPR GYWW | ICW
LC | 128662636 | 112/003 | T2 DI HUMBOLDT-TRINITY 112/3 RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-04-26 | 2024-04-20 | 2025-03-16 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345771 | T2 DI HUMBOLDT-TRINITY 112/3 RPR GYWW | ICW
LC | 128679205 | 004/049 | T3 DI DESABLA-CENTERVILLE 4/49 RPR INSW | TABLEMTN | ETL.6720.INSL.NCER | 2024-04-29 | 2024-04-20 | 2024-11-14 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46250405 | T3 DI DESABLA-CENTERVILLE 4/49 RPR INSW | ICW
LC | 128679248 | 026/008 | T2 DI GRBRVL LYTNVLE 26/8 RPR ANCW | WILLITS | ETL.8365.POLE.WOOD | 2024-04-29 | 2024-04-20 | 2025-04-16 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46414838 | T2 DI GRBRVL LYTNVLE 26/8 RPR ANCW | ICW
LC | 128679273 | 026/008 | T2 DI GRBRVL LYTNVLE 26/8 RPR GYWW | WILLITS | ETL.8365.POLE.WOOD | 2024-04-29 | 2024-04-20 | 2025-04-16 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46414837 | T2 DI GRBRVL LYTNVLE 26/8 RPR GYWW | ICW
LC | 128679325 | 010/100 | T2 DI PIT #5 RND MTN #1 10/100L RPL STRW | TABLEMTN | ETL.5420.POLE.WDPS | 2024-04-29 | 2024-04-20 | 2024-04-20 | Past Due |  | 2025-04-20 | 2025-04-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35607189 | T2 DI PIT #5 RND MTN #1 10/100 RPL STRW | 70Y
LC | 128679388 | 021/000 | T2 DI MNDCN WLTS FRT BRG 21/0 RPL ANCW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-29 | 2024-04-20 | 2025-04-08 | On-Time |  | 2025-04-20 | 2025-04-20 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574378 | T2 DI MNDCN WLTS FRT BRG 21/0 RPL ANCW | 93E
LC | 128679635 | 004/037 | T2NT DI PIT #1-COTTONWOOD 4/37 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-04-29 | 2024-04-20 | 2025-03-25 | On-Time |  | 2027-04-20 | 2025-04-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381510 | T2NT DI PIT #1-COTTONWOOD 4/37 RPR STRT | ICQ
LC | 128679821 | 033/004 | T2 DI MDCN-WLTS-FRT BRG 33/4 RPR CRSW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-29 | 2024-04-20 | 2025-04-10 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46310108 | T2 DI MDCN-WLTS-FRT BRG 33/4 RPR CRSW | ICW
LC | 128698512 | 000/008 | T2 DI KRCKHFF #1-KRCKHFF #2 0/8 RPR STRT | FRESNO | ETL.1880.TOWR | 2024-05-01 | 2024-04-20 | 2024-04-20 | Past Due |  | 2025-04-20 | 2025-04-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46292646 | T2 DI KRCKHFF #1-KRCKHFF #2 0/8 RPR STRT | ICQ
LC | 128698530 | 018/096 | T2 DI BALCH-SANGER 18/96 RPL INSS | FRESNO | ETL.1050.INSL.CERA | 2024-05-01 | 2024-04-20 | 2025-03-12 | On-Time |  | 2025-04-20 | 2025-04-20 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35571947 | T2 DI BALCH-SANGER 18/96 RPL INSS | 93K
LC | 128698762 | 025/006 | T2 DI GRBRVL-LYTNVL 25/6 RPR GYWW | WILLITS | ETL.8365.POLE.NWOD | 2024-05-01 | 2024-04-20 | 2025-02-06 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46414834 | T2 DI GRBRVL-LYTNVL 25/6 RPR GYWW | ICW
LC | 128698854 | 011/103 | T2 DI CRAG VIEW-CASCADE 11/103 RPR OPGW | TABLEMTN | ETL.1350.POLE.STPS | 2024-05-01 | 2024-04-20 | 2025-03-21 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | OPGW - Wood | Repair | 46454375 | T2 DI CRAG VIEW-CASCADE 11/103 RPR OPGW | ICW
LC | 128698962 | 035/281 | T2 DI BRIDGEVILL-CTTNWD 035/281 RPR HRDW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-05-01 | 2024-04-20 | 2024-06-01 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Missing | Hardware-Wood | Install | 46256585 | T2 DI BRIDGEVILL-CTTNWD 035/281 RPR HRDW | ICW
LC | 128698963 | 035/281 | T2 DI BRIDGEVILLE-CTTNWD 35/281 RPR STRW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-05-01 | 2024-04-20 | 2024-06-01 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46254925 | T2 DI BRIDGEVILLE-CTTNWD 35/281 RPR STRW | ICW
LC | 128699045 | 018/098 | T2 DI BALCH-SANGER 18/98 RPR STRT | FRESNO | ETL.1050.TOWR | 2024-05-01 | 2024-04-20 | 2025-03-12 | On-Time |  | 2025-04-20 | 2025-04-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46292653 | T2 DI BALCH-SANGER 18/98 RPR STRT | ICQ
LC | 128699049 | 033/271 | T2 DI BRIDGEVLL-CTTNWOOD 33/271 RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-05-01 | 2024-04-20 | 2025-03-23 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311092 | T2 DI BRIDGEVLL-CTTNWOOD 33/271 RPR GYWW | ICW
LC | 128700037 | 010/100 | T2 DI PIT #5 RND MTN #1 10/100R RPL STRW | TABLEMTN | ETL.5420.POLE.WDPS | 2024-05-02 | 2024-04-20 | 2024-04-20 | Past Due |  | 2025-04-20 | 2025-04-20 | 372 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35607189 | T2 DI PIT #5 RND MTN #1 10/100 RPL STRW | 70Y
LC | 128709603 | 025/007 | T2 DI GARBERVILLE-LTYN 25/7 RPR GYWW | WILLITS | ETL.8365.POLE.WOOD | 2024-05-03 | 2024-04-20 | 2025-03-06 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46414835 | T2 DI GARBERVILLE-LTYN 25/7 RPR GYWW | ICW
LC | 128716833 | 031/007 | T2NT DI FULTON-HOPLAND 031/007 RPR INSW | LAKEVLLE | ETL.6890.INSL.NCER | 2024-05-06 | 2024-04-20 | 2025-03-20 | On-Time |  | 2027-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46499611 | T2NT DI FULTON-HOPLAND 031/007 RPR INSW | ICW
LC | 128716982 | 027/003 | T2 DI GRBRVL LYTNVL 27/003 RPR GYWW | WILLITS | ETL.8365.POLE.NWOD | 2024-05-06 | 2024-04-20 | 2024-08-12 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46252718 | T2 DI GRBRVL LYTNVL 27/003 RPR GYWW | ICW
LC | 128717181 | 033/003 | T2 DI MDCNO WLTS FT BRG 33/003 RPL STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-06 | 2024-04-20 | 2025-04-19 | On-Time |  | 2025-04-20 | 2025-04-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574307 | T2 DI MDCNO WLTS FT BRG 33/003 RPL STRW | 70Y
LC | 128717755 | 013/113 | T2 DI CRG VIEW CASCD 13/113 INSP ANCW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-05-06 | 2024-04-20 | 2024-09-06 | On-Time |  | 2024-10-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46284250 | T2 DI CRG VIEW CASCD 13/113 INSP ANCW | ICW
LC | 128717756 | 013/113 | T2 DI CRG VIEW CASCD 13/113 RPL STRW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-05-06 | 2024-04-20 | 2024-04-20 | Past Due |  | 2025-04-20 | 2025-04-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557668 | T2 DI CRG VIEW CASCD 13/113 RPL STRW | 70Y
LC | 128717759 | 013/113 | T2 DI CRG VIEW CASCD 13/113 RPL STRW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-05-06 | 2024-04-20 | 2024-04-20 | Past Due |  | 2025-04-20 | 2025-04-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Rotten | Structure-Wood | Replace | 35557668 | T2 DI CRG VIEW CASCD 13/113 RPL STRW | 70Y
LC | 128723395 | 005/045 | T2 DI TRINITY-CTTNWD 5/045L RPR GYWW | TABLEMTN | ETL.4040.POLE.STPS | 2024-05-07 | 2024-04-20 | 2025-01-21 | On-Time |  | 2025-04-20 | 2025-04-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46455933 | T2 DI TRINITY-CTTNWD 5/045L RPR GYWW | ICW
LC | 123447396 | 003/020 | T2NT DI STNLS-MLNS-MTC #1 3/20 RPR STRT | VICTOR | ETL.3830.TOWR | 2022-04-28 | 2022-04-21 | 2023-03-23 | On-Time |  | 2025-04-21 | 2025-04-21 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Structure-Tower | Repair | 45591149 | T2 DI STNLS-MLNS-MTC #1 3/20 RPR STRT | ICQ
LC | 123561664 | 012/241 | T2NT DI CARIBOU-WESTWOOD 12/241 RMV BUTT | TABLEMTN | ETL.6300.POLE.WOOD | 2022-05-10 | 2022-04-21 | 2023-07-27 | On-Time |  | 2025-04-21 | 2025-04-21 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 45681240 | T2NT DI CARIBOU-WESTWOOD 12/241 RMV BUTT | ICW
LC | 123572762 | 009/056 | T2NT DI STNLUS-MNTCA#2 9/056 RPR INSS | VICTOR | ETL.3820.INSL.CERA | 2022-05-11 | 2022-04-21 | 2023-03-27 | On-Time |  | 2025-04-21 | 2025-04-21 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 45504250 | T2 DI STNLUS-MNTCA#2 9/056 RPR INSS | ICS
LC | 123573230 | 001/018 | T2NT DI COLGATE-SMARTVL #1 1/18 RMV BUTT | SACTO | ETL.6510.POLE.NWOD | 2022-05-11 | 2022-04-21 | 2023-02-13 | On-Time |  | 2023-04-21 | 2025-04-21 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 45672420 | T2NT DI COLGATE-SMARTVL #1 1/18 RMV BUTT | ICW
LC | 130737403 | 005/005 | T3 DIABLO UNIT #2 005/005 RPR FOND | PISMOBCH | ETL.5950.TOWR | 2025-01-13 | 2024-10-21 | 2025-04-21 | On-Time |  | 2025-04-21 | 2025-04-21 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46469026 | T3 DIABLO UNIT #2 005/005 RPR FOND | ICQ
LC | 123395854 | 024/193 | T2NT EI CRBRY SS-RND MTN 24/193 RPL INSS | TABLEMTN | ETL.5410.INSL | 2022-04-22 | 2022-04-22 | 2023-09-15 | On-Time |  | 2025-04-22 | 2025-04-22 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 31639948 | T2NT EI CRBRY SS-RND MTN 24/193 RPL INSS | 93K
LC | 123397829 | 081/413 | T2NT EI MLIN-RND MTN #2 081/413 RPR STRT | TABLEMTN | ETL.6020.TOWR | 2022-04-22 | 2022-04-22 | 2023-08-22 | On-Time |  | 2025-04-22 | 2025-04-22 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Steel | Repair | 45650813 | T2 EI MLIN-ROUND MTN #2 081/413 RPR STRT | ICS
LC | 123586583 | 001/014 | T2NT DI HATT CRK#1-PIT#1 001/014 MASTIC | TABLEMTN | ETL.7020.TOWR | 2022-05-13 | 2022-04-22 | 2023-08-01 | On-Time |  | 2025-04-22 | 2025-04-22 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45600105 | T2NT DI HATT CRK#1-PIT#1 001/014 MASTIC | ICQ
LC | 123593826 | 003/016B | T3NT DI EGL RK-FLTN-SLVRD 3/16B RPL HDWT | LAKEVLLE | ETL.4392.TOWR | 2022-05-14 | 2022-04-22 | 2023-11-29 | On-Time |  | 2025-04-22 | 2025-04-22 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 45644811 | T3 DI EGL RK-FLTN-SLVRDO 3/16B RPL HDWT | ICQ
LC | 128611276 | 033/007 | T2 FORT ROSS-GUALALA 033/007 REGR STRW | LAKEVLLE | ETL.6980.POLE.NWOD | 2024-04-22 | 2024-04-22 | 2025-03-03 | On-Time |  | 2025-04-22 | 2025-04-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46305934 | T2 FORT ROSS-GUALALA 033/007 REGR STRW | ICW
LC | 128611981 | 003/020 | T2 EI KRKHF-CLVS-SNGR #1 03/20 RMV ENCR | FRESNO | ETL.1890.TOWR | 2024-04-22 | 2024-04-22 | 2024-09-17 | On-Time |  | 2024-10-22 | 2025-04-22 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46249747 | T2 EI KRKHF-CLVS-SNGR #1 03/20 RMV ENCR | CHR
LC | 128611992 | 003/020 | T2 EI KRKHF-CLVS-SNGR #1 03/20 BNT STEEL | FRESNO | ETL.1890.TOWR | 2024-04-22 | 2024-04-22 | 2025-01-23 | On-Time |  | 2025-04-22 | 2025-04-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46292654 | T2 EI KRKHF-CLVS-SNGR #1 03/20 BNT STEEL | ICQ
LC | 128611993 | 003/020 | T2 EI KRKHF-CLVS-SNGR #1 03/20 UNBURY | FRESNO | ETL.1890.TOWR | 2024-04-22 | 2024-04-22 | 2025-01-23 | On-Time |  | 2025-04-22 | 2025-04-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46399426 | T2 EI KRKHF-CLVS-SNGR #1 03/20 UNBURY | ICQ
LC | 128612118 | 055/274 | T2 EI CORTINA-MENDOCNO #1 55/274 RMV VEG | WILLITS | ETL.1330.TOWR | 2024-04-22 | 2024-04-22 | 2025-04-17 | On-Time |  | 2025-04-22 | 2025-04-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128612159 | 019/136B | T2 WV CARIBOU-TBLE MTN 19/136B RPR STRT | TABLEMTN | ETL.4440.POLE.NWOD | 2024-04-22 | 2024-04-22 | 2025-04-05 | On-Time |  | 2025-04-22 | 2025-04-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354020 | T2 WV CARIBOU-TBLE MTN 19/136B RPR STRT | ICQ
LC | 128612273 | 012/153 | T2 WEST POINT-VLLY SPRNGS 12/153 TOUCH | VICTOR | ETL.8350.POLE.NWOD | 2024-04-22 | 2024-04-22 | 2024-04-22 | Past Due |  | 2024-10-22 | 2025-04-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46484788 | T2 WEST POINT-VLLY SPRNGS 12/153 TOUCH | ICW
LC | 128614043 | 001/074 | T2 EI SPAULDING-SUMMIT 01/074 COMPLETED | SACTO | ETL.8060.POLE.WOOD | 2024-04-22 | 2024-04-22 | 2024-06-26 | On-Time |  | 2024-10-22 | 2025-04-22 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35551031 | T2 EI SPAULDING-SUMMIT 01/074 RPL ANCW | 93E
LC | 128616325 | 054/235 | T2 EI RND MTN-TBL MTN #1 54/235 RPL INSS | TABLEMTN | ETL.6060.INSL.NCER | 2024-04-22 | 2024-04-22 | 2025-02-04 | On-Time |  | 2025-04-22 | 2025-04-22 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569940 | T2 EI RND MTN-TBL MTN #1 RPL INSS 9 TWRS | 93K
LC | 128616542 | 012/070 | T2 EI STANISLUS-MNTEA #2 12/070 RPR INSS | VICTOR | ETL.3820.INSL.NCER | 2024-04-22 | 2024-04-22 | 2025-04-08 | On-Time |  | 2025-04-22 | 2025-04-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46325894 | T2 EI STANISLUS-MNTEA #2 12/070 RPR INSS | ICS
LC | 128616608 | 005/014 | T2 EI VLY SPNGS-CLVS CMNT 05/14 RPL STRW | VICTOR | ETL.8220.POLE.WOOD | 2024-04-22 | 2024-04-22 | 2025-03-07 | On-Time |  | 2025-04-22 | 2025-04-22 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573399 | T2 EI VLY SPNGS-CLVS CMNT 05/14 RPL STRW | 70Y
LC | 128616784 | 009/065 | T2 EI WISHON-COPPERMINE 9/65 TOUCH | FRESNO | ETL.9330.TOWR | 2024-04-22 | 2024-04-22 | 2025-04-09 | On-Time |  | 2024-10-22 | 2025-04-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46484397 | T2 EI WISHON-COPPERMINE 9/65 TOUCH | ICQ
LC | 128616791 | 009/065 | T2 EI WISHON-COPPERMINE 9/65 RPR STRT | FRESNO | ETL.9330.TOWR | 2024-04-22 | 2024-04-22 | 2025-05-02 | Past Due |  | 2025-04-22 | 2025-04-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46292655 | T2 EI WISHON-COPPERMINE 9/65 RPR STRT | ICQ
LC | 128617161 | 005/012 | T2 EI VLY SPGS-CLVRS CMNT 05/12 RPR STRW | VICTOR | ETL.8220.POLE.WOOD | 2024-04-22 | 2024-04-22 | 2025-03-08 | On-Time |  | 2025-04-22 | 2025-04-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46326991 | T2 EI VLY SPGS-CLVRS CMNT 05/12 RPR STRW | ICW
LC | 128617529 | 022/090 | T2 DI DIABLO-MDWY #3 22/90 RPL INSS | PISMOBCH | ETL.5980.INSL.NCER | 2024-04-22 | 2024-04-22 | 2025-01-27 | On-Time |  | 2025-04-22 | 2025-04-22 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35585665 | T2 DI DIABLO-MDWY #3 22/90 RPL INSS | 93K
LC | 128617626 | 028/001 | T2 EI TRINITY-MAPLE CREEK 28/01 RMV VEG | EUREKA | ETL.8170.POLE.NWOD | 2024-04-22 | 2024-04-22 | 2024-11-20 | On-Time |  | 2025-04-22 | 2025-04-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128617737 | 004/060 | T2 WV BURNS-LONE STAR#1 4/60 INS DAMW | MOSSLNDG | ETL.6230.INSL | 2024-04-22 | 2024-04-22 | 2025-03-07 | On-Time |  | 2025-04-22 | 2025-04-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46391292 | T2 WV BURNS-LONE STAR#1 4/60 INS DAMW | ICW
LC | 128617935 | 060/253 | T2 EI RND MTN-TBL MTN #2 60/253 RPR INSS | TABLEMTN | ETL.6070.INSL.NCER | 2024-04-22 | 2024-04-22 | 2024-05-05 | On-Time |  | 2024-07-22 | 2025-04-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46238592 | T2 EI RND MTN-TBL MTN #2 60/253 RPR INSS | ICS
LC | 128617950 | 005/062 | T2 WV BURNS-LONE STAR#1 5/62 INS DAMW | MOSSLNDG | ETL.6230.INSL.NCER | 2024-04-22 | 2024-04-22 | 2023-03-07 | On-Time |  | 2025-04-22 | 2025-04-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46391289 | T2 WV BURNS-LONE STAR#1 5/62 INS DAMW | ICW
LC | 128617993 | 011/004 | T2 EI OAKHURST TAP 011/004 RMV ENCR | FRESNO | ETL.1252.POLE.NWOD | 2024-04-22 | 2024-04-22 | 2024-08-20 | On-Time |  | 2024-10-22 | 2025-04-22 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46249748 | T2 EI OAKHURST TAP 011/004 RMV ENCR | CHR
LC | 128618205 | 006/133 | T2 EI COLEMAN-SOUTH 006/133 RPR WDPKR | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-22 | 2024-04-22 | 2025-03-22 | On-Time |  | 2025-04-22 | 2025-04-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46389138 | T2 EI COLEMAN-SOUTH 006/133 RPR WDPKR | ICW
LC | 128618244 | 039/314 | T2 EI BRIDGEVIL-CTTNW 39/314L RMV VEG | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-22 | 2024-04-22 | 2024-11-12 | On-Time |  | 2025-04-22 | 2025-04-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128618475 | 031/006 | T2 EI FORT ROSS-GUALALA 31/6 RMV VEG | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-04-22 | 2024-04-22 | 2025-02-03 | On-Time |  | 2025-04-22 | 2025-04-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128618477 | 032/006 | T2 EI FORT ROSS-GUALALA 32/6 RMV VEG | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-04-22 | 2024-04-22 | 2025-02-03 | On-Time |  | 2025-04-22 | 2025-04-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128618499 | 029/006 | T2 EI FORT ROSS-GUALALA 29/6 RMV VEG | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-04-22 | 2024-04-22 | 2025-02-24 | On-Time |  | 2025-04-22 | 2025-04-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128618757 | 004/001 | T2 EI DUNLAP TAP 004/001 RPR GYWW | FRESNO | ETL.9061.POLE.NWOD | 2024-04-22 | 2024-04-22 | 2025-03-21 | On-Time |  | 2025-04-22 | 2025-04-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298196 | T2 EI DUNLAP TAP 004/001 RPR GYWW | ICW
LC | 128618798 | 005/003 | T2 EI DUNLAP TAP 005/003 COMPLETE | FRESNO | ETL.9061.POLE.NWOD | 2024-04-22 | 2024-04-22 | 2025-03-21 | On-Time |  | 2025-04-22 | 2025-04-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298197 | T2 EI DUNLAP TAP 005/003 RPR GYWW | ICW
LC | 128622227 | 054/270 | T2 EI CORTINA-MNDCN #154/270 RMV VEG | WILLITS | ETL.1330.TOWR | 2024-04-23 | 2024-04-22 | 2025-03-05 | On-Time |  | 2025-04-22 | 2025-04-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128622242 | 047/229 | T2 EI CORTINA-MNDCN #1 47/229 CANCEL | WILLITS | ETL.1330.TOWR | 2024-04-23 | 2024-04-22 | 2024-04-22 | Past Due |  | 2025-04-22 | 2025-04-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46414841 | T2 EI CORTINA-MNDCN #1 47/229 RMV NEST | ICS
LC | 128622314 | 005/029 | T2 EI METCALF-HICKS 1 & 2 5/29 RMV VEG | METCALF | ETL.4317.TOWR | 2024-04-23 | 2024-04-22 | 2025-04-08 | On-Time |  | 2025-04-22 | 2025-04-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128625218 | 015/064 | T2 EI DIABLO-GATES #1 15/64 RPR GYWT | PISMOBCH | ETL.5960.TOWR | 2024-04-23 | 2024-04-22 | 2025-04-02 | On-Time |  | 2025-04-22 | 2025-04-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46391252 | T2 EI DIABLO-GATES #1 15/64 RPR GYWT | ICQ
LC | 128625680 | 025/002A | T2 TRINITY-MAPLE CREEK 25/2A COMPLETE | EUREKA | ETL.8170.POLE.WOOD | 2024-04-23 | 2024-04-22 | 2025-04-14 | On-Time |  | 2025-04-22 | 2025-04-22 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35572084 | TRINITY-MAPLE CREEK 25/2A REPL O/L POLE | 93G
LC | 128628005 | 021/088 | T2 DIABLO-MIDWAY #2 21/88 TOUCH | PISMOBCH | ETL.5970.TOWR | 2024-04-23 | 2024-04-22 | 2025-06-05 | Past Due |  | 2024-10-22 | 2025-04-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476146 | T2 DI DIABLO-MIDWAY #2 21/88 TOUCH | ICQ
LC | 128630667 | 001/028 | T2 EI APPLE HILL #2 TAP 1/28 RMV VEG | SACTO | ETL.1541.POLE.WOOD | 2024-04-24 | 2024-04-22 | 2025-01-07 | On-Time |  | 2025-04-22 | 2025-04-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128630668 | 001/026 | T2 EI APPLE HILL #1 TAP 1/26 RMV VEG | SACTO | ETL.1531.POLE.NWOD | 2024-04-24 | 2024-04-22 | 2025-01-07 | On-Time |  | 2025-04-22 | 2025-04-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128651197 | 021/086 | T2 DI DIABLO MIDWAY #2 21/86 INSPECT | PISMOBCH | ETL.5970.TOWR | 2024-04-24 | 2024-04-22 | 2024-10-14 | On-Time |  | 2025-04-22 | 2025-04-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327078 | T2 DI DIABLO MIDWAY #2 21/86 INSPECT | ICQ
LC | 128679638 | 021/001 | T2 DI MENDO-WLTS-FRT BRG 21/1 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-29 | 2024-04-22 | 2025-02-07 | On-Time |  | 2025-04-22 | 2025-04-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310109 | T2 DI MENDO-WLTS-FRT BRG 21/1 RPR GYWW | ICW
LC | 128685000 | 002/031 | T2 EI PIT #5-ROUND MTN #2 2/31 RPR SHLW | TABLEMTN | ETL.5430.POLE.STPS | 2024-04-30 | 2024-04-22 | 2025-03-03 | On-Time |  | 2025-04-22 | 2025-04-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Wood | Repair | 46454288 | T2 EI PIT #5-ROUND MTN #2 2/31 RPR SHLW | ICW
LC | 129716704 | 000/001B | T3 GEYSERS #3-CLOVERDALE 0/1B RPL INSW | LAKEVLLE | ETL.1650.INSL.NCER | 2024-10-22 | 2024-10-22 | 2024-10-22 | Past Due |  | 2025-04-22 | 2025-04-22 | 508 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW OTHR OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 31651345 | T3 WV GEYSERS #3-CLOVERDALE 0/1 RPL POLE | 70Y
LC | 128622604 | 014/084 | T2 EI STANISLAUS-MNTCA #2 14/084 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-23 | 2024-04-23 | 2024-06-24 | On-Time |  | 2024-10-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46248672 | T2 EI STANISLAUS-MNTCA #2 14/084 UNBURY | ICQ
LC | 128623887 | 010/071 | T2 EI CTTNWD-DELEVAN #1 10/71 RPR SHLS | TABLEMTN | ETL.4550.TOWR | 2024-04-23 | 2024-04-23 | 2025-01-15 | On-Time |  | 2025-04-23 | 2025-04-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46300590 | T2 EI CTTNWD-DELEVAN #1 10/71 RPR SHLS | ICS
LC | 128624213 | 070/615 | T2 EI CTTNWD-DELEVAN #2 70/615 RMV VEG | TABLEMTN | ETL.4580.TOWR | 2024-04-23 | 2024-04-23 | 2024-04-23 | On-Time |  | 2025-04-23 | 2025-04-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128624216 | 027/137 | T2 ROUND MTN-TBL MTN #1 27/137 RPR INSS | TABLEMTN | ETL.6060.INSL | 2024-04-23 | 2024-04-23 | 2024-05-08 | On-Time |  | 2024-07-23 | 2025-04-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46239173 | T2 ROUND MTN-TBL MTN #1 27/137 RPR INSS | ICS
LC | 128624418 | 007/048 | T2 NEWARK-LIVERMORE 007/048 COTTER | CONCORD | ETL.7660.INSL.NCER | 2024-04-23 | 2024-04-23 | 2024-06-02 | On-Time |  | 2024-07-23 | 2025-04-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46237186 | T2 NEWARK-LIVERMORE 007/048 COTTER | ICS
LC | 128624531 | 017/238 | T2 EI SISQUOC-SANT YNZ SW 17/238 RPL PL | PISMOBCH | ETL.3700.POLE.WDPS | 2024-04-23 | 2024-04-23 | 2025-04-05 | On-Time |  | 2025-04-23 | 2025-04-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP NOAC CLR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573820 | T2 EI SISQUOC-SANT YNZ SW 17/238 RPL PL | 70Y
LC | 128624657 | 017/238 | T2 EI SISQUOC-SANT YNZ SW 17/238 RPL PL | PISMOBCH | ETL.3700.POLE.WDPS | 2024-04-23 | 2024-04-23 | 2025-04-05 | On-Time |  | 2025-04-23 | 2025-04-23 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP NOAC ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573820 | T2 EI SISQUOC-SANT YNZ SW 17/238 RPL PL | 70Y
LC | 128624671 | 017/238 | T2 EI SISQUOC-SANT YNZ SW 17/238 RPL PL | PISMOBCH | ETL.3700.POLE.WDPS | 2024-04-23 | 2024-04-23 | 2025-04-05 | On-Time |  | 2025-04-23 | 2025-04-23 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP NOAC CLR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573820 | T2 EI SISQUOC-SANT YNZ SW 17/238 RPL PL | 70Y
LC | 128624827 | 015/200 | T2 EI WATSNVILLE-SALINAS 15/200L RMV VEG | MOSSLNDG | ETL.8310.POLE.WDPS | 2024-04-23 | 2024-04-23 | 2025-03-28 | On-Time |  | 2025-04-23 | 2025-04-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP REMT SWRK ACCL COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128624829 | 013/000 | T2 EI EXCHEQUER-MARIPOSA 13/0 RPR GYWW | FRESNO | ETL.8640.POLE.NWOD | 2024-04-23 | 2024-04-23 | 2025-04-15 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298198 | T2 EI EXCHEQUER-MARIPOSA 13/0 RPR GYWW | ICW
LC | 128624832 | 015/085 | T2 CHRISTIE-SOBRANTE 015/085 RPL INSS | CONCORD | ETL.1260.INSL.CERA | 2024-04-23 | 2024-04-23 | 2025-01-17 | On-Time |  | 2025-04-23 | 2025-04-23 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577333 | T2 CHRISTIE-SOBRANTE 015/085 RPL INSS | 93K
LC | 128624895 | 005/027 | hhywETCALF-EL PATIO #1 05/027 RMV VEG | METCALF | ETL.2500.TOWR | 2024-04-23 | 2024-04-23 | 2025-04-09 | On-Time |  | 2025-04-23 | 2025-04-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP ACCL COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128624919 | 016/234 | T2 EI SISQUOC-SANTA YNZ SW 16/234 RPL PL | PISMOBCH | ETL.3700.POLE.WDPS | 2024-04-23 | 2024-04-23 | 2025-04-05 | On-Time |  | 2025-04-23 | 2025-04-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP NOAC CLR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573799 | T2 EI SISQUOC-SANTA YNZ SW 16/234 RPL PL | 70Y
LC | 128624985 | 022/128 | T2 STANISLS-MNTC #2 22/128 TOUCH | VICTOR | ETL.3820.TOWR | 2024-04-23 | 2024-04-23 | 2025-01-13 | On-Time |  | 2024-10-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472915 | T2 STANISLS-MNTC #2 22/128 TOUCH | ICQ
LC | 128624995 | 043/210 | T2 CORTINA-MNDCN #1 43/210 RMV NEST | WILLITS | ETL.1330.TOWR | 2024-04-23 | 2024-04-23 | 2024-04-23 | Past Due |  | 2025-04-23 | 2025-04-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46414845 | T2 EI CORTINA-MNDCN #1 43/210 RMV NEST | ICS
LC | 128624999 | 016/234 | T2 EI SISQUOC-SANTA YNZ SW 16/234 RPL PL | PISMOBCH | ETL.3700.POLE.WDPS | 2024-04-23 | 2024-04-23 | 2025-04-05 | On-Time |  | 2025-04-23 | 2025-04-23 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573799 | T2 EI SISQUOC-SANTA YNZ SW 16/234 RPL PL | 70Y
LC | 128625078 | 003/012 | T2 EI CHOWCHILLA-KERCKHOFF 3/12 RPL STRW | FRESNO | ETL.1250.POLE.WOOD | 2024-04-23 | 2024-04-23 | 2025-03-25 | On-Time |  | 2025-04-23 | 2025-04-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35576150 | T2 EI CHOWCHILLA-KERCKHOFF 3/12 RPL STRW | 70Y
LC | 128625096 | 004/002 | T2 EI CHOWCHILLA-KERCKHOFF 4/2 GO95 | FRESNO | ETL.1250.POLE.NWOD | 2024-04-23 | 2024-04-23 | 2025-03-26 | On-Time |  | 2025-04-23 | 2025-04-23 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35554461 | T2 EI CHOWCHILLA-KERCKHOFF 4/2 RPL POLE | 93G
LC | 128625338 | 016/234 | T2 EI SISQUOC-SANTA YNZ SW 16/234 RPL PL | PISMOBCH | ETL.3700.POLE.WDPS | 2024-04-23 | 2024-04-23 | 2025-04-05 | On-Time |  | 2025-04-23 | 2025-04-23 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573799 | T2 EI SISQUOC-SANTA YNZ SW 16/234 RPL PL | 70Y
LC | 128625398 | 016/233 | T2 EI SSQOC-SNTA YNZ SS 16/233L RPL STRW | PISMOBCH | ETL.3700.POLE.WDPS | 2024-04-23 | 2024-04-23 | 2025-04-05 | On-Time |  | 2025-04-23 | 2025-04-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP NOAC CLR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573797 | T2 EI SISQC-SNT YNZ SW STA 16/233 RPL PL | 70Y
LC | 128625439 | 015/207A | T2 EI WTSNVLLE-SALINAS 15/207A RPL POLE | MOSSLNDG | ETL.8310.POLE.WOOD | 2024-04-23 | 2024-04-23 | 2025-02-12 | On-Time |  | 2025-04-23 | 2025-04-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCL ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573393 | T2 EI WTSNVLLE-SALINAS 15/207A RPL POLE | 70Y
LC | 128625479 | 005/116 | T2 EI COLEMAN-SOUTH 5/116 RPL STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-23 | 2024-04-23 | 2025-03-25 | On-Time |  | 2025-04-23 | 2025-04-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556789 | T2 EI COLEMAN-SOUTH 05/115 RPL PL | 70Y
LC | 128625483 | 057/010 | T2 EI FORT ROSS-GUALALA 57/010 GO95 | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-04-23 | 2024-04-23 | 2025-04-07 | On-Time |  | 2025-04-23 | 2025-04-23 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35574246 | T2 EI FORT ROSS-GUALALA 57/010 GO95 | 93G
LC | 128625485 | 016/233 | T2 EI SSQOC-SNTA YNZ SS 16/233R RPL STRW | PISMOBCH | ETL.3700.POLE.WDPS | 2024-04-23 | 2024-04-23 | 2025-04-05 | On-Time |  | 2025-04-23 | 2025-04-23 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP NOAC CLR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573797 | T2 EI SISQC-SNT YNZ SW STA 16/233 RPL PL | 70Y
LC | 128625493 | 016/233 | T2 EI SSQOC-SNTA YNZ SS 16/233C RPL STRW | PISMOBCH | ETL.3700.POLE.WDPS | 2024-04-23 | 2024-04-23 | 2025-04-05 | On-Time |  | 2025-04-23 | 2025-04-23 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP NOAC CLR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573797 | T2 EI SISQC-SNT YNZ SW STA 16/233 RPL PL | 70Y
LC | 128625520 | 005/119 | T2 EI COLEMAN-SOUTH 5/119 RPL ANCW | TABLEMTN | ETL.6450.POLE.WDPS | 2024-04-23 | 2024-04-23 | 2024-12-10 | On-Time |  | 2025-04-23 | 2025-04-23 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572514 | T2 EI COLEMAN-SOUTH 5/119 RPL ANCW | 93E
LC | 128625522 | 005/119 | T2 EI COLEMAN-SOUTH 5/119C RPR GYWW | TABLEMTN | ETL.6450.POLE.WDPS | 2024-04-23 | 2024-04-23 | 2024-09-20 | On-Time |  | 2024-10-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46246208 | T2 EI COLEMAN-SOUTH 5/119C RPR GYWW | ICW
LC | 128625530 | 005/119 | T2 EI COLEMAN-SOUTH 5/119R RPR GYWW | TABLEMTN | ETL.6450.POLE.WDPS | 2024-04-23 | 2024-04-23 | 2024-09-20 | On-Time |  | 2024-10-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46246209 | T2 EI COLEMAN-SOUTH 5/119R RPR GYWW | ICW
LC | 128625579 | 011/072 | T2 EI CTTNWD-DELEVAN #1 11/72 RMV NEST | TABLEMTN | ETL.4550.TOWR | 2024-04-23 | 2024-04-23 | 2025-01-15 | On-Time |  | 2025-04-23 | 2025-04-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46300591 | T2 EI CTTNWD-DELEVAN #1 11/72 RMV NEST | ICS
LC | 128625617 | 004/044 | T2 EI WDLEAF-PALRMO 4/044 REGR STRW | TABLEMTN | ETL.4220.POLE.STPS | 2024-04-23 | 2024-04-23 | 2025-04-22 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46454336 | T2 EI WDLEAF-PALRMO 4/044 REGR STRW | ICW
LC | 128625659 | 004/044 | T2 EI WOODLEAF-PALERMO 004/044 RMV VEG | TABLEMTN | ETL.4220.POLE.STPS | 2024-04-23 | 2024-04-23 | 2024-10-22 | On-Time |  | 2025-04-23 | 2025-04-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128627129 | 007/057 | T2 EI WISHON-COPPERMINE 7/57 TOUCH | FRESNO | ETL.9330.TOWR | 2024-04-23 | 2024-04-23 | 2025-04-09 | On-Time |  | 2024-10-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46477346 | T2 EI WISHON-COPPERMINE 7/57 TOUCH | ICQ
LC | 128627508 | 010/153 | T2 EI SSQC-SNT YNZ SW ST 10/153 RPR GYWW | PISMOBCH | ETL.3700.POLE.WOOD | 2024-04-23 | 2024-04-23 | 2025-02-20 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK ACCL ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391102 | T2 EI SSQC-SNT YNZ SW ST 10/153 RPR GYWW | ICW
LC | 128627783 | 023/005 | T2 EI TRINITY-MAPLE CREEK 23/005 RMV VEG | EUREKA | ETL.8170.POLE.WOOD | 2024-04-23 | 2024-04-23 | 2024-10-29 | On-Time |  | 2025-04-23 | 2025-04-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128627786 | 024/005 | T2 EI TRINITY-MAPLE CREEK 24/05 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-04-23 | 2024-04-23 | 2024-08-20 | On-Time |  | 2024-10-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46246259 | T2 EI TRINITY-MAPLE CREEK 24/05 RPR GYWW | ICW
LC | 128627820 | 012/003 | T2 EI EXCHEQUER-MARIPOSA 12/3 RPR GYWW | FRESNO | ETL.8640.POLE.NWOD | 2024-04-23 | 2024-04-23 | 2025-04-14 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298199 | T2 EI EXCHEQUER-MARIPOSA 12/3 RPR GYWW | ICW
LC | 128627928 | 047/009 | T2 EI FORT ROSS-GUALALA 47/009 RPR ANCW | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-04-23 | 2024-04-23 | 2024-06-24 | On-Time |  | 2024-10-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46239205 | T2 EI FORT ROSS-GUALALA 47/009 RPR ANCW | ICW
LC | 128627958 | 005/115 | T2 EI COLEMAN-SOUTH 5/115 RPL STRW | TABLEMTN | ETL.6450.POLE.WOOD | 2024-04-23 | 2024-04-23 | 2025-03-25 | On-Time |  | 2025-04-23 | 2025-04-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556789 | T2 EI COLEMAN-SOUTH 05/115 RPL PL | 70Y
LC | 128628231 | 025/012 | T2 EI RIO DLL JCT-BRDGVLL 25/12 RPL POLE | EUREKA | ETL.7850.POLE.WOOD | 2024-04-23 | 2024-04-23 | 2025-06-12 | Past Due |  | 2025-04-23 | 2025-04-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35573023 | T2 EI RIO DLL JCT-BRDGVLL 25/12 RPL POLE | 70Y
LC | 128628263 | 035/005 | T2 EI RIO DLL JCT-BRDGVLL 35/5 RPL POLE | EUREKA | ETL.7850.POLE.WOOD | 2024-04-23 | 2024-04-23 | 2025-06-18 | Past Due |  | 2025-04-23 | 2025-04-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573195 | T2 EI RIO DLL JCT-BRDGVLL 35/5 RPL POLE | 70Y
LC | 128628304 | 060/298 | T2 EI MALIN-ROUND MTN #2 60/298 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-04-23 | 2024-04-23 | 2025-02-10 | On-Time |  | 2025-04-23 | 2025-04-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338191 | T2 EI MALIN-ROUND MTN #2 60/298 RPR SHLD | ICS
LC | 128628311 | 059/296 | T2 MALIN-ROUND MTN #2 59/296 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-04-23 | 2024-04-23 | 2025-04-09 | On-Time |  | 2025-04-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381397 | T2 EI MALIN-ROUND MTN #2 59/296 UNBURY | ICQ
LC | 128628319 | 011/051 | T2 EI LOS ESTEROS-METCALF 11/51 RPR FOND | METCALF | ETL.5353.TOWR | 2024-04-23 | 2024-04-23 | 2025-01-18 | On-Time |  | 2025-04-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46298830 | T2 EI LOS ESTEROS-METCALF 11/51 RPR FOND | ICQ
LC | 128628337 | 030/003 | T2 MNDCNO-WLTS-FRT BRG 30/3 REFRAME | WILLITS | ETL.7550.POLE.WOOD | 2024-04-23 | 2024-04-23 | 2024-04-23 | Past Due |  | 2025-04-23 | 2025-04-23 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35574305 | T2 DI MNDCNO-WLTS-FRT BRG 30/3 REFRAME | 93E
LC | 128628363 | 010/048 | T2 EI LS ESTEROS-METCALF 10/48 RPR FOND | METCALF | ETL.5353.TOWR | 2024-04-23 | 2024-04-23 | 2025-01-18 | On-Time |  | 2025-04-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46298831 | T2 EI LS ESTEROS-METCALF 10/48 RPR FOND | ICQ
LC | 128628382 | 011/061 | T2 TESLA-NEWARK #1 11/61 TOUCH | CONCORD | ETL.5720.TOWR | 2024-04-23 | 2024-04-23 | 2025-05-01 | Past Due |  | 2024-10-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485417 | T2 TESLA-NEWARK #1 11/61 TOUCH | ICQ
LC | 128628419 | 004/047 | T2 EI PIT #5-ROUND MTN #2 4/47 RMV VEG | TABLEMTN | ETL.5430.POLE.STPS | 2024-04-23 | 2024-04-23 | 2024-11-12 | On-Time |  | 2024-07-23 | 2025-04-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128628573 | 043/174 | T2 DI DIABLO-MIDWAY #2 43/174 RPR SHLS | PISMOBCH | ETL.5970.TOWR | 2024-04-23 | 2024-04-23 | 2024-12-06 | On-Time |  | 2024-10-23 | 2025-04-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46248676 | T2 DI DIABLO-MIDWAY #2 43/174 RPR SHLS | ICS
LC | 128628599 | 004/003A | T2 DI LYTNVLL-COVELO 004/003A RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-04-23 | 2024-04-23 | 2024-07-15 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46238958 | T2 DI LYTNVLL-COVELO 004/003A RPR JUMW | ICW
LC | 128628605 | 004/003B | T2 DI LYTNVLL-COVELO 004/003B RPR GYWW | WILLITS | ETL.7390.POLE.NWOD | 2024-04-23 | 2024-04-23 | 2024-07-17 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46239209 | T2 DI LYTNVLL-COVELO 004/003B RPR GYWW | ICW
LC | 128628606 | 004/003B | T2 DI LYTNVLL-COVELO 004/003B RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-04-23 | 2024-04-23 | 2024-07-15 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46238959 | T2 DI LYTNVLL-COVELO 004/003B RPR JUMW | ICW
LC | 128628627 | 019/077 | T2 EI TESLA-METCALF 19/77 COMPLETE | METCALF | ETL.6110.TOWR | 2024-04-23 | 2024-04-23 | 2024-08-12 | On-Time |  | 2025-04-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46256531 | T2 EI TESLA-METCALF 19/77 RPR FOND | ICQ
LC | 128628670 | 004/003C | T2 DI LYTNVLL-COVELO 004/003C RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-04-23 | 2024-04-23 | 2024-07-15 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46239240 | T2 DI LYTNVLL-COVELO 004/003C RPR JUMW | ICW
LC | 128628674 | 029/006 | T2 DI MNDCNO-WLTS-FRT BRG 29/6 RPL INSW | WILLITS | ETL.7550.INSL.CERA | 2024-04-23 | 2024-04-23 | 2025-04-18 | On-Time |  | 2025-04-23 | 2025-04-23 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574303 | T2 DI MNDCNO-WLTS-FRT BRG 29/6 RPL INSW | 93I
LC | 128628688 | 015/092 | T2 EI STNISLUS-MNTECA #2 15/092 RPR STRT | VICTOR | ETL.3820.TOWR | 2024-04-23 | 2024-04-23 | 2025-03-24 | On-Time |  | 2025-04-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416499 | T2 EI STNISLUS-MNTECA #2 15/092 RPR STRT | ICQ
LC | 128628689 | 015/092 | T2 EI STNISLUS-MNTECA #2 15/092 RMV NEST | VICTOR | ETL.3820.TOWR | 2024-04-23 | 2024-04-23 | 2025-02-25 | On-Time |  | 2025-04-23 | 2025-04-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46325895 | T2 EI STNISLUS-MNTECA #2 15/092 RMV NEST | ICS
LC | 128628720 | 015/091 | T2 EI STANISLAUS-MNTECA #2 15/091 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-23 | 2024-04-23 | 2025-03-24 | On-Time |  | 2025-04-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416520 | T2 EI STANISLAUS-MNTECA #2 15/091 UNBURY | ICQ
LC | 128628733 | 014/083 | T2 EI STANISLAUS-MNTCA #2 14/083 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-23 | 2024-04-23 | 2024-06-27 | On-Time |  | 2024-10-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46252430 | T2 EI STANISLAUS-MNTCA #2 14/083 UNBURY | ICQ
LC | 128628735 | 015/092 | T2 EI STANISLAUS-MNTECA #2 15/092 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-23 | 2024-04-23 | 2025-03-24 | On-Time |  | 2025-04-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416521 | T2 EI STANISLAUS-MNTECA #2 15/092 UNBURY | ICQ
LC | 128628738 | 014/083 | T2 EI STANSLAUS-MNTCA #2 14/083 RPR STRT | VICTOR | ETL.3820.TOWR | 2024-04-23 | 2024-04-23 | 2025-03-29 | On-Time |  | 2025-04-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416522 | T2 EI STANSLAUS-MNTCA #2 14/083 RPR STRT | ICQ
LC | 128628740 | 015/090 | T2 EI STNISLAUS-MNTECA #2 15/090 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-23 | 2024-04-23 | 2025-03-24 | On-Time |  | 2025-04-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416523 | T2 EI STNISLAUS-MNTECA #2 15/090 UNBURY | ICQ
LC | 128628742 | 015/090 | T2 EI STNISLAUS-MNTCA #2 15/090 RPR STRT | VICTOR | ETL.3820.TOWR | 2024-04-23 | 2024-04-23 | 2025-03-24 | On-Time |  | 2025-04-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416524 | T2 EI STNISLAUS-MNTCA #2 15/090 RPR STRT | ICQ
LC | 128628772 | 026/012 | T2 DI MNDCNO-WLTS-FRT BRG 26/12 RPR JUMW | WILLITS | ETL.7550.INSL.NCER | 2024-04-23 | 2024-04-23 | 2025-04-03 | On-Time |  | 2024-07-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46239241 | T2 DI MNDCNO-WLTS-FRT BRG 26/12 RPR JUMW | ICW
LC | 128628922 | 059/244 | T2 DI DIABLO-GATES #1 059/244 RPR SHLD | PISMOBCH | ETL.5960.TOWR | 2024-04-23 | 2024-04-23 | 2025-02-18 | On-Time |  | 2025-04-23 | 2025-04-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329572 | T2 DI DIABLO-GATES #1 059/244 RPR SHLS | ICS
LC | 128630174 | 005/064 | T2 EI WEST POINT-VALLEY 5/64L RPR GYWW | VICTOR | ETL.8350.POLE.STPS | 2024-04-24 | 2024-04-23 | 2025-02-06 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327611 | T2 EI WEST POINT-VALLEY 5/64L RPR GYWW | ICW
LC | 128630177 | 005/064 | T2 EI WEST POINT-VALLEY 5/64R RPR GYWW | VICTOR | ETL.8350.POLE.STPS | 2024-04-24 | 2024-04-23 | 2025-02-06 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327504 | T2 EI WEST POINT-VALLEY 5/64R RPR GYWW | ICW
LC | 128651035 | 014/124 | T2 DI CRAG VIEW CSCDE 14/124R RPR OPGW | TABLEMTN | ETL.1350.POLE.STPS | 2024-04-24 | 2024-04-23 | 2024-09-07 | On-Time |  | 2024-07-24 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Wood | Repair | 46249643 | T2 DI CRAG VIEW CSCDE 14/124R RPR OPGW | ICW
LC | 128678868 | 029/005 | T2 DI MDCN-WLTS-FRT BRG 29/5 RPR ANCW | WILLITS | ETL.7550.POLE.NWOD | 2024-04-29 | 2024-04-23 | 2025-03-04 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46310116 | T2 DI MDCN-WLTS-FRT BRG 29/5 RPR ANCW | ICW
LC | 128679006 | 000/017 | T2 DI MNDCNO-WLTS-FRT BRGG 0/17 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-29 | 2024-04-23 | 2025-01-21 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310110 | T2 DI MNDCNO-WLTS-FRT BRGG 0/17 RPR GYWW | ICW
LC | 128679073 | 020/010 | T2 DI MDCN-WLTS-FRT BRG 20/10 RPR ANCW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-29 | 2024-04-23 | 2025-04-08 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46310115 | T2 DI MDCN-WLTS-FRT BRG 20/10 RPR ANCW | ICW
LC | 128679145 | 034/002 | T2 DI MNDCNO-WLTS-FRT BRGG 34/2 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-29 | 2024-04-23 | 2025-04-04 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310117 | T2 DI MNDCNO-WLTS-FRT BRGG 34/2 RPR GYWW | ICW
LC | 128679189 | 005/114 | T2 DI BURNS-LONE STAR #2 5/114 RPR GRWW | MOSSLNDG | ETL.6240.POLE.WOOD | 2024-04-29 | 2024-04-23 | 2025-03-09 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46391200 | T2 DI BURNS-LONE STAR #2 5/114 RPR GRWW | ICW
LC | 128679231 | 021/006 | T2 DI MNDCN-WLTS-FORT BRG 21/6 RPR JUMW | WILLITS | ETL.7550.INSL.NCER | 2024-04-29 | 2024-04-23 | 2024-10-26 | On-Time |  | 2024-07-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46252588 | T2 DI MNDCN-WLTS-FORT BRG 21/6 RPR JUMW | ICW
LC | 128679276 | 003/030 | T2NT DI PIT #1 COTTONWOOD 3/30 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-04-29 | 2024-04-23 | 2025-04-08 | On-Time |  | 2027-04-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381509 | T2NT DI PIT #1 COTTONWOOD 3/30 RPR STRT | ICQ
LC | 128679312 | 059/293 | T2 DI MALIN-ROUND MTN #2 59/293 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-04-29 | 2024-04-23 | 2024-05-10 | On-Time |  | 2024-07-23 | 2025-04-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46240049 | T2 DI MALIN-ROUND MTN #2 59/293 RPR OPGW | ICS
LC | 128679367 | 008/083 | T2 DI PIT #5-RND MTN #1 8/83 RPL STRW | TABLEMTN | ETL.5420.POLE.WDPS | 2024-04-29 | 2024-04-23 | 2025-04-11 | On-Time |  | 2025-04-23 | 2025-04-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35607190 | T2 DI PIT #5-RND MTN #1 8/083 RPL STRW | 70Y
LC | 128679416 | 019/003 | T2 DI MNDOCINO-WLLTS-FRT 19/3 RPL HRDD | WILLITS | ETL.7550.POLE.NWOD | 2024-04-29 | 2024-04-23 | 2025-04-09 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46310113 | T2 DI MNDOCINO-WLLTS-FRT 19/3 RPL HRDD | ICW
LC | 128679603 | 111/005 | T2 DI HUMBOLDT-TRINITY 111/5L RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-04-29 | 2024-04-23 | 2025-03-15 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345772 | T2 DI HUMBOLDT-TRINITY 111/5L RPR GYWW | ICW
LC | 128679604 | 111/005 | T2 DI HUMBOLDT-TRINITY 111/5L RPR CRSW | EUREKA | ETL.1820.POLE.WDPS | 2024-04-29 | 2024-04-23 | 2025-03-15 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46345773 | T2 DI HUMBOLDT-TRINITY 111/5L RPR CRSW | ICW
LC | 128679677 | 014/125 | T2 DI CRAG VIEW-CASCADE 14/125L RPR OPGW | TABLEMTN | ETL.1350.POLE.STPS | 2024-04-29 | 2024-04-23 | 2024-09-09 | On-Time |  | 2024-10-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Wood | Repair | 46249644 | T2 DI CRAG VIEW-CASCADE 14/125L RPR OPGW | ICW
LC | 128680651 | 036/003 | T2 DI MDCN-WLTS-FRT BRG 36/3 RPLC INSW | WILLITS | ETL.7550.INSL.NCER | 2024-04-30 | 2024-04-23 | 2025-04-10 | On-Time |  | 2025-04-23 | 2025-04-23 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574706 | T2 DI MDCN-WLTS-FRT BRG 36/3 RPLC INSW | 93I
LC | 128700030 | 008/083 | T2 DI PIT #5-RND MTN #1 8/83 RPL STRW | TABLEMTN | ETL.5420.POLE.WDPS | 2024-05-02 | 2024-04-23 | 2025-04-11 | On-Time |  | 2025-04-23 | 2025-04-23 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35607190 | T2 DI PIT #5-RND MTN #1 8/083 RPL STRW | 70Y
LC | 128707451 | 004/008C | T2 DI LYTNVLL-CVLO 4/8C RPR GYWW | WILLITS | ETL.7390.POLE.NWOD | 2024-05-03 | 2024-04-23 | 2025-04-15 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46414843 | T2 DI LYTNVLL-CVLO 4/8C RPR GYWW | ICW
LC | 128707500 | 004/008B | T2 DI LYTNVLL-CVLO 4/8B RPR GYWW | WILLITS | ETL.7390.POLE.NWOD | 2024-05-03 | 2024-04-23 | 2025-04-15 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46414842 | T2 DI LYTNVLL-CVLO 4/8B RPR GYWW | ICW
LC | 128712951 | 015/207B | T2 EI WTSNVLLE-SALINAS 15/207B RPL POLE | MOSSLNDG | ETL.8310.POLE.WOOD | 2024-05-06 | 2024-04-23 | 2025-02-12 | On-Time |  | 2025-04-23 | 2025-04-23 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW INSP REMT SWRK CLR ACCL ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573393 | T2 EI WTSNVLLE-SALINAS 15/207A RPL POLE | 70Y
LC | 128716784 | 020/009 | T2 DI MENDOCINO-WFB 20/9 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-06 | 2024-04-23 | 2025-04-08 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310114 | T2 DI MENDOCINO-WFB 20/9 RPR GYWW | ICW
LC | 128717066 | 033/007 | T2 DI MNDCN-WLTS-FRT BRG 33/7 RPL INSW | WILLITS | ETL.7550.INSL.NCER | 2024-05-06 | 2024-04-23 | 2025-04-04 | On-Time |  | 2025-04-23 | 2025-04-23 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574703 | T2 DI MNDCN-WLTS-FRT BRG 33/7 RPL INSW | 93I
LC | 128744999 | 079/402 | T2 DI MALIN-ROUND MNTN#2 79/402 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-05-10 | 2024-04-23 | 2025-04-07 | On-Time |  | 2025-04-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381414 | T2 DI MALIN-ROUND MNTN#2 79/402 RPR FOND | ICQ
LC | 128745047 | 019/005 | T2 DI MNDCN WLLITS 19/5 RPR JUMW | WILLITS | ETL.7550.INSL.NCER | 2024-05-10 | 2024-04-23 | 2024-10-26 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251315 | T2 DI MNDCN WLLITS 19/5 RPR JUMW | ICW
LC | 128745060 | 004/066 | T2 DI WEIMAR #1 004/066 RPR JMPW | SACTO | ETL.7560.INSL.NCER | 2024-05-10 | 2024-04-23 | 2024-09-15 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46310843 | T2 DI WEIMAR #1 004/066 RPR JMPW | ICW
LC | 128745171 | 034/004 | T2 DI MNDO-WLITS-FRT BRG-34/04 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-10 | 2024-04-23 | 2025-04-04 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310118 | T2 DI MNDO-WLITS-FRT BRG-34/04 RPR GYWW | ICW
LC | 128745366 | 021/184B | T2 DI CRAG VIEW-CASCADE 21/184B RPR STRW | TABLEMTN | ETL.1350.POLE.NWOD | 2024-05-10 | 2024-04-23 | 2025-01-21 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454376 | T2 DI CRAG VIEW-CASCADE 21/184B RPR STRW | ICW
LC | 128746262 | 019/605 | T2 DI SPAULDING-SUMMIT 19/605 RPL HRDD | SACTO | ETL.8060.POLE.WOOD | 2024-05-10 | 2024-04-23 | 2024-04-23 | Past Due |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace
LC | 128746296 | 013/011-GUY | T2 DI MNDCN-WLT-FT BG 13/11-GUY RPR STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-10 | 2024-04-23 | 2025-02-07 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Structure-Wood | Repair | 46310112 | T2 DI MNDCN-WLT-FT BG 13/11-GUY RPR STRW | ICW
LC | 128746391 | 058/288 | T2 DI MALIN-ROUND MTN#2 58/288 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-05-10 | 2024-04-23 | 2025-02-10 | On-Time |  | 2025-04-23 | 2025-04-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338195 | T2 DI MALIN-ROUND MTN#2 58/288 RPR SHLD | ICS
LC | 128746772 | 058/289 | T2 MALIN-ROUND MTN#2 58/289 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-05-10 | 2024-04-23 | 2025-04-09 | On-Time |  | 2025-04-23 | 2025-04-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381418 | T2 DI MALIN-ROUND MTN#2 58/289 RPR GYWT | ICQ
LC | 128746833 | 013/011 | T2 DI MNDCN-WLTS-FRT BRG 13/11 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-10 | 2024-04-23 | 2025-02-07 | On-Time |  | 2025-04-23 | 2025-04-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310111 | T2 DI MNDCN-WLTS-FRT BRG 13/11 RPR GYWW | ICW
LC | 128629996 | 020/163 | T2 DRUM-HIGGINS 20/163 RPR INSS | SACTO | ETL.4393.INSL.CERA | 2024-04-24 | 2024-04-24 | 2025-01-10 | On-Time |  | 2025-04-24 | 2025-04-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46324627 | T2 DRUM-HIGGINS 20/163 RPR INSS | ICS
LC | 128630042 | 020/162 | T2 DRUM-HIGGINS 20/162 RPR JUMS | SACTO | ETL.4393.INSL.CERA | 2024-04-24 | 2024-04-24 | 2025-01-10 | On-Time |  | 2025-04-24 | 2025-04-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Jumper-Steel | Repair | 46236911 | T2 DRUM-HIGGINS 20/162 RPR JUMS | ICS
LC | 128630530 | 019/123 | T2 EI STNS-MLNS SS-MCA 19/123 UNBURY | VICTOR | ETL.3830.TOWR | 2024-04-24 | 2024-04-24 | 2025-04-04 | On-Time |  | 2025-04-24 | 2025-04-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46493480 | T2 EI STNS-MLNS SS-MCA 19/123 UNBURY | ICQ
LC | 128631125 | 020/116 | T2 EI STNSLS-MNTC #2 20/116 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-24 | 2024-04-24 | 2025-01-15 | On-Time |  | 2025-04-24 | 2025-04-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416525 | T2 EI STNSLS-MNTC #2 20/116 UNBURY | ICQ
LC | 128631171 | 020/116 | T2 EI STNSLS-MNTC #2 20/116 RPL HRDT | VICTOR | ETL.3820.TOWR | 2024-04-24 | 2024-04-24 | 2025-01-15 | On-Time |  | 2025-04-24 | 2025-04-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46248679 | T2 EI STNSLS-MNTC #2 20/116 RPL HRDT | ICQ
LC | 128631177 | 020/117 | T2 EI STNSLS-MNTC #2 020/117 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-24 | 2024-04-24 | 2025-01-15 | On-Time |  | 2025-04-24 | 2025-04-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416527 | T2 EI STNSLS-MNTC #2 020/117 UNBURY | ICQ
LC | 128634289 | 019/179 | T2 EI BRDGVLE-CTNWD 19/179 RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-24 | 2024-04-24 | 2025-03-22 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311088 | T2 EI BRDGVLE-CTNWD 19/179 RPR GYWW | ICW
LC | 128636762 | 020/119 | T2 EI STNSLS-MNTC #2 20/119 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-24 | 2024-04-24 | 2025-01-15 | On-Time |  | 2025-04-24 | 2025-04-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416528 | T2 EI STNSLS-MNTC #2 20/119 UNBURY | ICQ
LC | 128636763 | 028/002 | T2 MONTE RIO-FORT ROSS 28/002 RPR STRW | LAKEVLLE | ETL.6979.POLE.WOOD | 2024-04-24 | 2024-04-24 | 2025-05-21 | Past Due |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46499058 | T2 MONTE RIO-FORT ROSS 28/002 RPR STRW | ICW
LC | 128637111 | 000/003 | T2 EI WISHON-COPPERMINE 00/03 RMV ENCRCH | FRESNO | ETL.9330.TOWR | 2024-04-24 | 2024-04-24 | 2024-09-05 | On-Time |  | 2024-10-24 | 2025-04-24 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46249749 | T2 EI WISHON-COPPERMINE 00/03 RMV ENCRCH | CHR
LC | 128641151 | 035/003 | T2 EI RIO DLL JCT-BRDGVLE 35/3 RPR GYWW | EUREKA | ETL.7850.POLE.WOOD | 2024-04-24 | 2024-04-24 | 2024-07-22 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46246258 | T2 EI RIO DLL JCT-BRDGVLE 35/3 RPR GYWW | ICW
LC | 128641897 | 013/120 | T2 UKH-HPLND-CLVRDLE 13/120 RPL POLE | WILLITS | ETL.4050.POLE.WOOD | 2024-04-24 | 2024-04-24 | 2025-06-19 | Past Due |  | 2025-04-24 | 2025-04-24 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35571881 | T2 EI UKH-HPLND-CLVRDLE 13/120 RPL POLE | 70Y
LC | 128645294 | A001/031 | T2 WV VALLEY SPRINGS #1 A001/031 REFRAME | VICTOR | ETL.8210.POLE.NWOD | 2024-04-24 | 2024-04-24 | 2025-05-02 | Past Due |  | 2025-04-24 | 2025-04-24 | 637 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Crossarm-Wood | Replace | 31622463 | T2 VALLEY SPRINGS #1 001/032 RPL POLE | 70Y
LC | 128645312 | 011/011 | T2 EI EXCHEQUER-MARIPOSA 11/11 RPR GYWW | FRESNO | ETL.8640.POLE.NWOD | 2024-04-24 | 2024-04-24 | 2025-04-14 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SPCR ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298220 | T2 EI EXCHEQUER-MARIPOSA 11/11 RPR GYWW | ICW
LC | 128647427 | 011/008 | T2 EI EXCHEQUER-MARIPOSA 11/8 RPR GYWW | FRESNO | ETL.8640.POLE.NWOD | 2024-04-24 | 2024-04-24 | 2025-04-14 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298221 | T2 EI EXCHEQUER-MARIPOSA 11/8 RPR GYWW | ICW
LC | 128648636 | 004/002 | T2 EI DUNLAP TAP 004/002 COTTER | FRESNO | ETL.9061.INSL.NCER | 2024-04-24 | 2024-04-24 | 2024-07-16 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46247130 | T2 EI DUNLAP TAP 004/002 COTTER | ICW
LC | 128648724 | 004/002 | T2 EI DUNLAP TAP 004/002 RPR INSW | FRESNO | ETL.9061.INSL.NCER | 2024-04-24 | 2024-04-24 | 2025-03-21 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC ACCH COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298223 | T2 EI DUNLAP TAP 004/002 RPR INSW | ICW
LC | 128648854 | 018/170 | T2 EI BRDGVLLE-CTTNWD 18/170 RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-24 | 2024-04-24 | 2025-03-22 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311090 | T2 EI CTNWD-HMBLDT NO. 2 18/170 RPR GYWW | ICW
LC | 128648865 | 018/172 | T2 EI BRDGVLLE-CTTNWD 18/172 RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-24 | 2024-04-24 | 2025-03-22 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311089 | T2 EI CTNWD-HMBLDT NO. 2 18/172 RPR GYWW | ICW
LC | 128649722 | 009/147 | T2 EI SSQUOC-SNTA YNZ SS 9/147 RPL POLE | PISMOBCH | ETL.3700.POLE.WOOD | 2024-04-24 | 2024-04-24 | 2025-04-02 | On-Time |  | 2025-04-24 | 2025-04-24 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573783 | T2 EI SSQUOC-SNTA YNZ SS 9/147 RPL POLE | 70Y
LC | 128650489 | 040/006 | T2 TRINITY-MAPLE CREEK 40/6R RPL STRW | EUREKA | ETL.8170.POLE.WDPS | 2024-04-24 | 2024-04-24 | 2025-04-29 | Past Due |  | 2025-04-24 | 2025-04-24 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572019 | T2 EI TRINITY-MAPLE CREK_040/006R RPL PL | 70Y
LC | 128650501 | 040/006 | T2 TRINITY-MAPLE CREEK 40/6L RPL STRW | EUREKA | ETL.8170.POLE.WDPS | 2024-04-24 | 2024-04-24 | 2025-04-29 | Past Due |  | 2025-04-24 | 2025-04-24 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572019 | T2 EI TRINITY-MAPLE CREK_040/006R RPL PL | 70Y
LC | 128650507 | 040/006 | T2 TRINITY-MAPLE CREEK 40/6C RPL STRW | EUREKA | ETL.8170.POLE.WDPS | 2024-04-24 | 2024-04-24 | 2025-04-29 | Past Due |  | 2025-04-24 | 2025-04-24 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572019 | T2 EI TRINITY-MAPLE CREK_040/006R RPL PL | 70Y
LC | 128650805 | 000/011 | T2 EI WISHON-COPPERMINE 0/11 RPL INSS | FRESNO | ETL.9330.INSL.CERA | 2024-04-24 | 2024-04-24 | 2025-04-21 | On-Time |  | 2025-04-24 | 2025-04-24 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574071 | T2 EI WISHON-COPPERMINE 00/11 RPL INSS | 93K
LC | 128650816 | 008/081 | T2 EI PIT #5-ROUND MTN #2 8/81L RPR GYWW | TABLEMTN | ETL.5430.POLE.STPS | 2024-04-24 | 2024-04-24 | 2024-05-30 | On-Time |  | 2024-10-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46254930 | T2 EI PIT #5-ROUND MTN #2 8/81L RPR GYWW | ICW
LC | 128650818 | 008/081 | T2 EI PIT #5-ROUND MTN #2 8/81C RPR GYWW | TABLEMTN | ETL.5430.POLE.STPS | 2024-04-24 | 2024-04-24 | 2024-05-30 | On-Time |  | 2024-10-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46252095 | T2 EI PIT #5-ROUND MTN #2 8/81C RPR GYWW | ICW
LC | 128650844 | 008/081 | T2 EI PIT #5-ROUND MTN #2 8/81R RPR GYWW | TABLEMTN | ETL.5430.POLE.STPS | 2024-04-24 | 2024-04-24 | 2024-05-30 | On-Time |  | 2024-10-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46250269 | T2 EI PIT #5-ROUND MTN #2 8/81R RPR GYWW | ICW
LC | 128650943 | 035/010 | T2 EI RIO DLL JCT-BRDGVLE 35/10 RPL STRW | EUREKA | ETL.7850.POLE.WOOD | 2024-04-24 | 2024-04-24 | 2025-06-18 | Past Due |  | 2025-04-24 | 2025-04-24 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP ACCL COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573198 | T2 EI RIO DLL JCT-BRDGVLE 35/10 RPL STRW | 70Y
LC | 128651018 | 043/176 | T2 DI DIABLO-MIDWAY #2 43/176 RPR SHLD | PISMOBCH | ETL.5970.TOWR | 2024-04-24 | 2024-04-24 | 2025-04-11 | On-Time |  | 2025-04-24 | 2025-04-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329585 | T2 DI DIABLO-MIDWAY #2 43/176 RPR SHIELD | ICS
LC | 128651205 | 113/008 | T2 DI HUMBOLDT-BRDGVL 113/8 RPR JUMW | EUREKA | ETL.1810.INSL.NCER | 2024-04-24 | 2024-04-24 | 2024-04-24 | Past Due |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46238997 | T2 DI HUMBOLDT-BRDGVL 113/8 RPR JUMW | ICW
LC | 128651208 | 113/008 | T2 HUMBOLDT-BRIDGEVILLE 113/8C RPR ADSS | EUREKA | ETL.1810.POLE.STPS | 2024-04-24 | 2024-04-24 | 2024-04-24 | Past Due |  | 2024-07-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46238998 | T2 DI HUMBOLDT-BRDGVLLE 113/8 RPR ADSS | ICW
LC | 128651223 | 038/249 | T2 DI TRINITY CTNWD 38/249 RPL INSS | TABLEMTN | ETL.4040.INSL.NCER | 2024-04-24 | 2024-04-24 | 2025-02-24 | On-Time |  | 2025-04-24 | 2025-04-24 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574250 | T2 DI TRINITY CTNWD 38/249 RPL INSS | 93K
LC | 128651225 | 038/249 | T2 DI TRINITY CTNWD 38/249 RPR JUMS | TABLEMTN | ETL.4040.INSL.NCER | 2024-04-24 | 2024-04-24 | 2024-08-26 | On-Time |  | 2024-07-24 | 2025-04-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46237036 | T2 DI TRINITY CTNWD 38/249 RPR JUMS | ICS
LC | 128651228 | 039/000 | T2 DI MNDCN WLTS FRT BRG 39/0 COTTER | WILLITS | ETL.7550.POLE.WOOD | 2024-04-24 | 2024-04-24 | 2025-01-21 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310120 | T2 DI MNDCN WLTS FRT BRG 39/0 COTTER | ICW
LC | 128652321 | 000/012 | T2 EI BRCBRG JCT-MRPSA TAP 0/12 RPL INSW | FRESNO | ETL.8651.INSL.NCER | 2024-04-25 | 2024-04-24 | 2025-03-28 | On-Time |  | 2025-04-24 | 2025-04-24 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35554460 | T2 EI BRCBRG JCT-MRPSA TAP 0/12 RPL INSW | 93I
LC | 128652325 | 012/006 | T2 EI VLY SPRNGS-MARTEL #1 12/6 RPL SPLW | VICTOR | ETL.8240.INSL.NCER | 2024-04-25 | 2024-04-24 | 2025-04-13 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Splice-Wood | Replace | 46325899 | T2 EI VLY SPRNGS-MARTEL #1 12/6 RPL SPLW | ICW
LC | 128652433 | 011/004 | T2 EI VLLY SPRNGS-MRTL #1 11/4 RPR GYWW | VICTOR | ETL.8240.POLE.NWOD | 2024-04-25 | 2024-04-24 | 2024-05-22 | On-Time |  | 2024-10-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46236479 | T2 EI VLLY SPRNGS-MRTL #1 11/4 RPR GYWW | ICW
LC | 128653399 | 007/004 | T2 EI DUNLAP TAP 7/4 RPR JUMW | FRESNO | ETL.9061.INSL.NCER | 2024-04-25 | 2024-04-24 | 2025-03-21 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Jumper-Wood | Repair | 46298224 | T2 EI DUNLAP TAP 007/004 RPR JMPW | ICW
LC | 128653403 | 010/003 | T2 EI DUNLAP TAP 010/003 RPR GYWW | FRESNO | ETL.9061.POLE.NWOD | 2024-04-25 | 2024-04-24 | 2024-07-16 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46247131 | T2 EI DUNLAP TAP 010/003 RPR GYWW | ICW
LC | 128661574 | 028/333C | T2 DI DRUM-SUMMIT #2 28/33C COMPLETE | SACTO | ETL.1450.POLE.NWOD | 2024-04-26 | 2024-04-24 | 2024-05-16 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46247404 | T2 DI DRUM-SUMMIT #2 28/33C RPR GYWW | ICW
LC | 128661871 | 033/005 | T2 DI FULTON-HOPLAND 33/5 RPR JUMW | LAKEVLLE | ETL.6890.INSL.NCER | 2024-04-26 | 2024-04-24 | 2025-03-27 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46239883 | T2 DI FULTON-HOPLAND 33/5 RPR JUMW | ICW
LC | 128661931 | 89 | T2 DI MNDCNO-WLLTS-FRT BRG 14/0 RPR JUMW | WILLITS | ETL.7550.SWIT | 2024-04-26 | 2024-04-24 | 2025-04-14 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46246784 | T2 DI MENDOCINO-WILLITS 14/0 RPR JUMP | ICW
LC | 128662034 | 043/287B | T2 DI TRNTY-CTONWD-43/287B RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-04-26 | 2024-04-24 | 2024-08-18 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46239919 | T2 DI TRNTY-CTONWD-43/287B RPR JUMW | ICW
LC | 128662482 | 006/066 | T2 DI IGNACIO-BOLINAS #1 6/66 RPR GYWW | LAKEVLLE | ETL.7140.POLE.STPS | 2024-04-26 | 2024-04-24 | 2025-02-14 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46403748 | T2 DI IGNACIO-BOLINAS #1 6/66 RPR GYWW | ICW
LC | 128679054 | 032/005 | T2 DI FULTON-HOP 32/5 RPR GYWW | LAKEVLLE | ETL.6890.POLE.NWOD | 2024-04-29 | 2024-04-24 | 2025-01-22 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46403749 | T2 DI FULTON-HOP 32/5 RPR GYWW | ICW
LC | 128679147 | 023/204 | T2 DI BRIDGVIL-CTNWD-23/204R RPR ANCW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-29 | 2024-04-24 | 2024-05-29 | On-Time |  | 2024-10-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46239915 | T2 DI BRIDGVIL-CTNWD-23/204R RPR ANCW | ICW
LC | 128679320 | 112/003 | T2 DI HUMBOLDT-BRGV 112/3L RMV VEG | EUREKA | ETL.1810.POLE.STPS | 2024-04-29 | 2024-04-24 | 2024-10-18 | On-Time |  | 2024-10-24 | 2025-04-24 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128679323 | 112/003 | T2 DI HUMBOLDT-BRGV 112/3R RMV VEG | EUREKA | ETL.1810.POLE.STPS | 2024-04-29 | 2024-04-24 | 2024-10-18 | On-Time |  | 2024-10-24 | 2025-04-24 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128679351 | 112/003 | T2 DI HUMBOLDT-BRGV 112/3R RPR GYWW | EUREKA | ETL.1810.POLE.STPS | 2024-04-29 | 2024-04-24 | 2024-12-10 | On-Time |  | 2024-10-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46246382 | T2 DI HUMBOLDT-BRGV 112/3R RPR GYWW | ICW
LC | 128679478 | 016/114 | T2 DI HELMS-GREGG #1 16/114 RPL HRDT | FRESNO | ETL.4870.TOWR | 2024-04-29 | 2024-04-24 | 2025-01-21 | On-Time |  | 2025-04-24 | 2025-04-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46297867 | T2 DI HELMS-GREGG #1 16/114 RPL HRDT | ICQ
LC | 128679608 | 024/209 | T2 DI BRIDGEVILLE-CTTNWD 24/209 RPR STRW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-04-29 | 2024-04-24 | 2025-03-24 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311087 | T2 DI BRIDGEVILLE-CTTNWD 24/209 RPR STRW | ICW
LC | 128679730 | 023/208 | T2 DI BRIDGEVL-CWD 23/208 REGRADE | TABLEMTN | ETL.1110.POLE.STPS | 2024-04-29 | 2024-04-24 | 2024-05-29 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46254642 | T2 DI BRIDGEVL-CWD 23/208 REGRADE | ICW
LC | 128698673 | 040/010 | T2 DI MNDO-WILITS-FRT BRG 40/10 RPL STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-01 | 2024-04-24 | 2025-01-16 | On-Time |  | 2025-04-24 | 2025-04-24 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574710 | T2 DI MNDO-WILITS-FRT BRG 40/10 RPL STRW | 70Y
LC | 128698795 | 005/055C | T2 IGNACIO-BOLINAS #1 5/55C RPL INSW | LAKEVLLE | ETL.7140.INSL.CERA | 2024-05-01 | 2024-04-24 | 2024-04-24 | Past Due |  | 2025-04-24 | 2025-04-24 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35638119 | T2 IGNACIO-BOLINAS #1 5/55C RPL INSW | 93I
LC | 128698893 | 040/007 | T2 DI MNDCNO-WLITS-FRT BRG 40/7 RPL HRDD | WILLITS | ETL.7550.POLE.WOOD | 2024-05-01 | 2024-04-24 | 2024-04-24 | Past Due |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46544431 | T2 DI MNDCNO-WLITS-FRT BRG 40/7 RPL HRDD | ICW
LC | 128698895 | 040/007 | T2 DI MNDCNO-WLITS-FRT BRG 40/7 RPL SPLW | WILLITS | ETL.7550.INSL.NCER | 2024-05-01 | 2024-04-24 | 2025-01-16 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Splice-Wood | Replace | 46310121 | T2 DI MNDCNO-WLITS-FRT BRG 40/7 RPL SPLW | ICW
LC | 128745166 | 011/246 | T2 DI SNTA ROSA CORONA 11/246 RPR ANCW | LAKEVLLE | ETL.4309.POLE.WOOD | 2024-05-10 | 2024-04-24 | 2024-12-11 | On-Time |  | 2024-10-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46249730 | T2 DI SNTA ROSA CORONA 11/246 RPR ANCW | ICW
LC | 128745349 | 112/002 | T2 DI HMBLDT-BRDGVLL 112/002 RPR ADSS | EUREKA | ETL.1810.POLE.STPS | 2024-05-10 | 2024-04-24 | 2025-03-04 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | ADSS - Wood | Repair | 46345774 | T2 DI HMBLDT-BRDGVLL 112/002 RPR ADSS | ICW
LC | 128746320 | 041/006 | T2 DI MNDCIN-WLLTS-FRT BRG 41/6 RPR STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-10 | 2024-04-24 | 2025-01-15 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310122 | T2 DI MNDCIN-WLLTS-FRT BRG 41/6 RPR STRW | ICW
LC | 128746327 | 038/250B | T2 DI TRNTY-CTNWD- 38/250B RPR JMPS | TABLEMTN | ETL.4040.INSL.NCER | 2024-05-10 | 2024-04-24 | 2025-02-24 | On-Time |  | 2025-04-24 | 2025-04-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46452757 | T2 DI TRNTY-CTNWD- 38/250B RPR JMPS | ICS
LC | 128746335 | 017/092 | T2 DI BALCH-SANGER 017/092 RPL HRDT | FRESNO | ETL.1050.TOWR | 2024-05-10 | 2024-04-24 | 2025-03-12 | On-Time |  | 2025-04-24 | 2025-04-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46297871 | T2 DI BALCH-SANGER 017/092 RPL HRDT | ICQ
LC | 128746536 | 007/073 | T2 DI PIT #5-RND MTN#1-07/73 RPL HRDW | TABLEMTN | ETL.5420.POLE.WDPS | 2024-05-10 | 2024-04-24 | 2024-07-30 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46305287 | T2 DI PIT #5-RND MTN#1-07/73 RPL HRDW | ICW
LC | 128746681 | 036/293 | T2 DI BRDGVL CTTNWOOD 36/293 RPR STRW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-05-10 | 2024-04-24 | 2024-09-06 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311086 | T2 DI BRDGVL CTTNWOOD 36/293 RPR STRW | ICW
LC | 128746951 | 038/005 | T2 DI MDCNO WLTS FRT BG 38/005 RMV VEG | WILLITS | ETL.7550.POLE.WOOD | 2024-05-10 | 2024-04-24 | 2025-01-23 | On-Time |  | 2025-04-24 | 2025-04-24 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE ACCL CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128747071 | 017/091 | T2 DI BALCH-SANGER 17/91 RPL HRDT | FRESNO | ETL.1050.TOWR | 2024-05-10 | 2024-04-24 | 2025-03-13 | On-Time |  | 2025-04-24 | 2025-04-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46297869 | T2 DI BALCH-SANGER 17/91 RPL HRDT | ICQ
LC | 128747073 | 017/091 | T2 DI BALCH-SANGER 17/91 RPR JUMS | FRESNO | ETL.1050.INSL.CERA | 2024-05-10 | 2024-04-24 | 2025-04-21 | On-Time |  | 2025-04-24 | 2025-04-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46298171 | T2 DI BALCH-SANGER 17/91 RPR JMPS | ICS
LC | 128747077 | 014/075 | T2 DI BALCH-SANGER 14/75 RPR STRT | FRESNO | ETL.1050.TOWR | 2024-05-10 | 2024-04-24 | 2025-03-12 | On-Time |  | 2025-04-24 | 2025-04-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CGI COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46297866 | T2 DI BALCH-SANGER 14/75 RPR STRT | ICQ
LC | 128768497 | 022/149 | T2 DI HELMS-GREGG #1 22/149 RPL SHLS | FRESNO | ETL.4870.TOWR | 2024-05-13 | 2024-04-24 | 2025-03-25 | On-Time |  | 2025-04-24 | 2025-04-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298174 | T2 DI HELMS-GREGG #1 22/149 RPL SHLS | ICS
LC | 128768498 | 022/149 | T2 DI HELMS-GREGG #1 22/149 COTTER | FRESNO | ETL.4870.INSL.CERA | 2024-05-13 | 2024-04-24 | 2025-03-25 | On-Time |  | 2025-04-24 | 2025-04-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46298175 | T2 DI HELMS-GREGG #1 22/149 COTTER | ICS
LC | 128768533 | 014/073 | T2 DI KING RVR SNGR RDLY 14/73 RPR JUMS | FRESNO | ETL.2030.INSL.NCER | 2024-05-13 | 2024-04-24 | 2024-11-18 | On-Time |  | 2024-07-24 | 2025-04-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46250580 | T2 DI KING RVR SNGR RDLY 14/73 RPR JUMS | ICS
LC | 128768627 | 044/295A | T2 DI TRINITY CGNWOOD 44/295A RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-05-13 | 2024-04-24 | 2024-08-17 | On-Time |  | 2024-07-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46250271 | T2 DI TRINITY CGNWOOD 44/295A RPR JUMW | ICW
LC | 128768629 | 044/295C | T2 DI TRINITY CGNWOOD 44/295C RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-05-13 | 2024-04-24 | 2024-08-17 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251383 | T2 DI TRINITY CGNWOOD 44/295C RPR JUMW | ICW
LC | 128768798 | 000/001 | T2 DI BLACK TAP-TOWER 000/001 RMV VEG | TABLEMTN | ETL.5431.TOWR | 2024-05-13 | 2024-04-24 | 2025-02-10 | On-Time |  | 2025-04-24 | 2025-04-24 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128768958 | 006/064 | T2 DI GNACIO-BOLINAS #1 6/64 RPR GYWW | LAKEVLLE | ETL.7140.POLE.WOOD | 2024-05-13 | 2024-04-24 | 2025-02-14 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46403747 | T2 DI GNACIO-BOLINAS #1 6/64 RPR GYWW | ICW
LC | 128769083 | 044/295B | T2 DI TRYNITY-CTNWD 44/295B RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-05-13 | 2024-04-24 | 2024-08-17 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46250270 | T2 DI TRYNITY-CTNWD 44/295B RPR JUMW | ICW
LC | 128773457 | 026/197 | T2 DI DRUM-RIO OSO #1 26/197 RPR STRT | SACTO | ETL.1420.TOWR | 2024-05-14 | 2024-04-24 | 2025-01-02 | On-Time |  | 2025-04-24 | 2025-04-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46327692 | T2 DI DRUM-RIO OSO #1 26/197 RPR STRT | ICQ
LC | 128773621 | 030/007 | T2 DI FULTON HPLND 30/7 INSP STRW | LAKEVLLE | ETL.6890.POLE.NWOD | 2024-05-14 | 2024-04-24 | 2024-05-29 | On-Time |  | 2024-10-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46249712 | T2 DI FULTON HPLND 30/7 INSP STRW | ICW
LC | 128773660 | 032/007 | T2 DI FLTN-HPLAND 032/007 RPR GYWW | LAKEVLLE | ETL.6890.POLE.NWOD | 2024-05-14 | 2024-04-24 | 2025-01-22 | On-Time |  | 2025-04-24 | 2025-04-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305935 | T2 DI FLTN-HPLAND 032/007 RPR GYWW | ICW
LC | 128773868 | 024/212 | T2 DI BRDGVL-CTTNWD 024/212R RPL STRW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-05-14 | 2024-04-24 | 2025-04-07 | On-Time |  | 2025-04-24 | 2025-04-24 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572060 | T2 DI BRDGVL-CTTNWD 024/212R RPL STRW | 70Y
LC | 128773869 | 024/212 | T2 DI BRDGVL-CTTNWD 024/212L RPL STRW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-05-14 | 2024-04-24 | 2025-04-07 | On-Time |  | 2025-04-24 | 2025-04-24 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572060 | T2 DI BRDGVL-CTTNWD 024/212R RPL STRW | 70Y
LC | 128774294 | 013/070 | T2 DI KINGS RIVER-SANGER 13/70 RPR INSS | FRESNO | ETL.2030.INSL.CERA | 2024-05-14 | 2024-04-24 | 2025-03-11 | On-Time |  | 2025-04-24 | 2025-04-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46298188 | T2 DI KINGS RIVER-SANGER 13/70 RPR INSS | ICS
LC | 123409950 | 003/018 | T2NT EI PTTSBURG-MRTNZ #2 3/18 RPL INSS | CONCORD | ETL.3330.INSL | 2022-04-25 | 2022-04-25 | 2023-08-01 | On-Time |  | 2025-04-25 | 2025-04-25 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Insulator-Steel | Replace | 31626871 | T2 EI PITTSBURG-MARTNZ #2 RPL INSS IN 2 | 93K
LC | 123411920 | 016/062 | T2NT DI DBL MDWY #2 16/62 RPR SHLS | PISMOBCH | ETL.5970.TOWR | 2022-04-25 | 2022-04-25 | 2023-11-14 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire / OPGW-Steel | Repair | 45661138 | T2 DI DBL MDWY #2 16/62 RPR SHLS | ICS
LC | 123420474 | 086/437 | T2NT EI MLN-RND MTN #2 86/437 BNT STEEL | TABLEMTN | ETL.6020.TOWR | 2022-04-25 | 2022-04-25 | 2023-08-22 | On-Time |  | 2025-04-25 | 2025-04-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45616945 | T2 EI MALIN-RND MTN #2 86/437 BNT STEEL | ICQ
LC | 123420757 | 020/083 | T2NT DI DIABLO-MIDWAY #2 20/83 RPL HRDT | PISMOBCH | ETL.5970.TOWR | 2022-04-25 | 2022-04-25 | 2023-07-06 | On-Time |  | 2025-04-25 | 2025-04-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 45648865 | T2 DI DIABLO-MIDWAY #2- 20/83 RPL HRDT | ICQ
LC | 123432983 | 028/112 | T2NT DI DIBLO-MDWY #3 28/112 RPR SHLS | PISMOBCH | ETL.5980.TOWR | 2022-04-26 | 2022-04-25 | 2023-11-29 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire / OPGW-Steel | Repair | 45661162 | T2 DI DIBLO-MDWY #3 28/112 RPR SHLS | ICS
LC | 128652436 | 021/126 | T2 STANSLS-MNTC #2 21/126 TOUCH | VICTOR | ETL.3820.TOWR | 2024-04-25 | 2024-04-25 | 2025-01-13 | On-Time |  | 2024-10-25 | 2025-04-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472916 | T2 STANSLS-MNTC #2 21/126 TOUCH | ICQ
LC | 128652883 | :003/007 | T2 EI BLLT-RVRRBNK-MLNS SS :3/7 RPR STRW | VICTOR | ETL.1070.POLE.WOOD | 2024-04-25 | 2024-04-25 | 2025-03-15 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46327505 | T2 EI BLLT-RVRRBNK-MLNS SS :3/7 RPR STRW | ICW
LC | 128653630 | 008/053 | T2 EI STNLS-MLNS SW ST-MNT 08/53 RMV VEG | VICTOR | ETL.3830.TOWR | 2024-04-25 | 2024-04-25 | 2024-04-25 | Past Due |  | 2025-04-25 | 2025-04-25 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128653677 | 009/061 | T2 CTTNWD-DELEVAN #1 9/61 COMPLETE | TABLEMTN | ETL.4550.TOWR | 2024-04-25 | 2024-04-25 | 2025-04-09 | On-Time |  | 2025-04-25 | 2025-04-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310428 | T2 EI CTTNWD-DELEVAN #1 9/61 RPR STRT | ICQ
LC | 128653968 | 013/125 | T2 ARCO-CHOLAME 13/125 RPR INSW | MIDWAY | ETL.8440.INSL.NCER | 2024-04-25 | 2024-04-25 | 2025-01-08 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46302519 | T2 ARCO-CHOLAME 13/125 RPR INSW | ICW
LC | 128654046 | 050/218 | T2 EI RND MTN-TBL MT #2 50/218 RPL INSS | TABLEMTN | ETL.6070.INSL | 2024-04-25 | 2024-04-25 | 2025-02-21 | On-Time |  | 2025-04-25 | 2025-04-25 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35611184 | T2 EI RND MTN-TBL MT #2 50/218 RPL INSS | 93K
LC | 128654171 | 006/005 | T2 EI VLY SPRNGS-MARTEL #1 6/5 RMV VEG | VICTOR | ETL.8240.POLE.NWOD | 2024-04-25 | 2024-04-25 | 2024-09-21 | On-Time |  | 2025-04-25 | 2025-04-25 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128654246 | 018/257A | T2 WV CLAY-MARTEL 018/257A INS RPTS | VICTOR | ETL.8250.POLE.WOOD | 2024-04-25 | 2024-04-25 | 2025-04-12 | On-Time |  | 2025-04-25 | 2025-04-25 | 672 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Raptor Guard-Wood | Install | 31609432 | T2 EI CLAY-MARTEL+ 17/255 RPL STRW | 70Y
LC | 128654605 | 026/433 | T2 WV KESWICK-TRINITY 26/433 REFRAME | TABLEMTN | ETL.7270.POLE.WOOD | 2024-04-25 | 2024-04-25 | 2025-04-03 | On-Time |  | 2025-04-25 | 2025-04-25 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35573710 | T2 WV KESWICK-TRINITY 26/433 REFRAME | 93E
LC | 128654610 | 050/218 | T2 EI RND MTN-TBL MTN #1 50/218 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-04-25 | 2024-04-25 | 2025-01-25 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306282 | T2 EI RND MTN-TBL MTN #1 50/218 RMV NEST | ICS
LC | 128654632 | 000/004 | T2 EI MENDOCINO-UKIAH 000/004 RPL ANCW | WILLITS | ETL.2420.POLE.NWOD | 2024-04-25 | 2024-04-25 | 2025-03-26 | On-Time |  | 2025-04-25 | 2025-04-25 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574326 | T2 EI MENDOCINO-UKIAH 000/004 RPL ANCW | 93E
LC | 128654979 | 002/018 | T2 EI DIVIDE-VANDENBERG #1 2/18 RMV NEST | PISMOBCH | ETL.8620.POLE.WOOD | 2024-04-25 | 2024-04-25 | 2025-01-13 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Wood | Remove | 46329645 | T2 EI DIVIDE-VANDENBERG #1 2/18 RMV NEST | ICW
LC | 128654991 | 000/006 | T2 EI MENDOCINO-UKIAH 0/6 RPL POLE | WILLITS | ETL.2420.POLE.WOOD | 2024-04-25 | 2024-04-25 | 2025-03-25 | On-Time |  | 2025-04-25 | 2025-04-25 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574329 | T2 EI MENDOCINO-UKIAH 0/6 RPL POLE | 70Y
LC | 128655080 | 002/017 | T2 EI KRCKHF-CLVS-SNGR #1 02/17 RMV ENCR | FRESNO | ETL.1890.TOWR | 2024-04-25 | 2024-04-25 | 2024-08-20 | On-Time |  | 2024-10-25 | 2025-04-25 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46249750 | T2 EI KRCKHF-CLVS-SNGR #1 02/17 RMV ENCR | CHR
LC | 128655258 | 002/013 | T2 EI DIVIDE-VANDENBERG #2 2/13 X-BRACE | PISMOBCH | ETL.8630.POLE.WDPS | 2024-04-25 | 2024-04-25 | 2024-08-01 | On-Time |  | 2024-07-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Crossbrace - Wood | Repair | 46283184 | T2 EI DIVIDE-VANDENBERG #2 2/13 X-BRACE | ICW
LC | 128656327 | 002/015 | T2 EI DIVIDE-VANDENBERG #1 2/15 RMV NEST | PISMOBCH | ETL.8620.POLE.WOOD | 2024-04-25 | 2024-04-25 | 2024-12-05 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Wood | Remove | 46329646 | T2 EI DIVIDE-VANDENBERG #1 2/15 RMV NEST | ICW
LC | 128656629 | 073/371-GUY | T2 EI MLIN-RUND MTN #2 073/371B COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-04-25 | 2024-04-25 | 2024-07-31 | On-Time |  | 2025-04-25 | 2025-04-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46256496 | T2 EI MLIN-RUND MTN #2 073/371B RPR GYWT | ICQ
LC | 128656792 | 010/007 | T2 EI EXCHEQUER-MARIPOSA 10/7 RPR GYWW | FRESNO | ETL.8640.POLE.NWOD | 2024-04-25 | 2024-04-25 | 2025-04-14 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SPCR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298178 | T2 EI EXCHEQUER-MARIPOSA 10/7 RPR GYWW | ICW
LC | 128656878 | 008/159 | T2 CARIBOU-WESTWOOD 08/159 GO95 | TABLEMTN | ETL.6300.POLE.WOOD | 2024-04-25 | 2024-04-25 | 2025-03-11 | On-Time |  | 2025-04-25 | 2025-04-25 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35555479 | T2 CARIBOU-WESTWOOD 08/159 GO95 | 93G
LC | 128657014 | 004/112 | T2 DEL MONTE-VIEJO 04/112 GO95 | MOSSLNDG | ETL.6710.POLE.WOOD | 2024-04-25 | 2024-04-25 | 2025-04-24 | On-Time |  | 2025-04-25 | 2025-04-25 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35555545 | T2 DEL MONTE-VIEJO 04/112 GO95 | 93G
LC | 128657131 | 004/083 | T2 DEL MONTE-VIEJO 4/083 GO95 | MOSSLNDG | ETL.6710.POLE.WOOD | 2024-04-25 | 2024-04-25 | 2025-04-23 | On-Time |  | 2025-04-25 | 2025-04-25 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35555546 | T2 DEL MONTE-VIEJO 4/083 GO95 | 93G
LC | 128657267 | 034/164 | T2 EI RND MTN-TBL MTN #1 34/164 RPR CNDS | TABLEMTN | ETL.6060.INSL | 2024-04-25 | 2024-04-25 | 2025-02-10 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Conductor-Steel | Repair | 46306283 | T2 EI RND MTN-TBL MTN #1 34/164 RPR CNDS | ICS
LC | 128657429 | 009/082A | T2 EI CBRLL-SNT YNZ SW ST 9/82A RPL INSW | PISMOBCH | ETL.1200.INSL.NCER | 2024-04-25 | 2024-04-25 | 2025-02-25 | On-Time |  | 2025-04-25 | 2025-04-25 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35555581 | T2 EI CBRLLO-SNT YNZ SW ST 9/75 RPL INSW | 93I
LC | 128657459 | 009/075 | T2 EI CBRLLO-SNT YNZ SW ST 9/75 RPL INSW | PISMOBCH | ETL.1200.INSL.NCER | 2024-04-25 | 2024-04-25 | 2025-02-25 | On-Time |  | 2025-04-25 | 2025-04-25 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35555581 | T2 EI CBRLLO-SNT YNZ SW ST 9/75 RPL INSW | 93I
LC | 128657628 | :000/013 | T2 CARIBOU #2 :000/013 RPL INSW | TABLEMTN | ETL.6280.INSL.CERA | 2024-04-25 | 2024-04-25 | 2025-03-14 | On-Time |  | 2025-04-25 | 2025-04-25 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Replace | 35556121 | T2 CARIBOU #2 :000/013 RPL INSW | 93I
LC | 128657709 | 012/007 | T2 EI DUNLAP TAP 012/007 RPL STRW | FRESNO | ETL.9061.POLE.WOOD | 2024-04-25 | 2024-04-25 | 2025-03-21 | On-Time |  | 2025-04-25 | 2025-04-25 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573192 | T2 EI DUNLAP TAP 012/007 RPL STRW | 70Y
LC | 128657731 | 056/416 | T2 EI BRDGVLE-CTNWD 56/4 COTTER | TABLEMTN | ETL.1110.INSL.CERA | 2024-04-25 | 2024-04-25 | 2025-03-24 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46311124 | T2 EI BRDGVLE-CTNWD 56/4 COTTER | ICS
LC | 128657747 | 037/008 | T2 EI TRINITY-MPLE CREEK 37/8 RPR INSW | EUREKA | ETL.8170.INSL.NCER | 2024-04-25 | 2024-04-25 | 2024-10-15 | On-Time |  | 2024-10-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46246254 | T2 EI TRINITY-MPLE CREEK 37/8 RPR INSW | ICW
LC | 128657767 | 003/001 | T2 EI SALMON CREEK TAP_003/001L RMV VEG | LAKEVLLE | ETL.6981.POLE.WDPS | 2024-04-25 | 2024-04-25 | 2025-04-22 | On-Time |  | 2025-04-25 | 2025-04-25 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAR | Overgrown | Vegetation | Remove
LC | 128657830 | 003/002 | T2 EI SALMON CREEK TAP 3/002 RPL INSW | LAKEVLLE | ETL.6981.INSL | 2024-04-25 | 2024-04-25 | 2025-04-14 | On-Time |  | 2025-04-25 | 2025-04-25 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572894 | T2 EI SALMON CREEK TAP 3/002 RPL INSW | 93I
LC | 128657872 | 023/620 | T2 EI CARIBOU #2 23/620 RPR GYWW | TABLEMTN | ETL.6280.POLE.NWOD | 2024-04-25 | 2024-04-25 | 2024-09-16 | On-Time |  | 2024-10-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD REMT NOAC REAR ACCL COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46250282 | T2 EI CARIBOU #2 23/620 RPR GYWW | ICW
LC | 128657875 | 008/095 | T2 VEDDER TAP 8/95 RPL POLE | MIDWAY | ETL.2141.POLE.WOOD | 2024-04-25 | 2024-04-25 | 2025-04-10 | On-Time |  | 2025-04-25 | 2025-04-25 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW TNT SUBS SPCR USA COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35597335 | T2 VEDDER TAP 8/95 RPL POLE | 70Y
LC | 128657878 | 038/001 | T2 EI TRINITY-MPLE CREEK 38/1 RPL HRDD | EUREKA | ETL.8170.POLE.WOOD | 2024-04-25 | 2024-04-25 | 2025-04-28 | Past Due |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345775 | T2 EI TRINITY-MPLE CREEK 38/1 RPL HRDD | ICW
LC | 128658000 | 005/002 | T2 EI DUNLAP TAP 005/002 COMPLETED | FRESNO | ETL.9061.INSL.NCER | 2024-04-25 | 2024-04-25 | 2025-03-21 | On-Time |  | 2025-04-25 | 2025-04-25 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573190 | T2 EI DUNLAP TAP 005/002 RPL INSW | 93I
LC | 128658070 | 014/135 | T2 EI UKH-HPLND-CLVRDLE 14/135 RPL STRW | WILLITS | ETL.4050.POLE.WOOD | 2024-04-25 | 2024-04-25 | 2025-06-18 | Past Due |  | 2025-04-25 | 2025-04-25 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35571882 | T2 EI UKH-HPLND-CLVRDLE 14/135 RPL POLE | 70Y
LC | 128659576 | 003/016 | T2 EI BRCEBRG JCT-MRPSA TP 3/16 COMPLETE | FRESNO | ETL.8651.INSL.NCER | 2024-04-26 | 2024-04-25 | 2025-03-29 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298180 | T2 EI BRCEBRG JCT-MRPSA TP 3/16 RPR INSW | ICW
LC | 128659637 | 003/012 | T2 EI BRCEBRG JCT-MRPSA TP 3/12 RPR INSW | FRESNO | ETL.8651.INSL.CERA | 2024-04-26 | 2024-04-25 | 2025-03-28 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298181 | T2 EI BRCEBRG JCT-MRPSA TP 3/12 RPR INSW | ICW
LC | 128661771 | A004/097 | T2 DI CSCD BENTN DSCHTS A4/97 INSP ANCW | TABLEMTN | ETL.6310.POLE.WOOD | 2024-04-26 | 2024-04-25 | 2024-06-06 | On-Time |  | 2024-10-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46250716 | T2 DI CSCD BENTN DSCHTS A4/97 INSP ANCW | ICW
LC | 128662202 | 048/343 | T2 DI CRBOU TBL MTN 48/343 RPR JUMS | TABLEMTN | ETL.4440.INSL.NCER | 2024-04-26 | 2024-04-25 | 2024-06-08 | On-Time |  | 2024-10-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46240002 | T2 DI CRBOU TBL MTN 48/343 RPR JUMS | ICS
LC | 128662342 | 108/002 | T2 DI HUMBOLDT-BRIDGE 108/2L RPR GYWW | EUREKA | ETL.1810.POLE.WDPS | 2024-04-26 | 2024-04-25 | 2025-04-18 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345779 | T2 DI HUMBOLDT-BRIDGE 108/2L RPR GYWW | ICW
LC | 128662346 | A008/182 | T2 DI CSCDE-BNTN-DS A8/182 RPR JUMW | TABLEMTN | ETL.6310.INSL.NCER | 2024-04-26 | 2024-04-25 | 2024-11-18 | On-Time |  | 2024-07-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46250715 | T2 DI CASCADE-BENTON-DES A8/182 RPR JUMW | ICW
LC | 128662348 | A008/182 | T2 DI CASCADE-BENTON A8/182 RPR WDPKR | TABLEMTN | ETL.6310.POLE.WOOD | 2024-04-26 | 2024-04-25 | 2024-05-16 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46256649 | T2 DI CASCADE-BENTON A8/182 RPR WDPKR | ICW
LC | 128662349 | 108/002 | T2 DI HUMBOLDT-BRIDGE 108/2L RPR ADSS | EUREKA | ETL.1810.POLE.WDPS | 2024-04-26 | 2024-04-25 | 2025-04-18 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | ADSS - Wood | Repair | 46345780 | T2 DI HUMBOLDT-BRIDGE 108/2L RPR ADSS | ICW
LC | 128679283 | 016/115 | T2 DI HELMS-GREGG #1 16/115 RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-04-29 | 2024-04-25 | 2025-03-27 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298162 | T2 DI HELMS-GREGG #1 16/115 RPR SHLS | ICS
LC | 128679762 | 002/033 | T3 DI DESABLA-CNTRVILLE 2/33L RPL HRDD | TABLEMTN | ETL.6720.POLE.STPS | 2024-04-29 | 2024-04-25 | 2024-11-15 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace | 46247573 | T3 DI DESABLA-CNTRVILLE 2/33L RPL HRDD | ICW
LC | 128679764 | 056/004B | T2 DI HUMBOLDT-TRINITY 56/4B RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-04-29 | 2024-04-25 | 2025-02-17 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345777 | T2 DI HUMBOLDT-TRINITY 56/4B RPR GYWW | ICW
LC | 128679771 | 024/159 | T2 DI HELMS-GREGG #2 24/159 COTTER | FRESNO | ETL.4880.INSL.CERA | 2024-04-29 | 2024-04-25 | 2025-04-10 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46298163 | T2 DI HELMS-GREGG #2 24/159 COTTER | ICS
LC | 128679772 | 024/159 | T2 DI HELMS-GREGG #1 24/159 COTTER | FRESNO | ETL.4870.INSL.CERA | 2024-04-29 | 2024-04-25 | 2025-03-24 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46298164 | T2 DI HELMS-GREGG #1 24/159 COTTER | ICS
LC | 128679810 | 023/153 | T2 DI HELMS GREGG #1 23/153 RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-04-29 | 2024-04-25 | 2025-03-24 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298165 | T2 DI HELMS GREGG #1 23/153 RPR SHLS | ICS
LC | 128679849 | 002/032 | T3 DI DESABLA-CTRV 2/32 RPR CNDW | TABLEMTN | ETL.6720.INSL | 2024-04-29 | 2024-04-25 | 2024-11-15 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46247572 | T3 DI DESABLA-CTRV 2/32 RPR CNDW | ICW
LC | 128680935 | 024/001 | T2 DI MI-WUK-CURTIS 24/1L RPL POLE | VICTOR | ETL.1073.POLE.WDPS | 2024-04-30 | 2024-04-25 | 2024-10-10 | On-Time |  | 2025-04-25 | 2025-04-25 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35551320 | T2 DI MI-WUK-CURTIS 24/1 RPL POLE | 70Y
LC | 128698448 | 041/004 | T2 DI MNDCNO-WLTS-FRT BRG 41/4 RPR JUMW | WILLITS | ETL.7550.INSL.NCER | 2024-05-01 | 2024-04-25 | 2025-01-15 | On-Time |  | 2024-07-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46252593 | T2 DI MNDCNO-WLTS-FRT BRG 41/4 RPR JUMW | ICW
LC | 128698678 | 055/003 | T2 DI HMBDLT TRNTY 55/003L RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-01 | 2024-04-25 | 2024-11-09 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345776 | T2 DI HMBDLT TRNTY 55/003L RPR GYWW | ICW
LC | 128698749 | 000/005 | T2 DI KRCKHF#1-KRCKHF#2 0/5 RPR FOND | FRESNO | ETL.1880.TOWR | 2024-05-01 | 2024-04-25 | 2025-01-14 | On-Time |  | 2025-04-25 | 2025-04-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46297872 | T2 DI KRCKHF#1-KRCKHF#2 0/5 RPR FOND | ICQ
LC | 128698775 | 073/371 | T2 DI MALIN-RM#2 73/371 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-05-01 | 2024-04-25 | 2025-02-09 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46338192 | T2 DI MALIN-RM#2 73/371 RPR OPGW | ICS
LC | 128698829 | 047/414 | T2 DI RND MTN CTNWD#3 47/414 RMV VEG | TABLEMTN | ETL.5650.TOWR | 2024-05-01 | 2024-04-25 | 2024-11-20 | On-Time |  | 2025-04-25 | 2025-04-25 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128745141 | 048/421 | T2 DI RND MTN-CTTNWD #3 48/421 RPL HRDT | TABLEMTN | ETL.5650.TOWR | 2024-05-10 | 2024-04-25 | 2025-01-08 | On-Time |  | 2025-04-25 | 2025-04-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46310408 | T2 DI RND MTN-CTTNWD #3 48/421 RPL HRDT | ICQ
LC | 128746160 | 047/412 | T2NT DI RND MTN-CTTNWD#3 47/412 RPR STRT | TABLEMTN | ETL.5650.TOWR | 2024-05-10 | 2024-04-25 | 2025-04-10 | On-Time |  | 2027-04-25 | 2025-04-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310407 | T2NT DI RND MTN-CTTNWD#3 47/412 RPR STRT | ICQ
LC | 128746554 | 032/010 | T2 DI FULTON HPLAND 32/10 TOUCH | LAKEVLLE | ETL.6890.POLE.NWOD | 2024-05-10 | 2024-04-25 | 2025-06-23 | Past Due |  | 2024-10-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46505448 | T2 DI FULTON HPLAND 32/10 TOUCH | ICW
LC | 128746583 | 022/150 | T2 DI HELMS GREG #1 22/150 RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-10 | 2024-04-25 | 2025-03-25 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298169 | T2 DI HELMS GREG #1 22/150 RPR SHLS | ICS
LC | 128746744 | 023/152 | T2 DI HELM GREGG#1 23/152 RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-10 | 2024-04-25 | 2025-03-25 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298170 | T2 DI HELM GREGG#1 23/152 RPR SHLS | ICS
LC | 128766439 | 024/214 | T2 BRIDGEVILLE-CTTNWD 24/214 RPR ADSS | TABLEMTN | ETL.1110.POLE.STPS | 2024-05-13 | 2024-04-25 | 2025-05-08 | Past Due |  | 2024-07-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46253089 | T2 DI BRIDGEVILL-CTTNWD 24/214 RPR ADSS | ICW
LC | 128768361 | 024/157 | T2 DI HELMS-GREGG #1 24/157 RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-13 | 2024-04-25 | 2025-03-24 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298172 | T2 DI HELMS-GREGG #1 24/157 RPR SHLS | ICS
LC | 128768365 | 024/157 | T2 DI HELMS-GREGG #1 24/157 COTTER | FRESNO | ETL.4870.INSL.CERA | 2024-05-13 | 2024-04-25 | 2025-03-24 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46298173 | T2 DI HELMS-GREGG #1 24/157 COTTER | ICS
LC | 128768611 | 023/155 | T2 DI HELMS-GREGG #1 23/155 RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-13 | 2024-04-25 | 2025-03-24 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298176 | T2 DI HELMS-GREGG #1 23/155 RPR SHLS | ICS
LC | 128768793 | 047/414 | T2 DI PIT #1-CTONWOD 47/414 RMV ENCRCH | TABLEMTN | ETL.5390.TOWR | 2024-05-13 | 2024-04-25 | 2024-04-25 | Past Due |  | 2024-10-25 | 2025-04-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478220 | T2 DI PIT #1-CTONWOD 47/414 RMV ENCRCH | ICQ
LC | 128768859 | 014/123 | T2 DI COTTONWD-BN#2 14/123 RPL INSW | TABLEMTN | ETL.6650.INSL.NCER | 2024-05-13 | 2024-04-25 | 2025-04-04 | On-Time |  | 2025-04-25 | 2025-04-25 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35557461 | T2 DI COTTONWD-BN#2 14/123 RPL INSW | 93I
LC | 128768862 | 014/123 | T2 DI COTTONWD-BN#2 14/123L RMV VEG | TABLEMTN | ETL.6650.POLE.WDPS | 2024-05-13 | 2024-04-25 | 2024-04-25 | Past Due |  | 2025-04-25 | 2025-04-25 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128768865 | 014/123 | T2 DI COTTONWD-BN#2 14/123L RPR ANCW | TABLEMTN | ETL.6650.POLE.WDPS | 2024-05-13 | 2024-04-25 | 2025-04-04 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46477226 | T2 DI COTTONWD-BN#2 14/123L RPR ANCW | ICW
LC | 128768866 | 014/123 | T2 DI COTTONWD-BN#2 14/123L RPR ANCW | TABLEMTN | ETL.6650.POLE.WDPS | 2024-05-13 | 2024-04-25 | 2025-04-04 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46383860 | T2 DI COTTONWD-BN#2 14/123L RPR ANCW | ICW
LC | 128769020 | 003/039B | T3 DI DESABLA-CNTV 3/39 RPR SPLW | TABLEMTN | ETL.6720.INSL.NCER | 2024-05-13 | 2024-04-25 | 2024-11-15 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR3 PRTO AIR NTDE BRIN | No Good/Out of Stdrd | Splice-Wood | Repair | 46252235 | T3 DI DESABLA-CNTV 3/39 RPL SPLW | ICW
LC | 128769024 | 003/039 | T3 DI DESABLA-CNTRVLL 3/39C RPR GYWW | TABLEMTN | ETL.6720.POLE.STPS | 2024-05-13 | 2024-04-25 | 2024-11-14 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH XMPT TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46250403 | T3 DI DESABLA-CNTV 3/39C RPR GYWW | ICW
LC | 128774188 | 073/369 | T2 DI MALIN-ROUND MNTN#2 73/369 RMV VEG | TABLEMTN | ETL.6020.TOWR | 2024-05-14 | 2024-04-25 | 2024-10-29 | On-Time |  | 2025-04-25 | 2025-04-25 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128774201 | 016/117 | T2 DI HELMS GREG #1 16/117 RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-14 | 2024-04-25 | 2025-03-27 | On-Time |  | 2025-04-25 | 2025-04-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298177 | T2 DI HELMS GREG #1 16/117 RPR SHLS | ICS
LC | 128779905 | 002/031B | T3 DI DESABLA-CNTRVLLE 2/31B RPR INSW | TABLEMTN | ETL.6720.INSL.NCER | 2024-05-15 | 2024-04-25 | 2024-11-15 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46250296 | T3 DI DESABLA-CNTRVLLE 2/31B RPR INSW | ICW
LC | 128779910 | 016/118 | T2 HELMS-GREGG#1 16/118 RPR CRST | FRESNO | ETL.4870.TOWR | 2024-05-15 | 2024-04-25 | 2024-04-25 | Past Due |  | 2025-04-25 | 2025-04-25 | 93ZT | TR2 |  | E - Schd Compl Yr 0 | Open | RELW ACCL OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Tower | Repair | 31710593 | T2 DI HELMS-GREGG#1 16/118 RPL CRSSARMS | 93Z
LC | 128779941 | 002/031 | T3 DI DESABLA-CENTERVILLE 2/31L RPR GYWW | TABLEMTN | ETL.6720.POLE.STPS | 2024-05-15 | 2024-04-25 | 2024-11-15 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46250295 | T3 DI DESABLA-CENTERVILLE 2/31L RPR GYWW | ICW
LC | 128779998 | 004/104 | T2 DI CSCD-BNTN-DSCHTS 4/104 RPR STRW | TABLEMTN | ETL.6310.POLE.WOOD | 2024-05-15 | 2024-04-25 | 2025-04-10 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46383862 | T2 DI CSCD-BNTN-DSCHTS 4/104 RPR STRW | ICW
LC | 128779999 | 004/104 | T2 DI CSCD-BNTN-DSCHTS 4/104 RPR INSW | TABLEMTN | ETL.6310.INSL.NCER | 2024-05-15 | 2024-04-25 | 2025-04-10 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46383863 | T2 DI CSCD-BNTN-DSCHTS 4/104 RPR INSW | ICW
LC | 128780143 | 056/005 | T2 DI HUMBOLDT-TRINITY 56/5 RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-05-15 | 2024-04-25 | 2025-04-09 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46345778 | T2 DI HUMBOLDT-TRINITY 56/5 RPR JUMW | ICW
LC | 128780168 | 046/002 | T2 DI HUMBOLDT-TRINITY 46/2L RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-15 | 2024-04-25 | 2025-04-07 | On-Time |  | 2025-04-25 | 2025-04-25 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574657 | T2 DI HUMBOLDT-TRINITY 46/2R RPL STRW | 70Y
LC | 128792531 | 002/031 | T3 DI DESABLA-CENTERVILLE 2/31R RPR GYWW | TABLEMTN | ETL.6720.POLE.STPS | 2024-05-17 | 2024-04-25 | 2024-11-15 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46250292 | T3 DI DESABLA-CENTERVILLE 2/31R RPR GYWW | ICW
LC | 128792532 | 002/031 | T3 DI DESABLA-CENTERVILLE 2/31C RPR GYWW | TABLEMTN | ETL.6720.POLE.STPS | 2024-05-17 | 2024-04-25 | 2024-11-15 | On-Time |  | 2025-04-25 | 2025-04-25 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46250293 | T3 DI DESABLA-CENTERVILLE 2/31C RPR GYWW | ICW
LC | 128852413 | 046/002 | T2 DI HUMBOLDT-TRINITY 46/2R RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-23 | 2024-04-25 | 2025-04-07 | On-Time |  | 2025-04-25 | 2025-04-25 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574657 | T2 DI HUMBOLDT-TRINITY 46/2R RPL STRW | 70Y
LC | 129036045 | 108/004 | T2 HUMBOLDT-BRDGVLL 108/4L RPL ANCW | EUREKA | ETL.1810.POLE.STPS | 2024-06-07 | 2024-04-25 | 2024-04-25 | Past Due |  | 2025-04-25 | 2025-04-25 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Anchor-Wood | Replace | 35619958 | T2 DI HUMBOLDT-BRDGVLL 108/4L RPL ANCW | 93E
LC | 123430729 | 079/402 | T2NT EI MALN-RND MTN#2 79/402 BENT STEEL | TABLEMTN | ETL.6020.TOWR | 2022-04-26 | 2022-04-26 | 2023-08-23 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45616942 | T2 EI MALIN-RND MTN #2 79/402 BENT STEEL | ICQ
LC | 123431702 | 011/071 | T2NT EI OLEUM-G #2 11/71 RPL INSS | CONCORD | ETL.3160.INSL | 2022-04-26 | 2022-04-26 | 2023-08-24 | On-Time |  | 2025-04-26 | 2025-04-26 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO NTDE | No Good/Out of Stdrd | Insulator-Steel | Replace | 31625563 | EI OLEUM-G #2 RPL INSS IN 3 TWRS. | 93K
LC | 123433223 | 021/093 | T2NT DI MORRO BAY-MESA 21/93 RPL INSS | PISMOBCH | ETL.5290.INSL | 2022-04-26 | 2022-04-26 | 2023-08-24 | On-Time |  | 2025-04-26 | 2025-04-26 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 31602543 | T2 EI MORRO BAY-MESA RPL INSS 4TWR | 93K
LC | 123433251 | 021/093 | T2NT DI DIABLO-MESA 21/93 RPL INSS | PISMOBCH | ETL.4620.INSL | 2022-04-26 | 2022-04-26 | 2023-09-29 | On-Time |  | 2025-04-26 | 2025-04-26 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 31601767 | T2 EI DIABLO-MESA RPL INSS 8TWR | 93K
LC | 123439653 | 029/126 | T2NT DI MRO BY SS ST #1 29/126 RPL HRDT | PISMOBCH | ETL.5300.TOWR | 2022-04-27 | 2022-04-26 | 2023-07-18 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 45648879 | T2 DI MRO BY SS ST #1 29/126 RPL HRDT | ICQ
LC | 123440074 | 030/129 | T2NT DI MR BY-SLR SS #1 30/129 RPR FOND | PISMOBCH | ETL.5300.TOWR | 2022-04-27 | 2022-04-26 | 2023-07-18 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45649025 | T2 DI MRRO BY-SLR SS #1 30/129 RPR FOND | ICQ
LC | 123440426 | 033/148 | T2NT DI MORRO BAY-MESA 033/148 BNT STEEL | PISMOBCH | ETL.5290.TOWR | 2022-04-27 | 2022-04-26 | 2023-07-12 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45649033 | T2 DI MORRO BAY-MESA 033/148 BNT STEEL | ICQ
LC | 128660156 | 012/058 | T2 EI LS ESTERS-METCALF 12/58 RPR STRT | METCALF | ETL.5353.TOWR | 2024-04-26 | 2024-04-26 | 2025-01-18 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46298826 | T2 EI LS ESTERS-METCALF 12/58 RPR STRT | ICQ
LC | 128661430 | 032/155 | T2 EI RND MTN-TBL MTN #2 32/155 RPL INSS | TABLEMTN | ETL.6070.INSL | 2024-04-26 | 2024-04-26 | 2025-02-21 | On-Time |  | 2025-04-26 | 2025-04-26 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574244 | T2 EI RND MTN-TBL MTN #2 RPL INSS 6 TWRS | 93K
LC | 128661738 | 007/112 | T2 EI DELTA-MTN GATE JCT 7/112 RPR INSW | TABLEMTN | ETL.6750.INSL.NCER | 2024-04-26 | 2024-04-26 | 2024-07-16 | On-Time |  | 2025-04-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46250266 | T2 EI DELTA-MTN GATE JCT 7/112 RPR INSW | ICW
LC | 128661944 | 014/001 | T2 HUMBOLDT-MAPLE CREEK 14/1 TOUCH | EUREKA | ETL.7130.POLE.NWOD | 2024-04-26 | 2024-04-26 | 2025-06-03 | Past Due |  | 2024-10-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46505016 | T2 HUMBOLDT-MAPLE CREEK 14/1 TOUCH | ICW
LC | 128662035 | 042/274C | T2 DI TRNTY CTNWD 42/274C RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-04-26 | 2024-04-26 | 2024-08-19 | On-Time |  | 2025-04-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46239917 | T2 DI TRNTY CTNWD 42/274C RPR JUMW | ICW
LC | 128662039 | 042/274 | T2 DI TRINITY-COTTON 42/274B RPR JUMP | TABLEMTN | ETL.4040.INSL.NCER | 2024-04-26 | 2024-04-26 | 2024-08-19 | On-Time |  | 2024-07-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46239918 | T2 DI TRINITY-COTTON 42/274 RPR JUMP | ICW
LC | 128662047 | 012/097 | T2 EI TGR CRK-VLEY SPRNGS 12/97 RPR FOND | VICTOR | ETL.5790.TOWR | 2024-04-26 | 2024-04-26 | 2025-04-04 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416539 | T2 EI TGR CRK-VLEY SPRNGS 12/97 RPR FOND | ICQ
LC | 128662226 | 012/096 | T2 EI TGER CREK-VLY SPRNGS 12/096 MASTIC | VICTOR | ETL.5790.TOWR | 2024-04-26 | 2024-04-26 | 2025-04-04 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416580 | T2 EI TGER CREK-VLY SPRNGS 12/096 MASTIC | ICQ
LC | 128662247 | 035/143 | T2 DI DIABLO-MDWY #2 035/143 RPR INSS | PISMOBCH | ETL.5970.INSL.NCER | 2024-04-26 | 2024-04-26 | 2025-04-11 | On-Time |  | 2025-04-26 | 2025-04-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329578 | T2 DI DIABLO-MDWY #2 035/143 RPR INSS | ICS
LC | 128662868 | 012/098 | T2 EI TGR CRK-VLEY SPRNGS 12/98 RPR FOND | VICTOR | ETL.5790.TOWR | 2024-04-26 | 2024-04-26 | 2025-04-04 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416581 | T2 EI TGR CRK-VLEY SPRNGS 12/98 RPR FOND | ICQ
LC | 128663333 | 006/038 | T2 STANISLAUS-MANTECA 06/038 COTTER | VICTOR | ETL.3820.INSL.NCER | 2024-04-26 | 2024-04-26 | 2025-02-21 | On-Time |  | 2025-04-26 | 2025-04-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46325920 | T2 STANISLAUS-MANTECA 06/038 COTTER | ICS
LC | 128663361 | 006/045 | T2 WV WISHON-COPPERMINE 6/45 RPR STRT | FRESNO | ETL.9330.TOWR | 2024-04-26 | 2024-04-26 | 2024-04-26 | Past Due |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46297877 | T2 WV WISHON-COPPERMINE 6/45 RPR STRT | ICQ
LC | 128663451 | 008/117 | T2 DELTA-MTN GATE JCT 8/117R RPL POLE | TABLEMTN | ETL.6750.POLE.WDPS | 2024-04-26 | 2024-04-26 | 2024-04-26 | Past Due |  | 2025-04-26 | 2025-04-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35557674 | T2 EI DELTA-MTN GATE JCT 8/117R RPL POLE | 70Y
LC | 128663551 | 022/335 | T2 KESWICK-TRINITY 22/335 GO95 | TABLEMTN | ETL.7270.POLE.WOOD | 2024-04-26 | 2024-04-26 | 2025-04-14 | On-Time |  | 2025-04-26 | 2025-04-26 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35555620 | T2 KESWICK-TRINITY 22/335 GO95 | 93G
LC | 128663590 | 012/002 | T2 EI DUNLAP TAP 012/002 RPL DMPW | FRESNO | ETL.9061.INSL.NCER | 2024-04-26 | 2024-04-26 | 2025-03-21 | On-Time |  | 2025-04-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46298119 | T2 EI DUNLAP TAP 012/002 RPL DMPW | ICW
LC | 128663837 | 018/109 | T2 WV SAN LUIS OBSPO-OCN 18/109 RPR GYWW | PISMOBCH | ETL.3530.POLE.WOOD | 2024-04-26 | 2024-04-26 | 2025-03-12 | On-Time |  | 2025-04-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Replace | 46329628 | T2 WV SAN LUIS OBSPO-OCN 18/109 RPR GYWW | ICW
LC | 128663847 | 024/380 | T2 KESWICK-TRINITY 24/380 GO95 | TABLEMTN | ETL.7270.POLE.WOOD | 2024-04-26 | 2024-04-26 | 2025-04-17 | On-Time |  | 2025-04-26 | 2025-04-26 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35555621 | T2 KESWICK-TRINITY 24/380 GO95 | 93G
LC | 128664023 | 024/391 | T2 KESWICK-TRINITY 24/391 GO95 | TABLEMTN | ETL.7270.POLE.WOOD | 2024-04-26 | 2024-04-26 | 2025-04-03 | On-Time |  | 2025-04-26 | 2025-04-26 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35555621 | T2 KESWICK-TRINITY 24/380 GO95 | 93G
LC | 128664026 | 005/022 | T2 EI MNT VISTA-JFFRSN#1 5/22 RPR STRT | METCALF | ETL.5220.TOWR | 2024-04-26 | 2024-04-26 | 2025-01-21 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46298828 | T2 EI MNT VISTA-JFFRSN#1 5/22 RPR STRT | ICQ
LC | 128664127 | 009/006 | T2 EI EXCHEQUER-MARIPOSA 9/6 RMV ENCRCH | FRESNO | ETL.8640.POLE.NWOD | 2024-04-26 | 2024-04-26 | 2024-08-27 | On-Time |  | 2024-10-26 | 2025-04-26 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46249751 | T2 EI EXCHEQUER-MARIPOSA 9/6 RMV ENCRCH | CHR
LC | 128664128 | 009/008 | T2 EI EXCHEQUER-MARIPOSA 9/8 RMV ENCRCH | FRESNO | ETL.8640.POLE.NWOD | 2024-04-26 | 2024-04-26 | 2024-08-28 | On-Time |  | 2024-10-26 | 2025-04-26 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46249752 | T2 EI EXCHEQUER-MARIPOSA 9/8 RMV ENCRCH | CHR
LC | 128664132 | 009/005 | T2 EI EXCHEQUER-MARIPOSA 9/5 RMV ENCRCH | FRESNO | ETL.8640.POLE.NWOD | 2024-04-26 | 2024-04-26 | 2024-08-27 | On-Time |  | 2024-10-26 | 2025-04-26 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46249753 | T2 EI EXCHEQUER-MARIPOSA 9/5 RMV ENCRCH | CHR
LC | 128664133 | 009/007 | T2 EI EXCHEQUER-MARIPOSA 9/7 RMV ENCRCH | FRESNO | ETL.8640.POLE.NWOD | 2024-04-26 | 2024-04-26 | 2024-08-28 | On-Time |  | 2024-10-26 | 2025-04-26 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46249754 | T2 EI EXCHEQUER-MARIPOSA 9/7 RMV ENCRCH | CHR
LC | 128664134 | 009/009 | T2 EI EXCHEQUER-MRPSA 9/9 RMV ENCR | FRESNO | ETL.8640.POLE.NWOD | 2024-04-26 | 2024-04-26 | 2024-08-28 | On-Time |  | 2024-10-26 | 2025-04-26 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46300831 | T2 EI EXCHEQUER-MRPSA 9/9 RMV ENCR | CHR
LC | 128664185 | 008/116 | T2 EI DELTA-MTN GATE JCT 8/116L RPR ANCW | TABLEMTN | ETL.6750.POLE.WDPS | 2024-04-26 | 2024-04-26 | 2025-04-09 | On-Time |  | 2025-04-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46453111 | T2 EI DELTA-MTN GATE JCT 8/116L RPR ANCW | ICW
LC | 128664385 | 015/142 | T2 EI UKIAH-HPLND-CLVRDL 15/142L RMV VEG | WILLITS | ETL.4050.POLE.STPS | 2024-04-26 | 2024-04-26 | 2025-03-19 | On-Time |  | 2025-04-26 | 2025-04-26 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128667828 | 002/010 | T2 EI BRCEBRG JCT-MRPSA TP 2/10 RPR GYWW | FRESNO | ETL.8651.POLE.NWOD | 2024-04-29 | 2024-04-26 | 2025-03-28 | On-Time |  | 2025-04-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298183 | T2 EI BRCEBRG JCT-MRPSA TP 2/10 RPR GYWW | ICW
LC | 128667845 | 002/010 | T2 EI BRCEBRG JCT-MRPS TP 2/10 COTTER | FRESNO | ETL.8651.INSL.NCER | 2024-04-29 | 2024-04-26 | 2025-03-28 | On-Time |  | 2025-04-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298184 | T2 EI BRCEBRG JCT-MRPS TP 2/10 COTTER | ICW
LC | 128678976 | 036/000 | T2 DI MNDCN-WLTS-FORT BRG 36/0 RPR ANCW | WILLITS | ETL.7550.POLE.WOOD | 2024-04-29 | 2024-04-26 | 2025-02-27 | On-Time |  | 2025-04-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46310130 | T2 DI MNDCN-WLTS-FORT BRG 36/0 RPR ANCW | ICW
LC | 128679290 | 015/113 | T2 DI HELMS-GREGG #1 015/113 RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-04-29 | 2024-04-26 | 2025-03-27 | On-Time |  | 2025-04-26 | 2025-04-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298039 | T2 DI HELMS-GREGG #1 015/113 RPR SHLS | ICS
LC | 128679291 | 015/113 | T2 DI HELMS-GREGG #2 015/113 COTTER | FRESNO | ETL.4880.INSL.NCER | 2024-04-29 | 2024-04-26 | 2025-04-10 | On-Time |  | 2025-04-26 | 2025-04-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46298100 | T2 DI HELMS-GREGG #2 015/113 COTTER | ICS
LC | 128679296 | 013/097A | T2 DI HELMS-GREGG #1 13/097A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-04-29 | 2024-04-26 | 2024-10-14 | On-Time |  | 2025-04-26 | 2025-04-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298101 | T2 DI HELMS-GREGG #1 13/097A RPR SHLS | ICS
LC | 128679297 | 013/097A | T2 DI HELMS-GREGG #1 13/097A COTTER | FRESNO | ETL.4870.INSL.CERA | 2024-04-29 | 2024-04-26 | 2024-10-14 | On-Time |  | 2025-04-26 | 2025-04-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46298102 | T2 DI HELMS-GREGG #1 13/097A COTTER | ICS
LC | 128679657 | 023/175 | T2 DI DRUM-RIO OSO #1 23/175 RPR STRT | SACTO | ETL.1420.TOWR | 2024-04-29 | 2024-04-26 | 2024-12-31 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46327685 | T2 DI DRUM-RIO OSO #1 23/175 RPR STRT | ICQ
LC | 128679716 | 022/179 | T2 DI CRESTA-RIO OSO 22/179 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-04-29 | 2024-04-26 | 2024-12-26 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381266 | T2 DI CRESTA-RIO OSO 22/179 UNBURY | ICQ
LC | 128698534 | 035/008 | T2 DI MNDO-WLITS-FORT BRG 35/08 RPR INSW | WILLITS | ETL.7550.INSL.NCER | 2024-05-01 | 2024-04-26 | 2025-04-08 | On-Time |  | 2025-04-26 | 2025-04-26 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR NTDE | Missing | Insulator-Wood | Install | 35574705 | T2 DI MNDO-WLITS-FORT BRG 35/08 RPR INSW | 93I
LC | 128698600 | 011/152A | T2 DI JOLON TAP 11/152A RPR ANCW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-05-01 | 2024-04-26 | 2025-01-15 | On-Time |  | 2025-04-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46391168 | T2 DI JOLON TAP 11/152A RPR ANCW | ICW
LC | 128698722 | 053/377 | T2 DI CARIBOU-TABLE MTN-53/377 COTTER | TABLEMTN | ETL.4440.INSL | 2024-05-01 | 2024-04-26 | 2025-04-03 | On-Time |  | 2025-04-26 | 2025-04-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46337323 | T2 DI CARIBOU-TABLE MTN-53/377 COTTER | ICS
LC | 128699132 | 106/003C | T2 DI HMBLDT-TRNTY 106/3C RMV VEG | EUREKA | ETL.1820.POLE.NWOD | 2024-05-01 | 2024-04-26 | 2025-03-17 | On-Time |  | 2025-04-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Wood | Remove | 46488972 | T2 DI HMBLDT-TRNTY 106/3C RMV VEG | ICW
LC | 128699135 | 106/003C | T2 DI HMBLDT-TRNTY 106/3C RPR ANCW | EUREKA | ETL.1820.POLE.NWOD | 2024-05-01 | 2024-04-26 | 2025-03-16 | On-Time |  | 2025-04-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46345787 | T2 DI HMBLDT-TRNTY 106/3C RPR ANCW | ICW
LC | 128729377 | 008/117 | T2 DELTA-MTN GATE JCT 8/117L RPL POLE | TABLEMTN | ETL.6750.POLE.WDPS | 2024-05-09 | 2024-04-26 | 2024-04-26 | Past Due |  | 2025-04-26 | 2025-04-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35557674 | T2 EI DELTA-MTN GATE JCT 8/117R RPL POLE | 70Y
LC | 128747001 | 023/173 | T2 DI DRUM-RIO OSO #1 23/173 RPL HRDT | SACTO | ETL.1420.TOWR | 2024-05-10 | 2024-04-26 | 2024-12-17 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46327688 | T2 DI DRUM-RIO OSO #1 23/173 RPL HRDT | ICQ
LC | 128768501 | 035/004 | T2 MNDCNO-WLTS-FT BRG 35/04 RPL STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-13 | 2024-04-26 | 2024-04-26 | Past Due |  | 2025-04-26 | 2025-04-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCL OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574704 | T2 DI MNDCNO-WLTS-FT BRG 35/04 RPL STRW | 70Y
LC | 128768506 | 035/004 | T2NT DI MNDCNO-WLTS-FT BRG 35/04 RMV VEG | WILLITS | ETL.7550.POLE.WOOD | 2024-05-13 | 2024-04-26 | 2025-02-04 | On-Time |  | 2027-04-26 | 2025-04-26 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128768943 | 105/002 | T2 DI HUMBLT TRNIT 105/02L RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-13 | 2024-04-26 | 2024-09-01 | On-Time |  | 2024-10-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46249702 | T2 DI HUMBLT TRNIT 105/02L RPR GYWW | ICW
LC | 128768947 | 105/002 | T2 DI HUMBLT TRNIT 105/02L RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-13 | 2024-04-26 | 2024-04-26 | Past Due |  | 2025-04-26 | 2025-04-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574488 | T2 DI HUMBOLDT-TRINITY 105/002C RPL STRW | 70Y
LC | 128768987 | 005/033 | T2NT DI BALCH-SANGER 05/33 RMV VEG | FRESNO | ETL.1050.TOWR | 2024-05-13 | 2024-04-26 | 2024-04-26 | Past Due |  | 2027-04-26 | 2025-04-26 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128773624 | 000/002 | T2 DI BALCH-SANGER 0/2 RPL HRDT | FRESNO | ETL.1050.TOWR | 2024-05-14 | 2024-04-26 | 2025-01-15 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46297875 | T2 DI BALCH-SANGER 0/2 RPL HRDT | ICQ
LC | 128773625 | 019/156 | T2 DI DRUM-RIO OSO #2 19/156 RPR INSS | SACTO | ETL.1430.INSL.NCER | 2024-05-14 | 2024-04-26 | 2025-04-21 | On-Time |  | 2025-04-26 | 2025-04-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300568 | T2 DI DRUM-RIO OSO #2 19/156 RPR INSS | ICS
LC | 128773762 | 002/019 | T2 DI BALCH-SANGER 2/19 RPR JUMS | FRESNO | ETL.1050.INSL.CERA | 2024-05-14 | 2024-04-26 | 2025-05-12 | Past Due |  | 2025-04-26 | 2025-04-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Steel | Repair | 46298109 | T2 DI BALCH-SANGER 2/19 RPR JUMS | ICS
LC | 128780125 | 020/157 | T2 DI DRUM-RIO OSO #1 20/157 TOUCH | SACTO | ETL.1420.TOWR | 2024-05-15 | 2024-04-26 | 2025-02-19 | On-Time |  | 2024-10-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46463290 | T2 DI DRUM-RIO OSO #1 20/157 RPR STRT | ICQ
LC | 128780176 | 019/153 | T2 DI DRUM-RIO OSO #1 19/153 BNT STEEL | SACTO | ETL.1420.TOWR | 2024-05-15 | 2024-04-26 | 2024-12-18 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46327693 | T2 DI DRUM-RIO OSO #1 19/153 BNT STEEL | ICQ
LC | 128780276 | 012/113A | T2 DI DRUM-RIO OSO #1 12/113A RPR STRT | SACTO | ETL.1420.TOWR | 2024-05-15 | 2024-04-26 | 2024-12-17 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46327694 | T2 DI DRUM-RIO OSO #1 12/113A RPR STRT | ICQ
LC | 128799568 | 015/112A | T2 DI HELMS GREG #1 15/112A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-17 | 2024-04-26 | 2025-03-27 | On-Time |  | 2025-04-26 | 2025-04-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298110 | T2 DI HELMS GREG #1 15/112A RPR SHLS | ICS
LC | 128799645 | 031/006 | T2 DI MNDCNO-WLTS FRT BRG 31/6 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-17 | 2024-04-26 | 2025-04-02 | On-Time |  | 2025-04-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310127 | T2 DI MNDCNO-WLTS FRT BRG 31/6 RPR GYWW | ICW
LC | 128799682 | 031/006 | T2 DI MNDCNO-WLTS FRT BRG 31/6 RPL INSW | WILLITS | ETL.7550.INSL.CERA | 2024-05-17 | 2024-04-26 | 2025-04-02 | On-Time |  | 2025-04-26 | 2025-04-26 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574304 | T2 DI MNDCNO-WLTS FRT BRG 31/6 RPL INSW | 93I
LC | 128799995 | 012/113A | T2 DI DRUM-RIO OSO#2 12/113A RPL HRDT | SACTO | ETL.1430.TOWR | 2024-05-17 | 2024-04-26 | 2024-12-17 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46327696 | T2 DI DRUM-RIO OSO#2 12/113A RPL HRDT | ICQ
LC | 128799996 | 024/180 | T2 DI DRM RIO OSO #2 24/180 RPR INSS | SACTO | ETL.1430.INSL.NCER | 2024-05-17 | 2024-04-26 | 2025-04-21 | On-Time |  | 2025-04-26 | 2025-04-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300570 | T2 DI DRM RIO OSO #2 24/180 RPR INSS | ICS
LC | 128800097 | 014/104A | T2 DI HELMS-GREGG #1 14/104A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-17 | 2024-04-26 | 2025-03-26 | On-Time |  | 2025-04-26 | 2025-04-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298111 | T2 DI HELMS-GREGG #1 14/104A RPR SHLS | ICS
LC | 128800098 | 014/104A | T2 DI HELMS-GREGG #1 14/104A RPR INSS | FRESNO | ETL.4870.INSL.CERA | 2024-05-17 | 2024-04-26 | 2025-03-26 | On-Time |  | 2025-04-26 | 2025-04-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator-Steel | Repair | 46298112 | T2 DI HELMS-GREGG #1 14/104A RPR INSS | ICS
LC | 128800128 | 030/222 | T2 DI DRM RIO OSO #2 30/222 RPL INSS | SACTO | ETL.1430.INSL.CERA | 2024-05-17 | 2024-04-26 | 2025-04-21 | On-Time |  | 2025-04-26 | 2025-04-26 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570801 | T2 DI DRM RIO OSO #2 RPL INSS 3 TWRS | 93K
LC | 128800153 | 033/239 | T2 DI DRM RIO OSO #1 33/239 TOUCH | SACTO | ETL.1420.TOWR | 2024-05-17 | 2024-04-26 | 2025-02-19 | On-Time |  | 2024-10-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46463291 | T2 DI DRM RIO OSO #1 33/239 RPR STRT | ICQ
LC | 128800206 | 003/021 | T2 DI BALCH-SANGER-03/21 RMV VEG | FRESNO | ETL.1050.TOWR | 2024-05-17 | 2024-04-26 | 2025-05-05 | Past Due |  | 2025-04-26 | 2025-04-26 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128800225 | 013/100A | T2 DI HELMS GREG #1 13/100A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-17 | 2024-04-26 | 2025-03-26 | On-Time |  | 2025-04-26 | 2025-04-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298114 | T2 DI HELMS GREG #1 13/100A RPR SHLS | ICS
LC | 128800270 | A008/167 | T2 DI CASCADE-B-DSCH A8/167 RPL STRW | TABLEMTN | ETL.6310.POLE.WOOD | 2024-05-17 | 2024-04-26 | 2025-04-08 | On-Time |  | 2025-04-26 | 2025-04-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572153 | T2 DI CASCADE-B-DSCH A8/167 RPL STRW | 70Y
LC | 128800449 | :014/002 | T2 DI EAGLE ROCK CRTNA 14/2 CANCEL | WILLITS | ETL.1470.POLE.WOOD | 2024-05-17 | 2024-04-26 | 2024-04-26 | Past Due |  | 2025-04-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW ACCL OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310124 | T2 DI EAGLE ROCK CRTNA 14/2 RPR STRW | ICW
LC | 128800472 | 031/227 | T2 DI DRUM-RIO OSO #1-31/227 RPL HRDT | SACTO | ETL.1420.TOWR | 2024-05-17 | 2024-04-26 | 2024-12-31 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46327697 | T2 DI DRUM-RIO OSO #1-31/227 RPL HRDT | ICQ
LC | 128800558 | 024/182 | T2 DI DRM RIO OSO #1 24/182 TOUCH | SACTO | ETL.1420.TOWR | 2024-05-17 | 2024-04-26 | 2024-04-26 | Past Due |  | 2024-10-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472260 | T2 DI DRM RIO OSO #1 24/182 RPR STRT | ICQ
LC | 128800698 | 009/006 | T2 MENDOCINO-HARTLEY 9/6 RPR GYWW | WILLITS | ETL.7510.POLE.NWOD | 2024-05-17 | 2024-04-26 | 2024-04-26 | Past Due |  | 2025-04-26 | 2025-04-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW ACCM OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46340263 | T2 DI MENDOCINO-HARTLEY 9/6 RPR GYWW | ICW
LC | 128800799 | 022/172 | T2 DI DRM RIO OSO #1 22/172 RPL HRDT | SACTO | ETL.1420.TOWR | 2024-05-17 | 2024-04-26 | 2024-12-17 | On-Time |  | 2025-04-26 | 2025-04-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46327699 | T2 DI DRM RIO OSO #1 22/172 RPL HRDT | ICQ
LC | 123437248 | 044/382 | T2NT EI PIT #1-CTTNWD 045/382 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2022-04-27 | 2022-04-27 | 2023-07-06 | On-Time |  | 2025-04-27 | 2025-04-27 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45639738 | T2 EI PIT #1-COTTONWOOD 045/382 RPR STRT | ICQ
LC | 123437253 | 045/394 | T2NT EI PIT #1-COTTONWD 045/394 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2022-04-27 | 2022-04-27 | 2023-09-20 | On-Time |  | 2025-04-27 | 2025-04-27 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45581329 | T2 EI PIT #1-COTTONWOOD 045/394 RPR STRT | ICQ
LC | 123439133 | 021/091 | T3NT DI MORR BAY-SL SS #1 21/91 RPR STRT | PISMOBCH | ETL.5300.TOWR | 2022-04-27 | 2022-04-27 | 2023-07-19 | On-Time |  | 2025-04-27 | 2025-04-27 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648877 | T3 DI MORR BAY-SL SS #1 021/091 RPR STRT | ICQ
LC | 123440425 | 006/030 | T3NT DI MRRO BAY-TMPLTON 06/30 RPR OPGW | PISMOBCH | ETL.5933.TOWR | 2022-04-27 | 2022-04-27 | 2023-11-01 | On-Time |  | 2025-04-27 | 2025-04-27 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire / OPGW-Steel | Repair | 45672066 | T3 DI MORRO BAY-TEMPLETON 06/30 RPR OPGW | ICS
LC | 123468062 | 011/044 | T3NT DI MORRO BAY-TMPLTN 11/44 RPR FOND | PISMOBCH | ETL.5933.TOWR | 2022-04-30 | 2022-04-27 | 2023-07-21 | On-Time |  | 2025-04-27 | 2025-04-27 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45649442 | T3 DI MORRO BAY-TMPLTN 11/44 RPR FOND | ICQ
LC | 123488062 | 017/079 | T3NT DI MSS LNDG-MTCLF 17/079 RPR GYWS | MOSSLNDG | ETL.6050.TOWR | 2022-05-03 | 2022-04-27 | 2023-07-19 | On-Time |  | 2025-04-27 | 2025-04-27 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45650153 | T3 DI MSS LNDG-MTCLF 17/079 RPR GYWS | ICS
LC | 123581782 | 028/232 | T3NT DI RND MTN-CTNWD #3 28/232 BNT STL | TABLEMTN | ETL.5650.TOWR | 2022-05-12 | 2022-04-27 | 2023-09-13 | On-Time |  | 2025-04-27 | 2025-04-27 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648234 | T3 DI RND MTN-CTNWD #3 28/232 BNT STEEL | ICQ
LC | 128664734 | 001/009 | T2 KERCKHOFF-CLVS-SNGR #1 1/9 RMV ENCRCH | FRESNO | ETL.1890.TOWR | 2024-04-27 | 2024-04-27 | 2024-08-20 | On-Time |  | 2024-10-27 | 2025-04-27 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | Encroachment | Right of Way | Remove | 46249756 | T2 KERCKHOFF-CLVS-SNGR #1 1/9 RMV ENCRCH | CHR
LC | 128664829 | 010/131 | T2 WST PNT-VLLY SPRNGS 10/131 TOUCH | VICTOR | ETL.8350.POLE.NWOD | 2024-04-27 | 2024-04-27 | 2024-04-27 | Past Due |  | 2024-10-27 | 2025-04-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46477459 | T2 WST PNT-VLLY SPRNGS 10/131 TOUCH | ICW
LC | 128664950 | 003/020 | T2 STANISLAUS-MANTECA 3/20 TOUCH | VICTOR | ETL.3820.TOWR | 2024-04-27 | 2024-04-27 | 2025-01-22 | On-Time |  | 2024-10-27 | 2025-04-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472918 | T2 STANISLAUS-MANTECA 3/20 TOUCH | ICQ
LC | 128665273 | 011/000 | T2 OAKHURST TAP 011/000 RMV ENCR | FRESNO | ETL.1252.POLE.NWOD | 2024-04-27 | 2024-04-27 | 2024-08-20 | On-Time |  | 2024-10-27 | 2025-04-27 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | Encroachment | Right of Way | Remove | 46249757 | T2 OAKHURST TAP 011/000 RMV ENCR | CHR
LC | 128665286 | 021/135 | T2 STLS-MLNS SW SM #1 21/135 TOUCH | VICTOR | ETL.3830.TOWR | 2024-04-27 | 2024-04-27 | 2025-01-22 | On-Time |  | 2024-10-27 | 2025-04-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472919 | T2 STLS-MLNS SW SM #1 21/135 TOUCH | ICQ
LC | 128679413 | 006/008 | T2 DI MNDCN-WLTS FRT BRG 6/8 RPR JUMW | WILLITS | ETL.7550.INSL.NCER | 2024-04-29 | 2024-04-27 | 2025-01-14 | On-Time |  | 2024-07-27 | 2025-04-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46252595 | T2 DI MNDCN-WLTS FRT BRG 6/8 RPR JUMW | ICW
LC | 128679595 | 000/003 | T2 DI LUCERNE #1 TAP 0/3 RPR GYWW | WILLITS | ETL.1331.POLE.NWOD | 2024-04-29 | 2024-04-27 | 2024-12-16 | On-Time |  | 2024-07-27 | 2025-04-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46246703 | T2 DI LUCERNE #1 TAP 0/3 RPR GYWW | ICW
LC | 128699073 | 060/303 | T2 DI MLN RND MTN#2 60/303 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-05-01 | 2024-04-27 | 2025-02-10 | On-Time |  | 2025-04-27 | 2025-04-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338193 | T2 DI MLN RND MTN#2 60/303 RPR SHLD | ICS
LC | 128699111 | 016/076 | T2 DI MOS LNDNG LS BNS 16/76 BNT STEEL | MOSSLNDG | ETL.6040.TOWR | 2024-05-01 | 2024-04-27 | 2025-01-28 | On-Time |  | 2025-04-27 | 2025-04-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416607 | T2NT DI MOS LNDNG LS BNS 16/76 BNT STEEL | ICQ
LC | 128708351 | 030/218 | T2 DI DRUM-RIO OSO #1 30/218 RPR CONS | SACTO | ETL.1420.INSL.NCER | 2024-05-03 | 2024-04-27 | 2024-10-11 | On-Time |  | 2024-07-27 | 2025-04-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Conductor-Steel | Repair | 46247564 | T2 DI DRUM-RIO OSO #1 30/218 RPR CONS | ICS
LC | 128708358 | 014/125 | T2 DI DRUM-RIO OSO #1 14/125 TOUCH | SACTO | ETL.1420.TOWR | 2024-05-03 | 2024-04-27 | 2024-04-27 | Past Due |  | 2024-10-27 | 2025-04-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472259 | T2 DI DRUM-RIO OSO #1 14/125 RPR STRT | ICQ
LC | 128708420 | 014/125 | T2 DI DRUM-RIO OSO #1 14/125 RPR FOND | SACTO | ETL.1420.TOWR | 2024-05-03 | 2024-04-27 | 2024-12-26 | On-Time |  | 2025-04-27 | 2025-04-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46327686 | T2 DI DRUM-RIO OSO #1 14/125 RPR FOND | ICQ
LC | 128708422 | 022/006 | T2 DI KONOCTI MIDLTWN+ 22/6 RPL ANCW | WILLITS | ETL.6380.POLE.NWOD | 2024-05-03 | 2024-04-27 | 2025-03-17 | On-Time |  | 2025-04-27 | 2025-04-27 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574111 | T2 DI KONOCTI MIDLTWN+ 22/6 RPL ANCW | 93E
LC | 128708778 | 016/077 | T2 DI MOSS LANDING-LB 16/77 RPR FOND | MOSSLNDG | ETL.6040.TOWR | 2024-05-03 | 2024-04-27 | 2025-01-28 | On-Time |  | 2025-04-27 | 2025-04-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416617 | T2 DI MOSS LANDING-LB 16/77 RPR FOND | ICQ
LC | 123580628 | 020/164 | T2NT DI PIT #1-CTTNWOOD 20/164 BENT STL | TABLEMTN | ETL.5390.TOWR | 2022-05-12 | 2022-04-28 | 2023-07-27 | On-Time |  | 2025-04-28 | 2025-04-28 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45717905 | T2 DI PIT #1-COTTONWOOD 20/164 BENT STL | ICQ
LC | 125273540 | 024/292 | T2NT DI DRUM-SUMMIT #2 024/292L RPL PL | SACTO | ETL.1450.POLE.WDPS | 2023-01-03 | 2022-04-28 | 2023-08-23 | On-Time |  | 2025-04-28 | 2025-04-28 | 372 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE ACCM COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 31634271 | T2 DI DRUM-SUMMIT #2 024/292R RPL STRW | 70Y
LC | 128666560 | 003/022 | T2 EI BUTT VALLEY-CARIBOU 3/22 RPR CNDS | TABLEMTN | ETL.1180.INSL.CERA | 2024-04-28 | 2024-04-28 | 2025-04-02 | On-Time |  | 2025-04-28 | 2025-04-28 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Conductor-Steel | Repair | 46337322 | T2 EI BUTT VALLEY-CARIBOU 3/22 RPR CNDS | ICS
LC | 128668222 | 010/192 | T2 EI HAT CREEK #1-WSTWD 10/192 RPL POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-04-29 | 2024-04-28 | 2025-04-22 | On-Time |  | 2025-04-28 | 2025-04-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574745 | T2 EI HAT CREEK #1-WSTWD 10/192 RPL POLE | 70Y
LC | 123457251 | 007/047 | T2NT EI OLEUM-""G"" #2" 7/47 RPL INSS | CONCORD | ETL.3160.INSL | 2022-04-29 | 2022-04-29 | 2023-08-29 | On-Time |  | 2025-04-29 | 2025-04-29 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 31638850 | 12NT EI OLEUM-""G"" #2" 6/41 RPL INSS 2T | 93K
LC | 123459182 | 006/041 | T2NT EI OLEUM-""G"" #2" 6/41 RPL INSS | CONCORD | ETL.3160.INSL.CERA | 2022-04-29 | 2022-04-29 | 2023-08-24 | On-Time |  | 2025-04-29 | 2025-04-29 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 31638850 | 12NT EI OLEUM-""G"" #2" 6/41 RPL INSS 2T | 93K
LC | 123460375 | 005/039 | T2NT EI OLEUM-""G"" #2" 5/39 RPL INSS | CONCORD | ETL.3160.INSL.CERA | 2022-04-29 | 2022-04-29 | 2023-08-29 | On-Time |  | 2025-04-29 | 2025-04-29 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 31625563 | EI OLEUM-G #2 RPL INSS IN 3 TWRS. | 93K
LC | 123491505 | 014/388 | T3NT DI COLGATE-ALLGHNY 14/388 RPR GYWW | SACTO | ETL.6470.POLE.WOOD | 2022-05-03 | 2022-04-29 | 2023-06-24 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45686171 | T3 DI COLGATE-ALLEGHANY 14/388 RPR GYWW | ICW
LC | 123500972 | 014/398 | T3NT DI COLGATE-ALLEGHNY 14/398 RPL DAMW | SACTO | ETL.6470.INSL.CERA | 2022-05-04 | 2022-04-29 | 2023-06-05 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR | No Good/Out of Stdrd | Damper-Wood | Replace | 45686130 | T3 DI COLGATE-ALLEGHANY 14/398 RPL DAMW | ICW
LC | 123559247 | 013/349 | T3NT DI COLGATE-ALLGHNY 13/349 RPL SPLW | SACTO | ETL.6470.INSL.NCER | 2022-05-10 | 2022-04-29 | 2023-06-14 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR | No Good/Out of Stdrd | Splice-Wood | Replace | 45685523 | T3 DI COLGATE-ALLGHNY 13/349 RPL SPLW | ICW
LC | 128667265 | 032/136 | T2 TESLA-METCALF 32/136 COTTER | METCALF | ETL.6110.INSL.NCER | 2024-04-29 | 2024-04-29 | 2025-03-23 | On-Time |  | 2025-04-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46286779 | T2 TESLA-METCALF 32/136 COTTER | ICS
LC | 128668489 | 015/110 | T2 ELECTRA-BELLOTA 15/110 RPL INSS | VICTOR | ETL.4670.INSL | 2024-04-29 | 2024-04-29 | 2025-03-19 | On-Time |  | 2025-04-29 | 2025-04-29 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593221 | T2 EI ELECTRA-BELLOTA 002/024 RPL INSS | 93K
LC | 128668495 | 003/017 | T2 EI LOS ESTEROS-METCALF 3/17 COMPLETE | METCALF | ETL.5353.INSL | 2024-04-29 | 2024-04-29 | 2025-03-19 | On-Time |  | 2025-04-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46286780 | T2 EI LOS ESTEROS-METCALF 3/17 RPR INSS | ICS
LC | 128669332 | 018/105 | T2 EI STNISLS-MANTECA #2 18/105 COMPLETE | VICTOR | ETL.3820.TOWR | 2024-04-29 | 2024-04-29 | 2025-03-18 | On-Time |  | 2025-04-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46416586 | T2 EI STANISLS-MANTECA #2 18/105 UNBURY | ICQ
LC | 128671505 | 006/044 | T2 VALLEY SPRNGS-BELLOTA 06/044 COMPLETE | VICTOR | ETL.5860.INSL.CERA | 2024-04-29 | 2024-04-29 | 2025-03-25 | On-Time |  | 2025-04-29 | 2025-04-29 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593222 | T2 EI VLY SPRNGS-BELLTA 04/28 RPL INSS | 93K
LC | 128671978 | 044/215 | T2 CORTINA-MNDCN #1 44/215 RPR STRT | WILLITS | ETL.1330.TOWR | 2024-04-29 | 2024-04-29 | 2025-05-19 | Past Due |  | 2024-07-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NOAC REAR ACCL COMP OH FMOB TR2 PRTO FRAR NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472291 | T2 CORTINA-MNDCN #1 44/215 RPR STRT | ICQ
LC | 128672133 | 009/127 | T2 EI DELTA-MTN GATE JCT 9/127 RPL ANCW | TABLEMTN | ETL.6750.POLE.WOOD | 2024-04-29 | 2024-04-29 | 2025-04-09 | On-Time |  | 2025-04-29 | 2025-04-29 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35557675 | T2 EI DELTA-MTN GATE JCT 9/127 RPL ANCW | 93E
LC | 128672180 | 018/113 | T2 EI STNSS-MLN SW S-MNT 18/113 RPR STRT | VICTOR | ETL.3830.TOWR | 2024-04-29 | 2024-04-29 | 2025-04-10 | On-Time |  | 2025-04-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416588 | T2 EI STNSS-MLN SW S-MNT 18/113 RPR STRT | ICQ
LC | 128672226 | 018/114 | T2 EI STNSS-MLN SW S-MNT 18/114 RPR STRT | VICTOR | ETL.3830.TOWR | 2024-04-29 | 2024-04-29 | 2025-04-08 | On-Time |  | 2025-04-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416590 | T2 EI STNSS-MLN SW S-MNT 18/114 RPR STRT | ICQ
LC | 128674828 | 014/205 | T2 EI SSQC-SNTA YNZ SS 14/205 RPL POLE | PISMOBCH | ETL.3700.POLE.WOOD | 2024-04-29 | 2024-04-29 | 2025-04-04 | On-Time |  | 2025-04-29 | 2025-04-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573791 | T2 EI SSQC-SNTA YNZ SS 14/205 RPL POLE | 70Y
LC | 128675901 | 008/126 | T2 EI DELTA-MTN GATE JCT 008/126 COTTER | TABLEMTN | ETL.6750.INSL.NCER | 2024-04-29 | 2024-04-29 | 2024-07-17 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46265499 | T2 EI DELTA-MTN GATE JCT 008/126 COTTER | ICW
LC | 128675932 | 000/003 | T2 EI CLMN-CTTNWD 0/3 RPR GYWW | TABLEMTN | ETL.6430.POLE.NWOD | 2024-04-29 | 2024-04-29 | 2024-12-05 | On-Time |  | 2024-07-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46247125 | T2 EI CLMN-CTTNWD 0/3 RPR GYWW | ICW
LC | 128676098 | 015/005 | T2 EI DUNLAP TAP 15/5 RPR INSW | FRESNO | ETL.9061.INSL.NCER | 2024-04-29 | 2024-04-29 | 2025-03-21 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT ACCM COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298160 | T2 EI DUNLAP TAP 15/5 RPR INSW | ICW
LC | 128677992 | 036/169 | T2 EI RND MTN-TBL MTN #2 36/169 RPR INSS | TABLEMTN | ETL.6070.INSL | 2024-04-29 | 2024-04-29 | 2024-05-08 | On-Time |  | 2024-07-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46239172 | T2 EI RND MTN-TBL MTN #2 36/169 RPR INSS | ICS
LC | 128678329 | 033/005 | T2 EI RIO DL JCT-BRDGVLE 33/05 CANCEL | EUREKA | ETL.7850.INSL.NCER | 2024-04-29 | 2024-04-29 | 2024-04-29 | Past Due |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Splice-Wood | Replace | 46345790 | T2 EI RIO DL JCT-BRDGVLE 33/05 RPL SPLW | ICW
LC | 128678380 | 033/004 | T2 EI RIO DL JCT-BRDGVLE 33/04 CANCEL | EUREKA | ETL.7850.INSL.NCER | 2024-04-29 | 2024-04-29 | 2024-04-29 | Past Due |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Splice-Wood | Replace | 46345789 | T2 EI RIO DL JCT-BRDGVLE 33/04 RPL SPLW | ICW
LC | 128678391 | 032/006 | T2 EI RIO DLL JCT-BRDGVLE 32/6C RPR GYWW | EUREKA | ETL.7850.POLE.STPS | 2024-04-29 | 2024-04-29 | 2025-04-19 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345788 | T2 EI RIO DLL JCT-BRDGVLE 32/6C RPR GYWW | ICW
LC | 128678394 | 032/006 | T2 EI RIO DLL JCT-BRDGVLE 32/6L RPR GYWW | EUREKA | ETL.7850.POLE.STPS | 2024-04-29 | 2024-04-29 | 2024-11-18 | On-Time |  | 2024-10-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46249705 | T2 EI RIO DLL JCT-BRDGVLE 32/6L RPR GYWW | ICW
LC | 128678588 | 000/006 | T2 EI COLEMAN-COTTONWOOD 0/6 RPR INSW | TABLEMTN | ETL.6430.INSL.NCER | 2024-04-29 | 2024-04-29 | 2024-12-05 | On-Time |  | 2024-10-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46251422 | T2 EI COLEMAN-COTTONWOOD 0/6 RPR INSW | ICW
LC | 128678696 | 011/216 | T2 EI HT CRK #1-WSTWD 11/216 COMPLETE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-04-29 | 2024-04-29 | 2025-04-22 | On-Time |  | 2025-04-29 | 2025-04-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574746 | T2 EI HT CRK #1-WSTWD 11/216 RPL POLE | 70Y
LC | 128678748 | 000/004 | T2NT EI BKS CRK-RCK CRK-CRT 0/4 RPL HRDT | TABLEMTN | ETL.4430.TOWR | 2024-04-29 | 2024-04-29 | 2025-04-03 | On-Time |  | 2027-04-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46351479 | T2NT EI BKS CRK-RCK CRK-CRT 0/4 RPL HRDT | ICQ
LC | 128678783 | 023/612 | T2 EI CARIBOU #2 23/612 RPR INSW | TABLEMTN | ETL.6280.INSL.NCER | 2024-04-29 | 2024-04-29 | 2024-09-16 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC CLR ACCL COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46323231 | T2 EI CARIBOU #2 23/612 RPR INSW | ICW
LC | 128678789 | 000/003 | T2 EI BCKS CRK-RCK CRK-CRST 0/3 RPL HRDT | TABLEMTN | ETL.4430.TOWR | 2024-04-29 | 2024-04-29 | 2025-04-03 | On-Time |  | 2025-04-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46353960 | T2 EI BCKS CRK-RCK CRK-CRST 0/3 RPL HRDT | ICQ
LC | 128678812 | 000/004 | T2 EI BCKS CRK-RCK CRK-CRST 0/4 RPR STRT | TABLEMTN | ETL.4430.TOWR | 2024-04-29 | 2024-04-29 | 2025-04-03 | On-Time |  | 2025-04-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB NTDE | No Good/Out of Stdrd | Structure-Tower | Repair | 46353961 | T2 EI BCKS CRK-RCK CRK-CRST 0/4 RPR STRT | ICQ
LC | 128679005 | 017/231 | T2 WV KESWICK-TRINITY 17/231 INS DMPW | TABLEMTN | ETL.7270.INSL.NCER | 2024-04-29 | 2024-04-29 | 2025-03-31 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46311274 | T2 WV KESWICK-TRINITY 17/231 INS DMPW | ICW
LC | 128679081 | 000/020 | T2 BRICBRG JCT-MRPS TP 00/20 RMV VEG | FRESNO | ETL.8651.POLE.WOOD | 2024-04-29 | 2024-04-29 | 2025-04-03 | On-Time |  | 2025-04-29 | 2025-04-29 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128679253 | 016/156 | T2 EI UKH-HPLND-CLVERDLE 16/156 GO95 | WILLITS | ETL.4050.POLE.WOOD | 2024-04-29 | 2024-04-29 | 2025-06-18 | Past Due |  | 2025-04-29 | 2025-04-29 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35572242 | T2 EI UKH-HPLND-CLVERDLE 16/156 GO95 | 93G
LC | 128679289 | 012/003 | T2 DI FULTON-HOPLAND 12/3 RPL POLE | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-04-29 | 2024-04-29 | 2025-03-19 | On-Time |  | 2025-04-29 | 2025-04-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574252 | T2 DI FULTON-HOPLAND 12/3 RPL POLE | 70Y
LC | 128679448 | 018/011 | T2 DI MNDOCNO-WLTS FRT BRG 18/11 COTTER | WILLITS | ETL.7550.POLE.WOOD | 2024-04-29 | 2024-04-29 | 2025-04-09 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46246786 | T2 DI MNDOCNO-WLTS FRT BRG 18/11 COTTER | ICW
LC | 128679668 | 034/232C | T2 DI TRINITY-COTONWOD 34/232C RPR ANCW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-04-29 | 2024-04-29 | 2024-07-19 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46284298 | T2 DI TRINITY-COTONWOD 34/232C RPR ANCW | ICW
LC | 128679684 | 034/232C | T2 DI TRINITY-COTONWOD 34/232C RPR JUMW | TABLEMTN | ETL.4040.INSL.CERA | 2024-04-29 | 2024-04-29 | 2024-08-19 | On-Time |  | 2024-07-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46239916 | T2 DI TRINITY-COTONWOD 34/232C RPR JUMW | ICW
LC | 128679734 | 004/030 | T2 DI EL DORADO-MISORI FLT#1 4/30 COTTER | SACTO | ETL.1530.INSL.CERA | 2024-04-29 | 2024-04-29 | 2025-03-31 | On-Time |  | 2025-04-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46404595 | T2 DI EL DORADO-MISORI FLT#1 4/30 COTTER | ICS
LC | 128680385 | 003/017 | T2 EI EXCHQR-INDN FLT 3/17 RMV DBRS | FRESNO | ETL.8650.INSL.NCER | 2024-04-30 | 2024-04-29 | 2024-05-23 | On-Time |  | 2025-04-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Debris/Nest/etc. | Structure-Steel | Remove | 46250208 | T2 EI EXCHQR-INDN FLT 3/17 EMRGNCY RPR | IBE
LC | 128682506 | 014/085 | T2 EI STNLS-MLS SW ST-MN 14/085 UNBURY | VICTOR | ETL.3830.TOWR | 2024-04-30 | 2024-04-29 | 2025-03-29 | On-Time |  | 2025-04-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416591 | T2 EI STNLS-MLS SW ST-MN 14/085 UNBURY | ICQ
LC | 128684955 | 002/030 | T2 EI PIT #5-ROUND MTN #2 2/30R RPR GRWW | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-30 | 2024-04-29 | 2025-03-03 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46454337 | T2 EI PIT #5-ROUND MTN #2 2/30R RPR GRWW | ICW
LC | 128684971 | 002/030 | T2 EI PIT #5-ROUND MTN #2 2/30L RPR STRW | TABLEMTN | ETL.5430.POLE.WDPS | 2024-04-30 | 2024-04-29 | 2025-03-03 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454338 | T2 EI PIT #5-ROUND MTN #2 2/30L RPR STRW | ICW
LC | 128684980 | 002/026 | T2 EI PIT #5-RND MTN#2 2/26L RPR INSS | TABLEMTN | ETL.5430.INSL.NCER | 2024-04-30 | 2024-04-29 | 2025-03-03 | On-Time |  | 2025-04-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46443288 | T2 EI PIT #5-RND MTN#2 2/26L RPR INSS | ICS
LC | 128684981 | 002/024 | T2 EI PIT#5-RND MTN #2 2/24 RPR SHLD | TABLEMTN | ETL.5430.POLE.STPS | 2024-04-30 | 2024-04-29 | 2024-05-29 | On-Time |  | 2024-07-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Shield Wire - Wood | Repair | 46251397 | T2 EI PIT#5-RND MTN #2 2/24 RPR SHLD | ICW
LC | 128690519 | 010/175 | T2 EI TEJON-LEBEC 10/175 RMV VEG | MIDWAY | ETL.9250.POLE.WOOD | 2024-05-01 | 2024-04-29 | 2025-02-21 | On-Time |  | 2025-04-29 | 2025-04-29 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP ACCM COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128698592 | 034/233 | T2 DI TRINITY-COTTONWD 34/233 RPR JUMW | TABLEMTN | ETL.4040.INSL.CERA | 2024-05-01 | 2024-04-29 | 2024-08-19 | On-Time |  | 2024-07-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46247580 | T2 DI TRINITY-COTTONWD 34/233 RPR JUMW | ICW
LC | 128698820 | 027/221 | T2 DI PIT#1 CTTNWD 27/221 RPR JUMS | TABLEMTN | ETL.5390.INSL.NCER | 2024-05-01 | 2024-04-29 | 2024-11-08 | On-Time |  | 2024-07-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46251390 | T2 DI PIT#1 CTTNWD 27/221 RPR JUMS | ICS
LC | 128698904 | 027/220 | T2 DI PIT#1 CTTNWD 27/220 RPR JUMS | TABLEMTN | ETL.5390.INSL.NCER | 2024-05-01 | 2024-04-29 | 2024-11-08 | On-Time |  | 2024-07-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46250285 | T2 DI PIT#1 CTTNWD 27/220 RPR JUMS | ICS
LC | 128698991 | 054/485 | T2 DI PIT#1 CTTNWD 54/485 RPR INSS | TABLEMTN | ETL.5390.INSL.NCER | 2024-05-01 | 2024-04-29 | 2025-04-24 | On-Time |  | 2025-04-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46452769 | T2 DI PIT#1 CTTNWD 54/485 RPR INSS | ICS
LC | 128698995 | 013/098A | T2 DI HELMS GREGG #1 13/098A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-01 | 2024-04-29 | 2024-10-14 | On-Time |  | 2025-04-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298107 | T2 DI HELMS GREGG #1 13/098A RPR SHLS | ICS
LC | 128698999 | 013/098A | T2 DI HELMS GREGG #1 13/098A RPR JUMS | FRESNO | ETL.4870.INSL.NCER | 2024-05-01 | 2024-04-29 | 2024-10-14 | On-Time |  | 2024-07-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46257383 | T2 DI HELMS GREGG #1 13/098A RPR JUMS | ICS
LC | 128716722 | 020/001 | T2 DI CLR LK-KONOCTI 020/001 TOUCH | WILLITS | ETL.6852.POLE.NWOD | 2024-05-06 | 2024-04-29 | 2025-05-02 | Past Due |  | 2024-10-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46507558 | T2 DI CLR LK-KONOCTI 020/001 TOUCH | ICW
LC | 128716783 | 014/124 | T2 DI DRUM-RIO OSO #1 014/124 TOUCH | SACTO | ETL.1420.TOWR | 2024-05-06 | 2024-04-29 | 2024-04-29 | Past Due |  | 2024-10-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472280 | T2 DI DRUM-RIO OSO #1 014/124 RPR STRT | ICQ
LC | 128717094 | 037/005 | T2 DI MNDO-WILTS-FRT BRG 37/05 RPL INSW | WILLITS | ETL.7550.INSL.NCER | 2024-05-06 | 2024-04-29 | 2025-04-03 | On-Time |  | 2025-04-29 | 2025-04-29 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574707 | T2 DI MNDO-WILTS-FRT BRG 37/05 RPL INSW | 93I
LC | 128717125 | 054/380 | T2 DI CARIBOU-TABLE MTN 54/380 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2024-05-06 | 2024-04-29 | 2025-03-17 | On-Time |  | 2025-04-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310430 | T2 DI CARIBOU-TABLE MTN 54/380 RPR STRT | ICQ
LC | 128717645 | 004/032 | T2NT DI SOBRANTE"R"#1+" 4/32 RPL HRDT | CONCORD | ETL.3770.TOWR | 2024-05-06 | 2024-04-29 | 2025-03-05 | On-Time |  | 2027-04-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Hardware-Tower | Replace | 46287411 | T2NT DI SOBRANTE"R"#1+" 4/32 RPL HRDT | ICQ
LC | 128717655 | 054/490 | T2 DI RND MTN CTNWD#3 54/490 RPL INSS | TABLEMTN | ETL.5650.INSL.CERA | 2024-05-06 | 2024-04-29 | 2025-03-06 | On-Time |  | 2025-04-29 | 2025-04-29 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574240 | T2 ROUND MTN-COTNWD #3 47/411 RPL INSS | 93K
LC | 128717671 | 029/211 | T2 DI DRUM-RIO OSO #1 29/211 RPR INSS | SACTO | ETL.1420.INSL.NCER | 2024-05-06 | 2024-04-29 | 2025-04-22 | On-Time |  | 2025-04-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300567 | T2 DI DRUM-RIO OSO #1 29/211 RPR INSS | ICS
LC | 128717688 | 037/004 | T2 DI MNDCNO-WLTS-FRT BRG 37/4 RMV VEG | WILLITS | ETL.7550.POLE.WOOD | 2024-05-06 | 2024-04-29 | 2024-11-19 | On-Time |  | 2024-07-29 | 2025-04-29 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128768428 | 027/002 | T2 DI GRBRVLLE-LYTNVLLE 27/02 RPL STRW | WILLITS | ETL.8365.POLE.WOOD | 2024-05-13 | 2024-04-29 | 2025-04-17 | On-Time |  | 2025-04-29 | 2025-04-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574341 | T2 DI GRBRVLLE-LYTNVLLE 27/02 RPL STRW | 70Y
LC | 128768500 | 027/217 | T2 PIT #1-COTTONWOOD 27/217 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-05-13 | 2024-04-29 | 2025-04-14 | On-Time |  | 2025-04-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381516 | T2 DI PIT #1-COTTONWOOD 27/217 RPR FOND | ICQ
LC | 128779743 | 054/488 | T2 DI PIT #1-CTTNWD 54/488 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2024-05-15 | 2024-04-29 | 2025-03-27 | On-Time |  | 2025-04-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381522 | T2 DI PIT #1-CTTNWD 54/488 BNT STEEL | ICQ
LC | 128779815 | 051/363 | T2 DI CARIBOU-TABLE MTN 51/363 RPL INSS | TABLEMTN | ETL.4440.INSL.CERA | 2024-05-15 | 2024-04-29 | 2025-04-08 | On-Time |  | 2025-04-29 | 2025-04-29 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569572 | T2 DI CARIBOU-TBL MTN RPL INSS | 93K
LC | 128779950 | 028/003 | T2 DI GRBRVL-LYTNVL 28/3 RPL ANCW | WILLITS | ETL.8365.POLE.WOOD | 2024-05-15 | 2024-04-29 | 2025-04-17 | On-Time |  | 2025-04-29 | 2025-04-29 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574342 | T2 DI GRBRVL-LYTNVL 28/3 RPL ANCW | 93E
LC | 128780154 | 005/050 | T2 DI HLSDL JCT-HLF MN BY 5/50L RPR GYWW | METCALF | ETL.7060.POLE.STPS | 2024-05-15 | 2024-04-29 | 2024-06-12 | On-Time |  | 2024-07-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46251986 | T2 DI HLSDL JCT-HLF MN BY 5/50L RPR GYWW | ICW
LC | 128780157 | 005/050 | T2 DI HLSDL JCT-HLF MN BY 5/50 RPR INSW | METCALF | ETL.7060.INSL.NCER | 2024-05-15 | 2024-04-29 | 2025-02-27 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46286793 | T2 DI HLSDL JCT-HLF MN BY 5/50 RPR INSW | ICW
LC | 128780237 | 004/029 | T2 DI SOBRANTE-"R" #1+ 04/29 RPL HRDT | CONCORD | ETL.3770.TOWR | 2024-05-15 | 2024-04-29 | 2025-03-06 | On-Time |  | 2025-04-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Hardware-Tower | Replace | 46287408 | T2 DI SOBRANTE-"R" #1+ 04/29 RPL HRDT | ICQ
LC | 128799931 | 018/004 | T2 DI MNDCNO-WLTS-FRT BRGG 18/4 RPR INSW | WILLITS | ETL.7550.INSL.NCER | 2024-05-17 | 2024-04-29 | 2025-04-09 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310131 | T2 DI MNDCNO-WLTS-FRT BRGG 18/4 RPR INSW | ICW
LC | 128800621 | 014/105A | T2 DI HELMS-GREGG #1 14/105A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-17 | 2024-04-29 | 2025-03-26 | On-Time |  | 2025-04-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298115 | T2 DI HELMS-GREGG #1 14/105A RPR SHLS | ICS
LC | 128800623 | 033/228B | T2 DI TRINITY COTTONWD 33/228B RPR ANCW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-05-17 | 2024-04-29 | 2024-07-19 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46251385 | T2 DI TRINITY COTTONWD 33/228B RPR ANCW | ICW
LC | 128800629 | 033/228C | T2 DI TRINITY COTTONWD 33/228C RPR ANCW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-05-17 | 2024-04-29 | 2024-07-19 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46251386 | T2 DI TRINITY COTTONWD 33/228C RPR ANCW | ICW
LC | 128800637 | 004/030 | T2 DI SOBRANTE-""R""#1+" 4/30 RPL HRDT | CONCORD | ETL.3770.TOWR | 2024-05-17 | 2024-04-29 | 2025-03-05 | On-Time |  | 2025-04-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Hardware-Tower | Replace | 46287410 | T2 DI SOBRANTE-""R""#1+" 4/30 RPL HRDT | ICQ
LC | 128800656 | 033/228A | T2 DI TRINITY COTTONWD 33/228A RPR ANCW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-05-17 | 2024-04-29 | 2024-07-19 | On-Time |  | 2025-04-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46251384 | T2 DI TRINITY COTTONWD 33/228A RPR ANCW | ICW
LC | 128800921 | 014/102A | T2 DI HELMS-GREG #1 14/102A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-17 | 2024-04-29 | 2025-03-26 | On-Time |  | 2025-04-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298116 | T2 DI HELMS-GREG #1 14/102A RPR SHLS | ICS
LC | 128818874 | A000/001 | T2 DI KM GREEN TP A0/1 RPR INSS | VICTOR | ETL.3505.INSL.NCER | 2024-05-20 | 2024-04-29 | 2025-05-30 | Past Due |  | 2025-04-29 | 2025-04-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46325934 | T2 DI KM GREEN TP A0/1 RPR INSS | ICS
LC | 128819373 | 053/480 | T2 PIT #1-CTTONWOOD 53/480 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-05-20 | 2024-04-29 | 2024-04-29 | Past Due |  | 2025-04-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46381531 | T2NT DI PIT #1-CTTONWOOD 53/480 RPR STRT | ICQ
LC | 128819375 | 012/002 | T2 DI FULTON-HOPLAND-12/02 RMV VEG | LAKEVLLE | ETL.6890.POLE.NWOD | 2024-05-20 | 2024-04-29 | 2025-04-26 | On-Time |  | 2025-04-29 | 2025-04-29 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128819395 | 026/196 | T2 DI DRM-RI OSO #1-TWR 26/196 TOUCH | SACTO | ETL.1420.TOWR | 2024-05-20 | 2024-04-29 | 2025-02-19 | On-Time |  | 2024-10-29 | 2025-04-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46463294 | T2 DI DRM-RI OSO #1-TWR 26/196 RPR STRT | ICQ
LC | 128819484 | 029/001 | T2 DI GRBERVLE LYTNVLE 29/1 RPL STRW | WILLITS | ETL.8365.POLE.WOOD | 2024-05-20 | 2024-04-29 | 2025-04-22 | On-Time |  | 2025-04-29 | 2025-04-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574343 | T2 DI GRBERVLE LYTNVLE 29/1 RPL STRW | 70Y
LC | 128819520 | 031/004 | T2 DI FULTON-HOPLAND 31/04 RPL STRW | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-05-20 | 2024-04-29 | 2025-03-20 | On-Time |  | 2025-04-29 | 2025-04-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574258 | T2 DI FULTON-HOPLAND 31/04 RPL STRW | 70Y
LC | 128896592 | 005/050 | T2 DI HLSDL JCT-HLF MN BY 5/50R RPR GYWW | METCALF | ETL.7060.POLE.STPS | 2024-05-28 | 2024-04-29 | 2024-06-12 | On-Time |  | 2024-07-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46254816 | T2 DI HLSDL JCT-HLF MN BY 5/50R RPR GYWW | ICW
LC | 128896596 | 005/050 | T2 DI HLSDL JCT-HLF MN BY 5/50C RPR GYWW | METCALF | ETL.7060.POLE.STPS | 2024-05-28 | 2024-04-29 | 2024-06-12 | On-Time |  | 2024-07-29 | 2025-04-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46254815 | T2 DI HLSDL JCT-HLF MN BY 5/50C RPR GYWW | ICW
LC | 123468786 | 021/170 | T2NT EI CRBRY SS-RND MTN 21/170 RPL INSS | TABLEMTN | ETL.5410.INSL | 2022-04-30 | 2022-04-30 | 2023-09-16 | On-Time |  | 2025-04-30 | 2025-04-30 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO NTDE | No Good/Out of Stdrd | Insulator-Steel | Replace | 31639948 | T2NT EI CRBRY SS-RND MTN 24/193 RPL INSS | 93K
LC | 128682654 | 014/003 | T2 EI DUNLAP TAP 14/3 RPR GYWW | FRESNO | ETL.9061.POLE.NWOD | 2024-04-30 | 2024-04-30 | 2025-03-21 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46298161 | T2 EI DUNLAP TAP 14/3 RPR GYWW | ICW
LC | 128683282 | 017/102 | T2 EI STNSLS-MNTC #2 17/102 BNT STEEL | VICTOR | ETL.3820.TOWR | 2024-04-30 | 2024-04-30 | 2025-04-09 | On-Time |  | 2025-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46401502 | T2 EI STNSLS-MNTC #2 17/102 BNT STEEL | ICQ
LC | 128683284 | 017/102 | T2 STNSLS-MNTC #2 17/102 UNBURY | VICTOR | ETL.3820.TOWR | 2024-04-30 | 2024-04-30 | 2025-04-09 | On-Time |  | 2025-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46401077 | T2 EI STNSLS-MNTC #2 17/102 UNBURY | ICQ
LC | 128684145 | 016/228 | T2 EI SSQUOC-SNTA YNZ SS 16/228 RPL INSW | PISMOBCH | ETL.3700.INSL.NCER | 2024-04-30 | 2024-04-30 | 2025-04-04 | On-Time |  | 2025-04-30 | 2025-04-30 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573794 | T2 EI SSQUOC-SNTA YNZ SS 16/228 RPL INSW | 93I
LC | 128684224 | 005/088C | T2 EI DELTA-MTN GATE JCT 5/88C RPR GYWW | TABLEMTN | ETL.6750.POLE.NWOD | 2024-04-30 | 2024-04-30 | 2025-04-09 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46453114 | T2 EI DELTA-MTN GATE JCT 5/88C RPR GYWW | ICW
LC | 128684479 | 006/001 | T2 EI VLY SPRNGS-CLVRS CMNT 6/1 RPR STRW | VICTOR | ETL.8220.POLE.WOOD | 2024-04-30 | 2024-04-30 | 2025-03-08 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46326992 | T2 EI VLY SPRNGS-CLVRS CMNT 6/1 RPR POLE | ICW
LC | 128684866 | 017/099 | T2 EI STNSLS-MANTECA #2 17/099 MASTIC | VICTOR | ETL.3820.TOWR | 2024-04-30 | 2024-04-30 | 2025-03-25 | On-Time |  | 2025-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416593 | T2 EI STNSLS-MANTECA #2 17/099 MASTIC | ICQ
LC | 128684869 | 017/098 | T2 EI STANSLS-MANTECA #2 17/98 COMPLETE | VICTOR | ETL.3820.TOWR | 2024-04-30 | 2024-04-30 | 2025-03-25 | On-Time |  | 2025-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416595 | T2 EI STANSLS-MANTECA #2 17/98 RPR FOND | ICQ
LC | 128684880 | 017/100 | T2 EI STANISLS-MNTCA #2 17/100 COMPLETE | VICTOR | ETL.3820.TOWR | 2024-04-30 | 2024-04-30 | 2025-03-25 | On-Time |  | 2025-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416596 | T2 EI STANISLAUS-MANTCA #2 17/100 UNBURY | ICQ
LC | 128684881 | 017/100 | T2 EI STANISLAS-MNTC #2 17/100 COMPLETE | VICTOR | ETL.3820.TOWR | 2024-04-30 | 2024-04-30 | 2025-03-25 | On-Time |  | 2025-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416597 | T2 EI STANISLAS-MNTC #2 17/100 BNT STEEL | ICQ
LC | 128684887 | 017/099 | T2 EI STNSLS-MANTECA #2 17/099 COMPLETE | VICTOR | ETL.3820.TOWR | 2024-04-30 | 2024-04-30 | 2025-03-25 | On-Time |  | 2025-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416598 | T2 EI STNSLS-MANTECA #2 17/099 BNT STEEL | ICQ
LC | 128684890 | 017/099 | T2 EI STNSLS-MANTECA #2 17/099 COMPLETE | VICTOR | ETL.3820.TOWR | 2024-04-30 | 2024-04-30 | 2025-03-18 | On-Time |  | 2025-04-30 | 2025-04-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46325923 | T2 EI STNSLS-MANTECA #2 17/099 RMV NEST | ICS
LC | 128684899 | 016/097 | T2 EI STANSLS-MANTECA #2 16/97 COMPLETE | VICTOR | ETL.3820.TOWR | 2024-04-30 | 2024-04-30 | 2025-03-25 | On-Time |  | 2025-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416599 | T2 EI STANSLS-MANTECA #2 16/97 RPR FOND | ICQ
LC | 128685138 | 005/089 | T2 EI DELTA-MTN GATE JCT 5/89 RPL DMPW | TABLEMTN | ETL.6750.INSL.NCER | 2024-04-30 | 2024-04-30 | 2024-12-12 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Damper-Wood | Replace | 46247578 | T2 EI DELTA-MTN GATE JCT 5/89 RPL DMPW | ICW
LC | 128685184 | 016/230 | T2 EI SSQUOC-SNTA YNZ SS 16/230 RPR STRW | PISMOBCH | ETL.3700.POLE.WOOD | 2024-04-30 | 2024-04-30 | 2025-04-04 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46338924 | T2 EI SSQUOC-SNTA YNZ SS 16/230 RPR STRW | ICW
LC | 128686183 | 018/167 | T2 UKIAH-HPLAND-CLVRDLE 18/167 COTTER | WILLITS | ETL.4050.INSL.NCER | 2024-04-30 | 2024-04-30 | 2025-06-20 | Past Due |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46446649 | T2 EI UKIAH-HPLAND-CLVRDLE 18/167 COTTER | ICW
LC | 128688167 | 011/070 | T2 EI STNLS-MLS SW ST-MN 11/070 RPR STRT | VICTOR | ETL.3830.TOWR | 2024-04-30 | 2024-04-30 | 2025-03-29 | On-Time |  | 2025-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416601 | T2 EI STNLS-MLS SW ST-MN 11/070 RPR STRT | ICQ
LC | 128688262 | 028/006 | T2NT EI TRINITY-MAPLE CRK 28/6 RMV STEPS | EUREKA | ETL.8170.POLE.NWOD | 2024-04-30 | 2024-04-30 | 2025-05-08 | Past Due |  | 2027-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 46345793 | T2NT EI TRINITY-MAPLE CRK 28/6 RMV STEPS | ICW
LC | 128688271 | 029/005 | T2 EI TRINITY-MAPLE CREEK 29/5 RPL SPLW | EUREKA | ETL.8170.INSL.NCER | 2024-04-30 | 2024-04-30 | 2025-04-14 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Splice-Wood | Replace | 46345794 | T2 EI TRINITY-MAPLE CREEK 29/5 RPL SPLW | ICW
LC | 128688341 | :011/005 | T2 EI BLLT-RVBNK-MLNS S S :11/5 RPR STRW | VICTOR | ETL.1070.POLE.WOOD | 2024-04-30 | 2024-04-30 | 2024-05-28 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46251912 | T2 EI BLLT-RVBNK-MLNS S S :11/5 RPR STRW | ICW
LC | 128690514 | 001/011 | T2 EI DIVIDE-VANDNBRG #1 1/011R RPR GYWW | PISMOBCH | ETL.8620.POLE.STPS | 2024-05-01 | 2024-04-30 | 2024-07-19 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46282761 | T2 EI DIVIDE-VANDNBRG #1 1/011R RPR GYWW | ICW
LC | 128690515 | 001/011 | T2 EI DVIDE-VANDNBERG #1 1/011L RPR GYWW | PISMOBCH | ETL.8620.POLE.STPS | 2024-05-01 | 2024-04-30 | 2024-07-19 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46282760 | T2 EI DVIDE-VANDNBERG #1 1/011L RPR GYWW | ICW
LC | 128690912 | 001/011 | T2 EI DVDE-VANDENBERG #1 1/011C RPR GYWW | PISMOBCH | ETL.8620.POLE.STPS | 2024-05-01 | 2024-04-30 | 2024-07-19 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46281679 | T2 EI DVDE-VANDENBERG #1 1/011C RPR GYWW | ICW
LC | 128695825 | 014/212 | T2 EI SSQUOC-SNTA YNZ SS 14/212 RPR WDPK | PISMOBCH | ETL.3700.POLE.WOOD | 2024-05-01 | 2024-04-30 | 2025-04-04 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46391103 | T2 EI SSQUOC-SNTA YNZ SS 14/212 RPR WDPK | ICW
LC | 128698597 | 007/003 | T2 MENDCNO-WLLTS-FORT BRAGG 7/3 RPL INSW | WILLITS | ETL.7550.INSL.CERA | 2024-05-01 | 2024-04-30 | 2025-04-15 | On-Time |  | 2025-04-30 | 2025-04-30 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574193 | T2 DI MNDCNO-WLLTS-FRT BRG 7/3 RPL INSW | 93I
LC | 128708255 | 000/002 | T2 DI SMRTVIL-NICOLAUS #2 0/2 RPR ANCW | SACTO | ETL.8000.POLE.NWOD | 2024-05-03 | 2024-04-30 | 2025-02-21 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46310362 | T2 DI SMRTVIL-NICOLAUS #2 0/2 RPR ANCW | ICW
LC | 128716747 | 007/002 | T2 DI MNDCN WLTS FRT BRG 7/2 RPL STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-06 | 2024-04-30 | 2025-04-03 | On-Time |  | 2025-04-30 | 2025-04-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574192 | T2 DI MNDCN WLTS FRT BRG 7/2 RPL STRW | 70Y
LC | 128716749 | 023/002 | T2 DI GRBERVL LYTNVL 23/2 COMPLETE | WILLITS | ETL.8365.POLE.WOOD | 2024-05-06 | 2024-04-30 | 2024-08-13 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46252698 | T2 DI GRBERVL LYTNVL 23/2 RPR GYWW | ICW
LC | 128716801 | 025/187 | T2 DI DRUM-RIO OSO #1 25/187 TOUCH | SACTO | ETL.1420.TOWR | 2024-05-06 | 2024-04-30 | 2025-02-19 | On-Time |  | 2024-07-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46463288 | T2 DI DRUM-RIO OSO #1 25/187 RPR STRT | ICQ
LC | 128716802 | 75 | T3 DI DESABLA-CENTERVILLE 0/1B RPR JUMW | TABLEMTN | ETL.6720.SWIT | 2024-05-06 | 2024-04-30 | 2024-11-15 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46250406 | T3 DI DESABLA-CENTERVILLE 0/1B RPR JUMW | ICW
LC | 128716849 | 017/397 | T2 DI DRM GRS VLY WIMR 17/397 RMV VEG | SACTO | ETL.6760.POLE.WOOD | 2024-05-06 | 2024-04-30 | 2025-05-17 | Past Due |  | 2025-04-30 | 2025-04-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128716856 | 031/002 | T2 DI GRBRBLLE-LYTNVLLE 31/02R COTTER | WILLITS | ETL.8365.POLE.STPS | 2024-05-06 | 2024-04-30 | 2025-02-06 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446652 | T2 DI GRBRBLLE-LYTNVLLE 31/02R COTTER | ICW
LC | 128716944 | 007/006 | T2 DI MNDCN-WLTS-FRT BRG 7/6 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-06 | 2024-04-30 | 2025-01-21 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310136 | T2 DI MNDCN-WLTS-FRT BRG 7/6 RPR GYWW | ICW
LC | 128716978 | 052/468 | T2 DI PIT #1 CTTNWD 52/468 COTTER | TABLEMTN | ETL.5390.TOWR | 2024-05-06 | 2024-04-30 | 2025-03-27 | On-Time |  | 2025-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46491553 | T2 DI PIT #1 CTTNWD 52/468 COTTER | ICQ
LC | 128769002 | 044/382 | T2 DI PIT #1-COTTONWOOD 044/382 UNBURY | TABLEMTN | ETL.5390.TOWR | 2024-05-13 | 2024-04-30 | 2025-04-21 | On-Time |  | 2025-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381518 | T2 DI PIT #1-COTTONWOOD 044/382 UNBURY | ICQ
LC | 128777721 | 039/000 | T2 FULTON-HOPLAND 39/0 RPR POLE | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-05-15 | 2024-04-30 | 2025-03-27 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46305938 | T2 FULTON-HOPLAND 39/0 RPR POLE | ICW
LC | 128800126 | 017/400 | T2 DI DRM GRS VLY WMR 17/400 RPL INSW | SACTO | ETL.6760.INSL.NCER | 2024-05-17 | 2024-04-30 | 2025-04-22 | On-Time |  | 2025-04-30 | 2025-04-30 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573449 | T2 DI DRM GRS VLY WMR 17/400 RPL INSW | 93I
LC | 128800220 | 017/401 | T2 DI DRM GRS VLY WMR 17/401 RPR GYWW | SACTO | ETL.6760.POLE.WOOD | 2024-05-17 | 2024-04-30 | 2025-04-22 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324604 | T2 DI DRM GRS VLY WMR 17/401 RPR GYWW | ICW
LC | 128800318 | 035/009 | T2 DI FULTON-HOPLAND 35/009 RPL ANCW | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-05-17 | 2024-04-30 | 2025-03-19 | On-Time |  | 2025-04-30 | 2025-04-30 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574260 | T2 DI FULTON-HOPLAND 35/009 RPL ANCW | 93E
LC | 128800327 | 035/009 | T2 DI FULTON-HOPLAND 35/009 RPR POLE | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-05-17 | 2024-04-30 | 2025-03-19 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46305937 | T2 DI FULTON-HOPLAND 35/009 RPR POLE | ICW
LC | 128800440 | 000/006 | T3 DI DSABLA-CNTRVILE 0/6 RPR STRW | TABLEMTN | ETL.6720.POLE.WOOD | 2024-05-17 | 2024-04-30 | 2024-11-14 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46250290 | T3 DI DSABLA-CNTRVILE 0/6 RPR STRW | ICW
LC | 128811803 | 052/466 | T2 DI PIT #1-COTTONWOOD 52/466 RMV NEST | TABLEMTN | ETL.5390.TOWR | 2024-05-20 | 2024-04-30 | 2025-04-24 | On-Time |  | 2025-04-30 | 2025-04-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46452722 | T2 DI PIT #1-COTTONWOOD 52/466 RMV NEST | ICS
LC | 128818636 | 004/005 | T2 DI POTTER VALY-MNDO 04/05 UNBURY | WILLITS | ETL.7810.POLE.NWOD | 2024-05-20 | 2024-04-30 | 2025-03-24 | On-Time |  | 2025-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46446644 | T2 DI POTTER VALY-MNDO 04/05 UNBURY | ICS
LC | 128818727 | 046/399 | T2NT DI PIT#1 COTTONWOOD 46/399 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-05-20 | 2024-04-30 | 2025-03-27 | On-Time |  | 2027-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381526 | T2NT DI PIT#1 COTTONWOOD 46/399 RPR STRT | ICQ
LC | 128818880 | 004/005 | T2 DI POTTER VALY-MNDO 04/05 RMV NEST | WILLITS | ETL.7810.POLE.NWOD | 2024-05-20 | 2024-04-30 | 2025-04-15 | On-Time |  | 2025-04-30 | 2025-04-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46446645 | T2 DI POTTER VALY-MNDO 04/05 RMV NEST | ICS
LC | 128819150 | 052/462 | T2 DI PIT #1-COTTONWOOD 52/462 RPL HRDT | TABLEMTN | ETL.5390.TOWR | 2024-05-20 | 2024-04-30 | 2025-01-08 | On-Time |  | 2025-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381529 | T2 DI PIT #1-COTTONWOOD 52/462 RPL HRDT | ICQ
LC | 128819193 | 004/038 | T2 DI CRG VIEW-CSCD 004/038C RMV VEG | TABLEMTN | ETL.1350.POLE.STPS | 2024-05-20 | 2024-04-30 | 2024-10-31 | On-Time |  | 2025-04-30 | 2025-04-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128819319 | 031/003 | T2 DI GRBRVIL-LAYTNVIL 31/03 RPL ANCW | WILLITS | ETL.8365.POLE.WOOD | 2024-05-20 | 2024-04-30 | 2025-04-17 | On-Time |  | 2025-04-30 | 2025-04-30 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574344 | T2 DI GRBRVIL-LAYTNVIL 31/03 RPL ANCW | 93E
LC | 128819524 | 029/017 | T2 DI FULTON-HOPLAND 29/17 RPL STRW | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-05-20 | 2024-04-30 | 2025-03-20 | On-Time |  | 2025-04-30 | 2025-04-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574256 | T2 DI FULTON-HOPLAND 29/17 RPL STRW | 70Y
LC | 128837083 | 000/003 | T2 DI MORAGA CASGRO VLY 0/3 RPR OPGW | CONCORD | ETL.5250.TOWR | 2024-05-21 | 2024-04-30 | 2025-04-02 | On-Time |  | 2025-04-30 | 2025-04-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46287414 | T2 DI MORAGA CASGRO VLY 0/3 RPR OPGW | ICS
LC | 128837088 | 000/003 | T2 MORAGA CASGRO VLY 0/3 RPL INSS | CONCORD | ETL.5250.INSL | 2024-05-21 | 2024-04-30 | 2024-04-30 | Past Due |  | 2025-04-30 | 2025-04-30 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575287 | T2 DI MRGA CSTRO VLY RPL INSS IN 2 TWRS. | 93K
LC | 128837102 | 022/095 | T2 DI SAN RMN MORAGA 22/95 RPL INSS | CONCORD | ETL.5660.INSL | 2024-05-21 | 2024-04-30 | 2025-03-02 | On-Time |  | 2025-04-30 | 2025-04-30 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577339 | T2 DI SAN RMN MORAGA 22/95 RPL INSS | 93K
LC | 128837211 | 012/000 | T2 DI MENDOCINO-WFB 12/0 RPR STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-21 | 2024-04-30 | 2025-04-14 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310137 | T2 DI MENDOCINO-WFB 12/0 RPR STRW | ICW
LC | 128837281 | 022/015 | T2 DI GARBERVILLE-LYT 22/15 RPR JUMS | WILLITS | ETL.8365.INSL.NCER | 2024-05-21 | 2024-04-30 | 2025-04-16 | On-Time |  | 2025-04-30 | 2025-04-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46446650 | T2 DI GARBERVILLE-LYT 22/15 RPR JUMS | ICS
LC | 128887434 | 052/373 | T2 DI CARIBOU TBL MTN 52/373 COTTER | TABLEMTN | ETL.4440.INSL.NCER | 2024-05-24 | 2024-04-30 | 2025-04-03 | On-Time |  | 2025-04-30 | 2025-04-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46337336 | T2 DI CARIBOU TBL MTN 52/373 COTTER | ICS
LC | 128888287 | 003/034A | T2 DI CRAG VIEW-CASCAD 03/34A COTTER | TABLEMTN | ETL.1350.INSL.NCER | 2024-05-24 | 2024-04-30 | 2025-01-17 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46396446 | T2 DI CRAG VIEW-CASCAD 03/34A COTTER | ICW
LC | 128888363 | 003/034C | T2 DI CRAG VIEW-CASCAD 03/34C COTTER | TABLEMTN | ETL.1350.INSL.NCER | 2024-05-24 | 2024-04-30 | 2025-01-17 | On-Time |  | 2025-04-30 | 2025-04-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46396447 | T2 DI CRAG VIEW-CASCAD 03/34C COTTER | ICW
LC | 128888375 | 046/396 | T2 DI ROUND MT-COTT 46/396 RMV VEG | TABLEMTN | ETL.5650.TOWR | 2024-05-24 | 2024-04-30 | 2024-11-20 | On-Time |  | 2025-04-30 | 2025-04-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128897007 | 044/379 | T2 DI PIT #1-COTTONWOOD 44/379 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-05-28 | 2024-04-30 | 2025-04-21 | On-Time |  | 2025-04-30 | 2025-04-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381539 | T2 DI PIT #1-COTTONWOOD 44/379 BNT STEEL | ICQ
LC | 127395433 | 004/006 | T2 MENDOCINO-HARTLEY 004/006 RPR SPLW | WILLITS | ETL.7510.INSL.NCER | 2023-11-01 | 2023-11-01 | 2023-11-01 | Past Due |  | 2025-05-01 | 2025-05-01 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH FMOB XMPT TR2 PRTO AIR FRAB NTDE | Missing | Damper-Wood | Install | 46171423 | T2 DI MENDOCINO-HARTLEY 004/006 RPR SPLW | ICW
LC | 128690902 | 004/030 | T2 EI MORAGA-OAKLAND #1 4/30 TOUCH | CONCORD | ETL.2720.TOWR | 2024-05-01 | 2024-05-01 | 2024-05-01 | Past Due |  | 2024-11-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAR NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485714 | T2 EI MORAGA-OAKLAND #1 4/30 TOUCH | ICQ
LC | 128691539 | 016/095 | T2 EI STANSLS-MANTECA #2 16/95 RPR STRT | VICTOR | ETL.3820.TOWR | 2024-05-01 | 2024-05-01 | 2025-04-09 | On-Time |  | 2025-05-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416602 | T2 EI STANSLS-MANTECA #2 16/95 RPR STRT | ICQ
LC | 128691610 | 016/095 | T2 EI STANSLS-MANTECA #2 16/95 COTTER | VICTOR | ETL.3820.INSL.NCER | 2024-05-01 | 2024-05-01 | 2024-09-08 | On-Time |  | 2024-08-01 | 2025-05-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46263073 | T2 EI STANSLS-MANTECA #2 16/95 COTTER | ICS
LC | 128691705 | 016/100 | T2 EI SS-MLS SS-MTC #1 16/100 RPL DAMW | VICTOR | ETL.3830.INSL.CERA | 2024-05-01 | 2024-05-01 | 2025-04-14 | On-Time |  | 2025-05-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46325925 | T2 EI SS-MLS SS-MTC #1 16/100 RPL DAMW | ICW
LC | 128691760 | 025/107 | T2 EI LOS ESTEROS-METCLF 25/107 RPL INSS | METCALF | ETL.5353.INSL | 2024-05-01 | 2024-05-01 | 2025-03-28 | On-Time |  | 2025-05-01 | 2025-05-01 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574629 | T2 EI LOS ESTEROS-METCALF RPL INSS IN 7 | 93K
LC | 128692260 | 016/096 | T2 EI STANSLS-MANTECA #2 16/96 RPR FOND | VICTOR | ETL.3820.TOWR | 2024-05-01 | 2024-05-01 | 2025-04-09 | On-Time |  | 2025-05-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416604 | T2 EI STANSLS-MANTECA #2 16/96 RPR FOND | ICQ
LC | 128692337 | 000/004 | T2 SOBRANTE-STND OIL SS #1 0/4 RPR STRT | CONCORD | ETL.3800.TOWR | 2024-05-01 | 2024-05-01 | 2025-03-10 | On-Time |  | 2025-05-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46287416 | T2 SOBRANTE-STND OIL SS #1 3/17 RPR STRT | ICQ
LC | 128693016 | 008/054 | T2 VALLY SPRNGS-BLLTA 08/054 RPL INSS | VICTOR | ETL.5860.INSL.CERA | 2024-05-01 | 2024-05-01 | 2025-03-26 | On-Time |  | 2025-05-01 | 2025-05-01 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593222 | T2 EI VLY SPRNGS-BELLTA 04/28 RPL INSS | 93K
LC | 128693111 | 016/120 | T2 ELECTRA-BELLOTA 16/120 RPL INSS | VICTOR | ETL.4670.INSL | 2024-05-01 | 2024-05-01 | 2025-03-20 | On-Time |  | 2025-05-01 | 2025-05-01 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593221 | T2 EI ELECTRA-BELLOTA 002/024 RPL INSS | 93K
LC | 128693200 | 016/120 | T2 ELECTRA-BELLOTA 16/120 TOUCH | VICTOR | ETL.4670.TOWR | 2024-05-01 | 2024-05-01 | 2025-01-14 | On-Time |  | 2024-11-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46473020 | T2 ELECTRA-BELLOTA 16/120 TOUCH | ICQ
LC | 128693204 | 013/107 | T2 EI TGR CRK-VLY SPRNGS 13/107 RPR FOND | VICTOR | ETL.5790.TOWR | 2024-05-01 | 2024-05-01 | 2025-03-17 | On-Time |  | 2025-05-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416605 | T2 EI TGR CRK-VLY SPRNGS 13/107 RPR FOND | ICQ
LC | 128693260 | 024/104 | T2 EI LOS ESTEROS-METCLF 24/104 RPL INSS | METCALF | ETL.5353.INSL | 2024-05-01 | 2024-05-01 | 2025-03-28 | On-Time |  | 2025-05-01 | 2025-05-01 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574629 | T2 EI LOS ESTEROS-METCALF RPL INSS IN 7 | 93K
LC | 128693273 | 011/007 | T2 OAKHURST TAP 11/007 RMV ENCR | FRESNO | ETL.1252.POLE.NWOD | 2024-05-01 | 2024-05-01 | 2024-08-21 | On-Time |  | 2024-11-01 | 2025-05-01 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | Encroachment | Right of Way | Remove | 46265365 | T2 OAKHURST TAP 11/007 RMV FNCE | CHR
LC | 128693436 | 003/071 | T2 EI CLMN-CTTNWD 3/71 RPL STRW | TABLEMTN | ETL.6430.POLE.WOOD | 2024-05-01 | 2024-05-01 | 2025-03-28 | On-Time |  | 2025-05-01 | 2025-05-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35556139 | T2 EI CLMN-CTTNWD 3/71 RPL STRW | 70Y
LC | 128693558 | 013/105 | T2 TIGER CRK-VLLY SPRNGS 13/105 RPR STRT | VICTOR | ETL.5790.TOWR | 2024-05-01 | 2024-05-01 | 2025-04-07 | On-Time |  | 2025-05-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416606 | T2 EI TGR CRK-VLY SPRNGS 13/105 RPR STRT | ICQ
LC | 128693580 | 014/066 | T2 LOS ESTRS-MTCLF 14/66 TOUCH | METCALF | ETL.5353.TOWR | 2024-05-01 | 2024-05-01 | 2025-04-24 | On-Time |  | 2024-11-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485644 | T2 LOS ESTRS-MTCLF 14/66 TOUCH | ICQ
LC | 128693604 | 065/582 | T2 EI CTTNWD-DELEVAN #2 65/582 RPR INSS | TABLEMTN | ETL.4580.INSL.NCER | 2024-05-01 | 2024-05-01 | 2025-02-24 | On-Time |  | 2025-05-01 | 2025-05-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46452479 | T2 EI CTTNWD-DELEVAN #2 65/582 RPR INSS | ICS
LC | 128693650 | 000/013 | T2 SBRANTE-GRIZZLY-CLMT #1 0/13 TOUCH | CONCORD | ETL.3740.TOWR | 2024-05-01 | 2024-05-01 | 2025-05-01 | On-Time |  | 2024-11-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485640 | T2 SBRANTE-GRIZZLY-CLMT #1 0/13 TOUCH | ICQ
LC | 128696923 | 003/032 | T2 EI PIT #3-CRBERY SW STA 3/32 RPR INSS | TABLEMTN | ETL.5450.INSL.NCER | 2024-05-01 | 2024-05-01 | 2025-04-29 | On-Time |  | 2025-05-01 | 2025-05-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46416192 | T2 EI PIT #3-CRBERY SW STA 3/32 RPR INSS | ICS
LC | 128697108 | 009/001 | T2 CARIBOU-PLUMAS JCT 9/1 RPR INSS | TABLEMTN | ETL.6290.INSL.CERA | 2024-05-01 | 2024-05-01 | 2025-04-29 | On-Time |  | 2025-05-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46397981 | T2 CARIBOU-PLUMAS JCT 9/1 RPR INSS | ICW
LC | 128697162 | 005/035 | T2 KRCKHFF-CLVS-SNGR #1 05/35 RMV ENCR | FRESNO | ETL.1890.TOWR | 2024-05-01 | 2024-05-01 | 2024-09-24 | On-Time |  | 2024-11-01 | 2025-05-01 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | Encroachment | Right of Way | Remove | 46254521 | T2 KRCKHFF-CLVS-SNGR #1 05/35 RMV ENCR | CHR
LC | 128697622 | 027/011 | T2 PHILO JCT-ELK 27/011 GO95 | WILLITS | ETL.7780.POLE.WOOD | 2024-05-01 | 2024-05-01 | 2025-04-27 | On-Time |  | 2025-05-01 | 2025-05-01 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35555897 | T2 PHILO JCT-ELK 27/011 GO95 | 93G
LC | 128697663 | 016/122 | T2 EI CARIBOU-TABLE MTN 016/122 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2024-05-01 | 2024-05-01 | 2025-03-11 | On-Time |  | 2025-05-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | Missing | Hardware-Tower | Install | 46354021 | T2 EI CARIBOU-TABLE MTN 016/122 RPL HRDT | ICQ
LC | 128697671 | 005/024 | T2 DI MRRO BY SLR SS #1 5/24 RPL INSS | PISMOBCH | ETL.5300.INSL | 2024-05-01 | 2024-05-01 | 2025-04-10 | On-Time |  | 2025-05-01 | 2025-05-01 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35583345 | T0 EI MORRO BAY-SOLAR SS#1 REP INS 6 LST | 93K
LC | 128697674 | 005/024 | T2 DI MRRO BY SLR SS #2 5/24 RPL INSS | PISMOBCH | ETL.5310.INSL | 2024-05-01 | 2024-05-01 | 2025-05-03 | Past Due |  | 2025-05-01 | 2025-05-01 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577375 | T0 EI MORRO BAY-SOLAR SS#2 42/180 RPLC I | 93K
LC | 128697680 | 016/122 | T2 EI CARIBOU-TABLE MTN 016/122 RPR GYWT | TABLEMTN | ETL.4440.TOWR | 2024-05-01 | 2024-05-01 | 2025-03-11 | On-Time |  | 2025-05-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46354022 | T2 EI CARIBOU-TABLE MTN 016/122 RPR GYWT | ICQ
LC | 128697882 | 009/002A | T2 MELONES-CURTIS 09/002A RMV NEST | VICTOR | ETL.2390.POLE.NWOD | 2024-05-01 | 2024-05-01 | 2025-02-22 | On-Time |  | 2025-05-01 | 2025-05-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR REMT ACCM COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46325926 | T2 MELONES-CURTIS 09/002A RMV NEST | ICS
LC | 128698273 | 031/007 | T2 RIO DL JCT-BRDGVLE 31/7 RPL INSW | EUREKA | ETL.7850.INSL.NCER | 2024-05-01 | 2024-05-01 | 2024-05-01 | Past Due |  | 2025-05-01 | 2025-05-01 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573039 | T2 EI RIO DL JCT-BRDGVLE 31/7 RPL INSW | 93I
LC | 128698368 | 006/028 | T2 DI MORRO BAY-SWST#1 6/28 RPR INSS | PISMOBCH | ETL.5300.INSL | 2024-05-01 | 2024-05-01 | 2025-04-10 | On-Time |  | 2025-05-01 | 2025-05-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329540 | T2 DI MORRO BAY-SWST#1 6/28 RPR INSS | ICS
LC | 128698369 | :000/003 | T2 ROCK CREEK-POE_:000/003 RPR STRT | TABLEMTN | ETL.5630.TOWR | 2024-05-01 | 2024-05-01 | 2024-05-01 | Past Due |  | 2025-05-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381991 | T2 EI ROCK CREEK-POE_:000/003 RPR STRT | ICQ
LC | 128698371 | :000/003 | T2 ROCK CREEK-POE :000/003 RPL INSS | TABLEMTN | ETL.5630.INSL.CERA | 2024-05-01 | 2024-05-01 | 2025-04-25 | On-Time |  | 2025-05-01 | 2025-05-01 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO CLMB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35572041 | T2 ROCK CREEK-POE RPL INSS 5 TWRS | 93K
LC | 128698457 | 006/085C | T2 EI KESWICK-TRINITY 6/085C RMV VEG | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-01 | 2024-05-01 | 2024-11-06 | On-Time |  | 2025-05-01 | 2025-05-01 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128698475 | 006/088B | T2 EI KESWICK-TRINITY 6/088B RPR GYWW | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-01 | 2024-05-01 | 2025-04-24 | On-Time |  | 2025-05-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311270 | T2 EI KESWICK-TRINITY 6/088B RPR GYWW | ICW
LC | 128698479 | 025/003 | T2 EI MONTE RIO-FORT ROSS 25/3 REFRAME | LAKEVLLE | ETL.6979.POLE.WOOD | 2024-05-01 | 2024-05-01 | 2025-05-20 | Past Due |  | 2025-05-01 | 2025-05-01 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35574220 | T2 EI MONTE RIO-FORT ROSS 25/3 REFRAME | 93E
LC | 128698549 | 004/088 | T2 EI CORDELIA #1 TAP 004/088 RPR POLE | SACTO | ETL.8182.POLE.WOOD | 2024-05-01 | 2024-05-01 | 2025-04-25 | On-Time |  | 2025-05-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337394 | T2 EI CORDELIA #1 TAP 004/088 RPR POLE | ICW
LC | 128698566 | 032/001 | T2 DI GRBRVLE-LYTNVLE 32/1 COMPLETE | WILLITS | ETL.8365.INSL.NCER | 2024-05-01 | 2024-05-01 | 2024-08-09 | On-Time |  | 2025-05-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46246715 | T2 DI GRBRVLE-LYTNVLE 32/1 RPR JUMW | ICW
LC | 128698685 | 012/010 | T2 EI DUNLAP TAP 12/010 RPL STRW | FRESNO | ETL.9061.POLE.WOOD | 2024-05-01 | 2024-05-01 | 2025-03-21 | On-Time |  | 2025-05-01 | 2025-05-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573194 | T2 EI DUNLAP TAP 12/010 RPL STRW | 70Y
LC | 128698686 | 013/008 | T2 EI DUNLAP TAP 13/008 RMV VEG | FRESNO | ETL.9061.POLE.NWOD | 2024-05-01 | 2024-05-01 | 2024-05-08 | On-Time |  | 2025-05-01 | 2025-05-01 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128698791 | 013/007 | T2 EI DUNLAP TAP 13/007 RPL STRW | FRESNO | ETL.9061.POLE.WOOD | 2024-05-01 | 2024-05-01 | 2025-03-21 | On-Time |  | 2025-05-01 | 2025-05-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573196 | T2 EI DUNLAP TAP 13/007 RPL STRW | 70Y
LC | 128698836 | 059/241 | T2 EI DIABLO-GATES #1 59/241 INF ENG | PISMOBCH | ETL.5960.TOWR | 2024-05-01 | 2024-05-01 | 2025-04-03 | On-Time |  | 2025-05-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW REMT ACCL COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46391320 | T2 EI DIABLO-GATES #1 59/241 RPR GYWT | ICQ
LC | 128699071 | 031/004 | T2 DI GRBRVIL-LAYTNVIL 31/04 RPL INSW | WILLITS | ETL.8365.INSL.NCER | 2024-05-01 | 2024-05-01 | 2025-04-16 | On-Time |  | 2025-05-01 | 2025-05-01 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35551938 | T2 DI GRBRVIL-LAYTNVIL 31/04 RPL INSW | 93I
LC | 128699218 | 048/211 | T2 EI RND MTN-TL MN #1 48/211 RPR SHIELD | TABLEMTN | ETL.6060.TOWR | 2024-05-01 | 2024-05-01 | 2025-01-25 | On-Time |  | 2025-05-01 | 2025-05-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46306284 | T2 EI RND MTN-TL MN #1 48/211 RPR SHIELD | ICS
LC | 128699232 | 048/210 | T2 EI ROND MTN-TBL MTN #1 48/210 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-01 | 2024-05-01 | 2025-05-08 | Past Due |  | 2025-05-01 | 2025-05-01 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128716951 | 005/043 | T2 DI PIT#1-COTTONWOOD 5/43 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-05-06 | 2024-05-01 | 2025-01-14 | On-Time |  | 2025-05-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381511 | T2 DI PIT#1-COTTONWOOD 5/43 RPR STRT | ICQ
LC | 128717008 | 046/395 | T2 DI PIT#1-COTTONWOOD 46/395 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2024-05-06 | 2024-05-01 | 2025-04-10 | On-Time |  | 2025-05-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381512 | T2 DI PIT#1-COTTONWOOD 46/395 BNT STEEL | ICQ
LC | 128717026 | 000/003 | T2 DI GRAPEVINE TAP 00/03 RPL ANCW | MIDWAY | ETL.9252.POLE.WOOD | 2024-05-06 | 2024-05-01 | 2024-09-28 | On-Time |  | 2024-11-01 | 2025-05-01 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35552176 | T2 DI GRAPEVINE TAP 00/03 RPL ANCW | 93E
LC | 128717029 | 000/003 | T2 DI GRAPEVINE TAP 00/03 RPR JUMW | MIDWAY | ETL.9252.INSL | 2024-05-06 | 2024-05-01 | 2024-10-06 | On-Time |  | 2024-08-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46266124 | T2 DI GRAPEVINE TAP 00/03 RPR JUMW | ICW
LC | 128717118 | 062/002 | T2 DI HUMBOLDT-TRIN 62/2 RMV VEG | EUREKA | ETL.1820.POLE.STPS | 2024-05-06 | 2024-05-01 | 2024-11-12 | On-Time |  | 2025-05-01 | 2025-05-01 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128717119 | 062/002 | T2 DI HUMBOLDT-TRIN 62/2 RPR ANCW | EUREKA | ETL.1820.POLE.STPS | 2024-05-06 | 2024-05-01 | 2025-02-18 | On-Time |  | 2025-05-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46345798 | T2 DI HUMBOLDT-TRIN 62/2 RPR ANCW | ICW
LC | 128717129 | 009/074A | T2 DI HELMS-GREGG #1 9/74A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-06 | 2024-05-01 | 2025-06-02 | Past Due |  | 2025-05-01 | 2025-05-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298108 | T2 DI HELMS-GREGG #1 9/74A RPR SHLS | ICS
LC | 128746996 | 010/178 | T2 DI TEJON LEBEC 10/178 COTTER | MIDWAY | ETL.9250.INSL.NCER | 2024-05-10 | 2024-05-01 | 2025-03-05 | On-Time |  | 2025-05-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46302534 | T2 DI TEJON LEBEC 10/178 COTTER | ICW
LC | 128774077 | 046/398 | T2 DI PIT #1-CTTNWD 046/398 UNBURY | TABLEMTN | ETL.5390.TOWR | 2024-05-14 | 2024-05-01 | 2025-01-08 | On-Time |  | 2025-05-01 | 2025-05-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381519 | T2 DI PIT #1-CTTNWD 046/398 UNBURY | ICQ
LC | 128774213 | 012/210 | T2 DI TEJON-LEBEC 12/210 RPR GYWW | MIDWAY | ETL.9250.POLE.WOOD | 2024-05-14 | 2024-05-01 | 2025-02-01 | On-Time |  | 2025-05-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46302537 | T2 DI TEJON-LEBEC 12/210 RPR GYWW | ICW
LC | 128779974 | 032/000 | T2 DI GARBERVILLE-LYTNVLLE 32/0 REFRAME | WILLITS | ETL.8365.POLE.WOOD | 2024-05-15 | 2024-05-01 | 2025-04-17 | On-Time |  | 2025-05-01 | 2025-05-01 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35574345 | T2 DI GARBERVILLE-LYTNVLLE 32/0 REFRAME | 93E
LC | 128779977 | 032/000 | T2 DI GRBRVILLE-LYTNVLLE 32/0 RPR GYWW | WILLITS | ETL.8365.POLE.WOOD | 2024-05-15 | 2024-05-01 | 2025-02-12 | On-Time |  | 2025-05-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446654 | T2 DI GRBRVILLE-LYTNVLLE 32/0 RPR GYWW | ICW
LC | 128800619 | 012/203 | T2 DI TEJON-LEBEC 012/203 RPL POLE | MIDWAY | ETL.9250.POLE.WOOD | 2024-05-17 | 2024-05-01 | 2025-02-02 | On-Time |  | 2025-05-01 | 2025-05-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573703 | T2 EI TEJON-LEBEC 010/165 RPL STRW | 70Y
LC | 128800830 | 011/201 | T2 DI TEJON-LEBEC-11/201 RPR GYWW | MIDWAY | ETL.9250.POLE.WOOD | 2024-05-17 | 2024-05-01 | 2024-09-20 | On-Time |  | 2024-11-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46266125 | T2 DI TEJON-LEBEC-11/201 RPR GYWW | ICW
LC | 128806959 | 000/002 | T2 DI GRAPEVINE TAP 0/2 RPR CRSW | MIDWAY | ETL.9252.POLE.WOOD | 2024-05-20 | 2024-05-01 | 2025-05-09 | Past Due |  | 2025-05-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46302533 | T2 DI GRAPEVINE TAP 0/2 RPR CRSW | ICW
LC | 128818839 | 009/073A | T2 DI HELMS-GREGG #1 9/73A RPR SHIELD | FRESNO | ETL.4870.TOWR | 2024-05-20 | 2024-05-01 | 2025-06-02 | Past Due |  | 2025-05-01 | 2025-05-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298117 | T2 DI HELMS-GREGG #1 9/73A RPR SHIELD | ICS
LC | 128889334 | 015/111A | T2 HELMS-GREGG #1-15/111A RMV NEST | FRESNO | ETL.4870.TOWR | 2024-05-24 | 2024-05-01 | 2024-05-01 | Past Due |  | 2025-05-01 | 2025-05-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46298029 | T2 DI HELMS-GREGG #1-15/111A RMV NEST | ICS
LC | 128889337 | 015/111A | T2 DI HELMS-GREGG #1-15/111A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-24 | 2024-05-01 | 2025-03-26 | On-Time |  | 2025-05-01 | 2025-05-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298030 | T2 DI HELMS-GREGG #1-15/111A RPR SHLS | ICS
LC | 128889419 | 046/396 | T2 DI PIT #1-CTNWD 46/396 RMV VEG | TABLEMTN | ETL.5390.TOWR | 2024-05-24 | 2024-05-01 | 2024-11-06 | On-Time |  | 2025-05-01 | 2025-05-01 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128891113 | 010/075A | T2 DI HELMS GREG #1 10/75A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-25 | 2024-05-01 | 2024-10-29 | On-Time |  | 2025-05-01 | 2025-05-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298031 | T2 DI HELMS GREG #1 10/75A RPR SHLS | ICS
LC | 128901676 | 009/072A | T2 DI HLMS GREG #1 9/72A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-05-28 | 2024-05-01 | 2025-06-02 | Past Due |  | 2025-05-01 | 2025-05-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46298118 | T2 DI HLMS GREG #1 9/72A RPR SHLS | ICS
LC | 128901779 | 032/006 | T2 GARBRVL-LAYTNVL 32/06 RPR STRW | WILLITS | ETL.8365.POLE.WOOD | 2024-05-28 | 2024-05-01 | 2025-06-24 | Past Due |  | 2025-05-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46446655 | T2 DI GARBRVL-LAYTNVL 32/06 RPR STRW | ICW
LC | 128902073 | 000/003 | T2 DI JEFRSON-STANFORD 00/03 RPR JUMW | METCALF | ETL.7220.INSL.NCER | 2024-05-28 | 2024-05-01 | 2025-03-29 | On-Time |  | 2025-05-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46286827 | T2 DI JEFRSON-STANFORD 00/03 RPR JUMW | ICW
LC | 128902276 | 011/198 | T2 DI TEJON LEBEC 11/198 RPR STRW | MIDWAY | ETL.9250.POLE.NWOD | 2024-05-28 | 2024-05-01 | 2025-03-05 | On-Time |  | 2025-05-01 | 2025-05-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46302535 | T2 DI TEJON LEBEC 11/198 RPR STRW | ICW
LC | 123478297 | 020/165 | T2NT EI CRBRY SS-RND MTN 20/165 RPL INSS | TABLEMTN | ETL.5410.INSL | 2022-05-02 | 2022-05-02 | 2023-09-13 | On-Time |  | 2025-05-02 | 2025-05-02 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 31639948 | T2NT EI CRBRY SS-RND MTN 24/193 RPL INSS | 93K
LC | 123524277 | 091/463 | T2NT DI MALIN-RND MTN #2 91/463 UNBURY | TABLEMTN | ETL.6020.TOWR | 2022-05-06 | 2022-05-02 | 2023-08-18 | On-Time |  | 2025-05-02 | 2025-05-02 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45617410 | T2 DI MALIN-ROUND MTN #2 91/463 UNBURY | ICQ
LC | 123547284 | 090/461 | T2NT DI MLN-RND MTN #2 90/461 RPR FOND | TABLEMTN | ETL.6020.TOWR | 2022-05-09 | 2022-05-02 | 2023-08-15 | On-Time |  | 2025-05-02 | 2025-05-02 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45617409 | T2 DI MLN-RND MTN #2 90/461 RPR FOND | ICQ
LC | 123558856 | 003/005 | T2NT DI POTER VALEY-WILLITS 3/5 RPR GYWW | WILLITS | ETL.7820.POLE.NWOD | 2022-05-10 | 2022-05-02 | 2023-08-28 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45735874 | T2 DI POTTER VALLEY-WILLITS 3/5 RPR GYWW | ICW
LC | 127399654 | 012/000 | T2 MELONES-CURTIS 012/00 INST JUMPER | VICTOR | ETL.2390.POLE.WDPS | 2023-11-02 | 2023-11-02 | 2023-11-02 | Past Due |  | 2025-05-02 | 2025-05-02 | 508T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB XMPT TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Insulator-Wood | Replace | 35529949 | 32 EI MELONES-CURTIS 012/00 INST JUMPER | 93I
LC | 128700513 | 012/095 | T2 EI TIGR CRK-VLY SPRNGS 12/95 RPL INSS | VICTOR | ETL.5790.INSL.CERA | 2024-05-02 | 2024-05-02 | 2024-05-02 | Past Due |  | 2025-05-02 | 2025-05-02 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593059 | T2 EI TGR CRK-VLLY SPRINGS 4/33 RPL INSS | 93K
LC | 128700527 | 012/095 | T2 EI TGR CRK-VLY SPRNGS 12/095 RPL HRDT | VICTOR | ETL.5790.TOWR | 2024-05-02 | 2024-05-02 | 2025-04-04 | On-Time |  | 2025-05-02 | 2025-05-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46416608 | T2 EI TGR CRK-VLY SPRNGS 12/095 RPL HRDT | ICQ
LC | 128700538 | 012/008 | T2 WV FORT BRAGG-ELK 12/008 INS DMPW | WILLITS | ETL.2060.INSL.NCER | 2024-05-02 | 2024-05-02 | 2025-01-23 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46310139 | T2 WV FORT BRAGG-ELK 12/008 INS DMPW | ICW
LC | 128700631 | 009/174 | T2 WV COLGATE-PALERMO 9/174 INS DMPW | SACTO | ETL.6500.INSL.NCER | 2024-05-02 | 2024-05-02 | 2025-02-20 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46383053 | T2 WV COLGATE-PALERMO 9/174 INS DMPW | ICW
LC | 128700673 | 004/025 | T2 KRCKHFF-CLVS-SNGR #1 04/25 RMV ENCR | FRESNO | ETL.1890.TOWR | 2024-05-02 | 2024-05-02 | 2024-10-15 | On-Time |  | 2024-11-02 | 2025-05-02 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | Encroachment | Right of Way | Remove | 46254522 | T2 KRCKHFF-CLVS-SNGR #1 04/25 RMV ENCR | CHR
LC | 128700686 | 012/094 | T2 EI TGR CRK-VLY SPRNGS 12/095 RPR FOND | VICTOR | ETL.5790.TOWR | 2024-05-02 | 2024-05-02 | 2025-04-04 | On-Time |  | 2025-05-02 | 2025-05-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416610 | T2 EI TGR CRK-VLY SPRNGS 12/095 RPR FOND | ICQ
LC | 128700688 | 012/094 | T2 EI TGR CRK-VLY SPRNGS 12/094 COMPLETE | VICTOR | ETL.5790.TOWR | 2024-05-02 | 2024-05-02 | 2025-04-04 | On-Time |  | 2025-05-02 | 2025-05-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416611 | T2 EI TGR CRK-VLY SPRNGS 12/094 RPR STRT | ICQ
LC | 128700772 | 008/162 | T2 WV COLGATE-PALERMO 8/162 INS DMPW | SACTO | ETL.6500.INSL.NCER | 2024-05-02 | 2024-05-02 | 2025-02-20 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46383054 | T2 WV COLGATE-PALERMO 8/162 INS DMPW | ICW
LC | 128700869 | 002/002 | T2 EI RACETRACK TAP 002/002 RPL POLE | VICTOR | ETL.2393.POLE.WOOD | 2024-05-02 | 2024-05-02 | 2025-06-18 | Past Due |  | 2025-05-02 | 2025-05-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573813 | T2 EI RACETRACK TAP 002/002 RPL PL | 70Y
LC | 128700976 | 040/192 | T2 EI CRTIN-MNDCIN #1 40/192 RPR FOND | WILLITS | ETL.1330.TOWR | 2024-05-02 | 2024-05-02 | 2025-03-21 | On-Time |  | 2025-05-02 | 2025-05-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46290424 | T2 EI CRTIN-MNDCIN #1 40/192 RPR FOND | ICQ
LC | 128700980 | 040/192 | T2 EI CRTIN-MNDCIN #1 40/192 RMV VEG | WILLITS | ETL.1330.TOWR | 2024-05-02 | 2024-05-02 | 2025-02-25 | On-Time |  | 2025-05-02 | 2025-05-02 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128701119 | 000/001 | T2 EI DELTA-MTN GATE JCT 0/1 RMV VEG | TABLEMTN | ETL.6750.POLE.WOOD | 2024-05-02 | 2024-05-02 | 2024-12-24 | On-Time |  | 2025-05-02 | 2025-05-02 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128701150 | 000/003 | T2 EI DELTA-MTN GATE JCT 0/3 RMV VEG | TABLEMTN | ETL.6750.POLE.WOOD | 2024-05-02 | 2024-05-02 | 2024-12-26 | On-Time |  | 2025-05-02 | 2025-05-02 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128701151 | 000/003 | T2 EI DELTA-MTN GATE JCT 0/3 CANCEL | TABLEMTN | ETL.6750.INSL.NCER | 2024-05-02 | 2024-05-02 | 2024-05-02 | Past Due |  | 2025-05-02 | 2025-05-02 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35557673 | T2 EI DELTA-MTN GATE JCT 0/3 RPL INSW | 93I
LC | 128701312 | 047/209 | T2 EI RND MTN-TL MN #1 47/209 RPR SHIELD | TABLEMTN | ETL.6060.TOWR | 2024-05-02 | 2024-05-02 | 2025-01-25 | On-Time |  | 2025-05-02 | 2025-05-02 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46306285 | T2 EI RND MTN-TL MN #1 47/209 RPR SHIELD | ICS
LC | 128701335 | 025/145 | T2 TEL-SLD-MNTC 25/145 RPR INSW | VICTOR | ETL.4000.INSL.NCER | 2024-05-02 | 2024-05-02 | 2025-02-25 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46325927 | T2 TEL-SLD-MNTC 25/145 RPR INSW | ICW
LC | 128701369 | 004/080 | T2 DELTA-MTN GATE JCT 4/80 RPL INSS | TABLEMTN | ETL.6750.INSL | 2024-05-02 | 2024-05-02 | 2024-05-02 | Past Due |  | 2025-05-02 | 2025-05-02 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570502 | T2 EI DELTA-MTN GATE JCT 4/80 RPL INSS | 93K
LC | 128701384 | 007/085 | T2NT WV VEDDER TAP 07/85 INS DMPW | MIDWAY | ETL.2141.INSL.NCER | 2024-05-02 | 2024-05-02 | 2025-03-26 | On-Time |  | 2027-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46302539 | T2NT WV VEDDER TAP 07/85 INS DMPW | ICW
LC | 128701448 | 004/085 | T2 EI CORDELIA #1 TAP 004/085 RPR POLE | SACTO | ETL.8182.POLE.WOOD | 2024-05-02 | 2024-05-02 | 2025-04-24 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337392 | T2 EI CORDELIA #1 TAP 004/085 RPR POLE | ICW
LC | 128701500 | 004/083 | T2 EI CORDELIA #1 TAP 004/083 RPL POLE | SACTO | ETL.8182.POLE.WOOD | 2024-05-02 | 2024-05-02 | 2025-04-24 | On-Time |  | 2025-05-02 | 2025-05-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557137 | T2 EI CORDELIA #1 TAP 003/080 RPL POLE | 70Y
LC | 128701598 | 005/066 | T2 BURNS-LONE STAR #1 05/066 GO95 | MOSSLNDG | ETL.6230.POLE.WOOD | 2024-05-02 | 2024-05-02 | 2024-05-31 | On-Time |  | 2025-05-02 | 2025-05-02 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 31655006 | T2 BURNS-LONE STAR #1 05/65 GO95 | 93G
LC | 128701710 | :002/002 | T2 EI BELLT-RVRBNK-MLNS SS :2/2 RPR GYWW | VICTOR | ETL.1070.POLE.NWOD | 2024-05-02 | 2024-05-02 | 2024-09-23 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46253026 | T2 EI BELLT-RVRBNK-MLNS SS :2/2 RPR GYWW | ICW
LC | 128701909 | 040/193 | T2 CORTINA-MENDOCINO #1 40/193 COTTER | WILLITS | ETL.2410.INSL.CERA | 2024-05-02 | 2024-05-02 | 2024-05-02 | Past Due |  | 2025-05-02 | 2025-05-02 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46246702 | T2 EI CORTINA-MENDOCINO #1 40/193 COTTER | ICS
LC | 128701971 | 047/207 | T2 EI RD MTN-TBL MT #2 47/207 RPR SHIELD | TABLEMTN | ETL.6070.TOWR | 2024-05-02 | 2024-05-02 | 2025-02-21 | On-Time |  | 2025-05-02 | 2025-05-02 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46306286 | T2 EI RD MTN-TBL MT #2 47/207 RPR SHIELD | ICS
LC | 128702381 | 003/080 | T2 EI CORDELIA #1 TAP 003/080 RPL POLE | SACTO | ETL.8182.POLE.WOOD | 2024-05-02 | 2024-05-02 | 2025-04-24 | On-Time |  | 2025-05-02 | 2025-05-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557137 | T2 EI CORDELIA #1 TAP 003/080 RPL POLE | 70Y
LC | 128702449 | 011/088 | T2 EI TGR CRK-VLY SPRNGS 11/88 RPR STRT | VICTOR | ETL.5790.TOWR | 2024-05-02 | 2024-05-02 | 2025-04-07 | On-Time |  | 2025-05-02 | 2025-05-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416612 | T2 EI TGR CRK-VLY SPRNGS 11/088 RPR STRT | ICQ
LC | 128702450 | 003/079 | T2 CORDELIA #1 TAP 3/79 RPR POLE | SACTO | ETL.8182.POLE.WOOD | 2024-05-02 | 2024-05-02 | 2024-05-02 | Past Due |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair
LC | 128702524 | 024/345 | T2 CLAY-MARTEL 024/345 INS DAMP | VICTOR | ETL.8250.INSL.NCER | 2024-05-02 | 2024-05-02 | 2024-05-02 | Past Due |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46326993 | +T2 WV CLAY-MARTEL 024/345 INS DMPW | ICW
LC | 128702733 | 023/003B | T2 WV FORT BRAGG-ELK 23/003B INS HRDW | WILLITS | ETL.2060.POLE.NWOD | 2024-05-02 | 2024-05-02 | 2025-02-27 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Hardware-Wood | Install | 46310140 | T2 WV FORT BRAGG-ELK 23/003B INS HRDW | ICW
LC | 128702740 | 023/003C | T2 WV FORT BRAGG-ELK 23/003C INS HRDW | WILLITS | ETL.2060.POLE.NWOD | 2024-05-02 | 2024-05-02 | 2025-02-27 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Hardware-Wood | Install | 46310141 | T2 WV FORT BRAGG-ELK 23/003C INS HRDW | ICW
LC | 128702746 | 046/206 | T2 EI RND MTN-TBL MTN #2 46/206 COTTER | TABLEMTN | ETL.6070.INSL | 2024-05-02 | 2024-05-02 | 2025-02-21 | On-Time |  | 2025-05-02 | 2025-05-02 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46306287 | T2 EI RND MTN-TBL MTN #2 46/206 COTTER | ICS
LC | 128702777 | 056/004A | T2 HUMBOLDT-TRINITY 56/4A RPR JUMPER | EUREKA | ETL.1820.INSL.NCER | 2024-05-02 | 2024-05-02 | 2024-08-26 | On-Time |  | 2024-08-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46252217 | T2 HUMBOLDT-TRINITY 56/4A RPR JUMPER | ICW
LC | 128702778 | 056/004B | T2 HUMBOLDT-TRINITY 56/4B RPR JUMPER | EUREKA | ETL.1820.INSL.NCER | 2024-05-02 | 2024-05-02 | 2024-08-26 | On-Time |  | 2024-08-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46252218 | T2 HUMBOLDT-TRINITY 56/4B RPR JUMPER | ICW
LC | 128702857 | 056/004C | T2 HUMBOLDT-TRINITY 56/4C RPR JUMPER | EUREKA | ETL.1820.INSL.NCER | 2024-05-02 | 2024-05-02 | 2024-08-26 | On-Time |  | 2024-08-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46252219 | T2 HUMBOLDT-TRINITY 56/4C RPR JUMPER | ICW
LC | 128703306 | 010/078 | T2 EI TGR CRK-VLY SPRNGS 10/078 RPR FOND | VICTOR | ETL.5790.TOWR | 2024-05-02 | 2024-05-02 | 2025-04-07 | On-Time |  | 2025-05-02 | 2025-05-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416613 | T2 EI TGR CRK-VLY SPRNGS 10/078 RPR FOND | ICQ
LC | 128703455 | 003/076 | T2 EI CORDELIA #1 TAP 003/076 RPR POLE | SACTO | ETL.8182.POLE.WOOD | 2024-05-02 | 2024-05-02 | 2025-03-12 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337393 | T2 EI CORDELIA #1 TAP 003/076 RPR POLE | ICW
LC | 128703502 | 001/003 | T2 EI MENDOCINO-WILLITS 1/003 RMV VEG | WILLITS | ETL.7540.POLE.NWOD | 2024-05-02 | 2024-05-02 | 2025-02-28 | On-Time |  | 2025-05-02 | 2025-05-02 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP REMT REAR ACCL COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128703509 | 000/002 | T2 EI PT #3-CRBRY SW STA 00/02 RPR JMPS | TABLEMTN | ETL.5450.INSL.NCER | 2024-05-02 | 2024-05-02 | 2024-10-30 | On-Time |  | 2024-08-02 | 2025-05-02 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46251396 | T2 EI PT #3-CRBRY SW STA 00/02 RPR JMPS | ICS
LC | 128703631 | 000/010 | T2 EI OAKHURST TAP 00/010 RMV FNCE | FRESNO | ETL.1252.POLE.NWOD | 2024-05-02 | 2024-05-02 | 2024-08-19 | On-Time |  | 2024-11-02 | 2025-05-02 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46249760 | T2 EI OAKHURST TAP 00/010 RMV FNCE | CHR
LC | 128703677 | 000/011 | T2 EI OAKHURST TAP 00/011 RMV FNCE | FRESNO | ETL.1252.POLE.NWOD | 2024-05-02 | 2024-05-02 | 2024-08-19 | On-Time |  | 2024-07-02 | 2025-05-02 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46249761 | T2 EI OAKHURST TAP 00/011 RMV FNCE | CHR
LC | 128703678 | 000/012 | T2 EI OAKHURST TAP 00/012 RMV ENCR | FRESNO | ETL.1252.POLE.NWOD | 2024-05-02 | 2024-05-02 | 2024-08-19 | On-Time |  | 2024-11-02 | 2025-05-02 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46249762 | T2 EI OAKHURST TAP 00/012 RMV FNCE | CHR
LC | 128703818 | 023/101 | T2 EI LS ESTRS-MTCLF 23/101 RPL INSS | METCALF | ETL.5353.INSL | 2024-05-02 | 2024-05-02 | 2025-03-31 | On-Time |  | 2025-05-02 | 2025-05-02 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574629 | T2 EI LOS ESTEROS-METCALF RPL INSS IN 7 | 93K
LC | 128703909 | 016/099 | T2 SS-MLS SS-MTC #1 016/099 RPR FOND | VICTOR | ETL.3830.TOWR | 2024-05-02 | 2024-05-02 | 2024-05-02 | Past Due |  | 2025-05-02 | 2025-05-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416614 | T2 EI SS-MLS SS-MTC #1 16/199 RPR FOND | ICQ
LC | 128703989 | 022/099 | T2 EI LS ESTRS-MTCLF 22/99 RPL INSS | METCALF | ETL.5353.INSL | 2024-05-02 | 2024-05-02 | 2025-03-24 | On-Time |  | 2025-05-02 | 2025-05-02 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574629 | T2 EI LOS ESTEROS-METCALF RPL INSS IN 7 | 93K
LC | 128704046 | 014/179C | T2 EI DELTA-MT GATE JCT 14/179C RPR GYWW | TABLEMTN | ETL.6750.POLE.NWOD | 2024-05-02 | 2024-05-02 | 2024-06-25 | On-Time |  | 2024-11-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46251424 | T2 EI DELTA-MT GATE JCT 14/179C RPR GYWW | ICW
LC | 128704114 | 014/009 | T2 EI TRINITY-MAPLE CREEK 14/09 CGI | EUREKA | ETL.8170.POLE.NWOD | 2024-05-02 | 2024-05-02 | 2025-04-18 | On-Time |  | 2024-08-02 | 2025-05-02 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 128704140 | 015/009 | T2 EI TRINITY-MAPLE CREEK 15/09 CGI | EUREKA | ETL.8170.POLE.NWOD | 2024-05-02 | 2024-05-02 | 2025-04-18 | On-Time |  | 2024-08-02 | 2025-05-02 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 128704143 | 014/004 | T2 EI TRINITY-MAPLE CREEK 14/4 CGI | EUREKA | ETL.8170.POLE.WOOD | 2024-05-02 | 2024-05-02 | 2025-04-18 | On-Time |  | 2024-08-02 | 2025-05-02 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 128704146 | 016/000 | T2 EI TRINITY-MAPLE CREEK 16/00 CGI | EUREKA | ETL.8170.POLE.NWOD | 2024-05-02 | 2024-05-02 | 2025-04-18 | On-Time |  | 2024-08-02 | 2025-05-02 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 128704151 | 47 | T2 TRNTY-MAPLE CREEK 28/8 SW#47 RPL SWTC | EUREKA | ETL.8170.SWIT | 2024-05-02 | 2024-05-02 | 2024-05-02 | Past Due |  | 2025-05-02 | 2025-05-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Switch-Wood | Replace | 35570014 | T2 EI TRINITY-MAPLE CREEK 28/8 RPL STRW | 70Y
LC | 128704153 | 015/008 | T2 EI TRINITY-MAPLE CREEK 15/08 CGI | EUREKA | ETL.8170.POLE.NWOD | 2024-05-02 | 2024-05-02 | 2025-04-18 | On-Time |  | 2024-08-02 | 2025-05-02 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 128704154 | 016/002 | T2 EI TRINITY-MAPLE CREEK 16/02 CGI | EUREKA | ETL.8170.POLE.WOOD | 2024-05-02 | 2024-05-02 | 2025-04-18 | On-Time |  | 2024-08-02 | 2025-05-02 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 128704162 | 016/001 | T2 EI TRINITY-MAPLE CREEK 16/01 CGI | EUREKA | ETL.8170.POLE.WOOD | 2024-05-02 | 2024-05-02 | 2025-04-18 | On-Time |  | 2024-08-02 | 2025-05-02 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 128704196 | 007/095 | T2 EI KESWICK-TRINITY 7/095 RPR JMPW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-02 | 2024-05-02 | 2024-09-12 | On-Time |  | 2024-08-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251630 | T2 EI KESWICK-TRINITY 7/095 RPR JMPW | ICW
LC | 128704215 | 008/110 | T2 EI KESWICK-TRINITY 8/110 RPR JMPW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-02 | 2024-05-02 | 2024-09-11 | On-Time |  | 2024-08-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251632 | T2 EI KESWICK-TRINITY 8/110 RPR JMPW | ICW
LC | 128704225 | 006/077 | T2 EI KESWICK-TRINITY 6/077 RPR JMPW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-02 | 2024-05-02 | 2024-09-12 | On-Time |  | 2024-08-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251629 | T2 EI KESWICK-TRINITY 6/077 RPR JMPW | ICW
LC | 128704281 | 007/102 | T2 EI KESWICK-TRINITY 007/102R RPR GYWW | TABLEMTN | ETL.7270.POLE.STPS | 2024-05-02 | 2024-05-02 | 2024-09-10 | On-Time |  | 2024-11-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46253087 | T2 EI KESWICK-TRINITY 007/102R RPR GYWW | ICW
LC | 128708376 | 006/006 | T2 DI LAYTONVILLE-COVL 6/6L RPR GYWW | WILLITS | ETL.7390.POLE.STPS | 2024-05-03 | 2024-05-02 | 2025-03-28 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446659 | T2 DI LAYTONVILLE-COVL 6/6L RPR GYWW | ICW
LC | 128708509 | 057/004 | T2 DI HUMBOLDT-TRINITY 57/04R RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-05-03 | 2024-05-02 | 2025-02-17 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345842 | T2 DI HUMBOLDT-TRINITY 57/04R RPR GYWW | ICW
LC | 128708573 | 006/007 | T2 DI LAYTONVILLE-COVL 6/7 TOUCH | WILLITS | ETL.7390.POLE.NWOD | 2024-05-03 | 2024-05-02 | 2025-05-16 | Past Due |  | 2024-11-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46493496 | T2 DI LAYTONVILLE-COVL 6/7 TOUCH | ICW
LC | 128709137 | 019/374 | T2 HAT CREEK #1-WESTWOOD 19/374 RPR STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-03 | 2024-05-02 | 2024-06-14 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46265876 | T2 HAT CREEK #1-WESTWOOD 19/374 RPR STRW | ICW
LC | 128709499 | 052/001A | T2 DI HUMBOLDT-TRINITY 52/1A RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-05-03 | 2024-05-02 | 2024-11-09 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46252306 | T2 DI HUMBOLDT-TRINITY 52/1A RPR GYWW | ICW
LC | 128709600 | 052/001C | T2 DI HUMBOLDT-TRINITY 52/1C RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-05-03 | 2024-05-02 | 2024-11-09 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345841 | T2 DI HUMBOLDT-TRINITY 52/1C RPR GYWW | ICW
LC | 128716651 | 001/014 | T2 DI CRG-VW-CASCADE 001/014 RPR OPGW | TABLEMTN | ETL.1350.POLE.STPS | 2024-05-06 | 2024-05-02 | 2025-01-17 | On-Time |  | 2025-05-02 | 2025-05-02 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46452773 | T2 DI CRG-VW-CASCADE 001/014 RPR OPGW | ICS
LC | 128716938 | 003/038 | T2 DI HLSDL JT-HLF MN BY 3/038 RPL STRW | METCALF | ETL.7060.POLE.WOOD | 2024-05-06 | 2024-05-02 | 2025-03-07 | On-Time |  | 2025-05-02 | 2025-05-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573573 | T2 DI HLSDL JT-HLF MN BY 3/038 RPL STRW | 70Y
LC | 128717117 | 044/377 | T2NT DI PIT #1-CTTNWD 044/377 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-05-06 | 2024-05-02 | 2025-04-21 | On-Time |  | 2027-05-02 | 2025-05-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381514 | T2NT DI PIT #1-CTTNWD 044/377 RPR STRT | ICQ
LC | 128717121 | 044/377 | T2 DI PIT #1-COTTONWOOD 044/377 RPL HRDT | TABLEMTN | ETL.5390.TOWR | 2024-05-06 | 2024-05-02 | 2025-04-21 | On-Time |  | 2025-05-02 | 2025-05-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381515 | T2 DI PIT #1-COTTONWOOD 044/377 RPL HRDT | ICQ
LC | 128818869 | 000/006 | T2 DI CRG VIEW-CSCD 0/6 INSP STRW | TABLEMTN | ETL.1350.POLE.STPS | 2024-05-20 | 2024-05-02 | 2024-09-06 | On-Time |  | 2024-11-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46253225 | T2 DI CRG VIEW-CSCD 0/6 INSP STRW | ICW
LC | 128818990 | 000/006 | T2 DI CRG VIEW-CSCD 0/6l RMV VEG | TABLEMTN | ETL.1350.POLE.STPS | 2024-05-20 | 2024-05-02 | 2024-10-16 | On-Time |  | 2024-11-02 | 2025-05-02 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128818994 | 057/007B | T2 DI HMBLDT-TRNTY 057/007B COTTER | EUREKA | ETL.1820.INSL.NCER | 2024-05-20 | 2024-05-02 | 2025-04-09 | On-Time |  | 2025-05-02 | 2025-05-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46345843 | T2 DI HMBLDT-TRNTY 057/007B COTTER | ICW
LC | 128902101 | 010/051 | T2 DI FULTON-PUEBLO 10/51 RPL HRDT | LAKEVLLE | ETL.1600.TOWR | 2024-05-28 | 2024-05-02 | 2025-01-21 | On-Time |  | 2025-05-02 | 2025-05-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289507 | T2 DI FULTON-PUEBLO 10/51 RPL HRDT | ICQ
LC | 123526196 | 012/158 | T2NT DI JOLON TAP 12/158 MASTIC | MOSSLNDG | ETL.7321.POLE.NWOD | 2022-05-06 | 2022-05-03 | 2024-01-08 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46080738 | T2NT DI JOLON TAP 12/158 MASTIC | ICW
LC | 123582504 | 017/081 | T3NT DI MSS LNDG-METCLF 17/081 RPR GYWS | MOSSLNDG | ETL.6050.TOWR | 2022-05-12 | 2022-05-03 | 2023-07-25 | On-Time |  | 2025-05-03 | 2025-05-03 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45650189 | T3 DI MSS LNDG-METCLF 17/081 RPR GYWS | ICS
LC | 128705790 | 007/063 | T2 SALT SPRINGS-TIGER CRK 7/63 CANCEL | VICTOR | ETL.3500.INSL.NCER | 2024-05-03 | 2024-05-03 | 2024-05-03 | Past Due |  | 2025-05-03 | 2025-05-03 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35599721 | T2 EI SLT SPRINGS TGR CRK 7/63 RPL INSS | 93K
LC | 128707129 | 020/009 | T2 BRIDGEVILE-GRBRVIL 20/09 RPR INSW | EUREKA | ETL.6220.INSL.NCER | 2024-05-03 | 2024-05-03 | 2025-06-10 | Past Due |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46345844 | T2 BRIDGEVILE-GRBRVIL 20/09 RPR INSW | ICW
LC | 128707178 | 005/097 | T2 EI CORDELIA #1 TAP 05/097 RPR STRW | SACTO | ETL.8182.POLE.WOOD | 2024-05-03 | 2024-05-03 | 2025-04-24 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337387 | T2 EI CORDELIA #1 TAP 05/097 RPR STRW | ICW
LC | 128707216 | 009/068 | T2 EI TGR CRK-VLY SPRNGS 9/068 RPR FOND | VICTOR | ETL.5790.TOWR | 2024-05-03 | 2024-05-03 | 2025-03-17 | On-Time |  | 2025-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416615 | T2 EI TGR CRK-VLY SPRNGS 9/068 RPR FOND | ICQ
LC | 128707241 | 005/034 | T2 VACA-PARKWAY 005/034 TOUCH | SACTO | ETL.5850.TOWR | 2024-05-03 | 2024-05-03 | 2025-02-28 | On-Time |  | 2024-11-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46460825 | T2 VACA-PARKWAY 005/034 RPR STRT | ICQ
LC | 128707293 | 015/192 | T2 WV KESWICK-TRINITY 15/192 INS DMPW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-03 | 2024-05-03 | 2025-04-22 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46311268 | T2 WV KESWICK-TRINITY 15/192 INS DMPW | ICW
LC | 128707384 | 015/191 | T2 WV KESWICK-TRINITY 15/191 INS DMPW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-03 | 2024-05-03 | 2025-04-22 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46311269 | T2 WV KESWICK-TRINITY 15/191 INS DMPW | ICW
LC | 128707515 | 009/046 | T2 EI LOS ESTEROS-METCALF 9/46 BNT STEEL | METCALF | ETL.5353.TOWR | 2024-05-03 | 2024-05-03 | 2025-01-25 | On-Time |  | 2025-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46298825 | T2 EI LOS ESTEROS-METCALF 9/46 BNT STEEL | ICQ
LC | 128707641 | 001/007 | T2 EI MENDOCINO-WILLITS 1/007 RPL STRW | WILLITS | ETL.7540.POLE.WOOD | 2024-05-03 | 2024-05-03 | 2025-01-06 | On-Time |  | 2025-05-03 | 2025-05-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574334 | T2 EI MENDOCINO-WILLITS 1/007 RPL STRW | 70Y
LC | 128707698 | 002/007 | T2 EI OAKHURST TAP 2/007 COTTER | FRESNO | ETL.1252.INSL.NCER | 2024-05-03 | 2024-05-03 | 2024-08-20 | On-Time |  | 2024-11-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46265372 | T2 EI OAKHURST TAP 2/007 COTTER | ICW
LC | 128707806 | 013/077 | T2 EI SS-MLS SS-MTC #1 13/77 RPR FOND | VICTOR | ETL.3830.TOWR | 2024-05-03 | 2024-05-03 | 2025-04-30 | On-Time |  | 2025-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416616 | T2 EI SS-MLS SS-MTC #1 13/77 RPR FOND | ICQ
LC | 128708172 | 035/008 | T2 EI BRIDGEVLE-GARBRVILE 35/08 RPR GYWW | EUREKA | ETL.6220.POLE.NWOD | 2024-05-03 | 2024-05-03 | 2024-10-02 | On-Time |  | 2024-08-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46249613 | T2 EI BRIDGEVLE-GARBRVILE 35/08 RPR GYWW | ICW
LC | 128708288 | 005/096 | T2 EI CORDELIA #1 TAP 05/096 RPR STRW | SACTO | ETL.8182.POLE.WOOD | 2024-05-03 | 2024-05-03 | 2025-04-25 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337389 | T2 EI CORDELIA #1 TAP 05/096 RPR STRW | ICW
LC | 128708325 | 005/096 | T2 EI CORDELIA #1 TAP 05/096 RPL HRDW | SACTO | ETL.8182.POLE.WOOD | 2024-05-03 | 2024-05-03 | 2025-04-25 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46337388 | T2 EI CORDELIA #1 TAP 05/096 RPL HRDW | ICW
LC | 128708385 | 005/095 | T2 EI CORDELIA #1 TAP 05/95C RPR GYWW | SACTO | ETL.8182.POLE.STPS | 2024-05-03 | 2024-05-03 | 2025-04-26 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337391 | T2 EI CORDELIA #1 TAP 05/95C RPR GYWW | ICW
LC | 128708397 | 005/095 | T2 EI CORDELIA #1 TAP 05/95R RPR GYWW | SACTO | ETL.8182.POLE.STPS | 2024-05-03 | 2024-05-03 | 2025-04-26 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337390 | T2 EI CORDELIA #1 TAP 05/95R RPR GYWW | ICW
LC | 128708445 | 025/144 | T2 TSL-SLD-MNTC 25/144 RPR CONDW | VICTOR | ETL.4000.INSL.NCER | 2024-05-03 | 2024-05-03 | 2025-02-25 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Conductor-Wood | Repair | 46325928 | T2 TSL-SLD-MNTC 25/144 RPR CONDW | ICW
LC | 128708520 | 027/460 | T2 WV KESWICK-TRINITY 27/460 INS DMPW | TABLEMTN | ETL.7270.INSL | 2024-05-03 | 2024-05-03 | 2025-04-02 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46311267 | T2 WV KESWICK-TRINITY 27/460 INS DMPW | ICW
LC | 128708630 | 010/069 | T2 COTTORWOOD-LOGAN 10/069 RPR INSS | TABLEMTN | ETL.4570.INSL | 2024-05-03 | 2024-05-03 | 2024-12-17 | On-Time |  | 2025-05-03 | 2025-05-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300592 | T2 COTTORWOOD-LOGAN 10/069 RPR INSS | ICS
LC | 128708779 | 003/030B | T2 DI CRG VIEW-CASCADE 03/30B RPR JUMW | TABLEMTN | ETL.1350.INSL.NCER | 2024-05-03 | 2024-05-03 | 2024-09-06 | On-Time |  | 2024-08-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46249495 | T2 DI CRG VIEW-CASCADE 03/30B RPR JUMW | ICW
LC | 128708802 | 021/003 | T2 EI RIO DLL JCT-BRDGVLLE 21/3 RPL STRW | EUREKA | ETL.7850.POLE.WOOD | 2024-05-03 | 2024-05-03 | 2025-06-09 | Past Due |  | 2025-05-03 | 2025-05-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572961 | T2 EI RIO DLL JCT-BRDGVLLE 21/3 RPL STRW | 70Y
LC | 128708803 | 022/003 | T2 EI RIO DLL JCT-BRDGVLLE 22/3 RPL ANCW | EUREKA | ETL.7850.POLE.WOOD | 2024-05-03 | 2024-05-03 | 2025-05-17 | Past Due |  | 2025-05-03 | 2025-05-03 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572962 | T2 EI RIO DLL JCT-BRDGVLLE 22/3 RPL ANCW | 93E
LC | 128708815 | 021/112 | T2 TESLA-NEWARK #1 21/112 TOUCH | CONCORD | ETL.5720.TOWR | 2024-05-03 | 2024-05-03 | 2025-04-30 | On-Time |  | 2024-08-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485416 | T2 TESLA-NEWARK #1 21/112 TOUCH | ICQ
LC | 128708853 | 005/100 | T2 EI CORDELIA #1 TAP 05/100 WASH INSW | SACTO | ETL.8182.INSL | 2024-05-03 | 2024-05-03 | 2025-04-24 | On-Time |  | 2025-05-03 | 2025-05-03 | 622 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | Contaminated | Insulator | Ground Wash | 46337351 | T2 EI CORDELIA #1 TAP 05/100 WASH INSW | ICD
LC | 128708860 | 005/100 | T2 EI CORDELIA #1 TAP 05/100 RPR STRW | SACTO | ETL.8182.POLE.WOOD | 2024-05-03 | 2024-05-03 | 2025-04-24 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337386 | T2 EI CORDELIA #1 TAP 05/100 RPR STRW | ICW
LC | 128708862 | 005/030 | T2 WV MORR BY-SN LUS BSP#2 5/30 INS DAMS | PISMOBCH | ETL.2820.INSL | 2024-05-03 | 2024-05-03 | 2025-01-29 | On-Time |  | 2025-05-03 | 2025-05-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Steel | Install | 46329531 | T2 WV MORR BY-SN LUS BSP#2 5/30 INS DAMS | ICS
LC | 128708908 | 005/030 | T2 WV MORR BY-SN LUS BSP#2 5/30 RPR JUMS | PISMOBCH | ETL.2820.INSL | 2024-05-03 | 2024-05-03 | 2025-01-29 | On-Time |  | 2025-05-03 | 2025-05-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Jumper-Steel | Repair | 46329532 | T2 WV MORR BY-SN LUS BSP#2 5/30 RPR JUMS | ICS
LC | 128708912 | 028/003 | T2 TRINITY-MAPLE CREEK_028/003L GO95 | EUREKA | ETL.8170.POLE.WDPS | 2024-05-03 | 2024-05-03 | 2025-04-13 | On-Time |  | 2025-05-03 | 2025-05-03 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35557694 | T2 TRINITY-MAPLE CREEK_028/003R GO95 | 93G
LC | 128708913 | 028/003 | T2 TRINITY-MAPLE CREEK_028/003R GO95 | EUREKA | ETL.8170.POLE.WDPS | 2024-05-03 | 2024-05-03 | 2025-04-13 | On-Time |  | 2025-05-03 | 2025-05-03 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35557694 | T2 TRINITY-MAPLE CREEK_028/003R GO95 | 93G
LC | 128708914 | 028/003 | T2 TRINITY-MAPLE CREEK_028/003C GO95 | EUREKA | ETL.8170.POLE.WDPS | 2024-05-03 | 2024-05-03 | 2025-04-13 | On-Time |  | 2025-05-03 | 2025-05-03 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35557694 | T2 TRINITY-MAPLE CREEK_028/003R GO95 | 93G
LC | 128709030 | 011/157 | T2 DELTA-MTN GATE JCT 11/157 RPL STRW | TABLEMTN | ETL.6750.POLE.WOOD | 2024-05-03 | 2024-05-03 | 2024-05-03 | Past Due |  | 2025-05-03 | 2025-05-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557676 | T2 EI DELTA-MTN GATE JCT 11/157 RPL STRW | 70Y
LC | 128709078 | 003/073 | T2 VOLTA-SOUTH 3/073 GO95 | TABLEMTN | ETL.8300.POLE.NWOD | 2024-05-03 | 2024-05-03 | 2025-01-13 | On-Time |  | 2025-05-03 | 2025-05-03 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35556393 | T2 VOLTA-SOUTH 3/073 GO95 | 93G
LC | 128709097 | 003/030C | T2 DI CRG VIEW-CASCADE 03/30C RPR JUMW | TABLEMTN | ETL.1350.INSL.NCER | 2024-05-03 | 2024-05-03 | 2024-09-06 | On-Time |  | 2024-08-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46249497 | T2 DI CRG VIEW-CASCADE 03/30C RPR JUMW | ICW
LC | 128709219 | 003/030A | T2 DI CRG VIEW-CASCADE 03/30A RPR JUMW | TABLEMTN | ETL.1350.INSL.NCER | 2024-05-03 | 2024-05-03 | 2024-09-06 | On-Time |  | 2024-08-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46249494 | T2 DI CRG VIEW-CASCADE 03/30A RPR JUMW | ICW
LC | 128709350 | 004/001 | T2 DI LAYTONVILLE-COVELO 04/01 INS STRW | WILLITS | ETL.7390.POLE.WOOD | 2024-05-03 | 2024-05-03 | 2024-07-11 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46252699 | T2 DI LAYTONVILLE-COVELO 04/01 INS STRW | ICW
LC | 128709413 | 003/024 | T2NT EI PIT #3-CARBERRY SS 3/24 RMV STEP | TABLEMTN | ETL.5450.TOWR | 2024-05-03 | 2024-05-03 | 2025-04-11 | On-Time |  | 2027-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381993 | T2NT EI PIT #3-CARBERRY SS 3/24 RMV STEP | ICQ
LC | 128709417 | 002/020 | T2 EI PIT#3-CRBRRY SS 2/20 RMV STEPS | TABLEMTN | ETL.5450.TOWR | 2024-05-03 | 2024-05-03 | 2025-04-11 | On-Time |  | 2025-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381994 | T2 EI PIT#3-CRBRRY SS 2/20 RMV STEPS | ICQ
LC | 128709424 | 003/026 | T2 EI PIT#3-CARBERRY SS 3/26 RPR FOND | TABLEMTN | ETL.5450.TOWR | 2024-05-03 | 2024-05-03 | 2025-04-11 | On-Time |  | 2025-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381995 | T2 EI PIT#3-CARBERRY SS 3/26 RPR FOND | ICQ
LC | 128709433 | 002/019 | T2 EI PIT#3-CRBRRY SS 2/19 RMV STEPS | TABLEMTN | ETL.5450.TOWR | 2024-05-03 | 2024-05-03 | 2025-04-11 | On-Time |  | 2025-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381996 | T2 EI PIT#3-CRBRRY SS 2/19 RMV STEPS | ICQ
LC | 128709441 | 003/027 | T2NT EI PIT#3-CARBERRY SS 3/27 RMV STEP | TABLEMTN | ETL.5450.TOWR | 2024-05-03 | 2024-05-03 | 2025-04-11 | On-Time |  | 2027-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381997 | T2NT EI PIT#3-CARBERRY SS 3/27 RMV STEP | ICQ
LC | 128709642 | 005/102 | T2 EI CORDELIA #1 TAP 05/102R RPR GYWW | SACTO | ETL.8182.POLE.STPS | 2024-05-03 | 2024-05-03 | 2025-04-24 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337385 | T2 EI CORDELIA #1 TAP 05/102R RPR GYWW | ICW
LC | 128709660 | 000/003 | T2 DI PIT#1-MCARTHR 0/3 RPR JUMW | TABLEMTN | ETL.7790.INSL.NCER | 2024-05-03 | 2024-05-03 | 2024-09-04 | On-Time |  | 2024-08-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46247568 | T2 DI PIT#1-MCARTHR 0/3 RPR JUMW | ICW
LC | 128709782 | 000/000C | T2 DI PIT#3-PIT#1 0/0C RPR JUMS | TABLEMTN | ETL.5400.INSL.NCER | 2024-05-03 | 2024-05-03 | 2024-08-22 | On-Time |  | 2024-08-03 | 2025-05-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46247589 | T2 DI PIT#3-PIT#1 0/0C RPR JUMS | ICS
LC | 128709787 | 000/000B | T2 DI PIT#3-PIT#1 0/0B RPR JUMS | TABLEMTN | ETL.5400.INSL.NCER | 2024-05-03 | 2024-05-03 | 2024-08-22 | On-Time |  | 2024-08-03 | 2025-05-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46247588 | T2 DI PIT#3-PIT#1 0/0B RPR JUMS | ICS
LC | 128709919 | 033/002 | T2 EI TRINTY-MAPLE CRK 33/02L RMV VEG | EUREKA | ETL.8170.POLE.WDPS | 2024-05-03 | 2024-05-03 | 2024-11-06 | On-Time |  | 2025-05-03 | 2025-05-03 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128709950 | 031/006 | T2 EI TRINITY-MAPLE CREEK 31/06 CGI | EUREKA | ETL.8170.POLE.WOOD | 2024-05-03 | 2024-05-03 | 2025-04-18 | On-Time |  | 2024-08-03 | 2025-05-03 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 128710052 | 039/180 | T2 EI RND MT-TBL MTN #2 39/180 RPR ANCT | TABLEMTN | ETL.6070.TOWR | 2024-05-03 | 2024-05-03 | 2025-01-27 | On-Time |  | 2025-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46310381 | T2 EI RND MT-TBL MTN #2 39/180 RPR ANCT | ICQ
LC | 128710053 | 039/178 | T2 EI RND MTN-TBL MT #2 39/178 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2024-05-03 | 2024-05-03 | 2024-11-07 | On-Time |  | 2025-05-03 | 2025-05-03 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128710113 | 021/094 | T2 EI LS ESTRS-MTCLF 21/94 RPR FOND | METCALF | ETL.5353.TOWR | 2024-05-03 | 2024-05-03 | 2025-01-24 | On-Time |  | 2025-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46298824 | T2 EI LS ESTRS-MTCLF 21/94 RPR FOND | ICQ
LC | 128710149 | 010/122 | T2 EI KESWICK-TRINITY 10/122 RPR GYWW | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-03 | 2024-05-03 | 2024-08-21 | On-Time |  | 2024-08-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46252091 | T2 EI KESWICK-TRINITY 10/122 RPR GYWW | ICW
LC | 128717003 | 000/000A | T2 DI PIT #3-PIT #1-00/00A RPR JUMS | TABLEMTN | ETL.5400.INSL.NCER | 2024-05-06 | 2024-05-03 | 2024-08-22 | On-Time |  | 2024-08-03 | 2025-05-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46247587 | T2 DI PIT #3-PIT #1-00/00A RPR JUMS | ICS
LC | 128717044 | 000/009 | T2 DI PIT #1-MC ARTHUR 00/09 RPR JUMW | TABLEMTN | ETL.7790.INSL.NCER | 2024-05-06 | 2024-05-03 | 2024-09-04 | On-Time |  | 2024-08-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46250281 | T2 DI PIT #1-MC ARTHUR 00/09 RPR JUMW | ICW
LC | 128717079 | 009/072 | T2 DI CARIBOU-TABLE MTN-09/72 RPR JMPS | TABLEMTN | ETL.4440.INSL.CERA | 2024-05-06 | 2024-05-03 | 2024-06-06 | On-Time |  | 2024-08-03 | 2025-05-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46247585 | T2 DI CARIBOU-TABLE MTN-09/72 RPR JMPS | ICS
LC | 128717112 | 000/002 | T2NT DI PIT #1-CTNWD 00/02 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-05-06 | 2024-05-03 | 2025-04-08 | On-Time |  | 2027-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381513 | T2NT DI PIT #1-CTNWD 00/02 RPR STRT | ICQ
LC | 128717128 | 003/033 | T2 DI CRAG VIEW-CASCADE 03/33 COTTER | TABLEMTN | ETL.1350.INSL.NCER | 2024-05-06 | 2024-05-03 | 2024-09-06 | On-Time |  | 2025-05-03 | 2025-05-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46311390 | T2 DI CRAG VIEW-CASCADE 03/33 COTTER | ICS
LC | 128717131 | 008/084 | T2 DI PIT #5 RND MTN #1 8/84C RPR GYWW | TABLEMTN | ETL.5420.POLE.STPS | 2024-05-06 | 2024-05-03 | 2025-04-10 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46454289 | T2 DI PIT #5 RND MTN #1 8/84C RPR GYWW | ICW
LC | 128717182 | 003/033 | T2 DI CRAG VIEW-CASCADE 03/33 RPR JMPS | TABLEMTN | ETL.1350.INSL.NCER | 2024-05-06 | 2024-05-03 | 2024-09-06 | On-Time |  | 2024-08-03 | 2025-05-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46249499 | T2 DI CRAG VIEW-CASCADE 03/33 RPR JMPS | ICS
LC | 128717617 | 049/001B | T2 DI HUMBOLDT-TRINITY 49/1B RPR JMPW | EUREKA | ETL.1820.INSL.NCER | 2024-05-06 | 2024-05-03 | 2024-08-27 | On-Time |  | 2024-08-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46252301 | T2 DI HUMBOLDT-TRINITY 49/1B RPR JMPW | ICW
LC | 128717640 | 003/031 | T2 DI CRAG VIEW-CASCADE 3/31L TOUCH | TABLEMTN | ETL.1350.POLE.STPS | 2024-05-06 | 2024-05-03 | 2025-03-27 | On-Time |  | 2024-11-03 | 2025-05-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Steel | Repair | 46486717 | T2 DI CRAG VIEW-CASCADE 3/31L TOUCH | ICS
LC | 128717642 | 049/001A | T2 DI HUMBOLDT-TRIN 49/1A RPR JMPW | EUREKA | ETL.1820.INSL.NCER | 2024-05-06 | 2024-05-03 | 2024-08-27 | On-Time |  | 2024-08-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46252300 | T2 DI HUMBOLDT-TRIN 49/1A RPR JMPW | ICW
LC | 128717643 | 003/031 | T2 DI CRAG VIEW-CASCADE 03/31 RPR JMPS | TABLEMTN | ETL.1350.INSL.NCER | 2024-05-06 | 2024-05-03 | 2024-09-06 | On-Time |  | 2024-08-03 | 2025-05-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46249498 | T2 DI CRAG VIEW-CASCADE 03/31 RPR JMPS | ICS
LC | 128724938 | 049/001C | T2 DI HUMBOLT TRNITY 49/1C RPR JMPW | EUREKA | ETL.1820.INSL.NCER | 2024-05-08 | 2024-05-03 | 2024-08-27 | On-Time |  | 2024-08-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46252302 | T2 DI HUMBOLT TRNITY 49/1C RPR JMPW | ICW
LC | 128761462 | R002/019 | T2 DI RND MTN-CTTNWD #3 R2/19 RPR STRT | TABLEMTN | ETL.5650.TOWR | 2024-05-13 | 2024-05-03 | 2025-04-11 | On-Time |  | 2025-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310410 | T2 DI RND MTN-CTTNWD #3 R2/19 RPR STRT | ICQ
LC | 128767240 | 010/052 | T2 DI FULTON-PUEBLO-10/52 RPL RPTS | LAKEVLLE | ETL.1600.TOWR | 2024-05-13 | 2024-05-03 | 2025-03-11 | On-Time |  | 2025-05-03 | 2025-05-03 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46403750 | T2 DI FULTON-PUEBLO-10/52 RPL RPTS | ICB
LC | 128768388 | 005/026G | T2 PTSBURG SN MATEO 5/26G RPL INSS | CONCORD | ETL.5463.INSL | 2024-05-13 | 2024-05-03 | 2024-05-03 | Past Due |  | 2025-05-03 | 2025-05-03 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575041 | T2 DI PTSBURG SN MTEO 5/26E RPL INSS | 93K
LC | 128768466 | 091/462 | T2 MALIN-ROUND MNTN#2 91/462 RPR FOND | TABLEMTN | ETL.6020.TOWR | 2024-05-13 | 2024-05-03 | 2025-04-15 | On-Time |  | 2025-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381426 | T2 DI MALIN-ROUND MNTN#2 91/462 RPR FOND | ICQ
LC | 128768474 | 005/026F | T2 PTSBURG SAN MTEO 5/26F RPL INSS | CONCORD | ETL.5463.INSL | 2024-05-13 | 2024-05-03 | 2024-05-03 | Past Due |  | 2025-05-03 | 2025-05-03 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575041 | T2 DI PTSBURG SN MTEO 5/26E RPL INSS | 93K
LC | 128768476 | 005/026E | T2 PTSBRG SN MT 5/26E ATS RPL INSS | CONCORD | ETL.5463.INSL | 2024-05-13 | 2024-05-03 | 2024-05-03 | Past Due |  | 2025-05-03 | 2025-05-03 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575041 | T2 DI PTSBURG SN MTEO 5/26E RPL INSS | 93K
LC | 128768492 | 026/001 | T2 DI MNDCNO-WLTS-FT BRG 26/01 RPL ANCW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-13 | 2024-05-03 | 2025-04-03 | On-Time |  | 2025-05-03 | 2025-05-03 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574302 | T2 DI MNDCNO-WLTS-FT BRG 26/01 RPL ANCW | 93E
LC | 128768575 | 014/344 | T2 DI COTTONWD-BN#1 14/344 RPL STRW | TABLEMTN | ETL.6640.POLE.WOOD | 2024-05-13 | 2024-05-03 | 2025-04-29 | On-Time |  | 2025-05-03 | 2025-05-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Rotten | Structure-Wood | Replace | 35557359 | T2 DI COTTONWD-BN#1 14/344 RPL STRW | 70Y
LC | 128768624 | 044/381 | T2 PIT #1 COTONWOOD 44/381 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-05-13 | 2024-05-03 | 2024-05-03 | Past Due |  | 2025-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46381517 | T2NT DI PIT #1 COTONWOOD 44/381 RPR STRT | ICQ
LC | 128768786 | 008/066C | T2 DI CRAG VIEW-CASCADE 8/66C RPR JMPW | TABLEMTN | ETL.1350.INSL.NCER | 2024-05-13 | 2024-05-03 | 2024-09-07 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46249641 | T2 DI CRAG VIEW-CASCADE 8/66 RPR JMPW | ICW
LC | 128769084 | 039/005 | T2 DI MNDCNO-WLTS-FT BRG 39/05 RMV VEG | WILLITS | ETL.7550.POLE.WOOD | 2024-05-13 | 2024-05-03 | 2024-09-17 | On-Time |  | 2024-11-03 | 2025-05-03 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128769086 | 039/005 | T2 MNDCNO-WLTS-FT BRG 39/05 RPL ANCW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-13 | 2024-05-03 | 2024-05-03 | Past Due |  | 2025-05-03 | 2025-05-03 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35640750 | T2 MNDCNO-WLTS-FT BRG 39/05 RPL ANCW | 93E
LC | 128819397 | 020/007 | T2 DI MNDCN-WILTS-FRT BRG 20/7 RPR ANCW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-20 | 2024-05-03 | 2025-04-08 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46310145 | T2 DI MNDCN-WILTS-FRT BRG 20/7 RPR ANCW | ICW
LC | 128819399 | 009/074 | T2 DI CARIBOU-TBL MTN 9/74 RMV VEG | TABLEMTN | ETL.4440.TOWR | 2024-05-20 | 2024-05-03 | 2024-10-31 | On-Time |  | 2025-05-03 | 2025-05-03 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128837152 | 028/005 | T2 DI MNDCNO-WLTS-FRT BRG 28/5 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-21 | 2024-05-03 | 2025-04-03 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310154 | T2 DI MNDCNO-WLTS-FRT BRG 28/5 RPR GYWW | ICW
LC | 128837275 | 010/075C | T2 DI CARIBOU-TBL MTN 10/075C RPR GYWT | TABLEMTN | ETL.4440.POLE.NWOD | 2024-05-21 | 2024-05-03 | 2025-03-31 | On-Time |  | 2025-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46354031 | T2 DI CARIBOU-TBL MTN 10/075C RPR GYWT | ICQ
LC | 128837307 | 010/075A | T2 CARIBOU-TBL MTN 010/075A COMPLETE | TABLEMTN | ETL.4440.POLE.NWOD | 2024-05-21 | 2024-05-03 | 2025-03-31 | On-Time |  | 2025-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46354032 | T2 DI CARIBOU-TBL MTN 010/075A RPR GYWT | ICQ
LC | 128837332 | 010/075B | T2NT DI CARIBOU-TBL MTN 10/075B RPR STRT | TABLEMTN | ETL.4440.POLE.NWOD | 2024-05-21 | 2024-05-03 | 2025-04-02 | On-Time |  | 2027-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354033 | T2NT DI CARIBOU-TBL MTN 10/075B RPR STRT | ICQ
LC | 128837334 | 010/075B | T2 DI CARIBOU-TBL MTN 10/075B RPR GYWT | TABLEMTN | ETL.4440.POLE.NWOD | 2024-05-21 | 2024-05-03 | 2025-03-31 | On-Time |  | 2025-05-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46354034 | T2 DI CARIBOU-TBL MTN 10/075B RPR GYWT | ICQ
LC | 128902523 | 037/007 | T2 DI MNDCNO-WLTS-FRT BRG 37/7 RPL INSW | WILLITS | ETL.7550.INSL.NCER | 2024-05-28 | 2024-05-03 | 2025-04-09 | On-Time |  | 2025-05-03 | 2025-05-03 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574708 | T2 DI MNDCNO-WLTS-FRT BRG 37/7 RPL INSW | 93I
LC | 128902633 | 009/083 | T2 DI CRAG VIEW CSCADE 9/83R REGRADE | TABLEMTN | ETL.1350.POLE.STPS | 2024-05-28 | 2024-05-03 | 2025-03-20 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46454378 | T2 DI CRAG VIEW CSCADE 9/83R REGRADE | ICW
LC | 128902637 | 009/083 | T2 DI CRAG VIEW CSCADE 9/83 RPR OPGW | TABLEMTN | ETL.1350.POLE.STPS | 2024-05-28 | 2024-05-03 | 2025-03-20 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | OPGW - Wood | Repair | 46454379 | T2 DI CRAG VIEW CSCADE 9/83 RPR OPGW | ICW
LC | 128902673 | 016/117 | T2 DI CARIBOU TBL MTN 16/117 RPR JMPS | TABLEMTN | ETL.4440.INSL.NCER | 2024-05-28 | 2024-05-03 | 2025-04-05 | On-Time |  | 2025-05-03 | 2025-05-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46337443 | T2 DI CARIBOU TBL MTN 16/117 RPR JMPS | ICS
LC | 128902733 | 011/105 | T2 DI EL DDO-MSRI FLT #2 11/105 RPR JUMS | SACTO | ETL.1540.INSL.NCER | 2024-05-28 | 2024-05-03 | 2024-09-13 | On-Time |  | 2025-05-03 | 2025-05-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46257405 | T2 DI EL DDO-MSRI FLT #2 11/105 RPR JUMS | ICS
LC | 128902991 | 010/094 | T2 DI EL DORADO-MF #1 10/94 TOUCH | SACTO | ETL.1530.TOWR | 2024-05-28 | 2024-05-03 | 2025-02-24 | On-Time |  | 2024-11-03 | 2025-05-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46463296 | T2 DI EL DORADO-MF #1 10/94 RPR STRT | ICQ
LC | 128902993 | 010/094 | T2 DI EL DORADO-MF #2 10/94 RPR INSS | SACTO | ETL.1540.INSL | 2024-05-28 | 2024-05-03 | 2025-01-29 | On-Time |  | 2025-05-03 | 2025-05-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46452749 | T2 DI EL DORADO-MF #2 10/94 RPR INSS | ICS
LC | 128910531 | 013/013 | T2 DI MNDCNO-WLTS-FRT BRG 13/13 RPL INSW | WILLITS | ETL.7550.INSL.NCER | 2024-05-29 | 2024-05-03 | 2025-04-04 | On-Time |  | 2025-05-03 | 2025-05-03 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574195 | T2 DI MNDCNO-WLTS-FRT BRG 13/13 RPL INSW | 93I
LC | 128957600 | 038/004 | T2 DI MNDCN-WLTS-FRT BRG 38/4 RPL STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-31 | 2024-05-03 | 2025-01-21 | On-Time |  | 2025-05-03 | 2025-05-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35604944 | T2 DI MNDCN-WLTS-FRT BRG 38/4 RPL STRW | 70Y
LC | 128957967 | 013/013-GUY | T2 DI MDCO WLTS FRT BRG 13/13-G RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-31 | 2024-05-03 | 2025-02-07 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310142 | T2 DI MDCO WLTS FRT BRG 13/13-G RPR GYWW | ICW
LC | 128958331 | 038/004-GUY | T2 DI MNDCN-WLTS-FRT BRG 38/4 RMV VEG | WILLITS | ETL.7550.POLE.WOOD | 2024-05-31 | 2024-05-03 | 2025-01-23 | On-Time |  | 2025-05-03 | 2025-05-03 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128958847 | 019/006 | T2 DI MNDCN-WLTS-FRT BRG 19/6 RPR STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-31 | 2024-05-03 | 2025-04-09 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310143 | T2 DI MNDCN-WLTS-FRT BRG 19/6 RPR STRW | ICW
LC | 128959205 | 019/006 | T2 DI MNDCN-WLTS-FRT BRG 19/6 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-31 | 2024-05-03 | 2025-04-09 | On-Time |  | 2025-05-03 | 2025-05-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310144 | T2 DI MNDCN-WLTS-FRT BRG 19/6 RPR GYWW | ICW
LC | 123496490 | 001/012 | T3NT EI MRAGA-SN LEANDR #1 1/12 RPR FOND | CONCORD | ETL.2770.TOWR | 2022-05-04 | 2022-05-04 | 2023-04-18 | On-Time |  | 2025-05-04 | 2025-05-04 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3N PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45697860 | T3NT EI MRAGA-SN LEANDR #1 1/12 RPR FOND | ICQ
LC | 123508538 | 071/360A | T2NT EI MALIN-RND MTN #2 71/360A BNT STL | TABLEMTN | ETL.6020.TOWR | 2022-05-05 | 2022-05-04 | 2023-08-14 | On-Time |  | 2025-05-04 | 2025-05-04 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45616771 | T2 EI MALIN-RUND MTN #2 71/360A BNT STL | ICQ
LC | 123508687 | 071/360A | T2NT EI MALN-RND MTN #2 71/360A RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2022-05-05 | 2022-05-04 | 2023-10-11 | On-Time |  | 2025-05-04 | 2025-05-04 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45650757 | T2 EI MALIN-RUND MTN #2 71/360A RPR GYWT | ICS
LC | 123536212 | 005/066 | T2NT DI BRNS-LONE STAR#1 5/66 RPL HRDD | MOSSLNDG | ETL.6230.POLE.WOOD | 2022-05-07 | 2022-05-04 | 2023-04-13 | On-Time |  | 2025-05-04 | 2025-05-04 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 45606211 | T2 DI BRNS-LONE STAR#1 5/66 RPL HRDD | ICW
LC | 128710624 | 004/030 | T2 WISHON-COPPERMINE 04/30 RMV ENCR | FRESNO | ETL.9330.TOWR | 2024-05-04 | 2024-05-04 | 2024-09-10 | On-Time |  | 2024-11-04 | 2025-05-04 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46249763 | T2 WISHON-COPPERMINE 04/30 RMV ENCR | CHR
LC | 128710653 | 002/011 | T2 BRICBRG JCT-MRPS TP 02/11 RPL HRDW | FRESNO | ETL.8651.POLE.WOOD | 2024-05-04 | 2024-05-04 | 2025-03-28 | On-Time |  | 2025-05-04 | 2025-05-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Hardware-Wood | Replace | 46298034 | T2 BRICBRG JCT-MRPS TP 02/11 RPL HRDW | ICW
LC | 123512941 | 063/318 | T2NT EI MLN-RND MTN #2 63/318 RPR FOND | TABLEMTN | ETL.6020.TOWR | 2022-05-05 | 2022-05-05 | 2023-09-12 | On-Time |  | 2025-05-05 | 2025-05-05 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45616541 | T2 EI MLN-RND MTN #2 63/318 RPR FOND | ICQ
LC | 123513950 | 003/022 | T3NT EI MORAGA-SAN LNDRO #1 3/22 REGRADE | CONCORD | ETL.2770.TOWR | 2022-05-05 | 2022-05-05 | 2023-04-18 | On-Time |  | 2025-05-05 | 2025-05-05 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3N PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45691705 | T3NT EI MORAGA-SAN LNDRO #1 3/22 REGRADE | ICQ
LC | 123516508 | 002/062 | T2NT EI JEFFERSON-STANFORD 2/62 RMV VEG | METCALF | ETL.7220.POLE.WOOD | 2022-05-05 | 2022-05-05 | 2023-12-06 | On-Time |  | 2025-05-05 | 2025-05-05 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2N PRTO FRAB | Overgrown | Vegetation | Remove
LC | 123516804 | 071/362 | T2NT EI MLIN-RND MTN #2 71/362 BNT STEEL | TABLEMTN | ETL.6020.TOWR | 2022-05-05 | 2022-05-05 | 2023-08-26 | On-Time |  | 2025-05-05 | 2025-05-05 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | Anti-Climbing Guard | Structure-Tower | Repair | 45616807 | T2 EI MLIN-ROUND MTN #2 71/362 BNT STEEL | ICQ
LC | 123517326 | 003/029 | T3NT EI MORGA-SAN LNDR #1 3/29 BNT STEEL | CONCORD | ETL.2770.TOWR | 2022-05-05 | 2022-05-05 | 2023-04-18 | On-Time |  | 2025-05-05 | 2025-05-05 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45692022 | T3 EI MORGA-SAN LANDRO #1 3/29 BNT STEEL | ICQ
LC | 123517925 | 012/086 | T2NT EI GRN VALLEY-LLAGAS 12/86 RMV VEG | MOSSLNDG | ETL.1720.POLE.WDPS | 2022-05-05 | 2022-05-05 | 2023-12-07 | On-Time |  | 2025-05-05 | 2025-05-05 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO FRAB | Overgrown | Vegetation | Trim
LC | 123519863 | 091/467 | T2NT EI MLIN-RND MTN #2 91/467 BNT STEEL | TABLEMTN | ETL.6020.TOWR | 2022-05-05 | 2022-05-05 | 2023-08-16 | On-Time |  | 2025-05-05 | 2025-05-05 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45617413 | T2 EI MALIN-RND MTN #2 91/467 BNT STEEL | ICQ
LC | 123582470 | 001/007 | T2NT DI PIT #4 TAP 1/07 BNT STEEL | TABLEMTN | ETL.5432.TOWR | 2022-05-12 | 2022-05-05 | 2023-08-08 | On-Time |  | 2025-05-05 | 2025-05-05 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644268 | T2 DI PIT #4 TAP 001/007 BNT STEEL | ICQ
LC | 123592876 | 012/243 | T2NT DI COLGATE-PALERMO 012/243 RPL POLE | SACTO | ETL.6500.POLE.WOOD | 2022-05-14 | 2022-05-05 | 2023-06-02 | On-Time |  | 2025-05-05 | 2025-05-05 | 372 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 31607173 | T2 DI CLGTE-PLMERMO 6/113 RPL STRW | 70Y
LC | 123593651 | 009/219 | T2NT DI CLGTE-GRS VLY 009/219 RMV BUTT | SACTO | ETL.6490.POLE.WOOD | 2022-05-14 | 2022-05-05 | 2023-02-08 | On-Time |  | 2025-05-05 | 2025-05-05 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2N PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 45657039 | T2 DI CLGTE-GRS VLY 009/219 RMV BUTT | ICW
LC | 125273529 | 011/134 | T2NT EI DRUM-SUMMIT #2 011/134R RPL PL | SACTO | ETL.1450.POLE.WDPS | 2023-01-03 | 2022-05-05 | 2023-08-18 | On-Time |  | 2025-05-05 | 2025-05-05 | 372 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 31634269 | T3 DI DRUM-SUMMIT #2 001/013R RPL STRW | 70Y
LC | 128711635 | 029/211 | T2 DRUM-RIO OSO #2 29/211 RPL INSS | SACTO | ETL.1430.INSL.NCER | 2024-05-05 | 2024-05-05 | 2025-04-21 | On-Time |  | 2025-05-05 | 2025-05-05 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW NONR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570801 | T2 DI DRM RIO OSO #2 RPL INSS 3 TWRS | 93K
LC | 128711710 | 027/200 | T2 DRUM-RIO OSO #2 027/200 RPL INSS | SACTO | ETL.1430.INSL.CERA | 2024-05-05 | 2024-05-05 | 2025-04-21 | On-Time |  | 2025-05-05 | 2025-05-05 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW NONR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570801 | T2 DI DRM RIO OSO #2 RPL INSS 3 TWRS | 93K
LC | 123530951 | 000/003 | T3NT DI DIABLO-MDWY #3 0/3 RPR FOND | PISMOBCH | ETL.5980.TOWR | 2022-05-06 | 2022-05-06 | 2023-07-25 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45649556 | T3 DI DIABLO-MDWY #3 0/3 RPR FOND | ICQ
LC | 128712890 | 007/142 | T2 EI KESWICK-CASCADE 7/142 RPR STRW | TABLEMTN | ETL.7260.POLE.WOOD | 2024-05-06 | 2024-05-06 | 2025-01-09 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46300521 | T2 EI KESWICK-CASCADE 7/142 RPR STRW | ICW
LC | 128713584 | :000/004 | T2 EI STNSLS-MLN SS-MNTC#1 :0/4 RPR FOND | VICTOR | ETL.3830.TOWR | 2024-05-06 | 2024-05-06 | 2025-04-07 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416618 | T2 EI STNSLS-MLN SS-MNTC#1 :0/4 RPR FOND | ICQ
LC | 128713727 | 009/000 | T2 WV SALINAS-FORT ORD #2 09/00 RMV NEST | MOSSLNDG | ETL.8423.POLE.NWOD | 2024-05-06 | 2024-05-06 | 2025-02-21 | On-Time |  | 2025-05-06 | 2025-05-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46391199 | T2 WV SALINAS-FORT ORD #2 09/00 RMV NEST | ICS
LC | 128713837 | 015/071 | T2 EI PALERMO-COLGATE 15/71 RPR STRT | TABLEMTN | ETL.5360.TOWR | 2024-05-06 | 2024-05-06 | 2025-03-17 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310431 | T2 EI PALERMO-COLGATE 15/71 RPR STRT | ICQ
LC | 128714277 | 012/004 | T2 CARIBOU-PLUMAS JCT 12/4 RMV VEG | TABLEMTN | ETL.6290.POLE.NWOD | 2024-05-06 | 2024-05-06 | 2024-05-23 | On-Time |  | 2024-08-06 | 2025-05-06 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW PATR CNCL OH FMOB TR2 PRTO FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128714319 | 007/149 | T2 EI KESWICK-CASCADE 7/149 COMPLETE | TABLEMTN | ETL.7260.POLE.WOOD | 2024-05-06 | 2024-05-06 | 2025-03-29 | On-Time |  | 2025-05-06 | 2025-05-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573784 | T2 EI KESWICK-CASCADE 7/149 RPL POLE | 70Y
LC | 128714323 | ;000/019 | T2 CARIBOU #2 ;000/019 RMV VEG | TABLEMTN | ETL.6280.POLE.NWOD | 2024-05-06 | 2024-05-06 | 2024-06-04 | On-Time |  | 2024-08-06 | 2025-05-06 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW PATR CNCL OH FMOB TR2 PRTO FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128714340 | ;001/002 | T2 CARIBOU #2 ;001/002 RMV VEG | TABLEMTN | ETL.6280.POLE.NWOD | 2024-05-06 | 2024-05-06 | 2024-05-23 | On-Time |  | 2024-08-06 | 2025-05-06 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW PATR CNCL OH FMOB TR2 PRTO FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128714721 | 003/067 | T2 EI CORDELIA #1 TAP 03/067 RPR STRW | SACTO | ETL.8182.POLE.WOOD | 2024-05-06 | 2024-05-06 | 2025-03-12 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337384 | T2 EI CORDELIA #1 TAP 03/067 RPR STRW | ICW
LC | 128714906 | 003/024 | T2 EI CTTONWD-DELEVAN #1 3/24 RPL DMPS | TABLEMTN | ETL.4550.INSL | 2024-05-06 | 2024-05-06 | 2025-04-02 | On-Time |  | 2025-05-06 | 2025-05-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Damper-Steel | Replace | 46300593 | T2 EI CTTONWD-DELEVAN #1 3/24 RPL DMPS | ICS
LC | 128715013 | 071/619 | T2 COTONWD-DELVAN #2 71/619 TOUCH | TABLEMTN | ETL.4580.TOWR | 2024-05-06 | 2024-05-06 | 2025-03-03 | On-Time |  | 2024-11-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476193 | T2 COTONWD-DELVAN #2 71/619 TOUCH | ICQ
LC | 128715028 | 040/185 | T2 EI RND MT-TBL MTN #2 40/185 UNBURY | TABLEMTN | ETL.6070.TOWR | 2024-05-06 | 2024-05-06 | 2025-01-27 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46310382 | T2 EI RND MT-TBL MTN #2 40/185 UNBURY | ICQ
LC | 128715029 | 040/185 | T2 EI RND MT-TBL MTN #2 40/185 RPR ANCT | TABLEMTN | ETL.6070.TOWR | 2024-05-06 | 2024-05-06 | 2025-01-27 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46310383 | T2 EI RND MT-TBL MTN #2 40/185 RPR ANCT | ICQ
LC | 128715421 | 000/004 | T2 EI VLY SPRNGS CLVRS 0/4 RPL STRW | VICTOR | ETL.8220.POLE.WOOD | 2024-05-06 | 2024-05-06 | 2025-05-06 | On-Time |  | 2025-05-06 | 2025-05-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573396 | T2 EI VLY SPRNGS CLVRS 0/4 RPL STRW | 70Y
LC | 128715767 | 029/235 | T2 EI CRESTA-RIO OSO 029/235 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-06 | 2024-05-06 | 2024-12-30 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381267 | T2 EI CRESTA-RIO OSO 029/235 RPR FOND | ICQ
LC | 128715768 | 028/232 | T2 EI CRESTA-RIO OSO 028/232 INS HRDT | TABLEMTN | ETL.4590.TOWR | 2024-05-06 | 2024-05-06 | 2024-12-30 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381268 | T2 EI CRESTA-RIO OSO 028/232 INS HRDT | ICQ
LC | 128715814 | 011/106 | T2 UKIAH-HOPLND-CLVRDALE 11/106 TOUCH | WILLITS | ETL.4050.POLE.NWOD | 2024-05-06 | 2024-05-06 | 2025-04-29 | On-Time |  | 2024-11-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46507780 | T2 UKIAH-HOPLND-CLVRDALE 11/106 TOUCH | ICW
LC | 128716068 | :007/040 | T2 EI STLS-MLNS SW ST-MNT :7/40 RPR FND | VICTOR | ETL.3830.TOWR | 2024-05-06 | 2024-05-06 | 2025-04-08 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416620 | T2 EI STLS-MLNS SW ST-MNT :7/40 RPR FND | ICQ
LC | 128716131 | 029/515 | T2 KESWICK-TRINITY 29/515 GO95 | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-06 | 2024-05-06 | 2025-04-05 | On-Time |  | 2025-05-06 | 2025-05-06 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35555622 | T2 KESWICK-TRINITY 29/515 GO95 | 93G
LC | 128716132 | 029/004 | T2 EI TRINITY-MAPLE CREEK 29/4 RPR SPLW | EUREKA | ETL.8170.INSL.NCER | 2024-05-06 | 2024-05-06 | 2025-04-14 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Splice-Wood | Repair | 46345849 | T2 EI TRINITY-MAPLE CREEK 29/4 RPR SPLW | ICW
LC | 128716133 | 029/002 | T2 EI TRINITY-MAPLE CREEK 29/2 RPR ANCW | EUREKA | ETL.8170.POLE.WOOD | 2024-05-06 | 2024-05-06 | 2024-09-14 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46322230 | T2 EI TRINITY-MAPLE CREEK 29/2 RPR ANCW | ICW
LC | 128716134 | 029/004 | T2 EI TRINITY-MAPLE CREEK 29/4 RPR JMPW | EUREKA | ETL.8170.INSL.NCER | 2024-05-06 | 2024-05-06 | 2025-04-13 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Jumper-Wood | Repair | 46345850 | T2 EI TRINITY-MAPLE CREEK 29/4 RPR JMPW | ICW
LC | 128716147 | 030/000 | T2 EI TRINITY-MPLE CRK 30/000L RPL ANCW | EUREKA | ETL.8170.POLE.WDPS | 2024-05-06 | 2024-05-06 | 2025-04-14 | On-Time |  | 2025-05-06 | 2025-05-06 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572082 | T2 EI TRINITY-MPLE CRK 30/000L RPL ANCW | 93E
LC | 128716148 | 029/002 | T2 EI TRINITY-MAPLE CREEK 29/2 RPR JMPW | EUREKA | ETL.8170.INSL.NCER | 2024-05-06 | 2024-05-06 | 2025-04-14 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Jumper-Wood | Repair | 46345847 | T2 EI TRINITY-MAPLE CREEK 29/2 RPR JMPW | ICW
LC | 128716152 | 029/003 | T2 EI TRINITY-MAPLE CREEK 29/3 RPR JMPW | EUREKA | ETL.8170.INSL.NCER | 2024-05-06 | 2024-05-06 | 2025-04-14 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Jumper-Wood | Repair | 46345848 | T2 EI TRINITY-MAPLE CREEK 29/3 RPR JMPW | ICW
LC | 128716187 | 027/005 | T2 EI RIO DL JCT-BRDGVLLE 27/05 RPR GYWW | EUREKA | ETL.7850.POLE.NWOD | 2024-05-06 | 2024-05-06 | 2025-06-14 | Past Due |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345845 | T2 EI RIO DL JCT-BRDGVLLE 27/05 RPR GYWW | ICW
LC | 128716278 | 004/091 | T2 DEL MONTE-VIEJO 4/091 GO95 | MOSSLNDG | ETL.6710.POLE.WOOD | 2024-05-06 | 2024-05-06 | 2025-04-25 | On-Time |  | 2025-05-06 | 2025-05-06 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35555547 | T2 DEL MONTE-VIEJO 4/091 GO95 | 93G
LC | 128716328 | 015/120 | T2 EI PIT #3-CARBERY SS 15/120 BNT STEEL | TABLEMTN | ETL.5450.TOWR | 2024-05-06 | 2024-05-06 | 2025-04-22 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381998 | T2 EI PIT #3-CARBERY SS 15/120 BNT STEEL | ICQ
LC | 128716544 | 005/016 | T2 EI SONOMA-PUEBLO 5/16 RPL STRW | LAKEVLLE | ETL.3810.POLE.WOOD | 2024-05-06 | 2024-05-06 | 2025-04-30 | On-Time |  | 2025-05-06 | 2025-05-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572886 | T2 EI SONOMA-PUEBLO 5/16 RPL STRW | 70Y
LC | 128716547 | 003/009 | T2 SONOMA-PUEBLO 3/9 RPL STRW | LAKEVLLE | ETL.3810.POLE.WOOD | 2024-05-06 | 2024-05-06 | 2025-04-28 | On-Time |  | 2025-05-06 | 2025-05-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35636234 | T2 EI SONOMA-PUEBLO 3/9 RPL STRW | 70Y
LC | 128716616 | 016/072 | T2 EI LOS ESTEROS-MTCALF 16/072 RPL INSS | METCALF | ETL.5353.INSL | 2024-05-06 | 2024-05-06 | 2025-03-31 | On-Time |  | 2025-05-06 | 2025-05-06 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574629 | T2 EI LOS ESTEROS-METCALF RPL INSS IN 7 | 93K
LC | 128716618 | 016/074 | T2 LOS ESTEROS-METCLF 16/074 RPL INSS | METCALF | ETL.5353.INSL | 2024-05-06 | 2024-05-06 | 2024-05-06 | Past Due |  | 2025-05-06 | 2025-05-06 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574629 | T2 EI LOS ESTEROS-METCALF RPL INSS IN 7 | 93K
LC | 128716689 | 030/002 | T2 EI TRINITY-MAPLE CRK 31/002R RPR GYWW | EUREKA | ETL.8170.POLE.WDPS | 2024-05-06 | 2024-05-06 | 2024-06-17 | On-Time |  | 2024-11-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46247504 | T2 EI TRINITY-MAPLE CRK 31/002R RPR GYWW | ICW
LC | 128716691 | 030/002 | T2 TRINITY-MAPLE CRK 30/002R COMPLETE | EUREKA | ETL.8170.POLE.WDPS | 2024-05-06 | 2024-05-06 | 2025-04-15 | On-Time |  | 2025-05-06 | 2025-05-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572080 | T2 EI TRINITY-MAPLE CRK 30/002R RPL STRW | 70Y
LC | 128716694 | 030/002 | T2 TRINITY-MAPLE CRK 30/002C COMPLETE | EUREKA | ETL.8170.POLE.WDPS | 2024-05-06 | 2024-05-06 | 2025-04-15 | On-Time |  | 2025-05-06 | 2025-05-06 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572080 | T2 EI TRINITY-MAPLE CRK 30/002R RPL STRW | 70Y
LC | 128716697 | 008/112 | T2 EI KESWICK-TRINITY 8/112 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-06 | 2024-05-06 | 2024-09-11 | On-Time |  | 2024-08-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46250707 | T2 EI KESWICK-TRINITY 8/112 RPR JUMW | ICW
LC | 128716700 | 029/008 | T2 EI TRINITY-MAPLE CRK 29/08 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-05-06 | 2024-05-06 | 2024-09-14 | On-Time |  | 2024-08-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46252303 | T2 EI TRINITY-MAPLE CRK 29/08 RPR GYWW | ICW
LC | 128716701 | 030/002 | T2 TRINITY-MAPLE CRK 30/002L COMPLETE | EUREKA | ETL.8170.POLE.WDPS | 2024-05-06 | 2024-05-06 | 2025-04-15 | On-Time |  | 2025-05-06 | 2025-05-06 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572080 | T2 EI TRINITY-MAPLE CRK 30/002R RPL STRW | 70Y
LC | 128716717 | 011/140 | T2 EI KESWICK-TRINITY 11/140 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-06 | 2024-05-06 | 2024-09-09 | On-Time |  | 2024-08-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251639 | T2 EI KESWICK-TRINITY 11/140 RPR JUMS | ICW
LC | 128716750 | 011/136 | T2 EI KESWICK-TRINITY 11/136 RPR JUMW | TABLEMTN | ETL.7270.INSL.CERA | 2024-05-06 | 2024-05-06 | 2024-09-09 | On-Time |  | 2024-08-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251637 | T2 EI KESWICK-TRINITY 11/136 RPR JUMS | ICW
LC | 128716792 | 050/205 | T2 EI DIABLO-GATES #1 50/205 RPR GYWT | PISMOBCH | ETL.5960.TOWR | 2024-05-06 | 2024-05-06 | 2025-04-03 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW REMT ACCL COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46391322 | T2 EI DIABLO-GATES #1 50/205 RPR GYWT | ICQ
LC | 128716810 | 051/207 | T2 DIABLO-GATES #1 51/207 COMPLETE | PISMOBCH | ETL.5960.TOWR | 2024-05-06 | 2024-05-06 | 2025-04-03 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW REMT ACCL COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46391323 | T2 EI DIABLO-GATES #1 51/207 RPR GYWT | ICQ
LC | 128716910 | 005/113 | T2 DI COTTONWOOD RB 5/113 RPL INSW | TABLEMTN | ETL.6660.INSL.NCER | 2024-05-06 | 2024-05-06 | 2024-09-11 | On-Time |  | 2024-08-06 | 2025-05-06 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35552631 | T2 DI COTTONWOOD RB 5/113 RPL INSW | 93I
LC | 128717663 | 020/463 | T2 DI DRM GRS VLY WMR 20/463 RPR IBWW | SACTO | ETL.6760.INSL.NCER | 2024-05-06 | 2024-05-06 | 2025-04-21 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46324600 | T2 DI DRM GRS VLY WMR 20/463 RPR IBWW | ICW
LC | 128717694 | 027/222 | T2 DI PIT #1-COTTONWOOD 27/222 RPR JUMS | TABLEMTN | ETL.5390.INSL.NCER | 2024-05-06 | 2024-05-06 | 2024-11-08 | On-Time |  | 2024-08-06 | 2025-05-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46247596 | T2 DI PIT #1-COTTONWOOD 27/222 RPR JUMS | ICS
LC | 128717721 | 062/008 | T2 DI GRBRVL-LYTNVL 62/08 RPR JUMW | WILLITS | ETL.8365.INSL.NCER | 2024-05-06 | 2024-05-06 | 2024-08-16 | On-Time |  | 2024-11-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46252680 | T2 DI GRBRVL-LYTNVL 62/08 RPR JUMW | ICW
LC | 128717740 | 229 | T2 DI PIT #1-COTTONWOOD 0/1 RPR JUMS | TABLEMTN | ETL.5390.SWIT | 2024-05-06 | 2024-05-06 | 2024-11-05 | On-Time |  | 2024-08-06 | 2025-05-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46247594 | T2 DI PIT #1-COTTONWOOD 0/1 RPR JUMPS | ICS
LC | 128723133 | 015/006 | T2 DI MNDCNO-WLLTS-FRT BRG 15/6 RPR STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-07 | 2024-05-06 | 2025-04-14 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310157 | T2 DI MNDCNO-WLLTS-FRT BRG 15/6 RPR STRW | ICW
LC | 128723134 | 015/006 | T2 DI MNDCNO-WLTS-FRT BRG 15/6 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-07 | 2024-05-06 | 2025-04-14 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310158 | T2 DI MNDCNO-WLTS-FRT BRG 15/6 RPR GYWW | ICW
LC | 128723136 | 006/113 | T2 DI BRIONES TAP 006/113 RPR JUMW | CONCORD | ETL.7055.INSL.NCER | 2024-05-07 | 2024-05-06 | 2024-07-17 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46246793 | T2 DI BRIONES TAP 006/113 RPR JUMW | ICW
LC | 128723138 | 046/404 | T2 DI PIT #1-COTTONWOOD 046/404 RPR JUMS | TABLEMTN | ETL.5390.INSL.NCER | 2024-05-07 | 2024-05-06 | 2024-11-05 | On-Time |  | 2024-08-06 | 2025-05-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46247595 | T2 DI PIT #1-COTTONWOOD 046/404 RPR JUMS | ICS
LC | 128723399 | 016/000 | T2 DI MNDCNO-WLTS-FRT BRG 16/0 COTTER | WILLITS | ETL.7550.INSL.NCER | 2024-05-07 | 2024-05-06 | 2024-10-23 | On-Time |  | 2024-08-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46252596 | T2 DI MNDCNO-WLTS-FRT BRG 16/0 COTTER | ICW
LC | 128723935 | 005/103 | T2 EI CORDELIA #1 TAP 05/103 WASH INSW | SACTO | ETL.8182.INSL | 2024-05-08 | 2024-05-06 | 2025-04-24 | On-Time |  | 2025-05-06 | 2025-05-06 | 622 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | Contaminated | Insulator | Ground Wash | 46337350 | T2 EI CORDELIA #1 TAP 05/103 WASH INSW | ICD
LC | 128723950 | 005/104 | T2 EI CORDELIA #1 TAP 05/104 WASH INSW | SACTO | ETL.8182.INSL | 2024-05-08 | 2024-05-06 | 2025-04-24 | On-Time |  | 2025-05-06 | 2025-05-06 | 622 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | Contaminated | Insulator | Ground Wash | 46337349 | T2 EI CORDELIA #1 TAP 05/104 WASH INSW | ICD
LC | 128745140 | 000/004 | T2 DI PIT#1 CTTNWD 00/004 RPR JUMS | TABLEMTN | ETL.5390.INSL.NCER | 2024-05-10 | 2024-05-06 | 2025-04-21 | On-Time |  | 2025-05-06 | 2025-05-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46452725 | T2 DI PIT#1 CTTNWD 00/004 RPR JUMS | ICS
LC | 128746058 | 052/004A | T2 DI HUMBOLDT-TRINITY 52/04A INS STRW | EUREKA | ETL.1820.POLE.NWOD | 2024-05-10 | 2024-05-06 | 2024-08-26 | On-Time |  | 2024-11-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46247358 | T2 DI HUMBOLDT-TRINITY 52/04A INS STRW | ICW
LC | 128746162 | 052/004A | T2 DI HUMBOLDT-TRINITY 52/04A RPR JMPW | EUREKA | ETL.1820.INSL.NCER | 2024-05-10 | 2024-05-06 | 2024-08-26 | On-Time |  | 2024-08-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46247357 | T2 DI HUMBOLDT-TRINITY 52/04A RPR JMPW | ICW
LC | 128746208 | 008/010 | T2 DI TRINITY-MAPLE CREEK 8/10 RPR JUMW | EUREKA | ETL.8170.INSL.NCER | 2024-05-10 | 2024-05-06 | 2025-03-22 | On-Time |  | 2024-11-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46247503 | T2 DI TRINITY-MAPLE CREEK 08/10 RPR JMPW | ICW
LC | 128768751 | 012/067 | T2 DI FLTN-IGNACIO #1 12/67 TOUCH | LAKEVLLE | ETL.4680.TOWR | 2024-05-13 | 2024-05-06 | 2025-03-12 | On-Time |  | 2024-11-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAR DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46474469 | T2 DI FLTN-IGNACIO #1 12/67 TOUCH | ICQ
LC | 128773769 | 057/315 | T2 DI TMBLR SN LS OBSP 57/315 RMV VEG | PISMOBCH | ETL.3960.TOWR | 2024-05-14 | 2024-05-06 | 2025-02-25 | On-Time |  | 2025-05-06 | 2025-05-06 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128773931 | 057/315 | T2NT DI TMBLR SN LS OBSP 57/315 RPR STRT | PISMOBCH | ETL.3960.TOWR | 2024-05-14 | 2024-05-06 | 2025-03-24 | On-Time |  | 2027-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46303930 | T2NT DI TMBLR SN LS OBSP 57/315 RPR STRT | ICQ
LC | 128774115 | 063/003C | T2 DI HMBLDT-TRINITY 063/003C RPL POLE | EUREKA | ETL.1820.POLE.WOOD | 2024-05-14 | 2024-05-06 | 2025-04-24 | On-Time |  | 2025-05-06 | 2025-05-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574640 | T2 DI HMBLDT-TRINITY 063/003C RPL POLE | 70Y
LC | 128836788 | 053/478 | T2 DI RND MTN-CTTNWD #3 53/478 RPR FOND | TABLEMTN | ETL.5650.TOWR | 2024-05-21 | 2024-05-06 | 2025-01-08 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46310412 | T2 DI RND MTN-CTTNWD #3 53/478 RPR FOND | ICQ
LC | 128836906 | 015/007 | T2 DI MNDCNO-WLTS FRT BRG 15/7 RPR STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-21 | 2024-05-06 | 2025-03-31 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310159 | T2 DI MNDCNO-WLTS FRT BRG 15/7 RPR STRW | ICW
LC | 128837401 | 016/372 | T2 DI DRUM-GV-WEI 16/372 RPR GYWW | SACTO | ETL.6760.POLE.WOOD | 2024-05-21 | 2024-05-06 | 2025-04-23 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324602 | T2 DI DRUM-GV-WEI 16/372 RPR GYWW | ICW
LC | 128837408 | 053/476 | T2 DI RND MTN CTNWOOD 53/476 RPR STRT | TABLEMTN | ETL.5650.TOWR | 2024-05-21 | 2024-05-06 | 2025-04-24 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310411 | T2 DI RND MTN CTNWOOD 53/476 RPR STRT | ICQ
LC | 128837409 | 016/372 | T2 DI DRUM-GV-WEI 16/372 INSP STRW | SACTO | ETL.6760.POLE.WOOD | 2024-05-21 | 2024-05-06 | 2024-09-30 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46324603 | T2 DI DRUM-GV-WEI 16/372 INSP STRW | ICW
LC | 128837467 | 000/007 | T2 DI PIT#3-PIT#1 0/7 BNT STEEL | TABLEMTN | ETL.5400.TOWR | 2024-05-21 | 2024-05-06 | 2025-04-22 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46382003 | T2 DI PIT#3-PIT#1 0/7 BNT STEEL | ICQ
LC | 128886848 | 001/011 | T2 DI PIT #1-COTTONWOOD 1/011 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-05-24 | 2024-05-06 | 2025-04-28 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381532 | T2 DI PIT #1-COTTONWOOD 1/011 RPR STRT | ICQ
LC | 128887155 | 019/439 | T2 DI DRUM GRS VLY WIMR 19/439 RPL HRDW | SACTO | ETL.6760.POLE.WOOD | 2024-05-24 | 2024-05-06 | 2025-02-26 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46324601 | T2 DI DRUM GRS VLY WIMR 19/439 RPL HRDW | ICW
LC | 128887400 | 008/060 | T2 DI CARIBOU-TABLE MNTN 08/60 RPR SHLS | TABLEMTN | ETL.4440.TOWR | 2024-05-24 | 2024-05-06 | 2025-04-02 | On-Time |  | 2025-05-06 | 2025-05-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46337334 | T2 DI CARIBOU-TABLE MNTN 08/60 RPR SHLS | ICS
LC | 128887465 | 007/108 | T2 DI CENTERVLE-TBLE MTN 7/108 RPL STRW | TABLEMTN | ETL.6320.POLE.WOOD | 2024-05-24 | 2024-05-06 | 2025-03-03 | On-Time |  | 2025-05-06 | 2025-05-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35594061 | T2 DI CENTERVLE-TBLE MTN 7/108 RPL STRW | 70Y
LC | 128887606 | 008/062 | T2 DI CARIBOU TBL MTN 8/62 BNT STEEL | TABLEMTN | ETL.4440.TOWR | 2024-05-24 | 2024-05-06 | 2025-03-11 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354036 | T2 DI CARIBOU TBL MTN 8/62 BNT STEEL | ICQ
LC | 128887642 | 007/044 | T2 DI MONTA-VSTA-COYOTE SS 7/44 RPR SHLS | MOSSLNDG | ETL.5090.TOWR | 2024-05-24 | 2024-05-06 | 2025-05-06 | On-Time |  | 2025-05-06 | 2025-05-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46391296 | T2 DI MONTA-VSTA-COYOTE SS 7/44 RPR SHLS | ICS
LC | 128887646 | 007/044 | T2 MTCALF-MNTA VSTA #3 7/44 RPL INSS | MOSSLNDG | ETL.5091.INSL.NCER | 2024-05-24 | 2024-05-06 | 2024-05-06 | Past Due |  | 2025-05-06 | 2025-05-06 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35599726 | T2 DI MTCALF-MNTA VSTA #3 7/40 RPL INSS | 93K
LC | 128887817 | 015/003 | T2 DI MENDCN-WLTS-FRT BRG 15/3 TOUCH | WILLITS | ETL.7550.POLE.NWOD | 2024-05-24 | 2024-05-06 | 2025-05-20 | Past Due |  | 2024-11-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46507781 | T2 DI MENDCN-WLTS-FRT BRG 15/3 TOUCH | ICW
LC | 128887861 | 015/003 | T2 DI MENDCN WLTS FRT BRG 15/3 RPR GYWW | WILLITS | ETL.7550.POLE.NWOD | 2024-05-24 | 2024-05-06 | 2025-02-12 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310155 | T2 DI MENDCN WLTS FRT BRG 15/3 RPR GYWW | ICW
LC | 128887892 | 053/477 | T2 DI PIT #1-COTTONWOOD 53/477 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-05-24 | 2024-05-06 | 2025-04-15 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381536 | T2 DI PIT #1-COTTONWOOD 53/477 RPR STRT | ICQ
LC | 128888003 | 005/053 | T2 DI HLSDLE JCG HLF MN BY 5/53 RPL HRDT | METCALF | ETL.7060.POLE.NWOD | 2024-05-24 | 2024-05-06 | 2025-05-01 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46478090 | T2 DI HLSDLE JCG HLF MN BY 5/53 RPL HRDT | ICQ
LC | 128888041 | 005/053 | T2 DI HLSDLE JCG HLF MN BY 5/53 RPL INSS | METCALF | ETL.7060.INSL.CERA | 2024-05-24 | 2024-05-06 | 2025-03-11 | On-Time |  | 2025-05-06 | 2025-05-06 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593872 | T2 DI HLSDLE JCG HLF MN BY 5/53 RPL INSS | 93K
LC | 128888069 | 007/007 | T2 DI TRNTY-MAPLE CRK 07/07 RPL STRW | EUREKA | ETL.8170.POLE.WOOD | 2024-05-24 | 2024-05-06 | 2025-03-23 | On-Time |  | 2025-05-06 | 2025-05-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572114 | T2 DI TRNTY-MAPLE CRK 07/07 RPL STRW | 70Y
LC | 128901897 | 005/037 | T2 DI EL DRDO-MSR FLT #1 5/37 RPR STRT | SACTO | ETL.1530.TOWR | 2024-05-28 | 2024-05-06 | 2024-12-30 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46327702 | T2NT DI EL DRDO-MSR FLT #1 5/37 RPR STRT | ICQ
LC | 128902515 | 005/110 | T2 DI COTNWD RED BLUF 5/110 RPR STRW | TABLEMTN | ETL.6660.POLE.WOOD | 2024-05-28 | 2024-05-06 | 2025-01-09 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311264 | T2 DI COTNWD RED BLUF 5/110 RPR STRW | ICW
LC | 128960394 | 000/018 | T2 DI KILARC DESCHUTES 0/18 RPR CNDW | TABLEMTN | ETL.7300.INSL.NCER | 2024-05-31 | 2024-05-06 | 2025-03-10 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46306308 | T2 DI KILARC DESCHUTES 0/18 RPR CNDW | ICW
LC | 128960815 | 004/074 | T2 DI CNTRVLL-TBL MTN 004/074 RPR INSW | TABLEMTN | ETL.6320.INSL.NCER | 2024-05-31 | 2024-05-06 | 2025-03-01 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46311265 | T2 DI CNTRVLL-TBL MTN 004/074 RPR INSW | ICW
LC | 128960905 | 012/066 | T2 DI FULTON-IGNACIO #1 12/66 TOUCH | LAKEVLLE | ETL.4680.TOWR | 2024-05-31 | 2024-05-06 | 2025-03-12 | On-Time |  | 2024-11-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAR NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46477487 | T2 DI FULTON-IGNACIO #1 12/66 TOUCH | ICQ
LC | 128961029 | 023/110 | T2 DI FULTON-PUEBLO 023/110 TOUCH | LAKEVLLE | ETL.1600.TOWR | 2024-05-31 | 2024-05-06 | 2025-03-03 | On-Time |  | 2024-11-06 | 2025-05-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485391 | T2 DI FULTON-PUEBLO 023/110 TOUCH | ICQ
LC | 128961240 | 062/004 | T2 DI GRBRVLE LYTNVL 62/4 RPR GYWW | WILLITS | ETL.8365.POLE.NWOD | 2024-05-31 | 2024-05-06 | 2025-03-09 | On-Time |  | 2025-05-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446746 | T2 DI GRBRVLE LYTNVL 62/4 RPR GYWW | ICW
LC | 128961595 | 007/040 | T2 MTCALF-MNTA VSTA #3 7/40 CANCEL | MOSSLNDG | ETL.5091.INSL.NCER | 2024-05-31 | 2024-05-06 | 2024-05-06 | Past Due |  | 2025-05-06 | 2025-05-06 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35599726 | T2 DI MTCALF-MNTA VSTA #3 7/40 RPL INSS | 93K
LC | 128962188 | 028/000 | T2 DI GARBRVL LYTNVLE 28/0 RPR JUMW | WILLITS | ETL.8365.INSL.NCER | 2024-05-31 | 2024-05-06 | 2024-08-15 | On-Time |  | 2024-08-06 | 2025-05-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46255900 | T2 DI GARBRVL LYTNVLE 28/0 RPR JUMW | ICW
LC | 129782551 | 001/005 | T3 DIABLO-MIDWAY #3 1/005 RPL GYWT | PISMOBCH | ETL.5980.TOWR | 2024-11-06 | 2024-11-06 | 2024-11-07 | On-Time |  | 2025-05-06 | 2025-05-06 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Tower | Replace | 46382460 | T3 DIABLO-MIDWAY #3 1/005 RPL GYWT | ICQ
LC | 129783037 | ?002/007 | T3 SNTH LN HALF MN BY ?2/7 INS MKBL | METCALF | ETL.7212.INSL.NCER | 2024-11-06 | 2024-11-06 | 2025-05-05 | On-Time |  | 2025-05-06 | 2025-05-06 | 671 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR3 PRTO FRAB NTDE BRIN | Missing | FAA Lighting-Wood | Install | 31722636 | T3 SNTH LN HALF MN BY ?2/7 INS MKBL | 93P
LC | 130966460 | 063/003B | T2 DI HMBLDT-TRINITY 063/003B RPL POLE | EUREKA | ETL.1820.POLE.WOOD | 2025-03-12 | 2024-05-06 | 2025-04-24 | On-Time |  | 2025-05-06 | 2025-05-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574640 | T2 DI HMBLDT-TRINITY 063/003C RPL POLE | 70Y
LC | 130966465 | 063/003A | T2 DI HMBLDT-TRINITY 063/003A RPL POLE | EUREKA | ETL.1820.POLE.WOOD | 2025-03-12 | 2024-05-06 | 2025-04-24 | On-Time |  | 2025-05-06 | 2025-05-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574640 | T2 DI HMBLDT-TRINITY 063/003C RPL POLE | 70Y
LC | 123535044 | 016/077 | T2 EI METCALF-MSS LND #1 16/77 RPR FENCE | MOSSLNDG | ETL.5330.TOWR | 2022-05-07 | 2022-05-07 | 2023-07-11 | On-Time |  | 2023-05-07 | 2025-05-07 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Structure-Tower | Repair | 45650184 | T2 EI METCALF-MSS LND #1 16/77 RPR FENCE | ICQ
LC | 128718019 | 009/008 | T2 OAKHURST TAP 009/008 RMV FNCE | FRESNO | ETL.1252.POLE.NWOD | 2024-05-07 | 2024-05-07 | 2024-08-20 | On-Time |  | 2024-11-07 | 2025-05-07 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | Encroachment | Right of Way | Remove | 46249765 | T2 OAKHURST TAP 009/008 RMV FNCE | CHR
LC | 128718109 | 006/070 | T2 WST PNT-VALY SPNGS 06/70 TOUCH | VICTOR | ETL.8350.POLE.NWOD | 2024-05-07 | 2024-05-07 | 2024-05-07 | Past Due |  | 2024-11-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46477460 | T2 WST PNT-VALY SPNGS 06/70 TOUCH | ICW
LC | 128718586 | 002/006A | T2 VS-CALAVERAS CEMENT 02/06A REFRAME | VICTOR | ETL.8220.POLE.NWOD | 2024-05-07 | 2024-05-07 | 2024-09-26 | On-Time |  | 2025-05-07 | 2025-05-07 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35555805 | T2 VS-CALAVERAS CEMENT 02/06A REFRAME | 93E
LC | 128719231 | 013/099 | T2 SALT SPRINGS-TIGER CRK 13/99 COTTER | VICTOR | ETL.3500.INSL | 2024-05-07 | 2024-05-07 | 2024-05-07 | Past Due |  | 2025-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46326995 | T2 EI SALT SPRNGS-TGR CRK 13/99 RPR INSS | ICS
LC | 128719233 | 024/109 | T2 EI FNK SW ST-WSTLY 24/109 RPR FOND | VICTOR | ETL.1384.TOWR | 2024-05-07 | 2024-05-07 | 2025-03-28 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416619 | T2 EI FNK SW ST-WSTLY 24/109 RPR FOND | ICQ
LC | 128719380 | 002/017 | T2NT EI CTTNWD-DLVN #1 2/17 RMV NEST | TABLEMTN | ETL.4550.TOWR | 2024-05-07 | 2024-05-07 | 2025-04-02 | On-Time |  | 2027-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46300594 | T2NT EI CTTNWD-DLVN #1 2/17 RMV NEST | ICS
LC | 128719611 | 031/149 | T2 EI RND MTN-TBL MTN #2 31/149 RPL INSS | TABLEMTN | ETL.6070.INSL | 2024-05-07 | 2024-05-07 | 2025-02-21 | On-Time |  | 2025-05-07 | 2025-05-07 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574244 | T2 EI RND MTN-TBL MTN #2 RPL INSS 6 TWRS | 93K
LC | 128719846 | 010/005 | T2 EI MRCD FLS-EXCHQR 10/05 RPR JMPS | FRESNO | ETL.8990.INSL.NCER | 2024-05-07 | 2024-05-07 | 2024-11-05 | On-Time |  | 2024-08-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46247133 | T2 EI MRCD FLS-EXCHQR 10/05 RPR JMPS | ICS
LC | 128719854 | 002/006A | T2 EI VLY SPRGS-CLVS CMNT 2/06A RPR GYWW | VICTOR | ETL.8220.POLE.NWOD | 2024-05-07 | 2024-05-07 | 2024-10-02 | On-Time |  | 2024-08-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46246548 | T2 EI VLY SPRGS-CLVS CMNT 2/06A RPR GYWW | ICW
LC | 128719940 | 007/047 | T2 EI OLEUM-G #1 007/047 RPR STRT | CONCORD | ETL.3150.TOWR | 2024-05-07 | 2024-05-07 | 2025-02-03 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46289311 | T2NT EI OLEUM-G #1 007/047 RPR STRT | ICQ
LC | 128719957 | 003/014 | T2 EI VASONA-METCALF 003/014 RPR STRT | METCALF | ETL.5932.TOWR | 2024-05-07 | 2024-05-07 | 2025-02-28 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46298823 | T2 EI VASONA-METCALF 003/014 RPR STRT | ICQ
LC | 128720066 | :005/033 | T2 EI ST-MNS SW ST-MNT :5/33 RMV NEST | VICTOR | ETL.3830.TOWR | 2024-05-07 | 2024-05-07 | 2025-02-12 | On-Time |  | 2025-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46325930 | T2 EI ST-MNS SW ST-MNT :5/33 RMV NEST | ICS
LC | 128720224 | 000/003 | T2 HAAS-WOODCHUCK 000/003 RPL STRW | FRESNO | ETL.8730.POLE.WOOD | 2024-05-07 | 2024-05-07 | 2024-05-07 | Past Due |  | 2025-05-07 | 2025-05-07 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35649103 | T2 HAAS-WOODCHUCK 000/003 RPL STRW | 70Y
LC | 128720688 | 007/046 | T2 EI OLEUM-G #1 007/046 RPL HRDT | CONCORD | ETL.3150.TOWR | 2024-05-07 | 2024-05-07 | 2025-02-03 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289310 | T2 EI OLEUM-G #1 007/046 RPL HRDT | ICQ
LC | 128721018 | 030/245 | T2 EI CRESTA-RIO OSO 30/245 RMV NEST | TABLEMTN | ETL.4590.TOWR | 2024-05-07 | 2024-05-07 | 2024-05-07 | Past Due |  | 2025-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46337324 | T2 EI CRESTA-RIO OSO 30/245 RMV NEST | ICS
LC | 128721045 | 000/006 | T2 BRCBRG JCT-MRPS TP 00/06 RPR STRW | FRESNO | ETL.8651.POLE.WOOD | 2024-05-07 | 2024-05-07 | 2025-03-28 | On-Time |  | 2025-05-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Structure-Wood | Repair | 46298035 | T2 BRCBRG JCT-MRPS TP 00/06 RPR STRW | ICW
LC | 128721065 | 030/245 | T2 EI CRESTA-RIO OSO 030/245 RMV VEG | TABLEMTN | ETL.4590.TOWR | 2024-05-07 | 2024-05-07 | 2024-11-06 | On-Time |  | 2025-05-07 | 2025-05-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128721121 | 030/246 | T2 EI CRESTA-RIO OSO 030/246 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-07 | 2024-05-07 | 2024-12-30 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381269 | T2 EI CRESTA-RIO OSO 030/246 RPR FOND | ICQ
LC | 128721355 | 012/074 | T2 STNSLS-MNTCA#2 12/74 RPR STRT | VICTOR | ETL.3820.TOWR | 2024-05-07 | 2024-05-07 | 2024-05-07 | Past Due |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46416625 | T2NT EI STNSLS-MNTCA#2 12/74 RPR STRT | ICQ
LC | 128721391 | 013/077 | T2 STNSLS-MNTC#2 13/77 RPR STRT | VICTOR | ETL.3820.TOWR | 2024-05-07 | 2024-05-07 | 2024-05-07 | Past Due |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46416629 | T2NT EI STNSLS-MNTC#2 13/77 RPR STRT | ICQ
LC | 128721395 | 012/073 | T2 STNSL-MLN SS-RVR BK 12/73 RPR CNDS | VICTOR | ETL.3840.INSL.CERA | 2024-05-07 | 2024-05-07 | 2024-05-07 | Past Due |  | 2025-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Conductor-Steel | Repair | 46327516 | T2 EI STNSL-MLN SS-RVR BK 12/73 RPR CNDS | ICS
LC | 128721436 | 000/013 | T2 EI APPLE HILL #1 TAP 00/013 RPR GYWW | SACTO | ETL.1531.POLE.NWOD | 2024-05-07 | 2024-05-07 | 2025-01-21 | On-Time |  | 2025-05-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46397990 | T2 EI APPLE HILL #1 TAP 00/013 RPR GYWW | ICW
LC | 128721505 | 005/011 | T2 EI MRCD FLS-EXCHQR 05/11 RPR JMPS | FRESNO | ETL.8990.INSL.NCER | 2024-05-07 | 2024-05-07 | 2024-11-05 | On-Time |  | 2024-08-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46247134 | T2 EI MRCD FLS-EXCHQR 05/11 RPR JMPS | ICS
LC | 128721661 | 014/082 | T2 EI STNSLS-MNTC#2 14/82 RPR FOND | VICTOR | ETL.3820.TOWR | 2024-05-07 | 2024-05-07 | 2024-06-28 | On-Time |  | 2024-11-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46255451 | T2 EI STNSLS-MNTC#2 14/82 RPR FOND | ICQ
LC | 128721950 | 027/218 | T2 EI CRESTA-RIO OSO 027/218 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-07 | 2024-05-07 | 2024-12-30 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381270 | T2 EI CRESTA-RIO OSO 027/218 RPR FOND | ICQ
LC | 128722028 | 004/015 | T2 EI TRINITY-MPLE CRK 4/15L COMPLETE | EUREKA | ETL.8170.POLE.WDPS | 2024-05-07 | 2024-05-07 | 2024-10-31 | On-Time |  | 2024-11-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46249706 | T2 EI TRINITY-MPLE CRK 4/015L RPR ANCW | ICW
LC | 128722031 | 004/015 | T2 EI TRINITY-MPLE CRK 4/15C COMPLETE | EUREKA | ETL.8170.POLE.WDPS | 2024-05-07 | 2024-05-07 | 2024-10-31 | On-Time |  | 2024-11-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46249707 | T2 EI TRINITY-MPLE CRK 4/015C RPR ANCW | ICW
LC | 128722056 | 034/163 | T2 ROUND MTN-TBL MTN#2 34/163 RPL GRWT | TABLEMTN | ETL.6070.TOWR | 2024-05-07 | 2024-05-07 | 2025-02-06 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Ground Wire-Tower | Replace | 46310384 | T2 ROUND MTN-TBL MTN#2 34/163 RPL GRWT | ICQ
LC | 128722133 | 002/008 | T2 EI VLY SPRGS-CLVS CMNT 02/08 RPR GYWW | VICTOR | ETL.8220.POLE.WOOD | 2024-05-07 | 2024-05-07 | 2024-09-26 | On-Time |  | 2025-05-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46246730 | T2 EI VLY SPRGS-CLVS CMNT 02/08 RPR GYWW | ICW
LC | 128722182 | 005/041 | T2 DIVIDE-VANDNBRG #1 05/041 RPL STRW | PISMOBCH | ETL.8620.POLE.WOOD | 2024-05-07 | 2024-05-07 | 2024-05-07 | Past Due |  | 2025-05-07 | 2025-05-07 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573265 | T2 EI DIVIDE-VANDNBRG #1 05/041 RPL STRW | 70Y
LC | 128722183 | 005/041 | T2 EI DIVIDE-VANDENBERG #1 05/41 RMV VEG | PISMOBCH | ETL.8620.POLE.WOOD | 2024-05-07 | 2024-05-07 | 2025-03-14 | On-Time |  | 2025-05-07 | 2025-05-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128722262 | 005/000 | T2 EI TRINITY-MAPLE CRK 5/000L RPL STRW | EUREKA | ETL.8170.POLE.WDPS | 2024-05-07 | 2024-05-07 | 2025-03-23 | On-Time |  | 2024-11-07 | 2025-05-07 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35572117 | T2 EI TRINITY-MAPLE CRK 5/000R RPL STRW | 70Y
LC | 128722263 | 005/000 | T2 EI TRINITY-MAPLE CRK 5/000C RPL STRW | EUREKA | ETL.8170.POLE.WDPS | 2024-05-07 | 2024-05-07 | 2025-03-23 | On-Time |  | 2024-11-07 | 2025-05-07 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35572117 | T2 EI TRINITY-MAPLE CRK 5/000R RPL STRW | 70Y
LC | 128722381 | 005/000 | T2 EI TRINITY-MAPLE CRK 5/000R RPL STRW | EUREKA | ETL.8170.POLE.WDPS | 2024-05-07 | 2024-05-07 | 2025-03-23 | On-Time |  | 2024-11-07 | 2025-05-07 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35572117 | T2 EI TRINITY-MAPLE CRK 5/000R RPL STRW | 70Y
LC | 128722526 | 009/113 | T2 WV CLGATE-SMRTVILLE #2 9/113 RPL POLE | SACTO | ETL.6520.POLE.WOOD | 2024-05-07 | 2024-05-07 | 2025-03-06 | On-Time |  | 2025-05-07 | 2025-05-07 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557135 | T2 WV CLGATE-SMRTVILLE #2 9/113 RPL POLE | 70Y
LC | 128722624 | 006/040 | T2 EI OLEUM-G #1 006/040 RMV VEG | CONCORD | ETL.3150.TOWR | 2024-05-07 | 2024-05-07 | 2025-04-10 | On-Time |  | 2025-05-07 | 2025-05-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW CNCL OH FMOB TR2 PRTO CLMB FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128722648 | 006/040 | T2 EI OLEUM-G #1 006/040 RPL HNGR | CONCORD | ETL.3150.INSL.NCER | 2024-05-07 | 2024-05-07 | 2025-04-15 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46289309 | T2 EI OLEUM-G #1 006/040 RPL HNGR | ICQ
LC | 128722692 | 007/037 | T2 EI IGNACIO-SN RFEL #1 7/37 COMPLETE | LAKEVLLE | ETL.1850.TOWR | 2024-05-07 | 2024-05-07 | 2025-03-11 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46289508 | T2 EI IGNACIO-SN RFEL #1 7/37 RPR FOND | ICQ
LC | 128722791 | 021/002 | T2 EI TRINITY-MAPLE CRK 21/02 RPL STRW | EUREKA | ETL.8170.POLE.WOOD | 2024-05-07 | 2024-05-07 | 2024-05-07 | Past Due |  | 2025-05-07 | 2025-05-07 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572107 | T2 EI TRINITY-MAPLE CRK 21/02 RPL STRW | 70Y
LC | 128722894 | 025/003 | T2 EI TRINITY-MAPLE CREEK 25/3 RPR SPLW | EUREKA | ETL.8170.INSL.CERA | 2024-05-07 | 2024-05-07 | 2025-04-13 | On-Time |  | 2025-05-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Splice-Wood | Repair | 46345851 | T2 EI TRINITY-MAPLE CREEK 25/3 RPR SPLW | ICW
LC | 128723029 | 013/162 | T2 EI KESWICK-TRINITY 13/162 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-07 | 2024-05-07 | 2024-09-14 | On-Time |  | 2024-08-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251425 | T2 EI KESWICK-TRINITY 13/162 RPR JUMS | ICS
LC | 128723076 | 013/162 | T2 EI KESWICK-TRINITY 13/162 RPR GYWW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-07 | 2024-05-07 | 2024-09-14 | On-Time |  | 2024-08-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46250708 | T2 EI KESWICK-TRINITY 13/162 RPR GYWW | ICW
LC | 128723078 | 013/162 | T2 EI KESWICK-TRINITY 13/162 RMV VEG | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-07 | 2024-05-07 | 2025-02-10 | On-Time |  | 2025-05-07 | 2025-05-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128723227 | 007/062 | T2 DI PIT #1-COTTONWOOD 7/62 RPR JUMS | TABLEMTN | ETL.5390.INSL.NCER | 2024-05-07 | 2024-05-07 | 2024-11-05 | On-Time |  | 2024-08-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46247593 | T2 DI PIT #1-COTTONWOOD 007/062 RPR JUMS | ICS
LC | 128723241 | 012/097 | T2 SALT SPRNGS-TGR CRK 12/97 RPL DAMS | VICTOR | ETL.3500.INSL.NCER | 2024-05-07 | 2024-05-07 | 2024-05-07 | Past Due |  | 2025-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Damper-Steel | Replace | 46326996 | T2 EI SALT SPRNGS-TGR CRK 12/97 RPL DAMS | ICS
LC | 128723243 | 012/097 | T2 SALT SPRNGS-TGR CRK 12/97 RPR CNDS | VICTOR | ETL.3500.INSL.NCER | 2024-05-07 | 2024-05-07 | 2024-05-07 | Past Due |  | 2024-11-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP REMT NOAC CLR ACCH OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Conductor-Steel | Repair | 46246842 | T2 EI SALT SPRNGS-TGR CRK 12/97 RPR CNDS | ICS
LC | 128723411 | 023/096A | T2 TESLA-METCALF 23/096A RMV VEG | METCALF | ETL.6110.TOWR | 2024-05-07 | 2024-05-07 | 2025-04-15 | On-Time |  | 2025-05-07 | 2025-05-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR REMT ACCM CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128723443 | 043/368 | T2 DI PIT #1-COTTONWOOD 43/368 RPR JUMS | TABLEMTN | ETL.5390.INSL.NCER | 2024-05-07 | 2024-05-07 | 2024-11-05 | On-Time |  | 2024-08-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46247591 | T2 DI PIT #1-COTTONWOOD 43/368 RPR JUMS | ICS
LC | 128723522 | 001/022 | T2 HAAS-WOODCHUCK 1/22 RPR GYWW | FRESNO | ETL.8730.POLE.WOOD | 2024-05-07 | 2024-05-07 | 2024-05-07 | Past Due |  | 2025-05-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP REMT SPCR ACCH OH FMOB TR2 FRAB REJC BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46543087 | T2 HAAS-WOODCHUCK 1/22 RPR GYWW | ICW
LC | 128723897 | 007/122 | T2 EI CORDELIA #1 TAP 07/122 RPR ANCW | LAKEVLLE | ETL.8182.POLE.WOOD | 2024-05-08 | 2024-05-07 | 2025-04-26 | On-Time |  | 2025-05-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46401429 | T2 EI CORDELIA #1 TAP 07/122 RPR ANCW | ICW
LC | 128723898 | 006/118 | T2 EI CORDELIA #1 TAP 06/118 RMV VEG | LAKEVLLE | ETL.8182.POLE.WOOD | 2024-05-08 | 2024-05-07 | 2025-03-04 | On-Time |  | 2025-05-07 | 2025-05-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128723939 | 007/119 | T2 EI CORDELIA #1 TAP 07/119 RPR INSW | LAKEVLLE | ETL.8182.INSL.CERA | 2024-05-08 | 2024-05-07 | 2025-04-26 | On-Time |  | 2025-05-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46401427 | T2 EI CORDELIA #1 TAP 07/119 RPR INSW | ICW
LC | 128723959 | 021/079 | T2 EI EXCHEQUER-INDIAN FLT 21/79 RMV VEG | FRESNO | ETL.8650.POLE.NWOD | 2024-05-08 | 2024-05-07 | 2024-05-07 | Past Due |  | 2025-05-07 | 2025-05-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP REMT NOAC SWRK OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128724092 | 016/078 | T2 TBL MTN-RIO OSO 16/78 RPL INSS | TABLEMTN | ETL.5700.INSL | 2024-05-08 | 2024-05-07 | 2025-04-11 | On-Time |  | 2024-11-07 | 2025-05-07 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD REAR CLR ACCM COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574248 | T2 EI TBL MTN-RIO OSO 16/78 RPL INSS | 93K
LC | 128745264 | 008/063 | T2 DI CRBOU TBL MTN 08/063 RPR SHLS | TABLEMTN | ETL.4440.TOWR | 2024-05-10 | 2024-05-07 | 2025-04-02 | On-Time |  | 2025-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46337325 | T2 DI CRBOU TBL MTN 08/063 RPR SHLS | ICS
LC | 128745267 | 008/063 | T2 DI CRBOU TBL MTN 08/063 COTTER | TABLEMTN | ETL.4440.INSL | 2024-05-10 | 2024-05-07 | 2024-06-06 | On-Time |  | 2024-08-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46247586 | T2 DI CRBOU TBL MTN 08/063 COTTER | ICS
LC | 128745921 | 067/000 | T2 DI HUMBOLDT-TRINITY 67/00L RPL HRDD | EUREKA | ETL.1820.POLE.WDPS | 2024-05-10 | 2024-05-07 | 2025-04-18 | On-Time |  | 2025-05-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46247500 | T2 DI HUMBOLDT-TRINITY 67/00L RPL HRDD | ICW
LC | 128745927 | 067/000 | T2 DI HUMBOLDT-TRINITY 67/00R COTTER | EUREKA | ETL.1820.POLE.WDPS | 2024-05-10 | 2024-05-07 | 2024-08-28 | On-Time |  | 2024-11-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46247502 | T2 DI HUMBOLDT-TRINITY 67/00R COTTER | ICW
LC | 128745940 | 067/000 | T2 DI HUMBOLDT-TRINITY 67/00L RPL HRDW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-10 | 2024-05-07 | 2025-04-18 | On-Time |  | 2025-05-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345852 | T2 DI HUMBOLDT-TRINITY 67/00L RPL HRDW | ICW
LC | 128750497 | 067/000 | T2 DI HUMBOLDT-TRINITY 67/00R RPL HRDD | EUREKA | ETL.1820.POLE.WDPS | 2024-05-13 | 2024-05-07 | 2025-04-18 | On-Time |  | 2025-05-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345854 | T2 DI HUMBOLDT-TRINITY 67/00R RPL HRDD | ICW
LC | 128750693 | 067/000 | T2 DI HUMBOLDT-TRINITY 67/00L RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-13 | 2024-05-07 | 2025-04-18 | On-Time |  | 2025-05-07 | 2025-05-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345855 | T2 DI HUMBOLDT-TRINITY 67/00L RPR GYWW | ICW
LC | 128779654 | X005/024 | T2 DIABLO-MESA-X05/24 TOUCH | PISMOBCH | ETL.4620.TOWR | 2024-05-15 | 2024-05-07 | 2024-05-07 | Past Due |  | 2024-11-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW ACCM OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476168 | T2 DI DIABLO-MESA-X05/24 TOUCH | ICQ
LC | 128780047 | 006/048 | T2 DI ELDRDO-MSRI FLT#2 06/48 RPL HRDT | SACTO | ETL.1540.INSL.NCER | 2024-05-15 | 2024-05-07 | 2025-01-21 | On-Time |  | 2025-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46443291 | T2 DI ELDRDO-MSRI FLT#2 06/48 RPL HRDT | ICS
LC | 128780242 | 008/065 | T2 DI PIT #1-COTTONWOOD 08/65 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-05-15 | 2024-05-07 | 2025-01-22 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381524 | T2NT DI PIT #1-COTTONWOOD 08/65 RPR STRT | ICQ
LC | 128780293 | 007/060 | T2 DI PIT #1-COTTONWOOD 7/60 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-05-15 | 2024-05-07 | 2025-01-14 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381525 | T2 DI PIT #1-COTTONWOOD 7/60 RPR FOND | ICQ
LC | 128800286 | 007/058 | T2 DI EL DRDO-MSURI FLT #1 7/58 RPR STRT | SACTO | ETL.1530.TOWR | 2024-05-17 | 2024-05-07 | 2025-02-10 | On-Time |  | 2024-11-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46463292 | T2 DI EL DRDO-MSURI FLT #1 7/58 RPR STRT | ICQ
LC | 128800639 | 014/068 | T2 DI MSS LNDNG-LS BNS 14/68 CANCEL | MOSSLNDG | ETL.6040.TOWR | 2024-05-17 | 2024-05-07 | 2025-04-28 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46416634 | T2 DI MSS LNDNG-LS BNS 14/68 RPL HRDT | ICQ
LC | 128837432 | 023/108 | T2 DI FULTON-PUEBLO 023/108 MASTIC | LAKEVLLE | ETL.1600.TOWR | 2024-05-21 | 2024-05-07 | 2025-03-11 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46289545 | T2 DI FULTON-PUEBLO 023/108 MASTIC | ICQ
LC | 128837449 | 001/021 | T3 DI DSBLA-CNTRVLL 001/021 RPL ANCW | TABLEMTN | ETL.6720.POLE.STPS | 2024-05-21 | 2024-05-07 | 2024-11-08 | On-Time |  | 2025-05-07 | 2025-05-07 | 637T | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35557347 | T3 DI DSBLA-CNTRVLL 001/021 RPL ANCW | 93E
LC | 128887503 | 043/366 | T2 DI PIT#1-COTT 43/366 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-05-24 | 2024-05-07 | 2025-05-12 | Past Due |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381534 | T2 DI PIT#1-COTT 43/366 RPR STRT | ICQ
LC | 128887726 | 006/055 | T2 DI PIT#1-COTT 6/55 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-05-24 | 2024-05-07 | 2025-01-21 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381535 | T2 DI PIT#1-COTT 6/55 RPR STRT | ICQ
LC | 128887934 | 036/155 | T2 DI FLTN-LKVLL 036/155 RPR FOND | LAKEVLLE | ETL.4950.TOWR | 2024-05-24 | 2024-05-07 | 2025-01-15 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46289546 | T2 DI FLTN-LKVLL 036/155 RPR FOND | ICQ
LC | 128888315 | 006/055 | T2 DI PIT#3-PIT#1 6/55 RPR STRT | TABLEMTN | ETL.5400.TOWR | 2024-05-24 | 2024-05-07 | 2025-04-22 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46382008 | T2 DI PIT#3-PIT#1 6/55 RPR STRT | ICQ
LC | 128888539 | 074/375B | T2 DI MALIN-RND MNTN#2-74/375B RPR SHLS | TABLEMTN | ETL.6020.TOWR | 2024-05-24 | 2024-05-07 | 2025-01-30 | On-Time |  | 2025-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338265 | T2 DI MALIN-RND MNTN#2-74/375B RPR SHLS | ICS
LC | 128889013 | 042/358 | T2 DI ROUND MTN-CTNWD#3 42/358 COTTER | TABLEMTN | ETL.5650.INSL | 2024-05-24 | 2024-05-07 | 2025-03-04 | On-Time |  | 2025-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46416195 | T2 DI ROUND MTN-CTNWD#3 42/358 COTTER | ICS
LC | 128889081 | 005/042 | T2 DI EL DRDO-MSRI FLT #1 5/42 RPR STRT | SACTO | ETL.1530.TOWR | 2024-05-24 | 2024-05-07 | 2024-12-30 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46327700 | T2 DI EL DRDO-MSRI FLT #1 5/42 RPR STRT | ICQ
LC | 128889091 | 015/070B | T2 DI MSS LNDNG LS BNS 15/70B RMV VEG | MOSSLNDG | ETL.6040.TOWR | 2024-05-24 | 2024-05-07 | 2025-04-02 | On-Time |  | 2025-05-07 | 2025-05-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128889173 | 050/001 | T2 DI HUMBOLDT-TRINITY 50/1 RPL INSW | EUREKA | ETL.1820.INSL.NCER | 2024-05-24 | 2024-05-07 | 2025-04-07 | On-Time |  | 2025-05-07 | 2025-05-07 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574653 | T2 DI HUMBOLDT-TRINITY 50/1 RPL INSW | 93I
LC | 128890941 | 042/359 | T2 DI RND MTN-CTTNWD #3 42/359 COTTER | TABLEMTN | ETL.5650.INSL | 2024-05-25 | 2024-05-07 | 2025-03-04 | On-Time |  | 2025-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46416197 | T2 DI RND MTN-CTTNWD #3 42/359 COTTER | ICS
LC | 128891042 | 005/039 | T2 DI EL DRD-MSRI FLT #1 5/39 RPL HRDT | SACTO | ETL.1530.TOWR | 2024-05-25 | 2024-05-07 | 2024-12-30 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46327701 | T2 DI EL DRD-MSRI FLT #1 5/39 RPL HRDT | ICQ
LC | 128891117 | 043/371 | T2 PIT #1 COTNWD 43/371 RPR GYWS | TABLEMTN | ETL.5390.TOWR | 2024-05-25 | 2024-05-07 | 2025-04-29 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381538 | T2 DI PIT #1 COTNWD 43/371 RPR GYWS | ICQ
LC | 128902005 | 008/061 | T2 DI CARIBOU TBL MTN 8/61 BNT STEEL | TABLEMTN | ETL.4440.TOWR | 2024-05-28 | 2024-05-07 | 2025-03-17 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354060 | T2 DI CARIBOU TBL MTN 8/61 BNT STEEL | ICQ
LC | 128902060 | 006/046 | T2 DI EL DRDO-MSR FLT #1 6/46 TOUCH | SACTO | ETL.1530.TOWR | 2024-05-28 | 2024-05-07 | 2025-02-24 | On-Time |  | 2024-11-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46463295 | T2 DI EL DRDO-MSR FLT #1 6/46 RPR STRT | ICQ
LC | 128902161 | 018/125 | T2 DI HELMS GREG #1 18/125 RPR INSS | FRESNO | ETL.4870.INSL.CERA | 2024-05-28 | 2024-05-07 | 2025-03-27 | On-Time |  | 2025-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46298033 | T2 DI HELMS GREG #1 18/125 RPR INSS | ICS
LC | 128902168 | 050/204 | T2 DI MIDWAY WHRLWND 50/204 RPR GYWT | MIDWAY | ETL.6030.TOWR | 2024-05-28 | 2024-05-07 | 2025-03-26 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46297878 | T2 DI MIDWAY WHRLWND 50/204 RPR GYWT | ICQ
LC | 128961290 | 005/041 | T2 DI EL DORADO-MSR FLT #1 5/41 RMV VEG | SACTO | ETL.1530.TOWR | 2024-05-31 | 2024-05-07 | 2025-04-21 | On-Time |  | 2025-05-07 | 2025-05-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE SPCR CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128961293 | 005/041 | T2 DI EL DORADO-MSR FLT #1 5/41 TOUCH | SACTO | ETL.1530.TOWR | 2024-05-31 | 2024-05-07 | 2025-02-24 | On-Time |  | 2024-11-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46463297 | T2 DI EL DORADO-MSR FLT #1 5/41 RPR STRT | ICQ
LC | 128961453 | 006/043 | T2 DI EL DORADO-MSR FLT #1 6/43 TOUCH | SACTO | ETL.1530.TOWR | 2024-05-31 | 2024-05-07 | 2024-05-07 | Past Due |  | 2024-11-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472240 | T2 DI EL DORADO-MSR FLT #1 6/43 RPR STRT | ICQ
LC | 128961513 | 006/054 | T2 DI PIT #1-COTTONWOOD 6/54 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2024-05-31 | 2024-05-07 | 2025-04-28 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381547 | T2 DI PIT #1-COTTONWOOD 6/54 BNT STEEL | ICQ
LC | 128961550 | 036/156 | T2 DI FULTON LKVILE 36/156 COTTER | LAKEVLLE | ETL.4950.INSL.CERA | 2024-05-31 | 2024-05-07 | 2025-01-15 | On-Time |  | 2025-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46403751 | T2 DI FULTON LKVILE 36/156 COTTER | ICS
LC | 128962031 | 007/050 | T2 DI EL DRDO-MSR FLT #1 7/50 RPL HANGER | SACTO | ETL.1530.INSL | 2024-05-31 | 2024-05-07 | 2025-04-02 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46327703 | T2 DI EL DRDO-MSR FLT #1 7/50 RPL HANGER | ICQ
LC | 128962092 | 006/057 | T2 DI PIT #1-COTTONWOOD 06/057 RMV NEST | TABLEMTN | ETL.5390.TOWR | 2024-05-31 | 2024-05-07 | 2025-04-21 | On-Time |  | 2025-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46452774 | T2 DI PIT #1-COTTONWOOD 06/057 RMV NEST | ICS
LC | 128962093 | 006/057 | T2 DI PIT #1-COTTONWOOD 06/057 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2024-05-31 | 2024-05-07 | 2025-04-29 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46257249 | T2 DI PIT #1-COTTONWOOD 06/057 BNT STEEL | ICQ
LC | 128964169 | 043/365 | T2 DI PIT #1 COTTONWD 43/365 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-06-01 | 2024-05-07 | 2025-04-29 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381869 | T2 DI PIT #1 COTTONWD 43/365 RPR STRT | ICQ
LC | 128964423 | 014/067 | T2 DI MS LNDG-LS BNOS 14/067 RPR SHLS | MOSSLNDG | ETL.6040.TOWR | 2024-06-01 | 2024-05-07 | 2025-02-14 | On-Time |  | 2025-05-07 | 2025-05-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCH COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46305504 | T2 DI MS LNDG-LS BNOS 14/067 RPR SHLS | ICS
LC | 128964462 | 042/364 | T2 DI ROUND MTN-CTNWD#3 42/364 RPL HRDT | TABLEMTN | ETL.5650.TOWR | 2024-06-01 | 2024-05-07 | 2025-04-24 | On-Time |  | 2025-05-07 | 2025-05-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46310413 | T2 DI ROUND MTN-CTNWD#3 42/364 RPL HRDT | ICQ
LC | 129058160 | 003/035 | T2 DI MONTA VISTA-BURNS 3/35 RPL POLE | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-06-11 | 2024-05-07 | 2025-05-13 | Past Due |  | 2025-05-07 | 2025-05-07 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573800 | T2 DI MONTA VISTA-BURNS 3/35 RPL POLE | 70Y
LC | 128725502 | 005/035 | T2 EI OLEUM-G #1 005/035 RPL HRDT | CONCORD | ETL.3150.TOWR | 2024-05-08 | 2024-05-08 | 2025-02-03 | On-Time |  | 2025-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289312 | T2 EI OLEUM-G #1 005/035 RPL HRDT | ICQ
LC | 128725733 | 036/000 | T2 BRDGVILL-GRBERVLL 36/0 RPR GYWW | EUREKA | ETL.6220.POLE.WOOD | 2024-05-08 | 2024-05-08 | 2024-05-08 | Past Due |  | 2024-11-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR FIRE OH TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46239989 | T2 BRIDGEVILLE-GARBERVILLE 36/0 RPR GYWW | ICW
LC | 128725848 | 026/214 | T2 EI CRESTA-RIO OSO 026/214 RPL INSS | TABLEMTN | ETL.4590.INSL.CERA | 2024-05-08 | 2024-05-08 | 2025-04-28 | On-Time |  | 2025-05-08 | 2025-05-08 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570419 | T2 EI CRESTA-RIO OSO RPL INSS | 93K
LC | 128725917 | 005/106 | T2 EI CORDELIA #1 TAP 05/106 RPR INSW | SACTO | ETL.8182.INSL.NCER | 2024-05-08 | 2024-05-08 | 2025-04-24 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46337382 | T2 EI CORDELIA #1 TAP 05/106 RPR INSW | ICW
LC | 128725958 | 037/178 | T2 EI LAKEVILLE-IGNACIO#2 37/178 RMV VEG | LAKEVLLE | ETL.3745.TOWR | 2024-05-08 | 2024-05-08 | 2025-03-17 | On-Time |  | 2025-05-08 | 2025-05-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128725999 | 006/111 | T2 EI CORDELIA #1 TAP 06/111 RPR GYWW | LAKEVLLE | ETL.8182.POLE.NWOD | 2024-05-08 | 2024-05-08 | 2025-04-26 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337381 | T2 EI CORDELIA #1 TAP 06/111 RPR GYWW | ICW
LC | 128726239 | 006/072 | T2 EI MTN GTE JCT-CASCADE 06/72 RPL STRW | TABLEMTN | ETL.7640.POLE.WOOD | 2024-05-08 | 2024-05-08 | 2025-01-09 | On-Time |  | 2025-05-08 | 2025-05-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574136 | T2 EI MTN GTE JCT-CASCADE 06/72 RPL STRW | 70Y
LC | 128726271 | 027/136 | T2 EI ROUND MTN-TABL MTN#2 27/136 COTTER | TABLEMTN | ETL.6070.INSL.NCER | 2024-05-08 | 2024-05-08 | 2025-02-21 | On-Time |  | 2024-08-08 | 2025-05-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46250268 | T2 EI ROUND MTN-TABL MTN#2 27/136 COTTER | ICS
LC | 128726278 | 035/203 | T2 EI EXCHQR-NDN FLT 35/203 CANCEL | FRESNO | ETL.8650.TOWR | 2024-05-08 | 2024-05-08 | 2025-06-02 | Past Due |  | 2025-05-08 | 2025-05-08 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC SWRK COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46298025 | T2 EI EXCHQR-NDN FLT 35/203 RPL RPTS | ICB
LC | 128726383 | 016/073 | T2 TSSJRA-NWRK 16/73 RPL INSS | CONCORD | ETL.5920.INSL | 2024-05-08 | 2024-05-08 | 2024-05-08 | Past Due |  | 2025-05-08 | 2025-05-08 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575042 | T2 TSSJRA-NWRK 16/73 RPL INSS | 93K
LC | 128726512 | 027/135 | T2 EI ROND MTN-TBL MTN #2 27/135 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2024-05-08 | 2024-05-08 | 2024-11-06 | On-Time |  | 2025-05-08 | 2025-05-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128726525 | 036/006 | T2 EI TRINITY-MAPLE CRK 36/006 RPR ANCW | EUREKA | ETL.8170.POLE.WOOD | 2024-05-08 | 2024-05-08 | 2024-08-12 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46252304 | T2 EI TRINITY-MAPLE CRK 36/006 RPR ANCW | ICW
LC | 128726570 | 026/211 | T2 EI CRESTA-RIO OSO 026/211 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-05-08 | 2024-05-08 | 2024-12-26 | On-Time |  | 2025-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381271 | T2 EI CRESTA-RIO OSO 026/211 UNBURY | ICQ
LC | 128726580 | 026/211 | T2 CRESTA-RIO OSO 26/211 CANCEL | TABLEMTN | ETL.4590.INSL.CERA | 2024-05-08 | 2024-05-08 | 2024-05-08 | Past Due |  | 2025-05-08 | 2025-05-08 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570419 | T2 EI CRESTA-RIO OSO RPL INSS | 93K
LC | 128727117 | 025/206 | T2 EI CRESTA-RIO OSO 025/206 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-05-08 | 2024-05-08 | 2024-12-26 | On-Time |  | 2025-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381272 | T2 EI CRESTA-RIO OSO 025/206 UNBURY | ICQ
LC | 128727136 | 013/251 | T2 EI HAT CREEK #1-WSTWD 13/251 RPL POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-08 | 2024-05-08 | 2025-05-02 | On-Time |  | 2025-05-08 | 2025-05-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574749 | T2 EI HAT CREEK #1-WSTWD 13/251 RPL POLE | 70Y
LC | 128727174 | 027/133 | T2 ROUND MTN-TBL MTN#2 27/133 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2024-05-08 | 2024-05-08 | 2024-05-08 | Past Due |  | 2025-05-08 | 2025-05-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128727333 | 016/058 | T2 EI EXCHEQUER-INDIAN FLT 16/58 RMV VEG | FRESNO | ETL.8650.TOWR | 2024-05-08 | 2024-05-08 | 2024-03-28 | On-Time |  | 2025-05-08 | 2025-05-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP REMT NOAC SWRK COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128727390 | 027/206 | T2 WV DRUM-HGGNS 27/206 INS DAMS | SACTO | ETL.4393.INSL.NCER | 2024-05-08 | 2024-05-08 | 2025-01-10 | On-Time |  | 2025-05-08 | 2025-05-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Steel | Install | 46324628 | T2 WV DRUM-HGGNS 27/206 INS DAMS | ICS
LC | 128727657 | 001/017 | T2 EI DELTA-CASCADE_001/017 RPR GYWW | TABLEMTN | ETL.7640.POLE.WDPS | 2024-05-08 | 2024-05-08 | 2025-01-08 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46303869 | T2 EI DELTA-CASCADE_001/017 RPR GYWW | ICW
LC | 128727723 | 025/204 | T2 EI CRESTA-RIO OSO 025/204 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-05-08 | 2024-05-08 | 2025-03-13 | On-Time |  | 2025-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381273 | T2 EI CRESTA-RIO OSO 025/204 UNBURY | ICQ
LC | 128727743 | IG002/008 | T2 EI LAKEVLE-IGNACIO #1 IG02/08 RMV VEG | LAKEVLLE | ETL.4940.TOWR | 2024-05-08 | 2024-05-08 | 2025-03-12 | On-Time |  | 2025-05-08 | 2025-05-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128727833 | 001/030 | T2 EI HAAS-WOODCHUCK 01/30 RPL HRDD | FRESNO | ETL.8730.POLE.WOOD | 2024-05-08 | 2024-05-08 | 2024-05-08 | Past Due |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46298036 | T2 EI HAAS-WOODCHUCK 01/30 RPR HRDW | ICW
LC | 128727897 | 000/001 | T2 EI PIT #3-CARBRY SW ST 00/01 RPR FOND | TABLEMTN | ETL.5450.TOWR | 2024-05-08 | 2024-05-08 | 2025-04-23 | On-Time |  | 2025-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381999 | T2 EI PIT #3-CARBRY SW ST 00/01 RPR FOND | ICQ
LC | 128727986 | 025/203 | T2 EI CRESTA-RIO OSO 025/203 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-05-08 | 2024-05-08 | 2024-12-26 | On-Time |  | 2025-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381274 | T2 EI CRESTA-RIO OSO 025/203 UNBURY | ICQ
LC | 128728066 | 009/002 | T2 EXCHEQUER-MARIPOSA 09/002 RMV ENCR | FRESNO | ETL.8640.POLE.NWOD | 2024-05-08 | 2024-05-08 | 2024-08-27 | On-Time |  | 2024-11-08 | 2025-05-08 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | Encroachment | Right of Way | Remove | 46249766 | T2 EXCHEQUER-MARIPOSA 09/002 RMV ENCR | CHR
LC | 128728097 | 009/003 | T2 EXCHEQUER-MARIPOSA 09/003 RMV ENCR | FRESNO | ETL.8640.POLE.NWOD | 2024-05-08 | 2024-05-08 | 2024-08-27 | On-Time |  | 2024-11-08 | 2025-05-08 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | Encroachment | Right of Way | Remove | 46249767 | T2 EXCHEQUER-MARIPOSA 09/003 RMV ENCR | CHR
LC | 128728275 | 036/007 | T2 EI TRINITY-MAPLE CRK 36/007 RPR GYWW | EUREKA | ETL.8170.POLE.WOOD | 2024-05-08 | 2024-05-08 | 2024-08-12 | On-Time |  | 2024-11-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Replace | 46252305 | T2 EI TRINITY-MAPLE CRK 36/007 RPR GYWW | ICW
LC | 128728517 | 041/010C | T2 EI TRINITY-MAPLE CRK 41/010C RPL ANCW | EUREKA | ETL.8170.POLE.WOOD | 2024-05-08 | 2024-05-08 | 2025-04-29 | On-Time |  | 2025-05-08 | 2025-05-08 | 637 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572018 | T2 EI TRINITY-MAPLE CRK 41/010A RPL ANCW | 93E
LC | 128728549 | 65 | T2 EI CARIBOU #2 ;005/013A RPR SWTCH | TABLEMTN | ETL.6280.SWIT | 2024-05-08 | 2024-05-08 | 2024-10-02 | On-Time |  | 2024-08-08 | 2025-05-08 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP FIRE COMP OH FMOB TR2 PRTO DURA BRIN | Out of Adjustment | Switch | Repair | 46252230 | T2 EI CARIBOU #2 ;005/013A RPR SWTCH | ICE
LC | 128728559 | 041/010C | T2 TRINITY-MAPLE CRK 41/010C COMPLETE | EUREKA | ETL.8170.POLE.WOOD | 2024-05-08 | 2024-05-08 | 2025-04-29 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345858 | T2 EI TRINITY-MAPLE CRK 41/010C RPL HRDD | ICW
LC | 128728580 | 041/010B | T2 EI TRINITY-MAPLE CRK 41/010B RPL HRDD | EUREKA | ETL.8170.POLE.WOOD | 2024-05-08 | 2024-05-08 | 2025-04-29 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345857 | T2 EI TRINITY-MAPLE CRK 41/010B RPL HRDD | ICW
LC | 128728581 | 041/010A | T2 TRINITY-MAPLE CRK 41/010A COMPLETE | EUREKA | ETL.8170.POLE.WOOD | 2024-05-08 | 2024-05-08 | 2025-04-28 | On-Time |  | 2025-05-08 | 2025-05-08 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572018 | T2 EI TRINITY-MAPLE CRK 41/010A RPL ANCW | 93E
LC | 128728582 | 041/010B | T2 EI TRINITY-MAPLE CRK 41/010B RPL ANCW | EUREKA | ETL.8170.POLE.WOOD | 2024-05-08 | 2024-05-08 | 2025-04-29 | On-Time |  | 2025-05-08 | 2025-05-08 | 637 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572018 | T2 EI TRINITY-MAPLE CRK 41/010A RPL ANCW | 93E
LC | 128728590 | 041/010A | T2 EI TRINITY-MAPLE CRK 41/010A RPL HRDD | EUREKA | ETL.8170.POLE.WOOD | 2024-05-08 | 2024-05-08 | 2025-04-29 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345856 | T2 EI TRINITY-MAPLE CRK 41/010A RPL HRDD | ICW
LC | 128728604 | :002/017 | T2 EI STNSLS-MLNS SS MNTC :2/17 RMV NEST | VICTOR | ETL.3830.TOWR | 2024-05-08 | 2024-05-08 | 2025-02-12 | On-Time |  | 2025-05-08 | 2025-05-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46325931 | T2 EI STNSLS-MLNS SS MNTC :2/17 RMV NEST | ICS
LC | 128728625 | 69 | T2 EI CARIBOU-PLUMAS JCT 14/008 RPR SWTC | TABLEMTN | ETL.6290.SWIT | 2024-05-08 | 2024-05-08 | 2024-10-02 | On-Time |  | 2024-08-08 | 2025-05-08 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP FIRE COMP OH FMOB TR2 PRTO DURA BRIN | Out of Adjustment | Switch | Repair | 46252231 | T2 EI CARIBOU-PLUMAS JCT 14/008 RPR SWTC | ICE
LC | 128728951 | ;003/006 | T2 EI CARIBOU #2 ;003/006 RPL STRW | TABLEMTN | ETL.6280.POLE.WOOD | 2024-05-08 | 2024-05-08 | 2025-03-04 | On-Time |  | 2025-05-08 | 2025-05-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD REMT NOAC REAR CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35556126 | T2 EI CARIBOU #2 ;003/006 RPL STRW | 70Y
LC | 128729085 | 011/144 | T2 EI KESWICK-TRINITY 11/144 RMV VEG | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-09 | 2024-05-08 | 2025-02-10 | On-Time |  | 2025-05-08 | 2025-05-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128729088 | 015/183 | T2 EI KESWICK-TRINITY 15/183 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-09 | 2024-05-08 | 2024-09-13 | On-Time |  | 2024-08-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251640 | T2 EI KESWICK-TRINITY 15/183 RPR JUMW | ICW
LC | 128729103 | 012/154 | T2 EI KESWICK-TRINITY 12/154 CANCEL | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-09 | 2024-05-08 | 2025-02-18 | On-Time |  | 2025-05-08 | 2025-05-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128744404 | 011/112 | T2 ARCO-CHOLAME 11/112 RPR GYWW | MIDWAY | ETL.8440.POLE.NWOD | 2024-05-10 | 2024-05-08 | 2025-01-08 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46302544 | T2 ARCO-CHOLAME 11/112 RPR GYWW | ICW
LC | 128744778 | 000/017 | T2 DI CLGT-CHALLENGE 000/017 RPR JUMW | SACTO | ETL.6480.INSL.NCER | 2024-05-10 | 2024-05-08 | 2024-08-25 | On-Time |  | 2024-08-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46247490 | T2 DI CLGT-CHALLENGE 000/017 RPR JUMW | ICW
LC | 128745265 | 041/272 | T2 DI TRNTY-CTTNWD 41/272 RPR JMPW | TABLEMTN | ETL.4040.INSL.NCER | 2024-05-10 | 2024-05-08 | 2024-08-19 | On-Time |  | 2024-08-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46252097 | T2 DI TRNTY-CTTNWD 41/272 RPR JMPW | ICW
LC | 128746164 | 030/002 | T2 DI GARBERVILE-LAYTONVLE 30/2 RPR JUMW | WILLITS | ETL.8365.INSL.NCER | 2024-05-10 | 2024-05-08 | 2025-04-17 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46252681 | T2 DI GARBERVILE-LAYTONVLE 30/2 RPR JUMW | ICW
LC | 128800667 | 014/069 | T2 DI MS LNDNG-LS BNS 14/69 RMV VEG | MOSSLNDG | ETL.6040.TOWR | 2024-05-17 | 2024-05-08 | 2025-04-27 | On-Time |  | 2025-05-08 | 2025-05-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128800737 | 029/002 | T2 DI GARBRVL-LAYTNVL-29/02 RPR GYWW | WILLITS | ETL.8365.POLE.WOOD | 2024-05-17 | 2024-05-08 | 2025-03-06 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446751 | T2 DI GARBRVL-LAYTNVL-29/02 RPR GYWW | ICW
LC | 128811581 | 021/100 | T2 DI FULTON-PUEBLO 21/100 RPR STRT | LAKEVLLE | ETL.1600.TOWR | 2024-05-20 | 2024-05-08 | 2025-01-22 | On-Time |  | 2025-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46289509 | T2NT DI FULTON-PUEBLO 21/100 RPR STRT | ICQ
LC | 128819149 | 042/356 | T2NT DI PIT#1-COTTONWOOD 42/356 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-05-20 | 2024-05-08 | 2025-04-21 | On-Time |  | 2027-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381528 | T2NT DI PIT#1-COTTONWOOD 42/356 RPR STRT | ICQ
LC | 128819220 | 042/356 | T2 DI PIT #1-COTTONWOOD 42/356 RPL HRDT | TABLEMTN | ETL.5390.TOWR | 2024-05-20 | 2024-05-08 | 2025-04-21 | On-Time |  | 2025-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381530 | T2 DI PIT #1-COTTONWOOD 42/356 RPL HRDT | ICQ
LC | 128819339 | 35 | T2 DI COLGATE-CHALLENGE 0/16 RPR SWTC | SACTO | ETL.6480.SWIT | 2024-05-20 | 2024-05-08 | 2024-08-26 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Switch-Wood | Repair | 46304917 | T2 DI COLGATE-CHALLENGE 0/16 RPR SWTC | ICW
LC | 128887665 | 000/022 | T2 DI COLGATE-CHALLENGE 0/22 RPR STRW | SACTO | ETL.6480.POLE.WOOD | 2024-05-24 | 2024-05-08 | 2025-04-06 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337383 | T2 DI COLGATE-CHALLENGE 00/22 RPR STRW | ICW
LC | 128890729 | 061/006 | T2 HMBLDT-TRINITY 061/006 RPL HRDW | EUREKA | ETL.1820.POLE.STPS | 2024-05-25 | 2024-05-08 | 2024-05-08 | Past Due |  | 2024-11-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace
LC | 128902028 | 032/231 | T2 DI CARIBOU-TBL MTN 32/231 RPL INSS | TABLEMTN | ETL.4440.INSL.CERA | 2024-05-28 | 2024-05-08 | 2025-04-07 | On-Time |  | 2025-05-08 | 2025-05-08 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569572 | T2 DI CARIBOU-TBL MTN RPL INSS | 93K
LC | 128902160 | 033/239 | T2 DI CARIBOU-TBL MT 33/239 RPR INSS | TABLEMTN | ETL.4440.INSL.CERA | 2024-05-28 | 2024-05-08 | 2025-04-01 | On-Time |  | 2025-05-08 | 2025-05-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46337442 | T2 DI CARIBOU-TBL MT 33/239 RPR INSS | ICS
LC | 128902250 | 030/003 | T2 DI GARBRVIL-LYTNVL 30/03 RPR JUMW | WILLITS | ETL.8365.INSL.CERA | 2024-05-28 | 2024-05-08 | 2024-05-08 | Past Due |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Wood | Repair | 46446755 | T2 DI GARBRVIL-LYTNVL 30/03 RPR JUMW | ICW
LC | 128902255 | 030/003 | T2 DI GARBRVIL-LYTNVL 30/03 RPR STRW | WILLITS | ETL.8365.POLE.WOOD | 2024-05-28 | 2024-05-08 | 2025-06-23 | Past Due |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46446756 | T2 DI GARBRVIL-LYTNVL 30/03 RPR STRW | ICW
LC | 128902628 | 041/352 | T2 DI PIT 1-CTTNWD 041/352 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2024-05-28 | 2024-05-08 | 2025-04-29 | On-Time |  | 2025-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381542 | T2 DI PIT 1-CTTNWD 041/352 BNT STEEL | ICQ
LC | 128902684 | 042/355 | T2 DI PIT 1-CTTNWD 042/355 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-05-28 | 2024-05-08 | 2025-04-21 | On-Time |  | 2025-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381543 | T2 DI PIT 1-CTTNWD 042/355 RPR STRT | ICQ
LC | 128902747 | 042/354 | T2 DI PIT #1-CTNWOOD 42/354 RPR GYWT | TABLEMTN | ETL.5390.TOWR | 2024-05-28 | 2024-05-08 | 2025-04-29 | On-Time |  | 2025-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381544 | T2 DI PIT #1-CTNWOOD 42/354 RPR GYWT | ICQ
LC | 128902805 | 041/351 | T2 DI PIT 1-CTTNWD 041/351 UNBURY | TABLEMTN | ETL.5390.TOWR | 2024-05-28 | 2024-05-08 | 2025-04-29 | On-Time |  | 2025-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381545 | T2 DI PIT 1-CTTNWD 041/351 UNBURY | ICQ
LC | 128964218 | 030/008 | T2 DI GRBRVL-LYTNVL 30/8 RPR GYWW | WILLITS | ETL.8365.POLE.WOOD | 2024-06-01 | 2024-05-08 | 2025-04-16 | On-Time |  | 2024-11-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46255901 | T2 DI GRBRVL-LYTNVL 30/8 RPR GYWW | ICW
LC | 128964299 | 030/004 | T2 DI GARBERVILLE-LYT 30/4 RPR JUMW | WILLITS | ETL.8365.INSL.NCER | 2024-06-01 | 2024-05-08 | 2025-04-16 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46264535 | T2 DI GARBERVILLE-LYT 30/4 RPR JUMW | ICW
LC | 128964445 | 014/066 | T2 DI MOSS LANDING-LB 14/66 RPR SHLS | MOSSLNDG | ETL.6040.TOWR | 2024-06-01 | 2024-05-08 | 2025-02-11 | On-Time |  | 2025-05-08 | 2025-05-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46305502 | T2 DI MOSS LANDING-LB 14/66 RPR SHLS | ICS
LC | 129015483 | 042/275A | T2 DI TRINITY-CTTNWD 042/275A RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-06-03 | 2024-05-08 | 2025-02-24 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46471156 | T2 DI TRINITY-CTTNWD 042/275A RPR JUMW | ICW
LC | 129015657 | 041/353 | T2 DI PIT #1-COTTONWOOD 41/353 RPR GYWT | TABLEMTN | ETL.5390.TOWR | 2024-06-03 | 2024-05-08 | 2025-04-29 | On-Time |  | 2025-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381878 | T2 DI PIT #1-COTTONWOOD 41/353 RPR GYWT | ICQ
LC | 129015797 | 000/008A | T2 DI MTN GATE JCT-CASCDE 0/8A RPR GYWW | TABLEMTN | ETL.7640.POLE.NWOD | 2024-06-03 | 2024-05-08 | 2025-01-08 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46303868 | T2 DI MTN GATE JCT-CASCDE 0/8A RPR GYWW | ICW
LC | 129015888 | 048/423 | T2 DI PIT #1-COTTONWOOD 48/423 TOUCH | TABLEMTN | ETL.5390.TOWR | 2024-06-03 | 2024-05-08 | 2024-05-08 | Past Due |  | 2024-11-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478221 | T2 DI PIT #1-COTTONWOOD 48/423 TOUCH | ICQ
LC | 129016112 | 042/275B | T2 DI TRINITY-CTTNWD 42/275B RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-06-03 | 2024-05-08 | 2025-02-24 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46471157 | T2 DI TRINITY-CTTNWD 42/275B RPR JUMW | ICW
LC | 129016183 | 021/101 | T2 DI FULTON-PUEBLO 21/101 RPLC HRDT | LAKEVLLE | ETL.1600.TOWR | 2024-06-03 | 2024-05-08 | 2025-01-22 | On-Time |  | 2025-05-08 | 2025-05-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289510 | T2 DI FULTON-PUEBLO 21/101 RPLC HRDT | ICQ
LC | 129021551 | 029/003 | T2 DI GARERVLE-LAYTNVL 29/3L RPR GYWW | WILLITS | ETL.8365.POLE.WDPS | 2024-06-04 | 2024-05-08 | 2025-04-17 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446752 | T2 DI GARERVLE-LAYTNVL 29/3L RPR GYWW | ICW
LC | 129021553 | 029/003 | T2 DI GARERVLE-LAYTNVL 29/3C COMPLETE | WILLITS | ETL.8365.POLE.WDPS | 2024-06-04 | 2024-05-08 | 2025-06-23 | Past Due |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446753 | T2 DI GARERVLE-LAYTNVL 29/3C RPR GYWW | ICW
LC | 129021555 | 029/003 | T2 DI GARERVLE-LAYTNVL 29/3R RPR GYWW | WILLITS | ETL.8365.POLE.WDPS | 2024-06-04 | 2024-05-08 | 2025-04-17 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446754 | T2 DI GARERVLE-LAYTNVL 29/3R RPR GYWW | ICW
LC | 129793242 | 002/029 | T3 BURNS-LONE STAR #1 002/029 REFRAME | MOSSLNDG | ETL.6230.POLE.WOOD | 2024-11-08 | 2024-11-08 | 2025-03-16 | On-Time |  | 2025-05-08 | 2025-05-08 | 637T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35599006 | T3 BURNS-LONE STAR #1 002/029 REFRAME | 93E
LC | 129794048 | 009/228 | T3 WV DRM-GRSS VLLY-WEIMR 9/228 INS DMPW | SACTO | ETL.6760.INSL.NCER | 2024-11-08 | 2024-11-08 | 2025-01-09 | On-Time |  | 2025-05-08 | 2025-05-08 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO NTDE BRIN | Missing | Damper-Wood | Install | 46447701 | T3 WV DRM-GRSS VLLY-WEIMR 9/228 INS DMPW | ICW
LC | 123581678 | 005/081 | T2NT DI VLLY SPRNGS-CLAY 05/081 RPL HRDD | VICTOR | ETL.8264.POLE.WOOD | 2022-05-12 | 2022-05-09 | 2023-05-06 | On-Time |  | 2025-05-09 | 2025-05-09 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 45505111 | T2 DI VLLY SPRNGS-CLAY 005/081 RPL HRDD | ICW
LC | 123586080 | 006/053 | T2NT DI PARADISE-TABLE MTN 6/53 RMV VEG | TABLEMTN | ETL.4316.TOWR | 2022-05-13 | 2022-05-09 | 2023-08-31 | On-Time |  | 2025-05-09 | 2025-05-09 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 123687617 | Z009/003 | T3NT DI FULTON-CLSTGA 9/003 RPR STRT | LAKEVLLE | ETL.6880.POLE.NWOD | 2022-05-25 | 2022-05-09 | 2023-08-02 | On-Time |  | 2025-05-09 | 2025-05-09 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR3 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Structure-Tower | Repair | 45450252 | T3 DI FULTON-CLSTGA 9/003 RPR STRS | ICS
LC | 128728969 | 009/062 | T2 COTTONWOD-DELEVAN #1 9/62 TOUCH | TABLEMTN | ETL.4550.TOWR | 2024-05-09 | 2024-05-09 | 2025-03-03 | On-Time |  | 2024-11-09 | 2025-05-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476194 | T2 COTTONWOD-DELEVAN #1 9/62 TOUCH | ICQ
LC | 128730360 | 011/070 | T2 STNLS-MLS SW ST-MNT 11/70 TOUCH | VICTOR | ETL.3830.TOWR | 2024-05-09 | 2024-05-09 | 2025-01-22 | On-Time |  | 2024-11-09 | 2025-05-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW REMT SWRK ACCL COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46473023 | T2 STNLS-MLS SW ST-MNT 11/70 TOUCH | ICQ
LC | 128730846 | 006/009 | T2 VLLY SPRNGS-CLVRS 06/09 RPR CNDW | VICTOR | ETL.8220.INSL.NCER | 2024-05-09 | 2024-05-09 | 2025-03-08 | On-Time |  | 2025-05-09 | 2025-05-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Conductor-Wood | Repair | 46326997 | T2 VLLY SPRNGS-CLVRS 06/09 RPR CNDW | ICW
LC | 128731086 | 025/200 | T2 EI CRESTA-RIO OSO 025/200 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-05-09 | 2024-05-09 | 2025-02-03 | On-Time |  | 2025-05-09 | 2025-05-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381275 | T2 EI CRESTA-RIO OSO 025/200 UNBURY | ICQ
LC | 128731422 | 011/010 | T2 EXCHEQUER-MARIPOSA 11/010 RMV ENCR | FRESNO | ETL.8640.POLE.NWOD | 2024-05-09 | 2024-05-09 | 2024-08-28 | On-Time |  | 2024-11-09 | 2025-05-09 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | Encroachment | Right of Way | Remove | 46249768 | T2 EXCHEQUER-MARIPOSA 11/010 RMV ENCR | CHR
LC | 128731558 | 025/199 | T2 EI CRESTA-RIO OSO 025/199 CANCEL | TABLEMTN | ETL.4590.INSL.CERA | 2024-05-09 | 2024-05-09 | 2024-05-09 | Past Due |  | 2025-05-09 | 2025-05-09 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570419 | T2 EI CRESTA-RIO OSO RPL INSS | 93K
LC | 128731816 | 024/198 | T2 EI CRESTA-RIO OSO 024/198 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-05-09 | 2024-05-09 | 2025-02-03 | On-Time |  | 2025-05-09 | 2025-05-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381276 | T2 EI CRESTA-RIO OSO 024/198 UNBURY | ICQ
LC | 128731924 | 024/197 | T2 EI CRESTA-RIO OSO 024/197 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-05-09 | 2024-05-09 | 2025-02-03 | On-Time |  | 2025-05-09 | 2025-05-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381277 | T2 EI CRESTA-RIO OSO 024/197 UNBURY | ICQ
LC | 128732070 | 024/196 | T2 EI CRESTA-RIO OSO 24/196 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-05-09 | 2024-05-09 | 2025-02-05 | On-Time |  | 2025-05-09 | 2025-05-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381278 | T2 EI CRESTA-RIO OSO 24/196 UNBURY | ICQ
LC | 128732184 | 018/087 | T2 MONTA VISTA-SRTG 18/87 RMV VEG | METCALF | ETL.5240.TOWR | 2024-05-09 | 2024-05-09 | 2024-05-09 | Past Due |  | 2025-05-09 | 2025-05-09 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128732236 | 024/195 | T2 EI CRESTA-RIO OSO 24/195 CNCL | TABLEMTN | ETL.4590.INSL.CERA | 2024-05-09 | 2024-05-09 | 2024-05-09 | Past Due |  | 2025-05-09 | 2025-05-09 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570419 | T2 EI CRESTA-RIO OSO RPL INSS | 93K
LC | 128732237 | 024/195 | T2 EI CRESTA-RIO OSO 24/195 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-05-09 | 2024-05-09 | 2025-02-05 | On-Time |  | 2025-05-09 | 2025-05-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381279 | T2 EI CRESTA-RIO OSO 24/195 UNBURY | ICQ
LC | 128732387 | 024/194 | T2 EI CRESTA-RIO OSO 24/194 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-05-09 | 2024-05-09 | 2025-02-11 | On-Time |  | 2025-05-09 | 2025-05-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381320 | T2 EI CRESTA-RIO OSO 24/194 UNBURY | ICQ
LC | 128732440 | 018/086 | T2 EI MONTA VISTA-SARATGA 18/86 RPR OPGW | METCALF | ETL.5240.TOWR | 2024-05-09 | 2024-05-09 | 2024-08-22 | On-Time |  | 2025-05-09 | 2025-05-09 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46286783 | T2 EI MONTA VISTA-SARATGA 18/86 RPR OPGW | ICS
LC | 128732518 | 024/193 | T2 EI CRESTA-RIO OSO 024/193 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-05-09 | 2024-05-09 | 2024-12-26 | On-Time |  | 2025-05-09 | 2025-05-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381321 | T2 EI CRESTA-RIO OSO 024/193 UNBURY | ICQ
LC | 128732526 | 012/094 | T2 EI ELECTRA-BELLOTA 12/94 RPL INSS | VICTOR | ETL.4670.INSL | 2024-05-09 | 2024-05-09 | 2025-03-19 | On-Time |  | 2025-05-09 | 2025-05-09 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593221 | T2 EI ELECTRA-BELLOTA 002/024 RPL INSS | 93K
LC | 128732536 | 004/028 | T2 EI VLY SPRNGS-BELLTA 04/28 RPL INSS | VICTOR | ETL.5860.INSL.CERA | 2024-05-09 | 2024-05-09 | 2025-03-24 | On-Time |  | 2025-05-09 | 2025-05-09 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593222 | T2 EI VLY SPRNGS-BELLTA 04/28 RPL INSS | 93K
LC | 128732540 | 019/135 | T2 EI ELECTRA-BELLOTA 19/135 TOUCH | VICTOR | ETL.4670.TOWR | 2024-05-09 | 2024-05-09 | 2025-02-27 | On-Time |  | 2024-11-09 | 2025-05-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46477921 | T2 EI ELECTRA-BELLOTA 19/135 TOUCH | ICQ
LC | 128733050 | 010/008 | T2 EI TRINITY-MAPLE CRK 10/008 RMV VEG | EUREKA | ETL.8170.POLE.WOOD | 2024-05-09 | 2024-05-09 | 2025-01-22 | On-Time |  | 2025-05-09 | 2025-05-09 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 128733264 | 014/001 | T2 WV CARIBOU-PLUMAS JCT 14/01 REFRAME | TABLEMTN | ETL.6290.POLE.WOOD | 2024-05-09 | 2024-05-09 | 2025-04-30 | On-Time |  | 2025-05-09 | 2025-05-09 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35572133 | T2 WV CARIBOU-PLUMAS JCT 14/01 REFRAME | 93E
LC | 128733267 | 005/044 | T2 EI PIT #3-CARBERRY SS 5/44 RPR STRT | TABLEMTN | ETL.5450.TOWR | 2024-05-09 | 2024-05-09 | 2025-04-22 | On-Time |  | 2025-05-09 | 2025-05-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46382000 | T2 EI PIT #3-CARBERRY SS 5/44 RPR STRT | ICQ
LC | 128733276 | 027/170 | T2 WV TEL-SLD-MANTC 27/170 INST DMPW | VICTOR | ETL.4000.INSL.NCER | 2024-05-09 | 2024-05-09 | 2025-02-26 | On-Time |  | 2025-05-09 | 2025-05-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46325932 | T2 WV TEL-SLD-MANTC 27/170 INST DMPW | ICW
LC | 128733296 | 014/118 | T2 EI PIT #3-CRBRY SW ST 15/118 RPR FOND | TABLEMTN | ETL.5450.TOWR | 2024-05-09 | 2024-05-09 | 2025-04-23 | On-Time |  | 2025-05-09 | 2025-05-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46382002 | T2 EI PIT #3-CRBRY SW ST 15/118 RPR FOND | ICQ
LC | 128733298 | 005/043 | T2 EI PIT #3-CARBERRY SS 5/43 COTTER | TABLEMTN | ETL.5450.INSL.NCER | 2024-05-09 | 2024-05-09 | 2025-04-29 | On-Time |  | 2025-05-09 | 2025-05-09 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46416193 | T2 EI PIT #3-CARBERRY SS 5/43 COTTER | ICS
LC | 128733304 | 005/040 | T2 EI PIT #3-CARBERRY SS 5/40 RPR CONDS | TABLEMTN | ETL.5450.INSL.NCER | 2024-05-09 | 2024-05-09 | 2025-04-30 | On-Time |  | 2025-05-09 | 2025-05-09 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Conductor-Steel | Repair | 46416194 | T2 EI PIT #3-CARBERRY SS 5/40 RPR CONDS | ICS
LC | 128733320 | 005/042 | T2 EI PIT #3-CARBERRY SS 5/42 RMV VEG | TABLEMTN | ETL.5450.TOWR | 2024-05-09 | 2024-05-09 | 2024-11-07 | On-Time |  | 2025-05-09 | 2025-05-09 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128733325 | 015/119 | T2 EI PIT #3-CARBRY SW ST 15/119 RMV VEG | TABLEMTN | ETL.5450.TOWR | 2024-05-09 | 2024-05-09 | 2024-11-07 | On-Time |  | 2025-05-09 | 2025-05-09 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128733326 | 007/058 | T2 EI PIT #3-CARBRY SW ST 7/58 RPL SPLS | TABLEMTN | ETL.5450.INSL.NCER | 2024-05-09 | 2024-05-09 | 2024-10-30 | On-Time |  | 2024-08-09 | 2025-05-09 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Splice-Steel | Replace | 46257481 | T2 EI PIT #3-CARBRY SW ST 7/58 RPL SPLS | ICS
LC | 128733360 | 021/096 | T2 EI VACA-LAKEVILLE #1 21/96 RPR INSS | LAKEVLLE | ETL.5840.INSL.NCER | 2024-05-09 | 2024-05-09 | 2025-03-28 | On-Time |  | 2024-11-09 | 2025-05-09 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46252314 | T2 EI VACA-LAKEVILLE #1 21/96 RPR INSS | ICS
LC | 128733368 | 002/010 | T2 EI TULUCAY-VACA-VACA 002/010 RPR INSS | LAKEVLLE | ETL.5800.INSL | 2024-05-09 | 2024-05-09 | 2025-05-01 | On-Time |  | 2025-05-09 | 2025-05-09 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46512882 | T2 EI TULUCAY-VACA-VACA 002/010 RPR INSS | ICS
LC | 128733375 | 020/525 | T2 CARIBOU #2 20/525 COMPLETE | TABLEMTN | ETL.6280.POLE.NWOD | 2024-05-09 | 2024-05-09 | 2025-04-04 | On-Time |  | 2025-05-09 | 2025-05-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46337204 | T2 EI CARIBOU #2 20/525 RPR CRSW | ICW
LC | 128733385 | 020/528 | T2 CARIBOU #2 20/528 COMPLETE | TABLEMTN | ETL.6280.INSL.NCER | 2024-05-09 | 2024-05-09 | 2025-04-04 | On-Time |  | 2025-05-09 | 2025-05-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46337205 | T2 EI CARIBOU #2 20/528 COTTER | ICW
LC | 128733527 | 007/059 | T2 EI SALT SPRINGS-TIGER CRK 7/59 COTTER | VICTOR | ETL.3500.INSL.NCER | 2024-05-09 | 2024-05-09 | 2024-07-21 | On-Time |  | 2025-05-09 | 2025-05-09 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46253027 | T2 EI SALT SPRINGS-TIGER CRK 7/59 COTTER | ICS
LC | 128740315 | 017/222 | T2 EI KESWICK-TRINITY 17/222 RPR GYWW | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-10 | 2024-05-09 | 2024-09-15 | On-Time |  | 2025-05-09 | 2025-05-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311261 | T2 EI KESWICK-TRINITY 17/222 RPR GYWW | ICW
LC | 128740316 | 023/357A | T2 EI KESWICK-TRINITY 23/357A RPR JMPW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-10 | 2024-05-09 | 2024-09-13 | On-Time |  | 2024-08-09 | 2025-05-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251641 | T2 EI KESWICK-TRINITY 23/357A RPR JMPW | ICW
LC | 128740317 | 023/357C | T2 EI KESWICK-TRINITY 23/357C RPR JMPW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-10 | 2024-05-09 | 2024-09-13 | On-Time |  | 2024-08-09 | 2025-05-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251642 | T2 EI KESWICK-TRINITY 23/357C RPR JMPW | ICW
LC | 128742702 | 024/376 | T2 EI KESWICK-TRINITY 24/376 RPR STRW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-10 | 2024-05-09 | 2025-04-16 | On-Time |  | 2025-05-09 | 2025-05-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311260 | T2 EI KESWICK-TRINITY 24/376 RPR STRW | ICW
LC | 128742703 | 017/222 | T2 EI KESWICK-TRINITY 17/222 RMV VEG | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-10 | 2024-05-09 | 2025-02-10 | On-Time |  | 2025-05-09 | 2025-05-09 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128742705 | 024/383 | T2 EI KESWICK-TRINITY 24/383 RPL STRW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-10 | 2024-05-09 | 2025-04-16 | On-Time |  | 2025-05-09 | 2025-05-09 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573427 | T2 EI KESWICK-TRINITY 24/383 RPL STRW | 70Y
LC | 128742721 | 022/330 | T2 EI KESWICK-TRINITY 22/330 GO95 | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-10 | 2024-05-09 | 2025-04-15 | On-Time |  | 2025-05-09 | 2025-05-09 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35573425 | T2 EI KESWICK-TRINITY 22/330 GO95 | 93G
LC | 128744845 | 013/063 | T2 DI FULTON-PUEBLO 13/63 RMV VEG | LAKEVLLE | ETL.1600.TOWR | 2024-05-10 | 2024-05-09 | 2025-04-26 | On-Time |  | 2025-05-09 | 2025-05-09 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128744894 | 000/024 | T2 DI CLGT-ALLEGHANY 000/024 RPL INSW | SACTO | ETL.6470.INSL.NCER | 2024-05-10 | 2024-05-09 | 2024-06-21 | On-Time |  | 2024-08-09 | 2025-05-09 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35552968 | T2 DI CLGT-ALLEGHANY 000/024 RPL INSW | 93I
LC | 128746457 | 063/006 | T2 DI HUMBOLDT-TRINITY 63/06 RPR JMPW | EUREKA | ETL.1820.INSL.NCER | 2024-05-10 | 2024-05-09 | 2024-08-30 | On-Time |  | 2024-08-09 | 2025-05-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46247359 | T2 DI HUMBOLDT-TRINITY 63/06 RPR JMPW | ICW
LC | 128746875 | 002/062 | T2 DI COLGATE ALGHNAY 2/62 RMV VEG | SACTO | ETL.6470.POLE.WOOD | 2024-05-10 | 2024-05-09 | 2025-06-20 | Past Due |  | 2025-05-09 | 2025-05-09 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128746891 | 031/226 | T2 DI CARBOU-TBL MTN 31/226 RPL INSS | TABLEMTN | ETL.4440.INSL.CERA | 2024-05-10 | 2024-05-09 | 2025-04-07 | On-Time |  | 2025-05-09 | 2025-05-09 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569572 | T2 DI CARIBOU-TBL MTN RPL INSS | 93K
LC | 128746895 | 013/064 | T2 SILVERADO-FULTON JC 13/64 RPL INSS | LAKEVLLE | ETL.1610.INSL.CERA | 2024-05-10 | 2024-05-09 | 2024-05-09 | Past Due |  | 2025-05-09 | 2025-05-09 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35608529 | T2 DI SILVERADO-FULTON JC 13/64 RPL INSS | 93K
LC | 128765175 | 036/259 | T2 DI MIDL FORK-GOLD HIL 36/259 COTTER | SACTO | ETL.5140.INSL | 2024-05-13 | 2024-05-09 | 2024-08-04 | On-Time |  | 2025-05-09 | 2025-05-09 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46253088 | T2 DI MIDL FORK-GOLD HIL 36/259 COTTER | ICS
LC | 128765177 | 036/259 | T2 DI MIDL FORK-GOLD HIL 36/259 RPL INSS | SACTO | ETL.5140.INSL | 2024-05-13 | 2024-05-09 | 2025-01-28 | On-Time |  | 2025-05-09 | 2025-05-09 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570809 | T2 DI MIDL FORK-GOLD HIL 36/259 RPL INSS | 93K
LC | 128768502 | 054/002A | T2 DI HMBLDT-TRINITY 054/002A RPR STRW | EUREKA | ETL.1820.POLE.WOOD | 2024-05-13 | 2024-05-09 | 2025-03-18 | On-Time |  | 2025-05-09 | 2025-05-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46345880 | T2 DI HMBLDT-TRINITY 054/002A RPR POLE | ICW
LC | 128768550 | 053/006 | T2 DI HMBLDT-TRINITY 053/006R RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-13 | 2024-05-09 | 2025-04-08 | On-Time |  | 2025-05-09 | 2025-05-09 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574651 | T2 DI HMBLDT-TRINITY 053/006R RPL STRW | 70Y
LC | 128768554 | 053/006 | T2 DI HMBLDT-TRINITY 053/006L RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-13 | 2024-05-09 | 2025-04-08 | On-Time |  | 2025-05-09 | 2025-05-09 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574651 | T2 DI HMBLDT-TRINITY 053/006R RPL STRW | 70Y
LC | 128888687 | 009/081 | T2 DI CRAG VIEW-CASC 9/81R RPR OPGW | TABLEMTN | ETL.1350.POLE.WDPS | 2024-05-24 | 2024-05-09 | 2025-03-20 | On-Time |  | 2025-05-09 | 2025-05-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Wood | Repair | 46454291 | T2 DI CRAG VIEW-CASC 9/81R RPR OPGW | ICW
LC | 128888715 | 010/094 | T2 DI CRAG VIEW CASCADE 10/94 RPR ANCW | TABLEMTN | ETL.1350.POLE.STPS | 2024-05-24 | 2024-05-09 | 2025-03-19 | On-Time |  | 2025-05-09 | 2025-05-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46454377 | T2 DI CRAG VIEW CASCADE 10/94 RPR ANCW | ICW
LC | 128889448 | 036/158 | T2 DI FULTON-LAKEV 36/158 RPR FOND | LAKEVLLE | ETL.4950.TOWR | 2024-05-24 | 2024-05-09 | 2025-01-13 | On-Time |  | 2025-05-09 | 2025-05-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46289512 | T2 DI FULTON-LAKEV 36/158 RPR FOND | ICQ
LC | 128909951 | 000/019 | T2 DI CLGT-ALLEGHANY 000/019 RPL STRW | SACTO | ETL.6470.POLE.WOOD | 2024-05-29 | 2024-05-09 | 2025-05-06 | On-Time |  | 2025-05-09 | 2025-05-09 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572519 | T2 DI CLGT-ALLEGHANY 000/019 RPL STRW | 70Y
LC | 128910340 | 014/178 | T2 DI DLTA MTN GATE JCT 14/178L RPL STRW | TABLEMTN | ETL.6750.POLE.WDPS | 2024-05-29 | 2024-05-09 | 2024-12-11 | On-Time |  | 2025-05-09 | 2025-05-09 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35558793 | T2 DI DLT-MTN GT JT-MTN 14/178R RPL STRW | 70Y
LC | 128910476 | 015/127A | T2 DI CRG VIEW-CSCD 015/127A RPL ANCW | TABLEMTN | ETL.1350.POLE.NWOD | 2024-05-29 | 2024-05-09 | 2025-03-20 | On-Time |  | 2025-05-09 | 2025-05-09 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572998 | T2 DI CRG VIEW-CSCD 015/127A RPL ANCW | 93E
LC | 128959546 | 064/002B | T2 DI HUMBOLDT-TRINITY 64/002B RPL HRDW | EUREKA | ETL.1820.POLE.WOOD | 2024-05-31 | 2024-05-09 | 2025-04-19 | On-Time |  | 2025-05-09 | 2025-05-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345882 | T2 DI HUMBOLDT-TRINITY 64/002B RPL HRDW | ICW
LC | 128961051 | 002/056 | T2 DI COLGATE-ALLEGHANY 2/56 REFRAME | SACTO | ETL.6470.POLE.WOOD | 2024-05-31 | 2024-05-09 | 2025-05-05 | On-Time |  | 2025-05-09 | 2025-05-09 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35572540 | T2 DI COLGATE-ALLEGHANY 2/56 REFRAME | 93E
LC | 129021554 | 031/229 | T2 DI CARIBOU-TABLE MTN 31/229 RPR JMPS | TABLEMTN | ETL.4440.INSL.NCER | 2024-06-04 | 2024-05-09 | 2025-04-07 | On-Time |  | 2025-05-09 | 2025-05-09 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46337450 | T2 DI CARIBOU-TABLE MTN 31/229 RPR JMPS | ICS
LC | 129021558 | 031/229 | T2 DI CARIBOU-TABLE MTN 31/229 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2024-06-04 | 2024-05-09 | 2025-01-29 | On-Time |  | 2025-05-09 | 2025-05-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354064 | T2 DI CARIBOU-TABLE MTN 31/229 RPR STRT | ICQ
LC | 129022130 | 014/119 | T2 DI CRAG VIEW-CSCDE 14/119R COROCOAT | TABLEMTN | ETL.1350.POLE.STPS | 2024-06-04 | 2024-05-09 | 2025-01-21 | On-Time |  | 2025-05-09 | 2025-05-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Repair | 46454380 | T2 DI CRAG VIEW-CSCDE 14/119R COROCOAT | ICW
LC | 123565157 | 068/344 | T2NT EI MALIN-RND MTN #2 68/344 RPR GYWS | TABLEMTN | ETL.6020.TOWR | 2022-05-10 | 2022-05-10 | 2023-10-12 | On-Time |  | 2025-05-10 | 2025-05-10 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Replace | 45650753 | T2 EI MALIN-ROUND MTN #2 68/344 RPR GYWS | ICS
LC | 128742964 | 007/053 | T2 CTTNWD-DELEVAN #1 7/53 TOUCH | TABLEMTN | ETL.4550.TOWR | 2024-05-10 | 2024-05-10 | 2025-03-03 | On-Time |  | 2024-11-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476195 | T2 CTTNWD-DELEVAN #1 7/53 TOUCH | ICQ
LC | 128743441 | 014/176A | T2 EI DLTA-MTN GATE JCT 14/176A RPR GYWW | TABLEMTN | ETL.6750.POLE.NWOD | 2024-05-10 | 2024-05-10 | 2024-05-10 | Past Due |  | 2025-05-10 | 2025-05-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 46452720 | T2 EI DLTA-MTN GATE JCT 14/176A RPR GYWW | ICS
LC | 128745205 | 007/055 | T2 VACA-SUISUN 007/055 TOUCH | SACTO | ETL.4070.TOWR | 2024-05-10 | 2024-05-10 | 2025-03-04 | On-Time |  | 2024-11-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46460826 | T2 VACA-SUISUN 007/055 RPR STRT | ICQ
LC | 128745832 | 009/070 | T2 WISHON-COPPERMINE 9/70 RPL INSS | FRESNO | ETL.9330.INSL.CERA | 2024-05-10 | 2024-05-10 | 2025-04-22 | On-Time |  | 2025-05-10 | 2025-05-10 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW NONR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574071 | T2 EI WISHON-COPPERMINE 00/11 RPL INSS | 93K
LC | 128746346 | 023/182 | T2 EI CRESTA-RIO OSO 23/182 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-05-10 | 2024-05-10 | 2025-02-11 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381322 | T2 EI CRESTA-RIO OSO 23/182 UNBURY | ICQ
LC | 128746360 | 022/183 | T2 EI CARBERRY SS-RND MTN 22/183 HANGER | TABLEMTN | ETL.5410.INSL.NCER | 2024-05-10 | 2024-05-10 | 2025-01-15 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46354023 | T2 EI CARBERRY SS-RND MTN 22/183 HANGER | ICQ
LC | 128746364 | 022/186 | T2 EI CRBRY SW ST-RD MTN 22/186 RPR INSS | TABLEMTN | ETL.5410.INSL.NCER | 2024-05-10 | 2024-05-10 | 2024-05-28 | On-Time |  | 2024-11-10 | 2025-05-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46251399 | T2 EI CRBRY SW ST-RD MTN 22/186 RPR INSS | ICS
LC | 128746467 | 018/465 | T2 EI CARIBOU #2 18/465 REGRADE | TABLEMTN | ETL.6280.POLE.NWOD | 2024-05-10 | 2024-05-10 | 2025-03-28 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46337206 | T2 EI CARIBOU #2 18/465 REGRADE | ICW
LC | 128746520 | 022/180 | T2 EI CRESTA-RIO OSO 22/180 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-05-10 | 2024-05-10 | 2025-02-11 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381323 | T2 EI CRESTA-RIO OSO 22/180 UNBURY | ICQ
LC | 128746564 | 019/012 | T2 TRINITY-MAPLE CREEK 19/12 COTTER | EUREKA | ETL.8170.POLE.WOOD | 2024-05-10 | 2024-05-10 | 2024-05-10 | Past Due |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345883 | T2 EI TRINITY-MAPLE CREEK 19/12 COTTER | ICW
LC | 128746565 | 019/012 | T2 TRINITY-MAPLE CREEK 19/12 RPR JMPW | EUREKA | ETL.8170.INSL.CERA | 2024-05-10 | 2024-05-10 | 2024-05-10 | Past Due |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Jumper-Wood | Repair | 46345884 | T2 EI TRINITY-MAPLE CREEK 19/12 RPR JMPW | ICW
LC | 128746715 | 000/002 | T2 WV HALSEY-PLACER 000/002 REFRAME | SACTO | ETL.6990.POLE.NWOD | 2024-05-10 | 2024-05-10 | 2024-12-13 | On-Time |  | 2025-05-10 | 2025-05-10 | 637 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35518045 | T2 HALSEY-PLACER 000/002 RPL POLE | 70Y
LC | 128746810 | 006/027B | T2 DI MORRO BY-SLR SS #2 6/27B RPL HRDT | PISMOBCH | ETL.5310.TOWR | 2024-05-10 | 2024-05-10 | 2025-05-05 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46400014 | T2 DI MORRO BY-SLR SS #2 6/27B RPL HRDT | ICQ
LC | 128746863 | 022/438 | T2 EI HAT CRK #1-WSTWD 22/438 RPL POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-10 | 2024-05-10 | 2025-04-30 | On-Time |  | 2025-05-10 | 2025-05-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574763 | T2 EI HAT CRK #1-WSTWD 22/438 RPL POLE | 70Y
LC | 128746949 | 007/031 | T2 DI MORRO BAY-MESA 7/31 BNT STEEL | PISMOBCH | ETL.5290.TOWR | 2024-05-10 | 2024-05-10 | 2025-04-02 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46303931 | T2 DI MORRO BAY-MESA 007/031 BNT STEEL | ICQ
LC | 128746998 | 029/125A | T2 DI MORRO BAY-MESA 029/125A INSP STRT | PISMOBCH | ETL.5290.TOWR | 2024-05-10 | 2024-05-10 | 2024-10-22 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46303933 | T2 DI MORRO BAY-MESA 029/125A INSP STRT | ICQ
LC | 128747007 | 033/149 | T2 DI MORRO BAY-MESA 33/149 INSP STRT | PISMOBCH | ETL.5290.TOWR | 2024-05-10 | 2024-05-10 | 2024-10-03 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327166 | T2 DI MORRO BAY-MESA 33/149 INSP STRT | ICQ
LC | 128747112 | :009/003 | T2 BLLTA-RVRBNK-MLNS SW ST :9/3 RPR INSW | VICTOR | ETL.1070.INSL.NCER | 2024-05-10 | 2024-05-10 | 2025-04-04 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46327506 | T2 BLLTA-RVRBNK-MLNS SW ST_:9/3 RPR INSW | ICW
LC | 128747246 | 012/162 | T2 EI DELTA-MTN GATE JCT 12/162 RPR GYWW | TABLEMTN | ETL.6750.POLE.NWOD | 2024-05-10 | 2024-05-10 | 2024-06-25 | On-Time |  | 2024-11-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262786 | T2 EI DELTA-MTN GATE JCT 12/162 RPR GYWW | ICW
LC | 128747324 | A000/008 | T2 KM GREEN TAP A00/008 COMPLETE | VICTOR | ETL.3505.INSL.NCER | 2024-05-10 | 2024-05-10 | 2025-05-30 | Past Due |  | 2025-05-10 | 2025-05-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46325933 | T2 EI KM GREEN TAP A00/008 COTTER | ICS
LC | 128747402 | 037/172 | T2 EI VACA-LAKEVILLE #1 37/172 RMV VEG | LAKEVLLE | ETL.5840.TOWR | 2024-05-10 | 2024-05-10 | 2025-04-19 | On-Time |  | 2025-05-10 | 2025-05-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128747404 | 037/169 | T2 EI VACA-LAKEVILLE #1 37/169 RMV VEG | LAKEVLLE | ETL.5840.TOWR | 2024-05-10 | 2024-05-10 | 2025-04-19 | On-Time |  | 2025-05-10 | 2025-05-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128749237 | 024/394 | T2 EI KESWICK-TRINITY 24/394 RMV VEG | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-11 | 2024-05-10 | 2025-06-24 | Past Due |  | 2025-05-10 | 2025-05-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128749238 | 024/390 | T2 EI KESWICK-TRINITY 24/390 RPL STRW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-11 | 2024-05-10 | 2025-04-04 | On-Time |  | 2025-05-10 | 2025-05-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573428 | T2 EI KESWICK-TRINITY 24/390 RPL STRW | 70Y
LC | 128749276 | 024/394 | T2 EI KESWICK-TRINITY 24/394 REGRADE | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-11 | 2024-05-10 | 2025-04-03 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46321667 | T2 EI KESWICK-TRINITY 24/394 REGRADE | ICW
LC | 128749277 | 021/310 | T2 EI KESWICK-TRINITY 21/310 GO95 | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-11 | 2024-05-10 | 2025-03-31 | On-Time |  | 2025-05-10 | 2025-05-10 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35616002 | T2 EI KESWICK-TRINITY 21/310 GO95 | 93G
LC | 128757235 | 014/062 | T2 DI MORRO BAY-MESA 014/062 INSP STRT | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2024-09-25 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327160 | T2 DI MORRO BAY-MESA 014/062 INSP STRT | ICQ
LC | 128757238 | 034/150 | T2 DI MORRO BAY-MESA 034/150 TOUCH | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2024-05-10 | Past Due |  | 2024-11-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476155 | T2 DI MORRO BAY-MESA 034/150 TOUCH | ICQ
LC | 128758504 | 033/146 | T2 DI MORRO BAY-MESA 033/146 INSP STRT | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2024-10-03 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327164 | T2 DI MORRO BAY-MESA 033/146 INSP STRT | ICQ
LC | 128758506 | 033/145 | T2 DI MORRO BAY-MESA 033/145 INSP STRT | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2024-10-03 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327163 | T2 DI MORRO BAY-MESA 033/145 INSP STRT | ICQ
LC | 128761289 | 023/105 | T2 MORRO BAY-MESA 23/105 TOUCH | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2025-05-19 | Past Due |  | 2024-08-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476059 | T2 DI MORRO BAY-MESA 23/105 TOUCH | ICQ
LC | 128761466 | 014/171B | T2 DI KSWCK-TRINITY 014/171B RPR GYWW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-13 | 2024-05-10 | 2024-09-14 | On-Time |  | 2024-11-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46251643 | T2 DI KSWCK-TRINITY 014/171B RPR GYWW | ICW
LC | 128761981 | 024/106 | T2 DI MORRO BAY-MESA 24/106 TOUCH | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2024-05-10 | Past Due |  | 2024-11-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476150 | T2 DI MORRO BAY-MESA 24/106 TOUCH | ICQ
LC | 128762142 | 014/064 | T2 DI MORROW BAY MESA 14/64 INSP STRT | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2024-10-02 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327161 | T2 DI MORROW BAY MESA 14/64 INSP STRT | ICQ
LC | 128762143 | 014/064 | T2 DI MORROW BAY MESA 14/64 TOUCH | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2025-06-13 | Past Due |  | 2024-11-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476159 | T2 DI MORROW BAY MESA 14/64 TOUCH | ICQ
LC | 128762146 | 033/147 | T2 DI MORROW BAY MESA 33/147 INSP STRT | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2024-10-03 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327165 | T2 DI MORROW BAY MESA 33/147 INSP STRT | ICQ
LC | 128762148 | 014/063 | T2 MORROW BAY MESA 14/63 MASTIC | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2025-05-19 | Past Due |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46523222 | T2 DI MORROW BAY MESA 14/63 MASTIC | ICQ
LC | 128762833 | 034/151 | T2 DI MORRO BAY-MESA-34/151 INSP STRT | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2024-10-10 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327167 | T2 DI MORRO BAY-MESA-34/151 INSP STRT | ICQ
LC | 128762855 | 011/050 | T2 DI MORRO BAY-MESA 11/50 TOUCH | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2025-06-13 | Past Due |  | 2024-11-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46477347 | T2 DI MORRO BAY-MESA 11/50 TOUCH | ICQ
LC | 128763681 | 023/103 | T2 DI MORRO BAY-MESA 23/103 INSP STRT | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2024-09-26 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327162 | T2 DI MORRO BAY-MESA 23/103 INSP STRT | ICQ
LC | 128764141 | 034/153 | T2 DI MORRO BAY-MESA 34/153 INSP STRT | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2024-10-10 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327168 | T2 DI MORRO BAY-MESA 34/153 INSP STRT | ICQ
LC | 128765639 | 015/181 | T2 DI KESWICK TRINITH 15/181 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-13 | 2024-05-10 | 2024-09-14 | On-Time |  | 2024-08-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251647 | T2 DI KESWICK TRINITH 15/181 RPR JUMW | ICW
LC | 128767791 | 015/181 | T2 DI KESWICK TRINITH 15/181 RMV VEGN | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-13 | 2024-05-10 | 2025-02-06 | On-Time |  | 2025-05-10 | 2025-05-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128767793 | 015/181 | T2 DI KESWICK TRINITH 15/181 INSPECT | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-13 | 2024-05-10 | 2024-09-14 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46311251 | T2 DI KESWICK TRINITH 15/181 INSPECT | ICW
LC | 128768380 | 014/173A | T2 DI KESWICK TRINITY 14/173A RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-13 | 2024-05-10 | 2024-09-14 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311255 | T2 DI KESWICK TRINITY 14/173A RPR JUMW | ICW
LC | 128768381 | 014/173A | T2 DI KESWICK TRINITY 14/173A RMV VEGN | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-13 | 2024-05-10 | 2025-02-06 | On-Time |  | 2025-05-10 | 2025-05-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128768382 | 014/173A | T2 DI KESWICK TRINITY 14/173A INSPECT | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-13 | 2024-05-10 | 2024-09-14 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46311254 | T2 DI KESWICK TRINITY 14/173A INSPECT | ICW
LC | 128768385 | 014/173C | T2 DI KESWICK TRINITY 14/173C RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-13 | 2024-05-10 | 2024-09-13 | On-Time |  | 2024-08-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251645 | T2 DI KESWICK TRINITY 14/173C RPR JUMW | ICW
LC | 128768400 | 015/182 | T2 DI KESWICK-TRIN 15/182 RPR JUMW | TABLEMTN | ETL.7270.INSL.CERA | 2024-05-13 | 2024-05-10 | 2024-09-13 | On-Time |  | 2024-08-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251648 | T2 DI KESWICK-TRIN 15/182 RPR JUMW | ICW
LC | 128768402 | 015/182 | T2 DI KESWICK-TRIN 15/182L RMV VEG | TABLEMTN | ETL.7270.POLE.STPS | 2024-05-13 | 2024-05-10 | 2025-02-06 | On-Time |  | 2025-05-10 | 2025-05-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128768406 | 015/182 | T2 DI KESWICK-TRIN 15/182L INSP STRW | TABLEMTN | ETL.7270.POLE.STPS | 2024-05-13 | 2024-05-10 | 2024-09-13 | On-Time |  | 2024-11-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46250709 | T2 DI KESWICK-TRIN 15/182L INSP STRW | ICW
LC | 128768408 | 015/182 | T2 DI KESWICK-TRIN 15/182C INSP STRW | TABLEMTN | ETL.7270.POLE.STPS | 2024-05-13 | 2024-05-10 | 2024-09-13 | On-Time |  | 2024-11-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46250710 | T2 DI KESWICK-TRIN 15/182C INSP STRW | ICW
LC | 128768413 | 027/458 | T2 DI KESWICK-TRINITY-27/458 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-13 | 2024-05-10 | 2024-09-14 | On-Time |  | 2024-08-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251649 | T2 DI KESWICK-TRINITY-27/458 RPR JUMW | ICW
LC | 128768414 | 027/458 | T2 DI KESWICK-TRINITY-27/458 RPR GYWW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-13 | 2024-05-10 | 2024-09-14 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311249 | T2 DI KESWICK-TRINITY-27/458 RPR GYWW | ICW
LC | 128768472 | 013/167 | T2 DI KESWICK TRINITY 13/167 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-13 | 2024-05-10 | 2025-03-31 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311258 | T2 DI KESWICK TRINITY 13/167 RPR JUMW | ICW
LC | 128768473 | 013/167 | T2 DI KESWICK TRINITY 13/167R RPR GYWW | TABLEMTN | ETL.7270.POLE.WDPS | 2024-05-13 | 2024-05-10 | 2025-03-31 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311257 | T2 DI KESWICK TRINITY 13/167R RPR GYWW | ICW
LC | 128768479 | 014/173B | T2 DI KESWICK TRINITY 14/173B RPR GYWW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-13 | 2024-05-10 | 2024-09-14 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311253 | T2 DI KESWICK TRINITY 14/173B RPR GYWW | ICW
LC | 128768579 | 014/171C | T2 DI KSWCK-TRINITY 014/171C COTTER | TABLEMTN | ETL.7270.INSL.CERA | 2024-05-13 | 2024-05-10 | 2024-09-14 | On-Time |  | 2024-08-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46251644 | T2 DI KSWCK-TRINITY 014/171A COTTER | ICW
LC | 128768585 | 015/066 | T2 DI MORRO BAY-MESA 15/66 TOUCH | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2024-05-10 | Past Due |  | 2024-11-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478222 | T2 DI MORRO BAY-MESA 15/66 TOUCH | ICQ
LC | 128768586 | 005/023A | T2 DI MORRO BAY-MESA 005/023A RPR OPGW | PISMOBCH | ETL.5290.TOWR | 2024-05-13 | 2024-05-10 | 2024-09-25 | On-Time |  | 2024-08-10 | 2025-05-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46257569 | T2 DI MORRO BAY-MESA 005/023A RPR OPGW | ICS
LC | 128781814 | 016/072 | T2 LOS ESTROS-MTCALF 16/72 HANGER | METCALF | ETL.5353.INSL | 2024-05-16 | 2024-05-10 | 2025-03-31 | On-Time |  | 2025-05-10 | 2025-05-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46298816 | T2 LOS ESTROS-MTCALF 16/72 HANGER | ICQ
LC | 128819311 | 017/151A | T2 DI CRG VW-CASCDE 17/151A INSP ANCHW | TABLEMTN | ETL.1350.POLE.NWOD | 2024-05-20 | 2024-05-10 | 2024-09-06 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46306296 | T2 DI CRG VW-CASCDE 17/151A INSP ANCHW | ICW
LC | 128819313 | 017/151A | T2 DI CRG VIEW-CASCADE 17/151A RPR GYWW | TABLEMTN | ETL.1350.POLE.NWOD | 2024-05-20 | 2024-05-10 | 2024-09-06 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46253236 | T2 DI CRG VIEW-CASCADE 17/151A RPR GYWW | ICW
LC | 128836720 | 014/064 | T2 DI DIABLO-MESA 14/64 RPL INSS | PISMOBCH | ETL.4620.INSL.CERA | 2024-05-21 | 2024-05-10 | 2025-03-25 | On-Time |  | 2025-05-10 | 2025-05-10 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35585666 | T2 EI DIABLO-MESA RPL INSS 7 LSTS | 93K
LC | 128901774 | 014/172 | T2 DI KESWICK-TRINITY 14/172 GO95 USAGE | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-28 | 2024-05-10 | 2025-04-14 | On-Time |  | 2025-05-10 | 2025-05-10 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35573304 | T2 DI KESWICK-TRINITY 14/172 GO95 | 93G
LC | 128902088 | 063/317 | T2 DI MALIN-RND MTN #2 63/317 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-05-28 | 2024-05-10 | 2024-08-29 | On-Time |  | 2024-08-10 | 2025-05-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46256528 | T2 DI MALIN-RND MTN #2 63/317 RPR OPGW | ICS
LC | 128902104 | 035/236 | T2 DI TRINITY-COTTONWOOD 35/236 RPR JUMW | TABLEMTN | ETL.4040.INSL.CERA | 2024-05-28 | 2024-05-10 | 2024-08-18 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262801 | T2 DI TRINITY-COTTONWOOD 35/236 RPR JUMW | ICW
LC | 128902499 | 000/018 | T2 DI CLGT-CHALLENGE 000/018 RPL STRW | SACTO | ETL.6480.POLE.WOOD | 2024-05-28 | 2024-05-10 | 2025-04-06 | On-Time |  | 2024-11-10 | 2025-05-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35572545 | T2 DI CLGT-CHALLENGE 000/018 RPL STRW | 70Y
LC | 128957319 | 065/001 | T2 DI HMBLDT TRNTY65/001L RMV VEG | EUREKA | ETL.1820.POLE.STPS | 2024-05-31 | 2024-05-10 | 2024-11-07 | On-Time |  | 2025-05-10 | 2025-05-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128957963 | 065/001 | T2 DI HMBLDT TRNTY65/001 INSP STRW | EUREKA | ETL.1820.POLE.STPS | 2024-05-31 | 2024-05-10 | 2024-09-11 | On-Time |  | 2024-11-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46255663 | T2 DI HMBLDT TRNTY65/001 INSP STRW | ICW
LC | 128957964 | 065/001 | T2 DI HMBLDT TRNTY65/001L INSP STRW | EUREKA | ETL.1820.POLE.STPS | 2024-05-31 | 2024-05-10 | 2024-09-11 | On-Time |  | 2024-11-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46268301 | T2 DI HMBLDT TRNTY65/001L INSP STRW | ICW
LC | 128957966 | 065/001 | T2 DI HMBLDT TRNTY65/001 RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-05-31 | 2024-05-10 | 2025-04-18 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46345885 | T2 DI HMBLDT TRNTY65/001 RPR JUMW | ICW
LC | 128960941 | 013/169C | T2 DI KSWCK-TRINITY 013/169C COTTER | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-31 | 2024-05-10 | 2025-03-31 | On-Time |  | 2025-05-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46311256 | T2 DI KSWCK-TRINITY 013/169C COTTER | ICW
LC | 128961169 | 065/001 | T2 DI HMBLDT TRNTY 65/001R INSP STRW | EUREKA | ETL.1820.POLE.STPS | 2024-05-31 | 2024-05-10 | 2024-09-11 | On-Time |  | 2024-11-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46255664 | T2 DI HMBLDT TRNTY 65/001R INSP STRW | ICW
LC | 128961313 | 027/468 | T2 DI KESWICK TRNITY 27/468 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-31 | 2024-05-10 | 2024-09-13 | On-Time |  | 2024-08-10 | 2025-05-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262822 | T2 DI KESWICK TRNITY 27/468 RPR JUMW | ICW
LC | 128961438 | 014/177 | T2 DI KESWICK TRNITY 14/177 RPL POLE | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-31 | 2024-05-10 | 2025-04-15 | On-Time |  | 2025-05-10 | 2025-05-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573306 | T2 DI KESWICK TRNITY 14/177 RPL POLE | 70Y
LC | 123572581 | 027/135 | T2NT EI RND MTN-TBL MTN#2 27/135 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2022-05-11 | 2022-05-11 | 2023-08-22 | On-Time |  | 2025-05-11 | 2025-05-11 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2N PRTO CLMB FRAB | Overgrown | Vegetation | Remove
LC | 123572703 | 034/293 | T3NT EI PIT #1-CTTNWD 34/293 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2022-05-11 | 2022-05-11 | 2023-07-11 | On-Time |  | 2025-05-11 | 2025-05-11 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3N PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45639716 | T3 EI PIT #1-CTTNWD 34/293 BENT STEEL | ICQ
LC | 123572704 | 031/262 | T3NT EI PIT #1-CTTNWD 31/262 BENT STEEL | TABLEMTN | ETL.5390.TOWR | 2022-05-11 | 2022-05-11 | 2023-10-18 | On-Time |  | 2025-05-11 | 2025-05-11 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45639703 | T3 EI PIT #1-COTTONWD 31/262 BENT STEEL | ICQ
LC | 123592619 | 013/062 | T2NT DI FULTON-PUEBLO 13/62 RPR STRT | LAKEVLLE | ETL.1600.TOWR | 2022-05-14 | 2022-05-11 | 2023-07-31 | On-Time |  | 2025-05-11 | 2025-05-11 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644964 | T2 DI FULTON-PUEBLO 13/62 RPR STRT | ICQ
LC | 123615505 | 016/006 | T2NT DI EXCHQR MRPSA 16/6 REGRADE | FRESNO | ETL.8640.POLE.NWOD | 2022-05-17 | 2022-05-11 | 2023-06-07 | On-Time |  | 2025-05-11 | 2025-05-11 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Repair | 45489452 | T2 DI EXCHQR MRPSA 16/6 REGRADE | ICW
LC | 123629645 | 036/171 | T2NT DI RND MTN-TBL MTN#1 36/171 RPR FND | TABLEMTN | ETL.6060.TOWR | 2022-05-18 | 2022-05-11 | 2023-08-10 | On-Time |  | 2025-05-11 | 2025-05-11 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45644462 | T2 DI RND MTN-TBL MTN#1 36/171 RPR FOND | ICQ
LC | 123678092 | 013/015 | T2NT DI EXCHQR MRPS 13/15 RMV BUTT | FRESNO | ETL.8640.POLE.NWOD | 2022-05-24 | 2022-05-11 | 2023-06-06 | On-Time |  | 2025-05-11 | 2025-05-11 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE ACCM COMP OH TR2 PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 45489464 | T2NT DI EXCHQR MRPS 13/15 RMV BUTT | ICW
LC | 128763946 | 035/237C | T2 DI TRINITY-COTTNWD 35/237C RPR JMPW | TABLEMTN | ETL.4040.INSL.CERA | 2024-05-13 | 2024-05-11 | 2024-08-18 | On-Time |  | 2024-08-11 | 2025-05-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262787 | T2 DI TRINITY-COTTNWD 35/237C RPR JMPW | ICW
LC | 128768524 | 007/067 | T2 DI PARADISE-TBL MTN 7/067 RPL HRDT | TABLEMTN | ETL.4316.TOWR | 2024-05-13 | 2024-05-11 | 2025-05-05 | On-Time |  | 2025-05-11 | 2025-05-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46311043 | T2 DI PARADISE-TBL MTN 7/067 RPL HRDT | ICQ
LC | 128768527 | 007/067 | T2 DI PARADISE-TBL MTN 7/067 RPR INSS | TABLEMTN | ETL.4316.INSL | 2024-05-13 | 2024-05-11 | 2024-12-18 | On-Time |  | 2025-05-11 | 2025-05-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46311120 | T2 DI PARADISE-TBL MTN 7/067 RPR INSS | ICS
LC | 128902182 | 009/012 | T3 BRIDGVIL-GRBRVIL 9/12 TOUCH | EUREKA | ETL.6220.POLE.NWOD | 2024-05-28 | 2024-05-11 | 2025-06-06 | Past Due |  | 2025-05-11 | 2025-05-11 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH XMPT TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46505012 | T3 BRIDGVIL-GRBRVIL 9/12 TOUCH | ICW
LC | 128902193 | 005/006 | T2 DI LAKEVILLE #1 5/6 RPR STRW | LAKEVLLE | ETL.7360.POLE.WOOD | 2024-05-28 | 2024-05-11 | 2025-03-07 | On-Time |  | 2025-05-11 | 2025-05-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46305940 | T2 DI LAKEVILLE #1 5/6 RPR STRW | ICW
LC | 123581543 | 005/000 | T2NT EI LAKEVILLE #1 5/0 RPL ANCW | LAKEVLLE | ETL.7360.POLE.NWOD | 2022-05-12 | 2022-05-12 | 2024-09-24 | On-Time |  | 2025-05-12 | 2025-05-12 | 637T | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35482338 | T2NT EI LAKEVILLE #1 5/0 RPL ANCW | 93E
LC | 123593875 | T-158 | T2NT DI MIDWAY-SANTA MARIA T-158 RMV VEG | MIDWAY | ETL.9240.TOWR | 2022-05-14 | 2022-05-12 | 2023-12-27 | On-Time |  | 2025-05-12 | 2025-05-12 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2N PRTO AIR FRAA | Overgrown | Vegetation | Remove
LC | 123694707 | 015/005 | T2NT DI EXCHQR MRPS 15/5 INS STEP | FRESNO | ETL.8640.POLE.NWOD | 2022-05-25 | 2022-05-12 | 2023-06-07 | On-Time |  | 2025-05-12 | 2025-05-12 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2N PRTO AIR FRAB NTDE | Missing | Hardware-Wood | Install | 45489525 | T2 DI EXCHQR MRPS 15/5 INS STEP | ICW
LC | 129893996 | 000/000 | T3 EL DORADO-MSRI FLT #1 0/0 RPL HNGR | SACTO | ETL.1530.INSL.NCER | 2024-12-04 | 2024-11-12 | 2024-11-12 | Past Due |  | 2025-05-12 | 2025-05-12 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW PATR CLR FLAG OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46491518 | T0 WV EL DRDO-MSRI FLT #1 0/0 RPL HNGR | ICQ
LC | 131333199 | 000/000 | T3 EL DORADO-MSRI FLT #1 0/0 RPL INSS | SACTO | ETL.1530.INSL.NCER | 2025-06-09 | 2024-11-12 | 2024-11-12 | Past Due |  | 2025-05-12 | 2025-05-12 | 532T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW PATR CLR FLAG OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35649068 | T3 EL DORADO-MSRI FLT #1 0/0 RPL INSS | 93K
LC | 123634803 | 003/081 | T3NT DI BURNS-LONE STAR #2 3/81 RMV VEG | MOSSLNDG | ETL.6240.POLE.WOOD | 2022-05-19 | 2022-05-13 | 2024-10-25 | On-Time |  | 2025-05-13 | 2025-05-13 | 564 | TR3N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE ACCM CNCL OH TR3 PRTO AIR FRAB | Overgrown | Vegetation | Trim
LC | 123721185 | 000/010 | T3NT DI MDDL FRK-GLD HILL 0/10 RPR GRDW | SACTO | ETL.5140.POLE.WDPS | 2022-05-31 | 2022-05-13 | 2023-10-10 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 45741393 | T3 DI MDDL FRK-GLD HILL 0/010 RPR GRDW | ICW
LC | 128750027 | 046/289 | T2 MADISON-VACA 46/289 TOUCH | SACTO | ETL.2170.TOWR | 2024-05-13 | 2024-05-13 | 2024-05-13 | Past Due |  | 2024-11-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46463289 | T2 MADISON-VACA 46/289 RPR STRT | ICQ
LC | 128751812 | 003/017 | T2 METCALF-SANTA TERESA 003/017 RPR ADSS | METCALF | ETL.2480.TOWR | 2024-05-13 | 2024-05-13 | 2025-04-01 | On-Time |  | 2025-05-13 | 2025-05-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | ADSS - Steel | Repair | 46298627 | T2 METCALF-SANTA TERESA 003/017 RPR ADSS | ICS
LC | 128752150 | 016/117 | T2 EI ELECTRA-BELLOTA 16/117 RPL INSS | VICTOR | ETL.4670.INSL | 2024-05-13 | 2024-05-13 | 2025-03-20 | On-Time |  | 2025-05-13 | 2025-05-13 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593221 | T2 EI ELECTRA-BELLOTA 002/024 RPL INSS | 93K
LC | 128752155 | 012/085 | T2 EI VAC-VCVLL-JMSN-NRTH 12/85 RPR FOND | LAKEVLLE | ETL.4100.TOWR | 2024-05-13 | 2024-05-13 | 2024-12-17 | On-Time |  | 2024-08-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46252443 | T2 EI VAC-VCVLL-JMSN-NRTH 12/85 RPR FOND | ICQ
LC | 128753143 | 023/604 | T2 CARIBOU #2 23/604 COMPLETE | TABLEMTN | ETL.6280.INSL.NCER | 2024-05-13 | 2024-05-13 | 2025-04-04 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46337207 | T2 CARIBOU #2 23/604 RPR INSW | ICW
LC | 128753243 | :005/001 | T2 BELLT-RVRBNK-MLNS SS :5/1 RPR INSW | VICTOR | ETL.1070.INSL.NCER | 2024-05-13 | 2024-05-13 | 2025-01-30 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46327607 | T2 BELLT-RVRBNK-MLNS SS :5/1 RPR INSW | ICW
LC | 128753393 | 010/015 | T2 EI TRINITY-MAPLE CREEK 10/15 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-05-13 | 2024-05-13 | 2025-01-20 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345887 | T2 EI TRINITY-MAPLE CREEK 10/15 RPR GYWW | ICW
LC | 128753527 | 070/506 | T2 EI BRDGVLL-CTTNWDT 70/506L RPR GYWW | EUREKA | ETL.1110.POLE.WDPS | 2024-05-13 | 2024-05-13 | 2025-05-05 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345890 | T2 EI BRDGVLL-CTTNWDT 70/506L RPR GYWW | ICW
LC | 128753528 | 070/506 | T2 EI BRDGVILE-CTTONWD 70/506L RPR OPGW | EUREKA | ETL.1110.POLE.WDPS | 2024-05-13 | 2024-05-13 | 2025-05-05 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | OPGW - Wood | Repair | 46345891 | T2 EI BRDGVILE-CTTONWD 70/506L RPR OPGW | ICW
LC | 128753582 | 015/071 | T2 EI PALERMO-COLGATE 15/71 TOUCH | TABLEMTN | ETL.5360.TOWR | 2024-05-13 | 2024-05-13 | 2024-05-13 | Past Due |  | 2024-11-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW REMT ACCL OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491544 | T2 EI PALERMO-COLGATE 15/71 TOUCH | ICQ
LC | 128753996 | 014/070 | T2 PALERMO-COLGATE 14/70 TOUCH | TABLEMTN | ETL.5360.TOWR | 2024-05-13 | 2024-05-13 | 2024-05-13 | Past Due |  | 2024-11-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46505502 | T2 PALERMO-COLGATE 14/70 TOUCH | ICQ
LC | 128754111 | 000/000 | T2 POTTER VALLEY-WILLITS 0/0 GO95 CLEAR | WILLITS | ETL.7820.POLE.WOOD | 2024-05-13 | 2024-05-13 | 2024-05-13 | Past Due |  | 2025-05-13 | 2025-05-13 | 401T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAR NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35557697 | T2 POTTER VALLEY-WILLITS 0/0 GO95 CLEAR | 93G
LC | 128754169 | 005/048 | T2 EI DIVIDE-VANDENBERG #2 5/48 RPL INSW | PISMOBCH | ETL.8630.INSL | 2024-05-13 | 2024-05-13 | 2025-01-22 | On-Time |  | 2025-05-13 | 2025-05-13 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573276 | T2 EI DIVIDE-VANDENBERG #2 5/48 RPL INSW | 93I
LC | 128754313 | 000/014 | T2 BRCBRG JCT-MRPSA TP 00/14 RPR GYWW | FRESNO | ETL.8651.POLE.WOOD | 2024-05-13 | 2024-05-13 | 2024-09-04 | On-Time |  | 2024-08-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46250439 | T2 BRCBRG JCT-MRPSA TP 00/14 RPR GYWW | ICW
LC | 128754375 | 000/014 | T2 BRICEBURG JCT-MRPS TP 00/14 COMPLETE | FRESNO | ETL.8651.INSL.NCER | 2024-05-13 | 2024-05-13 | 2025-03-28 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298044 | T2 BRICEBURG JCT-MRPS TP 00/14 COTTER | ICW
LC | 128754445 | :000/001 | T2 EI BELLT-RVRBNK-MLNS SS :0/1 RPR GYWW | VICTOR | ETL.1070.POLE.NWOD | 2024-05-13 | 2024-05-13 | 2024-10-24 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327507 | T2 EI BELLT-RVRBNK-MLNS SS :0/1 RPR GYWW | ICW
LC | 128754624 | 001/024 | T2 EI KILARC-DESCHUTES 01/24 RPL STRW | TABLEMTN | ETL.7300.POLE.WOOD | 2024-05-13 | 2024-05-13 | 2025-03-10 | On-Time |  | 2025-05-13 | 2025-05-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573765 | T2 EI KILARC-DESCHUTES 01/24 RPL STRW | 70Y
LC | 128754750 | 005/047 | T2 EI DIVIDE-VANDENBERG #2 5/47 RPL INSW | PISMOBCH | ETL.8630.INSL.CERA | 2024-05-13 | 2024-05-13 | 2025-01-22 | On-Time |  | 2025-05-13 | 2025-05-13 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573274 | T2 EI DIVIDE-VANDENBERG #2 5/47 RPL INSW | 93I
LC | 128754791 | 046/205 | T2 EI RND MTN-TABL MTN#2 46/205 RPL HRDT | TABLEMTN | ETL.6070.TOWR | 2024-05-13 | 2024-05-13 | 2024-12-31 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Ground Wire-Tower | Replace | 46310388 | T2 EI RND MTN-TABL MTN#2 46/205 RPL HRDT | ICQ
LC | 128759433 | 065/328 | T2 EI MALIN-ROUND MTN#2 065/328 RPR INSS | TABLEMTN | ETL.6020.INSL.NCER | 2024-05-13 | 2024-05-13 | 2025-02-09 | On-Time |  | 2025-05-13 | 2025-05-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46337588 | T2 EI MALIN-ROUND MTN#2 065/328 RPR INSS | ICS
LC | 128759437 | 009/044 | T2 TABLE MTN-PALERMO 9/44 COMPLETE | TABLEMTN | ETL.5690.INSL | 2024-05-13 | 2024-05-13 | 2025-04-03 | On-Time |  | 2025-05-13 | 2025-05-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46389139 | T2 EI TABLE MTN-PALERMO 9/44 COTTER | ICS
LC | 128759581 | 065/329 | T2 EI MALIN-ROUND MTN#2 065/329 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-05-13 | 2024-05-13 | 2025-02-09 | On-Time |  | 2025-05-13 | 2025-05-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338196 | T2 EI MALIN-ROUND MTN#2 065/329 RPR SHLD | ICS
LC | 128761517 | 049/215 | T2 EI RND MTN-TBL MTN #2 49/215 RMV NEST | TABLEMTN | ETL.6070.TOWR | 2024-05-13 | 2024-05-13 | 2025-02-21 | On-Time |  | 2025-05-13 | 2025-05-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306288 | T2 EI RND MTN-TBL MTN #2 49/215 RMV NEST | ICS
LC | 128762608 | 010/018 | T2 EI TRINITY-MAPLE CREEK 10/18 RPR JMPW | EUREKA | ETL.8170.INSL.NCER | 2024-05-13 | 2024-05-13 | 2025-03-22 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Jumper-Wood | Repair | 46345888 | T2 EI TRINITY-MAPLE CREEK 10/18 RPR JMPW | ICW
LC | 128768781 | 013/056A | T2 EI TESLA-METCALF 13/56A RPR FOND | METCALF | ETL.6110.TOWR | 2024-05-13 | 2024-05-13 | 2025-03-04 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46298820 | T2 EI TESLA-METCALF 13/56A RPR FOND | ICQ
LC | 128769011 | 032/222A | T2 DI TRINITY CGNWOOD 32/222A RPR JUMW | TABLEMTN | ETL.4040.INSL.CERA | 2024-05-13 | 2024-05-13 | 2024-08-26 | On-Time |  | 2024-08-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46250275 | T2 DI TRINITY CGNWOOD 32/222A RPR JUMW | ICW
LC | 128769019 | 032/222B | T2 DI TRINITY CGNWOOD 32/222B RPR ANCW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-05-13 | 2024-05-13 | 2024-05-29 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46254932 | T2 DI TRINITY CGNWOOD 32/222B RPR ANCW | ICW
LC | 128769308 | 001/009 | T2 AUBERRY TAP 1/9 RPL INSW | FRESNO | ETL.9331.INSL.NCER | 2024-05-14 | 2024-05-13 | 2025-05-05 | On-Time |  | 2025-05-13 | 2025-05-13 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35554111 | T2 AUBERRY TAP 01/009 RPL INSW | 93I
LC | 128769327 | 025/126 | T2 RND MTN-TBLE MTN#2 25/126 RPR FOND | TABLEMTN | ETL.6070.TOWR | 2024-05-14 | 2024-05-13 | 2025-04-16 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46310387 | T2 EI RND MTN-TBLE MTN#2 25/126 RPR FOND | ICQ
LC | 128769395 | 022/174 | T2 EI CRESTA-RIO OSO 22/174 BNT STEEL | TABLEMTN | ETL.4590.TOWR | 2024-05-14 | 2024-05-13 | 2025-03-18 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381324 | T2 EI CRESTA-RIO OSO 22/174 BNT STEEL | ICQ
LC | 128769397 | 022/175 | T2 EI CRESTA-RIO OSO 22/175 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-14 | 2024-05-13 | 2025-02-10 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381325 | T2 EI CRESTA-RIO OSO 22/175 RPR FOND | ICQ
LC | 128769398 | 022/174 | T2 EI CRESTA-RIO OSO 22/174 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-14 | 2024-05-13 | 2025-02-10 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381326 | T2 EI CRESTA-RIO OSO 22/174 RPR FOND | ICQ
LC | 128769437 | 021/172 | T2 EI CRESTA-RIO OSO 21/172 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-14 | 2024-05-13 | 2025-02-10 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381327 | T2 EI CRESTA-RIO OSO 21/172 RPR FOND | ICQ
LC | 128769438 | 022/177 | T2 EI CRESTA-RIO OSO 22/177 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-14 | 2024-05-13 | 2025-02-11 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381328 | T2 EI CRESTA-RIO OSO 22/177 RPR FOND | ICQ
LC | 128769439 | 021/172 | T2 EI CRESTA-RIO OSO 21/172 CANCEL | TABLEMTN | ETL.4590.INSL.CERA | 2024-05-14 | 2024-05-13 | 2024-05-13 | Past Due |  | 2025-05-13 | 2025-05-13 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570419 | T2 EI CRESTA-RIO OSO RPL INSS | 93K
LC | 128769441 | 021/173 | T2 EI CRESTA-RIO OSO 21/173 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-14 | 2024-05-13 | 2025-02-10 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381329 | T2 EI CRESTA-RIO OSO 21/173 RPR FOND | ICQ
LC | 128769445 | 022/176 | T2 EI CRESTA-RIO OSO 22/176 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-14 | 2024-05-13 | 2025-02-11 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381330 | T2 EI CRESTA-RIO OSO 22/176 RPR FOND | ICQ
LC | 128769461 | 022/177 | T2 EI CRESTA-RIO OSO 22/177 BNT STEEL | TABLEMTN | ETL.4590.TOWR | 2024-05-14 | 2024-05-13 | 2025-03-13 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381331 | T2 EI CRESTA-RIO OSO 22/177 BNT STEEL | ICQ
LC | 128773860 | 000/009 | T2 DI COLGATE-CHALLENGE 0/09 RPR JUMW | SACTO | ETL.6480.INSL.NCER | 2024-05-14 | 2024-05-13 | 2024-08-25 | On-Time |  | 2024-08-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251421 | T2 DI COLGATE-CHALLENGE 0/09 RPR JUMW | ICW
LC | 128773936 | 013/103 | T2 DI PIT #3-PIT #1 13/103 RPR JUMS | TABLEMTN | ETL.5400.INSL.NCER | 2024-05-14 | 2024-05-13 | 2025-02-11 | On-Time |  | 2025-05-13 | 2025-05-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46382962 | T2 DI PIT #3-PIT #1 13/103 RPR JUMS | ICS
LC | 128774112 | 037/324 | T2 DI PIT #1-COTTONWOOD 37/324 RPR JUMS | TABLEMTN | ETL.5390.INSL.NCER | 2024-05-14 | 2024-05-13 | 2025-04-24 | On-Time |  | 2025-05-13 | 2025-05-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46452762 | T2 DI PIT #1-COTTONWOOD 37/324 RPR JUMS | ICS
LC | 128774214 | 034/235C | T2 DI TRINITY-COTT 34/235C RPR JUMW | TABLEMTN | ETL.4040.INSL.CERA | 2024-05-14 | 2024-05-13 | 2024-08-18 | On-Time |  | 2024-08-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46250278 | T2 DI TRINITY-COTT 34/235C RPR JUMW | ICW
LC | 128774215 | 034/235A | T2 DI TRINITY-COTT 34/235A RPR JUMW | TABLEMTN | ETL.4040.INSL.CERA | 2024-05-14 | 2024-05-13 | 2024-08-18 | On-Time |  | 2024-08-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46250276 | T2 DI TRINITY-COTT 34/235A RPR JUMW | ICW
LC | 128774222 | 020/007 | T2 DI TRINITY-MAPLE CRK 20/7 RPR JUMW | EUREKA | ETL.8170.INSL.NCER | 2024-05-14 | 2024-05-13 | 2024-08-16 | On-Time |  | 2024-08-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46249708 | T2 DI TRINITY-MAPLE CRK 20/7 RPR JUMW | ICW
LC | 128774263 | 037/328 | T2 DI RND MTN-CTTNWD #3 037/328 RPR INSS | TABLEMTN | ETL.5650.INSL | 2024-05-14 | 2024-05-13 | 2024-08-26 | On-Time |  | 2024-08-13 | 2025-05-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46250267 | T2 DI RND MTN-CTTNWD #3 037/328 RPR INSS | ICS
LC | 128774323 | 000/005 | T2 DI COLGATE-CHALLENGE 0/5 RPR JUMW | SACTO | ETL.6480.INSL.NCER | 2024-05-14 | 2024-05-13 | 2025-04-06 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46337380 | T2 DI COLGATE-CHALLENGE 0/05 RPR JUMW | ICW
LC | 128774328 | 034/235B | T2 DI TRINITY-COTT 34/235B RPR JUMW | TABLEMTN | ETL.4040.INSL.CERA | 2024-05-14 | 2024-05-13 | 2024-08-18 | On-Time |  | 2024-08-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46250277 | T2 DI TRINITY-COTT 34/235B RPR JUMW | ICW
LC | 128775826 | 105/002 | T2 DI HUMBOLDT-TRINITY 105/002R RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-15 | 2024-05-13 | 2024-09-01 | On-Time |  | 2024-11-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46249703 | T2 DI HUMBOLDT-TRINITY 105/002R RPR GYWW | ICW
LC | 128776141 | 105/002 | T2 HUMBOLDT-TRINITY 105/002R RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-15 | 2024-05-13 | 2025-04-09 | On-Time |  | 2025-05-13 | 2025-05-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35574488 | T2 DI HUMBOLDT-TRINITY 105/002C RPL STRW | 70Y
LC | 128776388 | 105/002 | T2 DI HUMBOLDT-TRINITY 105/002C RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-15 | 2024-05-13 | 2024-09-01 | On-Time |  | 2024-11-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46249704 | T2 DI HUMBOLDT-TRINITY 105/002C RPR GYWW | ICW
LC | 128776459 | 105/002 | T2 DI HUMBOLDT-TRINITY 105/002C RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-15 | 2024-05-13 | 2025-04-09 | On-Time |  | 2025-05-13 | 2025-05-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574488 | T2 DI HUMBOLDT-TRINITY 105/002C RPL STRW | 70Y
LC | 128781290 | 007/051 | T2 EI VALY SPRNGS-BELLOTA 7/51 RPL INSS | VICTOR | ETL.5860.INSL.CERA | 2024-05-16 | 2024-05-13 | 2025-03-25 | On-Time |  | 2025-05-13 | 2025-05-13 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH FMOB TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35593222 | T2 EI VLY SPRNGS-BELLTA 04/28 RPL INSS | 93K
LC | 128902071 | 015/062 | T2 PITTSBURG-EASTSHORE 15/62 RPL INSS | CONCORD | ETL.5462.INSL | 2024-05-28 | 2024-05-13 | 2024-05-13 | Past Due |  | 2025-05-13 | 2025-05-13 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35626540 | T2 DI PITTSBURG-EASTSHORE 9/36 RPL INSS | 93K
LC | 128902269 | 037/323 | T2 DI RND MTN-CTTNWD #3 37/323 BNT STEEL | TABLEMTN | ETL.5650.TOWR | 2024-05-28 | 2024-05-13 | 2025-05-06 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310415 | T2 DI RND MTN-CTTNWD #3 37/323 BNT STEEL | ICQ
LC | 128902351 | 037/326 | T2 DI PIT#1-COTT 37/326 MASTIC | TABLEMTN | ETL.5390.TOWR | 2024-05-28 | 2024-05-13 | 2025-04-30 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381540 | T2 DI PIT#1-COTT 37/326 MASTIC | ICQ
LC | 128902355 | 037/326 | T2 DI PIT #1 - COTTWD 37/326 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2024-05-28 | 2024-05-13 | 2025-04-30 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381541 | T2 DI PIT #1 - COTTWD 37/326 BNT STEEL | ICQ
LC | 128902510 | 037/326 | T2 DI RND MTN-CTNWD #3 37/326 RPL INSS | TABLEMTN | ETL.5650.INSL | 2024-05-28 | 2024-05-13 | 2025-03-04 | On-Time |  | 2025-05-13 | 2025-05-13 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574240 | T2 ROUND MTN-COTNWD #3 47/411 RPL INSS | 93K
LC | 128902556 | 006/109 | T2 DI PIT #1-HT CRK #2-BRNY 6/109 RM VEG | TABLEMTN | ETL.7040.POLE.WOOD | 2024-05-28 | 2024-05-13 | 2024-11-15 | On-Time |  | 2025-05-13 | 2025-05-13 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128902652 | 038/331 | T2 DI RND MTN-COTNWD#3 38/331 BNT STEEL | TABLEMTN | ETL.5650.TOWR | 2024-05-28 | 2024-05-13 | 2025-04-30 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310416 | T2 DI RND MTN-COTNWD#3 38/331 BNT STEEL | ICQ
LC | 128902654 | 038/331 | T2 DI RND MTN-COTNWD#3 38/331 RPL HRDT | TABLEMTN | ETL.5650.TOWR | 2024-05-28 | 2024-05-13 | 2025-04-30 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46310417 | T2 DI RND MTN-COTNWD#3 38/331 RPL HRDT | ICQ
LC | 128902743 | 003/096 | T2 DI COLGATE-ALLEGHANY 3/96 RPL POLE | SACTO | ETL.6470.POLE.WOOD | 2024-05-28 | 2024-05-13 | 2025-05-12 | On-Time |  | 2025-05-13 | 2025-05-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586836 | T2 DI COLGATE-ALLEGHANY 3/96 RPL POLE | 70Y
LC | 128903011 | 003/027 | T2 DI MORAGA-OAKLAND #3 3/27 RMV VEG | CONCORD | ETL.2740.TOWR | 2024-05-28 | 2024-05-13 | 2025-04-11 | On-Time |  | 2025-05-13 | 2025-05-13 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128909827 | 013/133 | T2 DI RND MTN CTNWD #3 13/133 TOUCH | TABLEMTN | ETL.5650.TOWR | 2024-05-29 | 2024-05-13 | 2025-03-08 | On-Time |  | 2024-11-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478223 | T2 DI RND MTN CTNWD #3 13/133 TOUCH | ICQ
LC | 128957901 | 004/111 | T2 DI CLGT-ALLEGHANY 004/111 RPR STRW | SACTO | ETL.6470.POLE.WOOD | 2024-05-31 | 2024-05-13 | 2025-05-12 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46460017 | T2 DI CLGT-ALLEGHANY 004/111 RPR STRW | ICW
LC | 128961198 | 003/090 | T2 DI COLGATE-ALLEGHANY 3/90 REFRAME | SACTO | ETL.6470.POLE.WOOD | 2024-05-31 | 2024-05-13 | 2025-05-12 | On-Time |  | 2025-05-13 | 2025-05-13 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35572544 | T2 DI COLGATE-ALLG 3/90 REFRAME | 93E
LC | 128961567 | 006/105 | T2 DI PT #1-HT CRK#2-BRNY 6/105 RPL HRDW | TABLEMTN | ETL.7040.POLE.WOOD | 2024-05-31 | 2024-05-13 | 2025-05-20 | Past Due |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46454293 | T2 DI PT #1-HT CRK#2-BRNY 6/105 RPL HRDW | ICW
LC | 128961886 | 016/114 | T2 IGNAC ALT SAUSLT #2 16/114 RMV VEG | LAKEVLLE | ETL.7170.POLE.WOOD | 2024-05-31 | 2024-05-13 | 2024-05-13 | Past Due |  | 2025-05-13 | 2025-05-13 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128961981 | 003/084 | T2 DI COLGATE ALLEGHANY 3/84 RPL POLE | SACTO | ETL.6470.POLE.WOOD | 2024-05-31 | 2024-05-13 | 2025-05-07 | On-Time |  | 2025-05-13 | 2025-05-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572542 | T2 DI COLGATE ALLEGHANY 3/84 RPL POLE | 70Y
LC | 128962393 | 017/122 | T2 DI HELMS-GREGG #1 17/122 RMV VEG | FRESNO | ETL.4870.TOWR | 2024-05-31 | 2024-05-13 | 2025-05-22 | Past Due |  | 2025-05-13 | 2025-05-13 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE SPCR CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128964184 | 002/022 | T2 DI MONTA VISTA-BURNS 2/22 RPR ANCW | MOSSLNDG | ETL.7590.POLE.WDPS | 2024-06-01 | 2024-05-13 | 2025-03-26 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46391299 | T2 DI MONTA VISTA-BURNS 2/22 RPR ANCW | ICW
LC | 128964186 | 002/022 | T2 DI MONTA VISTA-BURNS 2/22 RPR GYWW | MOSSLNDG | ETL.7590.POLE.WDPS | 2024-06-01 | 2024-05-13 | 2025-03-26 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391301 | T2 DI MONTA VISTA-BURNS 2/22 RPR GYWW | ICW
LC | 128964280 | 008/138 | T2 DI PIT#1-HAT CRK#2-BRNY-8/138 COTTER | TABLEMTN | ETL.7040.INSL.NCER | 2024-06-01 | 2024-05-13 | 2025-02-25 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46454294 | T2 DI PIT#1-HAT CRK#2-BRNY-8/138 COTTER | ICW
LC | 128964465 | 060/001 | T2 DI HUMBOLDT-TRINITY 060/001 RPR STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-01 | 2024-05-13 | 2025-04-18 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46345889 | T2 DI HUMBOLDT-TRINITY 060/001 RPR STRW | ICW
LC | 128964509 | 003/031 | T2 DI MORANGA OAKLAND#3 03/031 TOUCH | CONCORD | ETL.2740.TOWR | 2024-06-01 | 2024-05-13 | 2025-05-14 | Past Due |  | 2024-11-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAR NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485717 | T2 DI MORANGA OAKLAND#3 03/031 TOUCH | ICQ
LC | 129026154 | 003/088 | T2 DI COLGATE-ALLEGHANY 03/88 RPL POLE | SACTO | ETL.6470.POLE.WOOD | 2024-06-05 | 2024-05-13 | 2025-05-12 | On-Time |  | 2025-05-13 | 2025-05-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572543 | T2 DI COLGATE-ALLEGHANY 03/88 RPL POLE | 70Y
LC | 129026302 | 002/071 | T2 DI COLGATE-ALLG 2/71 RPR XARM | SACTO | ETL.6470.POLE.WOOD | 2024-06-05 | 2024-05-13 | 2025-05-05 | On-Time |  | 2025-05-13 | 2025-05-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46404599 | T2 DI COLGATE-ALLG 2/71 RPR XARM | ICW
LC | 129032106 | 013/134 | T2 DI RND MTN-CTTNWD 13/134 RPL HRDT | TABLEMTN | ETL.5650.TOWR | 2024-06-06 | 2024-05-13 | 2025-05-01 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46310414 | T2 DI RND MTN-CTTNWD 13/134 RPL HRDT | ICQ
LC | 129036274 | 037/323 | T2 DI PT #1-CTTNWD 37/323 BENT STEEL | TABLEMTN | ETL.5390.TOWR | 2024-06-07 | 2024-05-13 | 2025-04-30 | On-Time |  | 2025-05-13 | 2025-05-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381908 | T2 DI PT #1-CTTNWD 37/323 BENT STEEL | ICQ
LC | 129054984 | 013/132 | T2 DI RND MTN-CTNWD #3 13/132 RPR ADSS | TABLEMTN | ETL.5650.TOWR | 2024-06-10 | 2024-05-13 | 2025-02-26 | On-Time |  | 2025-05-13 | 2025-05-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | ADSS - Steel | Repair | 46416222 | T2NT DI RND MTN-CTNWD #3 13/132 RPR ADSS | ICS
LC | 123621811 | 004/032 | T2NT DI SBRANTE-MORAGA-TWR 4/32 INSS RPL | CONCORD | ETL.3742.INSL.NCER | 2022-05-17 | 2022-05-14 | 2023-08-25 | On-Time |  | 2025-05-14 | 2025-05-14 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2N PRTO AIR NTDE | No Good/Out of Stdrd | Insulator-Steel | Replace | 31618119 | T2 DI SOBRANTE-MORAGA RPL INSS 4TWR | 93K
LC | 128769290 | 003/005 | T2 POTTER VALLEY-MNDCNO 3/5 RPL INSS | WILLITS | ETL.7810.INSL.CERA | 2024-05-14 | 2024-05-14 | 2025-06-03 | Past Due |  | 2025-05-14 | 2025-05-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35608530 | T2 POTTER VALLEY-MNDCNO 3/5 RPL INSS | 93K
LC | 128769314 | 016/074 | T2 LOS ESTEROS-METCALF 16/74 RPL HNGR | METCALF | ETL.5353.INSL | 2024-05-14 | 2024-05-14 | 2024-05-14 | Past Due |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46299707 | T2 LOS ESTEROS-METCALF 16/74 RPL HNGR | ICQ
LC | 128769786 | 009/052 | T2 PARKWAY-MORAGA 09/052 RPR STRT | CONCORD | ETL.5930.TOWR | 2024-05-14 | 2024-05-14 | 2025-03-19 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46289317 | T2 PARKWAY-MORAGA 09/052 STAT HOLD | ICQ
LC | 128770136 | 015/189 | T2 WV KESWICK-TRINITY 015/189 INS DMPW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-14 | 2024-05-14 | 2025-04-19 | On-Time |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46311247 | T2 WV KESWICK-TRINITY 015/189 INS DMPW | ICW
LC | 128770239 | 004/018 | T2 MONTA VISTA-JEFFRSN #1 04/18 RPL INSS | METCALF | ETL.5220.INSL | 2024-05-14 | 2024-05-14 | 2025-01-04 | On-Time |  | 2025-05-14 | 2025-05-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574093 | T2 MONTA VISTA-JEFFRSN #1 RPL INSS IN 2 | 93K
LC | 128770278 | 004/018 | T2 MONTA VISTA-JEFFRSN #2 04/18 RPL INSS | METCALF | ETL.5230.INSL | 2024-05-14 | 2024-05-14 | 2025-01-06 | On-Time |  | 2025-05-14 | 2025-05-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574632 | T2 MONTA VISTA-JEFFRSN #2 RPL INSS IN 2T | 93K
LC | 128770647 | 001/005 | T2 EI VLLY SPRNGS-CLVRS 1/5 RPR GYWW | VICTOR | ETL.8220.POLE.NWOD | 2024-05-14 | 2024-05-14 | 2025-05-04 | On-Time |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46326998 | T2 EI VLLY SPRNGS-CLVRS 1/5 RPR GYWW | ICW
LC | 128770893 | 000/002 | T2 EI ROUND MTN-TABLE MTN #1 0/2 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-14 | 2024-05-14 | 2025-02-04 | On-Time |  | 2025-05-14 | 2025-05-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128771098 | 013/107 | T2 EI TIGER CREK-ELECTRA 13/107 RPL INSS | VICTOR | ETL.5780.INSL | 2024-05-14 | 2024-05-14 | 2025-05-10 | On-Time |  | 2025-05-14 | 2025-05-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK SPCR CLR ACCL COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35599725 | T2 EI TIGER CREK-ELECTRA 13/107 RPL INSS | 93K
LC | 128771256 | 069/285 | T2 EI RND MTN-TABL MTN#2 69/285 RMV NEST | TABLEMTN | ETL.6070.TOWR | 2024-05-14 | 2024-05-14 | 2025-02-19 | On-Time |  | 2025-05-14 | 2025-05-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306289 | T2 EI RND MTN-TABL MTN#2 69/285 RMV NEST | ICS
LC | 128771359 | 010/039 | T2 EI TESLA-METCALF 010/039 MASTIC | METCALF | ETL.6110.TOWR | 2024-05-14 | 2024-05-14 | 2025-03-04 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46298818 | T2 EI TESLA-METCALF 010/039 MASTIC | ICQ
LC | 128771398 | 010/177 | T2 TEJON-LEBEC 10/177 COTTER | MIDWAY | ETL.9250.INSL.NCER | 2024-05-14 | 2024-05-14 | 2025-03-05 | On-Time |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46302545 | T2 TEJON-LEBEC 10/177 COTTER | ICW
LC | 128771946 | 001/007 | T2 EI VLLY SPRNGS-CLVRS 1/7 RPL STRW | VICTOR | ETL.8220.POLE.WOOD | 2024-05-14 | 2024-05-14 | 2025-05-06 | On-Time |  | 2025-05-14 | 2025-05-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573398 | T2 EI VLLY SPRNGS-CLVRS 1/7 RPL STRW | 70Y
LC | 128772253 | 005/041 | T2 COTTONWOOD-DELEVAN #1 5/41 TOUCH | TABLEMTN | ETL.4550.TOWR | 2024-05-14 | 2024-05-14 | 2025-03-13 | On-Time |  | 2024-11-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46486823 | T2 COTTONWOOD-DELEVAN #1 5/41 TOUCH | ICQ
LC | 128772594 | 020/239A | T2 EI DRUM-SUMMIT #1 020/239A RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-05-14 | 2024-05-14 | 2024-07-16 | On-Time |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46273109 | T2 EI DRUM-SUMMIT #1 020/239A RPR GYWW | ICW
LC | 128772602 | 020/239C | T2 EI DRUM-SUMMIT #1 20/239C RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-05-14 | 2024-05-14 | 2024-07-16 | On-Time |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46273110 | T2 EI DRUM-SUMMIT #1 20/239C RPR GYWW | ICW
LC | 128772954 | 066/584 | T2 COTTONWOOD-GLENN 66/584 RPR INSS | TABLEMTN | ETL.4560.INSL.CERA | 2024-05-14 | 2024-05-14 | 2024-05-28 | On-Time |  | 2024-08-14 | 2025-05-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46249320 | T2 COTTONWOOD-GLENN 66/584 RPR INSS | ICS
LC | 128773007 | 010/067 | T2 EI OLEUM-G #1 010/067 RPL HRDT | CONCORD | ETL.3150.TOWR | 2024-05-14 | 2024-05-14 | 2025-02-11 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAR | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289318 | T2 EI OLEUM-G #1 010/067 RPL HRDT | ICQ
LC | 128773259 | 002/054 | T2 CARIBOU-WESTWOOD 02/054 RPR INSW | TABLEMTN | ETL.6300.INSL.NCER | 2024-05-14 | 2024-05-14 | 2025-03-06 | On-Time |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46337328 | T2 CARIBOU-WESTWOOD 02/054 RPR INSW | ICW
LC | 128773310 | 064/322 | T2 EI MALIN-ROUND MTN#2 064/322 RPR ANCT | TABLEMTN | ETL.6020.TOWR | 2024-05-14 | 2024-05-14 | 2025-04-11 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46381434 | T2 EI MALIN-ROUND MTN#2 064/322 RPR ANCT | ICQ
LC | 128773353 | 004/090 | T2 CORDELIA #1 TAP 04/90 RPR STRW | SACTO | ETL.8182.POLE.WOOD | 2024-05-14 | 2024-05-14 | 2025-04-25 | On-Time |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Structure-Wood | Repair | 46337359 | T2 CORDELIA #1 TAP 04/90 RPR STRW | ICW
LC | 128773362 | 003/002 | T2 CLEAR LAKE-HOPLAND 3/2 RPL STRW | WILLITS | ETL.6390.POLE.WOOD | 2024-05-14 | 2024-05-14 | 2024-05-14 | Past Due |  | 2024-08-14 | 2025-05-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35611933 | T2 EI CLEAR LAKE-HOPLAND 3/002 RPL STRW | 70Y
LC | 128773393 | 007/067A | T2 DI PARADISE-TBL MTN 7/067A TOUCH | TABLEMTN | ETL.4316.POLE.STPS | 2024-05-14 | 2024-05-14 | 2025-05-03 | On-Time |  | 2024-11-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46486719 | T2 DI PARADISE-TBL MTN 7/067A TOUCH | ICW
LC | 128773462 | 001/035 | T2 EI CARIBOU #2 01/035 RPR INSW | TABLEMTN | ETL.6280.INSL.NCER | 2024-05-14 | 2024-05-14 | 2025-05-06 | On-Time |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46337208 | T2 EI CARIBOU #2 01/035 RPR INSW | ICW
LC | 128773476 | 000/005 | T2 EI ROUND MTN-TBL MTN#1 0/5 RPR INSS | TABLEMTN | ETL.6060.INSL | 2024-05-14 | 2024-05-14 | 2025-01-30 | On-Time |  | 2025-05-14 | 2025-05-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46306290 | T2 EI ROUND MTN-TBL MTN#1 0/5 RPR INSS | ICS
LC | 128773477 | 000/005 | T2 EI ROUND MTN-TABLE MTN #1 0/5 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-14 | 2024-05-14 | 2024-11-20 | On-Time |  | 2025-05-14 | 2025-05-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128773478 | 014/082 | T2 HAAS-MCCALL 14/82 BENT STEEL | FRESNO | ETL.4850.TOWR | 2024-05-14 | 2024-05-14 | 2024-05-14 | Past Due |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46297879 | T2 EI HAAS-MCCALL 14/82 BENT STEEL | ICQ
LC | 128773507 | 002/055 | T2 EI KILARC-DESCHUTES 2/55 RPR GYWW | TABLEMTN | ETL.7300.POLE.NWOD | 2024-05-14 | 2024-05-14 | 2025-03-10 | On-Time |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46306291 | T2 EI KILARC-DESCHUTES 2/55 RPR GYWW | ICW
LC | 128773766 | 038/010 | T2 DI FULTON HPLND 38/10 RPR GYWW | LAKEVLLE | ETL.6890.POLE.NWOD | 2024-05-14 | 2024-05-14 | 2024-05-28 | On-Time |  | 2024-11-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46249713 | T2 DI FULTON HPLND 38/10 RPR GYWW | ICW
LC | 128773797 | 008/001 | T2 EI CLEAR LAKE-HOPLAND 8/001 RPR STRW | WILLITS | ETL.6390.POLE.WOOD | 2024-05-14 | 2024-05-14 | 2025-05-15 | Past Due |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310262 | T2 EI CLEAR LAKE-HOPLAND 8/001 RPR STRW | ICW
LC | 128774239 | 036/210 | T2 INDIAN FLAT-YOSEMITE 36/210 RPR JUMS | FRESNO | ETL.1112.INSL.NCER | 2024-05-14 | 2024-05-14 | 2024-05-14 | Past Due |  | 2025-05-14 | 2025-05-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46250581 | T2 DI INDN FLT-YOSEMITE 36/210 RPR JMPS | ICS
LC | 128774281 | 011/093 | T2 DI PIT #1-COTTONWOOD 11/93 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-05-14 | 2024-05-14 | 2025-05-07 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381520 | T2 DI PIT #1-COTTONWOOD 11/93 RPR FOND | ICQ
LC | 128774282 | 011/093 | T2 DI PIT #1-COTTONWOOD 11/93 COTTER | TABLEMTN | ETL.5390.INSL.NCER | 2024-05-14 | 2024-05-14 | 2024-11-06 | On-Time |  | 2024-11-14 | 2025-05-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46250286 | T2 DI PIT #1-COTTONWOOD 11/93 RPR INSS | ICS
LC | 128774745 | 018/239 | T2 EI KESWICK-TRINITY 18/239 RPR JUMW | TABLEMTN | ETL.7270.INSL.CERA | 2024-05-15 | 2024-05-14 | 2025-04-15 | On-Time |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311246 | T2 EI KESWICK-TRINITY 18/239 RPR JUMW | ICW
LC | 128774755 | 018/244 | T2 EI KESWICK-TRINITY 18/244 RPR GYWW | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-15 | 2024-05-14 | 2024-09-14 | On-Time |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46253090 | T2 EI KESWICK-TRINITY 18/244 RPR GYWW | ICW
LC | 128774928 | 007/065 | T2 EI BCKS CRK-RCK CK-CRST 7/65 RPL HRDT | TABLEMTN | ETL.4430.TOWR | 2024-05-15 | 2024-05-14 | 2025-04-29 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46353966 | T2 EI BCKS CRK-RCK CK-CRST 7/65 RPL HRDT | ICQ
LC | 128776425 | 026/000 | T2 PHILO JCT-ELK 26/000L RPL ANCW | WILLITS | ETL.7780.POLE.WDPS | 2024-05-15 | 2024-05-14 | 2024-06-15 | On-Time |  | 2025-05-14 | 2025-05-14 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CREW COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35522272 | T2 DI PHILO JCT-ELK 025/007 RPL ANCW | 93E
LC | 128776427 | 026/000 | T2 PHILO JCT-ELK 26/000C RPL ANCW | WILLITS | ETL.7780.POLE.WDPS | 2024-05-15 | 2024-05-14 | 2024-06-15 | On-Time |  | 2025-05-14 | 2025-05-14 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CREW COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35522272 | T2 DI PHILO JCT-ELK 025/007 RPL ANCW | 93E
LC | 128777830 | 024/196 | T2 PIT #1-COTTONWOOD 24/196 RPL HRDT | TABLEMTN | ETL.5390.TOWR | 2024-05-15 | 2024-05-14 | 2025-04-04 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381521 | T2 DI PIT #1-COTTONWOOD 24/196 RPL HRDT | ICQ
LC | 128777832 | 024/196 | T2 DI PIT #1-COTTONWOOD 24/196 RPR JUMS | TABLEMTN | ETL.5390.INSL.NCER | 2024-05-15 | 2024-05-14 | 2025-04-22 | On-Time |  | 2025-05-14 | 2025-05-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46452770 | T2 DI PIT #1-COTTONWOOD 24/196 RPR JUMS | ICS
LC | 128779799 | 024/193 | T2 DI PIT #1-COTTONWOOD 24/193 RPR JUMW | TABLEMTN | ETL.5390.INSL.NCER | 2024-05-15 | 2024-05-14 | 2024-11-08 | On-Time |  | 2024-08-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46253094 | T2 DI PIT #1-COTTONWOOD 24/193 RPR JUMW | ICW
LC | 128779850 | 041/346 | T2 DI RND MTN-COTTNWD #3 41/346 RPR STL | TABLEMTN | ETL.5650.TOWR | 2024-05-15 | 2024-05-14 | 2024-07-10 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46257385 | T2 DI RND MTN-COTTNWD #3 41/346 RPR STL | ICQ
LC | 128803603 | A013/291 | T2 SALINAS-LAURELES A013/291 RPR POLE | MOSSLNDG | ETL.7930.POLE.WOOD | 2024-05-19 | 2024-05-14 | 2025-04-01 | On-Time |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46329995 | T2 SALINAS-LAURELES A013/291 RPR POLE | ICW
LC | 128818868 | 000/001 | T2 GARCIA TAP 000/001 RMV IDLE ANCW | WILLITS | ETL.8411.POLE.WOOD | 2024-05-20 | 2024-05-14 | 2024-05-14 | Past Due |  | 2025-05-14 | 2025-05-14 | 673T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW CREW COMP OH TR2 PRTO FRAB NTDE | Idle | Structure-Wood | Remove | 35525872 | T2NT GARCIA TAP 000/002 RMV IDLE | 93J
LC | 128909945 | 015/278 | T2 DI FULTON-MOL-COT 15/278 INSP STRW | LAKEVLLE | ETL.6910.POLE.WOOD | 2024-05-29 | 2024-05-14 | 2024-07-24 | On-Time |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCH COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46255773 | T2 DI FULTON-MOL-COT 15/278 INSP STRW | ICW
LC | 128910155 | 015/279 | T2 DI FLTN-MLNO-COTATI 015/279 RPL INSW | LAKEVLLE | ETL.6910.INSL.CERA | 2024-05-29 | 2024-05-14 | 2025-01-10 | On-Time |  | 2025-05-14 | 2025-05-14 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574261 | T2 DI FLTN-MLNO-COTATI 015/279 RPL INSW | 93I
LC | 128910417 | 016/305 | T2 DI FLTON MLINO COTATI 16/305 INSP STR | LAKEVLLE | ETL.6910.POLE.WOOD | 2024-05-29 | 2024-05-14 | 2024-07-24 | On-Time |  | 2025-05-14 | 2025-05-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46255774 | T2 DI FLTON MLINO COTATI 16/305 INSP STR | ICW
LC | 128960816 | 012/061 | T2 DI FULTON-PUEBLO 12/61 RMV VEG | LAKEVLLE | ETL.1600.TOWR | 2024-05-31 | 2024-05-14 | 2025-05-08 | On-Time |  | 2025-05-14 | 2025-05-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128960854 | 012/061 | T2 DI FULTON-PUEBLO 12/61 TOUCH | LAKEVLLE | ETL.1600.TOWR | 2024-05-31 | 2024-05-14 | 2025-03-14 | On-Time |  | 2024-11-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485392 | T2 DI FULTON-PUEBLO 12/61 TOUCH | ICQ
LC | 128961952 | 075/380B | T2 DI MLN RD MTN#2 75/380B RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-05-31 | 2024-05-14 | 2025-03-21 | On-Time |  | 2025-05-14 | 2025-05-14 | 93Z | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716778 | T2 DI MLN RD MTN#2 RPL ANCT 10 TWRS | 93Z
LC | 128961954 | 075/380B | T2 DI MLN RD MTN#2 75/380B RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-05-31 | 2024-05-14 | 2025-02-09 | On-Time |  | 2025-05-14 | 2025-05-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46338269 | T2 DI MLN RD MTN#2 75/380B RPR OPGW | ICS
LC | 128963969 | 041/347 | T2 DI PIT #1-COTTONWOOD 41/347 MASTIC | TABLEMTN | ETL.5390.TOWR | 2024-06-01 | 2024-05-14 | 2025-05-05 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381548 | T2 DI PIT #1-COTTONWOOD 41/347 MASTIC | ICQ
LC | 128964065 | 025/206 | T2 DI PIT #1-COTTONWOOD 25/206 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-06-01 | 2024-05-14 | 2025-04-14 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381549 | T2 DI PIT #1-COTTONWOOD 25/206 RPR FOND | ICQ
LC | 128964081 | 012/099 | T2NT DI PIT #1-CTTNWD 12/99 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-06-01 | 2024-05-14 | 2024-05-14 | Past Due |  | 2027-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair
LC | 128964174 | 003/036 | T2 DI LAKEVILLE-SONOMA #1 3/36 RPL INSS | LAKEVLLE | ETL.2063.INSL.NCER | 2024-06-01 | 2024-05-14 | 2024-05-14 | Past Due |  | 2025-05-14 | 2025-05-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35608531 | T2 DI LAKEVILLE-SONOMA #1 3/36 RPL INSS | 93K
LC | 128964175 | 003/036 | T2 DI LAKEVILLE-SONOMA #2 3/36 RPL INSS | LAKEVLLE | ETL.2070.INSL.NCER | 2024-06-01 | 2024-05-14 | 2025-05-10 | On-Time |  | 2025-05-14 | 2025-05-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35608532 | T2 DI LAKEVILLE-SONOMA #2 3/36 RPL INSS | 93K
LC | 128964233 | 041/346 | T2 DI PIT #1-COTTONWOOD 41/346 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-06-01 | 2024-05-14 | 2025-05-05 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381870 | T2 DI PIT #1-COTTONWOOD 41/346 RPR STRT | ICQ
LC | 128964253 | 015/295 | T2 DI FULTON-MOL-COT 15/295 RMV VEG | LAKEVLLE | ETL.6910.POLE.WOOD | 2024-06-01 | 2024-05-14 | 2024-09-19 | On-Time |  | 2024-11-14 | 2025-05-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE SPCR ACCH COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128964384 | 022/107 | T2 DI MNTA VSTA-CYOT SS 22/107 RPR SHLS | MOSSLNDG | ETL.5090.TOWR | 2024-06-01 | 2024-05-14 | 2025-03-28 | On-Time |  | 2025-05-14 | 2025-05-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46391300 | T2 DI MNTA VSTA-CYOT SS 22/107 RPR SHLS | ICS
LC | 128964429 | 068/001 | T2 DI HMBLDT TRNTY 68/001 RMV VEG | EUREKA | ETL.1820.POLE.STPS | 2024-06-01 | 2024-05-14 | 2025-01-22 | On-Time |  | 2025-05-14 | 2025-05-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128964431 | 036/313 | T2 DI PIT #1-COTTONWOOD 36/313 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-06-01 | 2024-05-14 | 2025-02-07 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381872 | T2 DI PIT #1-COTTONWOOD 36/313 RPR STRT | ICQ
LC | 128964432 | 036/313 | T2 DI PIT #1-COTTONNWOOD 36/313 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-06-01 | 2024-05-14 | 2025-02-07 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381873 | T2 DI PIT #1-COTTONNWOOD 36/313 RPR FOND | ICQ
LC | 128964535 | 003/026 | T2 DI MORAGA-OAKLAND #4 03/26 RPL INSS | CONCORD | ETL.2750.INSL.NCER | 2024-06-01 | 2024-05-14 | 2025-06-01 | Past Due |  | 2025-05-14 | 2025-05-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575045 | T2 DI MORAGA-OAKLAND #4 03/26 RPL INSS. | 93K
LC | 128964536 | 003/026 | T2 DI MORAGA-OAKLAND#3 03/26 RPL INSS | CONCORD | ETL.2740.INSL.NCER | 2024-06-01 | 2024-05-14 | 2025-06-08 | Past Due |  | 2025-05-14 | 2025-05-14 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575044 | T0 DI MRAGA-OKLND #3 RPL INSLS IN 3 TWRS | 93K
LC | 128964609 | 015/284 | T2NT DI FLTN-MLNO-COTATI 15/284 RMV VEG | LAKEVLLE | ETL.6910.POLE.WOOD | 2024-06-01 | 2024-05-14 | 2024-05-14 | Past Due |  | 2027-05-14 | 2025-05-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129015887 | 032/152 | T2 DI TRACY-LOS BANOS 32/152 RPR SHLS | VICTOR | ETL.6130.TOWR | 2024-06-03 | 2024-05-14 | 2025-02-18 | On-Time |  | 2025-05-14 | 2025-05-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46325935 | T2 DI TRACY-LOS BANOS 32/152 RPR SHLS | ICS
LC | 129021538 | 022/104 | T2 DI FULTON-PUEB 22/104 RMV VEG | LAKEVLLE | ETL.1600.TOWR | 2024-06-04 | 2024-05-14 | 2025-03-19 | On-Time |  | 2025-05-14 | 2025-05-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129021808 | 041/345 | T2 DI RND MTN-CTNWD#3 41/345 BNT STEEL | TABLEMTN | ETL.5650.TOWR | 2024-06-04 | 2024-05-14 | 2025-05-08 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310418 | T2 DI RND MTN-CTNWD#3 41/345 BNT STEEL | ICQ
LC | 129021878 | 27 | T2 DI COLGATE-CHALLENGE B00/21 RPR SWTCH | SACTO | ETL.6480.SWIT | 2024-06-04 | 2024-05-14 | 2025-04-06 | On-Time |  | 2025-05-14 | 2025-05-14 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | Out of Adjustment | Switch | Repair | 46337352 | T2 DI COLGATE-CHALLENGE B00/21 RPR SWTCH | ICE
LC | 129021919 | 041/349 | T2 DI RND MTN CNWD #3 41/349 COTTER | TABLEMTN | ETL.5650.INSL | 2024-06-04 | 2024-05-14 | 2025-03-04 | On-Time |  | 2025-05-14 | 2025-05-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46416199 | T2 DI RND MTN CNWD #3 41/349 COTTER | ICS
LC | 129021987 | 009/078 | T2 DI PIT #3-PIT #2 9/78 TOUCH | TABLEMTN | ETL.5400.TOWR | 2024-06-04 | 2024-05-14 | 2025-03-08 | On-Time |  | 2024-11-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478226 | T2 DI PIT #3-PIT #2 9/78 TOUCH | ICQ
LC | 129022091 | 022/103 | T2 DI FULTON PUEBLO 22/103 RMV VEGN | LAKEVLLE | ETL.1600.TOWR | 2024-06-04 | 2024-05-14 | 2025-03-19 | On-Time |  | 2025-05-14 | 2025-05-14 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129054886 | 038/266 | T2 DI MDL FRK-GLD HL 38/266 RPL INSS | SACTO | ETL.5140.INSL | 2024-06-10 | 2024-05-14 | 2025-01-30 | On-Time |  | 2025-05-14 | 2025-05-14 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570809 | T2 DI MIDL FORK-GOLD HIL 36/259 RPL INSS | 93K
LC | 129054889 | 011/065 | T2 STAN-MLNS SS-RVRBNK 11/65 RPR STRT | VICTOR | ETL.3840.TOWR | 2024-06-10 | 2024-05-14 | 2025-05-08 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416705 | T2 DI STAN-MLNS SS-RVRBNK 11/65 RPR STRT | ICQ
LC | 129061520 | 012/098 | T2 DI PIT #3-PIT #1 12/98 RPL HRDT | TABLEMTN | ETL.5400.TOWR | 2024-06-11 | 2024-05-14 | 2025-04-11 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46382040 | T2 DI PIT #3-PIT #1 12/98 RPL HRDT | ICQ
LC | 129067382 | 036/159 | T2 DI MSS LNDNG-LS BNS 36/159 RPL INSS | MOSSLNDG | ETL.6040.INSL | 2024-06-12 | 2024-05-14 | 2025-04-16 | On-Time |  | 2025-05-14 | 2025-05-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35596168 | T2 DI MSS LNDNG-LS BNS 36/159 RPL INSS | 93K
LC | 129067437 | 025/205 | T2 DI PIT#1-COTTONWOOD 25/205 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-06-12 | 2024-05-14 | 2025-05-13 | On-Time |  | 2025-05-14 | 2025-05-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381912 | T2NT DI PIT#1-COTTONWOOD 25/205 RPR STRT | ICQ
LC | 129067474 | 036/208 | T2 INDIAN FLAT-YOSEMITE 36/208 RPR JUMS | FRESNO | ETL.1112.INSL.NCER | 2024-06-12 | 2024-05-14 | 2024-05-14 | Past Due |  | 2025-05-14 | 2025-05-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46265973 | T2 DI INDN FLT-YSMT 36/208 RPR JUMS | ICS
LC | 129818339 | 006/057 | T3 DI MONTA VISTA-BURNS 6/057 RPR JUMW | MOSSLNDG | ETL.7590.INSL.NCER | 2024-11-14 | 2024-11-14 | 2025-01-28 | On-Time |  | 2025-02-14 | 2025-05-14 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46453180 | T3 DI MONTA VISTA-BURNS 6/057 RPR JUMW | ICW
LC | 128774594 | 014/047 | T2 EXCHEQUER-INDIAN FLT 14/47 COTTER | FRESNO | ETL.8650.INSL.NCER | 2024-05-15 | 2024-05-15 | 2025-04-01 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297993 | T2 EXCHEQUER-INDIAN FLT 14/47 COTTER | ICS
LC | 128774918 | 032/154 | T2 RND MTN-TBL MTN#2 32/154 RPR INSS | TABLEMTN | ETL.6070.INSL | 2024-05-15 | 2024-05-15 | 2025-02-21 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46306292 | T2 RND MTN-TBL MTN#2 32/154 RPR INSS | ICS
LC | 128774942 | 003/015 | T2 EI MONTA VSTA-JFFRSN #1 3/15 RPL INSS | METCALF | ETL.5220.INSL | 2024-05-15 | 2024-05-15 | 2025-01-05 | On-Time |  | 2025-05-15 | 2025-05-15 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35587697 | T2 EI MONTA VSTA-JFFRSN #1 3/15 RPL INSS | 93K
LC | 128775279 | 028/011C | T2 PHILO JCT-ELK 028/010C GO95 CLEAR | WILLITS | ETL.7780.POLE.WOOD | 2024-05-15 | 2024-05-15 | 2025-01-28 | On-Time |  | 2025-05-15 | 2025-05-15 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35564029 | T2 PHILO JCT-ELK 28/011B GO95 CLEAR | 93G
LC | 128775336 | 036/002B | T2 PHILO JCT-ELK 36/002B GO95 | WILLITS | ETL.7780.POLE.WOOD | 2024-05-15 | 2024-05-15 | 2025-01-30 | On-Time |  | 2025-05-15 | 2025-05-15 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35557696 | T2 PHILO JCT-ELK 36/002A GO95 | 93G
LC | 128775349 | 028/011B | T2 PHILO JCT-ELK 28/011B GO95 CLEAR | WILLITS | ETL.7780.POLE.WOOD | 2024-05-15 | 2024-05-15 | 2025-01-28 | On-Time |  | 2025-05-15 | 2025-05-15 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35564029 | T2 PHILO JCT-ELK 28/011B GO95 CLEAR | 93G
LC | 128775361 | 036/002A | T2 PHILO JCT-ELK 36/002A GO95 | WILLITS | ETL.7780.POLE.WOOD | 2024-05-15 | 2024-05-15 | 2025-01-30 | On-Time |  | 2025-05-15 | 2025-05-15 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35557696 | T2 PHILO JCT-ELK 36/002A GO95 | 93G
LC | 128775380 | 036/002C | T2 PHILO JCT-ELK 36/002C GO95 | WILLITS | ETL.7780.POLE.WOOD | 2024-05-15 | 2024-05-15 | 2025-01-30 | On-Time |  | 2025-05-15 | 2025-05-15 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35557696 | T2 PHILO JCT-ELK 36/002A GO95 | 93G
LC | 128776159 | 020/106 | T2 EI HAAS-MCCALL 20/106 RMV NEST | FRESNO | ETL.4850.TOWR | 2024-05-15 | 2024-05-15 | 2025-05-08 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46297994 | T2 EI HAAS-MCCALL 20/106 RMV NEST | ICS
LC | 128777064 | 020/234C | T2 DRUM-SUMMIT #1 20/234C COMPLETE | SACTO | ETL.1440.POLE.NWOD | 2024-05-15 | 2024-05-15 | 2025-05-01 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46397991 | T2 EI DRUM-SUMMIT #1 20/234C RPR GYWW | ICW
LC | 128777316 | 000/016 | T2 DI LAYTONVILLE-COVELO 0/16 RPR STRW | WILLITS | ETL.7390.POLE.WOOD | 2024-05-15 | 2024-05-15 | 2025-06-10 | Past Due |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46446809 | T2 DI LAYTONVILLE-COVELO 0/16 RPR STRW | ICW
LC | 128777336 | 019/177 | T2 UKIAH-HOPLAND-CLVRDL 19/177 RPR GYWW | WILLITS | ETL.4050.POLE.NWOD | 2024-05-15 | 2024-05-15 | 2025-06-20 | Past Due |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446811 | T2 UKIAH-HOPLAND-CLVRDL 19/177 RPR GYWW | ICW
LC | 128777763 | 013/111 | T2 EI TGER CRK-VLY SPRNGS 13/111 RMV VEG | VICTOR | ETL.5790.TOWR | 2024-05-15 | 2024-05-15 | 2024-05-15 | Past Due |  | 2025-05-15 | 2025-05-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128778175 | 045/006 | T2 EI TRINITY-MAPLE CRK 45/6L COMPLETE | EUREKA | ETL.8170.POLE.STPS | 2024-05-15 | 2024-05-15 | 2025-05-08 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345901 | T2 EI TRINITY-MAPLE CRK 45/6 RPR GYWW | ICW
LC | 128778176 | 045/006 | T2 TRINITY-MAPLE CRK 45/6R COMPLETE | EUREKA | ETL.8170.POLE.STPS | 2024-05-15 | 2024-05-15 | 2025-05-08 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345902 | T2 EI TRINITY-MAPLE CRK 45/6 RPR GYWW | ICW
LC | 128778202 | 045/006 | T2 EI TRINITY-MAPLE CRK 45/6 RPR GYWW | EUREKA | ETL.8170.POLE.STPS | 2024-05-15 | 2024-05-15 | 2025-05-08 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345903 | T2 EI TRINITY-MAPLE CRK 45/6 RPR GYWW | ICW
LC | 128778286 | 016/091 | T2 EI HAAS-MCCALL 16/091 COTTER | FRESNO | ETL.4850.INSL | 2024-05-15 | 2024-05-15 | 2025-05-08 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SPCR ACCH COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297995 | T2 EI HAAS-MCCALL 16/091 COTTER | ICS
LC | 128778455 | :001/008 | T2 BELLT-RVRBNK-MLNS SS :1/8 RPR INSW | VICTOR | ETL.1070.INSL.NCER | 2024-05-15 | 2024-05-15 | 2025-01-31 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46327602 | T2 BELLT-RVRBNK-MLNS SS :1/8 RPR INSW | ICW
LC | 128778651 | 005/096 | T2 SAN MATEO-HILLSDALE JCT 5/96 GO95 | METCALF | ETL.7950.POLE.WOOD | 2024-05-15 | 2024-05-15 | 2024-05-15 | Past Due |  | 2025-05-15 | 2025-05-15 | 401 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW OTHR OH FMOB TR2 PRTO FRAR NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35542095 | T2 SAN MATEO-HILLSDALE JCT 5/97 GO95 | 93G
LC | 128779166 | 018/174 | T2 UKIAH-HPLND-CLVRDL 18/174 RPR STRW | WILLITS | ETL.4050.POLE.WOOD | 2024-05-15 | 2024-05-15 | 2025-06-20 | Past Due |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46446810 | T2 EI UKIAH-HPLND-CLVRDL 18/174 RPR STRW | ICW
LC | 128779241 | 010/002 | T2 WV LAKEVILLE #1 010/002 RPL POLE | LAKEVLLE | ETL.7360.POLE.WOOD | 2024-05-15 | 2024-05-15 | 2025-05-13 | On-Time |  | 2025-05-15 | 2025-05-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574117 | T2 WV LAKEVILLE #1 010/002 RPL POLE | 70Y
LC | 128779491 | 051/249 | T2 EI CORTINA-MENDOCIN#1 51/249 RPR STRT | WILLITS | ETL.1330.TOWR | 2024-05-15 | 2024-05-15 | 2024-09-25 | On-Time |  | 2025-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46290425 | T2 EI CORTINA-MENDOCIN#1 51/249 RPR STRT | ICQ
LC | 128779554 | 008/179 | T2 EI KILARC-DESCHUTES 8/179 RMV VEG | TABLEMTN | ETL.7300.POLE.WOOD | 2024-05-15 | 2024-05-15 | 2024-11-13 | On-Time |  | 2025-05-15 | 2025-05-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128779571 | 005/113 | T2 EI KILARC-DESCHUTES 005/113 RPL STRW | TABLEMTN | ETL.7300.POLE.WOOD | 2024-05-15 | 2024-05-15 | 2025-05-14 | On-Time |  | 2025-05-15 | 2025-05-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573772 | T2 EI KILARC-DESCHUTES 005/113 RPL POLE | 70Y
LC | 128779597 | 006/057 | T2NT EI BKS CRK-RK CRK-CRT 6/57 RPR STRT | TABLEMTN | ETL.4430.TOWR | 2024-05-15 | 2024-05-15 | 2025-03-18 | On-Time |  | 2027-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46353967 | T2NT EI BKS CRK-RK CRK-CRT 6/57 RPR STRT | ICQ
LC | 128779620 | 006/056 | T2NT EI BKS CRK-RK CRK-CRT 6/56 RPR STRT | TABLEMTN | ETL.4430.TOWR | 2024-05-15 | 2024-05-15 | 2025-03-18 | On-Time |  | 2027-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC CLR ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46353968 | T2NT EI BKS CRK-RK CRK-CRT 6/56 RPR STRT | ICQ
LC | 128779692 | 000/006 | T2 EI RND MTN-TBL MTN#1 0/6 RMV VEG | TABLEMTN | ETL.6060.POLE.NWOD | 2024-05-15 | 2024-05-15 | 2025-02-04 | On-Time |  | 2025-05-15 | 2025-05-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128779697 | 061/001 | T2 DI HUMBOLDT-TRINITY 61/01R RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-05-15 | 2024-05-15 | 2025-02-18 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345905 | T2 DI HUMBOLDT-TRINITY 61/01R RPR GYWW | ICW
LC | 128779698 | 061/001 | T2 DI HUMBOLDT-TRINITY 61/01 RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-05-15 | 2024-05-15 | 2024-08-30 | On-Time |  | 2024-08-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46249700 | T2 DI HUMBOLDT-TRINITY 61/01 RPR JUMW | ICW
LC | 128779710 | 000/006 | T2 EI RND MTN-TBL MTN#1 0/6 RPR JMPW | TABLEMTN | ETL.6060.INSL | 2024-05-15 | 2024-05-15 | 2025-01-30 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Jumper-Steel | Repair | 46306294 | T2 EI RND MTN-TBL MTN#1 0/6 RPR JMPW | ICS
LC | 128779793 | 028/484 | T2 EI KESWICK-TRINITY 28/484 RPL STRW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-15 | 2024-05-15 | 2025-04-02 | On-Time |  | 2025-05-15 | 2025-05-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573717 | T2 EI KESWICK-TRINITY 28/484 RPL STRW | 70Y
LC | 128779796 | 027/457 | T2 EI KESWICK-TRINITY 27/457 RPL STRW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-15 | 2024-05-15 | 2025-04-05 | On-Time |  | 2025-05-15 | 2025-05-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573715 | T2 EI KESWICK-TRINITY 27/457 RPL STRW | 70Y
LC | 128779806 | 028/471 | T2 EI KESWICK-TRINITY 28/471 RPR INSW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-15 | 2024-05-15 | 2025-04-15 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46311244 | T2 EI KESWICK-TRINITY 28/471 RPR INSW | ICW
LC | 128779823 | 027/470 | T2 EI KESWICK-TRINITY 27/470 RPR JMPW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-15 | 2024-05-15 | 2025-04-02 | On-Time |  | 2024-08-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311245 | T2 EI KESWICK-TRINITY 27/470 RPR JUMW | ICW
LC | 128780046 | 000/004 | T2 DI LAYTONVILLE-COVELO 0/4 RPR GYWW | WILLITS | ETL.7390.POLE.WOOD | 2024-05-15 | 2024-05-15 | 2025-04-14 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446808 | T2 DI LAYTONVILLE-COVELO 0/4 RPR GYWW | ICW
LC | 128780076 | 007/058 | T2NT EI VACA-VCVL-JMSN-NRTH 7/58 RPR FND | LAKEVLLE | ETL.4100.TOWR | 2024-05-15 | 2024-05-15 | 2024-05-15 | Past Due |  | 2027-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair
LC | 128780204 | 051/001A | T2 DI HUMBOLDT-TRINITY 51/01A RPR INSW | EUREKA | ETL.1820.INSL.CERA | 2024-05-15 | 2024-05-15 | 2025-04-07 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46345904 | T2 DI HUMBOLDT-TRINITY 51/01A RPR INSW | ICW
LC | 128780209 | 061/003C | T2 DI HUMBOLDT-TRINITY 61/3C RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-05-15 | 2024-05-15 | 2025-03-20 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345907 | T2 DI HUMBOLDT-TRINITY 61/3C RPR GYWW | ICW
LC | 128780245 | :007/061 | T2 DI PIT #3-PIT #1 :7/61 RPL INSS | TABLEMTN | ETL.5400.INSL.NCER | 2024-05-15 | 2024-05-15 | 2025-02-11 | On-Time |  | 2025-05-15 | 2025-05-15 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570818 | T2 DI PIT #3-PIT #1 :7/61 RPL INSS | 93K
LC | 128780246 | 052/002 | T2 DI HUMBOLDT-TRINITY 52/02 RPR JUMW | EUREKA | ETL.1820.INSL.CERA | 2024-05-15 | 2024-05-15 | 2024-08-26 | On-Time |  | 2024-08-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46249619 | T2 DI HUMBOLDT-TRINITY 52/02 RPR JUMW | ICW
LC | 128780267 | 034/295 | T2 DI RND MTN-CTTNWD #3 34/295 RPL INSS | TABLEMTN | ETL.5650.INSL | 2024-05-15 | 2024-05-15 | 2024-08-26 | On-Time |  | 2024-08-15 | 2025-05-15 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35555825 | T2 DI RND MTN-CTTNWD #3 RPL INSS 2 TWRS | 93K
LC | 128780269 | 013/114 | T2 DI CRAG VIEW-CASCADE 13/114 RPR OPGW | TABLEMTN | ETL.1350.TOWR | 2024-05-15 | 2024-05-15 | 2024-09-09 | On-Time |  | 2024-08-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46251380 | T2 DI CRAG VIEW-CASCADE 13/114 RPR OPGW | ICS
LC | 128780271 | 013/114 | T2 DI CRAG VIEW-CASCADE 13/114 RMV NEST | TABLEMTN | ETL.1350.TOWR | 2024-05-15 | 2024-05-15 | 2024-09-09 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46320185 | T2 DI CRAG VIEW-CASCADE 13/114 RMV NEST | ICS
LC | 128780277 | 013/171 | T2 DELTA-MTN GATE 13/171 RPR JUMS | TABLEMTN | ETL.6750.INSL.NCER | 2024-05-15 | 2024-05-15 | 2025-06-10 | Past Due |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Steel | Repair | 46452778 | T2 DI DELTA-MTN GATE 13/171 RPR JUMS | ICS
LC | 128780301 | 013/063 | T2 EI MOSS LANDING-COBURN 13/063 RMV VEG | MOSSLNDG | ETL.5330.TOWR | 2024-05-15 | 2024-05-15 | 2024-05-15 | Past Due |  | 2025-05-15 | 2025-05-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128780563 | 019/230 | T2 EI DRUM-SUMMIT #1_019/230 RPL DMPW | SACTO | ETL.1440.INSL.NCER | 2024-05-16 | 2024-05-15 | 2025-05-01 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46397992 | T2 EI DRUM-SUMMIT #1_019/230 RPL DMPW | ICW
LC | 128794931 | 061/001 | T2 DI HUMBOLDT-TRINITY 61/01C RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-05-17 | 2024-05-15 | 2025-02-18 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345906 | T2 DI HUMBOLDT-TRINITY 61/01C RPR GYWW | ICW
LC | 128799885 | 035/296 | T2 DI ROUND MTN-CTNWD #3 35/296 RPL INSS | TABLEMTN | ETL.5650.INSL | 2024-05-17 | 2024-05-15 | 2024-08-26 | On-Time |  | 2024-08-15 | 2025-05-15 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35555825 | T2 DI RND MTN-CTTNWD #3 RPL INSS 2 TWRS | 93K
LC | 128800134 | 023/189 | T2 DI PIT #1-COTTONWOOD 023/189 RPR JUMS | TABLEMTN | ETL.5390.INSL.NCER | 2024-05-17 | 2024-05-15 | 2024-11-08 | On-Time |  | 2024-08-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46251391 | T2 DI PIT #1-COTTONWOOD 023/189 RPR JUMS | ICS
LC | 128800213 | 004/043 | T2 DI HLSDL JCT-HLF MN BY 4/43R RPR GYWW | METCALF | ETL.7060.POLE.WDPS | 2024-05-17 | 2024-05-15 | 2025-02-18 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286677 | T2 DI HLSDL JCT-HLF MN BY 4/43R RPR GYWW | ICW
LC | 128800215 | 004/043 | T2 DI HLSDL JCT-HLF MN BY 4/43C RPR GYWW | METCALF | ETL.7060.POLE.WDPS | 2024-05-17 | 2024-05-15 | 2025-02-18 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286678 | T2 DI HLSDL JCT-HLF MN BY 4/43C RPR GYWW | ICW
LC | 128800292 | 000/003 | T2 DI RINCON #2 TAP 000/003 RPL INSS | LAKEVLLE | ETL.1611.INSL.CERA | 2024-05-17 | 2024-05-15 | 2025-04-01 | On-Time |  | 2025-05-15 | 2025-05-15 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577314 | T2 DI RINCON #2 TAP 000/003 RPL INSS | 93K
LC | 128800299 | 013/104 | T2 DI PIT #3-PIT #1 013/104 RPR INSS | TABLEMTN | ETL.5400.INSL.NCER | 2024-05-17 | 2024-05-15 | 2024-08-22 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300814 | T2 DI PIT #3-PIT #1 013/104 RPR INSS | ICS
LC | 128800351 | 013/104 | T2 DI PIT #3-PIT #1 013/104 RPR JUMS | TABLEMTN | ETL.5400.INSL.NCER | 2024-05-17 | 2024-05-15 | 2024-08-22 | On-Time |  | 2024-08-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46252098 | T2 DI PIT #3-PIT #1 013/104 RPR JUMS | ICS
LC | 128800419 | 014/093 | T2 DI JFFRSN-MARTIN 014/093 RPL HRDS | METCALF | ETL.5710.POLE.NWOD | 2024-05-17 | 2024-05-15 | 2025-04-25 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Steel | Replace | 46286790 | T2 DI JFFRSN-MARTIN 014/093 RPL HRDS | ICS
LC | 128964417 | 016/300 | T2 DI FLTN-MLN-COTATI 16/300 RPR INSW | LAKEVLLE | ETL.6910.INSL.NCER | 2024-06-01 | 2024-05-15 | 2025-01-08 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46305945 | T2 DI FLTN-MLN-COTATI 16/300 RPR INSW | ICW
LC | 128964443 | 013/104 | T2 DI PIT #1-COTTONWOOD 13/104 RPL HRDT | TABLEMTN | ETL.5390.TOWR | 2024-06-01 | 2024-05-15 | 2025-05-07 | On-Time |  | 2025-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381874 | T2 DI PIT #1-COTTONWOOD 13/104 RPL HRDT | ICQ
LC | 128964504 | 038/333 | T2 DI PIT #1 COTTONWOOD 38/333 RPL HRDT | TABLEMTN | ETL.5390.TOWR | 2024-06-01 | 2024-05-15 | 2025-05-06 | On-Time |  | 2025-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381875 | T2 DI PIT #1 COTTONWOOD 38/333 RPL HRDT | ICQ
LC | 128964659 | 033/269 | T2 DI BRIDGVIL-CTNWD-33/269R RPL POLE | TABLEMTN | ETL.1110.POLE.WDPS | 2024-06-01 | 2024-05-15 | 2025-04-27 | On-Time |  | 2025-05-15 | 2025-05-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35572065 | T2 DI BRIDGEVIL-CTTNWD 33/268C RPL STRW | 70Y
LC | 128964670 | 033/269 | T2 DI BRIDGEVIL-CTNWD-33/269L RPL POLE | TABLEMTN | ETL.1110.POLE.WDPS | 2024-06-01 | 2024-05-15 | 2025-04-27 | On-Time |  | 2025-05-15 | 2025-05-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35572065 | T2 DI BRIDGEVIL-CTTNWD 33/268C RPL STRW | 70Y
LC | 129015348 | :005/051 | T2 DI PIT #3-PIT #1 :005/051 RPR INSS | TABLEMTN | ETL.5400.INSL.NCER | 2024-06-03 | 2024-05-15 | 2025-02-11 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46382476 | T2 DI PIT #3-PIT #1 :005/051 RPR INSS | ICS
LC | 129015399 | 011/068 | T2 DI STNSLS-MLNS-RVRBN 11/68 RPL HRDT | VICTOR | ETL.3840.TOWR | 2024-06-03 | 2024-05-15 | 2025-05-08 | On-Time |  | 2025-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46416703 | T2 DI STNSLS-MLNS-RVRBN 11/68 RPL HRDT | ICQ
LC | 129015633 | 023/188 | T2 DI PIT #1-COTTONWOOD 23/188 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-06-03 | 2024-05-15 | 2025-04-03 | On-Time |  | 2025-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381876 | T2 DI PIT #1-COTTONWOOD 23/188 RPR FOND | ICQ
LC | 129015635 | 039/334 | T2 DI PIT #1-COTTONWOOD 39/334 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-06-03 | 2024-05-15 | 2025-05-08 | On-Time |  | 2025-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381877 | T2 DI PIT #1-COTTONWOOD 39/334 RPR STRT | ICQ
LC | 129015796 | 039/336 | T2 DI RND MTN-CTTNWD #3 39/336 RPR INSS | TABLEMTN | ETL.5650.INSL.NCER | 2024-06-03 | 2024-05-15 | 2025-03-04 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46416198 | T2 DI RND MTN-CTTNWD #3 39/336 RPR INSS | ICS
LC | 129015828 | 023/190 | T2 DI PIT #1-COTTONWOOD 23/190 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-06-03 | 2024-05-15 | 2025-04-04 | On-Time |  | 2025-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381879 | T2 DI PIT #1-COTTONWOOD 23/190 RPR STRT | ICQ
LC | 129015829 | 023/190 | T2 DI PIT #1-COTTONWOOD 23/190 RPL HRDT | TABLEMTN | ETL.5390.TOWR | 2024-06-03 | 2024-05-15 | 2025-04-04 | On-Time |  | 2025-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381900 | T2 DI PIT #1-COTTONWOOD 23/190 RPL HRDT | ICQ
LC | 129015870 | 011/099 | T2 DI CRAG VIEW-CASC 11/99 COMPLETE | TABLEMTN | ETL.1350.TOWR | 2024-06-03 | 2024-05-15 | 2025-04-16 | On-Time |  | 2025-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381341 | T2 DI CRAG VIEW-CASC 11/99 RPL HRDT | ICQ
LC | 129016011 | 067/005A | T2 DI HUMBOLDT-TRINITY 67/5A RPR STRW | EUREKA | ETL.1820.POLE.WOOD | 2024-06-03 | 2024-05-15 | 2025-04-11 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46345910 | T2 DI HUMBOLDT-TRINITY 67/5A RPR STRW | ICW
LC | 129016119 | 040/342 | T2 DI RND MTN-CTTNWD #3 40/342 RPR STRT | TABLEMTN | ETL.5650.TOWR | 2024-06-03 | 2024-05-15 | 2025-05-08 | On-Time |  | 2025-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310420 | T2 DI RND MTN-CTTNWD #3 40/342 RPR STRT | ICQ
LC | 129016217 | 026/118 | T2 DI TESLA-LOS BNS #1 26/118 RPR SHIELD | VICTOR | ETL.6100.TOWR | 2024-06-03 | 2024-05-15 | 2025-04-25 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46325936 | T2 DI TESLA-LOS BNS #1 26/118 RPR SHIELD | ICS
LC | 129016240 | 012/109 | T2 DI CRAG VIEW-CASC 12/109 COMPLETE | TABLEMTN | ETL.1350.TOWR | 2024-06-03 | 2024-05-15 | 2025-03-21 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46396448 | T2 DI CRAG VIEW-CASC 12/109 RPR OPGW | ICS
LC | 129021901 | 003/017D | T2 DI MCLF STA TSA EDVL#1 3/17D COMPLETE | METCALF | ETL.2480.TOWR | 2024-06-04 | 2024-05-15 | 2024-07-25 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Steel | Repair | 46256398 | T2 DI MCLF STA TSA EDVL#1 3/17D RPR ADSS | ICS
LC | 129021969 | 062/001 | T2 DI HUMBOLDT TRINITY 62/001 RPR JUMW | EUREKA | ETL.1820.INSL.CERA | 2024-06-04 | 2024-05-15 | 2025-04-18 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46345909 | T2 DI HUMBOLDT TRINITY 62/001 RPR JUMW | ICW
LC | 129022001 | 004/046A | T2 DI HILLSDALE JCT-HMB 4/46A RPR ANCW | METCALF | ETL.7060.POLE.WOOD | 2024-06-04 | 2024-05-15 | 2025-02-18 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46286709 | T2 DI HILLSDALE JCT-HMB 4/46A RPR ANCW | ICW
LC | 129022004 | 004/046B | T2 DI HILLSDALE JCT-HMB 4/46B RPR ANCW | METCALF | ETL.7060.POLE.WOOD | 2024-06-04 | 2024-05-15 | 2025-02-18 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46286712 | T2 DI HILLSDALE JCT-HMB 4/46B RPR ANCW | ICW
LC | 129022005 | 004/046C | T2 DI HILLSDALE JCT-HMB 4/46C RPR ANCW | METCALF | ETL.7060.POLE.WOOD | 2024-06-04 | 2024-05-15 | 2025-02-18 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46286713 | T2 DI HILLSDALE JCT-HMB 4/46C RPR ANCW | ICW
LC | 129022066 | 016/003A | T2 DI TRNTY-MAPLE CRK 016/003A RPR ANCW | EUREKA | ETL.8170.POLE.NWOD | 2024-06-04 | 2024-05-15 | 2025-01-23 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46345899 | T2 DI TRNTY-MAPLE CRK 016/003A RPR ANCW | ICW
LC | 129022161 | 035/297 | T2 DI PIT #1-COTTONWOOD 35/297 RPR GYWT | TABLEMTN | ETL.5390.TOWR | 2024-06-04 | 2024-05-15 | 2025-02-06 | On-Time |  | 2025-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381903 | T2 DI PIT #1-COTTONWOOD 35/297 RPR GYWT | ICQ
LC | 129022164 | 035/297 | T2 DI PIT #1-COTTONWOOD 35/297 RMV VEG | TABLEMTN | ETL.5390.TOWR | 2024-06-04 | 2024-05-15 | 2025-05-21 | Past Due |  | 2025-05-15 | 2025-05-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129022165 | 035/297 | T2 DI PIT #1-COTTONWOOD 35/297 RPR ANCT | TABLEMTN | ETL.5390.TOWR | 2024-06-04 | 2024-05-15 | 2025-02-06 | On-Time |  | 2025-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46381904 | T2 DI PIT #1-COTTONWOOD 35/297 RPR ANCT | ICQ
LC | 129022188 | 013/103A | T2 DI SPI BURNEY TAP 13/103A RPR JUMS | TABLEMTN | ETL.5392.INSL.CERA | 2024-06-04 | 2024-05-15 | 2024-08-22 | On-Time |  | 2024-08-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46265342 | T2 DI SPI BURNEY TAP 13/103A RPR JUMS | ICS
LC | 129022192 | 016/003C | T2 DI TRINITY-MAPLE CRK 16/3C RPR ANCW | EUREKA | ETL.8170.POLE.NWOD | 2024-06-04 | 2024-05-15 | 2025-01-23 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46345900 | T2 DI TRINITY-MAPLE CRK 16/3C RPR ANCW | ICW
LC | 129022304 | 058/002 | T2 DI HUMBOLDT-TRINITY 58/02C RPL POLE | EUREKA | ETL.1820.POLE.WDPS | 2024-06-04 | 2024-05-15 | 2025-04-10 | On-Time |  | 2025-05-15 | 2025-05-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574649 | T2 DI HUMBOLDT-TRINITY 58/02L RPL POLE | 70Y
LC | 129022305 | 058/002 | T2 DI HUMBOLDT-TRINITY 58/02R RPL POLE | EUREKA | ETL.1820.POLE.WDPS | 2024-06-04 | 2024-05-15 | 2025-04-10 | On-Time |  | 2025-05-15 | 2025-05-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574649 | T2 DI HUMBOLDT-TRINITY 58/02L RPL POLE | 70Y
LC | 129022306 | 058/002 | T2 DI HUMBOLDT-TRINITY 58/02L RPL POLE | EUREKA | ETL.1820.POLE.WDPS | 2024-06-04 | 2024-05-15 | 2025-04-10 | On-Time |  | 2025-05-15 | 2025-05-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574649 | T2 DI HUMBOLDT-TRINITY 58/02L RPL POLE | 70Y
LC | 129026305 | 002/058 | T2 DI COLGATE-ALLGHNY 2/58 REFRAME | SACTO | ETL.6470.POLE.WOOD | 2024-06-05 | 2024-05-15 | 2025-05-06 | On-Time |  | 2025-05-15 | 2025-05-15 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35572541 | T2 DI COLGATE-ALLGHNY 2/58 REFRAME | 93E
LC | 129026764 | :005/049 | T2 PIT #3-PIT #1 :5/49 RPR STRT | TABLEMTN | ETL.5400.TOWR | 2024-06-05 | 2024-05-15 | 2024-05-15 | Past Due |  | 2025-05-15 | 2025-05-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46382027 | T2NT DI PIT #3-PIT #1 :5/49 RPR STRT | ICQ
LC | 129032138 | 002/055 | T2 DI COLGATE ALLEGHANY 2/55 RPR STRW | SACTO | ETL.6470.POLE.WOOD | 2024-06-06 | 2024-05-15 | 2025-05-05 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46404741 | T2 DI COLGATE ALLEGHANY 2/55 RPR STRW | ICW
LC | 129032150 | 002/055 | T2 DI COLGATE ALLEGHANY 2/55 RPR GYWW | SACTO | ETL.6470.POLE.WOOD | 2024-06-06 | 2024-05-15 | 2025-05-05 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46404742 | T2 DI COLGATE ALLEGHANY 2/55 RPR GYWW | ICW
LC | 129061625 | 061/004 | T2 DI HMBLDT TRNTY 61/004L RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-11 | 2024-05-15 | 2024-08-30 | On-Time |  | 2024-08-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46268093 | T2 DI HMBLDT TRNTY 61/004L RPR GYWW | ICW
LC | 129061629 | 061/004 | T2 DI HMBLDT TRNTY 61/004 INSP ANCW | EUREKA | ETL.1820.POLE.STPS | 2024-06-11 | 2024-05-15 | 2024-08-30 | On-Time |  | 2024-11-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46268302 | T2 DI HMBLDT TRNTY 61/004 INSP ANCW | ICW
LC | 129061660 | 061/004 | T2 DI HMBLDT TRNTY 61/004 RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-06-11 | 2024-05-15 | 2025-04-18 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46345908 | T2 DI HMBLDT TRNTY 61/004 RPR JUMW | ICW
LC | 129061690 | 011/094 | T2 DI PIT #3-PIT #1 11/94 RMV VEG | TABLEMTN | ETL.5400.TOWR | 2024-06-11 | 2024-05-15 | 2025-01-03 | On-Time |  | 2025-05-15 | 2025-05-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129061806 | 035/237B | T2 DI TRNTY-CTTNWOOD 35/237B RPR JMPW | TABLEMTN | ETL.4040.INSL.CERA | 2024-06-11 | 2024-05-15 | 2024-08-18 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46306822 | T2 DI TRNTY-CTTNWOOD 35/237B RPR JMPW | ICW
LC | 129061862 | 035/237A | T2 DI TRNTY-CTTNWOOD 35/237A RPR JMPW | TABLEMTN | ETL.4040.INSL.CERA | 2024-06-11 | 2024-05-15 | 2024-08-18 | On-Time |  | 2025-05-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46306823 | T2 DI TRNTY-CTTNWOOD 35/237A RPR JMPW | ICW
LC | 129067487 | 065/328 | T2 DI MALIN-ROUND MTN #2 65/328 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-06-12 | 2024-05-15 | 2025-02-09 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46338273 | T2 DI MALIN-ROUND MTN #2 65/328 RPR OPGW | ICS
LC | 129075934 | 061/004 | T2 DI HMBLDT TRNTY 61/004R RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-14 | 2024-05-15 | 2024-08-30 | On-Time |  | 2024-08-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46268094 | T2 DI HMBLDT TRNTY 61/004R RPR GYWW | ICW
LC | 129075936 | 061/004 | T2 DI HMBLDT TRNTY 61/004C RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-14 | 2024-05-15 | 2024-08-30 | On-Time |  | 2024-08-15 | 2025-05-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46268095 | T2 DI HMBLDT TRNTY 61/004C RPR GYWW | ICW
LC | 129076673 | 010/043 | T2 DI TESLA-METCALF 10/43 RPR SHLS | CONCORD | ETL.6110.TOWR | 2024-06-14 | 2024-05-15 | 2025-05-07 | On-Time |  | 2025-05-15 | 2025-05-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46286791 | T2 DI TESLA-METCALF 10/43 RPR SHLS | ICS
LC | 123653089 | 031/136 | T3NT DI FLTN-LKVLLE 031/136 RPL INSS | LAKEVLLE | ETL.4950.INSL.CERA | 2022-05-20 | 2022-05-16 | 2024-07-29 | On-Time |  | 2025-05-16 | 2025-05-16 | 532 | TR3 | YES | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH XMPT TR3 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 31636790 | T3 DI FLTN-LKVL-IGNC+ 031/136 RPL INSS | 93K
LC | 123654730 | 000/001 | T3NT DI MORGA-SAN LNDRO #1 0/1 BNT STEEL | CONCORD | ETL.2770.TOWR | 2022-05-20 | 2022-05-16 | 2023-04-18 | On-Time |  | 2025-05-16 | 2025-05-16 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45691704 | T3NT DI MORGA-SAN LNDRO #1 0/1 BNT STEEL | ICQ
LC | 123658930 | 000/001 | T3NT DI MORAGA-OAKLAND #3 0/1 RPR STRT | CONCORD | ETL.2740.TOWR | 2022-05-21 | 2022-05-16 | 2023-07-24 | On-Time |  | 2025-05-16 | 2025-05-16 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45691979 | T3 DI MORAGA-OAKLAND #3 0/1 RPR STRT | ICQ
LC | 123668222 | 049/215 | T2NT DI RND MT-TBL MT #2 49/215 RPR STRT | TABLEMTN | ETL.6070.TOWR | 2022-05-23 | 2022-05-16 | 2023-09-05 | On-Time |  | 2025-05-16 | 2025-05-16 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647712 | T2 DI RND MTN-TBL MTN #2 49/215 RPR STRT | ICQ
LC | 123729586 | 017/062 | T2 DI EXCHQR INDIAN FLT 17/62 RMV VEG | FRESNO | ETL.8650.TOWR | 2022-06-01 | 2022-05-16 | 2023-07-18 | On-Time |  | 2023-05-16 | 2025-05-16 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 123777806 | 017/061 | T2NT DI EXCHQR-INDIAN FLT 17/061 RMV VEG | FRESNO | ETL.8650.TOWR | 2022-06-07 | 2022-05-16 | 2023-07-18 | On-Time |  | 2025-05-16 | 2025-05-16 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128780678 | 005/002 | T2 VLLY SPRNGS-CLVRS CMNT 5/2 RPR POLE | VICTOR | ETL.8220.POLE.WOOD | 2024-05-16 | 2024-05-16 | 2025-03-07 | On-Time |  | 2025-05-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Structure-Wood | Repair | 46326999 | T2 VLLY SPRNGS-CLVRS CMNT 5/2 RPR POLE | ICW
LC | 128780924 | 000/002 | T2 HAAS-WOODCHUCK 0/2 RPR JUMW | FRESNO | ETL.8730.INSL.NCER | 2024-05-16 | 2024-05-16 | 2024-05-16 | Past Due |  | 2024-08-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW ACCL OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46268356 | T2 HAAS-WOODCHUCK 00/02 RPR JMPW | ICW
LC | 128781439 | 034/219 | T2 EI CRZ HRS CYN-SN BNT 34/219 TOUCH | MOSSLNDG | ETL.2152.TOWR | 2024-05-16 | 2024-05-16 | 2024-05-16 | Past Due |  | 2024-11-16 | 2025-05-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478227 | T2 EI CRZ HRS CYN-SN BNT 34/219 TOUCH | ICQ
LC | 128782090 | 001/005 | T2 MENDOCINO-UKIAH 01/005 TOUCH | WILLITS | ETL.2420.POLE.NWOD | 2024-05-16 | 2024-05-16 | 2025-06-13 | Past Due |  | 2024-11-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46507783 | T2 MENDOCINO-UKIAH 01/005 TOUCH | ICW
LC | 128783113 | 039/178 | T2 RND MTN-TBL MNT #1 39/178 RPL JMPS | TABLEMTN | ETL.6060.INSL | 2024-05-16 | 2024-05-16 | 2025-01-29 | On-Time |  | 2025-05-16 | 2025-05-16 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35609715 | T2 RND MTN-TBL MNT #1 39/178 RPL JMPS | 93K
LC | 128783230 | 004/032 | T2 COTTONWOOD-DELEVAN #1 4/32 COMPLETE | TABLEMTN | ETL.4550.INSL | 2024-05-16 | 2024-05-16 | 2025-04-02 | On-Time |  | 2025-05-16 | 2025-05-16 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570417 | T2 COTTONWOOD-DELEVAN #1+ 2/16 RPL INSS | 93K
LC | 128783830 | 007/008 | T2 LAYTONVILLE-WILLITS 7/8 INS DMPW | WILLITS | ETL.8360.INSL.NCER | 2024-05-16 | 2024-05-16 | 2024-05-16 | Past Due |  | 2025-05-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46446812 | T2 WV LAYTONVILLE-WILLITS 7/8 INS DMPW | ICW
LC | 128785123 | 048/209 | T2 EI CBN-LS AGS SW ST 48/209 RMV NEST | MOSSLNDG | ETL.4460.TOWR | 2024-05-16 | 2024-05-16 | 2025-02-05 | On-Time |  | 2025-05-16 | 2025-05-16 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46391169 | T2 EI CBN-LS AGS SW ST 48/209 RMV NEST | ICS
LC | 128785186 | 004/105 | T2 HAMILTON BRNCH-CHSTR 04/105 RPL STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-05-16 | 2024-05-16 | 2024-07-29 | On-Time |  | 2025-05-16 | 2025-05-16 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35553887 | T2 HAMILTON BRNCH-CHSTR 04/105 RPL STRW | 70Y
LC | 128785188 | 016/094 | T2 EI MOSS LNDNG-DL MNT#1 16/94 RPL INSS | MOSSLNDG | ETL.2830.INSL | 2024-05-16 | 2024-05-16 | 2025-04-28 | On-Time |  | 2025-05-16 | 2025-05-16 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35624124 | T2 EI MOSS LNDNG-DL MNT#1 16/94 RPL INSS | 93K
LC | 128785218 | 235(SUB ASSET) | T2 PIT #3-PIT #1 000/002 RPL SWTC | TABLEMTN | ETL.5400.SWIT | 2024-05-16 | 2024-05-16 | 2024-05-16 | Past Due |  | 2025-05-16 | 2025-05-16 | 435T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH RTNR FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Switch-Steel | Replace | 35596706 | T2 EI PIT #3-PIT #1 000/002 RPL SWTC | 93S
LC | 128785251 | 019/082 | T2 DI MRRO BY-SLR SS #1 19/82 RPL INSS | PISMOBCH | ETL.5300.INSL | 2024-05-16 | 2024-05-16 | 2025-04-08 | On-Time |  | 2025-05-16 | 2025-05-16 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35583345 | T0 EI MORRO BAY-SOLAR SS#1 REP INS 6 LST | 93K
LC | 128785258 | 019/083 | T2 DI MRRO BY-SLR SS #2 19/83 RPL INSS | PISMOBCH | ETL.5310.INSL | 2024-05-16 | 2024-05-16 | 2024-05-16 | Past Due |  | 2025-05-16 | 2025-05-16 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577375 | T0 EI MORRO BAY-SOLAR SS#2 42/180 RPLC I | 93K
LC | 128785465 | 026/425 | T2 EI KESWICK-TRINITY 26/425 RPR GYWW | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-16 | 2024-05-16 | 2025-04-17 | On-Time |  | 2025-05-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311215 | T2 EI KESWICK-TRINITY 26/425 RPR GYWW | ICW
LC | 128785466 | 026/443 | T2 EI KESWICK-TRINITY 26/443 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-16 | 2024-05-16 | 2024-09-14 | On-Time |  | 2024-08-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262788 | T2 EI KESWICK-TRINITY 26/443 RPR JUMW | ICW
LC | 128785534 | 008/161 | T2 EI CARIBOU-WESTWOOD 008/161 RPR STRW | TABLEMTN | ETL.6300.POLE.WOOD | 2024-05-16 | 2024-05-16 | 2025-01-21 | On-Time |  | 2025-05-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337329 | T2 EI CARIBOU-WESTWOOD 008/161 RPR STRW | ICW
LC | 128785575 | 008/161 | T2 EI CARIBOU-WESTWOOD 008/161 RPL ANCW | TABLEMTN | ETL.6300.POLE.WOOD | 2024-05-16 | 2024-05-16 | 2025-03-11 | On-Time |  | 2025-05-16 | 2025-05-16 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572148 | T2 EI CARIBOU-WESTWOOD 008/161 RPL ANCW | 93E
LC | 128787951 | 006/002 | T2 EI CLEAR LAKE-HOPLAND 6/002 RPR GYWW | WILLITS | ETL.6390.POLE.WOOD | 2024-05-17 | 2024-05-16 | 2025-05-15 | On-Time |  | 2025-05-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46255398 | T2 EI CLEAR LAKE-HOPLAND 6/002 RPR GYWW | ICW
LC | 128787960 | 006/000 | T2 CLEAR LAKE-HOPLAND 6/00 RPL STRW | WILLITS | ETL.6390.POLE.WOOD | 2024-05-17 | 2024-05-16 | 2024-05-16 | Past Due |  | 2025-05-16 | 2025-05-16 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35642102 | T2 EI CLEAR LAKE-HOPLAND 6/00 RPL STRW | 70Y
LC | 128799935 | :003/026 | T2 DI PIT#3-PIT#1 :3/26 RPR JUMS | TABLEMTN | ETL.5400.INSL.NCER | 2024-05-17 | 2024-05-16 | 2024-08-23 | On-Time |  | 2024-08-16 | 2025-05-16 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46251388 | T2 DI PIT#3-PIT#1 :3/26 RPR JUMS | ICS
LC | 128800234 | 026/126 | T2 DI MNTA VSTA-CYTE SW 26/126 RPR SHLD | MOSSLNDG | ETL.5090.TOWR | 2024-05-17 | 2024-05-16 | 2025-03-28 | On-Time |  | 2025-05-16 | 2025-05-16 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46391294 | T2 DI MNTA VSTA-CYTE SW 26/126 RPR SHLD | ICS
LC | 128800333 | 015/187 | T2 DI KESWICK-TRINITY 15/187 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-17 | 2024-05-16 | 2025-04-19 | On-Time |  | 2025-05-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311216 | T2 DI KESWICK-TRINITY 15/187 RPR JUMW | ICW
LC | 128800631 | 058/003A | T2 DI HUMBOLDT-TRINITY 58/3A INSP STRW | EUREKA | ETL.1820.POLE.WOOD | 2024-05-17 | 2024-05-16 | 2024-08-26 | On-Time |  | 2024-11-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46254618 | T2 DI HUMBOLDT-TRINITY 58/3A INSP STRW | ICW
LC | 128800697 | 015/193 | T2 DI KESWICK-TRIN 15/193 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-17 | 2024-05-16 | 2024-09-15 | On-Time |  | 2024-08-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46251650 | T2 DI KESWICK-TRIN 15/193 RPR JUMW | ICW
LC | 128800721 | 015/186 | T2 DI KESWICK TRINITY 15/186 RPR GYWW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-17 | 2024-05-16 | 2024-08-21 | On-Time |  | 2024-11-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46250711 | T2 DI KESWICK TRINITY 15/186 RPR GYWW | ICW
LC | 128800767 | 058/003B | T2 DI HUMBOLDT-TRINITY 58/3B RPR JMPW | EUREKA | ETL.1820.INSL.CERA | 2024-05-17 | 2024-05-16 | 2024-08-26 | On-Time |  | 2024-08-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46254619 | T2 DI HUMBOLDT-TRINITY 58/3B RPR JMPW | ICW
LC | 128800870 | 058/003B | T2 DI HUMBOLDT-TRINITY 58/3B INSP STRW | EUREKA | ETL.1820.POLE.WOOD | 2024-05-17 | 2024-05-16 | 2024-08-26 | On-Time |  | 2024-11-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46254660 | T2 DI HUMBOLDT-TRINITY 58/3B INSP STRW | ICW
LC | 129022074 | 017/135 | T2 DI PIT #1-COTTONWOOD 17/135 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-06-04 | 2024-05-16 | 2025-04-22 | On-Time |  | 2025-05-16 | 2025-05-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381901 | T2 DI PIT #1-COTTONWOOD 17/135 RPR FOND | ICQ
LC | 129022116 | 068/343 | T2 DI MLN RND MTN#2 68/343 RPR SHLS | TABLEMTN | ETL.6020.TOWR | 2024-06-04 | 2024-05-16 | 2025-02-24 | On-Time |  | 2025-05-16 | 2025-05-16 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338272 | T2 DI MLN RND MTN#2 68/343 RPR SHLS | ICS
LC | 129022148 | :004/039 | T2 DI PIT #3-PIT #1 :004/039 RPR FOND | TABLEMTN | ETL.5400.TOWR | 2024-06-04 | 2024-05-16 | 2025-04-24 | On-Time |  | 2025-05-16 | 2025-05-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46382019 | T2 DI PIT #3-PIT #1 :004/039 RPR FOND | ICQ
LC | 129022183 | 016/133 | T2 DI PIT #1 COTTONWOOD 16/133 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-06-04 | 2024-05-16 | 2025-04-22 | On-Time |  | 2025-05-16 | 2025-05-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381906 | T2 DI PIT #1 COTTONWOOD 16/133 RPR FOND | ICQ
LC | 129022312 | :001/015 | T2 DI PIT #3 PIT #1 :01/15 RPL HRDT | TABLEMTN | ETL.5400.TOWR | 2024-06-04 | 2024-05-16 | 2025-04-11 | On-Time |  | 2025-05-16 | 2025-05-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46382020 | T2 DI PIT #3 PIT #1 :01/15 RPL HRDT | ICQ
LC | 129022313 | :001/015 | T2NT DI PIT #3 PIT #1 :1/15 RPR STRT | TABLEMTN | ETL.5400.TOWR | 2024-06-04 | 2024-05-16 | 2025-04-11 | On-Time |  | 2027-05-16 | 2025-05-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46382021 | T2NT DI PIT #3 PIT #1 :1/15 RPR STRT | ICQ
LC | 129025889 | 003/089 | T2 DI COLGATE-ALLEGHANY 3/89 RPL INSW | SACTO | ETL.6470.INSL.CERA | 2024-06-05 | 2024-05-16 | 2025-05-12 | On-Time |  | 2025-05-16 | 2025-05-16 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35643952 | COLGATE-ALLEGHANY 3/89 RPL INS-POST EST | 93I
LC | 129026420 | 009/036 | T2 PITTSBURG-EASTSHORE 9/36 RPL INSS | CONCORD | ETL.5462.INSL | 2024-06-05 | 2024-05-16 | 2024-05-16 | Past Due |  | 2025-05-16 | 2025-05-16 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35626540 | T2 DI PITTSBURG-EASTSHORE 9/36 RPL INSS | 93K
LC | 129026672 | 012/003C | T2 DI TRINITY-MPL CRK 12/3C RPR JUMW | EUREKA | ETL.8170.INSL.NCER | 2024-06-05 | 2024-05-16 | 2025-03-21 | On-Time |  | 2024-08-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46264482 | T2 DI TRINITY-MPL CRK 12/3C RPR JUMW | ICW
LC | 129026700 | :005/044 | T2 PIT #3-PIT #1 :5/44 RPR STRT | TABLEMTN | ETL.5400.TOWR | 2024-06-05 | 2024-05-16 | 2024-05-16 | Past Due |  | 2025-05-16 | 2025-05-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46382025 | T2NT DI PIT #3-PIT #1 :5/44 RPR STRT | ICQ
LC | 129026774 | ;000/007 | T2 DI SNTH LN-HLF MN BAY ;0/7L INSP STRW | METCALF | ETL.7212.POLE.WDPS | 2024-06-05 | 2024-05-16 | 2024-07-17 | On-Time |  | 2025-05-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46282858 | T2 DI SNTH LN-HLF MN BAY ;0/7L INSP STRW | ICW
LC | 129026816 | 009/037 | T2 DI PTTSBURG-EASTSHORE 9/37 RPL INSS | CONCORD | ETL.5462.INSL | 2024-06-05 | 2024-05-16 | 2024-05-16 | Past Due |  | 2025-05-16 | 2025-05-16 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35626540 | T2 DI PITTSBURG-EASTSHORE 9/36 RPL INSS | 93K
LC | 129031816 | 004/011 | T2 DI SONOMA-PUEBLO 4/11 RPL STRW | LAKEVLLE | ETL.3810.POLE.WOOD | 2024-06-06 | 2024-05-16 | 2025-04-29 | On-Time |  | 2025-05-16 | 2025-05-16 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572887 | T2 DI SONOMA-PUEBLO 4/11 RPL STRW | 70Y
LC | 129031836 | 013/086 | T2 DI JFFRSN-MRTN 13/86 CANCEL | METCALF | ETL.5710.INSL.NCER | 2024-06-06 | 2024-05-16 | 2024-05-16 | Past Due |  | 2025-05-16 | 2025-05-16 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574092 | T2 DI JFFRSN-MRTN 13/86 RPL INSS | 93K
LC | 129031838 | 013/086 | T2 DI MILLBRAE-SNTH LN 13/86 RPL INSS | METCALF | ETL.7570.INSL.NCER | 2024-06-06 | 2024-05-16 | 2025-04-25 | On-Time |  | 2025-05-16 | 2025-05-16 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574091 | T2 DI MILLBRAE-SNTH LN 13/86 RPL INSS | 93K
LC | 129031911 | 015/185 | T2 DI KSWCK-TRNTY 15/185 RPR GYWW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-06-06 | 2024-05-16 | 2025-04-22 | On-Time |  | 2025-05-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311218 | T2 DI KSWCK-TRNTY 15/185 RPR GYWW | ICW
LC | 129032113 | A001/035 | T2 DI VALLEY SPRINGS #1 A1/35 RPL STRW | VICTOR | ETL.8210.POLE.WOOD | 2024-06-06 | 2024-05-16 | 2025-05-02 | On-Time |  | 2025-05-16 | 2025-05-16 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Rotten | Structure-Wood | Replace | 35573569 | T2 DI VALLEY SPRINGS #1 A1/35 RPL STRW | 70Y
LC | 129032199 | 086/000D | T2 DI HMBLDT-BRDGVL 86/0D RPR JUMW | EUREKA | ETL.1810.INSL.NCER | 2024-06-06 | 2024-05-16 | 2024-05-16 | Past Due |  | 2025-05-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Wood | Repair | 46345912 | T2 DI HMBLDT-BRDGVL 86/0D RPR JUMW | ICW
LC | 129035108 | 012/232 | T2 DI VLLY SPNGS #1 12/232 RPL STRW | VICTOR | ETL.8210.POLE.WOOD | 2024-06-07 | 2024-05-16 | 2025-04-24 | On-Time |  | 2025-05-16 | 2025-05-16 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573567 | T2 DI VLLY SPNGS #1 12/232 RPL STRW | 70Y
LC | 129036567 | A001/023 | T2 DI VALLEY SPRINGS #1 A1/23 CANCEL | VICTOR | ETL.8210.INSL.CERA | 2024-06-07 | 2024-05-16 | 2024-05-16 | Past Due |  | 2025-05-16 | 2025-05-16 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573568 | T2 DI VLLY SPRNGS #1 A1/23 RPL INSW | 93I
LC | 129067440 | 008/166 | T2 DI VALLEY SPRINGS #1 08/166 RPR INSW | VICTOR | ETL.8210.INSL.NCER | 2024-06-12 | 2024-05-16 | 2025-04-21 | On-Time |  | 2025-05-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46327605 | T2 DI VALLEY SPRINGS #1 08/166 RPR INSW | ICW
LC | 129067720 | 086/000EA | T2 HUMBOLDT-BRIDGEVILLE 86/0EA RPR ADSS | EUREKA | ETL.1810.POLE.NWOD | 2024-06-12 | 2024-05-16 | 2024-05-16 | Past Due |  | 2024-08-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46537761 | T2 HUMBOLDT-BRIDGEVILLE 86/0EA RPR ADSS | ICW
LC | 129077229 | 011/004 | T2 DI FULTON-HOPLAND 011/004 RPR GYWW | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-06-14 | 2024-05-16 | 2025-01-20 | On-Time |  | 2025-05-16 | 2025-05-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305946 | T2 DI FULTON-HOPLAND 011/004 RPR GYWW | ICW
LC | 129077272 | 014/094 | T2 DI MILBRAE-SNEATH LANE 14/94 RPR JUMS | METCALF | ETL.7570.INSL.CERA | 2024-06-14 | 2024-05-16 | 2025-03-25 | On-Time |  | 2025-05-16 | 2025-05-16 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46286831 | T2 DI MILBRAE-SNEATH LANE 14/94 RPR JUMS | ICS
LC | 129077950 | 068/344 | T2 DI MLN RDN MTN#2 68/344 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-06-14 | 2024-05-16 | 2024-08-27 | On-Time |  | 2025-05-16 | 2025-05-16 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46299541 | T2 DI MLN RDN MTN#2 68/344 RPR SHLD | ICS
LC | 129078365 | 027/118 | T2 DI FINK SWSTA WSTLY 27/118 RPR SHLS | VICTOR | ETL.1384.TOWR | 2024-06-14 | 2024-05-16 | 2025-01-27 | On-Time |  | 2025-05-16 | 2025-05-16 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46325962 | T2 DI FINK SWSTA WSTLY 27/118 RPR SHLS | ICS
LC | 123815830 | 012/000 | T2NT DI MNDCNO-HRTLY 12/000 RPR GYWW | WILLITS | ETL.7510.POLE.WDPS | 2022-06-10 | 2022-05-17 | 2023-08-21 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45712014 | T2NT DI MNDCNO-HRTLY 12/000 RPR GYWW | ICW
LC | 123815831 | 012/000 | T2NT DI MNDCNO-HRTLY 12/000 RMV VEG | WILLITS | ETL.7510.POLE.WDPS | 2022-06-10 | 2022-05-17 | 2023-05-09 | On-Time |  | 2025-05-17 | 2025-05-17 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128788156 | 046/009 | T2 EI TRINITY-MAPLE CREEK 46/09 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-05-17 | 2024-05-17 | 2025-05-08 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345918 | T2 EI TRINITY-MAPLE CREEK 46/09 RPR GYWW | ICW
LC | 128789270 | 021/009-GUY | T2 EI FORT BRAGG-ELK 21/09-GUY RMV VEG | WILLITS | ETL.2060.POLE.WOOD | 2024-05-17 | 2024-05-17 | 2025-02-07 | On-Time |  | 2025-05-17 | 2025-05-17 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAR | Overgrown | Vegetation | Trim
LC | 128791352 | 011/187 | T2 WV SURF TAP 11/187 RPR INSS | PISMOBCH | ETL.1381.INSL.NCER | 2024-05-17 | 2024-05-17 | 2025-05-13 | On-Time |  | 2025-05-17 | 2025-05-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Insulator-Steel | Repair | 46460086 | T2 WV SURF TAP 11/187 RPR INSS | ICS
LC | 128792593 | 053/1032 | T2 EI HT CRK #1-WSTWD 53/1032 RPR POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-17 | 2024-05-17 | 2024-07-24 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46286842 | T2 EI HT CRK #1-WSTWD 53/1032 RPR POLE | ICW
LC | 128799280 | 016/075 | T2 LOS ESTEROS-METCALF 16/075 TOUCH | METCALF | ETL.5353.TOWR | 2024-05-17 | 2024-05-17 | 2024-05-17 | Past Due |  | 2024-11-17 | 2025-05-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485709 | T2 LOS ESTEROS-METCALF 16/075 TOUCH | ICQ
LC | 128799384 | 012/202 | T2 EI TEJON-LEBEC 012/202 RPR INSW | MIDWAY | ETL.9250.INSL.NCER | 2024-05-17 | 2024-05-17 | 2025-02-02 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46302559 | T2 EI TEJON-LEBEC 012/202 RPR INSW | ICW
LC | 128799657 | 009/184 | T2 CARIBU-WESTWOOD 09/184 RPR STRW | TABLEMTN | ETL.6300.POLE.WOOD | 2024-05-17 | 2024-05-17 | 2024-08-01 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46305289 | T2 CARIBU-WESTWOOD 09/184 RPR STRW | ICW
LC | 128800559 | 028/414 | T2 DI CLAY-MARTEL 28/414 GO95 | VICTOR | ETL.8250.POLE.WOOD | 2024-05-17 | 2024-05-17 | 2025-06-06 | Past Due |  | 2025-05-17 | 2025-05-17 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35573185 | T2 DI CLAY-MARTEL 28/414 GO95 | 93G
LC | 128800661 | 067/001 | T2 DI HMBLDT-TRINITY 67/01 RPR JUMW | EUREKA | ETL.1820.INSL.CERA | 2024-05-17 | 2024-05-17 | 2025-04-18 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46345941 | T2 DI HMBLDT-TRINITY 67/01 RPR JUMW | ICW
LC | 128800662 | 067/001 | T2 DI HUMBLDT-TRINITY 67/01L RPL HRDD | EUREKA | ETL.1820.POLE.WDPS | 2024-05-17 | 2024-05-17 | 2025-04-18 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345942 | T2 DI HUMBLDT-TRINITY 67/01L RPL HRDD | ICW
LC | 128800794 | 006/169 | T2 EI DRUM-SPAULDING 006/169 RPL INSW | SACTO | ETL.6770.INSL.NCER | 2024-05-17 | 2024-05-17 | 2025-05-04 | On-Time |  | 2025-05-17 | 2025-05-17 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573458 | T2 EI DRUM-SPAULDING 006/169 RPL INSW | 93I
LC | 128800999 | 025/420 | T2 EI KESWICK-TRINITY 25/420 RPL INSW | TABLEMTN | ETL.7270.INSL.CERA | 2024-05-17 | 2024-05-17 | 2025-04-17 | On-Time |  | 2025-05-17 | 2025-05-17 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573709 | T2 EI KESWICK-TRINITY 25/420 RPL INSW | 93I
LC | 128801022 | 026/426 | T2 EI KESWICK-TRINITY 26/426 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-17 | 2024-05-17 | 2025-04-17 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311211 | T2 EI KESWICK-TRINITY 26/426 RPR JUMW | ICW
LC | 128801088 | 000/011 | T2 EI CARIBOU-WESTWOOD 000/011 GO95 | TABLEMTN | ETL.6300.POLE.WOOD | 2024-05-17 | 2024-05-17 | 2025-03-09 | On-Time |  | 2025-05-17 | 2025-05-17 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35572137 | T2 EI CARIBOU-WESTWOOD 000/011 GO95 | 93G
LC | 128801114 | 000/009 | T2 EI CARIBOU-WESTWOOD 000/009 RPR GYWW | TABLEMTN | ETL.6300.POLE.WOOD | 2024-05-17 | 2024-05-17 | 2025-01-21 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337330 | T2 EI CARIBOU-WESTWOOD 000/009 RPR GYWW | ICW
LC | 128801147 | 004/005B | T2 EI CLEAR LAKE-HOPLAND 004/005B COTTER | WILLITS | ETL.6390.INSL.NCER | 2024-05-17 | 2024-05-17 | 2025-05-14 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310264 | T2 EI CLEAR LAKE-HOPLAND 004/005B COTTER | ICW
LC | 128801149 | 004/005A | T2 EI CLEAR LAKE-HOPLAND 4/005A RPR STRW | WILLITS | ETL.6390.POLE.WOOD | 2024-05-17 | 2024-05-17 | 2025-05-14 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310263 | T2 EI CLEAR LAKE-HOPLAND 4/005A RPR STRW | ICW
LC | 128801329 | 012/145B | T2 EI DRUM-SUMMIT #1 12/145B RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-05-18 | 2024-05-17 | 2024-06-23 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46269352 | T2 EI DRUM-SUMMIT #1 12/145B RPR GYWW | ICW
LC | 128801843 | 012/145C | T2 EI DRUM-SUMMIT #1 12/145C RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-05-18 | 2024-05-17 | 2024-06-23 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46273103 | T2 EI DRUM-SUMMIT #1 12/145C RPR GYWW | ICW
LC | 129022159 | 006/027 | T2 DI PITTSBURG-TESLA #1 6/27 RPR STRT | CONCORD | ETL.5510.TOWR | 2024-06-04 | 2024-05-17 | 2025-05-13 | On-Time |  | 2025-05-17 | 2025-05-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46289320 | T2 DI PITTSBURG-TESLA #1 6/27 RPR STRT | ICQ
LC | 129026512 | 063/004 | T2 DI HUMBOLDT-TRINITY 63/4 RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-05 | 2024-05-17 | 2025-04-19 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345919 | T2 DI HUMBOLDT-TRINITY 63/4 RPR GYWW | ICW
LC | 129026548 | 003/065 | T2 DI VALLEY SPRINGS #1 3/65 RPR INSW | VICTOR | ETL.8210.INSL.CERA | 2024-06-05 | 2024-05-17 | 2025-04-16 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46327509 | T2 DI VALLEY SPRINGS #1 3/065 RPR INSW | ICW
LC | 129026850 | 017/254 | T2 CLAY-MARTEL 17/254 TOUCH | VICTOR | ETL.8250.POLE.NWOD | 2024-06-05 | 2024-05-17 | 2024-05-17 | Past Due |  | 2024-11-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46477461 | T2 DI CLAY-MARTEL 17/254 TOUCH | ICW
LC | 129032137 | A000/016 | T2NT DI VALLEY SPGS#1 A0/16 RPL DAMW | VICTOR | ETL.8210.INSL.NCER | 2024-06-06 | 2024-05-17 | 2025-05-03 | On-Time |  | 2027-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46327510 | T2NT DI VALLEY SPGS#1 A0/16 RPL DAMW | ICW
LC | 129032294 | 068/000 | T2 DI HUMBOLDT-TRINITY 68/0R RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-06 | 2024-05-17 | 2025-04-11 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345943 | T2 DI HUMBOLDT-TRINITY 68/0R RPR GYWW | ICW
LC | 129032295 | 068/000 | T2 DI HUMBOLDT-TRINITY 68/0L RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-06 | 2024-05-17 | 2025-04-11 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345944 | T2 DI HUMBOLDT-TRINITY 68/0L RPR GYWW | ICW
LC | 129032689 | 028/428 | T2 DI CLAY-MARTEL 28/428 RPL STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-06-06 | 2024-05-17 | 2025-05-12 | On-Time |  | 2025-05-17 | 2025-05-17 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573187 | +T2 DI CLAY-MARTEL 28/428 RPL STRW | 70Y
LC | 129035498 | 004/026 | T2 DI PTSBURG-CLAYTON #4 4/26 RPL INSS | CONCORD | ETL.3291.INSL.NCER | 2024-06-07 | 2024-05-17 | 2025-05-16 | On-Time |  | 2025-05-17 | 2025-05-17 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575006 | T2 DI PTSBURG-CLAYTON #4 4/26 RPL INSS | 93K
LC | 129035499 | 009/188 | T2 DI VALLEY SPGS#1 9/188 RPR INSW | VICTOR | ETL.8210.INSL.NCER | 2024-06-07 | 2024-05-17 | 2025-04-23 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46327511 | T2 DI VALLEY SPGS#1 9/188 RPR INSW | ICW
LC | 129036355 | 018/262 | T2 DI CLAY-MARTEL 18/262 RPL STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-06-07 | 2024-05-17 | 2025-04-12 | On-Time |  | 2025-05-17 | 2025-05-17 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573180 | +T2 DI CLAY-MARTEL 18/262 RPL STRW | 70Y
LC | 129036513 | 021/304 | T2 DI CLAY-MARTEL 21/304 RPR GYWW | VICTOR | ETL.8250.POLE.WOOD | 2024-06-07 | 2024-05-17 | 2025-04-30 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327028 | +T2 DI CLAY-MARTEL 21/304 RPR GYWW | ICW
LC | 129036548 | 003/010 | T2 DI SONOMA-PUEBLO 03/10 RPR GYWW | LAKEVLLE | ETL.3810.POLE.NWOD | 2024-06-07 | 2024-05-17 | 2025-04-28 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46403754 | T2 DI SONOMA-PUEBLO 03/10 RPR GYWW | ICW
LC | 129036683 | 008/038 | T2 DI PTTSBRG-TSLA #1 8/38 RPL HRDT | CONCORD | ETL.5510.TOWR | 2024-06-07 | 2024-05-17 | 2025-02-12 | On-Time |  | 2025-05-17 | 2025-05-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289321 | T2 DI PTTSBRG-TSLA #1 8/38 RPL HRDT | ICQ
LC | 129036754 | 020/288 | T2 DI CLAY-MARTEL 20/288 RPL STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-06-07 | 2024-05-17 | 2025-04-30 | On-Time |  | 2025-05-17 | 2025-05-17 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573182 | +T2 DI CLAY-MARTEL 20/288 RPL STRW | 70Y
LC | 129055014 | 019/275 | T2 DI CLAY-MARTEL 19/275 RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-06-10 | 2024-05-17 | 2025-04-30 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46327029 | +T2 DI CLAY-MARTEL 19/275 RPR STRW | ICW
LC | 129056195 | 063/004 | T2 DI HUMBOLDT-TRINITY 63/4R RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-11 | 2024-05-17 | 2025-04-19 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345940 | T2 DI HUMBOLDT-TRINITY 63/4R RPR GYWW | ICW
LC | 129062896 | 021/300 | T2 DI CLAY MARTEL 21/300 RPR INSW | VICTOR | ETL.8250.INSL.NCER | 2024-06-12 | 2024-05-17 | 2024-10-17 | On-Time |  | 2024-11-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46266195 | T2 DI CLAY MARTEL 21/300 RPR INSW | ICW
LC | 129076960 | 024/347 | T2 CLAY-MARTEL 24/347 RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-06-14 | 2024-05-17 | 2024-05-17 | Past Due |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46327031 | +T2 DI CLAY-MARTEL 24/347 RPR STRW | ICW
LC | 129077005 | 028/416 | T2 DI CLAY-MARTEL 28/416 RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-06-14 | 2024-05-17 | 2025-04-30 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46327032 | +T2 DI CLAY-MARTEL 28/416 RPR STRW | ICW
LC | 129077068 | 004/025 | T2 DI PITTSBURG-CLY#4 4/25 RPL INSS | CONCORD | ETL.3291.INSL.NCER | 2024-06-14 | 2024-05-17 | 2025-05-14 | On-Time |  | 2025-05-17 | 2025-05-17 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35618645 | T2 DI PITTSBURG-CLY#4 4/25 RPL INSS | 93K
LC | 129077606 | 019/270 | T2 DI CLAY-MARTEL 19/270 RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-06-14 | 2024-05-17 | 2025-04-30 | On-Time |  | 2025-05-17 | 2025-05-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46327033 | +T2 DI CLAY-MARTEL 19/270 RPR STRW | ICW
LC | 129077765 | 069/000C | T2 DI HUMBOLDT-TRINITY 69/0C RPL STRW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-14 | 2024-05-17 | 2025-04-10 | On-Time |  | 2025-05-17 | 2025-05-17 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586917 | T2 DI HUMBOLDT-TRINITY 69/0C RPL STRW | 70Y
LC | 129078164 | 004/086 | T2 DI VALLEY SPRINGS #1 4/86 CANCEL | VICTOR | ETL.8210.INSL.CERA | 2024-06-14 | 2024-05-17 | 2024-05-17 | Past Due |  | 2025-05-17 | 2025-05-17 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace
LC | 123628736 | 003/047 | T2NT EI DIVIDE-CABRILLO #1 3/47 RMV VEG | PISMOBCH | ETL.1380.POLE.WOOD | 2022-05-18 | 2022-05-18 | 2023-08-29 | On-Time |  | 2025-05-18 | 2025-05-18 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO FRAB | Overgrown | Vegetation | Remove
LC | 123630414 | 007/119 | T2NT EI CORDELIA #1 TAP 7/119 RPR GYWW | SACTO | ETL.8182.POLE.WOOD | 2022-05-18 | 2022-05-18 | 2023-02-02 | On-Time |  | 2023-05-18 | 2025-05-18 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45674819 | T2NT EI CORDELIA #1 TAP 7/119 RPR GYWW | ICW
LC | 123631826 | 046/262 | T3NT EI TEMBLR-SN LS OBSP 46/262 UNBURY | PISMOBCH | ETL.3960.TOWR | 2022-05-18 | 2022-05-18 | 2023-07-21 | On-Time |  | 2025-05-18 | 2025-05-18 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45655387 | T3 EI TEMBLR-SN LS OBISPO 046/262 UNBURY | ICQ
LC | 123639679 | 043/178 | T2NT DI DBL MDWY #2 43/178 RPR GYWS | PISMOBCH | ETL.5970.TOWR | 2022-05-19 | 2022-05-18 | 2023-07-12 | On-Time |  | 2025-05-18 | 2025-05-18 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45655389 | T2 DI DBL MDWY #2 43/178 RPR GYWS | ICS
LC | 123639975 | 000/001A | T3NT DI DBL PP STNBY SPL 0/1A RPR FOND | PISMOBCH | ETL.4610.POLE.NWOD | 2022-05-19 | 2022-05-18 | 2023-07-25 | On-Time |  | 2025-05-18 | 2025-05-18 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45655390 | T3 DI DBL PP STNBY SPL 0/1A RPR FOND | ICQ
LC | 123646869 | 044/179 | T2NT DI DIABLO-MIDWAY #2 44/179 RPR GYWS | PISMOBCH | ETL.5970.TOWR | 2022-05-20 | 2022-05-18 | 2023-07-10 | On-Time |  | 2025-05-18 | 2025-05-18 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45655561 | T2 DI DIABLO-MIDWAY #2 44/179 RPR GYWS | ICS
LC | 123674794 | 000/004 | T3NT DI ROLLINS TAP 0/4 RPL HRDW | SACTO | ETL.6762.POLE.WOOD | 2022-05-23 | 2022-05-18 | 2023-05-23 | On-Time |  | 2025-05-18 | 2025-05-18 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 45685530 | T3NT DI ROLLINS TAP 0/4 RPL HRDW | ICW
LC | 123751153 | 010/042 | T2NT DI MNTA VTA-JEFFS#1 10/42 RPR FOND | METCALF | ETL.5220.TOWR | 2022-06-03 | 2022-05-18 | 2023-07-25 | On-Time |  | 2025-05-18 | 2025-05-18 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45706612 | T2NT DI MNTA VTA-JEFFS#1 10/42 RPR FOND | ICQ
LC | 128802077 | 002/017 | T2 MTA VISTA-CYTE SS 02/017 CANCEL | MOSSLNDG | ETL.5090.INSL.CERA | 2024-05-18 | 2024-05-18 | 2024-05-18 | Past Due |  | 2025-05-18 | 2025-05-18 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35597475 | T2 EI MTA VISTA-CYTE SS 02/016 RPL INSS | 93K
LC | 128802096 | 002/016 | T2 EI MTA VISTA-CYTE SS 02/016 RMV NEST | MOSSLNDG | ETL.5090.TOWR | 2024-05-18 | 2024-05-18 | 2025-02-05 | On-Time |  | 2025-05-18 | 2025-05-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46391170 | T2 EI MTA VISTA-CYTE SS 02/016 RMV NEST | ICS
LC | 128802153 | 002/016 | T2 MTA VISTA-CYTE SS 02/016 CANCEL | MOSSLNDG | ETL.5090.INSL | 2024-05-18 | 2024-05-18 | 2024-05-18 | Past Due |  | 2025-05-18 | 2025-05-18 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35597475 | T2 EI MTA VISTA-CYTE SS 02/016 RPL INSS | 93K
LC | 128802327 | 012/141 | T2 EI DRUM-SUMMIT#2_012/141 RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-05-18 | 2024-05-18 | 2025-04-24 | On-Time |  | 2025-05-18 | 2025-05-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458321 | T2 EI DRUM-SUMMIT#2_012/141 RPR GYWW | ICW
LC | 128802559 | 003/019 | T2 MTA VSTA-CYTE SS 03/019 RPL INSS | MOSSLNDG | ETL.5090.INSL | 2024-05-18 | 2024-05-18 | 2024-05-18 | Past Due |  | 2025-05-18 | 2025-05-18 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35597475 | T2 EI MTA VISTA-CYTE SS 02/016 RPL INSS | 93K
LC | 128802747 | C025/099 | T2 EI MSS LANDING-COBURN C25/99 RMV NEST | MOSSLNDG | ETL.5330.TOWR | 2024-05-18 | 2024-05-18 | 2025-02-05 | On-Time |  | 2025-05-18 | 2025-05-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46391171 | T2 EI MSS LANDING-COBURN C25/99 RMV NEST | ICS
LC | 128803114 | 013/007 | T2 EI TRINITY-MAPLE CREEK 13/07 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-05-18 | 2024-05-18 | 2025-01-21 | On-Time |  | 2025-05-18 | 2025-05-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345945 | T2 EI TRINITY-MAPLE CREEK 13/07 RPR GYWW | ICW
LC | 128803126 | 013/071 | T2 EI RND MTN-TBL MTN#2 13/71 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2024-05-18 | 2024-05-18 | 2024-11-14 | On-Time |  | 2025-05-18 | 2025-05-18 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128803127 | 013/071 | T2 EI RND MTN-TBL MTN#1 13/71 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-18 | 2024-05-18 | 2024-11-14 | On-Time |  | 2025-05-18 | 2025-05-18 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128803162 | 013/070 | T2 EI RND MTN-TBL MTN#2 13/70 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2024-05-18 | 2024-05-18 | 2024-11-14 | On-Time |  | 2025-05-18 | 2025-05-18 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128803164 | 013/071 | T2 EI RND MTN-TBL MTN#2 13/71 RPR ANCT | TABLEMTN | ETL.6070.TOWR | 2024-05-18 | 2024-05-18 | 2025-04-16 | On-Time |  | 2025-05-18 | 2025-05-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46381033 | T2 EI RND MTN-TBL MTN#2 13/71 RPR ANCT | ICQ
LC | 128803180 | C024/096 | T2 EI MSS LANDING-COBURN C24/96 RMV NEST | MOSSLNDG | ETL.5330.TOWR | 2024-05-18 | 2024-05-18 | 2025-02-05 | On-Time |  | 2025-05-18 | 2025-05-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46391173 | T2 EI MSS LANDING-COBURN C24/96 RMV NEST | ICS
LC | 128803216 | 020/124 | T2 MSS LNDNG-DL MNT#1 20/124 RPR FOND | MOSSLNDG | ETL.2830.TOWR | 2024-05-18 | 2024-05-18 | 2025-04-21 | On-Time |  | 2025-05-18 | 2025-05-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416636 | T2 EI MSS LNDNG-DL MNT#1 20/124 RPR FOND | ICQ
LC | 128803242 | 035/151 | T2 EI MSS LNDNG-LS GULS SS 35/151 COTTER | MOSSLNDG | ETL.5340.INSL | 2024-05-18 | 2024-05-18 | 2025-04-22 | On-Time |  | 2025-05-18 | 2025-05-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46391174 | T2 EI MSS LNDNG-LS GULS SS 35/151 COTTER | ICS
LC | 123636953 | 006/031 | T3NT MRRO BY-TMPLETON 006/031 RPR STRT | PISMOBCH | ETL.5933.TOWR | 2022-05-19 | 2022-05-19 | 2023-07-21 | On-Time |  | 2025-05-19 | 2025-05-19 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3N PRTO FRAB | No Good/Out of Stdrd | Structure-Steel | Repair | 45672068 | T3 MRRO BY-TMPLETON 006/031 RPR STRT | ICS
LC | 123638372 | 005/104 | T3NT EI BURNS-LNE STR #2 5/104C RPR GYWW | MOSSLNDG | ETL.6240.POLE.STPS | 2022-05-19 | 2022-05-19 | 2023-05-03 | On-Time |  | 2025-05-19 | 2025-05-19 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3N PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45659233 | T3 EI BURNS-LONE STAR #2 5/104C RPR GYWW | ICS
LC | 123674919 | 000/006 | T2NT DI RND MTN-TBL MTN #2 0/6 RPR JUMS | TABLEMTN | ETL.6070.INSL | 2022-05-23 | 2022-05-19 | 2023-02-15 | On-Time |  | 2025-05-19 | 2025-05-19 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 45457443 | T2 DI RND MTN-TBL MTN #2 0/6 RPR JUMS | ICS
LC | 128803649 | 050/250 | T2 EI MALIN-ROUND MTN #2 50/250 RPR FOND | TABLEMTN | ETL.6020.TOWR | 2024-05-19 | 2024-05-19 | 2025-04-08 | On-Time |  | 2025-05-19 | 2025-05-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381034 | T2 EI MALIN-ROUND MTN #2 50/250 RPR FOND | ICQ
LC | 128803674 | 050/250 | T2 MALIN-RND MTN #2 50/250 BNT STEEL | TABLEMTN | ETL.6020.TOWR | 2024-05-19 | 2024-05-19 | 2025-04-08 | On-Time |  | 2025-05-19 | 2025-05-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381035 | T2 EI MALIN-RND MTN #2 50/250 BNT STEEL | ICQ
LC | 128803746 | 053/264 | T2 MALIN-ROUND MTN #2 53/264 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-05-19 | 2024-05-19 | 2025-04-08 | On-Time |  | 2025-05-19 | 2025-05-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381439 | T2 EI MALIN-ROUND MTN #2 53/264 RPR GYWT | ICQ
LC | 128805276 | 055/274 | T2 MALIN-ROUND MTN #2 55/274 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-05-20 | 2024-05-19 | 2025-04-08 | On-Time |  | 2025-05-19 | 2025-05-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381440 | T2 EI MALIN-ROUND MTN #2 55/274 RPR GYWT | ICQ
LC | 128818687 | 042/277C | T2 DI TRNTY-COTTNWOD 42/277C RPR GYWW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-05-20 | 2024-05-19 | 2025-02-25 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46471158 | T2 DI TRNTY-COTTNWOD 42/277C RPR GYWW | ICW
LC | 128818688 | 042/277C | T2 DI TRNTY-COTTNWOD 42/277C RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-05-20 | 2024-05-19 | 2025-02-25 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46471159 | T2 DI TRNTY-COTTNWOD 42/277C RPR JUMW | ICW
LC | 128818788 | 042/277A | T2 DI TRINITY-COTNWOOD 42/277A RPR GYWW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-05-20 | 2024-05-19 | 2024-05-28 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46254934 | T2 DI TRINITY-COTNWOOD 42/277A RPR GYWW | ICW
LC | 128818900 | 017/226 | T2 DI KESWICK TRINITY 17/226 RPR GYWW | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-20 | 2024-05-19 | 2024-09-14 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311205 | T2 DI KESWICK TRINITY 17/226 RPR GYWW | ICW
LC | 128818902 | 017/226 | T2 DI KESWICK TRINITY 17/226 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-20 | 2024-05-19 | 2024-09-14 | On-Time |  | 2024-08-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46253226 | T2 DI KESWICK TRINITY 17/226 RPR JUMW | ICW
LC | 128818906 | 016/202 | T2 DI KESWICK TRINITY 16/202 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-20 | 2024-05-19 | 2024-09-15 | On-Time |  | 2024-08-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46253227 | T2 DI KESWICK TRINITY 16/202 RPR JUMW | ICW
LC | 128818908 | 016/202 | T2 DI KESWICK TRINITY 16/202 INSP ANCW | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-20 | 2024-05-19 | 2024-09-15 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46311210 | T2 DI KESWICK TRINITY 16/202 INSP ANCW | ICW
LC | 128818909 | 020/460 | T2 DI DRM-GRS VLY-WMAR 20/460 RPR GYWW | SACTO | ETL.6760.POLE.NWOD | 2024-05-20 | 2024-05-19 | 2025-04-21 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337426 | T2 DI DRM-GRS VLY-WMAR 20/460 RPR GYWW | ICW
LC | 128818933 | 100/004A | T2 DI HUMBOLDT-TRINITY 100/4A RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-05-20 | 2024-05-19 | 2024-08-28 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46250755 | T2 DI HUMBOLDT-TRINITY 100/4A RPR GYWW | ICW
LC | 128819031 | 020/460 | T2 DI DRM-GRS VLY-WMAR 20/460 INSP STRW | SACTO | ETL.6760.POLE.NWOD | 2024-05-20 | 2024-05-19 | 2024-10-02 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46324478 | T2 DI DRM-GRS VLY-WMAR 20/460 INSP STRW | ICW
LC | 128819032 | 016/200 | T2 DI KESWICK TRINITY 16/200 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-20 | 2024-05-19 | 2024-09-16 | On-Time |  | 2024-08-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46253229 | T2 DI KESWICK TRINITY 16/200 RPR JUMW | ICW
LC | 128819034 | 017/221 | T2 DI KESWICK TRINITY 17/221 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-20 | 2024-05-19 | 2024-09-15 | On-Time |  | 2024-08-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46253230 | T2 DI KESWICK TRINITY 17/221 RPR JUMW | ICW
LC | 128819038 | 066/000 | T2 DI HMBLT TRINITY 66/00C RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-20 | 2024-05-19 | 2025-04-19 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345946 | T2 DI HMBLT TRINITY 66/00C RPR GYWW | ICW
LC | 128819090 | 016/197 | T2 DI KESWICK-TRINITY 16/197 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-20 | 2024-05-19 | 2024-09-16 | On-Time |  | 2024-08-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46253231 | T2 DI KESWICK-TRINITY 16/197 RPR JUMW | ICW
LC | 128819131 | 066/000 | T2 DI HMBLT TRINITY 66/0 RPL INSW | EUREKA | ETL.1820.INSL.CERA | 2024-05-20 | 2024-05-19 | 2025-04-19 | On-Time |  | 2025-05-19 | 2025-05-19 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574614 | T2 DI HMBLT TRINITY 66/0 RPL INSW | 93I
LC | 128819135 | 041/267C | T2 DI TRNTY CTONWOOD 41/267C RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-05-20 | 2024-05-19 | 2025-02-24 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46471155 | T2 DI TRNTY CTONWOOD 41/267C RPR JUMW | ICW
LC | 128819136 | 041/267B | T2 DI TRNTY CTONWOOD 41/267B RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-05-20 | 2024-05-19 | 2025-02-24 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46471154 | T2 DI TRNTY CTONWOOD 41/267B RPR JUMW | ICW
LC | 128819181 | 016/205 | T2 DI KESWICK-TRINITY 16/205 REFRAME | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-20 | 2024-05-19 | 2025-04-11 | On-Time |  | 2025-05-19 | 2025-05-19 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35593470 | T2 DI KESWICK-TRINITY 16/205 REFRAME | 93E
LC | 128819183 | 015/094 | T2 DI STNS-MLNS STA-MNCA 15/94 UNBURY | VICTOR | ETL.3830.TOWR | 2024-05-20 | 2024-05-19 | 2025-04-10 | On-Time |  | 2025-05-19 | 2025-05-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46452728 | T2 DI STNS-MLNS STA-MNCA 15/94 UNBURY | ICQ
LC | 128819186 | 015/094 | T2 STNSLS-MLNS SS-MNTCA 15/94 RPR INSS | VICTOR | ETL.3830.INSL | 2024-05-20 | 2024-05-19 | 2024-05-19 | Past Due |  | 2024-11-19 | 2025-05-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46493123 | T2 DI STNS-MLNS SS-MNCA 15/94 RPR INSS | ICS
LC | 128819240 | 016/215 | T2 DI KESWICK-TRINITY 16/215 RMV VEG | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-20 | 2024-05-19 | 2025-02-10 | On-Time |  | 2025-05-19 | 2025-05-19 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128819241 | 016/215 | T2 DI KESWICK-TRINITY- 16/215 INSP STRW | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-20 | 2024-05-19 | 2024-09-18 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46311207 | T2 DI KESWICK-TRINITY- 16/215 INSP STRW | ICW
LC | 128819242 | 016/215 | T2 DI KESWICK-TRINITY 16/215 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-20 | 2024-05-19 | 2024-09-16 | On-Time |  | 2024-08-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46253232 | T2 DI KESWICK-TRINITY 16/215 RPR JUMW | ICW
LC | 128819264 | 020/464 | T2 DI DRUM GRS VLY WMAR 20/464 RPR GYWW | SACTO | ETL.6760.POLE.NWOD | 2024-05-20 | 2024-05-19 | 2025-04-21 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324477 | T2 DI DRUM GRS VLY WMAR 20/464 RPR GYWW | ICW
LC | 128819265 | 020/464 | T2 DI DRUM GRS VLY WMAR 20/464 RPR INSW | SACTO | ETL.6760.INSL.NCER | 2024-05-20 | 2024-05-19 | 2025-04-21 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46324476 | T2 DI DRUM GRS VLY WMAR 20/464 RPR INSW | ICW
LC | 128819298 | 017/222 | T2 DI KESWICK-TRINITY 17/222 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-20 | 2024-05-19 | 2024-09-15 | On-Time |  | 2024-08-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46253235 | T2 DI KESWICK-TRINITY 17/222 RPR JUMW | ICW
LC | 128819299 | B019/434 | T2 DI DRM-GRS VLY-WEIMR B19/434 RPR CRSW | SACTO | ETL.6760.POLE.WOOD | 2024-05-20 | 2024-05-19 | 2024-10-19 | On-Time |  | 2024-08-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46323926 | T2 DI DRM-GRS VLY-WEIMR B19/434 RPR CRSW | ICW
LC | 128837686 | 066/000 | T2 DI HUMBOLDT-TRINITY 66/000 RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-22 | 2024-05-19 | 2025-04-19 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345947 | T2 DI HUMBOLDT-TRINITY 66/000 RPR GYWW | ICW
LC | 129026289 | 035/302 | T2 DI PIT #1-COTTONWOOD 35/302 TOUCH | TABLEMTN | ETL.5390.TOWR | 2024-06-05 | 2024-05-19 | 2024-05-19 | Past Due |  | 2024-11-19 | 2025-05-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478239 | T2 DI PIT #1-COTTONWOOD 35/302 TOUCH | ICQ
LC | 129026325 | 004/107 | T2 DI CLGTE-ALLEGHANY 04/107 RPR STRW | SACTO | ETL.6470.POLE.WOOD | 2024-06-05 | 2024-05-19 | 2025-05-12 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46460016 | T2 DI CLGTE-ALLEGHANY 04/107 RPR STRW | ICW
LC | 129026347 | 017/224 | T2 DI KESWICK-TRINITY-17/224 RPR JMPW | TABLEMTN | ETL.7270.INSL.NCER | 2024-06-05 | 2024-05-19 | 2025-04-18 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311206 | T2 DI KESWICK-TRINITY-17/224 RPR JMPW | ICW
LC | 129031344 | 006/028 | T2 DI PITTSBURG-SM 6/28 TOUCH | CONCORD | ETL.5463.TOWR | 2024-06-06 | 2024-05-19 | 2025-04-29 | On-Time |  | 2024-11-19 | 2025-05-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46489045 | T2 DI PITTSBURG-SM 6/28 TOUCH | ICQ
LC | 129055233 | 031/476 | T2 CLAY-MARTEL 31/476 RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-06-10 | 2024-05-19 | 2024-05-19 | Past Due |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46327030 | +T2 DI CLAY-MARTEL 31/476 RPR STRW | ICW
LC | 129061377 | 001/017 | T2 DI JOLON TAP 1/17 RPL STRW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-06-11 | 2024-05-19 | 2025-01-28 | On-Time |  | 2025-05-19 | 2025-05-19 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573656 | T2 DI JOLON TAP 1/17 RPL STRW | 70Y
LC | 129061434 | 002/029 | T2 DI JOLON TAP 2/29 RPL STRW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-06-11 | 2024-05-19 | 2025-01-20 | On-Time |  | 2025-05-19 | 2025-05-19 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573658 | T2 DI JOLON TAP 2/29 RPL STRW | 70Y
LC | 129061529 | 013/300 | T2 DI DRUM GRS VY WMR 13/300 RPL SPLW | SACTO | ETL.6760.INSL.NCER | 2024-06-11 | 2024-05-19 | 2025-01-31 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Splice-Wood | Replace | 46324479 | T2 DI DRUM GRS VY WMR 13/300 RPL SPLW | ICW
LC | 129061545 | 073/001A | T2 DI HMBLDT-TRNTY-73/01A RPR GYWW | EUREKA | ETL.1820.POLE.WOOD | 2024-06-11 | 2024-05-19 | 2024-10-21 | On-Time |  | 2024-11-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46268097 | T2 DI HMBLDT-TRNTY-73/01A RPR GYWW | ICW
LC | 129061547 | 073/001A | T2 DI HMBLDT-TRNTY-73/01A RPR STRW | EUREKA | ETL.1820.POLE.WOOD | 2024-06-11 | 2024-05-19 | 2025-04-08 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46345948 | T2 DI HMBLDT-TRNTY-73/01A RPR STRW | ICW
LC | 129061613 | 073/001C | T2 DI HMBLDT-TRNTY-73/01C RPR GYWW | EUREKA | ETL.1820.POLE.WOOD | 2024-06-11 | 2024-05-19 | 2024-10-21 | On-Time |  | 2024-11-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46268099 | T2 DI HMBLDT-TRNTY-73/01C RPR GYWW | ICW
LC | 129061742 | 073/001B | T2 DI HUMBOLDT-TRINITY 73/1B RPR GYWW | EUREKA | ETL.1820.POLE.WOOD | 2024-06-11 | 2024-05-19 | 2024-10-21 | On-Time |  | 2024-11-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46268098 | T2 DI HUMBOLDT-TRINITY 73/1B RPR GYWW | ICW
LC | 129061846 | 012/294 | T2 DI DRM GRS VLY WMR 12/294 RPL STRW | SACTO | ETL.6760.POLE.WOOD | 2024-06-11 | 2024-05-19 | 2025-01-31 | On-Time |  | 2025-05-19 | 2025-05-19 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573448 | T2 DI DRM GRS VLY WMR 12/294 RPL STRW | 70Y
LC | 129061859 | 018/238 | T2 DI KESWICK-TRINITY 18/238 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-06-11 | 2024-05-19 | 2025-04-15 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311203 | T2 DI KESWICK-TRINITY 18/238 RPR JUMW | ICW
LC | 129078715 | 066/334 | T2 DI MALIN-RND MNTN#2 66/334 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-06-14 | 2024-05-19 | 2025-02-10 | On-Time |  | 2025-05-19 | 2025-05-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338274 | T2 DI MALIN-RND MNTN#2 66/334 RPR SHLD | ICS
LC | 129079086 | 016/209 | T2 DI KESWICK-TRINITY 16/209 RPL POLE | TABLEMTN | ETL.7270.POLE.WOOD | 2024-06-14 | 2024-05-19 | 2025-04-19 | On-Time |  | 2025-05-19 | 2025-05-19 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573307 | T2 DI KESWICK-TRINITY 16/209 RPL POLE | 70Y
LC | 129079197 | 067/337 | T2 DI MALIN-RND MNTN #2-67/337 RPR SHLS | TABLEMTN | ETL.6020.TOWR | 2024-06-14 | 2024-05-19 | 2025-02-24 | On-Time |  | 2025-05-19 | 2025-05-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338275 | T2 DI MALIN-RND MNTN #2-67/337 RPR SHLS | ICS
LC | 129087190 | 014/089 | T2 DI STNSLS-MLNS-MNTC #1 14/89 RPR STRT | VICTOR | ETL.3830.TOWR | 2024-06-17 | 2024-05-19 | 2025-04-16 | On-Time |  | 2025-05-19 | 2025-05-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416708 | T2 DI STNSLS-MLNS-MNTC #1 14/89 RPR STRT | ICQ
LC | 129087788 | B016/374 | T2 DI DRM-GRSS VLLY-WMR B16/374 RPL POLE | SACTO | ETL.6760.POLE.WOOD | 2024-06-17 | 2024-05-19 | 2025-05-17 | On-Time |  | 2025-05-19 | 2025-05-19 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573456 | T2 DI DRM-GRSS VLLY-WMR B16/374 RPL POLE | 70Y
LC | 129088187 | 016/207 | T2 DI KESWICK-TRINITY 16/207 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-06-17 | 2024-05-19 | 2025-04-19 | On-Time |  | 2025-05-19 | 2025-05-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311208 | T2 DI KESWICK-TRINITY 16/207 RPR JUMW | ICW
LC | 130737409 | 012/049 | T3NT PTTSBRG-SN MATEO 012/049 RPR FOND | CONCORD | ETL.5463.TOWR | 2025-01-13 | 2024-11-19 | 2024-11-19 | Past Due |  | 2027-11-19 | 2025-05-19 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR3 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair
LC | 123706761 | 027/129 | T3NT DI FULT-PUELBLO 27/129 RPR ACG | LAKEVLLE | ETL.1600.TOWR | 2022-05-27 | 2022-05-20 | 2024-06-10 | On-Time |  | 2025-05-20 | 2025-05-20 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB NTDE | Anti-Climbing Guard | Structure-Tower | Repair | 46204202 | T3NT DI FULT-PUELBLO 27/129 RPR ACG | ICQ
LC | 123779396 | 018/012 | T2NT DI MNDCNO-PHLO HPLND 18/12 RMV BUTT | WILLITS | ETL.7520.POLE.WOOD | 2022-06-07 | 2022-05-20 | 2023-05-10 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2N PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 45670960 | T2 DI MNDCNO-PHLO HPLND 18/12 RMV BUTT | ICW
LC | 128805963 | 015/098 | T2 STNSLS-MLNS SS-MNTCA 15/98 TOUCH | VICTOR | ETL.3830.TOWR | 2024-05-20 | 2024-05-20 | 2025-01-22 | On-Time |  | 2024-11-20 | 2025-05-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46473024 | T2 STNSLS-MLNS SS-MNTCA 15/98 TOUCH | ICQ
LC | 128806323 | 004/006-GUY | T2 EI VLY SPRNG-CLVRS CMNT 4/6-G CTL GRD | VICTOR | ETL.8220.POLE.WOOD | 2024-05-20 | 2024-05-20 | 2025-03-07 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Animal Guard-Wood | Install | 46327020 | T2 EI VLY SPRNG-CLVRS CMNT 4/6-G CTL GRD | ICW
LC | 128806368 | 011/130A | T2 EI DRUM-SUMMIT #2 011/130A RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-05-20 | 2024-05-20 | 2024-06-17 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46268267 | T2 EI DRUM-SUMMIT #2 011/130A RPR GYWW | ICW
LC | 128806464 | 004/002 | T2 WV TRINITY-MAPLE CREEK 4/2 INS DMPW | EUREKA | ETL.8170.INSL.NCER | 2024-05-20 | 2024-05-20 | 2025-03-25 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46345949 | T2 WV TRINITY-MAPLE CREEK 4/2 INS DMPW | ICW
LC | 128806560 | 011/083 | T2 GREEN VALLEY-LLAGAS 11/83L RPL ANCW | MOSSLNDG | ETL.1720.POLE.STPS | 2024-05-20 | 2024-05-20 | 2024-05-20 | Past Due |  | 2025-05-20 | 2025-05-20 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW CUST OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573310 | T2 GREEN VALLEY-LLAGAS 11/83 RPL ANCW | 93E
LC | 128806574 | 039/186 | T2 MENDOCINO-REDBUD 039/186 RPL INSS | WILLITS | ETL.2410.INSL.CERA | 2024-05-20 | 2024-05-20 | 2025-05-23 | Past Due |  | 2025-05-20 | 2025-05-20 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35608533 | T2 MENDOCINO-REDBUD 039/186 RPL INSS | 93K
LC | 128806661 | 090/461 | T2 MALIN-ROUND MTN #2 90/461 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-05-20 | 2024-05-20 | 2025-05-19 | On-Time |  | 2025-05-20 | 2025-05-20 | 93Z | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716778 | T2 DI MLN RD MTN#2 RPL ANCT 10 TWRS | 93Z
LC | 128806798 | 011/130C | T2 EI DRUM-SUMMIT #2 11/130C RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-05-20 | 2024-05-20 | 2024-06-17 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46268664 | T2 EI DRUM-SUMMIT #2 11/130C RPR GYWW | ICW
LC | 128806871 | 000/009 | T2 WV COLGATE-SMRTVLLE #1 0/9L RPR ANCW | SACTO | ETL.6510.POLE.STPS | 2024-05-20 | 2024-05-20 | 2025-02-20 | On-Time |  | 2025-05-20 | 2025-05-20 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 35572932 | T2 WV COLGATE-SMRTVLLE #1 0/9L RPL ANCW | 93E
LC | 128807015 | 004/005 | T2 EI VLY SPRNG-CLVRS CMNT 4/5 RPR POLE | VICTOR | ETL.8220.POLE.WOOD | 2024-05-20 | 2024-05-20 | 2025-03-07 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46327021 | T2 EI VLY SPRNG-CLVRS CMNT 4/5 RPR POLE | ICW
LC | 128807079 | :003/020 | T2 STAN-MELONES SS-MNTCA :3/20 RMV NEST | VICTOR | ETL.3830.TOWR | 2024-05-20 | 2024-05-20 | 2024-09-04 | On-Time |  | 2024-11-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR OTHR COMP OH TR2 PRTO FRAB DURA BRIN | Debris/Nest/etc. | Structure-Steel | Remove | 46252529 | T2 STAN-MELONES SS-MNTCA :3/20 RMV NEST | ICS
LC | 128807207 | 003/005 | T2 MENDOCINO-WILLITS 3/5 RPL STRW | WILLITS | ETL.7540.POLE.WOOD | 2024-05-20 | 2024-05-20 | 2024-05-20 | Past Due |  | 2024-11-20 | 2025-05-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP PUBL TRAF CLR ACCH OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35558797 | T2 EI MENDOCINO-WILLITS 003/005 RPL POLE | 70Y
LC | 128811454 | 003/030 | T2 HAT CREEK #1-PIT #1 03/30 RPL ANCW | TABLEMTN | ETL.7020.POLE.NWOD | 2024-05-20 | 2024-05-20 | 2024-09-20 | On-Time |  | 2024-08-20 | 2025-05-20 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP ACCM COMP OH TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35557055 | T2 HAT CREEK #1-PIT #1 03/30 RPL ANCW | 93E
LC | 128811667 | 005/037 | T2 EI DIVIDE-VANDENBERG #2 5/37 RMV VEG | PISMOBCH | ETL.8630.POLE.NWOD | 2024-05-20 | 2024-05-20 | 2025-03-14 | On-Time |  | 2025-05-20 | 2025-05-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128811708 | 57 | T2 TRINITY-MAPLE CREEK 17/1B RPR JMPW | EUREKA | ETL.8170.SWIT | 2024-05-20 | 2024-05-20 | 2024-05-20 | Past Due |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Jumper-Wood | Repair | 46345983 | T2 TRINITY-MAPLE CREEK 17/1B RPR JMPW | ICW
LC | 128811727 | 55 | T2 TRINITY-MAPLE CREEK 17/1 RPR JMPW | EUREKA | ETL.8170.SWIT | 2024-05-20 | 2024-05-20 | 2024-05-20 | Past Due |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Jumper-Wood | Repair | 46345981 | T2 EI TRINITY-MAPLE CREEK 17/1 RPR JMPW | ICW
LC | 128811746 | 011/133 | T2 EI DRUM-SUMMIT#2 11/133 RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-05-20 | 2024-05-20 | 2025-04-22 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458322 | T2 EI DRUM-SUMMIT#2 11/133 RPR GYWW | ICW
LC | 128811751 | 57 | T2 TRINITY-MAPLE CREEK 17/1B COTTER | EUREKA | ETL.8170.SWIT | 2024-05-20 | 2024-05-20 | 2025-05-20 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Switch-Wood | Repair | 46485323 | T2 TRINITY-MAPLE CREEK 17/1B COTTER | ICW
LC | 128811756 | C022/090 | T2 EI MSS LANDING-COBURN C22/90 RMV NEST | MOSSLNDG | ETL.5330.TOWR | 2024-05-20 | 2024-05-20 | 2025-02-05 | On-Time |  | 2025-05-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46391176 | T2 EI MSS LANDING-COBURN C22/90 RMV NEST | ICS
LC | 128812641 | 005/004 | T2 EI CLEAR LAKE-HOPLAND 05/004 RPL STRW | WILLITS | ETL.6390.POLE.WOOD | 2024-05-20 | 2024-05-20 | 2025-05-18 | On-Time |  | 2025-05-20 | 2025-05-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572386 | T2 EI CLEAR LAKE-HOPLAND 05/004 RPL STRW | 70Y
LC | 128816111 | 091/466 | T2 EI MALIN-ROUND MTN #2 91/466 RMV NEST | TABLEMTN | ETL.6020.TOWR | 2024-05-20 | 2024-05-20 | 2025-02-05 | On-Time |  | 2025-05-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46338197 | T2 EI MALIN-ROUND MTN #2 91/466 RMV NEST | ICS
LC | 128817431 | 020/094 | T2 CALLENDER SW ST-MESA 20/94 RMV VEG | PISMOBCH | ETL.1210.TOWR | 2024-05-20 | 2024-05-20 | 2025-05-15 | On-Time |  | 2025-05-20 | 2025-05-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO CLMB FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128817637 | 064/462 | T2 EI BRDGVL-CTNWD 64/462 RPR INSS | EUREKA | ETL.1110.INSL.CERA | 2024-05-20 | 2024-05-20 | 2025-05-03 | On-Time |  | 2025-05-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46345950 | T2 EI BRDGVL-CTNWD 64/462 RPR INSS | ICS
LC | 128817641 | 037/161 | T2 EI CBRN-LS AGUILAS SS 37/161 RMV NEST | MOSSLNDG | ETL.4460.TOWR | 2024-05-20 | 2024-05-20 | 2025-02-23 | On-Time |  | 2025-05-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46391177 | T2 EI CBRN-LS AGUILAS SS 37/161 RMV NEST | ICS
LC | 128818092 | 011/135A | T2 EI DRUM-SUMMIT #2 11/135A RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-05-20 | 2024-05-20 | 2024-06-17 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46268817 | T2 EI DRUM-SUMMIT #2 11/135A RPR GYWW | ICW
LC | 128818196 | 091/464 | T2 EI MALIN-ROUND MTN #2 91/464 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-05-20 | 2024-05-20 | 2025-02-05 | On-Time |  | 2025-05-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338198 | T2 EI MALIN-ROUND MTN #2 91/464 RPR SHLD | ICS
LC | 128818216 | 002/039B | T2 WV PIT #1-MCARTHUR 2/039B RPL INSW | TABLEMTN | ETL.7790.INSL.NCER | 2024-05-20 | 2024-05-20 | 2024-09-05 | On-Time |  | 2025-05-20 | 2025-05-20 | 508 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 31641265 | T2 DI PIT #1-MC ARTHUR 2/39C RPL INSW | 93I
LC | 128818289 | C023/091 | T2 EI COBURN-LAS AGLS SS C23/91 RPL INSS | MOSSLNDG | ETL.4460.INSL | 2024-05-20 | 2024-05-20 | 2025-04-04 | On-Time |  | 2025-05-20 | 2025-05-20 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577223 | T2 EI COBURN-LAS AGUILAS C23/91 RPL INSS | 93K
LC | 128818653 | 057/284 | T2 MALIN-ROUND MTN #2 57/284 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-05-20 | 2024-05-20 | 2025-04-10 | On-Time |  | 2025-05-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 46338199 | T2 MALIN-ROUND MTN #2 - 500 KV_057/284 | ICS
LC | 128818657 | 091/465 | T2 EI MALIN-ROUND MTN #2 91/465 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-05-20 | 2024-05-20 | 2025-02-06 | On-Time |  | 2025-05-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338260 | T2 EI MALIN-ROUND MTN #2 91/465 RPR SHLD | ICS
LC | 128818675 | 058/288 | T2 MALIN-RND MTN #2 58/288 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-05-20 | 2024-05-20 | 2025-04-09 | On-Time |  | 2025-05-20 | 2025-05-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381444 | T2 EI MALIN-ROUND MTN #2 58/288 RPR STRT | ICQ
LC | 128818677 | 058/288 | T2 MALIN-ROUND MTN #2 58/288 COMPLETE | TABLEMTN | ETL.6020.TOWR | 2024-05-20 | 2024-05-20 | 2025-04-09 | On-Time |  | 2025-05-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 46338261 | T2 MALIN-ROUND MTN #2 - 500 KV_058/288 | ICS
LC | 128818678 | 064/319 | T2 EI MLN-RND MTN #2 064/319 RPR INSS | TABLEMTN | ETL.6020.INSL.NCER | 2024-05-20 | 2024-05-20 | 2025-02-09 | On-Time |  | 2025-05-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO CLMB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46338262 | T2 EI MLN-RND MTN #2 064/319 RPR INSS | ICS
LC | 128818756 | 000/006A | T2 EI BKS CK-RK CK-CRST 0/6A RPR EROSION | TABLEMTN | ETL.4430.POLE.NWOD | 2024-05-20 | 2024-05-20 | 2025-03-19 | On-Time |  | 2025-05-20 | 2025-05-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46272343 | T2 EI BKS CK-RK CK-CRST 0/6A RPR EROSION | ICQ
LC | 128818757 | 000/006B | T2 EI BKS CK-RK CK-CRST 0/6B RPR EROSION | TABLEMTN | ETL.4430.POLE.NWOD | 2024-05-20 | 2024-05-20 | 2025-03-19 | On-Time |  | 2025-05-20 | 2025-05-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46353969 | T2 EI BKS CK-RK CK-CRST 0/6B RPR EROSION | ICQ
LC | 128818791 | 002/014 | T2 LAURELES-OTTER 002/014 RPL ANCW | MOSSLNDG | ETL.7380.POLE.WOOD | 2024-05-20 | 2024-05-20 | 2025-04-11 | On-Time |  | 2025-05-20 | 2025-05-20 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573691 | T2 EI LAURELES-OTTER 002/014 RPL ANCW | 93E
LC | 128818795 | 000/006C | T2 EI BKS CK-RK CK-CRST 0/6C RPR FOND | TABLEMTN | ETL.4430.POLE.NWOD | 2024-05-20 | 2024-05-20 | 2025-03-19 | On-Time |  | 2025-05-20 | 2025-05-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46353970 | T2 EI BKS CK-RK CK-CRST 0/6C RPR FOND | ICQ
LC | 128818796 | 000/006A | T2 EI BKS CK RK CK CST 0/6A RPR ANCT | TABLEMTN | ETL.4430.POLE.NWOD | 2024-05-20 | 2024-05-20 | 2025-03-19 | On-Time |  | 2025-05-20 | 2025-05-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46353971 | T2 EI BKS CK RK CK CST 0/6A RPR ANCT | ICQ
LC | 128818831 | 004/035 | T2 BCKS CK RCK CK CSTA 4/35 RPR STRT | TABLEMTN | ETL.4430.TOWR | 2024-05-20 | 2024-05-20 | 2025-04-30 | On-Time |  | 2025-05-20 | 2025-05-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC SWRK CLR ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46353973 | T2 EI BCKS CK RCK CK CSTA 4/35 BNT STEEL | ICQ
LC | 128818832 | 003/031 | T2 EI BCKS CK RCK CK CSTA 3/31 RPR JUMS | TABLEMTN | ETL.4430.INSL | 2024-05-20 | 2024-05-20 | 2025-05-16 | On-Time |  | 2025-05-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCM COMP OH FMOB TR2 PRTO FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46262789 | T2 EI BCKS CK RCK CK CSTA 3/031 RPR JMPS | ICS
LC | 128819005 | 008/070 | T2 EI CRESTA-RIO OSO 008/070 RPL INSS | TABLEMTN | ETL.4590.INSL | 2024-05-20 | 2024-05-20 | 2025-04-28 | On-Time |  | 2025-05-20 | 2025-05-20 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570419 | T2 EI CRESTA-RIO OSO RPL INSS | 93K
LC | 128819013 | 008/070 | T2 EI CRESTA-RIO OSO 008/070 RPL HNGR | TABLEMTN | ETL.4590.INSL | 2024-05-20 | 2024-05-20 | 2025-04-28 | On-Time |  | 2025-05-20 | 2025-05-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46381332 | T2 EI CRESTA-RIO OSO 008/070 RPL HNGR | ICQ
LC | 128819015 | 008/067 | T2 CRESTA-RIO OSO 008/067 RPL INSS | TABLEMTN | ETL.4590.INSL | 2024-05-20 | 2024-05-20 | 2025-05-03 | On-Time |  | 2025-05-20 | 2025-05-20 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570419 | T2 EI CRESTA-RIO OSO RPL INSS | 93K
LC | 128819129 | 010/082 | T2 EI CRESTA-RIO OSO 010/082 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-20 | 2024-05-20 | 2025-03-24 | On-Time |  | 2025-05-20 | 2025-05-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381333 | T2 EI CRESTA-RIO OSO 010/082 RPR FOND | ICQ
LC | 128819365 | 004/053 | T2 DI JOLON TAP 4/53 RPL STRW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-05-20 | 2024-05-20 | 2025-01-31 | On-Time |  | 2025-05-20 | 2025-05-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573680 | T2 DI JOLON TAP 4/53 RPL STRW | 70Y
LC | 128819405 | 005/088 | T2 EI SQC-SNTA YNZ SW ST 05/88 RPL STRW | PISMOBCH | ETL.3700.POLE.WOOD | 2024-05-20 | 2024-05-20 | 2025-02-10 | On-Time |  | 2025-05-20 | 2025-05-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573763 | T2 EI SQC-SNTA YNZ SW ST 05/88 RPL STRW | 70Y
LC | 128819416 | 008/058 | T2 DI MRAGA-SN LEANDRO #1 8/58 RPR INSS | CONCORD | ETL.2770.INSL | 2024-05-20 | 2024-05-20 | 2024-10-02 | On-Time |  | 2024-08-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46256024 | T2 DI MRAGA-SN LEANDRO #1 8/58 RPR INSS | ICS
LC | 128819439 | 011/074 | T2 CNTRA CSTA-LS PSTS 11/74 RMV NEST | CONCORD | ETL.4510.TOWR | 2024-05-20 | 2024-05-20 | 2024-05-20 | Past Due |  | 2025-05-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46404323 | T2 EI CNTRA CSTA LS PSTS 11/74 RMV NEST | ICS
LC | 128819506 | 002/039 | T2 HAAS-WOODCHUCK 2/39 RPR JUMW | FRESNO | ETL.8730.INSL.NCER | 2024-05-20 | 2024-05-20 | 2024-05-20 | Past Due |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46268357 | T2 HAAS-WOODCHUCK 02/39 RPR JMPW | ICW
LC | 128819562 | 010/073 | T2 EI CNTRA CSTA-LS PSTS 10/73 RPR CNDS | CONCORD | ETL.4510.INSL.NCER | 2024-05-20 | 2024-05-20 | 2024-05-20 | Past Due |  | 2025-05-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Conductor-Steel | Repair | 46289323 | T2 EI CNTRA CSTA-LS PSTS 10/73 RPR CNDS | ICS
LC | 128819846 | B016/370 | T2 DI DRM GRS VLY WMR B016/370 RPR IBWW | SACTO | ETL.6760.INSL.NCER | 2024-05-21 | 2024-05-20 | 2025-05-17 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46324469 | T2 DI DRM GRS VLY WMR B016/370 RPR IBWW | ICW
LC | 128836819 | 071/002B | T2 DI HUMBLT TRINITY 71/2B RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-21 | 2024-05-20 | 2024-12-11 | On-Time |  | 2024-08-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46250752 | T2 DI HUMBLT TRINITY 71/2B RPR GYWW | ICW
LC | 128836865 | 071/002B | T2 DI HUMBLT TRINITY 71/2B-R RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-21 | 2024-05-20 | 2024-12-11 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46250754 | T2 DI HUMBLT TRINITY 71/2B RPR GYWW | ICW
LC | 128836902 | 071/002B | T2 DI HUMBLT TRINITY 71/2B RPL HRDD | EUREKA | ETL.1820.POLE.WDPS | 2024-05-21 | 2024-05-20 | 2025-04-09 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345953 | T2 DI HUMBLT TRINITY 71/2B RPL HRDD | ICW
LC | 128836909 | 071/002B | T2 DI HUMBLT TRINITY 71/2B RPL HRDD | EUREKA | ETL.1820.POLE.WDPS | 2024-05-21 | 2024-05-20 | 2025-04-09 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345952 | T2 DI HUMBLT TRINITY 71/2B RPL HRDD | ICW
LC | 128836935 | 071/002B | T2 DI HUMBLT TRINITY 71/2B RPL ANCW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-21 | 2024-05-20 | 2025-04-09 | On-Time |  | 2025-05-20 | 2025-05-20 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574618 | T2 DI HUMBLT TRINITY 71/2B RPL ANCW | 93E
LC | 128836968 | 018/250 | T2 DI KESWICK-TRINTY 18/250 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-21 | 2024-05-20 | 2024-09-14 | On-Time |  | 2024-08-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46253248 | T2 DI KESWICK-TRINTY 18/250 RPR JUMW | ICW
LC | 128837000 | 071/000B | T2 DI HUMBLT TRINITY 71/0B RPR INSW | EUREKA | ETL.1820.INSL.CERA | 2024-05-21 | 2024-05-20 | 2025-04-08 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46345951 | T2 DI HUMBLT TRINITY 71/0B RPR INSW | ICW
LC | 128837008 | 071/003 | T2 DI HUMBLT TRINITY 71/3 RPL ANCW | EUREKA | ETL.1820.POLE.STPS | 2024-05-21 | 2024-05-20 | 2025-04-08 | On-Time |  | 2025-05-20 | 2025-05-20 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574603 | T2 DI HUMBLT TRINITY 71/3 RPL ANCW | 93E
LC | 128837034 | 072/000 | T2 DI HUMBLT TRINITY 72/0R RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-05-21 | 2024-05-20 | 2025-04-08 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345954 | T2 DI HUMBLT TRINITY 72/0R RPR GYWW | ICW
LC | 128837039 | 072/000 | T2 DI HUMBLT TRINITY 72/0C RMV VEG | EUREKA | ETL.1820.POLE.STPS | 2024-05-21 | 2024-05-20 | 2024-11-20 | On-Time |  | 2025-05-20 | 2025-05-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128837178 | 018/252 | T2 DI KESWICK-TRIN 18/252 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-21 | 2024-05-20 | 2024-09-14 | On-Time |  | 2024-08-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46253253 | T2 DI KESWICK-TRIN 18/252 RPR JUMW | ICW
LC | 128837189 | 018/251 | T2 DI KESWICK-TRINITY 18/251 RPR GYWW | TABLEMTN | ETL.7270.POLE.NWOD | 2024-05-21 | 2024-05-20 | 2024-09-14 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311179 | T2 DI KESWICK-TRINITY 18/251 RPR GYWW | ICW
LC | 128837210 | 018/251 | T2 DI KESWICK-TRINITY 18/251 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-21 | 2024-05-20 | 2024-09-14 | On-Time |  | 2024-08-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46253254 | T2 DI KESWICK-TRINITY 18/251 RPR JUMW | ICW
LC | 128837284 | 019/442 | T2 DI DRM-GRSS VLY-WMR 19/442 RPL INSW | SACTO | ETL.6760.INSL.CERA | 2024-05-21 | 2024-05-20 | 2025-03-11 | On-Time |  | 2025-05-20 | 2025-05-20 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573452 | T2 DI DRM-GRSS VLY-WMR 19/442 RPL INSW | 93I
LC | 128837349 | 072/004 | T2 DI HUMBLT TRNITY 72/4 RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-05-21 | 2024-05-20 | 2025-04-08 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46345955 | T2 DI HUMBLT TRNITY 72/4 RPR JUMW | ICW
LC | 128886760 | 012/054 | T2 DI MORRO BAY-MESA 12/54 INSP STRT | PISMOBCH | ETL.5290.TOWR | 2024-05-24 | 2024-05-20 | 2024-10-14 | On-Time |  | 2025-05-20 | 2025-05-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327169 | T2 DI MORRO BAY-MESA 12/54 INSP STRT | ICQ
LC | 128886947 | 027/119 | T2 DI MORROW BAY MESA 27/119 INSP STRT | PISMOBCH | ETL.5290.TOWR | 2024-05-24 | 2024-05-20 | 2024-09-26 | On-Time |  | 2025-05-20 | 2025-05-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Tower | Inspect | 46327170 | T2 DI MORROW BAY MESA 27/119 INSP STRT | ICQ
LC | 129021361 | 071/002A | T2 DI HUMBOLDT TRINITY 71/2AL RPL ANCW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-04 | 2024-05-20 | 2025-04-09 | On-Time |  | 2025-05-20 | 2025-05-20 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574615 | T2 DI HUMBOLDT TRINITY 71/2AL RPL ANCW | 93E
LC | 129021390 | 071/002A | T2 DI HUMBOLDT TRINITY 71/2AL RMV VEG | EUREKA | ETL.1820.POLE.WDPS | 2024-06-04 | 2024-05-20 | 2024-11-20 | On-Time |  | 2025-05-20 | 2025-05-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129021460 | 071/002A | T2 DI HUMBOLDT TRINITY 71/2A RPR JUMW | EUREKA | ETL.1820.INSL.CERA | 2024-06-04 | 2024-05-20 | 2025-04-11 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262165 | T2 DI HUMBOLDT TRINITY 71/2A RPR JUMW | ICW
LC | 129026643 | 019/269 | T2 DI KSWCK-TRNTY 19/269 RPR STRW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-06-05 | 2024-05-20 | 2025-04-11 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311176 | T2 DI KSWCK-TRNTY 19/269 RPR POLE | ICW
LC | 129026646 | 019/269 | T2 DI KSWCK-TRNTY 19/269 RPR JMPW | TABLEMTN | ETL.7270.INSL.CERA | 2024-06-05 | 2024-05-20 | 2025-04-11 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311175 | T2 DI KSWCK-TRNTY 19/269 RPR JMPW | ICW
LC | 129031775 | 035/301 | T2 DI PIT #1-COTTONWOOD 35/301 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-06-06 | 2024-05-20 | 2025-02-06 | On-Time |  | 2025-05-20 | 2025-05-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381907 | T2 DI PIT #1-COTTONWOOD 35/301 RPR STRT | ICQ
LC | 129031958 | B016/372 | T2 DI DRUM-GV-WEI B16/372 RPL STRW | SACTO | ETL.6760.POLE.WOOD | 2024-06-06 | 2024-05-20 | 2025-05-17 | On-Time |  | 2025-05-20 | 2025-05-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Rotten | Structure-Wood | Replace | 35573455 | T2 DI DRUM-GV-WEI B16/372 RPL STRW | 70Y
LC | 129032430 | 013/313 | T2 DI DRUM-GRSS VLL-WMAR 13/313 RPR STRW | SACTO | ETL.6760.POLE.WOOD | 2024-06-06 | 2024-05-20 | 2025-01-08 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46324475 | T2 DI DRUM-GRSS VLL-WMAR 13/313 RPR STRW | ICW
LC | 129032683 | B025/572 | T2 DI DRM-GRSS VLLY-WMR B25/572 RPR ADSS | SACTO | ETL.6760.POLE.WOOD | 2024-06-06 | 2024-05-20 | 2025-01-15 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | ADSS - Wood | Repair | 46324466 | T2 DI DRM-GRSS VLLY-WMR B25/572 RPR ADSS | ICW
LC | 129061154 | 004/004A | T2 DI HLSDLE JCT-HLFMN BY 04/04A RMV VEG | METCALF | ETL.7060.POLE.NWOD | 2024-06-11 | 2024-05-20 | 2025-04-15 | On-Time |  | 2025-05-20 | 2025-05-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129061220 | 004/004A | T2 DI HLSDLE JC-HLFMN BY 04/04A RPR INSS | METCALF | ETL.7060.POLE.NWOD | 2024-06-11 | 2024-05-20 | 2025-03-04 | On-Time |  | 2025-05-20 | 2025-05-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46286716 | T2 DI HLSDLE JC-HLFMN BY 04/04A RPR INSS | ICS
LC | 129061601 | 002/057 | T2 DI HAT CREEK #1-WESTWD 2/57 GO95 RPL | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-11 | 2024-05-20 | 2025-05-13 | On-Time |  | 2025-05-20 | 2025-05-20 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35574743 | T2 DI HAT CREEK #1-WESTWD 2/57 GO95 | 93G
LC | 129061737 | 018/430 | T2 DI DRM-GRS VLY-WEIMAR 18/430 RPL STRW | SACTO | ETL.6760.POLE.WOOD | 2024-06-11 | 2024-05-20 | 2025-03-11 | On-Time |  | 2025-05-20 | 2025-05-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573451 | T2 DI DRM-GRS VLY-WEIMAR 18/430 RPL STRW | 70Y
LC | 129061891 | 025/002 | T2 DI GARBRVL-LAYTONVL 25/02 RPR CNDW | WILLITS | ETL.8365.INSL.NCER | 2024-06-11 | 2024-05-20 | 2025-04-17 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46446814 | T2 DI GARBRVL-LAYTONVL 25/02 RPR CNDW | ICW
LC | 129062024 | 016/375 | T2 DI DRM-GRSS VLLY-WMR 16/375 RPR GYWW | SACTO | ETL.6760.POLE.WOOD | 2024-06-11 | 2024-05-20 | 2024-07-31 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305374 | T2 DI DRM-GRSS VLLY-WMR 16/375 RPR GYWW | ICW
LC | 129067662 | 004/050 | T2 DI JOLON TAP 4/50 RPR STRW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-06-12 | 2024-05-20 | 2025-02-03 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46391185 | T2 DI JOLON TAP 4/50 RPR STRW | ICW
LC | 129067734 | B025/570 | T2 DI DRUM-GV-WEI B25/570 RPL STRW | SACTO | ETL.6760.POLE.WOOD | 2024-06-12 | 2024-05-20 | 2025-05-18 | On-Time |  | 2025-05-20 | 2025-05-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573457 | T2 DI DRUM-GV-WEI B25/570 RPL STRW | 70Y
LC | 129067745 | 018/255 | T2 DI KESWICK-TRINITY 18/255 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-06-12 | 2024-05-20 | 2025-04-15 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311177 | T2 DI KESWICK-TRINITY 18/255 RPR JUMW | ICW
LC | 129077136 | 006/123 | T2 HAT CRK #1-WESTWD 6/123 RPL ANCW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-14 | 2024-05-20 | 2025-05-13 | On-Time |  | 2025-05-20 | 2025-05-20 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574744 | T2 DI HAT CRK #1-WESTWD 6/123 RPL ANCW | 93E
LC | 129077251 | B018/415 | T2 DI DRM-GRS VLY-WEMR B18/415 TOUCH | SACTO | ETL.6760.POLE.NWOD | 2024-06-14 | 2024-05-20 | 2025-03-28 | On-Time |  | 2024-11-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46484977 | T2 DI DRM-GRS VLY-WEMR B18/415 TOUCH | ICW
LC | 129078687 | B020/444 | T2 DI DRM-GRS VLLY-WM B20/444 INSP STRW | SACTO | ETL.6760.POLE.WOOD | 2024-06-14 | 2024-05-20 | 2024-10-01 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46324468 | T2 DI DRM-GRS VLLY-WM B20/444 INSP STRW | ICW
LC | 129078915 | 005/083 | T2 DI CENTERVILLE-TBL MT 5/83 RPR CNDW | TABLEMTN | ETL.6320.INSL.NCER | 2024-06-14 | 2024-05-20 | 2025-03-01 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46311200 | T2 DI CENTERVILLE-TBL MT 5/83 RPR CNDW | ICW
LC | 129087747 | 016/364 | T2 DI DRM-GRS VLY-WMR 16/364 RPL TIED | SACTO | ETL.6760.INSL.CERA | 2024-06-17 | 2024-05-20 | 2025-04-23 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Tie Wire-Wood | Replace | 46324474 | T2 DI DRM-GRS VLY-WMR 16/364 RPL TIED | ICW
LC | 129087930 | 015/095 | T2 DI STNLAUS-MLONES SW 015/095 RPL HRDT | VICTOR | ETL.3830.TOWR | 2024-06-17 | 2024-05-20 | 2025-03-24 | On-Time |  | 2025-05-20 | 2025-05-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46416709 | T2 DI STNLAUS-MLONES SW 015/095 RPL HRDT | ICQ
LC | 129088016 | 073/000 | T2 DI HMBLDT TRNTY 73/000 RPL INSW | EUREKA | ETL.1820.INSL.NCER | 2024-06-17 | 2024-05-20 | 2025-04-08 | On-Time |  | 2025-05-20 | 2025-05-20 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574601 | T2 DI HMBLDT TRNTY 73/000 RPL INSW | 93I
LC | 129088153 | 000/018 | T2 DI PLUMAS-SIERRA TAP 0/18 RPR JUMP | TABLEMTN | ETL.6291.INSL.NCER | 2024-06-17 | 2024-05-20 | 2025-01-24 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46389181 | T2 DI PLUMAS-SIERRA TAP 0/18 RPR JUMP | ICW
LC | 129088154 | 000/018 | T2 DI PLUMAS-SIERRA TAP 0/18 RPR HRDW | TABLEMTN | ETL.6291.POLE.WOOD | 2024-06-17 | 2024-05-20 | 2025-01-24 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Missing | Hardware-Wood | Install | 46389182 | T2 DI PLUMAS-SIERRA TAP 0/18 RPR HRDW | ICW
LC | 129088159 | 016/370 | T2 DI DRM-GRS VLY-WMR 016/370 INSP STRW | SACTO | ETL.6760.POLE.WOOD | 2024-06-17 | 2024-05-20 | 2024-10-01 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46324473 | T2 DI DRM-GRS VLY-WMR 016/370 INSP STRW | ICW
LC | 129088237 | 110/000B | T2 DI HUMBOLDT-TRINTY 110/000B RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-17 | 2024-05-20 | 2025-03-08 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345959 | T2 DI HUMBOLDT-TRINTY 110/000B RPR GYWW | ICW
LC | 129088300 | 020/469 | T2 DI DRUM-GRS VLY-WMR 20/469 RPR STRW | SACTO | ETL.6760.POLE.WOOD | 2024-06-17 | 2024-05-20 | 2025-04-21 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46324471 | T2 DI DRUM-GRS VLY-WMR 20/469 RPR STRW | ICW
LC | 129088301 | 020/469 | T2 DI DRUM-GRS VLY-WMR 20/469 RPL HRDD | SACTO | ETL.6760.POLE.WOOD | 2024-06-17 | 2024-05-20 | 2025-04-21 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46324470 | T2 DI DRUM-GRS VLY-WMR 20/469 RPL HRDD | ICW
LC | 129088305 | 110/000A | T2 DI HUMBOLDT-TRINITY 110/0A RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-17 | 2024-05-20 | 2025-03-08 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345958 | T2 DI HUMBOLDT-TRINITY 110/0A RPR GYWW | ICW
LC | 129088333 | 017/388 | T2 DI DRM-GRS VLY-WEIMR 017/388 RPR GYWW | SACTO | ETL.6760.POLE.WOOD | 2024-06-17 | 2024-05-20 | 2025-04-22 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324472 | T2 DI DRM-GRS VLY-WEIMR 017/388 RPR GYWW | ICW
LC | 129088335 | 017/388 | T2 DI DRM-GRS VLY-WEIMR 17/388 RPR IBWW | SACTO | ETL.6760.INSL.NCER | 2024-06-17 | 2024-05-20 | 2025-04-22 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46337424 | T2 DI DRM-GRS VLY-WEIMR 17/388 RPR IBWW | ICW
LC | 129088338 | 015/004 | T2 DI MDCN-WLTS-FRT BRG 015/004 RPR GYWW | WILLITS | ETL.7550.POLE.NWOD | 2024-06-17 | 2024-05-20 | 2025-02-12 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310266 | T2 DI MDCN-WLTS-FRT BRG 015/004 RPR GYWW | ICW
LC | 129088390 | 110/000C | T2 DI HUMBOLDT-TRINITY 110/0C RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-17 | 2024-05-20 | 2025-03-08 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345980 | T2 DI HUMBOLDT-TRINITY 110/0C RPR GYWW | ICW
LC | 129088393 | 018/245 | T2 DI KESWICK-TRINITY 18/245 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-06-17 | 2024-05-20 | 2024-09-14 | On-Time |  | 2024-08-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46269246 | T2 DI KESWICK-TRINITY 18/245 RPR JUMW | ICW
LC | 129088443 | 004/004B | T2 DI HLSDLE JCT-HLF MN BY 4/4B RMV VEG | METCALF | ETL.7060.POLE.WOOD | 2024-06-17 | 2024-05-20 | 2025-04-15 | On-Time |  | 2025-05-20 | 2025-05-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129094835 | 004/072 | T2 DI CNTRVLE-TABLE MTN 4/72 RPR CNDW | TABLEMTN | ETL.6320.INSL.NCER | 2024-06-18 | 2024-05-20 | 2025-03-01 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46311201 | T2 DI CNTRVLE-TABLE MTN 4/72 RPR CNDW | ICW
LC | 129095361 | B020/446 | T2 DI DRUM-GRS VLY-WMR B020/446 RPR INSW | SACTO | ETL.6760.INSL.CERA | 2024-06-18 | 2024-05-20 | 2025-05-18 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46324467 | T2 DI DRUM-GRS VLY-WMR B020/446 RPR INSW | ICW
LC | 129095468 | 073/003 | T2 DI HUMBOLDT-TRIN 73/3C RPR JUMW | EUREKA | ETL.1820.INSL.CERA | 2024-06-18 | 2024-05-20 | 2025-04-08 | On-Time |  | 2024-08-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46271072 | T2 DI HUMBOLDT-TRIN 73/3C RPR JUMW | ICW
LC | 129095520 | 073/003 | T2 DI HUMBOLDT-TRINTY 73/3L RPL HRDD | EUREKA | ETL.1820.POLE.WDPS | 2024-06-18 | 2024-05-20 | 2025-04-08 | On-Time |  | 2025-05-20 | 2025-05-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345956 | T2 DI HUMBOLDT-TRINTY 73/3L RPL HRDD | ICW
LC | 123658484 | 002/024 | T2NT EI PIT #1-COTTONWD 2/24 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2022-05-21 | 2022-05-21 | 2023-08-23 | On-Time |  | 2025-05-21 | 2025-05-21 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45620072 | T2 EI PIT #1-COTTONWOOD 2/24 BNT STEEL | ICQ
LC | 123659091 | 011/093 | T2NT EI PIT #1-COTTONWD 11/93 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2022-05-21 | 2022-05-21 | 2023-09-12 | On-Time |  | 2025-05-21 | 2025-05-21 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45620076 | T2 EI PIT #1-COTTONWOOD 11/093 BNT STEEL | ICQ
LC | 128819861 | 002/021 | T2 COTTONWOOD-DELEVAN #1+ 2/21 COMPLETE | TABLEMTN | ETL.4550.INSL | 2024-05-21 | 2024-05-21 | 2025-04-02 | On-Time |  | 2025-05-21 | 2025-05-21 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570417 | T2 COTTONWOOD-DELEVAN #1+ 2/16 RPL INSS | 93K
LC | 128819863 | 002/021 | T2 COTTONWOOD-LGN CRK 2/21 RPL INSS | TABLEMTN | ETL.4570.INSL | 2024-05-21 | 2024-05-21 | 2025-01-10 | On-Time |  | 2025-05-21 | 2025-05-21 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570418 | T2 COTTONWOOD-LGN CRK 2/21 RPL INSS | 93K
LC | 128820005 | 025/200 | T2 CRSTA-RO OSO 25/200 RMV NEST | TABLEMTN | ETL.4590.TOWR | 2024-05-21 | 2024-05-21 | 2024-05-21 | Past Due |  | 2025-05-21 | 2025-05-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46337332 | T2 EI CRESTA-RIO OSO 27/220 RMV NEST | ICS
LC | 128820185 | 002/016 | T2 COTTONWOOD-DELEVAN #1+ 2/16 RPL INSS | TABLEMTN | ETL.4550.INSL | 2024-05-21 | 2024-05-21 | 2025-04-02 | On-Time |  | 2025-05-21 | 2025-05-21 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570417 | T2 COTTONWOOD-DELEVAN #1+ 2/16 RPL INSS | 93K
LC | 128825489 | C022/087 | T2 EI MOSS LANDING-COBURN C22/87 RMV VEG | MOSSLNDG | ETL.5330.TOWR | 2024-05-21 | 2024-05-21 | 2025-04-23 | On-Time |  | 2025-05-21 | 2025-05-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128826702 | 066/276 | T2 EI RND MTN-TBLE MN #2 66/276 RPL HRDT | TABLEMTN | ETL.6070.TOWR | 2024-05-21 | 2024-05-21 | 2025-03-21 | On-Time |  | 2025-05-21 | 2025-05-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46310390 | T2 EI RND MTN-TBLE MN #2 66/276 RPL HRDT | ICQ
LC | 128826904 | 011/138 | T2 EI DRUM-SUMMIT#2_011/138 RPR INSW | SACTO | ETL.1450.INSL.NCER | 2024-05-21 | 2024-05-21 | 2024-06-18 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46265947 | T2 EI DRUM-SUMMIT#2_011/138 RPR INSW | ICW
LC | 128826905 | 011/138 | T2 EI DRUM-SUMMIT#2_011/138 RPR ANCW | SACTO | ETL.1450.POLE.WDPS | 2024-05-21 | 2024-05-21 | 2024-06-18 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46265945 | T2 EI DRUM-SUMMIT#2_011/138 RPR ANCW | ICW
LC | 128827340 | 007/119 | T2 CORDELIA #1 TAP 007/119 RPL HRDW | LAKEVLLE | ETL.8182.POLE.WOOD | 2024-05-21 | 2024-05-21 | 2025-04-26 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Hardware-Wood | Replace | 46401428 | T2 CORDELIA #1 TAP 007/119 RPL HRDW | ICW
LC | 128829143 | 011/138 | T2 EI DRUM-SUMMIT#2_011/138 RPR ANCW | SACTO | ETL.1450.POLE.WDPS | 2024-05-21 | 2024-05-21 | 2024-06-18 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46265946 | T2 EI DRUM-SUMMIT#2_011/138 RPR ANCW | ICW
LC | 128830137 | 014/092 | T2 CAYUCOS-CAMBRIA 14/092 COMPLETE | PISMOBCH | ETL.8560.INSL.NCER | 2024-05-21 | 2024-05-21 | 2025-05-04 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46391108 | T2 EI CAYUCOS-CAMBRIA 14/092 COTTER | ICW
LC | 128831051 | 011/136 | T2 EI DRUM-SUMMIT#2 11/136L RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-05-21 | 2024-05-21 | 2025-04-24 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458323 | T2 EI DRUM-SUMMIT#2 11/136L RPR GYWW | ICW
LC | 128831720 | 011/136 | T2 EI DRUM-SUMMIT#2 11/136R RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-05-21 | 2024-05-21 | 2025-04-24 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458324 | T2 EI DRUM-SUMMIT#2 11/136R RPR GYWW | ICW
LC | 128834061 | 025/227 | T2 RND MTN-CTNWD #2 25/227 RPR STRT | TABLEMTN | ETL.5640.TOWR | 2024-05-21 | 2024-05-21 | 2024-05-21 | Past Due |  | 2024-11-21 | 2025-05-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478261 | T2 RND MTN-CTNWD #2 25/227 TOUCH | ICQ
LC | 128834318 | 002/043 | T2 HAAS-WOODCHUCK 2/43 RPR JMPW | FRESNO | ETL.8730.INSL.NCER | 2024-05-21 | 2024-05-21 | 2024-05-21 | Past Due |  | 2024-11-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46250583 | T2 EI HAAS-WOODCHUCK 2/43 RPR JMPW | ICW
LC | 128834321 | 022/001 | T2 CLEAR LAKE-KONOCTI 22/1 RPL POLE | WILLITS | ETL.6852.POLE.WOOD | 2024-05-21 | 2024-05-21 | 2024-05-21 | Past Due |  | 2025-05-21 | 2025-05-21 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572507 | T2 EI CLEAR LAKE-KONOCTI 22/1 RPL POLE | 70Y
LC | 128834488 | 005/094 | T2 EI SQC-SNTA YNZ SW ST 05/94 RPL HRDW | PISMOBCH | ETL.3700.POLE.WOOD | 2024-05-21 | 2024-05-21 | 2025-04-03 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46391104 | T2 EI SQC-SNTA YNZ SW ST 05/94 RPL HRDW | ICW
LC | 128834910 | C021/084 | T2 EI MSS LANDING-COBURN C21/84 RMV NEST | MOSSLNDG | ETL.5330.TOWR | 2024-05-21 | 2024-05-21 | 2025-02-05 | On-Time |  | 2025-05-21 | 2025-05-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46391178 | T2 EI MSS LANDING-COBURN C21/84 RMV NEST | ICS
LC | 128835051 | 023/112 | T2 EI MTCLF-MNTA VSTA #3 23/112 COTTER | MOSSLNDG | ETL.5091.INSL.NCER | 2024-05-21 | 2024-05-21 | 2025-03-21 | On-Time |  | 2025-05-21 | 2025-05-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46391295 | T2 EI MTCLF-MNTA VSTA #3 23/112 COTTER | ICS
LC | 128835171 | 016/077 | T2 EI MOSS LANDING-CBRN 16/77 RMV ENCRCH | MOSSLNDG | ETL.5330.TOWR | 2024-05-21 | 2024-05-21 | 2024-08-13 | On-Time |  | 2024-11-21 | 2025-05-21 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Encroachment | Right of Way | Remove | 46298790 | T2 EI MOSS LANDING-CBRN 16/77 RMV ENCRCH | CHR
LC | 128835639 | 066/275 | T2 EI RND MTN-TBL MTN #1 66/275 UNBURY | TABLEMTN | ETL.6060.TOWR | 2024-05-21 | 2024-05-21 | 2025-02-21 | On-Time |  | 2025-05-21 | 2025-05-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46310389 | T2 EI RND MTN-TBL MTN #1 66/275 UNBURY | ICQ
LC | 128835680 | 066/275 | T2 EI RND MTN-TBL MTN #1 66/275 RPR INSS | TABLEMTN | ETL.6060.INSL | 2024-05-21 | 2024-05-21 | 2025-01-22 | On-Time |  | 2025-05-21 | 2025-05-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46306297 | T2 EI RND MTN-TBL MTN #1 66/275 RPR INSS | ICS
LC | 128835792 | 014/065 | T2 EI SN LS OBSPO-OCNO 14/65 RMV VEG | PISMOBCH | ETL.3530.TOWR | 2024-05-21 | 2024-05-21 | 2025-05-20 | On-Time |  | 2025-05-21 | 2025-05-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO CLMB FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128836600 | 014/074 | T2 EI RND MTN-TBL MTN #1 14/74 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-21 | 2024-05-21 | 2025-05-06 | On-Time |  | 2025-05-21 | 2025-05-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128836601 | 015/078 | T2 EI RND MTN-TBL MTN #1 015/078 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-21 | 2024-05-21 | 2025-02-05 | On-Time |  | 2025-05-21 | 2025-05-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128836883 | 022/108 | T2 EI MNTA VISTA-CYT SS 23/108 RMV VEG | MOSSLNDG | ETL.5090.TOWR | 2024-05-21 | 2024-05-21 | 2025-04-24 | On-Time |  | 2025-05-21 | 2025-05-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128836896 | 023/110 | T2 EI MONTA VSTA-COYOTE SS 23/110 MASTIC | MOSSLNDG | ETL.5090.TOWR | 2024-05-21 | 2024-05-21 | 2025-05-02 | On-Time |  | 2025-05-21 | 2025-05-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416639 | T2 EI MONTA VSTA-COYOTE SS 23/110 MASTIC | ICQ
LC | 128836950 | 022/108 | T2 EI MNTA VSTA-COYOTE SS 22/108 MASTIC | MOSSLNDG | ETL.5090.TOWR | 2024-05-21 | 2024-05-21 | 2025-05-02 | On-Time |  | 2025-05-21 | 2025-05-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416700 | T2 EI MNTA VSTA-COYOTE SS 22/108 MASTIC | ICQ
LC | 128836951 | 022/108 | T2 EI MNTA VST-COYOTE SS 22/108 COMPLETE | MOSSLNDG | ETL.5090.INSL.CERA | 2024-05-21 | 2024-05-21 | 2024-08-02 | On-Time |  | 2024-08-21 | 2025-05-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46266161 | T2 EI MNTA VSTA-COYOTE SS 22/108 COTTER | ICS
LC | 128837018 | 005/097 | T2 EI SQC-SNTA YNZ SW ST 05/97 RPR GYWW | PISMOBCH | ETL.3700.POLE.WOOD | 2024-05-21 | 2024-05-21 | 2025-04-03 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391105 | T2 EI SQC-SNTA YNZ SW ST 05/97 RPR GYWW | ICW
LC | 128837204 | 010/087 | T2 EI CRESTA-RIO OSO 010/087 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-21 | 2024-05-21 | 2025-03-24 | On-Time |  | 2025-05-21 | 2025-05-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381334 | T2 EI CRESTA-RIO OSO 010/087 RPR FOND | ICQ
LC | 128837209 | 001/010 | T2 EI SN LS OBSPO-SNT MRA 1/10 RPL INSS | PISMOBCH | ETL.3540.INSL.CERA | 2024-05-21 | 2024-05-21 | 2025-05-29 | Past Due |  | 2025-05-21 | 2025-05-21 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 31528665 | DI SN LS OBSPO-SNT MARIA 25/135 RPL INSS | 93K
LC | 128837220 | 011/089 | T2 EI CRESTA-RIO OSO 011/089 RPL INSS | TABLEMTN | ETL.4590.INSL.CERA | 2024-05-21 | 2024-05-21 | 2025-05-01 | On-Time |  | 2025-05-21 | 2025-05-21 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570419 | T2 EI CRESTA-RIO OSO RPL INSS | 93K
LC | 128837260 | 065/328 | T2 EI MALIN-ROUND MTN #2 65/328 RPR ANCT | TABLEMTN | ETL.6020.TOWR | 2024-05-21 | 2024-05-21 | 2025-04-11 | On-Time |  | 2025-05-21 | 2025-05-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46381446 | T2 EI MALIN-ROUND MTN #2 65/328 RPR ANCT | ICQ
LC | 128837303 | 034/001 | T2 DI MENDOCINO-WFB 34/1 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-21 | 2024-05-21 | 2025-03-05 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310267 | T2 DI MENDOCINO-WFB 34/1 RPR GYWW | ICW
LC | 128837309 | 034/001 | T2 MENDOCINO-WFB 34/1 RPL HRDD | WILLITS | ETL.7550.POLE.WOOD | 2024-05-21 | 2024-05-21 | 2024-05-21 | Past Due |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE SPCR ACCL OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace
LC | 128837312 | 034/001 | T2 DI MENDOCINO-WFB 34/1 RMV VEG | WILLITS | ETL.7550.POLE.WOOD | 2024-05-21 | 2024-05-21 | 2024-09-17 | On-Time |  | 2024-11-21 | 2025-05-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE SPCR ACCL COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128886969 | 043/288C | T2 DI TRINITY-COTTONWD 43/288C RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-05-24 | 2024-05-21 | 2024-08-17 | On-Time |  | 2024-08-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262792 | T2 DI TRINITY-COTTONWD 43/288C RPR JUMW | ICW
LC | 128887056 | 013/168A | T2 DI KESWICK-TRINITY-13/168A RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-24 | 2024-05-21 | 2024-09-14 | On-Time |  | 2024-08-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46253259 | T2 DI KESWICK-TRINITY-13/168A RPR JUMW | ICW
LC | 128887059 | 013/168A | T2 DI KESWICK-TRINITY-13/168A RPR GYWW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-24 | 2024-05-21 | 2024-09-14 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311174 | T2 DI KESWICK-TRINITY-13/168A RPR GYWW | ICW
LC | 128887367 | 013/168B | T2 DI KESWCK-TRINITY-13/168B RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-24 | 2024-05-21 | 2024-09-14 | On-Time |  | 2024-08-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46253261 | T2 DI KESWCK-TRINITY-13/168B RPR JUMW | ICW
LC | 128887402 | 014/095 | T2 DI MILLBRAE-SNTH LANE 14/95 RPR INSS | METCALF | ETL.7570.INSL.NCER | 2024-05-24 | 2024-05-21 | 2024-10-08 | On-Time |  | 2024-08-21 | 2025-05-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46255135 | T2 DI MILLBRAE-SNTH LANE 14/95 COTTER | ICS
LC | 128887508 | 013/168C | T2 DI KESWCK-TRINITY 13/168C RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-24 | 2024-05-21 | 2024-09-14 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311173 | T2 DI KESWCK-TRINITY 13/168C RPR JUMW | ICW
LC | 128888544 | 001/044 | T2 DI COTTONWD-BENTON #1 1/44 RPL STRW | TABLEMTN | ETL.6640.POLE.WOOD | 2024-05-24 | 2024-05-21 | 2025-05-07 | On-Time |  | 2025-05-21 | 2025-05-21 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572989 | T2 DI COTTONWD-BENTON #1 1/44 RPL STRW | 70Y
LC | 128888637 | 043/288B | T2 DI TRINITY-COTTONWD 43/288B RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-05-24 | 2024-05-21 | 2024-08-18 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46305290 | T2 DI TRINITY-COTTONWD 43/288B RPR JUMW | ICW
LC | 129036285 | 005/099 | T2 DI SAN MATEO-HDL JCT 5/99C RPR ANCW | METCALF | ETL.7950.POLE.WDPS | 2024-06-07 | 2024-05-21 | 2025-02-26 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Anchor-Wood | Repair | 46286867 | T2 DI SAN MATEO-HDL JCT 5/99C RPR ANCW | ICW
LC | 129036425 | 002/059 | T2 DI CTTNWD-BNTN #1 2/59 RPR STRW | TABLEMTN | ETL.6640.POLE.WOOD | 2024-06-07 | 2024-05-21 | 2025-05-08 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46463716 | T2 DI CTTNWD-BNTN #1 2/59 RPR STRW | ICW
LC | 129036619 | 000/022 | T2 DI CTTNWD-BNTN #1 0/22 RPR STRW | TABLEMTN | ETL.6640.POLE.WOOD | 2024-06-07 | 2024-05-21 | 2025-04-28 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46463717 | T2 DI CTTNWD-BNTN #1 0/22 RPR STRW | ICW
LC | 129036629 | 014/339 | T2 DI CTTNWD-BNTN #1 14/339 RPL INSW | TABLEMTN | ETL.6640.INSL.CERA | 2024-06-07 | 2024-05-21 | 2025-04-28 | On-Time |  | 2025-05-21 | 2025-05-21 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572990 | T2 DI CTTNWD-BNTN #1 14/339 RPL INSW | 93I
LC | 129077387 | 001/022D | T2 DI MTN QUARR TP 1/22D RPL MRKB | SACTO | ETL.6991.MKBL | 2024-06-14 | 2024-05-21 | 2025-03-19 | On-Time |  | 2025-05-21 | 2025-05-21 | 671T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | FAA Lighting-Steel | Replace | 35542519 | T2 MTN QUARRIES TAP 001/021D RPL MKBL | 93P
LC | 129077477 | 007/113 | T2 DI CENTRVLE-TABLE MTN 7/113 RPL STRW | TABLEMTN | ETL.6320.POLE.WOOD | 2024-06-14 | 2024-05-21 | 2025-03-02 | On-Time |  | 2025-05-21 | 2025-05-21 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572383 | T2 DI CNTRVL-TABLE MTN 07/113 RPL STRW | 70Y
LC | 129077760 | :012/000 | T2 DI EAGLE ROCK-CORTINA :12/0 TOUCH | WILLITS | ETL.1470.POLE.NWOD | 2024-06-14 | 2024-05-21 | 2025-04-01 | On-Time |  | 2024-11-21 | 2025-05-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Steel | Repair | 46493186 | T2 DI EAGLE ROCK-CORTINA :12/0 TOUCH | ICS
LC | 129078542 | 003/068 | T2 DI COTTONWOOD-BENTON #1 3/68 BACKFILL | TABLEMTN | ETL.6640.POLE.NWOD | 2024-06-14 | 2024-05-21 | 2025-04-28 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAR | Debris/Nest/etc. | Structure-Wood | Remove | 46463718 | T2 DI COTTONWOOD-BENTON #1 3/68 BACKFILL | ICW
LC | 129078558 | 006/100 | T2 DI CENTRVILE-TABLE MTN 6/100 RPL STRW | TABLEMTN | ETL.6320.POLE.WOOD | 2024-06-14 | 2024-05-21 | 2025-03-03 | On-Time |  | 2025-05-21 | 2025-05-21 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572382 | T2 DI CNTRVIL-TABLE MTN 06/100 RPL STRW | 70Y
LC | 129078591 | 007/114 | T2 DI CENTERVL-TBL MTN 7/114 RPL STRW | TABLEMTN | ETL.6320.POLE.WOOD | 2024-06-14 | 2024-05-21 | 2025-03-02 | On-Time |  | 2025-05-21 | 2025-05-21 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572383 | T2 DI CNTRVL-TABLE MTN 07/113 RPL STRW | 70Y
LC | 129079272 | 006/097 | T2 DI CNTRVLLE-TBL MTN 6/97 TOUCH | TABLEMTN | ETL.6320.POLE.NWOD | 2024-06-14 | 2024-05-21 | 2025-02-24 | On-Time |  | 2024-08-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46472109 | T2 DI CNTRVLLE-TBL MTN 6/97 TOUCH | ICW
LC | 129087419 | 007/054 | T2 DI MORAGA-SAN LNDRO #1 7/54 RPL HRDT | CONCORD | ETL.2770.TOWR | 2024-06-17 | 2024-05-21 | 2025-01-15 | On-Time |  | 2025-05-21 | 2025-05-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289328 | T2 DI MORAGA-SAN LNDRO #1 7/54 RPL HRDT | ICQ
LC | 129087752 | 009/076 | T2 DI CARIBOU-PALERMO 09/76 RPR STRT | TABLEMTN | ETL.3190.TOWR | 2024-06-17 | 2024-05-21 | 2025-03-25 | On-Time |  | 2025-05-21 | 2025-05-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46452744 | T2 DI CARIBOU-PALERMO 09/76 RPR STRT | ICQ
LC | 129095355 | 004/044B | T2 DI HLSDL HALF MN BAY 04/44B RMV VEG | METCALF | ETL.7060.POLE.WOOD | 2024-06-18 | 2024-05-21 | 2024-06-20 | On-Time |  | 2024-11-21 | 2025-05-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 129095371 | 004/044A | T2 DI HLSDL HALF MN BAY 04/44A RMV VEG | METCALF | ETL.7060.POLE.WOOD | 2024-06-18 | 2024-05-21 | 2024-11-13 | On-Time |  | 2024-11-21 | 2025-05-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 129095440 | 002/047 | T2 DI COTTONWD-BENTON #1 2/47 TOUCH | TABLEMTN | ETL.6640.POLE.NWOD | 2024-06-18 | 2024-05-21 | 2025-04-30 | On-Time |  | 2024-11-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46486745 | T2 DI COTTONWD-BENTON #1 2/47 TOUCH | ICW
LC | 129105173 | 004/044C | T2 DI HILLSDALE JT-HMB 4/44C RMV VEG | METCALF | ETL.7060.POLE.WOOD | 2024-06-20 | 2024-05-21 | 2024-11-13 | On-Time |  | 2024-11-21 | 2025-05-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 129105178 | 004/044C | T2 DI HILLSDALE JT-HMB 4/44C RPR GYWW | METCALF | ETL.7060.POLE.WOOD | 2024-06-20 | 2024-05-21 | 2025-02-18 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286761 | T2 DI HILLSDALE JT-HMB 4/44C RPR GYWW | ICW
LC | 129120691 | 018/428 | T2 DI DRUM-GV-WEI 18/428 RPR STRW | SACTO | ETL.6760.POLE.WOOD | 2024-06-24 | 2024-05-21 | 2025-03-11 | On-Time |  | 2025-05-21 | 2025-05-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46477802 | T2 DI DRUM-GV-WEI 18/428 RPR STRW | ICW
LC | 129120976 | ;000/005 | T2 DI SNTH LN-HLF MN BAY ;00/05 RPL INSS | METCALF | ETL.7212.INSL.NCER | 2024-06-24 | 2024-05-21 | 2025-06-17 | Past Due |  | 2025-05-21 | 2025-05-21 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573716 | T2 DI SNTH LN-HLF MN BAY ;00/05 RPL INSS | 93I
LC | 129120978 | ;000/005 | T2 DI SNTH LN-HLF MN BAY ;00/05 RMV VEG | METCALF | ETL.7212.POLE.WOOD | 2024-06-24 | 2024-05-21 | 2025-04-17 | On-Time |  | 2025-05-21 | 2025-05-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW ACCH COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129121266 | 073/372 | T2 DI MALIN-ROUND MTN#2 73/372 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-06-24 | 2024-05-21 | 2025-04-03 | On-Time |  | 2025-05-21 | 2025-05-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46338277 | T2 DI MALIN-ROUND MTN#2 73/372 RPR OPGW | ICS
LC | 131054596 | 011/138 | T2 DRUM-SUMMIT #2 11/138R RPL STRW | SACTO | ETL.1450.POLE.WDPS | 2025-04-07 | 2024-05-21 | 2024-05-21 | Past Due |  | 2025-05-21 | 2025-05-21 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35631087 | T2 DRUM-SUMMIT #2 11/138R RPL STRW | 70Y
LC | 131054680 | 011/138 | T2 DRUM-SUMMIT #2 11/138C RPL STRW | SACTO | ETL.1450.POLE.WDPS | 2025-04-07 | 2024-05-21 | 2025-06-27 | Past Due |  | 2025-05-21 | 2025-05-21 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35631087 | T2 DRUM-SUMMIT #2 11/138R RPL STRW | 70Y
LC | 128837590 | 000/001 | T2 PIT #3-CARBERRY SW STA 0/1 RPR STRT | TABLEMTN | ETL.5450.TOWR | 2024-05-22 | 2024-05-22 | 2024-05-22 | Past Due |  | 2024-11-22 | 2025-05-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491540 | T2 PIT #3-CARBERRY SW STA 00/01 TOUCH | ICQ
LC | 128838178 | 011/063 | T2 EI RND MTN-TBL MTN #1 11/63 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-22 | 2024-05-22 | 2025-03-13 | On-Time |  | 2025-05-22 | 2025-05-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128838226 | 003/065 | T2 EI COLEMAN-COTTONWD 3/65 RPR STRW | TABLEMTN | ETL.6430.POLE.WOOD | 2024-05-22 | 2024-05-22 | 2025-03-04 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46383864 | T2 EI COLEMAN-COTTONWD 3/65 RPR STRW | ICW
LC | 128838554 | 010/126C | T2 EI DRUM-SUMMIT #2 010/126C RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-05-22 | 2024-05-22 | 2024-06-26 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46283422 | T2 EI DRUM-SUMMIT #2 010/126C RPR GYWW | ICW
LC | 128838748 | 010/126A | T2 EI DRUM-SUMMIT #2 010/126A RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-05-22 | 2024-05-22 | 2024-06-26 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46273594 | T2 EI DRUM-SUMMIT #2 010/126A RPR GYWW | ICW
LC | 128838907 | 007/174 | T2 DRUM-SPAULDING 7/174 RPR STRW | SACTO | ETL.6770.POLE.WOOD | 2024-05-22 | 2024-05-22 | 2025-05-20 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337356 | T2 EI DRUM-SPAULDING 007/174 RPR POLE | ICW
LC | 128839729 | 003/064 | T2 HAAS-WOODCHUCK 03/64 RPR JMPW | FRESNO | ETL.8730.INSL.NCER | 2024-05-22 | 2024-05-22 | 2024-05-22 | Past Due |  | 2024-08-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO PGEQ DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46268420 | T2 HAAS-WOODCHUCK 03/64 RPR JMPW | ICW
LC | 128840054 | 017/212 | T2 EI DRUM-SUMMIT#2 17/212L RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-05-22 | 2024-05-22 | 2024-06-24 | On-Time |  | 2024-11-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46273385 | T2 EI DRUM-SUMMIT#2 17/212L RPR GYWW | ICW
LC | 128840076 | 017/212 | T2 EI DRUM-SUMMIT#2 17/212R RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-05-22 | 2024-05-22 | 2024-06-24 | On-Time |  | 2024-11-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46273384 | T2 EI DRUM-SUMMIT#2 17/212R RPR GYWW | ICW
LC | 128840123 | 009/040 | T2 EI MONTA VSTA-JFFRSN #2 9/40 RPL INSS | METCALF | ETL.5230.INSL | 2024-05-22 | 2024-05-22 | 2025-01-07 | On-Time |  | 2025-05-22 | 2025-05-22 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574632 | T2 MONTA VISTA-JEFFRSN #2 RPL INSS IN 2T | 93K
LC | 128840209 | 058/247 | T2 EI RND MTN-TBL MTN #1 58/247 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-05-22 | 2024-05-22 | 2025-01-25 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306298 | T2 EI RND MTN-TBL MTN #1 58/247 RMV NEST | ICS
LC | 128840689 | 004/008 | T2 MENDOCINO-UKIAH 04/008 RPR INSW | WILLITS | ETL.2420.INSL.NCER | 2024-05-22 | 2024-05-22 | 2024-05-22 | Past Due |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46340267 | T2 MENDOCINO-UKIAH 04/008 RPR INSW | ICW
LC | 128841480 | 015/067 | T2 EI MORO BAY-SLR SS #1 15/67 RPL INSS | PISMOBCH | ETL.5300.INSL | 2024-05-22 | 2024-05-22 | 2025-04-08 | On-Time |  | 2025-05-22 | 2025-05-22 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35583345 | T0 EI MORRO BAY-SOLAR SS#1 REP INS 6 LST | 93K
LC | 128841481 | 015/067 | T2 EI MORO BAY-SLR SS #2 15/67 RPL INSS | PISMOBCH | ETL.5310.INSL | 2024-05-22 | 2024-05-22 | 2024-05-22 | Past Due |  | 2025-05-22 | 2025-05-22 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577375 | T0 EI MORRO BAY-SOLAR SS#2 42/180 RPLC I | 93K
LC | 128841629 | 038/166 | T2 EI CBRN-LS AGUILAS SS 38/166 RMV NEST | MOSSLNDG | ETL.4460.TOWR | 2024-05-22 | 2024-05-22 | 2025-02-23 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46391179 | T2 EI CBRN-LS AGUILAS SS 38/166 RMV NEST | ICS
LC | 128841685 | 038/164 | T2 EI CBRN-LS AGUILAS SS 38/164 RMV NEST | MOSSLNDG | ETL.4460.TOWR | 2024-05-22 | 2024-05-22 | 2025-02-23 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46391180 | T2 EI CBRN-LS AGUILAS SS 38/164 RMV NEST | ICS
LC | 128841741 | 001/012 | T2 EI BUTT VALLEY-CARIBOU 1/012 RPR SHLS | TABLEMTN | ETL.1180.TOWR | 2024-05-22 | 2024-05-22 | 2025-04-02 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46337333 | T2 EI BUTT VALLEY-CARIBOU 1/012 RPR SHLD | ICS
LC | 128841746 | 002/018 | T2 EI BUTT VALLEY-CARIBOU 2/018 RPR STRT | TABLEMTN | ETL.1180.TOWR | 2024-05-22 | 2024-05-22 | 2025-03-21 | On-Time |  | 2025-05-22 | 2025-05-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354035 | T2 EI BUTT VALLEY-CARIBOU 2/018 RPR STRT | ICQ
LC | 128841779 | 011/061 | T2 EI RND MTN-TBL MTN #2 11/61 RPR ANCT | TABLEMTN | ETL.6070.TOWR | 2024-05-22 | 2024-05-22 | 2025-04-16 | On-Time |  | 2025-05-22 | 2025-05-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46382004 | T2 EI RND MTN-TBL MTN #2 11/61 RPR ANCT | ICQ
LC | 128841792 | 000/001 | T2 BCKS CRK-RCK CRK-CRSTA 0/1 RPR INSS | TABLEMTN | ETL.4430.INSL.NCER | 2024-05-22 | 2024-05-22 | 2025-05-16 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329286 | T2 EI BKS CRK-RCK CRK-CTA 00/01 RPR INSS | ICS
LC | 128841805 | 072/365 | T2 EI MALIN-RUND MTN #2 072/365 RPR INSS | TABLEMTN | ETL.6020.INSL.NCER | 2024-05-22 | 2024-05-22 | 2025-02-09 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46338263 | T2 EI MALIN-RUND MTN #2 072/365 RPR INSS | ICS
LC | 128841810 | 072/365 | T2 EI MALIN-RUND MTN #2 072/365 RPL SPCR | TABLEMTN | ETL.6020.INSL.NCER | 2024-05-22 | 2024-05-22 | 2025-02-09 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB | No Good/Out of Stdrd | Spacer-Steel | Replace | 46338264 | T2 EI MALIN-RUND MTN #2 072/365 RPL SPCR | ICS
LC | 128841823 | 011/059 | T2 EI RND TBL MTN#1 11/59 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-05-22 | 2024-05-22 | 2025-01-28 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306299 | T2 EI RND TBL MTN#1 11/59 RMV NEST | ICS
LC | 128841827 | 011/062 | T2 EI RND MTN-TBL MTN #1 11/62 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-22 | 2024-05-22 | 2025-03-12 | On-Time |  | 2025-05-22 | 2025-05-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128841855 | 011/062 | T2 EI RND MTN-TABLE MTN #2 11/62 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2024-05-22 | 2024-05-22 | 2025-02-24 | On-Time |  | 2025-05-22 | 2025-05-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128841857 | 011/060 | T2 EI RND MTN-TBL MTN #1 11/60 RPR ANCT | TABLEMTN | ETL.6060.TOWR | 2024-05-22 | 2024-05-22 | 2025-04-16 | On-Time |  | 2025-05-22 | 2025-05-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46382005 | T2 EI RND MTN-TBL MTN #1 11/60 RPR ANCT | ICQ
LC | 128841860 | 011/060 | T2 EI RND MTN-TBL MTN #1 11/60 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-05-22 | 2024-05-22 | 2025-01-28 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306300 | T2 EI RND MTN-TBL MTN #1 11/60 RMV NEST | ICS
LC | 128841861 | 011/063 | T2 EI RND MTN-TABLE MTN #2 11/63 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2024-05-22 | 2024-05-22 | 2025-02-24 | On-Time |  | 2025-05-22 | 2025-05-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128841871 | 011/061 | T2 EI RND MTN-TBL MTN #1 11/61 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-05-22 | 2024-05-22 | 2025-01-28 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306301 | T2 EI RND MTN-TBL MTN #1 11/61 RMV NEST | ICS
LC | 128841872 | 011/061 | T2 EI RND MTN-TBL MTN #1 11/61 RPR ANCT | TABLEMTN | ETL.6060.TOWR | 2024-05-22 | 2024-05-22 | 2025-04-16 | On-Time |  | 2025-05-22 | 2025-05-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46382007 | T2 EI RND MTN-TBL MTN #1 11/61 RPR ANCT | ICQ
LC | 128841893 | 008/093A | T2 EI DRUM-SUMMIT #1 8/093A RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-05-22 | 2024-05-22 | 2025-04-22 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46397993 | T2 EI DRUM-SUMMIT #1 8/093A RPR GYWW | ICW
LC | 128842363 | 011/058 | T2 EI RND MTN-TBL MTN #2 11/58 RMV NEST | TABLEMTN | ETL.6070.TOWR | 2024-05-22 | 2024-05-22 | 2025-01-28 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306302 | T2 EI RND MTN-TBL MTN #2 11/58 RMV NEST | ICS
LC | 128842364 | C020/081 | T2 EI MSS LANDING-COBURN C20/81 RMV NEST | MOSSLNDG | ETL.5330.TOWR | 2024-05-22 | 2024-05-22 | 2025-02-05 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46391181 | T2 EI MSS LANDING-COBURN C20/81 RMV NEST | ICS
LC | 128842587 | 052/1021 | T2 EI HAT CRK #1-WESTWD 52/1021 INS DMPW | TABLEMTN | ETL.7030.INSL | 2024-05-23 | 2024-05-22 | 2025-03-28 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46416035 | T2 EI HAT CRK #1-WESTWD 52/1021 INS DMPW | ICW
LC | 128885490 | 011/091 | T2 EI CRESTA-RIO OSO 11/091 RPL INSS | TABLEMTN | ETL.4590.INSL.CERA | 2024-05-23 | 2024-05-22 | 2025-05-02 | On-Time |  | 2025-05-22 | 2025-05-22 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570419 | T2 EI CRESTA-RIO OSO RPL INSS | 93K
LC | 128887107 | 018/258 | T2 DI KESWICK-TRINITY 18/258 COTTER | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-24 | 2024-05-22 | 2025-04-11 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46311172 | T2 DI KESWICK-TRINITY 18/258 COTTER | ICW
LC | 128888849 | 000/015 | T2 DI COLGATE CHALENGE 0/15 RPR JUMW | SACTO | ETL.6480.INSL.NCER | 2024-05-24 | 2024-05-22 | 2024-08-25 | On-Time |  | 2024-08-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262796 | T2 DI COLGATE CHALENGE 0/15 RPR JUMW | ICW
LC | 128888860 | 219 | T2 DI PIT #3-PIT #1 00/01 RPR JUMS | TABLEMTN | ETL.5400.SWIT | 2024-05-24 | 2024-05-22 | 2025-02-10 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46382478 | T2 DI PIT #3-PIT #1 00/01 RPR JUMS | ICS
LC | 128888865 | 066/001 | T2 DI HUMBOLDTD-TRIN 66/1C RPR HRDW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-24 | 2024-05-22 | 2024-08-28 | On-Time |  | 2024-08-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace | 46254661 | T2 DI HUMBOLDTD-TRIN 66/1C RPR HRDW | ICW
LC | 128888866 | 000/001 | T2 DI PIT #3-PIT #1 00/01 RPL HRDT | TABLEMTN | ETL.5400.TOWR | 2024-05-24 | 2024-05-22 | 2025-04-23 | On-Time |  | 2025-05-22 | 2025-05-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46382009 | T2 DI PIT #3-PIT #1 00/01 RPL HRDT | ICQ
LC | 128888877 | 066/001 | T2 DI HUMBOLDT-TRINITY 66/1 RPR INSW | EUREKA | ETL.1820.INSL.CERA | 2024-05-24 | 2024-05-22 | 2025-04-09 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46345985 | T2 DI HUMBOLDT-TRINITY 66/1 RPR INSW | ICW
LC | 128888932 | 023/005 | T2 DI MNDCN WLTS FRT BRG 23/5 GY COTTER | WILLITS | ETL.7550.POLE.NWOD | 2024-05-24 | 2024-05-22 | 2024-10-23 | On-Time |  | 2024-11-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46254723 | T2 DI MNDCN WLTS FRT BRG 23/5 GY COTTER | ICW
LC | 128888991 | 066/001X | T2 DI HUMBOLDT-TRNTY 66/01X RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-05-24 | 2024-05-22 | 2024-08-28 | On-Time |  | 2024-08-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262164 | T2 DI HUMBOLDT-TRNTY 66/01X RPR JUMW | ICW
LC | 128888995 | 066/001X | T2 DI HUMBOLDT-TRNTY 66/01XC RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-24 | 2024-05-22 | 2024-08-28 | On-Time |  | 2024-11-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46254663 | DI HUMBOLDT-TRNTY 66/01XC RPR GYWW | ICW
LC | 128889057 | 000/004 | T2 DI HAMLTN BRNCH-CHSTR 00/04 COMPLETE | TABLEMTN | ETL.7000.INSL.NCER | 2024-05-24 | 2024-05-22 | 2024-07-29 | On-Time |  | 2024-08-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46253267 | T2 DI HAMLTN BRNCH-CHSTR 00/04 RPR JUMW | ICW
LC | 129016006 | 028/000 | T2 DI MNDCNO-WLTS-FRT BRG 28/0 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-06-03 | 2024-05-22 | 2024-10-09 | On-Time |  | 2024-11-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46264539 | T2 DI MNDCNO-WLTS-FRT BRG 28/0 RPR GYWW | ICW
LC | 129016020 | 028/000 | T2 DI MNDCNO-WLTS-FRT BRG 28/0 RPR IBWW | WILLITS | ETL.7550.INSL.NCER | 2024-06-03 | 2024-05-22 | 2025-04-03 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46310269 | T2 DI MNDCNO-WLTS-FRT BRG 28/0 RPR IBWW | ICW
LC | 129026156 | 002/032 | T2 DI COLGATE-PALERMO 2/32 RPR IBWW | SACTO | ETL.6500.INSL.NCER | 2024-06-05 | 2024-05-22 | 2025-05-03 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46383056 | T2 DI COLGATE-PALERMO 2/32 RPR IBWW | ICW
LC | 129026341 | 002/030 | T2 DI COLGATE-PALERMO 02/30 RPR IBWW | SACTO | ETL.6500.INSL.NCER | 2024-06-05 | 2024-05-22 | 2025-05-03 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46383057 | T2 DI COLGATE-PALERMO 02/30 RPR IBWW | ICW
LC | 129055036 | 014/288 | T2 HAT CRK#1-WSTWOOD 14/288 RPR STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-10 | 2024-05-22 | 2025-05-02 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46416132 | T2 DI HAT CRK#1-WSTWOOD 14/288 RPR STRW | ICW
LC | 129055228 | 006/148 | T2 DI HMLTN BRNCH-CHSTR 06/148 RPR STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-06-10 | 2024-05-22 | 2025-01-09 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311130 | T2 DI HMLTN BRNCH-CHSTR 06/148 RPR STRW | ICW
LC | 129061182 | 007/087 | T2 DI JOLON TAP 7/87 RPL STRW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-06-11 | 2024-05-22 | 2025-01-17 | On-Time |  | 2025-05-22 | 2025-05-22 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573684 | T2 DI JOLON TAP 7/87 RPL STRW | 70Y
LC | 129061255 | 008/004 | T2 MENDOCINO HARTLEY 8/4 RPL INSW | WILLITS | ETL.7510.INSL.NCER | 2024-06-11 | 2024-05-22 | 2024-05-22 | Past Due |  | 2025-05-22 | 2025-05-22 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35560425 | T2 DI MENDOCINO HARTLEY 8/4 RPL INSW | 93I
LC | 129061934 | 006/083 | T2NT DI JOLON TAP 6/83 RMV VEG | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-06-11 | 2024-05-22 | 2025-01-02 | On-Time |  | 2027-05-22 | 2025-05-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129078974 | 000/013 | T2 DI COLGATE-CHALLENGE 0/13 RPR INSW | SACTO | ETL.6480.INSL.CERA | 2024-06-14 | 2024-05-22 | 2025-04-06 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46337357 | T2 DI COLGATE-CHALLENGE 0/13 RPR INSW | ICW
LC | 129087604 | 002/031 | T2 DI CLGTE PLMRO 02/031 RPR STRW | SACTO | ETL.6500.POLE.WOOD | 2024-06-17 | 2024-05-22 | 2025-05-03 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46397999 | T2 DI CLGTE PLMRO 02/031 RPR STRW | ICW
LC | 129087877 | 014/274 | T2 DI HAT CREEK #1-WSTWD 14/274 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-17 | 2024-05-22 | 2025-05-17 | On-Time |  | 2025-05-22 | 2025-05-22 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574751 | T2 DI HAT CREEK #1-WSTWD 14/274 RPL STRW | 70Y
LC | 129087968 | :000/001 | T2 DI PIT #3-PIT #1 :0/1 RPR STRT | TABLEMTN | ETL.5400.TOWR | 2024-06-17 | 2024-05-22 | 2025-04-23 | On-Time |  | 2025-05-22 | 2025-05-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46382051 | T2 DI PIT #3-PIT #1 :0/1 RPR STRT | ICQ
LC | 129088037 | 040/173 | T2 DI GEYSERS #9-LAKEVIL 40/173 RPR INSS | LAKEVLLE | ETL.4780.INSL | 2024-06-17 | 2024-05-22 | 2025-04-21 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46403755 | T2 DI GEYSERS #9-LAKEVIL 40/173 RPR INSS | ICS
LC | 129088105 | 018/265 | T2 DI KESWICK-TRIN 18/265 RPL HRDD | TABLEMTN | ETL.7270.POLE.NWOD | 2024-06-17 | 2024-05-22 | 2025-04-13 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46311171 | T2 DI KESWICK-TRIN 18/265 RPL HRDD | ICW
LC | 129088174 | ;000/002 | T2 DI SNTH LN-HLF MN BY 0/2L RPL HRDD | METCALF | ETL.7212.POLE.WDPS | 2024-06-17 | 2024-05-22 | 2025-06-16 | Past Due |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Hardware-Wood | Replace | 46286768 | T2 DI SNTH LN-HLF MN BY 0/2L RPL HRDD | ICW
LC | 129088176 | ;000/002 | T2 DI SNTH LN-HLF MN BY 0/2 RPL INSW | METCALF | ETL.7212.INSL.NCER | 2024-06-17 | 2024-05-22 | 2025-06-16 | Past Due |  | 2025-05-22 | 2025-05-22 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35597379 | T2 DI SNTH LN-HLF MN BY 0/2 RPL INSW | 93I
LC | 129094790 | 002/073 | T2 DI HMLTN BRNCH CHSTER 2/73 RPR STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-06-18 | 2024-05-22 | 2025-03-19 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311131 | T2 DI HMLTN BRNCH CHSTER 2/73 RPR STRW | ICW
LC | 129094853 | 006/143 | T2 DI HAMLTN BRNCH-CHSTR 06/143 RPL STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-06-18 | 2024-05-22 | 2025-03-19 | On-Time |  | 2025-05-22 | 2025-05-22 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Rotten | Structure-Wood | Replace | 35574582 | T2 DI HAMLTN BRNCH-CHSTR 06/143 RPL STRW | 70Y
LC | 129095178 | 014/285 | T2 DI HAT CRK #1-WSTWD 014/285 RMV VEG | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-18 | 2024-05-22 | 2024-11-21 | On-Time |  | 2025-05-22 | 2025-05-22 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129095320 | 000/001A | T2 DI PIT #1-MC ARTHUR 0/001A RPR GYWW | TABLEMTN | ETL.7790.POLE.NWOD | 2024-06-18 | 2024-05-22 | 2025-02-10 | On-Time |  | 2025-05-22 | 2025-05-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46383878 | T2 DI PIT #1-MC ARTHUR 0/001A RPR GYWW | ICW
LC | 129095352 | 006/142 | T2 DI HMLTN BRNCH-CHSTER-6/142 RPL STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-06-18 | 2024-05-22 | 2025-03-19 | On-Time |  | 2025-05-22 | 2025-05-22 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574531 | T2 DI HMLTN BRNCH-CHSTER-6/142 RPL STRW | 70Y
LC | 129105619 | 018/266 | T2 DI KESWICK-TRINITY-18/266 CANCEL | TABLEMTN | ETL.7270.INSL.NCER | 2024-06-20 | 2024-05-22 | 2024-05-22 | Past Due |  | 2025-05-22 | 2025-05-22 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573308 | T2 DI KESWICK-TRINITY-18/266 RPL INSW | 93I
LC | 129105741 | 012/006 | T2 DI MNDO-WLTS-FRT BRAG 12/06 RPL STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-06-20 | 2024-05-22 | 2025-04-11 | On-Time |  | 2025-05-22 | 2025-05-22 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574194 | T2 DI MNDO-WLTS-FRT BRAG 12/06 RPL STRW | 70Y
LC | 129120646 | 005/071 | T2 DI JOLON TAP 5/71 RPL POLE | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-06-24 | 2024-05-22 | 2025-01-26 | On-Time |  | 2025-05-22 | 2025-05-22 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573681 | T2 DI JOLON TAP 5/71 RPL POLE | 70Y
LC | 129121001 | 039/169 | T2 DI FULTON-LKVL 39/169 RPL HRDD | LAKEVLLE | ETL.4950.TOWR | 2024-06-24 | 2024-05-22 | 2024-09-26 | On-Time |  | 2025-05-22 | 2025-05-22 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289550 | T2 DI FULTON-LKVL 39/169 RPL HRDD | ICQ
LC | 129121191 | 076/385B | T2 DI MALIN-ROUND MTN#2 76/385B RPR SHLS | TABLEMTN | ETL.6020.TOWR | 2024-06-24 | 2024-05-22 | 2025-02-09 | On-Time |  | 2025-05-22 | 2025-05-22 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338276 | T2 DI MALIN-ROUND MTN#2 76/385B RPR SHLS | ICS
LC | 123701844 | 063/318 | T2NT DI MLN RND MTN#2 63/318 RPR GYWS | TABLEMTN | ETL.6020.TOWR | 2022-05-26 | 2022-05-23 | 2023-09-28 | On-Time |  | 2025-05-23 | 2025-05-23 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45650748 | T2 DI MLIN RND MTN#2 063/318 RPR GYWS | ICS
LC | 123709266 | 050/218 | T2NT DI RD MT-TB MT #2 50/218 RPR JMPS | TABLEMTN | ETL.6070.INSL | 2022-05-27 | 2022-05-23 | 2023-06-12 | On-Time |  | 2025-05-23 | 2025-05-23 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 45457515 | T2 DI RND MTN-TBL MTN #2 50/218 RPR JMPS | ICS
LC | 123817496 | 009/082 | T2 DI UKIAH-HPLND-CLVERDLE 9/82 RPL GYWW | WILLITS | ETL.4050.POLE.STPS | 2022-06-10 | 2022-05-23 | 2023-03-13 | On-Time |  | 2023-05-23 | 2025-05-23 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45593096 | T2 DI UKIAH-HPLND-CLVERDLE 9/82 RPL GYWW | ICW
LC | 128843267 | 008/099 | T2 EI DRM-SMT NO 1 8/99 RPR GYWW | SACTO | ETL.1440.POLE.STPS | 2024-05-23 | 2024-05-23 | 2024-07-19 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46283911 | T2 EI DRM-SMT NO 1 8/99 RPR GYWW | ICW
LC | 128843883 | 008/099 | T2 EI DRUM-SUMT NO. 1 8/99 RPR GYWW | SACTO | ETL.1440.POLE.STPS | 2024-05-23 | 2024-05-23 | 2024-07-19 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46283913 | T2 EI DRUM-SUMT NO. 1 8/99 RPR GYWW | ICW
LC | 128843886 | 014/000 | T2 WV HUMBLDT BY-RIO DLL 14/00 INS DMPW | EUREKA | ETL.7100.INSL.NCER | 2024-05-23 | 2024-05-23 | 2025-04-30 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46345986 | T2 WV HUMBLDT BY-RIO DLL 14/00 INS DMPW | ICW
LC | 128851515 | 024/378 | T2 KESWICK-TRINITY 24/378 RPL INSW | TABLEMTN | ETL.7270.INSL.CERA | 2024-05-23 | 2024-05-23 | 2025-04-16 | On-Time |  | 2025-05-23 | 2025-05-23 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573426 | T2 KESWICK-TRINITY 24/378 RPL INSW | 93I
LC | 128858696 | 008/096C | T2 EI DRUM-SUMMIT #1 8/096C RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-05-23 | 2024-05-23 | 2025-04-22 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46397994 | T2 EI DRUM-SUMMIT #1 8/096C RPR GYWW | ICW
LC | 128858697 | 008/096B | T2 EI DRUM-SUMMIT #1 8/096B RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-05-23 | 2024-05-23 | 2025-04-22 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46397995 | T2 EI DRUM-SUMMIT #1 8/096B RPR GYWW | ICW
LC | 128864606 | 001/024 | T2 EI CTONWOD-PANRMA 01/24 RPL INSW | TABLEMTN | ETL.1340.INSL | 2024-05-23 | 2024-05-23 | 2025-03-13 | On-Time |  | 2025-05-23 | 2025-05-23 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572995 | T2 EI CTONWOD-PANRMA 01/24 RPL INSW | 93I
LC | 128868569 | 067/278 | T2 EI RND MTN-TBL MTN #2 67/278 RMV NEST | TABLEMTN | ETL.6070.TOWR | 2024-05-23 | 2024-05-23 | 2025-02-19 | On-Time |  | 2025-05-23 | 2025-05-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306303 | T2 EI RND MTN-TBL MTN #2 67/278 RMV NEST | ICS
LC | 128878659 | 001/025 | T2 EI CTONWOD-PANORAMA 01/25 RPL INSW | TABLEMTN | ETL.1340.INSL.CERA | 2024-05-23 | 2024-05-23 | 2025-03-13 | On-Time |  | 2025-05-23 | 2025-05-23 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572996 | T2 EI CTONWOD-PANORAMA 01/25 RPL INSW | 93I
LC | 128879327 | 023/118 | T2 EI RND MTN-TBL MTN #1 23/118 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-23 | 2024-05-23 | 2025-03-10 | On-Time |  | 2025-05-23 | 2025-05-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128879661 | 023/117 | T2 EI RND MTN-TBL MTN #1 23/117 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-23 | 2024-05-23 | 2025-03-10 | On-Time |  | 2025-05-23 | 2025-05-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128879664 | 023/116 | T2 EI RND MTN-TBL MTN #1 23/116 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-23 | 2024-05-23 | 2025-03-10 | On-Time |  | 2025-05-23 | 2025-05-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128881419 | 026/311C | T2 DRUM-SUMMIT #1 26/311C COMPLETE | SACTO | ETL.1440.POLE.NWOD | 2024-05-23 | 2024-05-23 | 2025-05-01 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46398031 | T2 EI DRUM-SUMMIT #1 26/311C RPR GYWW | ICW
LC | 128882033 | 026/311B | T2 DRUM-SUMMIT #1 26/311B COMPLETE | SACTO | ETL.1440.POLE.NWOD | 2024-05-23 | 2024-05-23 | 2025-05-01 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46397996 | T2 EI DRUM-SUMMIT #1 26/311B RPR GYWW | ICW
LC | 128882071 | 026/311A | T2 DRUM-SUMMIT #1 26/311A COMPLETE | SACTO | ETL.1440.POLE.NWOD | 2024-05-23 | 2024-05-23 | 2025-05-01 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46397997 | T2 EI DRUM-SUMMIT #1 26/311A RPR GYWW | ICW
LC | 128882252 | 007/197 | T2 EI DRUM-SPAULDING 007/197 RPL INSW | SACTO | ETL.6770.INSL.NCER | 2024-05-23 | 2024-05-23 | 2025-05-21 | On-Time |  | 2025-05-23 | 2025-05-23 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573501 | T2 EI DRUM-SPAULDING 007/197 RPL INSW | 93I
LC | 128882334 | 041/175 | T2 EI MORRO BY-SLR SS #1 41/175 RPL INSS | PISMOBCH | ETL.5300.INSL | 2024-05-23 | 2024-05-23 | 2025-04-06 | On-Time |  | 2025-05-23 | 2025-05-23 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP REMT SWRK CLR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35623324 | T0 EI MORRO BY-SOLR SS#1 42/180 RPL INSS | 93K
LC | 128882357 | 041/175 | T2 EI MRO BAY-SLR SS #2 41/175 RPL INSS | PISMOBCH | ETL.5310.INSL | 2024-05-23 | 2024-05-23 | 2025-04-29 | On-Time |  | 2025-05-23 | 2025-05-23 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCL ACCM ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35641967 | T2 EI MRO BAY-SLR SS #2 41/175 RPL INSS | 93K
LC | 128882384 | 005/001 | T2 MENDOCINO-UKIAH 05/001 RPR GYWW | WILLITS | ETL.2420.POLE.WOOD | 2024-05-23 | 2024-05-23 | 2025-04-07 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46340268 | T2 MENDOCINO-UKIAH 05/001 RPR GYWW | ICW
LC | 128882795 | 007/199 | T2 EI DRUM-SPAULDING 007/199 RPL POLE | SACTO | ETL.6770.POLE.WOOD | 2024-05-23 | 2024-05-23 | 2025-05-21 | On-Time |  | 2025-05-23 | 2025-05-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35576471 | T2 EI DRUM-SPAULDING 007/199 RPL POLE | 70Y
LC | 128882949 | 004/000 | T2 EI MENDOCINO-WILLITS 4/000 RPL POLE | WILLITS | ETL.7540.POLE.WOOD | 2024-05-23 | 2024-05-23 | 2025-05-28 | Past Due |  | 2025-05-23 | 2025-05-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574335 | T2 EI MENDOCINO-WILLITS 4/000 RPL POLE | 70Y
LC | 128882974 | 016/071 | T2 EI MORRO BAY-SOLR SS #1 16/71 COTTER | PISMOBCH | ETL.5300.INSL.NCER | 2024-05-23 | 2024-05-23 | 2025-04-08 | On-Time |  | 2025-05-23 | 2025-05-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329544 | T2 EI MORRO BAY-SLR SS #1 16/071 COTTER | ICS
LC | 128883074 | 001/034 | T2 EI PINE GROVE TAP 001/034 RPR GYWW | VICTOR | ETL.8351.POLE.NWOD | 2024-05-23 | 2024-05-23 | 2025-03-24 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46325937 | T2 EI PINE GROVE TAP 001/034 RPR GYWW | ICW
LC | 128883454 | 024/120 | T2 EI RND MTN-TL MTN #1 24/120 BNT STEEL | TABLEMTN | ETL.6060.TOWR | 2024-05-23 | 2024-05-23 | 2025-04-24 | On-Time |  | 2025-05-23 | 2025-05-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310393 | T2 EI RND MTN-TL MTN #1 24/120 BNT STEEL | ICQ
LC | 128883484 | 024/120 | T2 EI RND MTN-TL MTN #1 24/120 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-23 | 2024-05-23 | 2025-03-10 | On-Time |  | 2025-05-23 | 2025-05-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128883715 | 045/192 | T2 CBRN-LS AGS SW ST 45/192 TOUCH | MOSSLNDG | ETL.4460.TOWR | 2024-05-23 | 2024-05-23 | 2024-05-23 | Past Due |  | 2024-08-23 | 2025-05-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491498 | T2 EI CBRN-LS AGS SW ST 45/192 TOUCH | ICQ
LC | 128883760 | 007/147 | T2 CARIBOU-WESTWOOD 7/147 RMV VEG | TABLEMTN | ETL.6300.POLE.WOOD | 2024-05-23 | 2024-05-23 | 2024-05-23 | Past Due |  | 2025-05-23 | 2025-05-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128884258 | C004/018 | T2 EI MOS LNDNG-COBURN C004/018 TOUCH | MOSSLNDG | ETL.5330.TOWR | 2024-05-23 | 2024-05-23 | 2024-05-23 | Past Due |  | 2024-11-23 | 2025-05-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491504 | T2 EI MOS LNDNG-COBURN C004/018 TOUCH | ICQ
LC | 128887021 | 000/006 | T2 DI MELONES RACETRACK 0/6 RPR IBWW | VICTOR | ETL.2400.INSL.CERA | 2024-05-24 | 2024-05-23 | 2024-10-31 | On-Time |  | 2024-11-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46266198 | T2 DI MELONES RACETRACK 0/6 RPR IBWW | ICW
LC | 128888615 | 003/050 | T2 DI COLGATE-SMRTVLE #1 3/50 RPR CNDW | SACTO | ETL.6510.INSL.NCER | 2024-05-24 | 2024-05-23 | 2025-04-11 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46324559 | T2 DI COLGATE-SMRTVLE #1 3/50 RPR CNDW | ICW
LC | 128890642 | 040/340 | T2 DI ROUND MTN-CTNWD #3 40/340 RPR JUMS | TABLEMTN | ETL.5650.INSL.CERA | 2024-05-25 | 2024-05-23 | 2025-03-03 | On-Time |  | 2025-05-23 | 2025-05-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46416196 | T2 DI ROUND MTN-CTNWD #3 40/340 RPR JUMS | ICS
LC | 128890669 | 69 | T2 DI HT CRK #1-PT#1 A0/1 SW 69 RPR JMPW | TABLEMTN | ETL.7020.SWIT | 2024-05-25 | 2024-05-23 | 2025-05-05 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Wood | Repair | 46416037 | T2 DI HT CRK #1-PT#1 A0/1 SW 69 RPR JMPW | ICW
LC | 128891229 | 004/052 | T2 DI PIT#1 HT CFK #2 BRNY 4/52 RPR GYWW | TABLEMTN | ETL.7040.POLE.WOOD | 2024-05-25 | 2024-05-23 | 2024-09-04 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46253271 | T2 DI PIT#1 HT CFK #2 BRNY 4/52 RPR GYWW | ICW
LC | 128961721 | 000/001A | T2 DI STNSL-MLNS SS-RVRBN 0/1A RPR GYWW | VICTOR | ETL.3840.POLE.NWOD | 2024-05-31 | 2024-05-23 | 2025-03-15 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327508 | T2 DI STNSL-MLNS SS-RVRBN 0/1A RPR GYWW | ICW
LC | 129032590 | 004/054 | T2 DI COLGATE-SMRTVIL #2 04/54 COTTER | SACTO | ETL.6520.INSL.NCER | 2024-06-06 | 2024-05-23 | 2025-03-05 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46324557 | T2 DI COLGATE-SMRTVIL #2 04/54 COTTER | ICW
LC | 129035212 | 020/301 | T2 DI KESWICK TRINITY 20/301 RMV VEG | TABLEMTN | ETL.7270.POLE.WOOD | 2024-06-07 | 2024-05-23 | 2024-08-09 | On-Time |  | 2025-05-23 | 2025-05-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129054455 | 003/040 | T2 DI COLGATE-PALERMO 03/40 RPL STRW | SACTO | ETL.6500.POLE.WOOD | 2024-06-10 | 2024-05-23 | 2025-04-28 | On-Time |  | 2025-05-23 | 2025-05-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572921 | T2 DI COLGATE-PALERMO 03/40 RPL STRW | 70Y
LC | 129054591 | 003/052 | T2 COLGATE-PALERMO 03/52 TOUCH | SACTO | ETL.6500.POLE.NWOD | 2024-06-10 | 2024-05-23 | 2025-04-28 | On-Time |  | 2024-11-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46463509 | T2 DI COLGATE-PALERMO 03/52 RPR STRW | ICW
LC | 129054671 | 004/055 | T2 DI COLGATE-SMRTVIL #1 4/55 RPR CNDW | SACTO | ETL.6510.INSL.NCER | 2024-06-10 | 2024-05-23 | 2025-04-10 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46324556 | T2 DI COLGATE-SMRTVIL #1 4/55 RPR CONW | ICW
LC | 129054846 | 005/062 | T2 DI COLGATE-SMRTVL #1 5/62 RPR CNDW | SACTO | ETL.6510.INSL.NCER | 2024-06-10 | 2024-05-23 | 2025-04-09 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46324555 | T2 DI COLGATE-SMRTVL #1 5/62 RPR CNDW | ICW
LC | 129055017 | 020/164 | T2 DI PIT #1-CTNWD 20/164 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-06-10 | 2024-05-23 | 2025-04-02 | On-Time |  | 2025-05-23 | 2025-05-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381909 | T2 DI PIT #1-CTNWD 20/164 RPR STRT | ICQ
LC | 129061393 | 000/005 | T2 DI MELONES-CURTIS 000/005L RPR GYWW | VICTOR | ETL.2390.POLE.STPS | 2024-06-11 | 2024-05-23 | 2025-05-14 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46325960 | T2 DI MELONES-CURTIS 000/005L RPR GYWW | ICW
LC | 129061540 | 019/000 | T2 DI MNDO-WLTS-FRT BRG 19/00 RPR IBWW | WILLITS | ETL.7550.INSL.NCER | 2024-06-11 | 2024-05-23 | 2025-04-09 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46310273 | T2 DI MNDO-WLTS-FRT BRG 19/00 RPR IBWW | ICW
LC | 129061648 | 003/050-GUY | T2 DI COLGATE-PALERMO 3/50 RPR STRW | SACTO | ETL.6500.POLE.WOOD | 2024-06-11 | 2024-05-23 | 2025-04-28 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46397998 | T2 DI COLGATE-PALERMO 3/50 RPR STRW | ICW
LC | 129061689 | 108/006 | T2 DI HMBLDT-BRDGVIL 108/06 TOUCH | EUREKA | ETL.1810.TOWR | 2024-06-11 | 2024-05-23 | 2025-03-07 | On-Time |  | 2024-11-23 | 2025-05-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46477328 | T2 DI HMBLDT-BRDGVIL 108/06 TOUCH | ICQ
LC | 129061832 | 019/159 | T2 DI PIT#1 COTTONWOOD 19/159 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-06-11 | 2024-05-23 | 2025-05-13 | On-Time |  | 2025-05-23 | 2025-05-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381910 | T2 DI PIT#1 COTTONWOOD 19/159 RPR FOND | ICQ
LC | 129087606 | 003/039 | T2 DI CLGTE PLMRO 03/039 RPR STRW | SACTO | ETL.6500.POLE.WOOD | 2024-06-17 | 2024-05-23 | 2025-04-28 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46398020 | T2 DI CLGTE PLMRO 03/039 RPR STRW | ICW
LC | 129088183 | 006/082 | T2NT DI JOLON TAP 006/082 RMV VEG | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-06-17 | 2024-05-23 | 2024-05-23 | Past Due |  | 2027-05-23 | 2025-05-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129088395 | 019/157 | T2 DI PIT #1-COTTONWOOD 19/157 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-06-17 | 2024-05-23 | 2025-05-13 | On-Time |  | 2025-05-23 | 2025-05-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381916 | T2 DI PIT #1-COTTONWOOD 19/157 RPR STRT | ICQ
LC | 129088441 | 027/001 | T2 DI GRBRVLE-LYTNVLE 027/001 RPL STRW | WILLITS | ETL.8365.POLE.WOOD | 2024-06-17 | 2024-05-23 | 2025-04-17 | On-Time |  | 2025-05-23 | 2025-05-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574340 | T2 DI GRBRVLE-LYTNVLE 027/001 RPL STRW | 70Y
LC | 129094802 | 000/002 | T2 DI SOBRANTE-R#1 0/2 TOUCH | CONCORD | ETL.3770.TOWR | 2024-06-18 | 2024-05-23 | 2025-06-16 | Past Due |  | 2024-11-23 | 2025-05-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485646 | T2 DI SOBRANTE-R#1 0/2 TOUCH | ICQ
LC | 129095117 | 005/072 | T2 DI JOLON TAP 005/072 RMV VEG | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-06-18 | 2024-05-23 | 2025-01-03 | On-Time |  | 2025-05-23 | 2025-05-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129105310 | 009/126 | T2 DI JOLON TAP 9/126 RPR GYWW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-06-20 | 2024-05-23 | 2025-01-30 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391186 | T2 DI JOLON TAP 9/126 RPR GYWW | ICW
LC | 129105404 | 004/045 | T2 DI HLSDL JCT-HAF MN BAY 4/45 RPL STRW | METCALF | ETL.7060.POLE.WOOD | 2024-06-20 | 2024-05-23 | 2025-03-07 | On-Time |  | 2025-05-23 | 2025-05-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573574 | T2 DI HLSDL JCT-HAF MN BAY 4/45 RPL STRW | 70Y
LC | 129105492 | 021/320 | T2 DI KSWCK-TRNTY 21/320 RPR STRW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-06-20 | 2024-05-23 | 2025-04-13 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311167 | T2 DI KSWCK-TRNTY 21/320 RPR STRW | ICW
LC | 129105566 | 020/165 | T2NT DI PIT #1-CTTNWD 020/165 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-06-20 | 2024-05-23 | 2025-04-02 | On-Time |  | 2027-05-23 | 2025-05-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381918 | T2NT DI PIT #1-CTTNWD 020/165 RPR STRT | ICQ
LC | 129121120 | 002/037 | T2 DI COLGATE-PALERMO 2/37 RPR WDPK | SACTO | ETL.6500.POLE.WOOD | 2024-06-24 | 2024-05-23 | 2025-04-28 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46398021 | T2 DI COLGATE-PALERMO 2/37 RPR WDPK | ICW
LC | 129126992 | 007/089 | T2 DI JOLON TAP 007/089 RPL POLE | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-06-25 | 2024-05-23 | 2025-01-27 | On-Time |  | 2025-05-23 | 2025-05-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573686 | T2 DI JOLON TAP 007/089 RPL POLE | 70Y
LC | 129127035 | 007/092 | T2 DI JOLON TAP 7/92 RPL POLE | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-06-25 | 2024-05-23 | 2025-01-27 | On-Time |  | 2025-05-23 | 2025-05-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573689 | T2 DI JOLON TAP 7/92 RPL POLE | 70Y
LC | 129127254 | 003/016 | T2 DI HMBLDT BAY-HMBLDT #1 3/16 RPL HRDT | EUREKA | ETL.1800.TOWR | 2024-06-25 | 2024-05-23 | 2025-04-23 | On-Time |  | 2025-05-23 | 2025-05-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289234 | T2 DI HMBLDT BAY-HMBLDT #1 3/16 RPL HRDT | ICQ
LC | 129127263 | 009/039 | T2 DI EAGLE ROCK FLTN SLV 9/39 TOUCH | LAKEVLLE | ETL.4392.TOWR | 2024-06-25 | 2024-05-23 | 2025-05-01 | On-Time |  | 2024-11-23 | 2025-05-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46474467 | T2 DI EAGLE ROCK FLTN SLV 9/39 TOUCH | ICQ
LC | 129127279 | 001/027 | T2 DI COLGATE-PALERMO 001/027 RPL POLE | SACTO | ETL.6500.POLE.WOOD | 2024-06-25 | 2024-05-23 | 2025-05-02 | On-Time |  | 2025-05-23 | 2025-05-23 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572920 | T2 DI COLGATE-PALERMO 001/027 RPL POLE | 70Y
LC | 129134466 | 005/061 | T2 DI COLGATE-SMRTVIL#2 05/61 RPR GYWW | SACTO | ETL.6520.POLE.STPS | 2024-06-26 | 2024-05-23 | 2025-02-18 | On-Time |  | 2025-05-23 | 2025-05-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337423 | T2 DI COLGATE-SMRTVIL#2 05/61 RPR GYWW | ICW
LC | 129134584 | 010/129 | T2NT DI JOLON TAP 010/129 RMV VEG | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-06-26 | 2024-05-23 | 2025-01-02 | On-Time |  | 2027-05-23 | 2025-05-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129134796 | 113/004 | T2 HUMBOLDT-BRIDGEVILE 113/4L RMV VEG | EUREKA | ETL.1810.POLE.STPS | 2024-06-26 | 2024-05-23 | 2024-05-23 | Past Due |  | 2025-05-23 | 2025-05-23 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR | Overgrown | Vegetation | Remove
LC | 129134811 | 267 | T2 DI HUMBOLDT-BRIDGLLE 108/3 RPR SWTC | EUREKA | ETL.1810.SWIT | 2024-06-26 | 2024-05-23 | 2024-05-23 | Past Due |  | 2025-05-23 | 2025-05-23 | 623 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR ACCL OH TR2 PRTO AIR | Out of Adjustment | Switch | Repair | 46345988 | T2 DI HUMBOLDT-BRIDGLLE 108/3 RPR SWTC | ICE
LC | 129134812 | 108/003 | T2 DI HUMBOLDT-BRIDGLLE 108/3 RPR ADSS | EUREKA | ETL.1810.TOWR | 2024-06-26 | 2024-05-23 | 2024-11-04 | On-Time |  | 2024-08-23 | 2025-05-23 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Steel | Repair | 46272347 | T2 DI HUMBOLDT-BRIDGLLE 108/3 RPR ADSS | ICS
LC | 123682906 | 008/044 | T3NT EI RND MTN-TBL MTN #2 8/44 BNT STL | TABLEMTN | ETL.6070.TOWR | 2022-05-24 | 2022-05-24 | 2023-07-31 | On-Time |  | 2025-05-24 | 2025-05-24 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644877 | T3 EI RND MTN-TBL MTN #2 8/44 BENT STEEL | ICQ
LC | 123683520 | 008/045 | T3NT EI RND MTN-TBL MTN #2 8/45 BNT STL | TABLEMTN | ETL.6070.TOWR | 2022-05-24 | 2022-05-24 | 2023-07-31 | On-Time |  | 2025-05-24 | 2025-05-24 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644878 | T3 EI RND MTN-TBL MTN #2 8/45 BENT STEEL | ICQ
LC | 123714660 | 032/214 | T2NT DI POE-RIO OSO-RIO 32/214 BNT STEEL | TABLEMTN | ETL.5540.TOWR | 2022-05-28 | 2022-05-24 | 2023-07-21 | On-Time |  | 2025-05-24 | 2025-05-24 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648171 | T2 DI POE-RIO OSO-RIO 32/214 BNT STEEL | ICQ
LC | 123793063 | 009/179 | T2NT DI COTTONWOO-RD BLFF 9/179 RMV BUTT | TABLEMTN | ETL.6660.POLE.NWOD | 2022-06-08 | 2022-05-24 | 2023-02-13 | On-Time |  | 2023-05-24 | 2025-05-24 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 45456764 | T2NT DI COTTONWOO-RD BLFF 9/179 RMV BUTT | ICW
LC | 123816791 | 021/172 | T2NT DI PIT#1-CTTNWD 21/172 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2022-06-10 | 2022-05-24 | 2023-07-27 | On-Time |  | 2025-05-24 | 2025-05-24 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45620321 | T2 DI PIT#1-COTTNWOOD 21/172 BNT STEEL | ICQ
LC | 123900923 | 000/003 | T2NT DI LUCERNE # 1 TAP 000/003 RPL HRDD | WILLITS | ETL.1331.POLE.NWOD | 2022-06-22 | 2022-05-24 | 2023-11-30 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46077565 | T2NT DI LUCERNE # 1 TAP 000/003 RPL HRDD | ICW
LC | 123901513 | 006/058 | T3NT DI MONTA VISTA-BURNS 6/58 RMV STEP | MOSSLNDG | ETL.7590.POLE.NWOD | 2022-06-22 | 2022-05-24 | 2023-08-18 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 45618812 | T3 DI MONTA VISTA-BURNS 6/58 RMV STEP | ICW
LC | 128886075 | 020/094 | T2 VACA-LAKEVILLE 020/094 RPL INSS | LAKEVLLE | ETL.5840.INSL.CERA | 2024-05-24 | 2024-05-24 | 2025-04-18 | On-Time |  | 2025-05-24 | 2025-05-24 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35608973 | T2 VACA-LAKEVILLE 020/094 RPL INSS. | 93K
LC | 128886814 | 003/014 | T2 WV SONOMA-PUEBLO 003/014 RPR INSW | LAKEVLLE | ETL.3810.INSL.NCER | 2024-05-24 | 2024-05-24 | 2025-04-28 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46403756 | T2 WV SONOMA-PUEBLO 003/014 RPR INSW | ICW
LC | 128886961 | 053/002 | T2 WV ELK-GUALALA 053/002 RPR INSW | WILLITS | ETL.8410.INSL.NCER | 2024-05-24 | 2024-05-24 | 2024-05-24 | Past Due |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310274 | T2 WV ELK-GUALALA 053/002 RPR INSW | ICW
LC | 128887567 | 008/204 | T2 DRUM-SPAULDING 008/204 COMPLETE | SACTO | ETL.6770.POLE.WOOD | 2024-05-24 | 2024-05-24 | 2025-05-21 | On-Time |  | 2025-05-24 | 2025-05-24 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573502 | T2 EI DRUM-SPAULDING 008/204 RPL POLE | 70Y
LC | 128887633 | A000/001 | T2 WV CHOWCHILLA-KERCKHOFF A0/1 RPR INSS | FRESNO | ETL.1250.INSL.NCER | 2024-05-24 | 2024-05-24 | 2025-03-25 | On-Time |  | 2025-05-24 | 2025-05-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297996 | T2 WV CHOWCHILLA-KERCKHOFF A0/1 RPR INSS | ICS
LC | 128888231 | 008/203 | T2 EI DRUM-SPAULDING 008/203 RPR POLE | SACTO | ETL.6770.POLE.WOOD | 2024-05-24 | 2024-05-24 | 2025-05-21 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337354 | T2 EI DRUM-SPAULDING 008/203 RPR POLE | ICW
LC | 128888358 | 030/243 | T2 CRESTA-RIO OSO 30/243 RMV NEST | TABLEMTN | ETL.4590.TOWR | 2024-05-24 | 2024-05-24 | 2024-05-24 | Past Due |  | 2025-05-24 | 2025-05-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46337337 | T2 EI CRESTA-RIO OSO 30/243 RMV NEST | ICS
LC | 128888562 | 004/002 | T2 WV LAKEVILLE #1 04/002 INS DAMP | LAKEVLLE | ETL.7360.INSL.NCER | 2024-05-24 | 2024-05-24 | 2025-05-14 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46305949 | T2 WV LAKEVILLE #1 04/002 INS DMPW | ICW
LC | 128888590 | 030/242 | T2 EI CRESTA-RIO OSO 30/242 RMV NEST | TABLEMTN | ETL.4590.TOWR | 2024-05-24 | 2024-05-24 | 2024-12-10 | On-Time |  | 2024-11-24 | 2025-05-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | Debris/Nest/etc. | Structure-Steel | Remove | 46256540 | T2 EI CRESTA-RIO OSO 30/242 RMV NEST | ICS
LC | 128888837 | 038/330 | T2 EI CASCADE-COTTONWD 038/330L RPR GYWW | TABLEMTN | ETL.1240.POLE.STPS | 2024-05-24 | 2024-05-24 | 2024-10-01 | On-Time |  | 2024-11-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262795 | T2 EI CASCADE-COTTONWD 038/330L RPR GYWW | ICW
LC | 128888843 | 007/191 | T2 DRUM-SPAULDING 007/191 RPL POLE | SACTO | ETL.6770.POLE.WOOD | 2024-05-24 | 2024-05-24 | 2024-05-24 | Past Due |  | 2025-05-24 | 2025-05-24 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573500 | T2 EI DRUM-SPAULDING 007/191 RPL POLE | 70Y
LC | 128888961 | 038/330 | T2 EI CASCADE-COTTONWD 038/330C RPR GYWW | TABLEMTN | ETL.1240.POLE.STPS | 2024-05-24 | 2024-05-24 | 2024-10-01 | On-Time |  | 2024-11-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262797 | T2 EI CASCADE-COTTONWD 038/330C RPR GYWW | ICW
LC | 128888963 | 030/241 | T2 EI CRESTA-RIO OSO 030/241 UNBURY | TABLEMTN | ETL.4590.TOWR | 2024-05-24 | 2024-05-24 | 2025-03-25 | On-Time |  | 2025-05-24 | 2025-05-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381335 | T2 EI CRESTA-RIO OSO 030/241 UNBURY | ICQ
LC | 128888987 | 038/330 | T2 EI CASCADE-COTTONWD 038/330R RPR GYWW | TABLEMTN | ETL.1240.POLE.STPS | 2024-05-24 | 2024-05-24 | 2024-10-01 | On-Time |  | 2024-11-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262798 | T2 EI CASCADE-COTTONWD 038/330R RPR GYWW | ICW
LC | 128889147 | 024/286 | T2 EI DRUM-SUMMIT # 1 024/286R RPR POLE | SACTO | ETL.1440.POLE.WDPS | 2024-05-24 | 2024-05-24 | 2025-05-02 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46398032 | T2 EI DRUM-SUMMIT # 1 024/286R RPR POLE | ICW
LC | 128889236 | 007/192 | T2 EI DRUM-SPAULDING 007/192 RPR POLE | SACTO | ETL.6770.POLE.WOOD | 2024-05-24 | 2024-05-24 | 2025-05-21 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337355 | T2 EI DRUM-SPAULDING 007/192 RPR POLE | ICW
LC | 128889348 | 007/189 | T2 DRUM-SPAULDING 7/189 RPL INSW | SACTO | ETL.6770.INSL.NCER | 2024-05-24 | 2024-05-24 | 2025-05-20 | On-Time |  | 2025-05-24 | 2025-05-24 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573459 | T2 EI DRUM-SPAULDING 007/189 RPL INSW | 93I
LC | 128889354 | 009/041 | T2 EI SN LS OBPO-SNTA MRA 09/41 RPL DMPS | PISMOBCH | ETL.3540.INSL.CERA | 2024-05-24 | 2024-05-24 | 2025-05-27 | Past Due |  | 2025-05-24 | 2025-05-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB NTDE | Missing | Damper-Steel | Install | 46329669 | T2 EI SN LS OBPO-SNTA MRA 09/41 RPL DMPS | ICS
LC | 128889427 | 024/123 | T2 EI RND MTN-TBLE MTN #1 24/123 COTTER | TABLEMTN | ETL.6060.INSL | 2024-05-24 | 2024-05-24 | 2025-01-22 | On-Time |  | 2025-05-24 | 2025-05-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46306304 | T2 EI RND MTN-TBLE MTN #1 24/123 COTTER | ICS
LC | 128889436 | 024/122 | T2NT EI RND MTN-TBLE MTN#1 24/122 RM VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-24 | 2024-05-24 | 2025-03-10 | On-Time |  | 2027-05-24 | 2025-05-24 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128889544 | C014/058 | T2 EI MOS LANDNG-COBURN C014/058 RMV VEG | MOSSLNDG | ETL.5330.TOWR | 2024-05-24 | 2024-05-24 | 2025-05-07 | On-Time |  | 2025-05-24 | 2025-05-24 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128889715 | 018/353 | T2 HAT CREEK #1-WSTWD 18/353 RPR POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-24 | 2024-05-24 | 2025-05-02 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46416036 | T2 EI HAT CREEK #1-WSTWD 18/353 RPR POLE | ICW
LC | 128891078 | 073/002AA | T2 DI HMBLDT-TRINITY 73/2AA RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-05-25 | 2024-05-24 | 2024-08-27 | On-Time |  | 2024-08-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46254664 | T2 DI HMBLDT-TRINITY 73/2AA RPR JUMW | ICW
LC | 128891123 | 020/302 | T2 DI KESWICK-TRINITY 20/302 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-05-25 | 2024-05-24 | 2025-04-15 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311165 | T2 DI KESWICK-TRINITY 20/302 RPR JUMW | ICW
LC | 128891250 | 011/012 | T2 DI LWR LK-HOMESTAKE 11/12 RPR IBWW | WILLITS | ETL.1481.INSL.NCER | 2024-05-25 | 2024-05-24 | 2025-05-06 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46340269 | T2 DI LWR LK-HOMESTAKE 11/12 RPR IBWW | ICW
LC | 128896301 | 053/1029 | T2 EI HT CRK #1-WSTWD 53/1029 RPR POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-28 | 2024-05-24 | 2025-03-29 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46416038 | T2 EI HT CRK #1-WSTWD 53/1029 RPR POLE | ICW
LC | 128901711 | 077/003A | T2 DI HUMBOLDT-TRINITY 77/03A RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-05-28 | 2024-05-24 | 2025-04-16 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345997 | T2 DI HUMBOLDT-TRINITY 77/03A RPR GYWW | ICW
LC | 128901910 | 077/003C | T2 DI HUMBOLDT-TRINITY 77/03C COTTER | EUREKA | ETL.1820.INSL.NCER | 2024-05-28 | 2024-05-24 | 2025-04-16 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46345998 | T2 DI HUMBOLDT-TRINITY 77/03C COTTER | ICW
LC | 128902107 | 008/146 | T2 DI PIT#1-HAT CRK#2-BRNY 8/146 COTTER | TABLEMTN | ETL.7040.INSL.NCER | 2024-05-28 | 2024-05-24 | 2025-05-21 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46454292 | T2 DI PIT#1-HAT CRK#2-BRNY 8/146 COTTER | ICW
LC | 128902273 | 005/116 | T2 DI HAT CRK #1 WESTWD 5/116 COMPLETE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-28 | 2024-05-24 | 2024-08-15 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46262804 | T2 DI HAT CRK #1 WESTWD 5/116 INSP STRW | ICW
LC | 128902350 | 073/002A | T2 DI HUMBLT TRINITY 73/2A RPR GYWW | EUREKA | ETL.1820.POLE.WOOD | 2024-05-28 | 2024-05-24 | 2025-04-08 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345992 | T2 DI HUMBLT TRINITY 73/2A RPR GYWW | ICW
LC | 128902359 | 019/281 | T2 DI KESWICK TRINITY 19/281 RPR JUMW | TABLEMTN | ETL.7270.INSL.CERA | 2024-05-28 | 2024-05-24 | 2024-09-14 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262805 | T2 DI KESWICK TRINITY 19/281 RPR JUMW | ICW
LC | 128902511 | 019/284 | T2 DI KESWICK TRINITY 19/284 RPL BOND | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-28 | 2024-05-24 | 2024-09-13 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46262808 | T2 DI KESWICK TRINITY 19/284 RPL BOND | ICW
LC | 128902566 | 073/006B | T2 DI HUMBOLDT-TRINITY 073/006B RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-05-28 | 2024-05-24 | 2025-04-07 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345995 | T2 DI HUMBOLDT-TRINITY 073/006B RPR GYWW | ICW
LC | 129021649 | 003/017 | T2 DI HUMBOLDT BY-HMBLDT#2 3/17 RPL INSS | EUREKA | ETL.7090.INSL | 2024-06-04 | 2024-05-24 | 2025-03-11 | On-Time |  | 2025-05-24 | 2025-05-24 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35579437 | T2 DI HUMBOLDT BY-HMBLDT#2 3/17 RPL INSS | 93K
LC | 129061403 | 093/473 | T2 MALIN-ROUND MTN #2 93/473 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-06-11 | 2024-05-24 | 2025-05-19 | On-Time |  | 2025-05-24 | 2025-05-24 | 93Z | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716789 | T2 DI MLN-RND MTN #2 93/473 RPL ANCT | 93Z
LC | 129061988 | 018/145 | T2 DI PIT#1-COTTONWOOD 18/145 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-06-11 | 2024-05-24 | 2025-04-23 | On-Time |  | 2025-05-24 | 2025-05-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381911 | T2 DI PIT#1-COTTONWOOD 18/145 RPR STRT | ICQ
LC | 129094677 | 004/053 | T2 DI PIT #5-RND MTN #1 4/53 RPL INSS | TABLEMTN | ETL.5420.INSL | 2024-06-18 | 2024-05-24 | 2025-04-10 | On-Time |  | 2024-11-24 | 2025-05-24 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35621181 | T2 DI PIT #5-RND MTN #1 4/53 RPL INSS | 93K
LC | 129094804 | 018/143 | T2 DI PIT #1-COTTONWOOD 18/143 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-06-18 | 2024-05-24 | 2025-04-22 | On-Time |  | 2025-05-24 | 2025-05-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381917 | T2 DI PIT #1-COTTONWOOD 18/143 RPR FOND | ICQ
LC | 129094882 | :000/005 | T2 DI PIT #3-PIT #1 :0/5 RPR FOND | TABLEMTN | ETL.5400.TOWR | 2024-06-18 | 2024-05-24 | 2025-04-11 | On-Time |  | 2025-05-24 | 2025-05-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46382052 | T2 DI PIT #3-PIT #1 :0/5 RPR FOND | ICQ
LC | 129095139 | :000/004 | T2 DI PIT #3-PIT #1 :000/004 RPR FOND | TABLEMTN | ETL.5400.TOWR | 2024-06-18 | 2024-05-24 | 2025-04-11 | On-Time |  | 2025-05-24 | 2025-05-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46382053 | T2 DI PIT #3-PIT #1 :000/004 RPR FOND | ICQ
LC | 129095407 | 012/012 | T2 DI LOWER LAKE-HMS 12/12 RPR STRW | WILLITS | ETL.1481.POLE.WOOD | 2024-06-18 | 2024-05-24 | 2024-05-24 | Past Due |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR ACCL OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46446819 | T2 DI LOWER LAKE-HMS 12/12 RPR STRW | ICW
LC | 129105324 | 003/075 | T2 DI HAT CREEK #1 WESTWD 3/75 RPR STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-20 | 2024-05-24 | 2025-05-13 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46416141 | T2 DI HAT CREEK #1 WESTWD 3/75 RPR STRW | ICW
LC | 129105636 | A006/143 | T2 DI CSCDE-BNTN-DSCHTS A6/143 TOUCH | TABLEMTN | ETL.6310.POLE.NWOD | 2024-06-20 | 2024-05-24 | 2024-05-24 | Past Due |  | 2024-11-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46486746 | T2 DI CSCDE-BNTN-DSCHTS A6/143 TOUCH | ICW
LC | 129105638 | 012/015 | T2 DI LWR LK-HMSTK 12/15 RPR STRW | WILLITS | ETL.1481.POLE.WOOD | 2024-06-20 | 2024-05-24 | 2024-05-24 | Past Due |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46446900 | T2 DI LWR LK-HMSTK 12/15 RPR STRW | ICW
LC | 129105722 | 008/162 | T2 HAT CRK#1-WW 8/162 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-20 | 2024-05-24 | 2025-05-18 | On-Time |  | 2025-05-24 | 2025-05-24 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Rotten | Structure-Wood | Replace | 35574779 | T2 DI HAT CRK#1-WW 8/162 RPL STRW | 70Y
LC | 129105816 | 013/014 | T2 DI LWR LK-HMSTK 13/14 RPR STRW | WILLITS | ETL.1481.POLE.WOOD | 2024-06-20 | 2024-05-24 | 2024-05-24 | Past Due |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW ACCL OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46446901 | T2 DI LWR LK-HMSTK 13/14 RPR STRW | ICW
LC | 129119903 | 019/271 | T2 DI KESWICK-TRINITY 019/271 RPR CNDW | TABLEMTN | ETL.7270.INSL.NCER | 2024-06-24 | 2024-05-24 | 2025-04-11 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46311166 | T2 DI KESWICK-TRINITY 019/271 RPR CNDW | ICW
LC | 129120234 | 008/148 | T2 DI PT #1-HT CRK#2-BRNY 8/148 RPR STRW | TABLEMTN | ETL.7040.POLE.WOOD | 2024-06-24 | 2024-05-24 | 2025-05-21 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454361 | T2 DI PT #1-HT CRK#2-BRNY 8/148 RPR STRW | ICW
LC | 129120389 | 022/180 | T2 DI PIT #1-CTTNWD 022/180 UNBURY | TABLEMTN | ETL.5390.TOWR | 2024-06-24 | 2024-05-24 | 2025-04-03 | On-Time |  | 2025-05-24 | 2025-05-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381919 | T2 DI PIT #1-CTTNWD 022/180 UNBURY | ICQ
LC | 129120568 | 019/276 | T2 DI KESWICK-TRIN 19/276 GO95 | TABLEMTN | ETL.7270.POLE.WOOD | 2024-06-24 | 2024-05-24 | 2025-04-13 | On-Time |  | 2025-05-24 | 2025-05-24 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35573312 | T2 DI KESWICK-TRIN 19/276 GO95 | 93G
LC | 129121008 | 074/003A | T2 DI HUMBOLDT-TRINITY 74/3A RMV VEG | EUREKA | ETL.1820.POLE.NWOD | 2024-06-24 | 2024-05-24 | 2024-11-21 | On-Time |  | 2025-05-24 | 2025-05-24 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129134636 | 007/116 | T2 DI PIT#1-HCRK#2-BRN 7/116 REFRAME | TABLEMTN | ETL.7040.POLE.WOOD | 2024-06-26 | 2024-05-24 | 2025-05-22 | On-Time |  | 2025-05-24 | 2025-05-24 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35573309 | T2 DI PIT#1-HCRK#2-BRN 7/116 REFRAME | 93E
LC | 129141161 | 018/150 | T2 DI PIT #1 COTONWD 18/150 RPL HRDT | TABLEMTN | ETL.5390.TOWR | 2024-06-28 | 2024-05-24 | 2025-05-20 | On-Time |  | 2025-05-24 | 2025-05-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381943 | T2 DI PIT #1 COTONWD 18/150 RPL HRDT | ICQ
LC | 129141214 | 054/002C | T2 DI HMBLDT-TRINITY 054/002C RPR STRW | EUREKA | ETL.1820.POLE.WOOD | 2024-06-28 | 2024-05-24 | 2025-03-18 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46345990 | T2 DI HMBLDT-TRINITY 054/002C RPR STRW | ICW
LC | 129141215 | 054/002C | T2 DI HMBLDT-TRINITY 054/002C RPR GYWW | EUREKA | ETL.1820.POLE.WOOD | 2024-06-28 | 2024-05-24 | 2025-03-18 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345991 | T2 DI HMBLDT-TRINITY 054/002C RPR GYWW | ICW
LC | 129141341 | 008/145 | T2 DI PIT#1-HCRK#2-BRN 8/145 RPR STRW | TABLEMTN | ETL.7040.POLE.WOOD | 2024-06-28 | 2024-05-24 | 2025-05-21 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454364 | T2 DI PIT#1-HCRK#2-BRN 8/145 RPR STRW | ICW
LC | 129141754 | 073/004 | T2 DI HMBLDT-TRINITY 73/004 RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-06-28 | 2024-05-24 | 2025-04-22 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46273504 | T2 DI HMBLDT-TRINITY 73/004 RPR JUMW | ICW
LC | 129141758 | 073/004 | T2 DI HMBLDT-TRINITY 73/004 RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-28 | 2024-05-24 | 2025-04-07 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345994 | T2 DI HMBLDT-TRINITY 73/004 RPR GYWW | ICW
LC | 129141867 | :000/002 | T2 DI PIT#3 PIT#1 00/002 RMV VEG | TABLEMTN | ETL.5400.TOWR | 2024-06-28 | 2024-05-24 | 2024-11-19 | On-Time |  | 2025-05-24 | 2025-05-24 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129141943 | 002/050 | T2 DI HAT CRK #1-WSTWD 002/050 RMV VEG | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-28 | 2024-05-24 | 2024-11-21 | On-Time |  | 2025-05-24 | 2025-05-24 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129154092 | 080/003B | T2 DI HUMBOLDT-TRINITY 80/3B RPL ANCW | EUREKA | ETL.1820.POLE.WOOD | 2024-07-01 | 2024-05-24 | 2025-04-17 | On-Time |  | 2025-05-24 | 2025-05-24 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574556 | T2 DI HUMBOLDT-TRINITY 80/3B RPL ANCW | 93E
LC | 129156929 | 022/180 | T2 DI PIT #1-COTTONWOOD 022/180 COTTER | TABLEMTN | ETL.5390.INSL.NCER | 2024-07-02 | 2024-05-24 | 2025-04-22 | On-Time |  | 2025-05-24 | 2025-05-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46452802 | T2 DI PIT #1-COTTONWOOD 022/180 COTTER | ICS
LC | 129187772 | 076/000C | T2 DI HUMBOLDT-TRINITY 76/0C RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-07-08 | 2024-05-24 | 2025-04-17 | On-Time |  | 2025-05-24 | 2025-05-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345996 | T2 DI HUMBOLDT-TRINITY 76/0C RPR GYWW | ICW
LC | 130940495 | 080/003A | T2 DI HUMBOLDT-TRINITY 080/003A RPL ANCW | EUREKA | ETL.1820.POLE.WOOD | 2025-03-07 | 2024-05-24 | 2025-04-17 | On-Time |  | 2025-05-24 | 2025-05-24 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574556 | T2 DI HUMBOLDT-TRINITY 80/3B RPL ANCW | 93E
LC | 130940496 | 080/003C | T2 DI HUMBOLDT-TRINITY 080/003C RPL ANCW | EUREKA | ETL.1820.POLE.WOOD | 2025-03-07 | 2024-05-24 | 2025-04-17 | On-Time |  | 2025-05-24 | 2025-05-24 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574556 | T2 DI HUMBOLDT-TRINITY 80/3B RPL ANCW | 93E
LC | 123687254 | 010/053 | T2NT EI RD MTN-TBL MTN #2 10/53 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2022-05-25 | 2022-05-25 | 2023-08-22 | On-Time |  | 2025-05-25 | 2025-05-25 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 123690558 | 011/057 | T2NT EI RD MTN-TBL MTN #2 11/57 RPR STRT | TABLEMTN | ETL.6070.TOWR | 2022-05-25 | 2022-05-25 | 2023-08-16 | On-Time |  | 2025-05-25 | 2025-05-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644929 | T2 EI RD MTN-TBL MTN #2 011/057 RPR STRT | ICQ
LC | 123690559 | 010/056 | T2NT EI RD MTN-TBL MTN #2 10/56 RPR STRT | TABLEMTN | ETL.6070.TOWR | 2022-05-25 | 2022-05-25 | 2023-08-16 | On-Time |  | 2025-05-25 | 2025-05-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644928 | T2 EI RD MTN-TBL MTN #2 010/056 RPR STRT | ICQ
LC | 123690572 | 010/054 | T2NT EI RD MTN-TBL MTN #2 10/54 RPR STRT | TABLEMTN | ETL.6070.TOWR | 2022-05-25 | 2022-05-25 | 2023-08-18 | On-Time |  | 2025-05-25 | 2025-05-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644926 | T2 EI RD MTN-TBL MTN #2 010/054 RPR STRT | ICQ
LC | 123690573 | 010/055 | T2NT EI RD MTN-TBL MTN #2 10/55 RPR GYWS | TABLEMTN | ETL.6070.TOWR | 2022-05-25 | 2022-05-25 | 2023-08-16 | On-Time |  | 2025-05-25 | 2025-05-25 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45700166 | T2 EI RD MTN-TBL MTN #2 010/055 RPR GYWS | ICS
LC | 123691363 | 011/059 | T2NT EI RD MTN-TBL MTN #2 11/59 RPR STRT | TABLEMTN | ETL.6070.TOWR | 2022-05-25 | 2022-05-25 | 2023-08-15 | On-Time |  | 2025-05-25 | 2025-05-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644932 | T2 EI RD MTN-TBL MTN #2 011/059 RPR STRT | ICQ
LC | 123691373 | 011/058 | T2NT EI RD MTN-TBL MTN #2 11/58 RPR STRT | TABLEMTN | ETL.6070.TOWR | 2022-05-25 | 2022-05-25 | 2023-08-15 | On-Time |  | 2025-05-25 | 2025-05-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644931 | T2 EI RD MTN-TBL MTN #2 011/058 RPR STRT | ICQ
LC | 123691773 | 011/060 | T2NT EI RD MTN-TBL MTN #2 11/60 RPR STRT | TABLEMTN | ETL.6070.TOWR | 2022-05-25 | 2022-05-25 | 2023-08-15 | On-Time |  | 2025-05-25 | 2025-05-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644933 | T2 EI RD MTN-TBL MTN #2 011/060 RPR STRT | ICQ
LC | 123693584 | 011/063 | T2NT EI RD MTN-TBL MTN #2 11/63 RPR STRT | TABLEMTN | ETL.6070.TOWR | 2022-05-25 | 2022-05-25 | 2023-08-21 | On-Time |  | 2025-05-25 | 2025-05-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647412 | T2 EI RD MTN-TBL MTN #2 011/063 RPR STRT | ICQ
LC | 123693776 | 011/062 | T2NT EI RD MTN-TBL MTN #2 11/62 RPR STRT | TABLEMTN | ETL.6070.TOWR | 2022-05-25 | 2022-05-25 | 2023-08-21 | On-Time |  | 2025-05-25 | 2025-05-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647410 | T2 EI RD MTN-TBL MTN #2 011/062 RPR STRT | ICQ
LC | 123695075 | 005/106 | T3NT EI COLGATE-CHALLENGE 5/106 RPL HRDW | SACTO | ETL.6480.POLE.NWOD | 2022-05-25 | 2022-05-25 | 2023-05-01 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR3N | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR3N PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 45660974 | T3 EI COLGATE-CHALLENGE 5/106 RPL HRDW | ICW
LC | 123713836 | 008/070 | T3NT DI MDDL FRK-GLD HLL 8/70 BNT STEEL | SACTO | ETL.5140.TOWR | 2022-05-28 | 2022-05-25 | 2023-09-20 | On-Time |  | 2025-05-25 | 2025-05-25 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45600185 | T3 DI MDDL FRK-GLD HLL 8/70 BNT STEEL | ICQ
LC | 123713894 | B017/386 | T3NT DI DRM-GRS VLY-WMR B17/386 RPR STRW | SACTO | ETL.6760.POLE.WOOD | 2022-05-28 | 2022-05-25 | 2023-05-22 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 45685481 | T3 DI DRM-GRS VLY-WEMR B17/386 RPR STRW | ICW
LC | 123722690 | 027/011 | T2NT DI MDCNO-WLTS-FT BRG 27/11 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2022-05-31 | 2022-05-25 | 2023-06-14 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45654654 | T2 DI MDCNO-WLTS-FT BRG 27/11 RPR GYWW | ICW
LC | 123742670 | 008/069 | T3NT DI MDDLE FRK-GLD HLL 8/69 BNT STEEL | SACTO | ETL.5140.TOWR | 2022-06-02 | 2022-05-25 | 2023-09-20 | On-Time |  | 2025-05-25 | 2025-05-25 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45600184 | T3 DI MIDDLE FRK-GLD HLL 8/69 BNT STEEL | ICQ
LC | 123793700 | 001/011 | T2NT DI HAT CRK #1-PIT #1 1/11 RPR STRT | TABLEMTN | ETL.7020.TOWR | 2022-06-08 | 2022-05-25 | 2023-08-24 | On-Time |  | 2025-05-25 | 2025-05-25 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45600103 | T2 DI HAT CREEK #1-PIT #1 1/11 RPR STRT | ICQ
LC | 123909561 | 026/003 | T2NT DI MONTE RIO-FRT RSS 26/3 RPR GYWW | LAKEVLLE | ETL.6979.POLE.NWOD | 2022-06-23 | 2022-05-25 | 2023-08-08 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45575315 | T2 DI MONTE RIO-FORT ROSS 26/3 RPR GYWW | ICW
LC | 128890594 | 006/049 | T2 VACA-VCVLE-JMON-NTH 06/49 TOUCH | LAKEVLLE | ETL.4100.TOWR | 2024-05-25 | 2024-05-25 | 2025-03-28 | On-Time |  | 2024-11-25 | 2025-05-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491088 | T2 VACA-VCVLE-JMON-NTH 06/49 TOUCH | ICQ
LC | 128891581 | 000/006 | T2 EI SPAULDING-SUMMIT 0/6 CANCEL | SACTO | ETL.8060.INSL.NCER | 2024-05-25 | 2024-05-25 | 2024-05-25 | Past Due |  | 2025-05-25 | 2025-05-25 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572864 | T2 EI SPAULDING-SUMMIT 000/006 RPL INSW | 93I
LC | 128901538 | 002/117 | T2 DI SPAULDING-SUMMIT 2/117 COTTER | SACTO | ETL.8060.POLE.NWOD | 2024-05-28 | 2024-05-25 | 2025-04-25 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46398034 | T2 DI SPAULDING-SUMMIT 2/117 COTTER | ICW
LC | 128901971 | 024/187 | T2 DI PRDS-TBL MTN 24/187R RPR GYWW | TABLEMTN | ETL.4316.POLE.STPS | 2024-05-28 | 2024-05-25 | 2024-09-09 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310844 | T2 DI PRDS-TBL MTN 24/187R RPR GYWW | ICW
LC | 128902006 | 009/066 | T2 DI ROCK CREEK-POE 9/66 RPR STRT | TABLEMTN | ETL.5630.TOWR | 2024-05-28 | 2024-05-25 | 2025-03-24 | On-Time |  | 2025-05-25 | 2025-05-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46382011 | T2 DI ROCK CREEK-POE 9/66 RPR STRT | ICQ
LC | 128902344 | B016/376 | T2 DI DRM-GRS VLY-WEMAR-B16/376 RPR STRW | SACTO | ETL.6760.POLE.WOOD | 2024-05-28 | 2024-05-25 | 2025-05-17 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337422 | T2 DI DRM-GRS VLY-WEMAR-B16/376 RPR STRW | ICW
LC | 128902495 | 015/182 | T2 DI KESWICK-TRINITY 15/182C COTTER | TABLEMTN | ETL.7270.POLE.STPS | 2024-05-28 | 2024-05-25 | 2024-09-13 | On-Time |  | 2024-08-25 | 2025-05-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262807 | T2 DI KESWICK-TRINITY 15/182C COTTER | ICW
LC | 128902522 | 009/068 | T2 ROCK CREEK-POE 9/68 RPR INSS | TABLEMTN | ETL.5630.INSL.NCER | 2024-05-28 | 2024-05-25 | 2025-04-27 | On-Time |  | 2025-05-25 | 2025-05-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46383935 | T2 DI ROCK CK-POE 9/68 RPR INSS | ICS
LC | 128902745 | 000/004 | T2 DI COLGATE-ALLEGHANY 0/4 COTTER | SACTO | ETL.6470.POLE.WOOD | 2024-05-28 | 2024-05-25 | 2025-05-06 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46404596 | T2 DI COLGATE-ALLEGHANY 0/4 RPR GYWW | ICW
LC | 128902780 | 002/108 | T2 DI SPAULDING-SUMMIT 2/108 COMPLETE | SACTO | ETL.8060.POLE.NWOD | 2024-05-28 | 2024-05-25 | 2024-06-13 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262109 | T2 DI SPAULDING-SUMMIT 2/108 RPR GYWW | ICW
LC | 128926050 | 015/182 | T2 DI KESWICK-TRINITY 15/182R COTTER | TABLEMTN | ETL.7270.POLE.STPS | 2024-05-30 | 2024-05-25 | 2024-09-13 | On-Time |  | 2024-08-25 | 2025-05-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262819 | T2 DI KESWICK-TRINITY 15/182R COTTER | ICW
LC | 129077114 | B015/358 | T2 DI DRM-GRS VLY-WMR B15/358 RPL STRW | SACTO | ETL.6760.POLE.WOOD | 2024-06-14 | 2024-05-25 | 2025-05-16 | On-Time |  | 2025-05-25 | 2025-05-25 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573454 | T2 DI DRM-GRS VLY-WMR B15/358 RPL STRW | 70Y
LC | 129077117 | 020/415 | T2 DI COLGATE-PALERMO 20/415 RPR STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-06-14 | 2024-05-25 | 2025-02-05 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46398069 | T2 DI COLGATE-PALERMO 20/415 RPR STRW | ICW
LC | 129120210 | B016/360 | T2 DI DRM-GRSS VLLY-WMR B16/360 TOUCH | SACTO | ETL.6760.POLE.NWOD | 2024-06-24 | 2024-05-25 | 2025-03-28 | On-Time |  | 2024-11-25 | 2025-05-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46484975 | T2 DI DRM-GRSS VLLY-WMR B16/360 TOUCH | ICW
LC | 129120671 | B016/362 | T2 DI DRM-GRSS VLLY-WMR B16/362 RPR STRW | SACTO | ETL.6760.POLE.WOOD | 2024-06-24 | 2024-05-25 | 2025-05-16 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46324554 | T2 DI DRM-GRSS VLLY-WMR B16/362 RPR STRW | ICW
LC | 129141548 | 032/005 | T2 DI GRBRVLE LAYTONVILE 32/5 RPR GYWW | WILLITS | ETL.8365.POLE.NWOD | 2024-06-28 | 2024-05-25 | 2025-02-26 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446906 | T2 DI GRBRVLE LAYTONVILE 32/5 RPR GYWW | ICW
LC | 129187805 | B015/359 | T2 DI DRM-GRS VLY-WEMR B15/359 RMV VEG | SACTO | ETL.6760.POLE.NWOD | 2024-07-08 | 2024-05-25 | 2024-05-25 | Past Due |  | 2025-05-25 | 2025-05-25 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129187807 | B015/359 | T2 DI DRM-GRS VLY-WEMR B15/359 INSP STRW | SACTO | ETL.6760.POLE.NWOD | 2024-07-08 | 2024-05-25 | 2024-10-02 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46330893 | T2 DI DRM-GRS VLY-WEMR B15/359 INSP STRW | ICW
LC | 129187865 | 021/174 | T2 DI PIT #1-COTTONWOOD 21/174 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-07-08 | 2024-05-25 | 2025-04-03 | On-Time |  | 2025-05-25 | 2025-05-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381944 | T2 DI PIT #1-COTTONWOOD 21/174 RPR FOND | ICQ
LC | 129193303 | 031/008 | T2 DI GARBRVIL-LYTNVIL 31/08 RPR GYWW | WILLITS | ETL.8365.POLE.NWOD | 2024-07-09 | 2024-05-25 | 2025-02-13 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446905 | T2 DI GARBRVIL-LYTNVIL 31/08 RPR GYWW | ICW
LC | 129193691 | B016/366 | T2 DI DRM GRS VLY-WMR B16/366 TOUCH | SACTO | ETL.6760.POLE.NWOD | 2024-07-09 | 2024-05-25 | 2025-05-16 | On-Time |  | 2024-11-25 | 2025-05-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46484976 | T2 DI DRM GRS VLY-WMR B16/366 TOUCH | ICW
LC | 129862550 | 001/022 | T3 DI DESABLA CNTRVLLE 1/22 RPR CNDW | TABLEMTN | ETL.6720.INSL.NCER | 2024-11-25 | 2024-11-25 | 2025-04-16 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46459954 | T3 DI DESABLA CNTRVLLE 1/22 RPR CNDW | ICW
LC | 129879415 | 004/049 | T3 DI DSBLA-CNTRVLL 4/49 RPR JMPW | TABLEMTN | ETL.6720.INSL.NCER | 2024-11-27 | 2024-11-25 | 2025-04-16 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46459956 | T3 DI DSBLA-CNTRVLL 4/49 RPR JMPW | ICW
LC | 129879417 | 001/020B | T3 DI DSBLA-CNTRVLL 1/20B RPR CNDW | TABLEMTN | ETL.6720.INSL.NCER | 2024-11-27 | 2024-11-25 | 2025-04-16 | On-Time |  | 2025-05-25 | 2025-05-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46459955 | T3 DI DSBLA-CNTRVLL 1/20B RPR CNDW | ICW
LC | 123701497 | 013/072 | T2NT EI RND MT-TBL MT #2 13/72 BNT STEEL | TABLEMTN | ETL.6070.TOWR | 2022-05-26 | 2022-05-26 | 2023-08-01 | On-Time |  | 2025-05-26 | 2025-05-26 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647414 | T2 EI RND MTN-TBL MTN #2 13/72 BNT STEEL | ICQ
LC | 123712792 | 006/035 | T3NT DI RND MTN-TBL MTN #1 6/35 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2022-05-27 | 2022-05-26 | 2023-08-22 | On-Time |  | 2025-05-26 | 2025-05-26 | 564 | TR3N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR3N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 123786425 | 001/027 | T3NT DI KESWICK-TRINITY 001/027 RPL DMPW | TABLEMTN | ETL.7270.INSL.NCER | 2022-06-08 | 2022-05-26 | 2023-05-23 | On-Time |  | 2025-05-26 | 2025-05-26 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR | No Good/Out of Stdrd | Damper-Wood | Replace | 45729330 | T3NT DI KESWICK-TRINITY 001/027 RPL DMPW | ICW
LC | 123852933 | 010/100 | T2NT DI BRDGVLLE-CTTNWD 10/100L RPR ADSS | TABLEMTN | ETL.1110.POLE.STPS | 2022-06-15 | 2022-05-26 | 2023-08-05 | On-Time |  | 2025-05-26 | 2025-05-26 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45644355 | T2 DI BRIDGEVLLE-CTTNWD 10/100L RPR ADSS | ICW
LC | 129879484 | 005/077 | T3 DI DSBLA-CNTRVLL 5/77 RPR CNDW | TABLEMTN | ETL.6720.INSL | 2024-11-27 | 2024-11-26 | 2025-04-14 | On-Time |  | 2025-05-26 | 2025-05-26 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46459957 | T3 DI DSBLA-CNTRVLL 5/77 RPR CNDW | ICW
LC | 123714591 | 087/443 | T2NT DI MLIN-ROUND MTN#2 87/443 RPR STRT | TABLEMTN | ETL.6020.TOWR | 2022-05-28 | 2022-05-27 | 2023-08-23 | On-Time |  | 2025-05-27 | 2025-05-27 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45617403 | T2 DI MLIN-ROUND MTN #2 087/443 RPR STRT | ICQ
LC | 123793382 | 006/055 | T2NT DI PRDS TBL MTN 6/55 BNT STEEL | TABLEMTN | ETL.4316.TOWR | 2022-06-08 | 2022-05-27 | 2023-07-25 | On-Time |  | 2025-05-27 | 2025-05-27 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45617486 | T2 DI PRDS TBL MTN 6/55 BNT STEEL | ICQ
LC | 123821992 | 006/056 | T2NT DI PARADSE-TBLE MTN 6/56 BENT STEEL | TABLEMTN | ETL.4316.TOWR | 2022-06-11 | 2022-05-27 | 2023-07-25 | On-Time |  | 2025-05-27 | 2025-05-27 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45617487 | T2 DI PARADISE-TABLE MTN 6/56 BENT STEEL | ICQ
LC | 125273523 | 001/013 | T3NT DI DRUM-SUMMIT #2 001/013C RPL STRW | SACTO | ETL.1450.POLE.WDPS | 2023-01-03 | 2022-05-27 | 2023-02-22 | On-Time |  | 2025-05-27 | 2025-05-27 | 372 | TR3N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 31634269 | T3 DI DRUM-SUMMIT #2 001/013R RPL STRW | 70Y
LC | 129879185 | ?002/000 | T3 SNTH LNE-HLF MOON BAY ?2/0 RPR CNDW | METCALF | ETL.7212.INSL.NCER | 2024-11-27 | 2024-11-27 | 2024-12-12 | On-Time |  | 2025-05-27 | 2025-05-27 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH FMOB TR3 PRTO | No Good/Out of Stdrd | Conductor-Wood | Repair | 46404058 | T3 SNTH LNE-HLF MOON BAY ?2/0 RPR CNDW | ICW
LC | 128896242 | 001/037 | T2 HAAS-WOODCHUCK 1/37 RPR JMPW | FRESNO | ETL.8730.INSL.NCER | 2024-05-28 | 2024-05-28 | 2024-05-28 | Past Due |  | 2024-08-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46298045 | T2 HAAS-WOODCHUCK 1/37 RPR INSW | ICW
LC | 128896523 | 010/013 | T2 TRINITY-MAPLE CREEK 010/013 RPR INSW | EUREKA | ETL.8170.INSL.NCER | 2024-05-28 | 2024-05-28 | 2025-03-23 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46489387 | T2 TRINITY-MAPLE CREEK 010/013 RPR INSW | ICW
LC | 128898516 | 035/158 | T2 EI MTCLF-MS LDNG #1 35/158 RMV VEG | MOSSLNDG | ETL.5100.TOWR | 2024-05-28 | 2024-05-28 | 2025-04-25 | On-Time |  | 2025-05-28 | 2025-05-28 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128899230 | 006/042A | T2 COTNWOD-DLVN #1 06/42A TOUCH | TABLEMTN | ETL.4550.TOWR | 2024-05-28 | 2024-05-28 | 2024-05-28 | Past Due |  | 2024-11-28 | 2025-05-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491519 | T2 COTNWOD-DLVN #1 06/42A TOUCH | ICQ
LC | 128899977 | 010/083 | T2 EI CRESTA-RIO OSO 010/083 RPL INSS | TABLEMTN | ETL.4590.INSL.CERA | 2024-05-28 | 2024-05-28 | 2025-05-02 | On-Time |  | 2025-05-28 | 2025-05-28 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570419 | T2 EI CRESTA-RIO OSO RPL INSS | 93K
LC | 128900840 | 000/004 | T2 JESSUP TAP 000/004 RPR GYWW | TABLEMTN | ETL.4041.POLE.NWOD | 2024-05-28 | 2024-05-28 | 2024-06-06 | On-Time |  | 2024-08-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46255479 | T2 JESSUP TAP 000/004 RPR GYWW | ICW
LC | 128900855 | C025/099 | T2 EI MOS LNDNG-COBURN C025/099 TOUCH | MOSSLNDG | ETL.5330.TOWR | 2024-05-28 | 2024-05-28 | 2025-03-11 | On-Time |  | 2024-11-28 | 2025-05-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476005 | T2 EI MOS LNDNG-COBURN C025/099 TOUCH | ICQ
LC | 128900955 | 000/006 | T2 JESSUP TAP 000/006 RPR GYWW | TABLEMTN | ETL.4041.POLE.NWOD | 2024-05-28 | 2024-05-28 | 2024-06-06 | On-Time |  | 2024-08-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46255661 | T2 JESSUP TAP 000/006 RPR GYWW | ICW
LC | 128901250 | 014/010 | T2 WV PHILO JCT-ELK 014/010 INS DMPW | WILLITS | ETL.7780.INSL.NCER | 2024-05-28 | 2024-05-28 | 2025-04-26 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46340273 | T2 WV PHILO JCT-ELK 014/010 INS DMPW | ICW
LC | 128901635 | 004/081 | T2 EI CARIBOU-WESTWOOD 4/081 RPR INSW | TABLEMTN | ETL.6300.INSL.NCER | 2024-05-28 | 2024-05-28 | 2025-03-06 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46337441 | T2 EI CARIBOU-WESTWOOD 4/081 RPR INSW | ICW
LC | 128901813 | 037/324 | T2 EI CASCADE-CTTNWD 37/324R RPR OPGW | TABLEMTN | ETL.1240.POLE.STPS | 2024-05-28 | 2024-05-28 | 2024-10-01 | On-Time |  | 2024-08-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Wood | Repair | 46265952 | T2 EI CASCADE-COTTONWOOD 37/324 RPR OPGW | ICW
LC | 128901978 | 018/097 | T2 EI RND MTN-TBL MTN #1 18/97 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-28 | 2024-05-28 | 2025-02-05 | On-Time |  | 2025-05-28 | 2025-05-28 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128901990 | 019/100 | T2 EI RND MTN-TBL MTN #1 19/100 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-28 | 2024-05-28 | 2025-02-04 | On-Time |  | 2025-05-28 | 2025-05-28 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128902347 | 005/045 | T2 ROCK CREEK-POE 005/045 COMPLETE | TABLEMTN | ETL.5630.TOWR | 2024-05-28 | 2024-05-28 | 2025-03-25 | On-Time |  | 2025-05-28 | 2025-05-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46382012 | T2 DI ROCK CREEK-POE 005/045 RPR STRT | ICQ
LC | 128902692 | 023/179A | T2 DI MDLE FRK-GLD HL 23/179A RPR GYWW | SACTO | ETL.5140.POLE.NWOD | 2024-05-28 | 2024-05-28 | 2024-07-29 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305366 | T2 DI MDLE FRK-GLD HL 23/179A RPR GYWW | ICW
LC | 128902695 | 008/059 | T2 DI ROCK CREEK-POE 8/59 RPL HRDT | TABLEMTN | ETL.5630.TOWR | 2024-05-28 | 2024-05-28 | 2025-03-24 | On-Time |  | 2025-05-28 | 2025-05-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46382013 | T2 DI ROCK CREEK-POE 8/59 RPL HRDT | ICQ
LC | 128902698 | 021/166A | T2 DI MID FRK-GOLD HILL 21/166A RPR GYWW | SACTO | ETL.5140.POLE.NWOD | 2024-05-28 | 2024-05-28 | 2024-07-29 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305367 | T2 DI MID FRK-GOLD HILL 21/166A RPR GYWW | ICW
LC | 128902707 | 003/129 | T2 DI SPAULDING-SUMMIT 3/129 RMV VEG | SACTO | ETL.8060.POLE.WOOD | 2024-05-28 | 2024-05-28 | 2024-10-30 | On-Time |  | 2024-08-28 | 2025-05-28 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB DURA | Overgrown | Vegetation | Remove
LC | 128902708 | 004/037 | T2 RE ROCK CREEK-POE 004/037 RPL INSS | TABLEMTN | ETL.5630.INSL | 2024-05-28 | 2024-05-28 | 2025-04-26 | On-Time |  | 2025-05-28 | 2025-05-28 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35572041 | T2 ROCK CREEK-POE RPL INSS 5 TWRS | 93K
LC | 128902709 | 023/179B | T2 DI MDDL FRK-GLD HLL 23/179B COTTER | SACTO | ETL.5140.INSL.NCER | 2024-05-28 | 2024-05-28 | 2024-07-29 | On-Time |  | 2024-08-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46262813 | T2 DI MDDL FRK-GLD HLL 23/179B COTTER | ICW
LC | 128902725 | 008/040 | T2 FULTON-PUEBLO 8/40 RPR STRT | LAKEVLLE | ETL.1600.TOWR | 2024-05-28 | 2024-05-28 | 2024-05-28 | Past Due |  | 2025-05-28 | 2025-05-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46289513 | T2NT DI FULTON-PUEBLO 8/40 RPR STRT | ICQ
LC | 128902753 | 021/166B | T2 DI MIDDLE-FK-GH 21/166B RPR GYWW | SACTO | ETL.5140.POLE.NWOD | 2024-05-28 | 2024-05-28 | 2024-07-29 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305368 | T2 DI MIDDLE-FK-GH 21/166B RPR GYWW | ICW
LC | 128902760 | 007/056 | T2 ROCK CREEK-POE 007/056 RPR STRT | TABLEMTN | ETL.5630.TOWR | 2024-05-28 | 2024-05-28 | 2025-05-17 | On-Time |  | 2025-05-28 | 2025-05-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46257406 | T2 DI ROCK CREEK-POE 007/056 RPR STRT | ICQ
LC | 128902782 | 021/166C | T2 DI MIDDLE FRK-GLD HL 21/166C RPR GYWW | SACTO | ETL.5140.POLE.NWOD | 2024-05-28 | 2024-05-28 | 2024-07-29 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262814 | T2 DI MIDDLE FRK-GLD HL 21/166C RPR GYWW | ICW
LC | 128902813 | 017/011 | T2 DI MENDOCINO-WFB 17/11 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-05-28 | 2024-05-28 | 2025-04-09 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310276 | T2 DI MENDOCINO-WFB 17/11 RPR GYWW | ICW
LC | 128902814 | 017/011 | T2 DI MENDOCINO-WFB 17/11 RPR INSW | WILLITS | ETL.7550.INSL.NCER | 2024-05-28 | 2024-05-28 | 2025-04-09 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46517184 | T2 DI MENDOCINO-WFB 17/11 RPR INSW | ICW
LC | 128902934 | 012/240 | T2 EI HT CRK #1-WSTWD 12/240 RPR POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-28 | 2024-05-28 | 2025-05-03 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46416120 | T2 EI HT CRK #1-WSTWD 12/240 RPR POLE | ICW
LC | 128902948 | 007/050 | T2 DI ROCK CREEK-POE 7/50 RPR JUMS | TABLEMTN | ETL.5630.INSL.NCER | 2024-05-28 | 2024-05-28 | 2024-07-24 | On-Time |  | 2025-05-28 | 2025-05-28 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46256527 | T2 DI ROCK CREEK-POE 7/50 RPR JUMS | ICS
LC | 128902985 | 013/268 | T2 EI HT CRK #1-WSTWD 13/268 RPR POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-28 | 2024-05-28 | 2025-05-02 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46416122 | T2 EI HT CRK #1-WSTWD 13/268 RPR POLE | ICW
LC | 128902987 | 013/254 | T2 EI HT CRK #1-WSTWD 13/254 RPR POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-28 | 2024-05-28 | 2025-05-02 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46416123 | T2 EI HT CRK #1-WSTWD 13/254 RPR POLE | ICW
LC | 128955667 | 112/005 | T2 DI HMBLDT BRGEVIL 112/005 RMV VEG | EUREKA | ETL.1810.POLE.STPS | 2024-05-31 | 2024-05-28 | 2024-10-17 | On-Time |  | 2024-11-28 | 2025-05-28 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 128957312 | 112/005 | T2 HMBLDT BRGEVIL 112/005 RPR JUMW | EUREKA | ETL.1810.INSL.NCER | 2024-05-31 | 2024-05-28 | 2024-05-28 | Past Due |  | 2024-08-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46446427 | T2 DI HMBLDT BRGEVIL 112/005 RPR JUMW | ICW
LC | 128958855 | 007/052 | T2 DI ROCK CREEK-POE 07/52 RPR JUMS | TABLEMTN | ETL.5630.INSL.NCER | 2024-05-31 | 2024-05-28 | 2025-04-27 | On-Time |  | 2025-05-28 | 2025-05-28 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46383936 | T2 DI ROCK CREEK-POE 07/52 RPR JUMS | ICS
LC | 129016176 | 082/000 | T2 DI HUMBLDT-TRINITY 82/000R RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-03 | 2024-05-28 | 2025-04-22 | On-Time |  | 2025-05-28 | 2025-05-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574554 | T2 DI HUMBLDT-TRINITY 82/000L RPL STRW | 70Y
LC | 129016178 | 082/000 | T2 DI HUMBLDT-TRINITY 82/000C RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-03 | 2024-05-28 | 2025-04-22 | On-Time |  | 2025-05-28 | 2025-05-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574554 | T2 DI HUMBLDT-TRINITY 82/000L RPL STRW | 70Y
LC | 129016221 | 082/000 | T2 DI HUMBLDT-TRINITY 82/000L RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-03 | 2024-05-28 | 2025-04-22 | On-Time |  | 2025-05-28 | 2025-05-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574554 | T2 DI HUMBLDT-TRINITY 82/000L RPL STRW | 70Y
LC | 129067479 | 000/002 | T2 DI PIT #3-PIT #1 0/2 RPL HRDT | TABLEMTN | ETL.5400.TOWR | 2024-06-12 | 2024-05-28 | 2025-04-23 | On-Time |  | 2025-05-28 | 2025-05-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46382044 | T2 DI PIT #3-PIT #1 0/2 RPL HRDT | ICQ
LC | 129067753 | 000/003 | T2 DI PIT #3-PIT #1 00/03 RPR INSW | TABLEMTN | ETL.5400.INSL.NCER | 2024-06-12 | 2024-05-28 | 2025-02-10 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46382960 | T2 DI PIT #3-PIT #1 00/03 RPR INSW | ICW
LC | 129078772 | 025/204 | T2 DI PIT #1-COTTONWOOD 25/204 RPR ANCT | TABLEMTN | ETL.5390.TOWR | 2024-06-14 | 2024-05-28 | 2025-05-20 | On-Time |  | 2025-05-28 | 2025-05-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46381914 | T2 DI PIT #1-COTTONWOOD 25/204 RPR ANCT | ICQ
LC | 129078917 | 009/163 | T2 DI PIT#1-HCRK#2-BRN 9/163 GO95 | TABLEMTN | ETL.7040.POLE.WOOD | 2024-06-14 | 2024-05-28 | 2025-05-21 | On-Time |  | 2025-05-28 | 2025-05-28 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35573311 | T2 DI PIT#1-HCRK#2-BRN 9/163 GO95 | 93G
LC | 129087468 | 025/201 | T2 DI PIT #1-COTTONWOOD 25/201 RMV VEG | TABLEMTN | ETL.5390.TOWR | 2024-06-17 | 2024-05-28 | 2025-02-05 | On-Time |  | 2025-05-28 | 2025-05-28 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129120474 | 006/108 | T2 DI PT #1-HT CRK#2-BRNY 6/108 RPR STRW | TABLEMTN | ETL.7040.POLE.WOOD | 2024-06-24 | 2024-05-28 | 2025-05-20 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454362 | T2 DI PT #1-HT CRK#2-BRNY 6/108 RPR STRW | ICW
LC | 129120505 | B025/579 | T2 DI DRM GRS VLY WMAR B25/579 RPR IBWW | SACTO | ETL.6760.INSL.NCER | 2024-06-24 | 2024-05-28 | 2025-05-18 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAR NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46324552 | T2 DI DRM GRS VLY WMAR B25/579 RPR IBWW | ICW
LC | 129120548 | 017/151B | T2 DI CRG VIEW-CSCD 017/151B INSP STRW | TABLEMTN | ETL.1350.POLE.NWOD | 2024-06-24 | 2024-05-28 | 2024-09-06 | On-Time |  | 2024-11-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46272222 | T2 DI CRG VIEW-CSCD 017/151B INSP STRW | ICW
LC | 129120620 | 017/151B | T2 DI CRG VIEW-CSCD 017/151B RPR CNDW | TABLEMTN | ETL.1350.INSL.NCER | 2024-06-24 | 2024-05-28 | 2024-09-06 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46306318 | T2 DI CRG VIEW-CSCD 017/151B RPR CNDW | ICW
LC | 129120628 | 017/151A | T2 DI CRG VIEW-CSCD 017/151A RMV VEG | TABLEMTN | ETL.1350.POLE.NWOD | 2024-06-24 | 2024-05-28 | 2024-08-26 | On-Time |  | 2024-11-28 | 2025-05-28 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 129120728 | 009/003 | T2 DI LOWER LAKE HOMESTAKE 9/3 RPR IBWW | WILLITS | ETL.1481.INSL.CERA | 2024-06-24 | 2024-05-28 | 2025-05-08 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46340271 | T2 DI LOWER LAKE HOMESTAKE 9/3 RPR IBWW | ICW
LC | 129120729 | 004/003 | T2 DI LOWER LAKE HOMESTAKE 4/3 RPR IBWW | WILLITS | ETL.1481.INSL.NCER | 2024-06-24 | 2024-05-28 | 2025-05-07 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46340270 | T2 DI LOWER LAKE HOMESTAKE 4/3 RPR IBWW | ICW
LC | 129120732 | 012/006 | T2 DI FULTON-HOPLAND 12/006 RPR GYWW | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-06-24 | 2024-05-28 | 2025-01-20 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305952 | T2 DI FULTON-HOPLAND 12/006 RPR GYWW | ICW
LC | 129121210 | 006/107 | T2 DI SAN MATEO-HLSDL 06/107 RPR ANCW | METCALF | ETL.7950.POLE.WOOD | 2024-06-24 | 2024-05-28 | 2024-10-23 | On-Time |  | 2024-11-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAR DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46280444 | T2 DI SAN MATEO-HLSDL 06/107 RPR ANCW | ICW
LC | 129121223 | 027/209 | T2 DI MIDDLE FRK-GH 27/209L RPR GYWW | SACTO | ETL.5140.POLE.STPS | 2024-06-24 | 2024-05-28 | 2025-01-29 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46398071 | T2 DI MIDDLE FRK-GH 27/209L RPR GYWW | ICW
LC | 129126871 | 101/001 | T2 DI HMBLT TRNTY 101/001L RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-25 | 2024-05-28 | 2025-04-10 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346001 | T2 DI HMBLT TRNTY 101/001L RPR GYWW | ICW
LC | 129126874 | 101/001 | T2 DI HMBLT TRNTY 101/001C RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-25 | 2024-05-28 | 2025-04-10 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346002 | T2 DI HMBLT TRNTY 101/001C RPR GYWW | ICW
LC | 129126915 | 101/001 | T2 DI HMBLT TRNTY 101/001R RPL HRDW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-25 | 2024-05-28 | 2025-04-10 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46346003 | T2 DI HMBLT TRNTY 101/001R RPL HRDW | ICW
LC | 129126916 | 101/001 | T2 DI HMBLT TRNTY 101/001C RPL HRDW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-25 | 2024-05-28 | 2025-04-10 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46346004 | T2 DI HMBLT TRNTY 101/001C RPL HRDW | ICW
LC | 129126917 | 101/001 | T2 DI HMBLT TRNTY 101/001L RPL HRDW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-25 | 2024-05-28 | 2025-04-10 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46346007 | T2 DI HMBLT TRNTY 101/001L RPL HRDW | ICW
LC | 129127234 | 008/169 | T2 MONTA VSTA-LS GATOS 8/169 RPL POLE | METCALF | ETL.7610.POLE.WOOD | 2024-06-25 | 2024-05-28 | 2024-05-28 | Past Due |  | 2024-11-28 | 2025-05-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35573805 | T2 DI MONTA VSTA-LS GATOS 8/169 RPL POLE | 70Y
LC | 129153988 | 075/005 | T2 DI HMBLDT-TRNTY 75/5L RPL ANCW | EUREKA | ETL.1820.POLE.WDPS | 2024-07-01 | 2024-05-28 | 2025-04-17 | On-Time |  | 2025-05-28 | 2025-05-28 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574558 | T2 DI HMBLDT-TRNTY 75/5L RPL ANCW | 93E
LC | 129154010 | 075/005 | T2 DI HUMBOLDT-TRINITY 75/5R RPL ANCW | EUREKA | ETL.1820.POLE.WDPS | 2024-07-01 | 2024-05-28 | 2025-04-17 | On-Time |  | 2025-05-28 | 2025-05-28 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574558 | T2 DI HMBLDT-TRNTY 75/5L RPL ANCW | 93E
LC | 129154011 | 075/005 | T2 DI HUMBOLDT-TRINITY 75/5C RPL ANCHW | EUREKA | ETL.1820.POLE.WDPS | 2024-07-01 | 2024-05-28 | 2025-04-17 | On-Time |  | 2025-05-28 | 2025-05-28 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574558 | T2 DI HMBLDT-TRNTY 75/5L RPL ANCW | 93E
LC | 129154012 | 075/005 | T2 DI HMBLDT-TRNTY 75/5R RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-07-01 | 2024-05-28 | 2025-04-17 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345999 | T2 DI HMBLDT-TRNTY 75/5R RPR GYWW | ICW
LC | 129154018 | 011/097 | T2 DI CRAG VIEW-CASCADE 11/97 RPL HRDT | TABLEMTN | ETL.1350.TOWR | 2024-07-01 | 2024-05-28 | 2025-04-16 | On-Time |  | 2025-05-28 | 2025-05-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381343 | T2 DI CRAG VIEW-CASCADE 11/97 RPL HRDT | ICQ
LC | 129193296 | 008/039 | T2 DI FULTON-PUEBLO-TOWER 8/39 RPL HRDT | LAKEVLLE | ETL.1600.TOWR | 2024-07-09 | 2024-05-28 | 2025-04-22 | On-Time |  | 2025-05-28 | 2025-05-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289551 | T2 DI FULTON-PUEBLO-TOWER 8/39 RPL HRDT | ICQ
LC | 129193408 | 035/000 | T2 DI MENDOCINO-WLLTS-FRT 35/0 RPR XARM | WILLITS | ETL.7550.POLE.WOOD | 2024-07-09 | 2024-05-28 | 2025-04-04 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46310279 | T2 DI MENDOCINO-WLLTS-FRT 35/0 RPR XARM | ICW
LC | 129193444 | 035/000 | T2 DI MENDOCINO-WLLTS-FRT 35/0 RPR ANCW | WILLITS | ETL.7550.POLE.WOOD | 2024-07-09 | 2024-05-28 | 2025-03-07 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46310320 | T2 DI MENDOCINO-WLLTS-FRT 35/0 RPR ANCW | ICW
LC | 129193526 | 035/000 | T2 DI MENDOCINO-WLLTS-FRT 35/0 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-07-09 | 2024-05-28 | 2025-03-07 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310324 | T2 DI MENDOCINO-WLLTS-FRT 35/0 RPR GYWW | ICW
LC | 129214455 | 005/041 | T2 DI TRINITY-COTTONWOOD 5/41 RMV VEG | TABLEMTN | ETL.4040.POLE.STPS | 2024-07-12 | 2024-05-28 | 2024-05-14 | On-Time |  | 2025-05-28 | 2025-05-28 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129214836 | 008/142 | T2 DI PT#1-HT CRK#2-BURNY 8/142 RPR STRW | TABLEMTN | ETL.7040.POLE.WOOD | 2024-07-12 | 2024-05-28 | 2025-05-21 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454365 | T2 DI PT#1-HT CRK#2-BURNY 8/142 RPR STRW | ICW
LC | 129215759 | 048/419 | T2 DI RND MTN-COTNWD #3 48/419 RPL INSS | TABLEMTN | ETL.5650.INSL | 2024-07-12 | 2024-05-28 | 2025-03-03 | On-Time |  | 2025-05-28 | 2025-05-28 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574240 | T2 ROUND MTN-COTNWD #3 47/411 RPL INSS | 93K
LC | 129215807 | 041/272 | T2 DI TRINTY-COTTONWD 41/272 RPR ANCW | TABLEMTN | ETL.4040.POLE.STPS | 2024-07-12 | 2024-05-28 | 2024-08-19 | On-Time |  | 2025-05-28 | 2025-05-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46305300 | T2 DI TRINTY-COTTONWD 41/272 RPR ANCW | ICW
LC | 129215808 | 041/272 | T2 DI TRINTY-COTTONWD 41/272 RMV VEG | TABLEMTN | ETL.4040.POLE.STPS | 2024-07-12 | 2024-05-28 | 2025-01-17 | On-Time |  | 2025-05-28 | 2025-05-28 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129271638 | 006/070 | T2 WV PIT #5-RND MTN #1 6/70 INS JUMS | TABLEMTN | ETL.5420.INSL.NCER | 2024-07-22 | 2024-05-28 | 2024-07-30 | On-Time |  | 2025-05-28 | 2025-05-28 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB NTDE | Missing | Insulator-Steel | Install | 35570819 | T2 WV PIT #5-RND MTN #1 6/70 INS JUMS | 93K
LC | 128905424 | 069/287 | T2 RND MTN-TBLE MTN #2 69/287 RPR INSS | TABLEMTN | ETL.6070.INSL.NCER | 2024-05-29 | 2024-05-29 | 2025-02-19 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO NTDE PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46306305 | T2 RND MTN-TBLE MTN #2 69/287 RPR INSS | ICS
LC | 128905834 | 007/058 | T2 VACA-VCVL-JMSN-NRTH 7/58 TOUCH | LAKEVLLE | ETL.4100.TOWR | 2024-05-29 | 2024-05-29 | 2025-03-28 | On-Time |  | 2024-11-29 | 2025-05-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485396 | T2 VACA-VCVL-JMSN-NRTH 7/58 TOUCH | ICQ
LC | 128906231 | 008/065 | T2 EI EL DRDO-MSRI FLT #2 8/65 RPR GYWW | SACTO | ETL.1540.POLE.WOOD | 2024-05-29 | 2024-05-29 | 2025-01-29 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46454271 | T2 EI EL DRDO-MSRI FLT #2 8/65 RPR GYWW | ICW
LC | 128906392 | :014/014 | T2 DI EGL RCK CRTNA :14/14 RPL BOND | WILLITS | ETL.1470.POLE.WOOD | 2024-05-29 | 2024-05-29 | 2025-03-12 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46310332 | T2 DI EGL RCK CRTNA :14/14 RPL BOND | ICW
LC | 128906756 | 008/097 | T2 EI DRUM-SUMMIT #2 08/97L COTTER | SACTO | ETL.1450.POLE.WDPS | 2024-05-29 | 2024-05-29 | 2024-06-16 | On-Time |  | 2024-08-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46265567 | T2 EI DRUM-SUMMIT #2 08/97L COTTER | ICW
LC | 128906872 | 001/024 | T2 APPLE HILL #1 1/024 COTTER | SACTO | ETL.1531.INSL.NCER | 2024-05-29 | 2024-05-29 | 2025-01-21 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46398035 | T2 APPLE HILL #1 1/024 COTTER | ICW
LC | 128906959 | 037/168 | T2 EI METCALF-MOS LNDNG #1 37/168 COTTER | MOSSLNDG | ETL.5100.INSL | 2024-05-29 | 2024-05-29 | 2025-04-23 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46391444 | T2 EI METCALF-MOS LNDNG #1 37/168 COTTER | ICS
LC | 128906975 | 008/097 | T2 EI DRUM-SUMMIT #2 08/97C RPR GYWW | SACTO | ETL.1450.POLE.WDPS | 2024-05-29 | 2024-05-29 | 2024-06-16 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46266109 | T2 EI DRUM-SUMMIT #2 08/97C RPR GYWW | ICW
LC | 128907090 | 008/006B | T2 CLR LK-HPLND 8/6B RPR INSW | WILLITS | ETL.6390.INSL.NCER | 2024-05-29 | 2024-05-29 | 2025-05-21 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310501 | T2 CLR LK-HPLND 8/6B RPR INSW | ICW
LC | 128907095 | 008/097 | T2 EI DRUM-SUMMIT #2 08/97R RPR GYWW | SACTO | ETL.1450.POLE.WDPS | 2024-05-29 | 2024-05-29 | 2024-06-16 | On-Time |  | 2024-11-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46266182 | T2 EI DRUM-SUMMIT #2 08/97R RPR GYWW | ICW
LC | 128907208 | 013/063 | T2 MOSS LANDING-COBURN 13/063 RPL INSS | MOSSLNDG | ETL.5330.INSL | 2024-05-29 | 2024-05-29 | 2025-04-07 | On-Time |  | 2025-05-29 | 2025-05-29 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35609254 | T2 MOSS LANDING-COBURN 13/063 RPL INSS | 93K
LC | 128907660 | 003/008 | T2 EI VLLY SPRNG-CLVRS CMNT 3/8 RMV VEG | VICTOR | ETL.8220.POLE.WOOD | 2024-05-29 | 2024-05-29 | 2025-01-15 | On-Time |  | 2025-05-29 | 2025-05-29 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128907691 | 034/219 | T2 CRAZY HRS CNYN-SN BNT 34/219 RMV NEST | MOSSLNDG | ETL.2152.TOWR | 2024-05-29 | 2024-05-29 | 2025-01-10 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | Debris/Nest/etc. | Structure-Steel | Remove | 46391182 | T2 CRAZY HRS CNYN-SN BNT 34/219 RMV NEST | ICS
LC | 128909115 | 026/316C | T2 DRUM-SUMMIT #1 26/316C RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-05-29 | 2024-05-29 | 2025-05-01 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46398036 | T2 EI DRUM-SUMMIT #1 26/316C RPR GYWW | ICW
LC | 128909186 | 026/316B | T2 DRUM-SUMMIT #1 26/316B RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-05-29 | 2024-05-29 | 2025-05-01 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46398037 | T2 EI DRUM-SUMMIT #1 26/316B RPR GYWW | ICW
LC | 128909263 | 026/316A | T2 DRUM-SUMMIT #1 26/316A RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-05-29 | 2024-05-29 | 2025-05-01 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46398038 | T2 EI DRUM-SUMMIT #1 26/316A RPR GYWW | ICW
LC | 128909689 | 037/321 | T2 EI CSCDE-CTTNWOOD 37/321 COTTER | TABLEMTN | ETL.1240.INSL.CERA | 2024-05-29 | 2024-05-29 | 2025-04-09 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46306328 | T2 EI CSCDE-CTTNWOOD 37/321 COTTER | ICW
LC | 128909771 | 017/090 | T2 EI RND MTN-TBL MTN #1 17/90 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-29 | 2024-05-29 | 2025-03-10 | On-Time |  | 2025-05-29 | 2025-05-29 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128909772 | 018/096 | T2 EI RND MTN-TBL MTN #1 18/96 RPR ANCT | TABLEMTN | ETL.6060.TOWR | 2024-05-29 | 2024-05-29 | 2025-04-21 | On-Time |  | 2025-05-29 | 2025-05-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46382014 | T2 EI RND MTN-TBL MTN #1 18/96 RPR ANCT | ICQ
LC | 128909782 | 018/096 | T2 EI RND MTN-TBL MTN #1 18/96 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-29 | 2024-05-29 | 2024-09-10 | On-Time |  | 2025-05-29 | 2025-05-29 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128909784 | 017/093 | T2 EI RND MTN-TBL MTN #1 17/93 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-29 | 2024-05-29 | 2025-01-28 | On-Time |  | 2025-05-29 | 2025-05-29 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128909877 | 017/360 | T2 EI CARIBOU-WESTWOOD 17/360 RPR INSW | TABLEMTN | ETL.6300.INSL.NCER | 2024-05-29 | 2024-05-29 | 2024-07-22 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46280130 | T2 EI CARIBOU-WESTWOOD 17/360 RPR INSW | ICW
LC | 128909955 | 006/005 | T2 DI LOWER LAKE-HOMESTAKE 6/5 RPR STRW | WILLITS | ETL.1481.POLE.WOOD | 2024-05-29 | 2024-05-29 | 2025-05-08 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46340275 | T2 DI LWR LK-HOMESTAKE 6/5 RPR POLE | ICW
LC | 128910442 | 000/005C | T2 ROCK CREEK-POE 0/5C COMPLETE | TABLEMTN | ETL.5630.INSL.CERA | 2024-05-29 | 2024-05-29 | 2025-04-27 | On-Time |  | 2025-05-29 | 2025-05-29 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35572041 | T2 ROCK CREEK-POE RPL INSS 5 TWRS | 93K
LC | 128954366 | 015/119 | T2 DI PIT #1-COTTONWOOD 15/119 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-05-31 | 2024-05-29 | 2025-05-21 | On-Time |  | 2025-05-29 | 2025-05-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381546 | T2 DI PIT #1-COTTONWOOD 15/119 RPR FOND | ICQ
LC | 128960698 | :017/015 | T2 DI EAGLE ROCK CRTNA :17/15 RPR GYWW | WILLITS | ETL.1470.POLE.WOOD | 2024-05-31 | 2024-05-29 | 2024-09-05 | On-Time |  | 2024-08-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46255396 | T2 DI EAGLE ROCK CRTNA 17/15 RPR GYWW | ICW
LC | 128960699 | 008/065 | T2 DI VACA-SUISUN-JMSN 008/065 RPR INSS | SACTO | ETL.4080.INSL.CERA | 2024-05-31 | 2024-05-29 | 2025-03-31 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46324617 | T2 DI VACA-SUISUN-JMSN 008/065 RPR INSS | ICS
LC | 128960863 | :016/000 | T2 DI EAGLE ROCK-CORTINA :16/0 RPR GYWW | WILLITS | ETL.1470.POLE.WOOD | 2024-05-31 | 2024-05-29 | 2025-03-12 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310334 | T2 DI EAGLE ROCK-CORTINA :16/0 RPR GYWW | ICW
LC | 128961092 | 071/362A | T2 DI MALIN RND MTN #2 71/362A RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-05-31 | 2024-05-29 | 2025-02-08 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46338268 | T2 DI MALIN RND MTN #2 71/362A RPR OPGW | ICS
LC | 128961210 | 008/063 | T2 DI VACA-SUISUN 8/63 RPL INSS | SACTO | ETL.4070.INSL.CERA | 2024-05-31 | 2024-05-29 | 2025-03-15 | On-Time |  | 2025-05-29 | 2025-05-29 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577313 | T2 EI VACA-SUISUN RPL INSS 2 TWRS | 93K
LC | 128961988 | 031/223 | T2 DI CARIBOU-TBL MTN 031/223 RPL INSS | TABLEMTN | ETL.4440.INSL.CERA | 2024-05-31 | 2024-05-29 | 2025-04-07 | On-Time |  | 2025-05-29 | 2025-05-29 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569572 | T2 DI CARIBOU-TBL MTN RPL INSS | 93K
LC | 128962336 | 035/282 | T2 DI BRIDGEVIL-COTONWOD 35/282 RPR GRWW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-05-31 | 2024-05-29 | 2025-05-08 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46311084 | T2 DI BRIDGEVIL-COTONWOD 35/282 RPR GRWW | ICW
LC | 128964085 | 018/128 | T2 DI HELMS-GRGG#1 18/128 RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-06-01 | 2024-05-29 | 2024-10-14 | On-Time |  | 2024-11-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46264438 | T2 DI HELMS-GRGG#1 18/128 COTTER | ICS
LC | 128964378 | 015/123 | T2 DI PIT #1-COTTONWOOD 15/123 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-06-01 | 2024-05-29 | 2025-05-21 | On-Time |  | 2025-05-29 | 2025-05-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381871 | T2 DI PIT #1-COTTONWOOD 15/123 RPR STRT | ICQ
LC | 129021463 | :014/000 | T2 DI EAGLE ROCK CORTINA :14/0 RPR GYWW | WILLITS | ETL.1470.POLE.WOOD | 2024-06-04 | 2024-05-29 | 2025-03-12 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310331 | T2 DI EAGLE ROCK CORTINA :14/0 RPR GYWW | ICW
LC | 129026287 | 010/099 | T2 DI PIT#5-ROUND MTN#1 10/99L RPR STRW | TABLEMTN | ETL.5420.POLE.WDPS | 2024-06-05 | 2024-05-29 | 2025-04-08 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454297 | T2 DI PIT#5-ROUND MTN#1 10/99L RPR STRW | ICW
LC | 129031346 | 022/148 | T2 DI POE-RIO OSO 22/148 RPR JUMS | TABLEMTN | ETL.5540.INSL.CERA | 2024-06-06 | 2024-05-29 | 2024-09-17 | On-Time |  | 2024-08-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46265950 | T2 DI POE-RIO OSO 22/148 RPR JUMS | ICS
LC | 129035541 | 021/142 | T2 DI HELMS-GREGG #2 21/142 COTTER | FRESNO | ETL.4880.INSL.CERA | 2024-06-07 | 2024-05-29 | 2025-04-10 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297970 | T2 DI HELMS-GREGG #2 21/142 COTTER | ICS
LC | 129035543 | 021/142 | T2 DI HELMS-GREGG #2 21/142 COTTER | FRESNO | ETL.4870.INSL.CERA | 2024-06-07 | 2024-05-29 | 2025-03-25 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297971 | T2 DI HELMS-GREGG #2 21/142 COTTER | ICS
LC | 129035808 | 019/132 | T2 DI HELMS GREG #1 19/132 RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-06-07 | 2024-05-29 | 2025-03-26 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46297972 | T2 DI HELMS GREG #1 19/132 RPR SHLD | ICS
LC | 129035953 | 019/132 | T2 DI HELMS GREG #1 19/132 COTTER | FRESNO | ETL.4880.INSL.CERA | 2024-06-07 | 2024-05-29 | 2025-04-10 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297973 | T2 DI HELMS GREG #1 19/132 COTTER | ICS
LC | 129035971 | 019/132 | T2 DI HELMS GREG #1 19/132 COTTER | FRESNO | ETL.4870.INSL.NCER | 2024-06-07 | 2024-05-29 | 2025-03-26 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297974 | T2 DI HELMS GREG #1 19/132 COTTER | ICS
LC | 129076969 | :017/012 | T2 EAGLE-RCK-CORTNA :17/12 RPR INSW | WILLITS | ETL.1470.INSL.NCER | 2024-06-14 | 2024-05-29 | 2024-05-29 | Past Due |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR ACCL OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310337 | T2 DI EAGLE-RCK-CORTNA :17/12 RPR INSW | ICW
LC | 129077483 | :018/011 | T2 DI EAGLE ROCK-CORTINA :18/11 RPR STRW | WILLITS | ETL.1470.POLE.WOOD | 2024-06-14 | 2024-05-29 | 2025-03-13 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310339 | T2 DI EAGLE ROCK-CORTINA :18/11 RPR STRW | ICW
LC | 129077484 | :018/011 | T2 DI EAGLE ROCK-CORTINA :18/11 RPL HRDD | WILLITS | ETL.1470.POLE.WOOD | 2024-06-14 | 2024-05-29 | 2025-03-13 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46310500 | T2 DI EAGLE ROCK-CORTINA :18/11 RPL HRDD | ICW
LC | 129078710 | 011/081A | T2 DI HELMS-GREGG #1 11/81A RPR SHIELD | FRESNO | ETL.4870.TOWR | 2024-06-14 | 2024-05-29 | 2024-10-08 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46297975 | T2 DI HELMS-GREGG #1 11/81A RPR SHIELD | ICS
LC | 129087267 | :013/015 | T2 DI EGL RK CRTNA :13/015 RPR GYWW | WILLITS | ETL.1470.POLE.WOOD | 2024-06-17 | 2024-05-29 | 2025-03-12 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCH COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310327 | T2 DI EGL RK CRTNA :13/015 RPR GYWW | ICW
LC | 129087757 | 010/077A | T2 DI HELMS-GREGG #1 10/77A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-06-17 | 2024-05-29 | 2024-09-26 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46297976 | T2 DI HELMS-GREGG #1 10/77A RPR SHLS | ICS
LC | 129105381 | 023/011 | T2 DI KNCTI-MDDLTWN 23/11 RPR IBWW | WILLITS | ETL.6380.INSL.NCER | 2024-06-20 | 2024-05-29 | 2025-03-17 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46340277 | T2 DI KNCTI-MDDLTWN 23/11 RPR IBWW | ICW
LC | 129105766 | 004/058 | T2 DI PT #1-HT CRK#2-BRNY 4/58 RPR STRW | TABLEMTN | ETL.7040.POLE.WOOD | 2024-06-20 | 2024-05-29 | 2025-05-21 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454360 | T2 DI PT #1-HT CRK#2-BRNY 4/58 RPR STRW | ICW
LC | 129120550 | 008/151 | T2 DI PT #1-HT CRK#2-BRNY 8/151 RPR STRW | TABLEMTN | ETL.7040.POLE.WOOD | 2024-06-24 | 2024-05-29 | 2025-05-21 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454363 | T2 DI PT #1-HT CRK#2-BRNY 8/151 RPR STRW | ICW
LC | 129121018 | :013/011 | T2 DI EAGLE ROCK-CORTINA :13/11 RPR IBWW | WILLITS | ETL.1470.INSL.CERA | 2024-06-24 | 2024-05-29 | 2025-03-12 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46310326 | T2 DI EAGLE ROCK-CORTINA :13/11 RPR IBWW | ICW
LC | 129121221 | 019/134 | a2 DI HELMS-GREGG #1 19/134 RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-06-24 | 2024-05-29 | 2025-03-25 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46297977 | T2 DI HELMS-GREGG #1 19/134 RPR SHLD | ICS
LC | 129121222 | 019/134 | T2 DI HELMS-GREGG#1 19/134 RPR INSS | FRESNO | ETL.4870.INSL.CERA | 2024-06-24 | 2024-05-29 | 2025-03-25 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297978 | T2 DI HELMS-GREGG#1 19/134 RPR INSS | ICS
LC | 129121253 | 019/133 | T2 DI HELMS-GREGG #1 19/133 RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-06-24 | 2024-05-29 | 2025-03-25 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46297979 | T2 DI HELMS-GREGG #1 19/133 RPR SHLD | ICS
LC | 129121323 | 020/137 | T2 DI HELMS-GREGG #1 20/137 RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-06-24 | 2024-05-29 | 2025-03-25 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46297980 | T2 DI HELMS-GREGG #1 20/137 RPR SHLD | ICS
LC | 129126867 | :015/005 | T2 DI EAGLE ROCK CORTINA 15/5 RPR GYWW | WILLITS | ETL.1470.POLE.WOOD | 2024-06-25 | 2024-05-29 | 2025-03-13 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310333 | T2 DI EAGLE ROCK CORTINA 15/5 RPR GYWW | ICW
LC | 129127121 | 020/138 | T2 DI HELMS-GREGG #1 20/138 COTTER | FRESNO | ETL.4870.INSL.CERA | 2024-06-25 | 2024-05-29 | 2025-03-25 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297981 | T2 DI HELMS-GREGG #1 20/138 COTTER | ICS
LC | 129127123 | :018/006 | T2 DI EAGLE ROCK-CORTINA :18/6 RPR IBWW | WILLITS | ETL.1470.INSL.CERA | 2024-06-25 | 2024-05-29 | 2025-03-13 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46310338 | T2 DI EAGLE ROCK-CORTINA :18/6 RPR IBWW | ICW
LC | 129127247 | 019/130 | T2 DI HELMS-GREGG #1 19/130 RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-06-25 | 2024-05-29 | 2025-03-26 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46297982 | T2 DI HELMS-GREGG #1 19/130 RPR SHLD | ICS
LC | 129193262 | 010/076A | T2 DI HELMS-GREGG #1 10/76A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-07-09 | 2024-05-29 | 2024-09-26 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46297986 | T2 DI HELMS-GREGG #1 10/76A RPR SHLS | ICS
LC | 129193683 | 021/141 | T2 DI HELMS GREGG #1 21/141 COTTER | FRESNO | ETL.4870.INSL.CERA | 2024-07-09 | 2024-05-29 | 2025-03-25 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297987 | T2 DI HELMS GREGG #1 21/141 COTTER | ICS
LC | 129193745 | 010/078A | T2 DI HELMS-GREGG #1 10/078A RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-07-09 | 2024-05-29 | 2024-10-29 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46297988 | T2 DI HELMS-GREGG #1 10/078A RPR SHLD | ICS
LC | 129193748 | 010/078A | T2 DI HELMS-GREGG #1 10/078A COTTER | FRESNO | ETL.4870.INSL.NCER | 2024-07-09 | 2024-05-29 | 2024-10-29 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297989 | T2 DI HELMS-GREGG #1 10/078A COTTER | ICS
LC | 129193795 | 020/135 | T2 DI HELMS-GREGG #1 20/135 RPR INSS | FRESNO | ETL.4870.INSL.CERA | 2024-07-09 | 2024-05-29 | 2025-03-25 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297990 | T2 DI HELMS-GREGG #1 20/135 RPR INSS | ICS
LC | 129213796 | 023/008 | T2 DI KONOCTI-MIDDLETOWN 23/8 RPL STRW | WILLITS | ETL.6380.POLE.WOOD | 2024-07-12 | 2024-05-29 | 2025-03-18 | On-Time |  | 2025-05-29 | 2025-05-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574116 | T2 DI KONOCTI-MIDDLETOWN 23/8 RPL STRW | 70Y
LC | 129214453 | 030/220 | T2 DI CARIBOU-TABLE MTN 30/220 RPR JUMS | TABLEMTN | ETL.4440.INSL.NCER | 2024-07-12 | 2024-05-29 | 2024-12-20 | On-Time |  | 2024-08-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46328451 | T2 DI CARIBOU-TABLE MTN 30/220 RPR JUMS | ICS
LC | 129250026 | 010/001 | T2 DI LWR LK HMSTK 10/001 RPR STRW | WILLITS | ETL.1481.POLE.WOOD | 2024-07-19 | 2024-05-29 | 2025-05-06 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46340276 | T2 DI LWR LK HMSTK 10/001 RPR STRW | ICW
LC | 129274538 | :017/008 | T2 EGL RCK-CRTNA :17/8 RPL ANCW | WILLITS | ETL.1470.POLE.WOOD | 2024-07-22 | 2024-05-29 | 2025-05-22 | On-Time |  | 2025-05-29 | 2025-05-29 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586902 | T2 DI EGL RCK-CRTNA :17/8 RPL ANCW | 93E
LC | 129274682 | :019/008 | T2 DI EGL RCK-CRTNA :19/8 RPR STRW | WILLITS | ETL.1470.POLE.WOOD | 2024-07-22 | 2024-05-29 | 2024-05-29 | Past Due |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW ACCM OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Repair | 46401508 | T2 DI EGL RCK-CRTNA :19/8 RPR STRW | ICW
LC | 129280023 | 020/140 | T2 DI HELMS-GREGG #1 20/140 RPR SHIELD | FRESNO | ETL.4870.TOWR | 2024-07-23 | 2024-05-29 | 2025-03-25 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46343226 | T2 DI HELMS-GREGG #1 20/140 RPR SHIELD | ICS
LC | 129280132 | :016/009 | T2 DI EAGLE ROCK-CORTINA :16/9 RPL HRDW | WILLITS | ETL.1470.POLE.WOOD | 2024-07-23 | 2024-05-29 | 2024-05-29 | Past Due |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW SPCR ACCL OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46401506 | T2 DI EAGLE ROCK-CORTINA :16/9 RPL HRDW | ICW
LC | 129280257 | :018/007 | T2 DI EAGLE ROCK-CORTINA :18/7 RPR IBWW | WILLITS | ETL.1470.INSL.CERA | 2024-07-23 | 2024-05-29 | 2025-03-13 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CUSI ACCL COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46401507 | T2 DI EAGLE ROCK-CORTINA :18/7 RPR IBWW | ICW
LC | 129280293 | 007/060A | T2 DI HELMS-GREGG #1 007/060A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-07-23 | 2024-05-29 | 2025-06-02 | Past Due |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46343227 | T2 DI HELMS-GREGG #1 007/060A RPR SHLS | ICS
LC | 129280312 | 018/126 | T2 DI HELMS-GREGG #1 018/126 RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-07-23 | 2024-05-29 | 2025-03-27 | On-Time |  | 2025-05-29 | 2025-05-29 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46343228 | T2 DI HELMS-GREGG #1 018/126 RPR SHLS | ICS
LC | 129280325 | :015/002 | T2 DI EAGLE ROCK-CORTINA :15/2 RPL HRDW | WILLITS | ETL.1470.POLE.WOOD | 2024-07-23 | 2024-05-29 | 2025-03-13 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46401504 | T2 DI EAGLE ROCK-CORTINA :15/2 RPL HRDW | ICW
LC | 129305150 | 018/001 | T2 DI HMBLDT BAY-RO DL JCT 18/1 RPL HRDW | EUREKA | ETL.7100.POLE.WOOD | 2024-07-29 | 2024-05-29 | 2025-03-13 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46403063 | T2 DI HMBLDT BAY-RO DL JCT 18/1 RPL HRDW | ICW
LC | 129306610 | 024/197 | T2 DI PIT #1-CTNWD-24/197 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2024-07-29 | 2024-05-29 | 2025-04-04 | On-Time |  | 2025-05-29 | 2025-05-29 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46452775 | T2 DI PIT #1-CTNWD-24/197 BNT STEEL | ICQ
LC | 129306676 | 024/006 | T2 DI KONOCTI MDLTWN+ 24/06 RPR STRW | WILLITS | ETL.6380.POLE.WOOD | 2024-07-29 | 2024-05-29 | 2025-03-20 | On-Time |  | 2025-05-29 | 2025-05-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46402744 | T2 DI KONOCTI MDLTWN+ 24/06 RPR STRW | ICW
LC | 130785134 | 000/005A | T2 ROCK CREEK-POE 0/5A COMPLETE | TABLEMTN | ETL.5630.INSL.CERA | 2025-01-23 | 2024-05-29 | 2025-04-27 | On-Time |  | 2025-05-29 | 2025-05-29 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35612879 | T2 ROCK CREEK-POE 0/5A RPL INSS | 93K
LC | 130785135 | 000/005B | T2 ROCK CREEK-POE 0/5B COMPLETE | TABLEMTN | ETL.5630.INSL.CERA | 2025-01-23 | 2024-05-29 | 2025-04-27 | On-Time |  | 2025-05-29 | 2025-05-29 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35612879 | T2 ROCK CREEK-POE 0/5A RPL INSS | 93K
LC | 128911198 | 007/055 | T2 VACA-VCVL-JMSN-NRTH 7/55 TOUCH | LAKEVLLE | ETL.4100.TOWR | 2024-05-30 | 2024-05-30 | 2025-05-07 | On-Time |  | 2024-11-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485397 | T2 VACA-VCVL-JMSN-NRTH 7/55 TOUCH | ICQ
LC | 128912398 | 057/245 | T2 EI METCLF-MOS LNDING #1 57/245 MASTIC | MOSSLNDG | ETL.5100.TOWR | 2024-05-30 | 2024-05-30 | 2025-04-28 | On-Time |  | 2025-05-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416702 | T2 EI METCLF-MOS LNDING #1 57/245 MASTIC | ICQ
LC | 128912556 | 003/002 | T2 EI VLY SPRNG-CLVRS CMNT 3/2 RPR GYWW | VICTOR | ETL.8220.POLE.NWOD | 2024-05-30 | 2024-05-30 | 2025-03-06 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327023 | T2 EI VLY SPRNG-CLVRS CMNT 3/2 RPR GYWW | ICW
LC | 128912898 | 027/223 | T2 EI CRESTA-RIO OSO 27/223 RPL INSS | TABLEMTN | ETL.4590.INSL.CERA | 2024-05-30 | 2024-05-30 | 2025-04-29 | On-Time |  | 2025-05-30 | 2025-05-30 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570419 | T2 EI CRESTA-RIO OSO RPL INSS | 93K
LC | 128913944 | 027/223 | T2 EI CRESTA-RIO OSO 27/223 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-30 | 2024-05-30 | 2025-03-27 | On-Time |  | 2025-05-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381337 | T2 EI CRESTA-RIO OSO 27/223 RPR FOND | ICQ
LC | 128914885 | 010/121B | T2 EI DRUM-SUMMIT #2 010/121B RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-05-30 | 2024-05-30 | 2025-04-24 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458325 | T2 EI DRUM-SUMMIT #2 010/121B RPR GYWW | ICW
LC | 128915372 | 027/220 | T2 EI CRESTA-RIO OSO 27/220 RMV VEG | TABLEMTN | ETL.4590.TOWR | 2024-05-30 | 2024-05-30 | 2025-04-07 | On-Time |  | 2025-05-30 | 2025-05-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128915377 | 027/224 | T2 CRESTA-RIO OSO 27/224 RMV NEST | TABLEMTN | ETL.4590.TOWR | 2024-05-30 | 2024-05-30 | 2024-05-30 | Past Due |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46337446 | T2 EI CRESTA-RIO OSO 27/224 RMV NEST | ICS
LC | 128915378 | 027/224 | T2 EI CRESTA-RIO OSO 27/224 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-30 | 2024-05-30 | 2025-03-27 | On-Time |  | 2025-05-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381338 | T2 EI CRESTA-RIO OSO 27/224 RPR FOND | ICQ
LC | 128915416 | 035/160 | T2 EI MTCLF-MS LDNG #1 35/160 RMV VEG | MOSSLNDG | ETL.5100.TOWR | 2024-05-30 | 2024-05-30 | 2025-05-21 | On-Time |  | 2025-05-30 | 2025-05-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128916272 | 001/029 | T2 EI CTONWD-PANORAMA 01/29 RMV VEG | TABLEMTN | ETL.1340.POLE.NWOD | 2024-05-30 | 2024-05-30 | 2025-02-06 | On-Time |  | 2025-05-30 | 2025-05-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128916781 | 027/221 | T2 EI CRESTA-RIO OSO 27/221 RPL INSS | TABLEMTN | ETL.4590.INSL.CERA | 2024-05-30 | 2024-05-30 | 2025-04-28 | On-Time |  | 2025-05-30 | 2025-05-30 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570419 | T2 EI CRESTA-RIO OSO RPL INSS | 93K
LC | 128917093 | 079/322 | T2 EI RND MTN-TBLE MTN#1 79/322 RPR STRT | TABLEMTN | ETL.6060.TOWR | 2024-05-30 | 2024-05-30 | 2024-05-30 | Past Due |  | 2025-05-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310397 | T2 EI RND MTN-TBLE MTN#1 79/322 RPR STRT | ICQ
LC | 128917349 | 003/007 | T2 EI VLLY SPRNG-CLVRS CMNT 3/7 RPL HRDW | VICTOR | ETL.8220.POLE.WOOD | 2024-05-30 | 2024-05-30 | 2025-03-06 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46327024 | T2 EI VLLY SPRNG-CLVRS CMNT 3/7 RPL HRDW | ICW
LC | 128918936 | 028/225 | T2 EI CRESTA-RIO OSO 28/225 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-30 | 2024-05-30 | 2025-03-27 | On-Time |  | 2025-05-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381339 | T2 EI CRESTA-RIO OSO 28/225 RPR FOND | ICQ
LC | 128921365 | 009/072 | T2 VACA-VCVL-CRDLIA 9/72 RPR INSS | SACTO | ETL.4090.INSL.CERA | 2024-05-30 | 2024-05-30 | 2025-05-16 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46403757 | T2 VACA-VCVL-CRDLIA 9/72 RPR INSS | ICS
LC | 128921701 | 003/020 | T2 EI MONTA VISTA-CYTE SS 03/20 RMV NEST | MOSSLNDG | ETL.5090.TOWR | 2024-05-30 | 2024-05-30 | 2025-03-21 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46391183 | T2 EI MONTA VISTA-CYTE SS 03/20 RMV NEST | ICS
LC | 128922499 | 035/161 | T2 EI MTCLF-MS LDNG #1 35/161 RMV VEG | MOSSLNDG | ETL.5100.TOWR | 2024-05-30 | 2024-05-30 | 2025-04-25 | On-Time |  | 2025-05-30 | 2025-05-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128923000 | 035/161 | T2 EI MTCLF-MS LDNG #1 35/161 COMPLETE | MOSSLNDG | ETL.5100.INSL | 2024-05-30 | 2024-05-30 | 2024-07-26 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46256382 | T2 EI MTCLF-MS LDNG #1 35/161 COTTER | ICS
LC | 128923796 | 035/222 | T2 CRAZY HORSE CYN-HOLLSTR 35/222 COTTER | MOSSLNDG | ETL.2153.INSL.CERA | 2024-05-30 | 2024-05-30 | 2024-07-15 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46256383 | T2 CRAZY HORSE CYN-HOLLSTR 35/222 COTTER | ICS
LC | 128926601 | 020/234A | T2 DRUM-SUMMIT #1 20/234A COMPLETE | SACTO | ETL.1440.POLE.NWOD | 2024-05-30 | 2024-05-30 | 2025-05-01 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46398060 | T2 DRUM-SUMMIT #1 20/234A RPR GYWW | ICW
LC | 128927956 | 001/026 | T2 EI CTONWOD-PANORAMA 01/26 RMV VEG | TABLEMTN | ETL.1340.POLE.NWOD | 2024-05-30 | 2024-05-30 | 2025-02-06 | On-Time |  | 2025-05-30 | 2025-05-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128927993 | 003/005 | T2 EI VLY SPRNG-CLVRS CMNT 3/5 RPR INSW | VICTOR | ETL.8220.INSL.NCER | 2024-05-30 | 2024-05-30 | 2024-08-28 | On-Time |  | 2024-08-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46265932 | T2 EI VLY SPRNG-CLVRS CMNT 3/5 RPR INSW | ICW
LC | 128929820 | 016/098 | T2 MOSS LANDING-DEL MONTE#1 16/98 COTTER | MOSSLNDG | ETL.2830.INSL.NCER | 2024-05-30 | 2024-05-30 | 2024-07-26 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46256385 | T2 MOSS LANDING-DEL MONTE#1 16/98 COTTER | ICS
LC | 128933379 | 005/025A | T2 PTTSBRG-SAN RAMON 05/025A TOUCH | CONCORD | ETL.5490.POLE.NWOD | 2024-05-30 | 2024-05-30 | 2025-05-19 | On-Time |  | 2024-11-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491566 | T2 WV PITSBRG-SAN RAMON 05/025A TOUCH | ICS
LC | 128935478 | 003/073 | T2 WV DEL MONTE-VIEJO 3/073 INS DAMW | MOSSLNDG | ETL.6710.INSL.NCER | 2024-05-30 | 2024-05-30 | 2025-04-18 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46329997 | T2 WV DEL MONTE-VIEJO 3/073 INS DAMW | ICW
LC | 128935526 | 036/311 | T2 EI CASCADE-CTTNWD 36/311L RPR GYWW | TABLEMTN | ETL.1240.POLE.STPS | 2024-05-30 | 2024-05-30 | 2025-04-09 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46383865 | T2 EI CASCADE-CTTNWD 36/311L RPR GYWW | ICW
LC | 128935558 | 036/311 | T2 EI CASCADE-CTTNWD 36/311C RPR GYWW | TABLEMTN | ETL.1240.POLE.STPS | 2024-05-30 | 2024-05-30 | 2025-04-09 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46383866 | T2 EI CASCADE-CTTNWD 36/311C RPR GYWW | ICW
LC | 128935563 | 036/311 | T2 EI CASCADE-CTTNWD 36/311R COMPLETE | TABLEMTN | ETL.1240.POLE.STPS | 2024-05-30 | 2024-05-30 | 2025-04-09 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46383867 | T2 EI CASCADE-CTTNWD 36/311R RPR GYWW | ICW
LC | 128935724 | 071/362 | T2 EI MALIN-RND MTN #2 71/362 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-05-30 | 2024-05-30 | 2025-02-08 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | OPGW - Steel | Repair | 46338266 | T2 EI MALIN-RND MTN #2 71/362 RPR OPGW | ICS
LC | 128935894 | 043/839 | T2 EI HAT CRK #1-WSTWD 43/839 INS ANMW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-30 | 2024-05-30 | 2024-07-26 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Animal Guard-Wood | Install | 46305293 | T2 EI HAT CRK #1-WSTWD 43/839 INS ANMW | ICW
LC | 128935895 | 043/843 | T2 HAT CRK #1-WESTWD 43/843 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-30 | 2024-05-30 | 2025-05-28 | On-Time |  | 2025-05-30 | 2025-05-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574518 | T2 EI HAT CRK #1-WESTWD 43/843 RPL STRW | 70Y
LC | 128935912 | 043/841 | T2 EI HAT CRK #1-WSTWD 43/841 INS ANMW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-30 | 2024-05-30 | 2025-05-21 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Animal Guard-Wood | Install | 46416126 | T2 EI HAT CRK #1-WSTWD 43/841 INS ANMW | ICW
LC | 128935921 | 043/844 | T2 EI HAT CRK #1-WESTWD 43/844 INS ANMW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-30 | 2024-05-30 | 2024-07-26 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Animal Guard-Wood | Install | 46287525 | T2 EI HAT CRK #1-WESTWD 43/844 INS ANMW | ICW
LC | 128937716 | 012/066 | T2 RND MTN-TBLE MTN #2 12/66 RPR ANCT | TABLEMTN | ETL.6070.TOWR | 2024-05-30 | 2024-05-30 | 2025-04-21 | On-Time |  | 2025-05-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46382015 | T2 EI RND MTN-TBLE MTN #2 12/66 RPR ANCT | ICQ
LC | 128937730 | 012/065 | T2 EI RND MTN-TBL MTN #1 12/65 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-05-30 | 2024-05-30 | 2025-01-28 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306306 | T2 EI RND MTN-TBL MTN #1 12/65 RMV NEST | ICS
LC | 128937739 | 013/069 | T2 ROUND MTN-TABLE MTN #2 13/69 RPR ANCT | TABLEMTN | ETL.6070.TOWR | 2024-05-30 | 2024-05-30 | 2025-04-21 | On-Time |  | 2025-05-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46452736 | T2 EI RND MTN-TBLE MTN #2 13/69 RPR ANCT | ICQ
LC | 128937757 | 012/065 | T2 RG RND MTN-TBL MTN #1 12/65 RPL ANCT | TABLEMTN | ETL.6060.TOWR | 2024-05-30 | 2024-05-30 | 2025-05-29 | On-Time |  | 2025-05-30 | 2025-05-30 | 93Z | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716792 | T2 EI RND MTN-TBL MTN #1 12/65 RPL ANCT | 93Z
LC | 128937759 | 013/068 | T2 EI RND MTN-TBL MTN #1 13/68 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-05-30 | 2024-05-30 | 2024-07-01 | On-Time |  | 2025-05-30 | 2025-05-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128938222 | 028/227 | T2 EI CRESTA-RIO OSO 28/227 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2024-05-31 | 2024-05-30 | 2025-03-27 | On-Time |  | 2025-05-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381340 | T2 EI CRESTA-RIO OSO 28/227 RPR FOND | ICQ
LC | 128938224 | 035/159 | T2 EI MTCLF-MS LDNG #1 35/159 RMV VEG | MOSSLNDG | ETL.5100.TOWR | 2024-05-31 | 2024-05-30 | 2025-04-28 | On-Time |  | 2025-05-30 | 2025-05-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128938232 | 028/226 | T2 EI CRESTA-RIO OSO 28/226 RPL INSS | TABLEMTN | ETL.4590.INSL.CERA | 2024-05-31 | 2024-05-30 | 2025-04-29 | On-Time |  | 2025-05-30 | 2025-05-30 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570419 | T2 EI CRESTA-RIO OSO RPL INSS | 93K
LC | 128947331 | 003/004 | T2 VALLY SPRNG-CALAVRS CMNT 3/4 RPR GYWW | VICTOR | ETL.8220.POLE.WOOD | 2024-05-31 | 2024-05-30 | 2025-05-29 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46327027 | T2 EI VLY SPRNG-CLVRS CMNT 3/4 RPR GYWW | ICW
LC | 128960186 | 100/001 | 122 DI HUMBOLDT-TRINITY 100/1R RPR STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-05-31 | 2024-05-30 | 2025-04-19 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46346016 | T2 DI HUMBOLDT-TRINITY 100/1R RPR STRW | ICW
LC | 128960835 | 028/241 | T2 DI BRIDGEVILLE-COTT 28/241 RPR JUMW | TABLEMTN | ETL.1110.INSL.NCER | 2024-05-31 | 2024-05-30 | 2025-04-28 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262821 | T2 DI BRIDGEVILLE-COTT 28/241 RPR JUMW | ICW
LC | 128960956 | 068/347 | T2 DI MLN RD MTN#2 68/347 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-05-31 | 2024-05-30 | 2025-01-31 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46338267 | T2 DI MLN RD MTN#2 68/347 RPR OPGW | ICS
LC | 128961622 | 043/289B | T2 DI TRINITY CTNWOOD 43/289B RPR JMPW | TABLEMTN | ETL.4040.INSL.NCER | 2024-05-31 | 2024-05-30 | 2025-02-26 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46471241 | T2 DI TRINITY CTNWOOD 43/289B RPR JMPW | ICW
LC | 128961625 | 086/004C | T2 DI HUMBOLDT-TRINITY 86/004C RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-05-31 | 2024-05-30 | 2024-08-27 | On-Time |  | 2024-08-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262168 | T2 DI HUMBOLDT-TRINITY 86/004C RPR JUMW | ICW
LC | 128961627 | 086/004B | T2 DI HUMBOLT TRINITY 86/4B RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-05-31 | 2024-05-30 | 2024-08-27 | On-Time |  | 2024-08-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262167 | T2 DI HUMBOLT TRINITY 86/4B RPR JUMW | ICW
LC | 128961713 | 043/289C | T2 DI TRINITY-CTTNWD 043/289C RPR JMPW | TABLEMTN | ETL.4040.INSL.NCER | 2024-05-31 | 2024-05-30 | 2025-02-26 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46471242 | T2 DI TRINITY-CTTNWD 043/289C RPR JMPW | ICW
LC | 128961866 | 025/218 | T2 DI BRDVL CTTNWD 25/218L RPL HRDW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-05-31 | 2024-05-30 | 2025-04-27 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46311080 | T2 DI BRDVL CTTNWD 25/218L RPL HRDW | ICW
LC | 128961887 | 043/289A | T2 DI TRINITY-CTTNWD 043/289A RPR JMPW | TABLEMTN | ETL.4040.INSL.NCER | 2024-05-31 | 2024-05-30 | 2025-02-26 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46471240 | T2 DI TRINITY-CTTNWD 043/289A RPR JMPW | ICW
LC | 128961937 | 086/004A | T2 DI HMBLDT-TRINITY 086/004A RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-05-31 | 2024-05-30 | 2024-08-27 | On-Time |  | 2024-08-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46255666 | T2 DI HMBLDT-TRINITY 086/004A RPR JUMW | ICW
LC | 128962018 | 010/004 | T2 DI FLTN HPLND 10/004 RPR INSW | LAKEVLLE | ETL.6890.INSL.NCER | 2024-05-31 | 2024-05-30 | 2024-07-13 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46255772 | T2 DI FLTN HPLND 10/004 RPR INSW | ICW
LC | 128962469 | 021/323 | T2 DI KESWICK-TRINITY 21/323 GO95 | TABLEMTN | ETL.7270.POLE.WOOD | 2024-05-31 | 2024-05-30 | 2025-04-12 | On-Time |  | 2025-05-30 | 2025-05-30 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35573315 | T2 DI KESWICK-TRINITY 21/323 GO95 | 93G
LC | 128964468 | 013/117 | T2 DI CRG VIEW-CSCD 013/117 RPR OPGW | TABLEMTN | ETL.1350.TOWR | 2024-06-01 | 2024-05-30 | 2025-03-20 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | OPGW - Steel | Repair | 46452800 | T2 DI CRG VIEW-CSCD 013/117 RPR OPGW | ICS
LC | 128964514 | 013/117 | T2 DI CRG VIEW-CSCD 013/117 TOUCH | TABLEMTN | ETL.1350.TOWR | 2024-06-01 | 2024-05-30 | 2025-03-12 | On-Time |  | 2024-08-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478263 | T2 DI CRG VIEW-CSCD 013/117 TOUCH | ICQ
LC | 128964518 | 013/174 | T2 DLTA-MTN GT JCT 013/174 RPL JMPW | TABLEMTN | ETL.6750.INSL.NCER | 2024-06-01 | 2024-05-30 | 2025-06-10 | Past Due |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Steel | Repair | 46452732 | T2 DI DLTA-MTN GT JCT 013/174 RPL JMPW | ICS
LC | 128980538 | 025/218 | T2 DI BRDVL CTTNWD 25/218R RPL HRDW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-06-03 | 2024-05-30 | 2025-04-27 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46311082 | T2 DI BRDVL CTTNWD 25/218R RPL HRDW | ICW
LC | 129016113 | 018/003 | T2 DI KONOCTI-MIDDLETOWN 18/3 RPR GYWW | WILLITS | ETL.6380.POLE.NWOD | 2024-06-03 | 2024-05-30 | 2025-03-18 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46340401 | T2 DI KONOCTI-MIDDLETOWN 18/3 RPR GYWW | ICW
LC | 129026411 | 004/051 | T2 DI HAT CREEK #1-PIT #1 4/51 RPL STRW | TABLEMTN | ETL.7020.POLE.WOOD | 2024-06-05 | 2024-05-30 | 2025-05-07 | On-Time |  | 2025-05-30 | 2025-05-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574667 | T2 DI HAT CREEK #1-PIT #1 4/51 RPL STRW | 70Y
LC | 129035619 | 026/228 | T2 DI BRDGVLE-COTNWOD 26/228L RPR GYWW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-06-07 | 2024-05-30 | 2025-04-27 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311076 | T2 DI BRDGVLE-COTNWOD 26/228L RPR GYWW | ICW
LC | 129035668 | 026/228 | T2 DI BRDGVLE-COTNWOD 26/228C RPR IBWW | TABLEMTN | ETL.1110.INSL.NCER | 2024-06-07 | 2024-05-30 | 2025-04-27 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46311077 | T2 DI BRDGVLE-COTNWOD 26/228C RPR IBWW | ICW
LC | 129035837 | 085/004C | T2 DI HUMBOLDT-TRINITY 85/4C RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-07 | 2024-05-30 | 2025-04-22 | On-Time |  | 2024-11-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46264481 | T2 DI HUMBOLDT-TRINITY 85/4C RPR GYWW | ICW
LC | 129087787 | 000/001 | T2 HAT CREEK#1-WSTWD 0/1 RPR STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-17 | 2024-05-30 | 2025-05-13 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46416134 | T2 DI HAT CREEK#1-WSTWD 0/1 RPR STRW | ICW
LC | 129087878 | 029/213 | T2 DI CARIBOU-TBLE MNTN 29/213 RPR JUMS | TABLEMTN | ETL.4440.INSL.NCER | 2024-06-17 | 2024-05-30 | 2025-04-06 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46337592 | T2 DI CARIBOU-TBLE MNTN 29/213 RPR JUMS | ICS
LC | 129088103 | 014/122 | T2 DI CRAG VIEW-CAS 14/122L RPR ANCW | TABLEMTN | ETL.1350.POLE.STPS | 2024-06-17 | 2024-05-30 | 2025-03-20 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46454299 | T2 DI CRAG VIEW-CAS 14/122L RPR ANCW | ICW
LC | 129088181 | 033/243 | T2 DI CARIBOU-TBLE MNTN 33/243 RPR JUMS | TABLEMTN | ETL.4440.INSL.NCER | 2024-06-17 | 2024-05-30 | 2025-04-07 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46337593 | T2 DI CARIBOU-TBLE MNTN 33/243 RPR JUMS | ICS
LC | 129088182 | 033/243 | T2 DI CARIBOU-TBLE MNTN 33/243 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2024-06-17 | 2024-05-30 | 2025-03-26 | On-Time |  | 2025-05-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354065 | T2 DI CARIBOU-TBLE MNTN 33/243 RPR STRT | ICQ
LC | 129088313 | 038/251C | T2 DI TRINITY-CTNWD 38/251C RPR GYWW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-06-17 | 2024-05-30 | 2024-08-23 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305298 | T2 DI TRINITY-CTNWD 38/251C RPR GYWW | ICW
LC | 129088315 | 038/251B | T2 DI TRINITY-CTNWD 38/251B RPR GYWW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-06-17 | 2024-05-30 | 2024-08-23 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305299 | T2 DI TRINITY-CTNWD 38/251B RPR GYWW | ICW
LC | 129120788 | 014/099A | T2 DI IGCO-ALTO-SSLTO #1 14/99A RPR GYWW | LAKEVLLE | ETL.7160.POLE.WOOD | 2024-06-24 | 2024-05-30 | 2025-02-12 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46403758 | T2 DI IGCO-ALTO-SSLTO #1 14/99A RPR GYWW | ICW
LC | 129121193 | 039/310 | T2 DI BRDGVL CTNWD 9/310L RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-06-24 | 2024-05-30 | 2025-02-17 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311070 | T2 DI BRDGVL CTNWD 9/310L RPR GYWW | ICW
LC | 129121196 | 039/310 | T2 DI BRDGVL CTNWD 9/310R RPR GYWW | TABLEMTN | ETL.1110.POLE.STPS | 2024-06-24 | 2024-05-30 | 2025-02-17 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311069 | T2 DI BRDGVL CTNWD 9/310R RPR GYWW | ICW
LC | 129127000 | 005/024 | T2 DI HMBLDT BAY-HMBLDT#1 5/24 RPL HRDT | EUREKA | ETL.1800.TOWR | 2024-06-25 | 2024-05-30 | 2025-03-12 | On-Time |  | 2025-05-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289236 | T2 DI HMBLDT BAY-HMBLDT#1 5/24 RPL HRDT | ICQ
LC | 129127001 | 005/024 | T2 DI HUMBLDT BAY-HMBLDT#1 5/24 RPR CNDS | EUREKA | ETL.7090.INSL.NCER | 2024-06-25 | 2024-05-30 | 2025-03-11 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Steel | Repair | 46305953 | T2 DI HUMBLDT BAY-HMBLDT#1 5/24 RPR CNDS | ICS
LC | 129127160 | 033/242 | T2 DI CARIBOU-TABLE MTN 33/242 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2024-06-25 | 2024-05-30 | 2025-03-26 | On-Time |  | 2025-05-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Missing | Hardware-Tower | Install | 46354066 | T2 DI CARIBOU-TABLE MTN 33/242 RPL HRDT | ICQ
LC | 129134234 | 069/350A | T2 DI MALIN-ROUND TBL 69/350A RPR SHLS | TABLEMTN | ETL.6020.TOWR | 2024-06-26 | 2024-05-30 | 2025-02-25 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338278 | T2 DI MALIN-ROUND TBL 69/350A RPR SHLS | ICS
LC | 129134352 | 099/001 | T2 DI HMBLT TRNTY 99/001 RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-26 | 2024-05-30 | 2025-04-19 | On-Time |  | 2025-05-30 | 2025-05-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574492 | T2 DI HMBLT TRNTY 99/001 RPL STRW | 70Y
LC | 129134355 | 099/001 | T2 DI HMBLT TRNTY 99/001 RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-26 | 2024-05-30 | 2025-04-19 | On-Time |  | 2025-05-30 | 2025-05-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574492 | T2 DI HMBLT TRNTY 99/001 RPL STRW | 70Y
LC | 129134413 | 016/111 | T2 IGNCIO-ALT-SSLT#2 16/111 RMV VEG | LAKEVLLE | ETL.7170.POLE.WOOD | 2024-06-26 | 2024-05-30 | 2024-05-30 | Past Due |  | 2025-05-30 | 2025-05-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129134470 | 013/009 | T2 DI KONOCTI MDDLTWN 13/9 RPR STRW | WILLITS | ETL.6380.POLE.WOOD | 2024-06-26 | 2024-05-30 | 2025-03-17 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46340119 | T2 DI KONOCTI MDDLTWN 13/9 RPR STRW | ICW
LC | 129134481 | 000/005 | T2 DI PIT #3-PIT #1 000/005 RMV NEST | TABLEMTN | ETL.5400.TOWR | 2024-06-26 | 2024-05-30 | 2025-02-12 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46382961 | T2 DI PIT #3-PIT #1 000/005 RMV NEST | ICS
LC | 129134494 | 083/005 | T2 DI HUMBOLDT-TRINITY 83/05 RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-26 | 2024-05-30 | 2025-04-23 | On-Time |  | 2025-05-30 | 2025-05-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574495 | T2 DI HUMBOLDT-TRINITY 83/05 RPL STRW | 70Y
LC | 129134498 | 083/005 | T2 DI HUMBOLDT-TRINITY 83/05 RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-26 | 2024-05-30 | 2025-04-23 | On-Time |  | 2025-05-30 | 2025-05-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574495 | T2 DI HUMBOLDT-TRINITY 83/05 RPL STRW | 70Y
LC | 129134507 | 087/002A | T2 DI HUMBOLDT-TRIN 87/2A RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-26 | 2024-05-30 | 2025-04-22 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346011 | T2 DI HUMBOLDT-TRIN 87/2A RPR GYWW | ICW
LC | 129134517 | 002/035 | T2 DI PIT #1 MCARTHUR 2/35 RPL CRSW | TABLEMTN | ETL.7790.POLE.WOOD | 2024-06-26 | 2024-05-30 | 2025-02-13 | On-Time |  | 2025-05-30 | 2025-05-30 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35573301 | T2 DI PIT #1 MCARTHUR 2/35 RPL CRSW | 93E
LC | 129134579 | 029/207 | T2 DI CARIBOU-TBLE MTN 29/207 BNT STEEL | TABLEMTN | ETL.4440.TOWR | 2024-06-26 | 2024-05-30 | 2025-03-26 | On-Time |  | 2025-05-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354067 | T2 DI CARIBOU-TBLE MTN 29/207 BNT STEEL | ICQ
LC | 129134639 | 027/001 | T2 DI MENDOCINO-WFB 27/1 RPR GYWW | WILLITS | ETL.7550.POLE.NWOD | 2024-06-26 | 2024-05-30 | 2025-03-04 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310502 | T2 DI MENDOCINO-WFB 27/1 RPR GYWW | ICW
LC | 129134663 | 029/001 | T2 DI KONOCTI-MIDDLETOWN 29/1 TOUCH | WILLITS | ETL.6380.POLE.NWOD | 2024-06-26 | 2024-05-30 | 2025-06-04 | Past Due |  | 2024-11-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46507786 | T2 DI KONOCTI-MIDDLETOWN 29/1 TOUCH | ICW
LC | 129134775 | 050/004 | T2 DI HUMBOLDT-TRINITY 50/4 RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-06-26 | 2024-05-30 | 2025-04-08 | On-Time |  | 2024-08-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46273500 | T2 DI HUMBOLDT-TRINITY 50/4 RPR JUMW | ICW
LC | 129134890 | 065/003 | T2 DI HMBLT TRNITY 65/003R RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-26 | 2024-05-30 | 2025-04-19 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346010 | T2 DI HMBLT TRNITY 65/003R RPR GYWW | ICW
LC | 129137452 | 087/002B | T2 DI HUMBOLDT-TRIN 87/2B RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-27 | 2024-05-30 | 2025-04-22 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346012 | T2 DI HUMBOLDT-TRIN 87/2B RPR GYWW | ICW
LC | 129141083 | 036/017 | T2 DI FULTON-HOPLAND 36/17 RPR CRSW | LAKEVLLE | ETL.6890.POLE.NWOD | 2024-06-28 | 2024-05-30 | 2025-05-01 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46305954 | T2 DI FULTON-HOPLAND 36/17 RPR CRSW | ICW
LC | 129141154 | 027/232 | T2 DI BRDGVLL-CTTNWD 027/232 RPL INSW | TABLEMTN | ETL.1110.INSL.NCER | 2024-06-28 | 2024-05-30 | 2025-04-27 | On-Time |  | 2025-05-30 | 2025-05-30 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572064 | T2 DI BRDGVLL-CTTNWD 027/232 RPL INSW | 93I
LC | 129141245 | 099/002 | T2 DI HMBLT TRNITY 99/002L RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-28 | 2024-05-30 | 2025-04-18 | On-Time |  | 2025-05-30 | 2025-05-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574491 | T2 DI HMBLT TRNITY 99/002L RPL STRW | 70Y
LC | 129141247 | 099/002 | T2 DI HMBLT TRNITY 99/002R RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-28 | 2024-05-30 | 2025-04-18 | On-Time |  | 2025-05-30 | 2025-05-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574491 | T2 DI HMBLT TRNITY 99/002L RPL STRW | 70Y
LC | 129141316 | 013/084 | T2 DI JEFFERSON-MARTIN 013/084 RPR FOND | METCALF | ETL.5710.POLE.NWOD | 2024-06-28 | 2024-05-30 | 2025-01-29 | On-Time |  | 2025-05-30 | 2025-05-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46298841 | T2 DI JEFFERSON-MARTIN 013/084 RPR FOND | ICQ
LC | 129213502 | 025/221 | T2 DI BRDGVLL-CTTNWD 025/221R RPR STRW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-07-12 | 2024-05-30 | 2025-05-08 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311079 | T2 DI BRDGVLL-CTTNWD 025/221R RPR STRW | ICW
LC | 129213505 | 025/221 | T2 DI BRDGVLL-CTTNWD 025/221C RPR GYWW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-07-12 | 2024-05-30 | 2025-05-08 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311078 | T2 DI BRDGVLL-CTTNWD 025/221C RPR GYWW | ICW
LC | 129213741 | 039/312 | T2 DI BRDGVIL CTTNWD 39/312L RPR OPGW | TABLEMTN | ETL.1110.POLE.STPS | 2024-07-12 | 2024-05-30 | 2025-04-25 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Wood | Repair | 46311068 | T2 DI BRDGVIL CTTNWD 39/312L RPR OPGW | ICW
LC | 129213745 | 039/312 | T2 DI BRIDGVLLE-COTTONWD 39/312 RPR JUMW | TABLEMTN | ETL.1110.INSL.NCER | 2024-07-12 | 2024-05-30 | 2025-04-25 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311118 | T2 DI BRDGVIL CTTNWD 39/312 RPR JUMW | ICW
LC | 129213749 | 090/003 | T2 DI HMBLDT TRNTY 90/003 RPL HRDD | EUREKA | ETL.1820.POLE.WDPS | 2024-07-12 | 2024-05-30 | 2025-04-22 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46346013 | T2 DI HMBLDT TRNTY 90/003 RPL HRDD | ICW
LC | 129213897 | 069/349A | T2 DI MLN RND MTN#2 69/349A RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-07-12 | 2024-05-30 | 2025-01-31 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46338279 | T2 DI MLN RND MTN#2 69/349A RPR OPGW | ICS
LC | 129213898 | 069/349A | T2 DI MLN RND MTN#2 69/349A RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-07-12 | 2024-05-30 | 2025-01-30 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338300 | T2 DI MLN RND MTN#2 69/349A RPR SHLD | ICS
LC | 129213972 | 090/004 | T2 DI HMBLDT TRNTY 90/004R RPR STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-07-12 | 2024-05-30 | 2025-04-23 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46346015 | T2 DI HMBLDT TRNTY 90/004R RPR STRW | ICW
LC | 129214647 | 015/001 | T2 DI KONOCTI MIDDLETOWN 15/1 RMV VEG | WILLITS | ETL.6380.POLE.WOOD | 2024-07-12 | 2024-05-30 | 2025-04-10 | On-Time |  | 2025-05-30 | 2025-05-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129235866 | 039/313 | T2 DI BRDGVL-CTNWD 39/313 RMV VEG | TABLEMTN | ETL.1110.POLE.WDPS | 2024-07-17 | 2024-05-30 | 2024-12-19 | On-Time |  | 2025-05-30 | 2025-05-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129235867 | 039/313 | T2 DI BRDGVL-CTNWD 39/313L RPR ANCW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-07-17 | 2024-05-30 | 2025-04-06 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46311067 | T2 DI BRDGVL-CTNWD 39/313 RPR ANCW | ICW
LC | 129235868 | 039/313 | T2 DI BRDGVL-CTNWD 39/313L RPL HRDD | TABLEMTN | ETL.1110.POLE.WDPS | 2024-07-17 | 2024-05-30 | 2025-04-06 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46311066 | T2 DI BRDGVL-CTNWD 39/313L RPL HRDD | ICW
LC | 129292914 | B011/008 | T2 DI FLTN-CALISTOGA B011/008 RPR STRW | LAKEVLLE | ETL.6880.POLE.WOOD | 2024-07-26 | 2024-05-30 | 2025-05-19 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401433 | T2 DI FLTN-CALISTOGA B011/008 RPR STRW | ICW
LC | 129305001 | 078/003C | T2 DI HUMBOLDT TRINITY 78/3C RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-07-29 | 2024-05-30 | 2025-04-22 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46403064 | T2 DI HUMBOLDT TRINITY 78/3C RPR GYWW | ICW
LC | 129305134 | 015/107 | T2 DI IGNCIO-ALT-SALTO#1 15/107 RPR GYWW | LAKEVLLE | ETL.7160.POLE.WOOD | 2024-07-29 | 2024-05-30 | 2025-02-12 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46401520 | T2 DI IGNCIO-ALT-SALTO#1 15/107 RPR GYWW | ICW
LC | 129311497 | 098/004 | T2 HUMBOLDT-TRINITY 98/4 RPL INSS | EUREKA | ETL.1820.INSL.CERA | 2024-07-30 | 2024-05-30 | 2024-05-30 | Past Due |  | 2025-05-30 | 2025-05-30 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35586945 | T2 DI HUMBOLDT-TRINITY 98/4 RPL INSS | 93I
LC | 129311776 | 000/009 | T2 DI PIT #1-COTTONWOOD 0/9 RPR CNDS | TABLEMTN | ETL.5390.INSL.NCER | 2024-07-30 | 2024-05-30 | 2024-11-05 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Steel | Repair | 46382474 | T2 DI PIT #1-COTTONWOOD 0/9 RPR CNDS | ICS
LC | 129316770 | 111/001C | T2 DI HMBLDT-TRINITY 111/001C RMV VEG | EUREKA | ETL.1820.POLE.NWOD | 2024-07-31 | 2024-05-30 | 2024-11-13 | On-Time |  | 2024-11-30 | 2025-05-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 129316772 | 111/001B | T2 DI HMBLDT-TRINITY 111/001B RMV VEG | EUREKA | ETL.1820.POLE.NWOD | 2024-07-31 | 2024-05-30 | 2024-11-13 | On-Time |  | 2024-11-30 | 2025-05-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 129316874 | 014/100A | T2 DI IGNCO-ATO SLTO #1 14/100A RPR GYWW | LAKEVLLE | ETL.7160.POLE.WOOD | 2024-07-31 | 2024-05-30 | 2025-02-12 | On-Time |  | 2025-05-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46401439 | T2 DI IGNCO-ATO SLTO #1 14/100A RPR GYWW | ICW
LC | 129334059 | 89 | T2 FULTON HOPLAND 12/4 RPR SWTC | LAKEVLLE | ETL.6890.SWIT | 2024-08-05 | 2024-05-30 | 2024-05-30 | Past Due |  | 2024-11-30 | 2025-05-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCM OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Switch-Wood | Repair | 46329208 | DI FULTON HOPLAND 12/4 RPR SWTC | ICW
LC | 129334574 | 069/348A | T2 DI MALIN-RND MTN #2 69/348A RPR SHLS | TABLEMTN | ETL.6020.TOWR | 2024-08-05 | 2024-05-30 | 2025-01-30 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338304 | T2 DI MALIN-RND MTN #2 69/348A RPR SHLS | ICS
LC | 129334575 | 069/348A | T2 DI MALIN-RND MTN #2 69/348A RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-08-05 | 2024-05-30 | 2025-04-03 | On-Time |  | 2025-05-30 | 2025-05-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46338305 | T2 DI MALIN-RND MTN #2 69/348A RPR OPGW | ICS
LC | 129339433 | 014/099 | T2 IGCO ALTO SUSLTO#1 14/099 RMV VEG | LAKEVLLE | ETL.7160.POLE.WOOD | 2024-08-06 | 2024-05-30 | 2024-05-30 | Past Due |  | 2025-05-30 | 2025-05-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 123721584 | T-157 | T2NT EI MIDWAY-SANTA MARIA T-157 RMV VEG | MIDWAY | ETL.9240.TOWR | 2022-05-31 | 2022-05-31 | 2023-12-22 | On-Time |  | 2025-05-31 | 2025-05-31 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO FRAA | Overgrown | Vegetation-Tower | Cage Clearing
LC | 123745861 | 055/236 | T2NT DI RND MN-TBL MN #1 55/236 BENT STL | TABLEMTN | ETL.6060.TOWR | 2022-06-02 | 2022-05-31 | 2023-06-28 | On-Time |  | 2025-05-31 | 2025-05-31 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644491 | T2 DI RND MTN-TBL MTN #1 55/236 BENT STL | ICQ
LC | 123752075 | 056/240 | T2NT DI RND MTN-TB MT #2 56/240 RPR GYWS | TABLEMTN | ETL.6070.TOWR | 2022-06-03 | 2022-05-31 | 2023-09-12 | On-Time |  | 2025-05-31 | 2025-05-31 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45703133 | T2 DI RND MTN-TBL MTN #2 56/240 RPR GYWS | ICS
LC | 123855689 | Z005/004 | T3NT DI FULTON-CALISTG Z5/4 BNT STEEL | LAKEVLLE | ETL.6880.POLE.NWOD | 2022-06-16 | 2022-05-31 | 2023-07-17 | On-Time |  | 2025-05-31 | 2025-05-31 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644894 | T3 DI FULTON-CALISTG Z5/4 BNT STEEL | ICQ
LC | 123925647 | 001/019 | T3NT DI DRUM-SUMMIT #1 1/019 MASTIC | SACTO | ETL.1440.POLE.STPS | 2022-06-25 | 2022-05-31 | 2023-06-17 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 45732867 | T3 DI DRUM-SUMMIT #1 001/019 MASTIC | ICW
LC | 123933185 | 008/056 | T2NT DI MORGA-SN LNDR0 #1 8/56 RPL HRDT | CONCORD | ETL.2770.TOWR | 2022-06-27 | 2022-05-31 | 2023-06-08 | On-Time |  | 2025-05-31 | 2025-05-31 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 45697940 | T2 DI MORGA-SN LNDR0 #1 008/056 RPL HRDT | ICQ
LC | 128938097 | 018/099 | T2 HAAS-MCCALL 18/099 RMV ENCR | FRESNO | ETL.4850.TOWR | 2024-05-31 | 2024-05-31 | 2024-09-04 | On-Time |  | 2024-12-01 | 2025-05-31 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | Encroachment | Right of Way | Remove | 46262613 | T2 HAAS-MCCALL 18/099 RMV ENCR | CHR
LC | 128944154 | 005/064 | T2 BURNS-LONE STAR #1 05/64 RPL ANCW | MOSSLNDG | ETL.6230.POLE.NWOD | 2024-05-31 | 2024-05-31 | 2025-03-25 | On-Time |  | 2025-05-31 | 2025-05-31 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR REMT COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35572854 | T2 BURNS-LONE STAR #1 05/64 RPL ANCW | 93E
LC | 128946345 | 004/005C | T2 CLEAR LAKE-HOPLAND 04/05C COTTER | WILLITS | ETL.6390.INSL.NCER | 2024-05-31 | 2024-05-31 | 2025-05-14 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46255397 | T2 CLEAR LAKE-HOPLAND 04/05C COTTER | ICW
LC | 128953535 | 003/070 | T2 EI CARIBOU-PLUMAS JCT 003/70 RPR GYWW | TABLEMTN | ETL.6290.POLE.NWOD | 2024-05-31 | 2024-05-31 | 2025-04-29 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46397982 | T2 EI CARIBOU-PLUMAS JCT 003/70 RPR GYWW | ICW
LC | 128953536 | 053/001 | T2 WV ELK-GUALALA 053/001 INS DMPW | WILLITS | ETL.8410.INSL.NCER | 2024-05-31 | 2024-05-31 | 2025-03-03 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46310513 | T2 WV ELK-GUALALA 053/001 INS DMPW | ICW
LC | 128955389 | 014/074 | T2 EI RND MTN-TBLE MTN #2 14/74 RM VEG | TABLEMTN | ETL.6070.TOWR | 2024-05-31 | 2024-05-31 | 2024-05-31 | On-Time |  | 2025-05-31 | 2025-05-31 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128956481 | 014/074 | T2 EI RND MTN-TBLE MTN #2 14/74 COTTER | TABLEMTN | ETL.6070.INSL | 2024-05-31 | 2024-05-31 | 2025-02-20 | On-Time |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46306307 | T2 EI RND MTN-TBLE MTN #2 14/74 COTTER | ICS
LC | 128958102 | 003/071 | T2 EI CARIBOU #2 003/071 RPR INSW | TABLEMTN | ETL.6280.INSL.NCER | 2024-05-31 | 2024-05-31 | 2025-05-06 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46337209 | T2 EI CARIBOU #2 003/071 RPR INSW | ICW
LC | 128960752 | 026/315C | T2 EI DRUM-SUMMIT #1 26/315C RPR STRW | SACTO | ETL.1440.POLE.NWOD | 2024-05-31 | 2024-05-31 | 2024-06-18 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46267994 | T2 EI DRUM-SUMMIT #1 26/315C RPR STRW | ICW
LC | 128961189 | 024/103 | T2 EI MOSS LANDING-METCLF 24/103 RMV VEG | MOSSLNDG | ETL.6050.TOWR | 2024-05-31 | 2024-05-31 | 2025-05-22 | On-Time |  | 2025-05-31 | 2025-05-31 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128961334 | 026/317 | T2 EI DRUM-SUMMIT #1 26/317 RPR POLE | SACTO | ETL.1440.POLE.WDPS | 2024-05-31 | 2024-05-31 | 2024-07-20 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46283615 | T2 EI DRUM-SUMMIT #1 26/317 RPR POLE | ICW
LC | 128962001 | 014/103 | T2 DI IGNC ALT SSLITO #1 14/103 RPR GYWW | LAKEVLLE | ETL.7160.POLE.WOOD | 2024-05-31 | 2024-05-31 | 2024-06-27 | On-Time |  | 2024-11-30 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46264371 | T2 DI IGNC ALT SSLITO #1 14/103 RPR GYWW | ICW
LC | 128962007 | 014/103 | T2 DI IGNC ALT SSLITO #1 14/103 RPR ANCW | LAKEVLLE | ETL.7160.POLE.WOOD | 2024-05-31 | 2024-05-31 | 2024-06-27 | On-Time |  | 2024-11-30 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46268430 | T2 DI IGNC ALT SSLITO #1 14/103 RPR ANCW | ICW
LC | 128962041 | 006/035 | T2 EI MTCLF-MNTA VSTA #3 06/035 COTTER | MOSSLNDG | ETL.5091.INSL.NCER | 2024-05-31 | 2024-05-31 | 2025-05-05 | On-Time |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46391297 | T2 EI MTCLF-MNTA VSTA #3 06/035 COTTER | ICS
LC | 128962042 | 006/038 | T2 EI MONTA VISTA-CYTE SS 06/38 RMV VEG | MOSSLNDG | ETL.5090.TOWR | 2024-05-31 | 2024-05-31 | 2025-04-23 | On-Time |  | 2025-05-31 | 2025-05-31 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128962102 | 111/000 | T2 DI HUMBOLDT-BRIDGEVLLE 111/0 RPL STRW | EUREKA | ETL.1810.POLE.WDPS | 2024-05-31 | 2024-05-31 | 2024-05-31 | Past Due |  | 2024-11-30 | 2025-05-31 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35574607 | T2 DI HUMBOLDT-BRIDGEVLLE 111/0 RPL STRW | 70Y
LC | 128962107 | 111/000 | T2 DI HUMBOLDT-BRIDGEVLLE 111/0 RPL STRW | EUREKA | ETL.1810.POLE.WDPS | 2024-05-31 | 2024-05-31 | 2024-05-31 | Past Due |  | 2024-11-30 | 2025-05-31 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35574607 | T2 DI HUMBOLDT-BRIDGEVLLE 111/0 RPL STRW | 70Y
LC | 128962429 | 028/236 | T2 DI BRDGVLL-CTTNWD 028/236 RPR STRW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-05-31 | 2024-05-31 | 2025-04-28 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311065 | T2 DI BRDGVLL-CTTNWD 028/236 RPR STRW | ICW
LC | 128962475 | 028/236 | T2 DI BRDGVLL-CTTNWD 28/236 RPR JUMW | TABLEMTN | ETL.1110.INSL.NCER | 2024-05-31 | 2024-05-31 | 2025-04-28 | On-Time |  | 2024-08-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262827 | T2 DI BRDGVLL-CTTNWD 028/236 RPR JUMW | ICW
LC | 128962717 | 025/122 | T2 MNTA VST-CYT SW STA 25/122 RPR CNDS | MOSSLNDG | ETL.5090.INSL | 2024-05-31 | 2024-05-31 | 2024-05-31 | Past Due |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP REMT NOAC SPCR ACCH OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Conductor-Steel | Repair | 46391298 | T2 EI MTCLF-MNTA VSTA #3 25/122 RPR CNDS | ICS
LC | 128962742 | 010/053 | T2 EI RND MTN-TBLE MTN#2 10/53 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2024-05-31 | 2024-05-31 | 2024-05-31 | On-Time |  | 2025-05-31 | 2025-05-31 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128962855 | 003/071 | T2 EI CARIBOU-WESTWOOD 3/071R RPL HRDD | TABLEMTN | ETL.6300.POLE.WDPS | 2024-05-31 | 2024-05-31 | 2025-03-08 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46337448 | T2 EI CARIBOU-WESTWOOD 3/071R RPL HRDD | ICW
LC | 128962872 | 003/071 | T2 EI CARIBOU-WESTWOOD 003/071 RPR GYWW | TABLEMTN | ETL.6300.POLE.WDPS | 2024-05-31 | 2024-05-31 | 2024-07-09 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46278106 | T2 EI CARIBOU-WESTWOOD 003/071 RPR GYWW | ICW
LC | 128962873 | 003/072 | T2 EI CARIBOU-WESTWOOD 003/072 RPL INSW | TABLEMTN | ETL.6300.INSL.CERA | 2024-05-31 | 2024-05-31 | 2025-03-08 | On-Time |  | 2025-05-31 | 2025-05-31 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35576900 | T2 EI CARIBOU-WESTWOOD 003/072 RPL INSW | 93I
LC | 128962982 | 009/109 | T2 EI DRUM-SUMMIT #2 9/109 RPR INSW | SACTO | ETL.1450.INSL.CERA | 2024-05-31 | 2024-05-31 | 2025-04-23 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46458326 | T2 EI DRUM-SUMMIT #2 9/109 RPR INSW | ICW
LC | 128963013 | 021/254A | T2 EI DRUM-SUMMIT #2 021/254A RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-05-31 | 2024-05-31 | 2024-06-16 | On-Time |  | 2024-11-30 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46265944 | T2 EI DRUM-SUMMIT #2 021/254A RPR GYWW | ICW
LC | 128963022 | 021/254B | T2 EI DRUM-SUMMIT #2 021/254B RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-05-31 | 2024-05-31 | 2024-06-16 | On-Time |  | 2024-08-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46265943 | T2 EI DRUM-SUMMIT #2 021/254B RPR GYWW | ICW
LC | 128963031 | 021/254C | T2 EI DRUM-SUMMIT #2 021/254C RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-05-31 | 2024-05-31 | 2024-06-16 | On-Time |  | 2024-11-30 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46265942 | T2 EI DRUM-SUMMIT #2 021/254C RPR GYWW | ICW
LC | 128963135 | 042/825 | T2 HAT CREEK #1-WESTWOOD 42/825 GO95 RPL | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-31 | 2024-05-31 | 2025-05-28 | On-Time |  | 2025-05-31 | 2025-05-31 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35574517 | T2 EI HAT CRK #1-WSTWD 42/825 GO95 | 93G
LC | 128963178 | 025/106 | T2 EI MOSS LNDING-METCALF 25/106 RMV VEG | MOSSLNDG | ETL.6050.TOWR | 2024-05-31 | 2024-05-31 | 2025-05-09 | On-Time |  | 2025-05-31 | 2025-05-31 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128963383 | 006/039 | T2 EI MNTA VSTA-CYOTE SS 06/39 RMV VEG | MOSSLNDG | ETL.5090.TOWR | 2024-05-31 | 2024-05-31 | 2025-04-24 | On-Time |  | 2025-05-31 | 2025-05-31 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128964107 | 024/173 | T2 DI CARIBU-TBL MTN 24/173 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2024-06-01 | 2024-05-31 | 2025-05-01 | On-Time |  | 2025-05-31 | 2025-05-31 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354061 | T2 DI CARIBU-TBL MTN 24/173 RPR STRT | ICQ
LC | 128964122 | 015/080 | T2 DI BALCH-SNGR 15/80 COTTER | FRESNO | ETL.1050.INSL.CERA | 2024-06-01 | 2024-05-31 | 2024-11-18 | On-Time |  | 2024-08-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46256481 | T2 DI BALCH-SNGR 15/80 COTTER | ICS
LC | 128964131 | 024/173 | T2 DI CARIBOU-TBL MTN 24/173 RPR JUMS | TABLEMTN | ETL.4440.INSL.CERA | 2024-06-01 | 2024-05-31 | 2025-04-06 | On-Time |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46337590 | T2 DI CARIBOU-TBL MTN 24/173 RPR JUMS | ICS
LC | 128964160 | 031/217 | T2 DI TRINITY CTNWOOD 31/217C RPR GYWW | TABLEMTN | ETL.4040.POLE.STPS | 2024-06-01 | 2024-05-31 | 2025-02-25 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46471151 | T2 DI TRINITY CTNWOOD 31/217C RPR GYWW | ICW
LC | 128964194 | 017/345 | T2 HT CRK #1-WESTWD 17/345 RPR POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-01 | 2024-05-31 | 2025-05-03 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46328728 | T2 EI HT CRK #1-WESTWD 17/345 RPR POLE | ICW
LC | 128964202 | 078/558 | T2 COTTONWD-HUMBOLDT 78/558 RPR GRWW | EUREKA | ETL.1110.POLE.WDPS | 2024-06-01 | 2024-05-31 | 2024-05-31 | Past Due |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46346018 | T2 EI COTTONWD-HUMBOLDT 78/558 RPR GRWW | ICW
LC | 128964231 | 008/063A | T2 DI HELMS-GREGG #1 08/63A RPR JUMS | FRESNO | ETL.4870.INSL.CERA | 2024-06-01 | 2024-05-31 | 2024-10-14 | On-Time |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46297929 | T2 DI HELMS-GREGG #1 08/63A RPR JUMS | ICS
LC | 128964394 | 028/008 | T2 DI MNDCN WLTS FRT BRG 28/8 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-06-01 | 2024-05-31 | 2025-04-03 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310512 | T2 DI MNDCN WLTS FRT BRG 28/8 RPR GYWW | ICW
LC | 128964515 | 038/167 | T2 DI FULTON-LAKEVILLE 38/167 RPR INSS | LAKEVLLE | ETL.4950.INSL | 2024-06-01 | 2024-05-31 | 2025-01-30 | On-Time |  | 2024-08-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46255775 | T2 DI FULTON-LAKEVILLE 38/167 RPR INSS | ICS
LC | 128964526 | 044/293B | T2 DI TRINITY CTNWOOD 44/293B RPR GYWW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-06-01 | 2024-05-31 | 2024-07-22 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46284297 | T2 DI TRINITY CTNWOOD 44/293B RPR GYWW | ICW
LC | 128964539 | 080/001 | T2 DI HUMBOLDT-TRIN 80/1L RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-01 | 2024-05-31 | 2025-04-22 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346019 | T2 DI HUMBOLDT-TRIN 80/1L RPR GYWW | ICW
LC | 128964595 | 080/001 | T2 DI HUMBOLDT-TRIN 80/1C RMV VEG | EUREKA | ETL.1820.POLE.WDPS | 2024-06-01 | 2024-05-31 | 2025-05-16 | On-Time |  | 2025-05-31 | 2025-05-31 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR | Overgrown | Vegetation | Remove
LC | 128964599 | 010/123 | T2 DI DRUM-SMMT#1 10/123 RPL INSW | SACTO | ETL.1440.INSL.CERA | 2024-06-01 | 2024-05-31 | 2024-07-14 | On-Time |  | 2025-05-31 | 2025-05-31 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35557797 | T2 DI DRUM-SMMT#1 10/123 RPL INSW | 93I
LC | 128967087 | 089/010 | T2 DI HUMBLT TRINITY 9/10 RPR JMPW | EUREKA | ETL.1820.INSL.NCER | 2024-06-03 | 2024-05-31 | 2025-04-21 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46346021 | T2 DI HUMBLT TRINITY 9/10 RPR JMPW | ICW
LC | 128980535 | 080/001 | T2 HUMBOLDT-TRIN 80/1R INSP STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-03 | 2024-05-31 | 2024-07-10 | On-Time |  | 2024-11-30 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46262166 | T2 HUMBOLDT-TRIN 80/1R INSP STRW | ICW
LC | 129015162 | 036/318 | T2 DI RND MTN-CTTNWD #3 36/318 RMV VEG | TABLEMTN | ETL.5650.TOWR | 2024-06-03 | 2024-05-31 | 2024-06-26 | On-Time |  | 2025-05-31 | 2025-05-31 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 129015598 | 082/006A | T2 DI HUMBLDT-TRINITY 82/006A RPR IBWW | EUREKA | ETL.1820.INSL.NCER | 2024-06-03 | 2024-05-31 | 2025-04-22 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46346020 | T2 DI HUMBLDT-TRINITY 82/006A RPR IBWW | ICW
LC | 129015790 | 070/355 | T2 DI MALIN-RM#2 70/355 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-06-03 | 2024-05-31 | 2025-02-22 | On-Time |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46338271 | T2 DI MALIN-RM#2 70/355 RPR OPGW | ICS
LC | 129015884 | 000/009 | T2 DI JEFFERSON-STANFORD 0/9 COMPLETE | METCALF | ETL.7220.POLE.WOOD | 2024-06-03 | 2024-05-31 | 2025-03-30 | On-Time |  | 2025-05-31 | 2025-05-31 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573646 | T2 DI JEFFERSON-STANFORD 0/9 RPL POLE | 70Y
LC | 129015981 | 111/007 | T2 DI HUMBLDT-TRINITY 111/007 RPR GYWT | EUREKA | ETL.1820.TOWR | 2024-06-03 | 2024-05-31 | 2025-03-04 | On-Time |  | 2025-05-31 | 2025-05-31 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46289237 | T2 DI HUMBLDT-TRINITY 111/007 RPR GYWT | ICQ
LC | 129026297 | 090/010C | T2 DI HUMBLT-TRNTY 90/10C RPR INSW | EUREKA | ETL.1820.INSL.CERA | 2024-06-05 | 2024-05-31 | 2025-04-21 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46346024 | T2 DI HUMBLT-TRNTY 90/10C RPR INSW | ICW
LC | 129026740 | 033/272 | T2 DI BRDGVL-CTNWD 33/272 RPR ANCW | TABLEMTN | ETL.1110.POLE.STPS | 2024-06-05 | 2024-05-31 | 2025-05-09 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46311063 | T2 DI BRDGVL-CTNWD 33/272 RPR ANCW | ICW
LC | 129031687 | 109/001 | T2 DI HMBLDT-TRNTY 109/1R RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-06 | 2024-05-31 | 2025-04-09 | On-Time |  | 2025-05-31 | 2025-05-31 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574485 | T2 DI HMBLDT-TRNTY 109/1L RPL STRW | 70Y
LC | 129057902 | 109/001 | T2 DI HMBLDT-TRNTY 109/1L RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-11 | 2024-05-31 | 2025-04-09 | On-Time |  | 2025-05-31 | 2025-05-31 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574485 | T2 DI HMBLDT-TRNTY 109/1L RPL STRW | 70Y
LC | 129057908 | 109/001 | T2 DI HMBLDT-TRNTY 109/1C RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-11 | 2024-05-31 | 2025-04-09 | On-Time |  | 2025-05-31 | 2025-05-31 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574485 | T2 DI HMBLDT-TRNTY 109/1L RPL STRW | 70Y
LC | 129134630 | ;001/011 | T2 DI SNEATH LANE-HMB ;1/11 RPR GYWW | METCALF | ETL.7212.POLE.WOOD | 2024-06-26 | 2024-05-31 | 2025-03-30 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCH COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286773 | T2 DI SNEATH LANE-HMB ;1/11 RPR GYWW | ICW
LC | 129137286 | 046/397 | T2 DI PIT#1-COTT 46/397 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2024-06-27 | 2024-05-31 | 2025-04-15 | On-Time |  | 2025-05-31 | 2025-05-31 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381942 | T2 DI PIT#1-COTT 46/397 BNT STEEL | ICQ
LC | 129141026 | 017/004 | T2 DI MNDCNO WLTS FRT BRG 17/4 RPR GYWW | WILLITS | ETL.7550.POLE.NWOD | 2024-06-28 | 2024-05-31 | 2025-02-12 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310507 | T2 DI MNDCNO WLTS FRT BRG 17/4 RPR GYWW | ICW
LC | 129141048 | 031/007 | T2 MNDCNO-WLTS-FRT BRG 31/7 RPL STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-06-28 | 2024-05-31 | 2024-05-31 | Past Due |  | 2025-05-31 | 2025-05-31 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574306 | T2 DI MNDCNO-WLTS-FRT BRG 31/7 RPL STRW | 70Y
LC | 129141163 | 090/000 | T2 DI HMBLT TRNITY 90/000 RPR CRSW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-28 | 2024-05-31 | 2025-04-21 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46346022 | T2 DI HMBLT TRNITY 90/000 RPR CRSW | ICW
LC | 129141241 | 014/100 | T2 DI IGNCO ALT SUSLTO#1 14/100 RPR STRW | LAKEVLLE | ETL.7170.POLE.WOOD | 2024-06-28 | 2024-05-31 | 2025-05-01 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46403759 | T2 DI IGNCO ALT SUSLTO#1 14/100 RPR STRW | ICW
LC | 129141630 | 028/200 | T2 DI CARIBOU-TBL MNTN 28/200 RPR JUMS | TABLEMTN | ETL.4440.INSL.NCER | 2024-06-28 | 2024-05-31 | 2025-04-06 | On-Time |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46337595 | T2 DI CARIBOU-TBL MNTN 28/200 RPR JUMS | ICS
LC | 129141685 | :013/068 | T2 DI CZYHRS CNY SLNS #1 :13/68 RPL INSS | MOSSLNDG | ETL.2900.INSL.CERA | 2024-06-28 | 2024-05-31 | 2024-11-04 | On-Time |  | 2024-11-30 | 2025-05-31 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35587172 | T2 DI CZYHRS CNY SLNS #1 RPL INSS :13/68 | 93K
LC | 129141762 | 011/224 | T2 DI COLGATE-PALERMO 11/224 RPL STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-06-28 | 2024-05-31 | 2025-05-01 | On-Time |  | 2025-05-31 | 2025-05-31 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572925 | T2 DI COLGATE-PALERMO 11/224 RPL STRW | 70Y
LC | 129142169 | 009/070A | T2 DI HELM GREGG#1 09/070A RPR SHLD | FRESNO | ETL.4870.TOWR | 2024-06-28 | 2024-05-31 | 2025-06-02 | Past Due |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46297938 | T2 DI HELM GREGG#1 09/070A RPR SHLD | ICS
LC | 129142212 | 009/070A | T2 HELM GREGG #1 09/070A RMV VEG | FRESNO | ETL.4870.TOWR | 2024-06-28 | 2024-05-31 | 2024-05-31 | Past Due |  | 2025-05-31 | 2025-05-31 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE ACCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129142831 | 090/007 | T2 DI HUMBOLDT TRINITY 90/7L RPR CRSW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-28 | 2024-05-31 | 2025-04-23 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46346023 | T2 DI HUMBOLDT TRINITY 90/7L RPR CRSW | ICW
LC | 129155190 | :013/068 | T2 DI CHC-SLNS-SOLDAD #1 :13/68 RPL HNGR | MOSSLNDG | ETL.2900.INSL.CERA | 2024-07-02 | 2024-05-31 | 2024-11-04 | On-Time |  | 2024-11-30 | 2025-05-31 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46273849 | T2 CZYHRS CNY SLNS #1 :13/68 RPL HNGR | ICQ
LC | 129193012 | 008/065A | T2 DI HELMS-GREGG #1 8/65A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-07-09 | 2024-05-31 | 2025-06-02 | Past Due |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46297963 | T2 DI HELMS-GREGG #1 8/65A RPR SHLS | ICS
LC | 129193239 | 129 | T2 DI HUMBOLDT-TRINITY 70/1X RPR SWTCH | EUREKA | ETL.1820.SWIT | 2024-07-09 | 2024-05-31 | 2025-04-14 | On-Time |  | 2025-05-31 | 2025-05-31 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR NTDE | Out of Adjustment | Switch | Repair | 46346028 | T2 DI HUMBOLDT-TRINITY 70/1X RPR SWTCH | ICE
LC | 129193681 | 020/293 | T2 DI KESWICK-TRINITY 20/293 RPL SPLW | TABLEMTN | ETL.7270.INSL.CERA | 2024-07-09 | 2024-05-31 | 2025-04-11 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Splice-Wood | Replace | 46311160 | T2 DI KESWICK-TRINITY 20/293 RPL SPLW | ICW
LC | 129213537 | 025/184 | T2 DI CARIBOU-TBL MTN 25/184 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2024-07-12 | 2024-05-31 | 2025-04-06 | On-Time |  | 2025-05-31 | 2025-05-31 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46311045 | T2 DI CARIBOU-TB MT 025/184 RPR STRT | ICQ
LC | 129213563 | 025/184 | T2 DI CARIBOU-TBL MTN 25/184 RPR JMPS | TABLEMTN | ETL.4440.INSL.NCER | 2024-07-12 | 2024-05-31 | 2025-04-06 | On-Time |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46337596 | T2 DI CARIBOU-TBL MTN 25/184 RPR JMPS | ICS
LC | 129213601 | 113/001 | T2 DI HMBLDT-BRDGVLL 113/001 RPR GYWW | EUREKA | ETL.1810.POLE.WDPS | 2024-07-12 | 2024-05-31 | 2025-05-07 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346025 | T2 DI HMBLDT-BRDGVLL 113/001 RPR GYWW | ICW
LC | 129213700 | 010/117 | T2 DI DRUM-SUMMIT #1 10/117R TOUCH | SACTO | ETL.1440.POLE.STPS | 2024-07-12 | 2024-05-31 | 2025-04-24 | On-Time |  | 2024-11-30 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46398073 | T2 DI DRUM-SUMMIT #1 10/117R RMV DBRW | ICW
LC | 129214208 | 012/143A | T2 DI DRUM-SUMMIT #1 12/143A RPR ANCW | SACTO | ETL.1440.POLE.NWOD | 2024-07-12 | 2024-05-31 | 2025-04-24 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46398074 | T2 DI DRUM-SUMMIT #1 12/143A RPR ANCW | ICW
LC | 129214234 | 012/143B | T2 DI DRUM-SUMMIT #1 12/143B RPR ANCW | SACTO | ETL.1440.POLE.NWOD | 2024-07-12 | 2024-05-31 | 2025-04-24 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46398075 | T2 DI DRUM-SUMMIT #1 12/143B RPR ANCW | ICW
LC | 129214335 | 19 | T2 DI KESWICK-TRINITY 11/151 RMV NEST | TABLEMTN | ETL.7270.SWIT | 2024-07-12 | 2024-05-31 | 2025-04-24 | On-Time |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | Debris/Nest/etc. | Structure-Steel | Remove | 46311300 | T2 DI KESWICK-TRINITY 11/151 RMV NEST | ICS
LC | 129214506 | 007/059A | T2 DI HELMS-GREGG #1 7/59A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-07-12 | 2024-05-31 | 2024-10-08 | On-Time |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46297991 | T2 DI HELMS-GREGG #1 7/59A RPR SHLS | ICS
LC | 129214561 | 025/186 | T2 DI CRBOU-TBL MT 25/186 TOUCH POTENTL | TABLEMTN | ETL.4440.TOWR | 2024-07-12 | 2024-05-31 | 2025-05-01 | On-Time |  | 2025-05-31 | 2025-05-31 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Structure-Tower | Repair | 46354070 | T2 DI CRBOU-TBL MT 25/186 TOUCH POTENTL | ICQ
LC | 129214666 | 19 | T2 DI KESWICK-TRINITY 11/151 RPR SWTC | TABLEMTN | ETL.7270.SWIT | 2024-07-12 | 2024-05-31 | 2025-04-24 | On-Time |  | 2025-05-31 | 2025-05-31 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | Out of Adjustment | Switch | Repair | 46311142 | T2 DI KESWICK-TRINITY 11/151 RPR SWTC | ICE
LC | 129214970 | 026/227 | T2 DI BRDGVLL-CTTNWD 026/227L RPL GYWW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-07-12 | 2024-05-31 | 2024-11-14 | On-Time |  | 2024-11-30 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Replace | 46282242 | T2 DI BRDGVLL-CTTNWD 026/227L RPL GYWW | ICW
LC | 129215179 | 023/169 | T2 DI CARIBOU-TABLE MTN 23/169 RPR FOND | TABLEMTN | ETL.4440.TOWR | 2024-07-12 | 2024-05-31 | 2025-05-01 | On-Time |  | 2025-05-31 | 2025-05-31 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46354071 | T2 DI CARIBOU-TABLE MTN 23/169 RPR FOND | ICQ
LC | 129215430 | 070/353 | T2 DI MALIN-ROUND MNT #2 70/353 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-07-12 | 2024-05-31 | 2025-02-22 | On-Time |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46338301 | T2 DI MALIN-ROUND MNT #2 70/353 RPR OPGW | ICS
LC | 129215431 | 070/353 | T2 DI MALIN-ROUND MNT #2 70/353 RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-07-12 | 2024-05-31 | 2025-02-22 | On-Time |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338302 | T2 DI MALIN-ROUND MNT #2 70/353 RPR SHLD | ICS
LC | 129215512 | 008/066A | T2 DI HELMS GREGG #1 08/066A RPR SHLS | FRESNO | ETL.4870.TOWR | 2024-07-12 | 2024-05-31 | 2025-06-02 | Past Due |  | 2025-05-31 | 2025-05-31 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46297964 | T2 DI HELMS GREGG #1 08/066A RPR SHLS | ICS
LC | 129215777 | 004/025 | T2 DI ULUCAY-VACA-VACA 4/25 RPL INSS | SACTO | ETL.5800.INSL | 2024-07-12 | 2024-05-31 | 2025-05-01 | On-Time |  | 2025-05-31 | 2025-05-31 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574251 | T2 DI ULUCAY-VACA-VACA 4/25 RPL INSS | 93K
LC | 129235937 | 027/235 | T2 DI BRDGVLL-CTTNWD 27/235R RPL STRW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-07-17 | 2024-05-31 | 2025-04-28 | On-Time |  | 2025-05-31 | 2025-05-31 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572063 | T2 DI BRDGVL-CTNWD 27/229L RPL POLE | 70Y
LC | 129235938 | 027/235 | T2 DI BRDGVLL-CTTNWD 27/235L RPL STRW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-07-17 | 2024-05-31 | 2025-04-28 | On-Time |  | 2025-05-31 | 2025-05-31 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572063 | T2 DI BRDGVL-CTNWD 27/229L RPL POLE | 70Y
LC | 129236026 | 029/245 | T2 DI BRDGVLL-CTTNWD 29/245 RPR ADSS | TABLEMTN | ETL.1110.POLE.STPS | 2024-07-17 | 2024-05-31 | 2024-11-14 | On-Time |  | 2024-08-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46311117 | T2 DI BRDGVLL-CTTNWD 29/245 RPR ADSS | ICW
LC | 129236121 | 027/229 | T2 DI BRDGVL-CTNWD 27/229L RPL POLE | TABLEMTN | ETL.1110.POLE.WDPS | 2024-07-17 | 2024-05-31 | 2025-04-26 | On-Time |  | 2025-05-31 | 2025-05-31 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572063 | T2 DI BRDGVL-CTNWD 27/229L RPL POLE | 70Y
LC | 129264199 | 027/229 | T2 DI BRDGVL-CTNWD 27/229R RPL POLE | TABLEMTN | ETL.1110.POLE.WDPS | 2024-07-22 | 2024-05-31 | 2025-04-27 | On-Time |  | 2025-05-31 | 2025-05-31 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572063 | T2 DI BRDGVL-CTNWD 27/229L RPL POLE | 70Y
LC | 129316991 | 015/108 | T2 DI IGCO ALTO SUSLTO#2 15/108 RPR ANCW | LAKEVLLE | ETL.7170.POLE.NWOD | 2024-07-31 | 2024-05-31 | 2025-05-01 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46345552 | T2 DI IGCO ALTO SUSLTO#2 15/108 RPR ANCW | ICW
LC | 129324409 | 001/024 | T2 DI JEFFERSON-STNFRD 1/024 RPR ADSS | METCALF | ETL.7220.POLE.WOOD | 2024-08-02 | 2024-05-31 | 2024-08-23 | On-Time |  | 2024-08-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46298750 | T2 DI JEFFERSON-STNFRD 1/024 RPR ADSS | ICW
LC | 129324481 | 001/024 | T2 JEFFERSON-STNFRD 1/24 RMV VEG | METCALF | ETL.7220.POLE.WOOD | 2024-08-02 | 2024-05-31 | 2025-05-05 | On-Time |  | 2025-05-31 | 2025-05-31 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129324524 | 014/099 | T2 DI IGNCO-ALTO SLTO#2 14/99 RPR ANCW | LAKEVLLE | ETL.7170.POLE.WOOD | 2024-08-02 | 2024-05-31 | 2025-05-01 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46401521 | T2 DI IGNCO-ALTO SLTO#2 14/99 RPR ANCW | ICW
LC | 129324909 | 038/332 | T2 DI RND MTN-CTTNWD #3 38/332 RPR STRT | TABLEMTN | ETL.5650.TOWR | 2024-08-02 | 2024-05-31 | 2025-05-05 | On-Time |  | 2025-05-31 | 2025-05-31 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46404701 | T2 DI RND MTN-CTTNWD #3 38/332 RPR STRT | ICQ
LC | 129333898 | 004/052 | T2 DI SNEATH LANE PACIFICA 4/52 RPR ANCW | METCALF | ETL.7575.POLE.WOOD | 2024-08-05 | 2024-05-31 | 2025-01-31 | On-Time |  | 2025-05-31 | 2025-05-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46333530 | T2 DI SNEATH LANE PACIFICA 4/52 RPR ANCW | ICW
LC | 129333973 | 080/002 | T2 DI HUMBOLDT TRINITY 80/2L RPL ANCW | EUREKA | ETL.1820.POLE.WDPS | 2024-08-05 | 2024-05-31 | 2025-04-23 | On-Time |  | 2025-05-31 | 2025-05-31 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586918 | T2 DI HUMBOLDT TRINITY 80/2L RPL ANCW | 93E
LC | 123730206 | 043/249 | T3NT EI TMBLR-SAN LS BISP 43/249 BNT STL | PISMOBCH | ETL.3960.TOWR | 2022-06-01 | 2022-06-01 | 2023-07-18 | On-Time |  | 2025-06-01 | 2025-06-01 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45655643 | T3 EI TEMBLR-SAN LS BISP 43/249 BNT STEL | ICQ
LC | 123749149 | 055/238 | T2NT DI RND MTN-TBL MN#2 55/238 RPR GYWS | TABLEMTN | ETL.6070.TOWR | 2022-06-03 | 2022-06-01 | 2023-09-11 | On-Time |  | 2025-06-01 | 2025-06-01 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45703129 | T2 DI RND MTN-TBL MTN#2 55/238 RPR GYWS | ICS
LC | 123749729 | 056/239 | T2NT DI RND MTN-TB MT #2 56/239 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2022-06-03 | 2022-06-01 | 2023-08-15 | On-Time |  | 2025-06-01 | 2025-06-01 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 123752535 | 000/004 | T2NT DI NRTH DUBLN-CAYETANO 0/4 RPL INSS | CONCORD | ETL.4500.INSL.NCER | 2022-06-03 | 2022-06-01 | 2023-08-24 | On-Time |  | 2025-06-01 | 2025-06-01 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 31600501 | T2 DI NORTH DUBLIN-CAYETANO RPL INSS 4T | 93K
LC | 123752570 | 000/004 | T2NT DI NRTH DBLN-VNEYRD 0/4 RPL INSS | CONCORD | ETL.4501.INSL | 2022-06-03 | 2022-06-01 | 2023-08-11 | On-Time |  | 2025-06-01 | 2025-06-01 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 31624214 | T2 DI NORTH DUBLIN-VINEYARD RPL INSS 4TW | 93K
LC | 123759026 | 000/003 | T2NT DI NRTH DUBLN-CAYETANO 0/3 RPL INSS | CONCORD | ETL.4500.INSL.NCER | 2022-06-03 | 2022-06-01 | 2023-08-23 | On-Time |  | 2025-06-01 | 2025-06-01 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 31600501 | T2 DI NORTH DUBLIN-CAYETANO RPL INSS 4T | 93K
LC | 123767725 | 000/003 | T2NT DI NRTH DBLIN-VINEYARD 0/3 RPL INSS | CONCORD | ETL.4501.INSL | 2022-06-06 | 2022-06-01 | 2023-08-11 | On-Time |  | 2025-06-01 | 2025-06-01 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 31624214 | T2 DI NORTH DUBLIN-VINEYARD RPL INSS 4TW | 93K
LC | 123852810 | 013/110 | T2NT DI PRDISE-TBL MTN 13/110 BNT STEEL | TABLEMTN | ETL.4316.TOWR | 2022-06-15 | 2022-06-01 | 2023-07-18 | On-Time |  | 2025-06-01 | 2025-06-01 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45620068 | T2 DI PRDISE-TBL MTN 13/110 BNT STEEL | ICQ
LC | 123869998 | 001/009 | T2NT DI NORTH DUBLIN-VNYRD 1/9 RPL INSS | CONCORD | ETL.4501.INSL | 2022-06-18 | 2022-06-01 | 2023-08-11 | On-Time |  | 2025-06-01 | 2025-06-01 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 31608769 | DI NORTH DUBLIN-VNYRD 1/9 RPL INSS | 93K
LC | 123941036 | 000/004 | T3NT DI MORAGA-SN LNDRO #1 0/4 BNT STEEL | CONCORD | ETL.2770.TOWR | 2022-06-28 | 2022-06-01 | 2023-06-08 | On-Time |  | 2025-06-01 | 2025-06-01 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45697947 | T3NT DI MORAGA-SN LNDRO #1 0/4 BNT STEEL | ICQ
LC | 125273527 | 009/113B | T2NT DI DRUM-SUMMIT #2 009/113B RPL STRW | SACTO | ETL.1450.POLE.WOOD | 2023-01-03 | 2022-06-01 | 2023-07-29 | On-Time |  | 2025-06-01 | 2025-06-01 | 372 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE ACCL COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 31634269 | T3 DI DRUM-SUMMIT #2 001/013R RPL STRW | 70Y
LC | 128964198 | 009/114 | T2 DRUM-SUMMIT #2 9/114R RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-06-01 | 2024-06-01 | 2025-04-23 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458327 | T2 EI DRUM-SUMMIT#2 9/114R RPR GYWW | ICW
LC | 128964266 | 009/114 | T2 DRUM-SUMMIT #2 9/114L RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-06-01 | 2024-06-01 | 2025-04-23 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458328 | T2 EI DRUM-SUMMIT#2 9/114L RPR GYWW | ICW
LC | 128964317 | 009/113B | T2 EI DRUM-SUMMIT #2 009/113B RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-06-01 | 2024-06-01 | 2024-06-16 | On-Time |  | 2024-12-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46265839 | T2 EI DRUM-SUMMIT #2 009/113B RPR GYWW | ICW
LC | 128964361 | 009/113A | T2 EI DRUM-SUMMIT #2 009/113A RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-06-01 | 2024-06-01 | 2024-06-16 | On-Time |  | 2024-12-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46265860 | T2 EI DRUM-SUMMIT #2 009/113A RPR GYWW | ICW
LC | 128964367 | 009/113C | T2 EI DRUM-SUMMIT #2 009/113C RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-06-01 | 2024-06-01 | 2024-06-16 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46266183 | T2 EI DRUM-SUMMIT #2 009/113C RPR GYWW | ICW
LC | 128964582 | 027/194 | T2 DI CARIBOU TBL MTN 27/194 RPR FOND | TABLEMTN | ETL.4440.TOWR | 2024-06-01 | 2024-06-01 | 2025-05-19 | On-Time |  | 2025-06-01 | 2025-06-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46354062 | T2 DI CARIBOU TBL MTN 27/194 RPR FOND | ICQ
LC | 128964822 | 007/136C | T2 EI CARIBOU-WESTWOOD 007/136C RPR STRW | TABLEMTN | ETL.6300.POLE.WOOD | 2024-06-01 | 2024-06-01 | 2025-01-21 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337449 | T2 EI CARIBOU-WESTWOOD 007/136C RPR STRW | ICW
LC | 128965114 | 021/250 | T2 EI DRUM-SUMMIT #1 021/250R RPR GYWW | SACTO | ETL.1440.POLE.STPS | 2024-06-01 | 2024-06-01 | 2025-05-28 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46325981 | T2 EI DRUM-SUMMIT #1 021/250R RPR GYWW | ICW
LC | 128965135 | 009/108C | T2 DRUM-SUMMIT #2 009/108C RPL ANCW | SACTO | ETL.1450.POLE.NWOD | 2024-06-01 | 2024-06-01 | 2025-06-18 | Past Due |  | 2025-06-01 | 2025-06-01 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573632 | T2 EI DRUM-SUMMIT #2 RPL ANCW 4 STRT | 93E
LC | 128965146 | 021/250 | T2 EI DRUM-SUMMIT #1 021/250C RPR GYWW | SACTO | ETL.1440.POLE.STPS | 2024-06-01 | 2024-06-01 | 2025-05-28 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46325982 | T2 EI DRUM-SUMMIT #1 021/250C RPR GYWW | ICW
LC | 128965167 | 021/250 | T2 EI DRUM-SUMMIT #1 021/250L RPR GYWW | SACTO | ETL.1440.POLE.STPS | 2024-06-01 | 2024-06-01 | 2025-05-28 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46325983 | T2 EI DRUM-SUMMIT #1 021/250L RPR GYWW | ICW
LC | 128965188 | 007/042 | T2 EI MONTA VISTA-COYOTE SS 7/42 RMV VEG | MOSSLNDG | ETL.5090.TOWR | 2024-06-01 | 2024-06-01 | 2025-04-24 | On-Time |  | 2025-06-01 | 2025-06-01 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128965416 | 003/082 | T2 EI CARIBOU #2 003/082 RPR INSW | TABLEMTN | ETL.6280.INSL.NCER | 2024-06-01 | 2024-06-01 | 2025-05-06 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46337210 | T2 EI CARIBOU #2 003/082 RPR INSW | ICW
LC | 128965494 | 003/020 | T2 EI MOSS LANDING-METCALF 3/20 RMV VEG | MOSSLNDG | ETL.6050.TOWR | 2024-06-01 | 2024-06-01 | 2025-05-07 | On-Time |  | 2025-06-01 | 2025-06-01 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 128965573 | 028/243 | T2 EI CASCADE-CTTNWD 28/243 RPL INSS | TABLEMTN | ETL.1240.INSL.CERA | 2024-06-01 | 2024-06-01 | 2025-05-18 | On-Time |  | 2025-06-01 | 2025-06-01 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572156 | T2 EI CASCADE-CTTNWD 28/243 RPL INSS | 93I
LC | 128965574 | 024/209 | T2 EI CASCADE-COTTONWOOD 24/209 COTTER | TABLEMTN | ETL.1240.INSL.NCER | 2024-06-01 | 2024-06-01 | 2024-10-03 | On-Time |  | 2024-09-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46265951 | T2 EI CASCADE-COTTONWOOD 24/209 RPR INSW | ICW
LC | 128965580 | 026/308 | T2 EI DRUM-SUMMIT #1 26/308L RPR GYWW | SACTO | ETL.1440.POLE.WDPS | 2024-06-01 | 2024-06-01 | 2024-06-23 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46269350 | T2 EI DRUM-SUMMIT #1 26/308L RPR GYWW | ICW
LC | 128965653 | 069/351A | T2 EI MALIN-RUND MTN #2 69/351A RPR SHLD | TABLEMTN | ETL.6020.TOWR | 2024-06-01 | 2024-06-01 | 2025-02-25 | On-Time |  | 2025-06-01 | 2025-06-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338270 | T2 EI MALIN-RUND MTN #2 69/351A RPR SHLD | ICS
LC | 128965762 | 052/1019 | T2 EI HAT CRK #1-WSTWD 52/1019 INS ANMW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-01 | 2024-06-01 | 2025-03-28 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Animal Guard-Wood | Install | 46416128 | T2 EI HAT CRK #1-WSTWD 52/1019 INS ANMW | ICW
LC | 128965770 | 052/1019 | T2 EI HAT CRK #1-WSTWD 52/1019 RPR STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-01 | 2024-06-01 | 2025-03-29 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46416129 | T2 EI HAT CRK #1-WSTWD 52/1019 RPR STRW | ICW
LC | 128965772 | 052/1020 | T2 EI HAT CRK #1-WSTWD 52/1020 INS DMPW | TABLEMTN | ETL.7030.INSL | 2024-06-01 | 2024-06-01 | 2025-03-28 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46285872 | T2 EI HAT CRK #1-WSTWD 52/1020 INS DMPW | ICW
LC | 129015594 | 001/073 | T2 DI SPAULDING-SUMMIT 1/73 RPR GYWW | SACTO | ETL.8060.POLE.WOOD | 2024-06-03 | 2024-06-01 | 2024-06-26 | On-Time |  | 2024-12-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262108 | T2 DI SPAULDING-SUMMIT 1/73 RPR GYWW | ICW
LC | 129015599 | 014/284 | T2 DI COLGATE-PALERMO 14/284 RPL INSW | SACTO | ETL.6500.INSL.NCER | 2024-06-03 | 2024-06-01 | 2024-08-23 | On-Time |  | 2024-12-01 | 2025-06-01 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35558792 | T2 DI COLGATE-PALERMO 14/284 RPL INSW | 93I
LC | 129015799 | 011/054 | T2 DI VACA-LAKEVILLE #1 11/54 RPR INSS | SACTO | ETL.5840.INSL.NCER | 2024-06-03 | 2024-06-01 | 2025-03-31 | On-Time |  | 2025-06-01 | 2025-06-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46403760 | T2 DI VACA-LAKEVILLE #1 11/54 RPR INSS | ICS
LC | 129015827 | 011/054 | T2 DI VACA-LAKEVILLE #1 11/54 TOUCH | SACTO | ETL.5840.TOWR | 2024-06-03 | 2024-06-01 | 2025-03-16 | On-Time |  | 2024-12-01 | 2025-06-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46514376 | T2 DI VACA-LAKEVILLE #1 11/54 TOUCH | ICQ
LC | 129016171 | 034/246 | T2 DI CARIBOU-TBL MTN 034/246 RPL INSS | TABLEMTN | ETL.4440.INSL.CERA | 2024-06-03 | 2024-06-01 | 2025-04-06 | On-Time |  | 2025-06-01 | 2025-06-01 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569572 | T2 DI CARIBOU-TBL MTN RPL INSS | 93K
LC | 129016227 | 034/247 | T2 DI CARIBOU-TM 34/247 BNT STEEL | TABLEMTN | ETL.4440.TOWR | 2024-06-03 | 2024-06-01 | 2025-05-20 | On-Time |  | 2025-06-01 | 2025-06-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46354063 | T2 DI CARIBOU-TM 34/247 BNT STEEL | ICQ
LC | 129021850 | 000/001B | T2 DI PIT #1-MC ARTHUR 0/1B RPR HRDW | TABLEMTN | ETL.7790.POLE.NWOD | 2024-06-04 | 2024-06-01 | 2025-02-10 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46383870 | T2 DI PIT #1-MC ARTHUR 0/1B RPR HRDW | ICW
LC | 129021851 | 000/001B | T2 DI PIT #1-MC ARTHUR 0/1B COTTER | TABLEMTN | ETL.7790.INSL.NCER | 2024-06-04 | 2024-06-01 | 2025-02-10 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46383871 | T2 DI PIT #1-MC ARTHUR 0/1B COTTER | ICW
LC | 129021907 | 038/224 | T2 INDIAN FLAT-YOSEMITE 38/224 COTTER | FRESNO | ETL.1112.INSL.NCER | 2024-06-04 | 2024-06-01 | 2024-06-01 | Past Due |  | 2025-06-01 | 2025-06-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297930 | T2 DI INDIAN FLAT YSMITE 38/224 COTTER | ICS
LC | 129141496 | 012/246 | T2 DI CLGT-PALERMO 012/246 TOUCH | TABLEMTN | ETL.6500.POLE.NWOD | 2024-06-28 | 2024-06-01 | 2025-02-28 | On-Time |  | 2024-12-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46463546 | T2 DI CLGT-PALERMO 012/246 RPR STRW | ICW
LC | 129141551 | 011/221 | T2 DI COCLGATE-PALERMO 11/221 RMV VEG | SACTO | ETL.6500.POLE.WOOD | 2024-06-28 | 2024-06-01 | 2025-01-16 | On-Time |  | 2025-06-01 | 2025-06-01 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129141553 | 011/221 | T2 DI COLGATE-PALERMO 11/221 INSP STRW | SACTO | ETL.6500.POLE.WOOD | 2024-06-28 | 2024-06-01 | 2024-10-08 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Structure-Wood | Inspect | 46329132 | T2 DI COLGATE-PALERMO 11/221 INSP STRW | ICW
LC | 129141935 | 027/193 | T2 DI CRIBU TBL MTN 27/193 RPR JUMS | TABLEMTN | ETL.4440.INSL.NCER | 2024-06-28 | 2024-06-01 | 2024-12-20 | On-Time |  | 2024-09-01 | 2025-06-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46274115 | T2 DI CRIBU TBL MTN 27/193 RPR JMPS | ICS
LC | 129142163 | 007/057 | T2 DI CARIBOU TBL MTN 7/57 RPR GYWT | TABLEMTN | ETL.4440.TOWR | 2024-06-28 | 2024-06-01 | 2025-05-19 | On-Time |  | 2025-06-01 | 2025-06-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46354068 | T2 DI CARIBOU TBL MTN 7/57 RPR GYWT | ICQ
LC | 129142336 | 003/080 | T2 DI CSCD-BENTON-DSCHTS 3/80 RPR GYWW | TABLEMTN | ETL.6310.POLE.WOOD | 2024-06-28 | 2024-06-01 | 2025-05-16 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46383879 | T2 DI CSCD-BENTON-DSCHTS 3/80 RPR GYWW | ICW
LC | 129142711 | 039/231 | T2 INDN FLT-YOSEMITE 39/231 CANCEL | FRESNO | ETL.1112.POLE.NWOD | 2024-06-28 | 2024-06-01 | 2024-06-01 | Past Due |  | 2025-06-01 | 2025-06-01 | 93Z | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31722176 | T2 DI INDN FLT-YOSEMITE 39/231 RPL ANCT | 93Z
LC | 129142712 | 039/231 | T2 INDN FLT-YOSEMITE 39/231 RPL HRDT | FRESNO | ETL.1112.POLE.NWOD | 2024-06-28 | 2024-06-01 | 2024-06-01 | Past Due |  | 2025-06-01 | 2025-06-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46297901 | T2 DI INDN FLT-YOSEMITE 39/231 RPL HRDT | ICQ
LC | 129153813 | 027/197 | T2 DI CRBU TBL MTN 27/197 RPR JUMS | TABLEMTN | ETL.4440.INSL.NCER | 2024-07-01 | 2024-06-01 | 2024-12-20 | On-Time |  | 2024-12-01 | 2025-06-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46273974 | T2 DI CRBU TBL MTN 27/197 RPR JUMS | ICS
LC | 129187701 | 001/016 | T2 DI CRAG VIEW-CSCD 001/016 RPR INSW | TABLEMTN | ETL.1350.INSL.NCER | 2024-07-08 | 2024-06-01 | 2025-01-17 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46454381 | T2 DI CRAG VIEW-CSCD 001/016 RPR INSW | ICW
LC | 129215757 | 000/003 | T2 DI CASCDE-BENTN-DSCHUTES 0/3 RPR STRW | TABLEMTN | ETL.6310.POLE.WOOD | 2024-07-12 | 2024-06-01 | 2025-03-31 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46383920 | T2 DI CASCDE-BENTN-DSCHUTES 0/3 RPR STRW | ICW
LC | 129224163 | 008/064 | T2 DI VCA-VCVIL-JMSN-NRTH 8/64 RPR INSS | SACTO | ETL.4100.INSL.CERA | 2024-07-15 | 2024-06-01 | 2025-05-23 | On-Time |  | 2025-06-01 | 2025-06-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46324618 | T2 DI VCA-VCVIL-JMSN-NRTH 8/64 RPR INSS | ICS
LC | 129236200 | 000/020 | T2 DI CASCAD-BNTN-DSCHTS 00/20 RPR STRW | TABLEMTN | ETL.6310.POLE.WOOD | 2024-07-17 | 2024-06-01 | 2025-03-31 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46383922 | T2 DI CASCAD-BNTN-DSCHTS 00/20 RPR STRW | ICW
LC | 129245508 | 012/147B | T2 DI DRUM-SUMMIT #2 12/147B RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-07-19 | 2024-06-01 | 2025-04-24 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458341 | T2 DI DRUM-SUMMIT #2 12/147B RPR GYWW | ICW
LC | 129245534 | 027/196 | T2 DI CARIBOU-TBL MTN 027/196 RPR JMPS | TABLEMTN | ETL.4440.INSL.NCER | 2024-07-19 | 2024-06-01 | 2025-04-05 | On-Time |  | 2025-06-01 | 2025-06-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46337600 | T2 DI CARIBOU-TBL MTN 027/196 RPR JMPS | ICS
LC | 129245911 | 012/147A | T2 DRUM-SUMMIT #2 12/147A RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-07-19 | 2024-06-01 | 2025-04-24 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458342 | T2 DI DRUM-SUMMIT #2 12/147A RPR GYWW | ICW
LC | 129247311 | 016/087 | T2 DI VACA-PARKWAY 16/87 RPR SHLS | SACTO | ETL.5850.TOWR | 2024-07-19 | 2024-06-01 | 2025-01-24 | On-Time |  | 2025-06-01 | 2025-06-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46324633 | T2 DI VACA-PARKWAY 16/87 RPR SHLS | ICS
LC | 129274900 | 033/236 | T2 DI CARIBOU-TBL MTN 033/236 BNT STEEL | TABLEMTN | ETL.4440.TOWR | 2024-07-22 | 2024-06-01 | 2025-05-17 | On-Time |  | 2025-06-01 | 2025-06-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46337129 | T2 DI CARIBOU-TBL MTN 033/236 BNT STEEL | ICQ
LC | 129280144 | 035/262 | T2 DI CARIBOU-TBL MTN 035/262 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2024-07-23 | 2024-06-01 | 2025-05-20 | On-Time |  | 2025-06-01 | 2025-06-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46337131 | T2 DI CARIBOU-TBL MTN 035/262 RPR STRT | ICQ
LC | 129280221 | 007/098 | T2 DI JOLON TAP 007/098 RPR STRW | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-07-23 | 2024-06-01 | 2025-01-27 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46391187 | T2 DI JOLON TAP 007/098 RPR STRW | ICW
LC | 129280222 | 007/098 | T2 DI JOLON TAP 007/098 RPR IBWW | MOSSLNDG | ETL.7321.INSL | 2024-07-23 | 2024-06-01 | 2025-01-27 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46391188 | T2 DI JOLON TAP 007/098 RPR IBWW | ICW
LC | 129333968 | 012/248 | T2 DI CLGTE PLMRO 12/248 RPR STRW | SACTO | ETL.6500.POLE.NWOD | 2024-08-05 | 2024-06-01 | 2024-11-22 | On-Time |  | 2024-12-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46329131 | T2 DI CLGTE PLMRO 12/248 RPR STRW | ICW
LC | 129334413 | 014/289 | T2 DI COLGATE-PALERMO 14/289 RPR STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-08-05 | 2024-06-01 | 2025-02-07 | On-Time |  | 2025-06-01 | 2025-06-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401366 | T2 DI COLGATE-PALERMO 14/289 RPR STRW | ICW
LC | 129347555 | 035/260 | T2 DI CARIBOU-TBL MTN 35/260 RPR CRSS | TABLEMTN | ETL.4440.POLE.STPS | 2024-08-07 | 2024-06-01 | 2025-04-01 | On-Time |  | 2025-06-01 | 2025-06-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Steel | Repair | 46337601 | T2 DI CARIBOU-TBL MTN 35/260 RPR CRSS | ICS
LC | 129353852 | 009/047 | T2 DI VACA LAKEVILLE#1 09/047 RPR INSS | SACTO | ETL.5840.INSL.CERA | 2024-08-08 | 2024-06-01 | 2025-03-31 | On-Time |  | 2025-06-01 | 2025-06-01 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46401535 | T2 DI VACA LAKEVILLE#1 09/047 RPR INSS | ICS
LC | 123740759 | 040/228 | T2NT EI TMBLR-SN LS OBPO 40/228 INS RPTS | PISMOBCH | ETL.3960.INSL.NCER | 2022-06-02 | 2022-06-02 | 2023-07-19 | On-Time |  | 2025-06-02 | 2025-06-02 | 593 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO NTDE | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 45672089 | T2 EI TMBLR-SAN LUS OBPO 40/228 INS RPTS | ICB
LC | 123742190 | 018/095 | T2NT EI RND MTN-TLE MN #2 18/95 RPR GYWS | TABLEMTN | ETL.6070.TOWR | 2022-06-02 | 2022-06-02 | 2023-08-12 | On-Time |  | 2025-06-02 | 2025-06-02 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45700181 | T2 EI RND MTN-TABL MTN #2 18/95 RPR GYWS | ICS
LC | 123743323 | 045/393 | T2NT EI RND MTN-CTTNWD #3 45/3 RPR STRT | TABLEMTN | ETL.5650.TOWR | 2022-06-02 | 2022-06-02 | 2023-08-23 | On-Time |  | 2025-06-02 | 2025-06-02 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45581854 | T2 EI RND MTN-CTTNWD #3 45/3 RPR STRT | ICQ
LC | 123743871 | 023/116 | T2NT EI RND MT-TBL MT #2 23/116 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2022-06-02 | 2022-06-02 | 2023-08-23 | On-Time |  | 2025-06-02 | 2025-06-02 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO FRAB | Overgrown | Vegetation | Remove
LC | 123744540 | 040/161 | T2NT DI DBL MDWY #3 40/161 RPR GYWS | PISMOBCH | ETL.5980.TOWR | 2022-06-02 | 2022-06-02 | 2023-07-12 | On-Time |  | 2025-06-02 | 2025-06-02 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45655644 | T2 DI DBL MDWY #3 40/161 RPR GYWS | ICS
LC | 123767917 | 063/258 | T0 T2NT DI DIABLO-GATES #1 63/258 RPR ST | PISMOBCH | ETL.5960.TOWR | 2022-06-06 | 2022-06-02 | 2023-05-31 | On-Time |  | 2025-06-02 | 2025-06-02 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH PRTO AIR FRAA TER0 | No Good/Out of Stdrd | Structure-Tower | Repair | 45655647 | DI DIABLO-GATES #1 63/258 RPR STRT | ICQ
LC | 123769661 | 017/071 | T3NT DI DIABLO-GATES#1 17/071 RPR GYWS | PISMOBCH | ETL.5960.TOWR | 2022-06-06 | 2022-06-02 | 2023-07-21 | On-Time |  | 2025-06-02 | 2025-06-02 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45655650 | T3 DI DIABLO-GATES#1 17/071 RPR GYWS | ICS
LC | 123769666 | 062/256 | T0 T2NT DI DIABLO-GATES #1 62/256 RPR ST | PISMOBCH | ETL.5960.TOWR | 2022-06-06 | 2022-06-02 | 2023-06-01 | On-Time |  | 2025-06-02 | 2025-06-02 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH PRTO AIR FRAA TER0 | No Good/Out of Stdrd | Structure-Tower | Repair | 45655651 | T0 DI DIABLO-GATES #1 62/256 RPR STRT | ICQ
LC | 123770681 | 040/162 | T2NT DI DBLO- MIDWAY#2 40/162 RPR GYWS | PISMOBCH | ETL.5970.TOWR | 2022-06-06 | 2022-06-02 | 2023-07-12 | On-Time |  | 2025-06-02 | 2025-06-02 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45655653 | T2 DI DIABLO- MIDWAY#2 40/162 RPR GYWS | ICS
LC | 123770799 | 002/015 | T3NT DI DIABLO-GATES#1 2/015 RPL INSS | PISMOBCH | ETL.5960.INSL | 2022-06-06 | 2022-06-02 | 2023-11-07 | On-Time |  | 2025-06-02 | 2025-06-02 | 532 | TR3N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE ACCM COMP OH TR3 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 31618032 | T3 DI DIABLO-GATES#1 2/015 RPL INSS | 93K
LC | 123778541 | 060/253 | T2NT DI RND MN TBL MN #1 60/253 RPR GYWS | TABLEMTN | ETL.6060.TOWR | 2022-06-07 | 2022-06-02 | 2023-08-23 | On-Time |  | 2025-06-02 | 2025-06-02 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45699308 | T2 DI RND MTN TBL MTN #1 60/253 RPR GYWS | ICS
LC | 123862412 | 006/042 | T3NT DI MRGA-SAN LNDRO #1 6/042 RPR STRT | CONCORD | ETL.2770.TOWR | 2022-06-17 | 2022-06-02 | 2023-09-12 | On-Time |  | 2025-06-02 | 2025-06-02 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45697893 | T3 DI MRGA-SAN LNDRO #1 006/042 RPR STRT | ICQ
LC | 123950508 | 006/049 | T3NT DI MRAGA-SN LNDRO#1 6/049 RMV VEG | CONCORD | ETL.2770.TOWR | 2022-06-28 | 2022-06-02 | 2023-04-24 | On-Time |  | 2025-06-02 | 2025-06-02 | 564 | TR3N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR3N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129015048 | 011/392 | T2 SPAULDING-SUMMIT 11/392 RPR IBWW | SACTO | ETL.8060.INSL.NCER | 2024-06-03 | 2024-06-02 | 2025-05-30 | On-Time |  | 2024-09-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46398061 | T2 DI SPAULDING-SUMMIT 11/392 RPR IBWW | ICW
LC | 129021245 | 011/243 | T2 DI CSCDE-BNTN-DSUTS 11/243 RPR GYWW | TABLEMTN | ETL.6310.POLE.WOOD | 2024-06-04 | 2024-06-02 | 2024-11-17 | On-Time |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262877 | T2 DI CSCDE-BNTN-DSUTS 11/243 RPR GYWW | ICW
LC | 129021513 | 093/014A | T2 DI HMBLDT TRNTY 93/014A RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-04 | 2024-06-02 | 2025-04-23 | On-Time |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346031 | T2 DI HMBLDT TRNTY 93/014A RPR GYWW | ICW
LC | 129021515 | 093/014A | T2 DI HMBLDT TRNTY 93/014A RPR JMPW | EUREKA | ETL.1820.INSL.NCER | 2024-06-04 | 2024-06-02 | 2025-04-23 | On-Time |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46346032 | T2 DI HMBLDT TRNTY 93/014A RPR JMPW | ICW
LC | 129021556 | 093/014C | T2 DI HMBLDT TRNTY 93/014C RPR JMPW | EUREKA | ETL.1820.INSL.NCER | 2024-06-04 | 2024-06-02 | 2025-04-23 | On-Time |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46346034 | T2 DI HMBLDT TRNTY 93/014C RPR JMPW | ICW
LC | 129021559 | 093/014C | T2 DI HMBLDT TRNTY 93/14C COTTER | EUREKA | ETL.1820.INSL.NCER | 2024-06-04 | 2024-06-02 | 2025-04-23 | On-Time |  | 2024-12-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46262173 | T2 DI HMBLDT TRNTY 93/014C COTTER | ICW
LC | 129021591 | 093/014B | T2 DI HMBLDT-TRNTY 93/014B RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-04 | 2024-06-02 | 2025-04-23 | On-Time |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346033 | T2 DI HMBLDT-TRNTY 93/014B RPR GYWW | ICW
LC | 129021751 | 018/594 | T2 SPAULDING-SUMMIT 18/594 RPR GYWW | SACTO | ETL.8060.POLE.WOOD | 2024-06-04 | 2024-06-02 | 2025-05-30 | On-Time |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46398062 | T2 DI SPAULDING-SUMMIT 18/594 RPR GYWW | ICW
LC | 129021770 | T001/002 | T2 DI TYLUCAY NAPA#1 T1/002 RPL STRW | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-06-04 | 2024-06-02 | 2025-04-24 | On-Time |  | 2025-06-02 | 2025-06-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573264 | T2 DI TYLUCAY NAPA#1 T1/002 RPL STRW | 70Y
LC | 129022037 | :013/069 | T2 DI CHC-SLINS-SLEDAD :13/69 RPR STRT | MOSSLNDG | ETL.2900.TOWR | 2024-06-04 | 2024-06-02 | 2025-04-29 | On-Time |  | 2025-06-02 | 2025-06-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416704 | T2 DI CHC-SLINS-SLEDAD :13/69 RPR STRT | ICQ
LC | 129022084 | T002/005 | T2 DI TULUCAY-NAPA#1 T02/05 RPL INSW | LAKEVLLE | ETL.8180.INSL.NCER | 2024-06-04 | 2024-06-02 | 2024-10-28 | On-Time |  | 2024-09-02 | 2025-06-02 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35558900 | T2 DI TULUCAY-NAPA#1 T02/05 RPL INSW | 93I
LC | 129022252 | C011/008 | T2 DI FULTON-CALISTOGA C11/08 RMV VEG | LAKEVLLE | ETL.6880.POLE.WOOD | 2024-06-04 | 2024-06-02 | 2025-01-21 | On-Time |  | 2025-06-02 | 2025-06-02 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW ACCM CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129022253 | C011/008 | T2 DI FULTON-CALISTOGA C11/08 RPR ANCW | LAKEVLLE | ETL.6880.POLE.WOOD | 2024-06-04 | 2024-06-02 | 2025-01-15 | On-Time |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46308644 | T2 DI FULTON-CALISTOGA C11/08 RPR ANCW | ICW
LC | 129022256 | C011/008 | T2 DI FULTON-CALISTOGA C11/8 RPL INSW | LAKEVLLE | ETL.6880.INSL.CERA | 2024-06-04 | 2024-06-02 | 2025-05-05 | On-Time |  | 2025-06-02 | 2025-06-02 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35559517 | T2 DI FULTON-CALISTOGA C11/08 RPL INSW | 93I
LC | 129153966 | 039/230 | T2 DI INDIAN FLT YSMITE 39/230 RMV VEG | FRESNO | ETL.1112.POLE.NWOD | 2024-07-01 | 2024-06-02 | 2025-01-06 | On-Time |  | 2025-06-02 | 2025-06-02 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129187409 | T001/004 | T2 DI TULUCAY-NAPA #1 T01/04 RPR STRW | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-07-08 | 2024-06-02 | 2025-04-29 | On-Time |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46403764 | T2 DI TULUCAY-NAPA #1 T01/04 RPR STRW | ICW
LC | 129187615 | T001/008 | T2 TULUCAY-NAPA #1 T1/8 RPL STRW | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-07-08 | 2024-06-02 | 2024-06-02 | Past Due |  | 2025-06-02 | 2025-06-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573263 | T2 DI TULUCAY-NAPA #1 T1/8 RPL STRW | 70Y
LC | 129192937 | T001/007 | T2 TULUCAY-NAPA #1 T01/07 RPR STRW | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-07-09 | 2024-06-02 | 2024-06-02 | Past Due |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46403765 | T2 DI TULUCAY-NAPA #1 T01/07 RPR STRW | ICW
LC | 129192939 | T001/007 | T2 DI TULUCAY-NAPA #1 T01/07 RPR ANCW | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-07-09 | 2024-06-02 | 2025-04-25 | On-Time |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46403766 | T2 DI TULUCAY-NAPA #1 T01/07 RPR ANCW | ICW
LC | 129193268 | 045/393 | T2 DI PIT#1-COTTNWD 45/393 RPR GYWT | TABLEMTN | ETL.5390.TOWR | 2024-07-09 | 2024-06-02 | 2025-04-10 | On-Time |  | 2025-06-02 | 2025-06-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381945 | T2 DI PIT#1-COTTNWD 45/393 RPR GYWT | ICQ
LC | 129193293 | 027/322 | T2NT DI DRUM-SUMMIT #2 27/322 RPR STRT | SACTO | ETL.1450.TOWR | 2024-07-09 | 2024-06-02 | 2025-03-24 | On-Time |  | 2027-06-02 | 2025-06-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381469 | T2NT DI DRUM-SUMMIT #2 27/322 RPR STRT | ICQ
LC | 129193658 | 027/332 | T2 DI DRUM SUMMIT #2 27/332 RPR STRT | SACTO | ETL.1450.TOWR | 2024-07-09 | 2024-06-02 | 2025-03-24 | On-Time |  | 2025-06-02 | 2025-06-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381470 | T2 DI DRUM SUMMIT #2 27/332 RPR STRT | ICQ
LC | 129193682 | 239 | T2 DRUM SUMMIT #2 27/332 RPR SWTC | SACTO | ETL.1450.SWIT | 2024-07-09 | 2024-06-02 | 2024-06-02 | Past Due |  | 2025-06-02 | 2025-06-02 | 623 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR OH TR2 PRTO AIR FRAB | Out of Adjustment | Switch | Repair | 46457803 | T2 DI DRUM SUMMIT #2 27/332 RPR SWTC | ICE
LC | 129193685 | 045/394 | T2 DI ROUND MTN-CTNWD #3 45/394 TOUCH | TABLEMTN | ETL.5650.TOWR | 2024-07-09 | 2024-06-02 | 2025-03-13 | On-Time |  | 2024-12-02 | 2025-06-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46477850 | T2 DI ROUND MTN-CTNWD #3 45/394 TOUCH | ICQ
LC | 129193810 | 009/050 | T2 DI VACA-PARKWAY 9/50 RPL HRDT | SACTO | ETL.5850.TOWR | 2024-07-09 | 2024-06-02 | 2025-01-06 | On-Time |  | 2025-06-02 | 2025-06-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46382057 | T2 DI VACA-PARKWAY 9/50 RPL HRDT | ICQ
LC | 129204024 | T002/009 | T2 DI TULUCAY-NAPA #1 T2/9 RPL STRW | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-07-10 | 2024-06-02 | 2025-04-30 | On-Time |  | 2025-06-02 | 2025-06-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35571899 | T2 DI TULUCAY-NAPA #1 T2/9 RPL STRW | 70Y
LC | 129213530 | 021/258 | T2 DRUM-SUMMIT #1 21/258L RPL HRDD | SACTO | ETL.1440.POLE.WDPS | 2024-07-12 | 2024-06-02 | 2025-05-29 | On-Time |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Hardware-Wood | Replace | 46398072 | T2 DI DRUM-SUMMIT #1 21/258 RPL HRDD | ICW
LC | 129214923 | 008/047 | T2 DI VACA-PARKWAY 8/47 COTTER | SACTO | ETL.5850.INSL | 2024-07-12 | 2024-06-02 | 2025-01-24 | On-Time |  | 2025-06-02 | 2025-06-02 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46324634 | T2 DI VACA-PARKWAY 8/47 COTTER | ICS
LC | 129224468 | 009/172 | T2 DI COLGATE-PALERMO 9/172 RPL INSW | SACTO | ETL.6500.INSL | 2024-07-15 | 2024-06-02 | 2025-04-30 | On-Time |  | 2025-06-02 | 2025-06-02 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573055 | T2 DI COLGATE-PALERMO 9/172 RPL INSW | 93I
LC | 129224541 | 053/001 | T2 DI HUMBOLDT-TRINITY 53/1L COMPLETE | EUREKA | ETL.1820.POLE.WDPS | 2024-07-15 | 2024-06-02 | 2025-04-23 | On-Time |  | 2025-06-02 | 2025-06-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35621843 | T2 DI HUMBOLDT-TRINITY 53/1L RPL STRW | 70Y
LC | 129224542 | 053/001 | 129224542 | EUREKA | ETL.1820.POLE.WDPS | 2024-07-15 | 2024-06-02 | 2025-04-23 | On-Time |  | 2025-06-02 | 2025-06-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35621843 | T2 DI HUMBOLDT-TRINITY 53/1L RPL STRW | 70Y
LC | 129224572 | 045/388 | T2 DI RND MTN-COTTNWD #3 45/388 COTTER | TABLEMTN | ETL.5650.INSL | 2024-07-15 | 2024-06-02 | 2025-03-04 | On-Time |  | 2025-06-02 | 2025-06-02 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46416223 | T2 DI RND MTN-COTTNWD #3 45/388 COTTER | ICS
LC | 129224597 | T001/003 | T2 DI TULUCAY-NAPA #1 T001/3 RPR GYWW | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-07-15 | 2024-06-02 | 2025-04-29 | On-Time |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46403763 | T2 DI TULUCAY-NAPA #1 T001/3 RPR GYWW | ICW
LC | 129284795 | 011/388 | T2 SPAULDING-SUMMIT 11/388 RPR STRW | SACTO | ETL.8060.POLE.WOOD | 2024-07-24 | 2024-06-02 | 2025-05-30 | On-Time |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401360 | T2 DI SPAULDING-SUMMIT 11/388 RPR STRW | ICW
LC | 129284876 | 038/223 | T2 DI INDIAN FLAT-YSMT 38/223 RMV VEG | FRESNO | ETL.1112.TOWR | 2024-07-24 | 2024-06-02 | 2025-01-06 | On-Time |  | 2025-06-02 | 2025-06-02 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129293301 | 011/151C | T2 DI JOLON TAP 011/151C RPL POLE | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-07-26 | 2024-06-02 | 2025-01-19 | On-Time |  | 2025-06-02 | 2025-06-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35587537 | T2 DI JOLON TAP 011/151C RPL PL | 70Y
LC | 129295080 | 089/007C | T2 HMBLDT-TRINITY 89/07C RPL STRW | EUREKA | ETL.1820.POLE.WOOD | 2024-07-26 | 2024-06-02 | 2024-06-02 | Past Due |  | 2025-06-02 | 2025-06-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586941 | T2 DI HMBLDT-TRINITY 89/07A RPL STRW | 70Y
LC | 129295606 | 009/175 | T2 DI CLGT-PALERMO 009/175 RMV VEG | SACTO | ETL.6500.POLE.WOOD | 2024-07-26 | 2024-06-02 | 2024-09-23 | On-Time |  | 2025-06-02 | 2025-06-02 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129313488 | 089/007A | T2 HMBLDT-TRINITY 89/07A RPL STRW | EUREKA | ETL.1820.POLE.WOOD | 2024-07-31 | 2024-06-02 | 2024-06-02 | Past Due |  | 2025-06-02 | 2025-06-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586941 | T2 DI HMBLDT-TRINITY 89/07A RPL STRW | 70Y
LC | 129313508 | 089/007B | T2 HMBLDT-TRINITY 89/07B RPL STRW | EUREKA | ETL.1820.POLE.WOOD | 2024-07-31 | 2024-06-02 | 2024-06-02 | Past Due |  | 2025-06-02 | 2025-06-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586941 | T2 DI HMBLDT-TRINITY 89/07A RPL STRW | 70Y
LC | 129333965 | 093/012 | T2 DI HUMBOLDT-TRINITY 93/12L RPR STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-08-05 | 2024-06-02 | 2025-04-23 | On-Time |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46403065 | T2 DI HUMBOLDT-TRINITY 93/12L RPR STRW | ICW
LC | 129353628 | 093/013 | T2 DI HMBLDT-TRINITY 93/13 COTTER | EUREKA | ETL.1820.INSL.CERA | 2024-08-08 | 2024-06-02 | 2025-04-23 | On-Time |  | 2024-12-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46308603 | T2 DI HMBLDT-TRINITY 093/013 RPR INSW | ICW
LC | 129376270 | 008/165 | T2 DI COLGATE PALERMO 8/165 RPL STRW | SACTO | ETL.6500.POLE.WOOD | 2024-08-12 | 2024-06-02 | 2025-04-30 | On-Time |  | 2025-06-02 | 2025-06-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586884 | T2 DI CLGTE PLMRO 08/165 RPL STRW | 70Y
LC | 129382221 | 011/137 | T2 DUM-SUMMT #1 11/137 RMV VEG | SACTO | ETL.1440.POLE.WDPS | 2024-08-13 | 2024-06-02 | 2024-06-02 | Past Due |  | 2025-06-02 | 2025-06-02 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129382289 | 045/391 | T2 DI RND MTN-CTTNWD #3 45/391 RMV VEG | TABLEMTN | ETL.5650.TOWR | 2024-08-13 | 2024-06-02 | 2024-08-27 | On-Time |  | 2025-06-02 | 2025-06-02 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129409154 | T002/008 | T2 DI TULUCAY NAPA #1 T002/8 RPR INSW | LAKEVLLE | ETL.8180.INSL.NCER | 2024-08-19 | 2024-06-02 | 2025-04-25 | On-Time |  | 2025-06-02 | 2025-06-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46401532 | T2 DI TULUCAY NAPA #1 T002/8 RPR INSW | ICW
LC | 129886247 | 018/124 | T3 MTCLF-GRN VLY 18/124 PTT NRP COMPLETE | MOSSLNDG | ETL.2540.POLE.WDPS | 2024-12-02 | 2024-12-02 | 2025-01-17 | On-Time |  | 2025-06-02 | 2025-06-02 | 539 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO FRAB | Investigate | Non-Routine Patrol | Ground Patrol | 46403037 | T3 METCALF-GREEN VALLEY 18/124 PTT NRP | BFY
LC | 123871209 | 000/001 | T2NT DI CLGTE-PLRMO 0/1 RMV VEG | SACTO | ETL.6500.POLE.WOOD | 2022-06-18 | 2022-06-03 | 2023-12-21 | On-Time |  | 2025-06-03 | 2025-06-03 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 128986121 | C002/010 | T2 EI PALERMO-COLGATE C002/010 RPL INSS | SACTO | ETL.5360.INSL.CERA | 2024-06-03 | 2024-06-03 | 2025-05-03 | On-Time |  | 2025-06-03 | 2025-06-03 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570811 | T2 EI PALERMO-COLGATE C002/010 RPL INSS | 93K
LC | 128988234 | 002/027 | T2 EI COLGTE-SMARTVILLE #2 2/27 RPR GYWW | SACTO | ETL.6520.POLE.NWOD | 2024-06-03 | 2024-06-03 | 2024-08-30 | On-Time |  | 2024-11-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46279750 | T2 EI COLGTE-SMARTVILLE #2 2/27 RPR GYWW | ICW
LC | 128996586 | 018/079 | T2 EI MORRO BAY-SLR SS #1 18/79 RPL INSS | PISMOBCH | ETL.5300.INSL | 2024-06-03 | 2024-06-03 | 2025-04-07 | On-Time |  | 2025-06-03 | 2025-06-03 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35583345 | T0 EI MORRO BAY-SOLAR SS#1 REP INS 6 LST | 93K
LC | 128997088 | 021/189 | T2 EI CSCDE-CTTNWD 21/189L RPR GYWW | TABLEMTN | ETL.1240.POLE.STPS | 2024-06-03 | 2024-06-03 | 2025-02-04 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46383869 | T2 EI CSCDE-CTTNWD 21/189L RPR GYWW | ICW
LC | 128997339 | 018/079 | T2 EI MORRO BAY-SLR SS #2 18/79 RPL INSS | PISMOBCH | ETL.5310.INSL | 2024-06-03 | 2024-06-03 | 2024-06-03 | Past Due |  | 2025-06-03 | 2025-06-03 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577375 | T0 EI MORRO BAY-SOLAR SS#2 42/180 RPLC I | 93K
LC | 129002787 | 003/036 | T2 EI COLGTE-SMARTVILLE #2 3/36 RPR GYWW | SACTO | ETL.6520.POLE.NWOD | 2024-06-03 | 2024-06-03 | 2025-02-19 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324549 | T2 EI COLGTE-SMARTVILLE #2 3/36 RPR GYWW | ICW
LC | 129002791 | 005/062 | T2 EI COLGATE-SMRTVLLE #2 5/62L RPR GYWW | SACTO | ETL.6520.POLE.STPS | 2024-06-03 | 2024-06-03 | 2025-03-05 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324547 | T2 EI COLGATE-SMRTVLLE #2 5/62L RPR GYWW | ICW
LC | 129003166 | 005/062 | T2 EI COLGATE-SMRTVLLE #2 5/62R RPR GYWW | SACTO | ETL.6520.POLE.STPS | 2024-06-03 | 2024-06-03 | 2025-03-05 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324546 | T2 EI COLGATE-SMRTVLLE #2 5/62R RPR GYWW | ICW
LC | 129003273 | 005/062 | T2 EI COLGATE-SMRTVLLE #2 5/62C RPR GYWW | SACTO | ETL.6520.POLE.STPS | 2024-06-03 | 2024-06-03 | 2025-03-05 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324545 | T2 EI COLGATE-SMRTVLLE #2 5/62C RPR GYWW | ICW
LC | 129003663 | 003/035 | T2 EI COLGTE-SMARTVILLE #2 3/35 RPR GYWW | SACTO | ETL.6520.POLE.NWOD | 2024-06-03 | 2024-06-03 | 2025-02-19 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324550 | T2 EI COLGTE-SMARTVILLE #2 3/35 RPR GYWW | ICW
LC | 129003666 | 002/033 | T2 EI COLGTE-SMARTVILLE #1 2/33 COMPLETE | SACTO | ETL.6510.POLE.NWOD | 2024-06-03 | 2024-06-03 | 2025-02-19 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324551 | T2 EI COLGTE-SMARTVILLE #1 2/33 RPR GYWW | ICW
LC | 129003668 | 003/038 | T2 EI COLGTE-SMARTVILLE #2 3/38 RPR GYWW | SACTO | ETL.6520.POLE.NWOD | 2024-06-03 | 2024-06-03 | 2025-02-18 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324548 | T2 EI COLGTE-SMARTVILLE #2 3/38 RPR GYWW | ICW
LC | 129008428 | C004/017 | T2 EI PALERMO-COLGATE C004/017 RPR FOND | TABLEMTN | ETL.5360.TOWR | 2024-06-03 | 2024-06-03 | 2025-05-21 | On-Time |  | 2025-06-03 | 2025-06-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46310432 | T2 EI PALERMO-COLGATE C004/017 RPR FOND | ICQ
LC | 129011961 | 039/170 | T2 EI MRRO BY-SLR SS #1 39/170 INS ZENA | PISMOBCH | ETL.5300.TOWR | 2024-06-03 | 2024-06-03 | 2025-04-06 | On-Time |  | 2025-06-03 | 2025-06-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Animal Guard-Steel | Install | 46329545 | T2 EI MRRO BY-SLR SS #1 39/170 INS ZENA | ICS
LC | 129014201 | 010/078 | T2 EI TIGER CRK-ELCTRA 10/78 TOUCH | VICTOR | ETL.5780.TOWR | 2024-06-03 | 2024-06-03 | 2025-02-04 | On-Time |  | 2024-12-03 | 2025-06-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46475628 | T2 EI TIGER CRK-ELCTRA 10/78 TOUCH | ICQ
LC | 129014863 | 012/049 | T2 EI MORRO BAY-SLR SS #2 12/49 RPL INSS | PISMOBCH | ETL.5310.INSL | 2024-06-03 | 2024-06-03 | 2025-04-28 | On-Time |  | 2025-06-03 | 2025-06-03 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35577375 | T0 EI MORRO BAY-SOLAR SS#2 42/180 RPLC I | 93K
LC | 129015094 | T036 | T2 EI MIDWAY-SANTA MARIA T36 INS CTL GRD | PISMOBCH | ETL.9240.TOWR | 2024-06-03 | 2024-06-03 | 2025-02-21 | On-Time |  | 2025-06-03 | 2025-06-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Animal Guard-Steel | Install | 46391113 | T2 EI MIDWAY-SANTA MARIA T36 INS CTL GRD | ICS
LC | 129016055 | 006/073 | T2 EI HAT CREEK #1-PIT #1 06/073 RPL PL | TABLEMTN | ETL.7020.POLE.WOOD | 2024-06-03 | 2024-06-03 | 2025-05-06 | On-Time |  | 2025-06-03 | 2025-06-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574671 | T2 EI HAT CREEK #1-PIT #1 06/073 RPL PL | 70Y
LC | 129016080 | 059/430 | T2 EI BRIDGVIL-COTONWOD 59/430 BNT STEEL | TABLEMTN | ETL.1110.TOWR | 2024-06-03 | 2024-06-03 | 2025-04-28 | On-Time |  | 2025-06-03 | 2025-06-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46353974 | T2 EI BRIDGVIL-COTONWOD 59/430 BNT STEEL | ICQ
LC | 129016431 | 001/015 | T2 EI COLGATE-SMRTVLLE #2 1/15 RPR GYWW | SACTO | ETL.6520.POLE.WDPS | 2024-06-04 | 2024-06-03 | 2025-02-20 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337421 | T2 EI COLGATE-SMRTVLLE #2 1/15 RPR GYWW | ICW
LC | 129021121 | 009/041 | T2 DI EGL RCK-FLTN-SLVRD 9/41 RPR INSS | LAKEVLLE | ETL.4392.INSL.CERA | 2024-06-04 | 2024-06-03 | 2025-04-04 | On-Time |  | 2025-06-03 | 2025-06-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46403768 | T2 DI EGL RCK-FLTN-SLVRD 9/41 RPR INSS | ICS
LC | 129021758 | 012/012 | T2 BRIDGEVLLE-GARBERVILLE 12/12 RPR GYWW | EUREKA | ETL.6220.POLE.WOOD | 2024-06-04 | 2024-06-03 | 2025-05-05 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346036 | T2 DI BRDGVLL-GRBRVILLE 12/012 RPR GYWW | ICW
LC | 129021911 | 094/009B | T2 DI HUMBOLDT-TRINITY 94/9B RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-04 | 2024-06-03 | 2025-05-16 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346064 | T2 DI HUMBOLDT-TRINITY 94/9B RPR GYWW | ICW
LC | 129021986 | 094/009C | T2 DI HUMBOLDT-TRINITY 94/9C RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-04 | 2024-06-03 | 2025-05-16 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346065 | T2 DI HUMBOLDT-TRINITY 94/9C RPR GYWW | ICW
LC | 129022030 | 004/049 | T2 DI HLSDL JCT-HF MN BY 4/49R RPR HRDW | METCALF | ETL.7060.POLE.WDPS | 2024-06-04 | 2024-06-03 | 2025-02-27 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46286714 | T2 DI HLSDL JCT-HF MN BY 4/49R RPR HRDW | ICW
LC | 129022110 | 091/005 | T2 DI HMBLDT TRNTY 91/005 RPR CNDW | EUREKA | ETL.1820.INSL.NCER | 2024-06-04 | 2024-06-03 | 2025-04-21 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46346062 | T2 DI HMBLDT TRNTY 91/005 RPR CNDW | ICW
LC | 129022185 | 031/009 | T2 DI GRBRVL-LYTNVL 31/9 COMPLETE | WILLITS | ETL.8365.INSL.NCER | 2024-06-04 | 2024-06-03 | 2024-08-09 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46264605 | T2 DI GRBRVL-LYTNVL 31/9 RPR JUMW | ICW
LC | 129022207 | 012/012-GUY | T2 BRDGVLLE-GARBRVLLE 12/12-GUY RPR GYWW | EUREKA | ETL.6220.POLE.WOOD | 2024-06-04 | 2024-06-03 | 2025-05-05 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346037 | T2 DI BRDGVLL-GRBRVLL 12/12-GUY RPR GYWW | ICW
LC | 129022278 | 110/000B | T2 DI HMBLDT BRDGEVL 110/000B RMV VEG | EUREKA | ETL.1810.POLE.NWOD | 2024-06-04 | 2024-06-03 | 2024-10-17 | On-Time |  | 2024-12-03 | 2025-06-03 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Vegetation | Remove
LC | 129022316 | 071/358B | T2 DI MALIN RND MTN #2 71/358B RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-06-04 | 2024-06-03 | 2024-08-27 | On-Time |  | 2024-12-03 | 2025-06-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46262901 | T2 DI MALIN RND MTN #2 71/358B RPR OPGW | ICS
LC | 129022360 | 092/002A | T2 DI HUMBOLDT-TRIN 92/2A RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-04 | 2024-06-03 | 2024-07-09 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262170 | T2 DI HUMBOLDT-TRIN 92/2A RPR GYWW | ICW
LC | 129026433 | 097/000B | T2 DI HUMBOLDT-TRIN 97/0B RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-05 | 2024-06-03 | 2024-07-08 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262180 | T2 DI HUMBOLDT-TRIN 97/0B RPR GYWW | ICW
LC | 129026535 | 097/000A | T2 DI HUMBOLDT-TRIN 97/0A RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-05 | 2024-06-03 | 2024-07-08 | On-Time |  | 2024-09-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262177 | T2 DI HUMBOLDT-TRIN 97/0A RPR GYWW | ICW
LC | 129026605 | 097/000C | T2 DI HUMBOLDT-TRIN 97/0C RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-05 | 2024-06-03 | 2024-07-08 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262178 | T2 DI HUMBOLDT-TRIN 97/0C RPR GYWW | ICW
LC | 129026655 | 096/004A | T2 DI HUMBOLDT-TRIN 96/4A RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-05 | 2024-06-03 | 2024-07-08 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262174 | T2 DI HUMBOLDT-TRIN 96/4A RPR GYWW | ICW
LC | 129026659 | 092/000 | T2 DI HUMBOLDT-TRIN 92/0B RPR INSW | EUREKA | ETL.1820.INSL.NCER | 2024-06-05 | 2024-06-03 | 2025-04-23 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46306014 | T2 DI HUMBOLDT-TRIN 92/0B RPR INSW | ICW
LC | 129026675 | 092/002B | T2 HMBLDT-TRNTY 92/2B RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-06-05 | 2024-06-03 | 2024-06-03 | Past Due |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW ACCM OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262171 | T2 DI HMBLDT-TRNTY 92/2B RPR JMPW | ICW
LC | 129026676 | 092/002C | T2 DI HMBLDT-TRNTY 92/2C RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-05 | 2024-06-03 | 2024-07-09 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262172 | T2 DI HMBLDT-TRNTY 92/2C RPR GYWW | ICW
LC | 129026697 | 096/004B | T2 DI HUMBOLDT-TRIN 96/4B RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-05 | 2024-06-03 | 2024-07-08 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262175 | T2 DI HUMBOLDT-TRIN 96/4B RPR GYWW | ICW
LC | 129026757 | 096/004C | T2 DI HUMBOLDT-TRIN 96/4C RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-05 | 2024-06-03 | 2024-07-08 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262176 | T2 DI HUMBOLDT-TRIN 96/4C RPR GYWW | ICW
LC | 129026766 | 091/004B | T2 DI HMBLDT-TRINITY 091/004B RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-05 | 2024-06-03 | 2025-04-21 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346061 | T2 DI HMBLDT-TRINITY 091/004B RPR GYWW | ICW
LC | 129026770 | 091/004A | T2 DI HMBLDT-TRINITY 091/004A RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-05 | 2024-06-03 | 2025-04-21 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346060 | T2 DI HMBLDT-TRINITY 091/004A RPR GYWW | ICW
LC | 129026843 | 029/004 | T2 DI GRBRVLL-LYTNVLL 29/4 RPR JUMW | WILLITS | ETL.8365.INSL.NCER | 2024-06-05 | 2024-06-03 | 2024-08-15 | On-Time |  | 2024-09-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46264536 | T2 DI GRBRVLL-LYTNVLL 29/4 RPR JUMW | ICW
LC | 129026851 | 092/000A | T2 DI HUMBOLDT-TRIN 92/0A RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-06-05 | 2024-06-03 | 2024-11-10 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46262169 | T2 DI HUMBOLDT-TRIN 92/0A RPR GYWW | ICW
LC | 129026931 | 052/000 | T2 DI HMBLDT-TRNTY 52/0 RPR INSW | EUREKA | ETL.1820.INSL.CERA | 2024-06-05 | 2024-06-03 | 2024-09-03 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46262162 | T2 DI HMBLDT-TRNTY 52/0 RPR INSW | ICW
LC | 129026939 | 052/000 | T2 DI HMBLDT-TRNTY 52/0 RPR JUMW | EUREKA | ETL.1820.INSL.CERA | 2024-06-05 | 2024-06-03 | 2025-04-07 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46346038 | T2 DI HMBLDT-TRNTY 52/0 RPR JUMW | ICW
LC | 129027060 | 007/098 | T2 DI KSWCK-TRNTY 7/98 RMV VEG | TABLEMTN | ETL.7270.POLE.STPS | 2024-06-05 | 2024-06-03 | 2024-04-18 | On-Time |  | 2025-06-03 | 2025-06-03 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129031681 | 005/022 | T2 DI PITTSBURG-SAN RAMON 5/22 BNT STEEL | CONCORD | ETL.5490.TOWR | 2024-06-06 | 2024-06-03 | 2025-02-10 | On-Time |  | 2025-06-03 | 2025-06-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46289136 | T2 DI PITTSBURG-SAN RAMON 5/22 BNT STEEL | ICQ
LC | 129032162 | 065/002 | T2 DI HUMBOLDT-TRINITY 65/2 RPR JUMW | EUREKA | ETL.1820.INSL.CERA | 2024-06-06 | 2024-06-03 | 2025-04-11 | On-Time |  | 2024-09-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46262163 | T2 DI HUMBOLDT-TRINITY 65/2 RPR JUMW | ICW
LC | 129032205 | 065/002 | T2 DI HUMBOLDT-TRINITY 65/2R RPL ANCW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-06 | 2024-06-03 | 2025-04-09 | On-Time |  | 2025-06-03 | 2025-06-03 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574772 | T2 WV COTTONWD-HUMBOLDT 65/002 RPL ANCW | 93E
LC | 129193259 | 091/006 | T2 DI HUMBOLDT-TRINITY 91/006 RPR INSW | EUREKA | ETL.1820.INSL.NCER | 2024-07-09 | 2024-06-03 | 2025-04-21 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46346063 | T2 DI HUMBOLDT-TRINITY 91/006 RPR INSW | ICW
LC | 129193275 | 004/046C | T2 DI HLSDL JCT-HLF MN BY 4/46C RPR GYWW | METCALF | ETL.7060.POLE.WOOD | 2024-07-09 | 2024-06-03 | 2025-02-18 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286762 | T2 DI HLSDL JCT-HLF MN BY 4/46C RPR GYWW | ICW
LC | 129193279 | 004/046B | T2 DI HLSDL JCT-HLF MN BY 4/46B RPR GYWW | METCALF | ETL.7060.POLE.WOOD | 2024-07-09 | 2024-06-03 | 2025-02-18 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286764 | T2 DI HLSDL JCT-HLF MN BY 4/46B RPR GYWW | ICW
LC | 129193816 | 073/373 | T2 DI MALIN-ROUND MTN#2 73/373 RPR OPGW | TABLEMTN | ETL.6020.TOWR | 2024-07-09 | 2024-06-03 | 2024-08-28 | On-Time |  | 2024-09-03 | 2025-06-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46282436 | T2 DI MALIN-ROUND MTN#2 73/373 RPR OPGW | ICS
LC | 129193850 | 073/373 | T2 DI MALIN-ROUND MTN#2 73/373 RPL DMPS | TABLEMTN | ETL.6020.INSL.NCER | 2024-07-09 | 2024-06-03 | 2025-02-06 | On-Time |  | 2025-06-03 | 2025-06-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Damper-Steel | Replace | 46300817 | T2 DI MALIN-ROUND MTN#2 73/373 RPL DMPS | ICS
LC | 129213512 | 008/044 | T2 DI VACA-LAKEVILLE #1 08/044 RPL INSS | SACTO | ETL.5840.INSL.CERA | 2024-07-12 | 2024-06-03 | 2025-03-29 | On-Time |  | 2025-06-03 | 2025-06-03 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35608974 | T2 DI VACA-LAKEVILLE #1 08/044 RPL INSS. | 93K
LC | 129213513 | 008/044 | T2 DI VACA LAKEVILLE#1 08/044 RPL HNGR | SACTO | ETL.5840.INSL.CERA | 2024-07-12 | 2024-06-03 | 2025-03-29 | On-Time |  | 2025-06-03 | 2025-06-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46289514 | T2 DI VACA LAKEVILLE#1 08/044 RPL HNGR | ICQ
LC | 129213568 | 096/005A | T2 DI HUMBOLDT-TRINITY 96/5A RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-07-12 | 2024-06-03 | 2025-04-09 | On-Time |  | 2024-09-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46338674 | T2 DI HUMBOLDT-TRINITY 96/5A RPR JUMW | ICW
LC | 129213608 | 096/005C | T2 DI HUMBOLDT-TRINITY 96/5C RPR INSW | EUREKA | ETL.1820.INSL.NCER | 2024-07-12 | 2024-06-03 | 2025-04-09 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46346067 | T2 DI HUMBOLDT-TRINITY 96/5C RPR INSW | ICW
LC | 129213664 | 008/044 | T2 DI VACA LAKEVILLE#1 08/044 RPR SHLS | SACTO | ETL.5840.TOWR | 2024-07-12 | 2024-06-03 | 2025-03-30 | On-Time |  | 2025-06-03 | 2025-06-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46403767 | T2 DI VACA LAKEVILLE#1 08/044 RPR SHLS | ICS
LC | 129213669 | 008/044 | T2 DI VACA LAKEVILLE#1 08/044 BNT STEEL | SACTO | ETL.5840.TOWR | 2024-07-12 | 2024-06-03 | 2025-01-14 | On-Time |  | 2025-06-03 | 2025-06-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46289553 | T2 DI VACA LAKEVILLE#1 08/044 BNT STEEL | ICQ
LC | 129213678 | 077/000 | T2 DI HUMBOLDT-TRINITY 77/000C RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-07-12 | 2024-06-03 | 2025-04-16 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346039 | T2 DI HUMBOLDT-TRINITY 77/000C RPR GYWW | ICW
LC | 129213791 | 001/033 | T2 DI COLGATE-GRASS VALLEY 1/33 RPL INSW | SACTO | ETL.6490.INSL.CERA | 2024-07-12 | 2024-06-03 | 2025-02-28 | On-Time |  | 2025-06-03 | 2025-06-03 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572548 | T2 DI COLGATE-GRASS VALLEY 1/33 RPL INSW | 93I
LC | 129213863 | 005/024B | T2 DI PITTSBURG-SAN RAMON 5/24B RPR GYWT | CONCORD | ETL.5490.POLE.NWOD | 2024-07-12 | 2024-06-03 | 2025-02-03 | On-Time |  | 2025-06-03 | 2025-06-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46289137 | T2 DI PITTSBURG-SAN RAMON 5/24B RPR GYWT | ICQ
LC | 129213866 | 005/024B | T2 DI PITTSBURG-SAN RAMON 5/24B COTTER | CONCORD | ETL.5490.INSL.NCER | 2024-07-12 | 2024-06-03 | 2025-05-30 | On-Time |  | 2025-06-03 | 2025-06-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46289138 | T2 DI PITTSBURG-SAN RAMON 5/24B COTTER | ICS
LC | 129214347 | 001/024 | T2 DI COLGATE-GRASS VALLY 1/24 REFRAME | SACTO | ETL.6490.POLE.WOOD | 2024-07-12 | 2024-06-03 | 2025-02-28 | On-Time |  | 2025-06-03 | 2025-06-03 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35619383 | T2 DI COLGATE-GRASS VALLY 1/24 REFRAME | 93E
LC | 129215005 | 037/246C | T2 DI TRINITY-COTTNWD 37/246C RPR GYWW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-07-12 | 2024-06-03 | 2025-02-24 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46471153 | T2 DI TRINITY-COTTNWD 37/246C RPR GYWW | ICW
LC | 129215031 | 037/246A | T2 DI TRINTY-COTTNWD 37/246A RPR INSW | TABLEMTN | ETL.4040.INSL.NCER | 2024-07-12 | 2024-06-03 | 2025-02-24 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46471152 | T2 DI TRINTY-COTTNWD 37/246A RPR INSW | ICW
LC | 129215647 | 012/250 | T2 DI COLGATE-PALERMO 012/250 TOUCH | SACTO | ETL.6500.POLE.NWOD | 2024-07-12 | 2024-06-03 | 2025-02-28 | On-Time |  | 2024-12-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46463505 | T2 DI COLGATE-PALERMO 012/250 RPR STRW | ICW
LC | 129224351 | 001/027 | T2 DI COLGATE GRAS VALLEY 1/27 REFRAME | SACTO | ETL.6490.POLE.WOOD | 2024-07-15 | 2024-06-03 | 2025-05-28 | On-Time |  | 2025-06-03 | 2025-06-03 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35611788 | T2 DI COLGATE GRAS VALLEY 1/27 REFRAME | 93E
LC | 129225617 | 000/014 | T2 DI CLGT-GRSS VLLY 0/14 COMPLETE | SACTO | ETL.6490.INSL.CERA | 2024-07-16 | 2024-06-03 | 2025-02-28 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46400345 | T2 DI CLGT-GRSS VLLY 0/14 RPR INSW | ICW
LC | 129230066 | 000/003 | T2 DI PITTSBURG-TESLA#2 00/03 RMV NEST | CONCORD | ETL.5520.POLE.NWOD | 2024-07-16 | 2024-06-03 | 2025-01-15 | On-Time |  | 2025-06-03 | 2025-06-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46289134 | T2 DI PITTSBURG-TESLA#2 00/03 RMV NEST | ICS
LC | 129230107 | 003/031 | T2 DI MORAGA-OAKLAND #3 3/31 RPR STRT | CONCORD | ETL.2740.TOWR | 2024-07-16 | 2024-06-03 | 2025-01-18 | On-Time |  | 2025-06-03 | 2025-06-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Structure-Tower | Repair | 46289135 | T2 DI MORAGA-OAKLAND #3 3/31 RPR STRT | ICQ
LC | 129230455 | 093/002 | T2 HUMBOLDT-TRINITY 93/2L RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-07-16 | 2024-06-03 | 2024-06-03 | Past Due |  | 2025-06-03 | 2025-06-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574494 | T2 DI HMBLDT-TRINITY 093/002 RPL STRW | 70Y
LC | 129230456 | 093/002 | T2 HUMBOLDT-TRINITY 93/2R RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-07-16 | 2024-06-03 | 2024-06-03 | Past Due |  | 2025-06-03 | 2025-06-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574494 | T2 DI HMBLDT-TRINITY 093/002 RPL STRW | 70Y
LC | 129236180 | 094/011 | T2 DI HUMBOLDT-TRINITY 94/11 RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-07-17 | 2024-06-03 | 2025-05-16 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346066 | T2 DI HUMBOLDT-TRINITY 94/11 RPR GYWW | ICW
LC | 129295265 | 013/001C | T2 BRIDGEVILLE-GARBERVILLE 13/1C TOUCH | EUREKA | ETL.6220.POLE.NWOD | 2024-07-26 | 2024-06-03 | 2024-06-03 | Past Due |  | 2024-12-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46505015 | T2 DI BRIDGEVIL-GARBRVIL-13/01C TOUCH | ICW
LC | 129304964 | 013/001A | T2 BRIDGEVILLE-GARBERVILLE 13/1A TOUCH | EUREKA | ETL.6220.POLE.NWOD | 2024-07-29 | 2024-06-03 | 2024-06-03 | Past Due |  | 2024-12-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46505014 | T2 DI BRDGVLL-GARBERVILLE 13/1A TOUCH | ICW
LC | 129306756 | 092/004 | T2 HUMBOLDT-TRINITY 92/4R RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-07-29 | 2024-06-03 | 2024-06-03 | Past Due |  | 2025-06-03 | 2025-06-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35586942 | T2 DI HUMBOLDT-TRINITY 92/4R RPL POLE | 70Y
LC | 129306757 | 092/004 | T2 HUMBOLDT-TRINITY 92/4L RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-07-29 | 2024-06-03 | 2024-06-03 | Past Due |  | 2025-06-03 | 2025-06-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35586942 | T2 DI HUMBOLDT-TRINITY 92/4R RPL POLE | 70Y
LC | 129311681 | 009/038 | T2 DI EAGLE RCK-FLTN-SLVRD 9/38 RPR STRT | LAKEVLLE | ETL.4392.TOWR | 2024-07-30 | 2024-06-03 | 2025-01-15 | On-Time |  | 2025-06-03 | 2025-06-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46345551 | T2 DI EAGLE RCK-FLTN-SLVRD 9/38 RPR STRT | ICQ
LC | 129316655 | 001/029 | T2 DI CLGTE GRSS VLLY 1/29 COMPLETE | SACTO | ETL.6490.POLE.WOOD | 2024-07-31 | 2024-06-03 | 2025-02-28 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401365 | T2 DI CLGTE GRSS VLLY 1/29 RPR STRW | ICW
LC | 129316658 | 098/001A | T2 DI HMBLDT TRNTY 98/001A RPR ANCW | EUREKA | ETL.1820.POLE.NWOD | 2024-07-31 | 2024-06-03 | 2025-03-08 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46403071 | T2 DI HMBLDT TRNTY 98/001A RPR ANCW | ICW
LC | 129316712 | 098/001B | T2 DI HMBLDT TRNTY 98/001B RPR ANCW | EUREKA | ETL.1820.POLE.NWOD | 2024-07-31 | 2024-06-03 | 2025-03-08 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46403072 | T2 DI HMBLDT TRNTY 98/001B RPR ANCW | ICW
LC | 129316715 | 098/001C | T2 DI HMBLDT TRNTY 98/001C RPR ANCW | EUREKA | ETL.1820.POLE.NWOD | 2024-07-31 | 2024-06-03 | 2025-03-08 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46403073 | T2 DI HMBLDT TRNTY 98/001C RPR ANCW | ICW
LC | 129316828 | 026/212 | T2 DI CRBRY SS-RND MTN 26/212 RPR STRT | TABLEMTN | ETL.5410.TOWR | 2024-07-31 | 2024-06-03 | 2025-04-14 | On-Time |  | 2025-06-03 | 2025-06-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46404339 | T2 DI CRBRY SS-RND MTN 26/212 RPR STRT | ICQ
LC | 129316857 | 095/005 | T2 DI HUMBOLDT-TRINITY 95/5R SPLIT BOLT | EUREKA | ETL.1820.POLE.WDPS | 2024-07-31 | 2024-06-03 | 2025-04-21 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Missing | Hardware-Wood | Install | 46403068 | T2 DI HUMBOLDT-TRINITY 95/5R SPLIT BOLT | ICW
LC | 129316858 | 095/005 | T2 DI HUMBOLDT-TRINITY 95/5L SPLIT BOLT | EUREKA | ETL.1820.POLE.WDPS | 2024-07-31 | 2024-06-03 | 2025-04-21 | On-Time |  | 2025-06-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Missing | Hardware-Wood | Install | 46403069 | T2 DI HUMBOLDT-TRINITY 95/5L SPLIT BOLT | ICW
LC | 129316878 | 003/026 | T2 DI MORGA-OAKLAND #3 003/026 TOUCH | CONCORD | ETL.2740.TOWR | 2024-07-31 | 2024-06-03 | 2025-05-08 | On-Time |  | 2024-12-03 | 2025-06-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485716 | T2 DI MORGA-OAKLAND #3 003/026 TOUCH | ICQ
LC | 129353856 | 000/010 | T2 DI COLGATE GRASS VLLY 0/10 RPR GYWW | SACTO | ETL.6490.POLE.NWOD | 2024-08-08 | 2024-06-03 | 2024-10-09 | On-Time |  | 2024-12-03 | 2025-06-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46329129 | T2 DI COLGATE GRASS VLLY 0/10 RPR GYWW | ICW
LC | 129376389 | 005/052 | T2 DI HLSDL JCT-HLF MN BY 5/52C RPL POLE | METCALF | ETL.7060.POLE.WDPS | 2024-08-12 | 2024-06-03 | 2025-03-11 | On-Time |  | 2025-06-03 | 2025-06-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35587531 | T2 DI HLSDL JCT-HLF MN BY 5/52L RPL POLE | 70Y
LC | 129376430 | 005/052 | T2 DI HLSDL JCT-HLF MN BY 5/52R RPL POLE | METCALF | ETL.7060.POLE.WDPS | 2024-08-12 | 2024-06-03 | 2025-03-11 | On-Time |  | 2025-06-03 | 2025-06-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35587531 | T2 DI HLSDL JCT-HLF MN BY 5/52L RPL POLE | 70Y
LC | 129376433 | 005/052 | T2 DI HLSDL JCT-HLF MN BY 5/52L RPL POLE | METCALF | ETL.7060.POLE.WDPS | 2024-08-12 | 2024-06-03 | 2025-03-11 | On-Time |  | 2025-06-03 | 2025-06-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35587531 | T2 DI HLSDL JCT-HLF MN BY 5/52L RPL POLE | 70Y
LC | 129376471 | 005/025A | T2 DI PITTSBURG-EASTSHORE 5/25A RPL HRDS | CONCORD | ETL.5462.POLE.NWOD | 2024-08-12 | 2024-06-03 | 2025-04-06 | On-Time |  | 2025-06-03 | 2025-06-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Steel | Replace | 46345723 | T2 DI PITTSBURG-EASTSHORE 5/25A RPL HRDS | ICS
LC | 129376472 | 005/025A | T2 PITTSBURG-EASTSHORE 5/25A COMPLETE | CONCORD | ETL.5462.POLE.NWOD | 2024-08-12 | 2024-06-03 | 2025-04-06 | On-Time |  | 2025-06-03 | 2025-06-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Steel | Regrade | 46345724 | T2 DI PITTSBURG-EASTSHORE 5/25A REGRADE | ICS
LC | 123849396 | 007/138 | T2NT DI TEJON-LEBEC 007/138 RPR STRW | MIDWAY | ETL.9250.POLE.NWOD | 2022-06-15 | 2022-06-04 | 2023-10-22 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Repair | 45599296 | T2 DI TEJON-LEBEC 007/138 RPR STRW | ICW
LC | 123919352 | 032/265 | T2NT DI BRDGEVLL-CTTNWD 32/265 RPR ADSS | TABLEMTN | ETL.1110.POLE.STPS | 2022-06-24 | 2022-06-04 | 2024-06-04 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 46093199 | T2NT DI BRDGEVLL-CTTNWD 32/265 RPR ADSS | ICW
LC | 127538473 | 004/085 | T2 DELTA-MTN GATE JCT 004/085 RPL INSS | TABLEMTN | ETL.6750.INSL.NCER | 2023-12-04 | 2023-12-04 | 2024-12-11 | On-Time |  | 2025-06-04 | 2025-06-04 | 508 | TR2 | YES | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB XMPT TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 31618698 | T2 EI DLT-MTN GT JCT-MTN 4/85 RPL INSW | 93I
LC | 129016397 | 018/009 | T2 CLEAR LAKE-KONOCTI 018/009 RPL INSW | WILLITS | ETL.6852.INSL.CERA | 2024-06-04 | 2024-06-04 | 2024-06-04 | Past Due |  | 2025-06-04 | 2025-06-04 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572506 | T2 CLEAR LAKE-KONOCTI 018/009 RPL INSW | 93I
LC | 129016533 | 066/276 | T2 RND MTN-TBLE MTN #2 66/276 TOUCH | TABLEMTN | ETL.6070.TOWR | 2024-06-04 | 2024-06-04 | 2025-03-21 | On-Time |  | 2024-12-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478265 | T2 RND MTN-TBLE MTN #2 66/276 TOUCH | ICQ
LC | 129017161 | 021/166 | T2 DRUM-RIO OSO 021/166 RPL HRDT | SACTO | ETL.1420.TOWR | 2024-06-04 | 2024-06-04 | 2024-06-04 | Past Due |  | 2025-06-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46381454 | T2 DRUM-RIO OSO 021/166 RPL HRDT | ICQ
LC | 129017797 | X010/044 | T2 WV DIABLO-MESA X010/044 RPL INSS | PISMOBCH | ETL.4620.INSL | 2024-06-04 | 2024-06-04 | 2025-03-23 | On-Time |  | 2025-06-04 | 2025-06-04 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO | Missing | Insulator-Steel | Install | 35585666 | T2 EI DIABLO-MESA RPL INSS 7 LSTS | 93K
LC | 129017966 | 019/081 | T2 EI MORRO BAY-SLR SS #1 19/81 RPL INSS | PISMOBCH | ETL.5300.INSL | 2024-06-04 | 2024-06-04 | 2025-04-07 | On-Time |  | 2025-06-04 | 2025-06-04 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35583345 | T0 EI MORRO BAY-SOLAR SS#1 REP INS 6 LST | 93K
LC | 129018422 | 058/427 | T2 EI BRIDGEVIL-COTONWD 58/427 RMV VEG | TABLEMTN | ETL.1110.TOWR | 2024-06-04 | 2024-06-04 | 2024-06-04 | On-Time |  | 2025-06-04 | 2025-06-04 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 129019140 | 006/082 | T2 EI HAT CRK #1-PIT #1 6/082 RPR GYWW | TABLEMTN | ETL.7020.POLE.WOOD | 2024-06-04 | 2024-06-04 | 2025-05-06 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46416130 | T2 EI HAT CRK #1-PIT #1 6/082 RPR GYWW | ICW
LC | 129019488 | 011/051 | T2 EI SN LS OBSPO-OCEANO 11/51 RMV VEG | PISMOBCH | ETL.3530.TOWR | 2024-06-04 | 2024-06-04 | 2025-05-16 | On-Time |  | 2025-06-04 | 2025-06-04 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO CLMB FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 129019768 | T035 | T2 EI MIDWAY-SANTA MARIA T35R RPL POLE | PISMOBCH | ETL.9240.POLE.WDPS | 2024-06-04 | 2024-06-04 | 2025-02-25 | On-Time |  | 2025-06-04 | 2025-06-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Replace | 35573538 | T2 EI MIDWAY-SANTA MARIA T35R RPL POLE | 70Y
LC | 129019812 | T032 | T2 EI MIDWAY-SANTA MARIA T032 RPL INSW | PISMOBCH | ETL.9240.INSL.CERA | 2024-06-04 | 2024-06-04 | 2025-02-25 | On-Time |  | 2025-06-04 | 2025-06-04 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35626254 | T2 EI MIDWAY-SANTA MARIA T032 RPL INSW | 93I
LC | 129019820 | T025 | T2 EI MIDWAY-SANTA MARIA T025 RPR POLE | PISMOBCH | ETL.9240.POLE.WOOD | 2024-06-04 | 2024-06-04 | 2025-02-21 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46391115 | T2 EI MIDWAY-SANTA MARIA T025 RPR POLE | ICW
LC | 129019938 | 000/000F | T2 EI HAT CREK #1-PIT #1 00/0F RPL PL | TABLEMTN | ETL.7020.POLE.WOOD | 2024-06-04 | 2024-06-04 | 2025-05-30 | On-Time |  | 2025-06-04 | 2025-06-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574666 | T2 EI HAT CREK #1-PIT #1 00/0F RPL PL | 70Y
LC | 129020245 | 024/007 | T2 WV FULTON-HOPLAND 024/007 RPL STRW | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-06-04 | 2024-06-04 | 2024-06-04 | Past Due |  | 2025-06-04 | 2025-06-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574255 | T2 WV FULTON-HOPLAND 024/007 RPL STRW | 70Y
LC | 129021228 | 041/796 | T2 HAT CRK #1-WSTWD 41/796 RPL POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-04 | 2024-06-04 | 2024-06-04 | Past Due |  | 2025-06-04 | 2025-06-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574771 | T2 EI HAT CRK #1-WSTWD 41/796 RPL PL | 70Y
LC | 129021435 | 009/043 | T2 BRENTWOOD-KELS 09/43 RPL INSS | CONCORD | ETL.4410.INSL | 2024-06-04 | 2024-06-04 | 2024-06-04 | Past Due |  | 2025-06-04 | 2025-06-04 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575008 | T2 EI BRENTWOOD-KELS RPL INSS IN 2 TWRS | 93K
LC | 129021586 | 015/080 | T2 EI RND MTN-TBLE MTN #1 15/80 RPR FOND | TABLEMTN | ETL.6060.TOWR | 2024-06-04 | 2024-06-04 | 2025-04-25 | On-Time |  | 2025-06-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46382017 | T2 EI RND MTN-TBLE MTN #1 15/80 RPR FOND | ICQ
LC | 129021619 | 016/083 | T2 EI RND MTN-TBLE MTN #1 16/83 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2024-06-04 | 2024-06-04 | 2025-02-25 | On-Time |  | 2025-06-04 | 2025-06-04 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129021863 | 059/428 | T2 EI BRIDGEVIL-COTONWD 59/428 RMV VEG | TABLEMTN | ETL.1110.TOWR | 2024-06-04 | 2024-06-04 | 2024-06-04 | On-Time |  | 2025-06-04 | 2025-06-04 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129021885 | 013/007 | T2 EI MENDOCINO-WILLITS 13/007 RMV VEG | WILLITS | ETL.7540.POLE.WOOD | 2024-06-04 | 2024-06-04 | 2025-01-21 | On-Time |  | 2025-06-04 | 2025-06-04 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 129022201 | 000/003C | T2 ROCK CREEK-POE 00/03C COMPLETE | TABLEMTN | ETL.5630.INSL.CERA | 2024-06-04 | 2024-06-04 | 2025-04-26 | On-Time |  | 2025-06-04 | 2025-06-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Steel | Repair | 46383937 | T2 DI ROCK CREEK-POE 00/03C RPR JUMS | ICS
LC | 129022412 | 039/759 | T2 HAT CRK #1-WESTWD 39/759 RPR CRSW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-04 | 2024-06-04 | 2025-05-30 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46416160 | T2 EI HAT CRK #1-WESTWD 39/759 RPR CRSW | ICW
LC | 129022420 | 039/755 | T2 HAT CRK #1-WSTWD 39/755 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-04 | 2024-06-04 | 2025-05-29 | On-Time |  | 2025-06-04 | 2025-06-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574685 | T2 EI HAT CRK #1-WSTWD 39/755 RPL STRW | 70Y
LC | 129022421 | 039/758 | T2 HAT CRK #1-WESTWD 39/758 REFRAME | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-04 | 2024-06-04 | 2025-05-29 | On-Time |  | 2025-06-04 | 2025-06-04 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35574686 | T2 EI HAT CRK #1-WESTWD 39/758 REFRAME | 93E
LC | 129026510 | 088/005 | T2 DI HUMBOLDT-TRINITY 88/5 RPR INSW | EUREKA | ETL.1820.INSL.CERA | 2024-06-05 | 2024-06-04 | 2025-04-21 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46346068 | T2 DI HUMBOLDT-TRINITY 88/5 RPR INSW | ICW
LC | 129026555 | 014/149 | T2 DI ROUND MT-COTT#2 14/149 RPR OPGW | TABLEMTN | ETL.5640.TOWR | 2024-06-05 | 2024-06-04 | 2024-08-25 | On-Time |  | 2024-09-04 | 2025-06-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46264439 | T2 DI ROUND MT-COTT#2 14/149 RPR OPGW | ICS
LC | 129026639 | :010/072 | T2 ROCK CREEK-POE :10/72 RMV VEG | TABLEMTN | ETL.5630.TOWR | 2024-06-05 | 2024-06-04 | 2024-06-04 | Past Due |  | 2025-06-04 | 2025-06-04 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129026703 | :006/042 | T2 DI ROCK CREEK-POE :006/042 RPL INSS | TABLEMTN | ETL.5630.INSL.CERA | 2024-06-05 | 2024-06-04 | 2025-04-26 | On-Time |  | 2025-06-04 | 2025-06-04 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35572041 | T2 ROCK CREEK-POE RPL INSS 5 TWRS | 93K
LC | 129030225 | 139 | T2 DI HUMBOLDT-TRINITY 89/3 COTTER | EUREKA | ETL.1820.SWIT | 2024-06-06 | 2024-06-04 | 2025-04-14 | On-Time |  | 2025-06-04 | 2025-06-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46346071 | T2 DI HUMBOLDT-TRINITY 89/3 COTTER | ICS
LC | 129030227 | 089/003 | T2 DI HUMBOLDT-TRINITY 89/3 RPL HRDT | EUREKA | ETL.1820.TOWR | 2024-06-06 | 2024-06-04 | 2025-04-23 | On-Time |  | 2025-06-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289502 | T2 DI HUMBOLDT-TRINITY 89/3 RPL HRDT | ICQ
LC | 129031986 | 006/027 | T2 DI PTTSBRG-SN MTEO 6/27 RMV NEST | CONCORD | ETL.5463.TOWR | 2024-06-06 | 2024-06-04 | 2025-01-15 | On-Time |  | 2025-06-04 | 2025-06-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46289380 | T2 DI PTTSBRG-SN MTEO 6/27 RMV NEST | ICS
LC | 129032263 | 019/012 | T2 DI MENDOCINO-WFB 19/12 RPL INSW | WILLITS | ETL.7550.INSL.CERA | 2024-06-06 | 2024-06-04 | 2025-04-09 | On-Time |  | 2025-06-04 | 2025-06-04 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCH COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574199 | T2 DI MENDOCINO-WFB 19/12 RPL INSW | 93I
LC | 129032270 | 024/215 | T2 DI RND MTN CGNWD #2 24/215 RPL HRDT | TABLEMTN | ETL.5640.TOWR | 2024-06-06 | 2024-06-04 | 2025-05-22 | On-Time |  | 2025-06-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46310422 | T2 DI RND MTN CGNWD #2 24/215 RPL HRDT | ICQ
LC | 129032277 | 024/215 | T2NT DI RND MTN CGNWD #2 24/215 RPR STRT | TABLEMTN | ETL.5640.TOWR | 2024-06-06 | 2024-06-04 | 2025-05-22 | On-Time |  | 2027-06-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310423 | T2NT DI RND MTN CGNWD #2 24/215 RPR STRT | ICQ
LC | 129072196 | 009/043 | T2 BRENTWOOD-KELS 09/43 RPL HNGR | CONCORD | ETL.4410.INSL | 2024-06-13 | 2024-06-04 | 2024-06-04 | Past Due |  | 2025-06-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46289381 | T2 EI BRENTWOOD-KELS 09/43 RPL HNGR | ICQ
LC | 129158815 | 111/004 | T2 HUMBOLDT-BRIDGEVILLE 111/4 RPR ADSS | EUREKA | ETL.1810.POLE.WDPS | 2024-07-02 | 2024-06-04 | 2024-06-04 | Past Due |  | 2024-09-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46280144 | T2 DI HMBLDT BRDGVIL 111/4 RPR ADSS | ICW
LC | 129213782 | 022/178 | T2 DI CARBRRY SS-RND MTN 22/178 DUP CNCL | TABLEMTN | ETL.5410.TOWR | 2024-07-12 | 2024-06-04 | 2024-11-04 | On-Time |  | 2024-12-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46327348 | T2 DI CARBRRY SS-RND MTN 21/178 RPR STRT | ICQ
LC | 129214595 | 001/026 | T2 DI COLGATE-GRASS VALLEY 1/26 REFRAME | SACTO | ETL.6490.POLE.WOOD | 2024-07-12 | 2024-06-04 | 2025-05-28 | On-Time |  | 2025-06-04 | 2025-06-04 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35611787 | T2 DI COLGATE-GRASS VALLEY 1/26 REFRAME | 93E
LC | 129214880 | 003/007 | T2 DI LWR LK-HMSTK 003/007 RPR INSW | WILLITS | ETL.1481.INSL.NCER | 2024-07-12 | 2024-06-04 | 2025-05-06 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46340402 | T2 DI LWR LK-HMSTK 003/007 RPR INSW | ICW
LC | 129214953 | 098/000 | T2 DI HMBLDT-TRINITY 098/0L RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-07-12 | 2024-06-04 | 2025-03-08 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346069 | T2 DI HMBLDT-TRINITY 098/0L RPR GYWW | ICW
LC | 129215125 | 000/004 | T2 DI COLGATE-GRASS VALLEY 0/4 RPR STRW | SACTO | ETL.6490.POLE.WOOD | 2024-07-12 | 2024-06-04 | 2025-02-28 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46398078 | T2 DI COLGATE-GRASS VALLEY 0/4 RPR STRW | ICW
LC | 129215126 | 000/004 | T2 DI CLGT-GRASS VLLY 0/4 RPR INSW | SACTO | ETL.6490.INSL.NCER | 2024-07-12 | 2024-06-04 | 2025-02-28 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46398079 | T2 DI CLGT-GRASS VLLY 0/4 RPR INSW | ICW
LC | 129215140 | 003/015 | T2 DI HUMBLDT BY-HUMBLDT#1 3/15 RPL HRDW | EUREKA | ETL.1800.TOWR | 2024-07-12 | 2024-06-04 | 2025-03-08 | On-Time |  | 2025-06-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46289239 | T2 DI HUMBLDT BY-HUMBLDT#1 3/15 RPL HRDW | ICQ
LC | 129215332 | 004/020 | T2 DI PITTSBURG-TASSAJARA 4/20 RPR CNDS | CONCORD | ETL.5470.INSL | 2024-07-12 | 2024-06-04 | 2025-05-15 | On-Time |  | 2025-06-04 | 2025-06-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Conductor-Steel | Repair | 46289139 | T2 DI PITTSBURG-TASSAJARA 4/20 RPR CNDS | ICS
LC | 129215560 | 008/149 | T2 DI COLEMAN-RED BLUFF 8/149 RPL STRW | TABLEMTN | ETL.6440.POLE.WOOD | 2024-07-12 | 2024-06-04 | 2025-04-22 | On-Time |  | 2025-06-04 | 2025-06-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572512 | T2 DI COLEMAN-RED BLUFF 8/149 RPL STRW | 70Y
LC | 129224605 | 003/000 | T2 DI PTR VLY-WLTS 03/000 RPR GYWW | WILLITS | ETL.7820.POLE.NWOD | 2024-07-15 | 2024-06-04 | 2025-02-22 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310515 | T2 DI PTR VLY-WLTS 03/000 RPR GYWW | ICW
LC | 129224644 | 021/197 | T2 DI RND MTN CTNWOD #2 21/197 BNT STEEL | TABLEMTN | ETL.5640.TOWR | 2024-07-15 | 2024-06-04 | 2025-05-27 | On-Time |  | 2025-06-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46310421 | T2 DI RND MTN CTNWOD #2 21/197 BNT STEEL | ICQ
LC | 129224740 | 024/197 | T2 CRBRY SS-RND MTN 24/197 COMPLETE | TABLEMTN | ETL.5410.TOWR | 2024-07-15 | 2024-06-04 | 2025-04-04 | On-Time |  | 2025-06-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46354076 | T2 DI CRBRY SS-RND MTN 24/197 RPL HRDT | ICQ
LC | 129230212 | 003/006 | T2 DI POTTER VALLEY-WILLITS 3/6 RPR INSW | WILLITS | ETL.7820.INSL.NCER | 2024-07-16 | 2024-06-04 | 2025-02-22 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310518 | T2 DI POTTER VALLEY-WILLITS 3/6 RPR INSW | ICW
LC | 129230213 | 003/006 | T2 DI POTTER VALLEY-WILLITS 3/6 RPR GYWW | WILLITS | ETL.7820.POLE.WOOD | 2024-07-16 | 2024-06-04 | 2025-02-22 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310519 | T2 DI POTTER VALLEY-WILLITS 3/6 RPR GYWW | ICW
LC | 129230485 | 003/003 | T2 DI POTTER VLLY-WILLITS 3/003 RPR GYWW | WILLITS | ETL.7820.POLE.WOOD | 2024-07-16 | 2024-06-04 | 2025-02-22 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310517 | T2 DI POTTER VLLY-WILLITS 3/003 RPR GYWW | ICW
LC | 129235823 | 006/004 | T2 MENDCNO-WILTS-FT BRG 6/4 RPL STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-07-17 | 2024-06-04 | 2024-06-04 | Past Due |  | 2025-06-04 | 2025-06-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574191 | T2 DI MENDCNO-WILTS-FT BRG 6/4 RPL STRW | 70Y
LC | 129235945 | 109/002C | T2 DI HUMBOLDT-TRINITY 109/2C RPR GYWW | EUREKA | ETL.1820.POLE.NWOD | 2024-07-17 | 2024-06-04 | 2025-04-09 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46346070 | T2 DI HUMBOLDT-TRINITY 109/2C RPR GYWW | ICW
LC | 129236214 | 000/015 | T2 DI HT CRK # 1- WSTWD 0/15 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-07-17 | 2024-06-04 | 2025-05-18 | On-Time |  | 2025-06-04 | 2025-06-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574740 | T2 DI HT CRK # 1- WSTWD 0/15 RPL STRW | 70Y
LC | 129316957 | 016/161 | T2 DI RND MTN-CTTNWD #2 16/161 RPL HRDT | TABLEMTN | ETL.5640.TOWR | 2024-07-31 | 2024-06-04 | 2025-05-22 | On-Time |  | 2025-06-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46404700 | T2 DI RND MTN-CTTNWD #2 16/161 RPL HRDT | ICQ
LC | 129324238 | 022/186 | T2 DI CRBRY SS-RND MTN 22/186 RPR INSS | TABLEMTN | ETL.5410.INSL.NCER | 2024-08-02 | 2024-06-04 | 2025-03-11 | On-Time |  | 2025-06-04 | 2025-06-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46416224 | T2 DI CRBRY SS-RND MTN 22/186 RPR INSS | ICS
LC | 129334339 | 006/030 | T2 PITTSBURG SAN RAMON 6/30 RPR JUMS | CONCORD | ETL.5490.INSL.NCER | 2024-08-05 | 2024-06-04 | 2024-06-04 | Past Due |  | 2024-12-04 | 2025-06-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46516825 | T2 PITTSBURG SAN RAMON 6/30 RPR JUMS | ICS
LC | 129334372 | 006/030 | T2 DI PTSBURG SAN RAMON 6/30 RMV VEG | CONCORD | ETL.5490.TOWR | 2024-08-05 | 2024-06-04 | 2025-04-15 | On-Time |  | 2025-06-04 | 2025-06-04 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129375941 | 000/007 | T2 DI COLGATE-GRASS VALLEY 0/7 RPL PL | SACTO | ETL.6490.POLE.WOOD | 2024-08-12 | 2024-06-04 | 2025-05-27 | On-Time |  | 2025-06-04 | 2025-06-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586837 | T2 DI COLGATE-GRASS VALLEY 0/7 RPL PL | 70Y
LC | 129376221 | 022/179 | T2 DI CRBERRY SS-RND MTN 22/179 RPR JUMS | TABLEMTN | ETL.5410.INSL.NCER | 2024-08-12 | 2024-06-04 | 2025-03-11 | On-Time |  | 2025-06-04 | 2025-06-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46416225 | T2 DI CRBERRY SS-RND MTN 22/179 RPR JUMS | ICS
LC | 129376296 | 025/205 | T2 DI CARBRY SS-RND MTN 25/205 RPR STRT | TABLEMTN | ETL.5410.TOWR | 2024-08-12 | 2024-06-04 | 2025-04-23 | On-Time |  | 2025-06-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46404702 | T2 DI CARBRY SS-RND MTN 25/205 RPR STRT | ICQ
LC | 129376298 | 025/205 | T2 CARBRY SS-RND MTN 25/205 RPR STRT | TABLEMTN | ETL.5410.TOWR | 2024-08-12 | 2024-06-04 | 2024-06-04 | Past Due |  | 2024-12-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478264 | T2 DI CARBRY SS-RND MTN 25/205 TOUCH | ICQ
LC | 129382272 | 112/000 | T2 HMBLDT-BRDGVL 112/0 RPR ADSS | EUREKA | ETL.1810.TOWR | 2024-08-13 | 2024-06-04 | 2024-06-04 | Past Due |  | 2024-09-04 | 2025-06-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Steel | Repair | 46308604 | T2 DI HMBLDT-BRDGVL 112/0 RPR ADSS | ICS
LC | 129382309 | 008/167 | T2 DI HT CRK #1-WSTWD 8/167 INS HRDW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-08-13 | 2024-06-04 | 2025-05-13 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Missing | Hardware-Wood | Install | 46416181 | T2 DI HT CRK #1-WSTWD 8/167 INS HRDW | ICW
LC | 129382561 | 009/036 | T2 DI PITTSBURG SAN RAMON 9/36 RPR STRT | CONCORD | ETL.5490.TOWR | 2024-08-13 | 2024-06-04 | 2025-04-28 | On-Time |  | 2025-06-04 | 2025-06-04 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46339719 | T2 DI PITTSBURG SAN RAMON 9/36 RPR STRT | ICQ
LC | 129382652 | 008/163 | T2 DI COTTONWD-RED BLUFF 8/163 RPR CRSW | TABLEMTN | ETL.6660.POLE.WOOD | 2024-08-13 | 2024-06-04 | 2025-04-23 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46337218 | T2 DI COTTONWD-RED BLUFF 8/163 RPR CRSW | ICW
LC | 129393567 | 000/003A | T2 DI COLGATE-GRASS VALLEY 0/3A COMPLETE | SACTO | ETL.6490.INSL.NCER | 2024-08-15 | 2024-06-04 | 2025-02-28 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46401373 | T2 DI COLGATE-GRASS VALLEY 0/3A RPR IBWW | ICW
LC | 129393568 | 000/003A | T2 DI COLGATE-GRASS VALLEY 0/3A RMV VEG | SACTO | ETL.6490.POLE.WOOD | 2024-08-15 | 2024-06-04 | 2024-06-04 | Past Due |  | 2025-06-04 | 2025-06-04 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129393569 | 000/003A | T2 DI CLGT-GRS VLY 0/3A COMPLETE | SACTO | ETL.6490.POLE.WOOD | 2024-08-15 | 2024-06-04 | 2025-02-28 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46401374 | T2 DI CLGT-GRS VLY 0/3A RPR ANCW | ICW
LC | 129393662 | 000/003A | T2 DI COLGATE-GRASS VALLEY 0/3A COMPLETE | SACTO | ETL.6490.POLE.WOOD | 2024-08-15 | 2024-06-04 | 2025-02-28 | On-Time |  | 2025-06-04 | 2025-06-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46401375 | T2 DI COLGATE-GRASS VALLEY 0/3A RPR GYWW | ICW
LC | 129393943 | 098/003 | T2 DI HUMBOLDT-TRINITY 98/3L RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-08-15 | 2024-06-04 | 2025-04-18 | On-Time |  | 2025-06-04 | 2025-06-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35586944 | T2 DI HUMBOLDT-TRINITY 98/3L RPL STRW | 70Y
LC | 129393944 | 098/003 | T2 DI HUMBOLDT-TRINITY 98/3R RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-08-15 | 2024-06-04 | 2025-04-18 | On-Time |  | 2025-06-04 | 2025-06-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586944 | T2 DI HUMBOLDT-TRINITY 98/3L RPL STRW | 70Y
LC | 129408884 | 037/001 | T2 DI FULTN-HPLND-WD PL 37/1 RPL STRW | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-08-19 | 2024-06-04 | 2024-06-04 | Past Due |  | 2025-06-04 | 2025-06-04 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586910 | T2 DI FULTN-HPLND-WD PL 37/1 RPL STRW | 70Y
LC | 123764751 | 013/002 | T2NT EI COALNG #1-SN MGL 13/2 BNT STL | FRESNO | ETL.8580.TOWR | 2022-06-05 | 2022-06-05 | 2023-06-13 | On-Time |  | 2025-06-05 | 2025-06-05 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAA | No Good/Out of Stdrd | Structure-Tower | Repair | 45639651 | T0 EI COALNG #1-SN MGL 13/2 BNT STEEL | ICQ
LC | 129022977 | 010/124 | T2 DRUM-SUMMIT #1 10/124 COTTER | SACTO | ETL.1440.INSL.NCER | 2024-06-05 | 2024-06-05 | 2024-07-14 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46273107 | T2 DRUM-SUMMIT #1 10/124 COTTER | ICW
LC | 129023236 | 018/144 | T2 EI CRBRRY SS-RND MTN 18/144 INS DAMS | TABLEMTN | ETL.5410.INSL.NCER | 2024-06-05 | 2024-06-05 | 2025-03-11 | On-Time |  | 2025-06-05 | 2025-06-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Steel | Install | 46416220 | T2 EI CRBRRY SS-RND MTN 18/144 INS DAMS | ICS
LC | 129024081 | 008/139 | T2 WV COLEMAN-RED BLUFF 8/139 INS DMPW | TABLEMTN | ETL.6440.INSL.NCER | 2024-06-05 | 2024-06-05 | 2025-04-22 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46389180 | T2 WV COLEMAN-RED BLUFF 8/139 INS DMPW | ICW
LC | 129024946 | 006/004 | T2 WV EHMBLDT-MPLE CRK 06/04 INS DMPW | EUREKA | ETL.7130.INSL.NCER | 2024-06-05 | 2024-06-05 | 2025-04-02 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46346073 | T2 WV EHMBLDT-MPLE CRK 06/04 INS DMPW | ICW
LC | 129025155 | 039/764 | T2 HAT CREEK #1-WESTWD 39/764 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-05 | 2024-06-05 | 2025-05-29 | On-Time |  | 2025-06-05 | 2025-06-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574687 | T2 EI HAT CREEK #1-WESTWD 39/764 RPL PL | 70Y
LC | 129025156 | 040/766 | T2 EI HAT CREEK #1-WESTWD 40/766 RMV VEG | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-05 | 2024-06-05 | 2024-09-24 | On-Time |  | 2024-09-05 | 2025-06-05 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB DURA BRIN | Overgrown | Vegetation | Trim
LC | 129025312 | 030/262 | T2 EI DELTA-COTTONWD 30/262L RPR OPGW | TABLEMTN | ETL.1240.POLE.STPS | 2024-06-05 | 2024-06-05 | 2025-02-06 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | OPGW - Wood | Repair | 46383872 | T2 EI DELTA-COTTONWD 30/262L RPR OPGW | ICW
LC | 129026087 | 000/018 | T2 WV TRINITY-MAPLE CREEK 00/18 INS DMPW | EUREKA | ETL.8170.INSL.NCER | 2024-06-05 | 2024-06-05 | 2025-02-25 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46346072 | T2 WV TRINITY-MAPLE CREEK 00/18 INS DMPW | ICW
LC | 129026091 | 041/793 | T2 EI HT CRK#1-WSTWD 41/793 INS ANML GRD | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-05 | 2024-06-05 | 2025-05-21 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Animal Guard-Wood | Install | 46416161 | T2 EI HT CRK#1-WSTWD 41/793 INS ANML GRD | ICW
LC | 129026169 | 010/048 | T2 BRENTWOOD-KELSO 10/048 RPL INSS | CONCORD | ETL.4410.INSL | 2024-06-05 | 2024-06-05 | 2024-06-05 | Past Due |  | 2025-06-05 | 2025-06-05 | 532 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575008 | T2 EI BRENTWOOD-KELS RPL INSS IN 2 TWRS | 93K
LC | 129026175 | 014/067 | T2 CONTRA COSTA-DELTA 14/067 RPL INSS | CONCORD | ETL.4490.INSL | 2024-06-05 | 2024-06-05 | 2024-06-05 | Past Due |  | 2025-06-05 | 2025-06-05 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575009 | T2 EI CONTRA COSTA-DELTA 14/067 RPL INSS | 93K
LC | 129026270 | 003/044 | T2 LAKEVILLE #1 03/044 RPR STRW | LAKEVLLE | ETL.7360.POLE.NWOD | 2024-06-05 | 2024-06-05 | 2024-06-05 | Past Due |  | 2024-12-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46505451 | T2 WV LAKEVILLE #1 03/044 TOUCH | ICW
LC | 129026553 | 002/051 | T2 WV BRIONES TAP 2/51 TOUCH | CONCORD | ETL.7055.POLE.NWOD | 2024-06-05 | 2024-06-05 | 2025-04-23 | On-Time |  | 2024-12-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46505856 | T2 WV BRIONES TAP 2/51 TOUCH | ICW
LC | 129026951 | :006/041 | T2 ROCK CREEK-POE :006/041 RPR FOND | TABLEMTN | ETL.5630.TOWR | 2024-06-05 | 2024-06-05 | 2025-05-22 | On-Time |  | 2025-06-05 | 2025-06-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46382030 | T2 DI ROCK CREEK-POE :006/041 RPR FOND | ICQ
LC | 129027903 | 019/231A | T2 DRUM-SUMMIT #2 19/231A RPL STRW | SACTO | ETL.1450.POLE.NWOD | 2024-06-06 | 2024-06-05 | 2025-06-25 | Past Due |  | 2025-06-05 | 2025-06-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35610069 | T2 DI DRUM SUMMIT #2 RPL 2 STRW | 70Y
LC | 129031845 | T003/001 | T2 DI TULUCAY-NAPA #1 T3/01 RPR GYWW | LAKEVLLE | ETL.8180.POLE.NWOD | 2024-06-06 | 2024-06-05 | 2025-04-29 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46403773 | T2 DI TULUCAY-NAPA #1 T3/01 RPR GYWW | ICW
LC | 129032022 | :005/032 | T2 DI ROCK CREEK-POE :005/032 RPL HRDT | TABLEMTN | ETL.5630.TOWR | 2024-06-06 | 2024-06-05 | 2025-05-21 | On-Time |  | 2025-06-05 | 2025-06-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46382032 | T2 DI ROCK CREEK-POE :005/032 RPL HRDT | ICQ
LC | 129032026 | :005/038 | T2 DI ROCK CREEK-POE :005/038 RPR FOND | TABLEMTN | ETL.5630.TOWR | 2024-06-06 | 2024-06-05 | 2024-09-04 | On-Time |  | 2024-12-05 | 2025-06-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46268039 | T2 DI ROCK CREEK-POE :005/038 RPR FOND | ICQ
LC | 129032091 | :005/040 | T2 DI ROCK CREEK-POE :005/040 RPR JMPS | TABLEMTN | ETL.5630.INSL | 2024-06-06 | 2024-06-05 | 2025-04-26 | On-Time |  | 2025-06-05 | 2025-06-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46383938 | T2 DI ROCK CREEK-POE :005/040 RPR JMPS | ICS
LC | 129032190 | 036/001 | T2 DI MNDCNO-WLLTS-FRT BRG 36/1 RPR GYWW | WILLITS | ETL.7550.POLE.NWOD | 2024-06-06 | 2024-06-05 | 2025-04-10 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310521 | T2 DI MNDCNO-WLLTS-FRT BRG 36/1 RPR GYWW | ICW
LC | 129032264 | 019/382 | T2 DI COLGATE PALERMO 19/382 RPL INSW | TABLEMTN | ETL.6500.INSL.NCER | 2024-06-06 | 2024-06-05 | 2025-02-06 | On-Time |  | 2025-06-05 | 2025-06-05 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572928 | T2 DI COLGATE PALERMO 19/382 RPL INSW | 93I
LC | 129032266 | 019/382 | T2 DI COLGATE PALERMO 19/382 RPR CNDW | TABLEMTN | ETL.6500.INSL.NCER | 2024-06-06 | 2024-06-05 | 2025-02-06 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46398064 | T2 DI COLGATE PALERMO 19/382 RPR CNDW | ICW
LC | 129036257 | 010/340 | T2 DI SPAULDING-SUMMIT 10/340 RPL INSW | SACTO | ETL.8060.INSL.NCER | 2024-06-07 | 2024-06-05 | 2024-07-22 | On-Time |  | 2025-06-05 | 2025-06-05 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35561835 | T2 DI SPAULDING-SUMMIT 10/340 RPL INSW | 93I
LC | 129071212 | 014/067 | T2 CONTRA COSTA-DELTA 14/067 RPL HNGR | CONCORD | ETL.4490.INSL | 2024-06-13 | 2024-06-05 | 2024-06-05 | Past Due |  | 2025-06-05 | 2025-06-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46289384 | T2 EI CONTRA COSTA-DELTA 14/067 RPL HNGR | ICQ
LC | 129116361 | 010/048 | T2 BRENTWOOD-KELSO 10/048 RPL HNGR | CONCORD | ETL.4410.INSL | 2024-06-24 | 2024-06-05 | 2024-06-05 | Past Due |  | 2025-06-05 | 2025-06-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46289383 | T2 EI BRENTWOOD-KELSO 10/048 RPL HNGR | ICQ
LC | 129215147 | 008/006 | T2 DI TULUCAY-NAPA #1 8/6 RPR INSW | LAKEVLLE | ETL.8180.INSL.NCER | 2024-07-12 | 2024-06-05 | 2025-04-30 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46403771 | T2 DI TULUCAY-NAPA #1 8/6 RPR INSW | ICW
LC | 129215784 | 008/013 | T2 DI TULUCAY-NAPA #1 8/013 RPR STRW | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-07-12 | 2024-06-05 | 2025-04-30 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46403772 | T2 DI TULUCAY-NAPA #1 8/013 RPR STRW | ICW
LC | 129215855 | 005/005 | T2 DI POTTER VLY-MENDOCNO 5/5 RMV NEST | WILLITS | ETL.7810.POLE.NWOD | 2024-07-12 | 2024-06-05 | 2025-06-03 | On-Time |  | 2025-06-05 | 2025-06-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46446908 | T2 DI POTTER VLY-MENDOCNO 5/5 RMV NEST | ICS
LC | 129224046 | 021/433 | T2 DI COLGATE-PALERMO 021/433 RPL HRDD | TABLEMTN | ETL.6500.POLE.NWOD | 2024-07-15 | 2024-06-05 | 2025-02-07 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46398100 | T2 DI COLGATE-PALERMO 021/433 RPL HRDD | ICW
LC | 129224284 | 009/195 | T2 DI CTTNWD-RED BLUFF 009/195 RPR JUMW | TABLEMTN | ETL.6660.INSL.NCER | 2024-07-15 | 2024-06-05 | 2025-04-23 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311155 | T2 DI CTTNWD-RED BLUFF 009/195 RPR JUMW | ICW
LC | 129224402 | 013/448 | T2 SPLDNG-SUMMIT 13/448 RPL STRW | SACTO | ETL.8060.POLE.WOOD | 2024-07-15 | 2024-06-05 | 2024-06-05 | Past Due |  | 2025-06-05 | 2025-06-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35639842 | T2 SPLDNG-SUMMIT 13/448 RPL STRW | 70Y
LC | 129224403 | 014/346 | T2 DI COTTONWD BENTON# 1 14/346 RPL STRW | TABLEMTN | ETL.6640.POLE.WOOD | 2024-07-15 | 2024-06-05 | 2025-04-29 | On-Time |  | 2025-06-05 | 2025-06-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572991 | T2 DI COTTONWD BENTON# 1 14/346 RPL STRW | 70Y
LC | 129224448 | 021/146A | T2 DI CARIBOU-TBL MTN 21/146A RMV VEG | TABLEMTN | ETL.4440.POLE.NWOD | 2024-07-15 | 2024-06-05 | 2024-06-05 | Past Due |  | 2025-06-05 | 2025-06-05 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129224473 | 010/200 | T2 DI CTTNWD-RED BLUFF 010/200 RPL HRDD | TABLEMTN | ETL.6660.POLE.NWOD | 2024-07-15 | 2024-06-05 | 2025-04-23 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46311154 | T2 DI CTTNWD-RED BLUFF 010/200 RPL HRDD | ICW
LC | 129224525 | 034/254 | T2 DI CARIBOU TBL MTN 34/254 RPR JUMS | TABLEMTN | ETL.4440.INSL.NCER | 2024-07-15 | 2024-06-05 | 2025-04-09 | On-Time |  | 2025-06-05 | 2025-06-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46337597 | T2 DI CARIBOU TBL MTN 34/254 RPR JUMS | ICS
LC | 129224545 | 022/444 | T2 DI COLGATE-PALEMRO 22/444 RPL POLE | TABLEMTN | ETL.6500.POLE.WOOD | 2024-07-15 | 2024-06-05 | 2025-05-20 | On-Time |  | 2025-06-05 | 2025-06-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572930 | T2 DI COLGATE-PALEMRO 22/444 RPL POLE | 70Y
LC | 129224652 | 004/086 | T2 DI COTTONWOOD-RED BLUFF 4/86 RPL INSW | TABLEMTN | ETL.6660.INSL.NCER | 2024-07-15 | 2024-06-05 | 2025-04-24 | On-Time |  | 2025-06-05 | 2025-06-05 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 35572997 | T2 DI COTTONWOOD-RED BLUFF 4/86 RPL INSW | 93I
LC | 129224653 | 004/086 | T2 DI COTNWD-RED BLUFF 04/86 RPR JUMW | TABLEMTN | ETL.6660.INSL.NCER | 2024-07-15 | 2024-06-05 | 2025-04-24 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311156 | T2 DI COTNWD-RED BLUFF 04/86 RPR JUMW | ICW
LC | 129224655 | 007/000 | T2 DI POTR VLY-MENDO 07/00 RPR ACG | WILLITS | ETL.7810.POLE.NWOD | 2024-07-15 | 2024-06-05 | 2025-03-24 | On-Time |  | 2025-06-05 | 2025-06-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | Anti-Climbing Guard | Structure-Tower | Repair | 46290427 | T2 DI POTR VLY-MENDO 07/00 RPR ACG | ICQ
LC | 129224657 | 007/000 | T2 DI POTR VLY-MENDO 07/00 RPR FOND | WILLITS | ETL.7810.POLE.NWOD | 2024-07-15 | 2024-06-05 | 2025-03-24 | On-Time |  | 2025-06-05 | 2025-06-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46290428 | T2 DI POTR VLY-MENDO 07/00 RPR FOND | ICQ
LC | 129224687 | T002/012 | T2 TULUCAY-NAPA #1 T2/12 RPL POLE | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-07-15 | 2024-06-05 | 2024-06-05 | Past Due |  | 2025-06-05 | 2025-06-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35584566 | T2 DI TULUCAY-NAPA #1 T2/12 RPL POLE | 70Y
LC | 129230304 | 008/214 | T2 DI CTTNWD-BENTON #1 008/214 RMV VEG | TABLEMTN | ETL.6640.POLE.NWOD | 2024-07-16 | 2024-06-05 | 2025-04-15 | On-Time |  | 2025-06-05 | 2025-06-05 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129235847 | 014/360 | T2 DI CTONWD-BENTON #1 14/360 RPL STRW | TABLEMTN | ETL.6640.POLE.WOOD | 2024-07-17 | 2024-06-05 | 2025-04-28 | On-Time |  | 2025-06-05 | 2025-06-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572993 | T2 DI CTONWD-BENTON #1 14/360 RPL STRW | 70Y
LC | 129245389 | 009/197 | T2 DI CTTNWD-RED BLUFF 9/197 TOUCH | TABLEMTN | ETL.6660.POLE.NWOD | 2024-07-19 | 2024-06-05 | 2024-06-05 | Past Due |  | 2024-12-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46486750 | T2 DI CTTNWD-RED BLUFF 9/197 TOUCH | ICW
LC | 129245488 | 021/151 | T2 DI CARIBOU-TBL MTN 021/151 RMV ENCRCH | TABLEMTN | ETL.4440.TOWR | 2024-07-19 | 2024-06-05 | 2024-09-16 | On-Time |  | 2024-12-05 | 2025-06-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46322493 | T2 DI CARIBOU-TBL MTN 021/151 RMV ENCRCH | ICQ
LC | 129247417 | 008/215 | T2 DI CTTNWD-BNTN #1 08/215 RMV VEG | TABLEMTN | ETL.6640.POLE.NWOD | 2024-07-19 | 2024-06-05 | 2025-04-15 | On-Time |  | 2025-06-05 | 2025-06-05 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE ACCH COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129250123 | 004/085 | T2 DI CTTNWD-RD BLF 04/085 RPR INSW | TABLEMTN | ETL.6660.INSL.NCER | 2024-07-19 | 2024-06-05 | 2025-04-24 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46311157 | T2 DI CTTNWD-RD BLF 04/085 RPR INSW | ICW
LC | 129339367 | 010/215 | T2 DI COTNWD RED BLF 10/215 RPL DAMW | TABLEMTN | ETL.6660.INSL.NCER | 2024-08-06 | 2024-06-05 | 2025-04-23 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Damper-Wood | Replace | 46337216 | T2 DI COTNWD RED BLF 10/215 RPL DAMW | ICW
LC | 129340241 | 006/027 | T2 DI PITSBURG SN RMN 06/027 RPL HRDT | CONCORD | ETL.5490.TOWR | 2024-08-06 | 2024-06-05 | 2025-04-28 | On-Time |  | 2025-06-05 | 2025-06-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46339718 | T2 DI PITSBURG SN RMN 06/027 RPL HRDT | ICQ
LC | 129347213 | 022/106 | T2 DI MNTA VSTA-CYTE SS 22/106 RPR SHLS | MOSSLNDG | ETL.5090.TOWR | 2024-08-07 | 2024-06-05 | 2025-03-28 | On-Time |  | 2025-06-05 | 2025-06-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46393857 | T2 DI MNTA VSTA-CYTE SS 22/106 RPR SHLS | ICS
LC | 129347459 | 007/010 | T2 DI TULUCAY NAPA #1 7/10 RPL STRW | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-08-07 | 2024-06-05 | 2025-05-03 | On-Time |  | 2025-06-05 | 2025-06-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586957 | T2 DI TULUCAY NAPA #1 7/10 RPL STRW | 70Y
LC | 129347506 | 005/087 | T2 DI COLGATE-PALERMO 5/087 RPR INSW | SACTO | ETL.6500.INSL.CERA | 2024-08-07 | 2024-06-05 | 2025-04-29 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46401367 | T2 DI COLGATE-PALERMO 5/087 RPR INSW | ICW
LC | 129347713 | 005/083 | T2 DI COLGATE-PALERMO 5/83 RPL STRW | SACTO | ETL.6500.POLE.WOOD | 2024-08-07 | 2024-06-05 | 2025-04-29 | On-Time |  | 2025-06-05 | 2025-06-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586839 | T2 DI COLGATE-PALERMO 5/83 RPL POLE | 70Y
LC | 129353613 | 010/192 | T2 DI COLGATE PALERMO 10/192 RPL POLE | SACTO | ETL.6500.POLE.WOOD | 2024-08-08 | 2024-06-05 | 2025-04-30 | On-Time |  | 2025-06-05 | 2025-06-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586886 | T2 DI COLGATE PALERMO 10/192 RPL POLE | 70Y
LC | 129353666 | 014/343 | T2 DI COTTONWD BENTON#1 14/343 RPL STRW | TABLEMTN | ETL.6640.POLE.WOOD | 2024-08-08 | 2024-06-05 | 2025-04-29 | On-Time |  | 2025-06-05 | 2025-06-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586891 | T2 DI COTTONWD BENTON#1 14/343 RPL STRW | 70Y
LC | 129353789 | 017/212 | T2 DRUM-SUMMIT #2 17/212R RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-08-08 | 2024-06-05 | 2025-05-01 | On-Time |  | 2025-06-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458348 | T2 DI DRUM-SUMMIT #2 017/212 RPR GYWW | ICW
LC | 129353791 | 010/191 | T2 DI COLGATE PALERMO 10/191 RPL POLE | SACTO | ETL.6500.POLE.WOOD | 2024-08-08 | 2024-06-05 | 2025-04-30 | On-Time |  | 2025-06-05 | 2025-06-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586885 | T2 DI COLGATE PALERMO 10/191 RPL POLE | 70Y
LC | 129382138 | 007/144 | T2 DI CTNWD-RED BLF-RD 7/144 RPL INSW | TABLEMTN | ETL.6660.INSL.NCER | 2024-08-13 | 2024-06-05 | 2024-12-04 | On-Time |  | 2025-06-05 | 2025-06-05 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35586892 | T2 DI CTNWD-RED BLF-RD 7/144 RPL INSW | 93I
LC | 129382161 | 007/144 | T2 DI CTNWD-RED BLF-RD 7/144 RPR JUMW | TABLEMTN | ETL.6660.INSL.NCER | 2024-08-13 | 2024-06-05 | 2024-12-04 | On-Time |  | 2024-09-05 | 2025-06-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46305310 | T2 DI CTNWD-RED BLF-RD 7/144 RPR JUMW | ICW
LC | 129382351 | 022/108 | T2 DI MTA VTA CYTE SWSTA 22/108 RPR SHLS | MOSSLNDG | ETL.5090.TOWR | 2024-08-13 | 2024-06-05 | 2025-03-28 | On-Time |  | 2025-06-05 | 2025-06-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46393855 | T2 DI MTA VTA CYTE SWSTA 22/108 RPR SHLS | ICS
LC | 129382353 | 022/108 | T2 DI MTA VTA CYTE SS 22/108 RMV NEST | MOSSLNDG | ETL.5090.TOWR | 2024-08-13 | 2024-06-05 | 2024-12-12 | On-Time |  | 2025-06-05 | 2025-06-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46414818 | T2 DI MTA VTA CYTE SS 22/108 RMV NEST | ICS
LC | 129382355 | 022/108 | T2 DI MTA VTA CYTE SS 22/108 RMV VEG | MOSSLNDG | ETL.5090.TOWR | 2024-08-13 | 2024-06-05 | 2025-04-24 | On-Time |  | 2025-06-05 | 2025-06-05 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129382542 | 006/001 | T2 DI PTTR VLLY-MNDCNO 6/1 RMV NEST | WILLITS | ETL.7810.POLE.NWOD | 2024-08-13 | 2024-06-05 | 2025-06-03 | On-Time |  | 2025-06-05 | 2025-06-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46446910 | T2 DI PTTR VLLY-MNDCNO 6/1 RMV NEST | ICS
LC | 123773860 | :000/005 | T2NT EI STAN-MEL SS-MAN :0/5 RPR ROAD | VICTOR | ETL.3830.TOWR | 2022-06-06 | 2022-06-06 | 2024-10-23 | On-Time |  | 2025-06-06 | 2025-06-06 | 932 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Grade Change | Road | Repair | 45659991 | T2NT EI STAN-MEL SS-MAN :0/5 RPR ROAD | CHS
LC | 123777287 | 036/170 | T2NT DI RND MTN-TB MT#1 36/170 RPR GYWS | TABLEMTN | ETL.6060.TOWR | 2022-06-07 | 2022-06-06 | 2023-08-11 | On-Time |  | 2025-06-06 | 2025-06-06 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45699161 | T2 DI RND MTN-TBL MTN#1 36/170 RPR GYWS | ICS
LC | 123784826 | 035/167 | T2NT DI RND MT-TB MN #2 35/167 BNT STEEL | TABLEMTN | ETL.6070.TOWR | 2022-06-07 | 2022-06-06 | 2023-08-09 | On-Time |  | 2025-06-06 | 2025-06-06 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647639 | T2 DI RND MTN-TBL MN #2 35/167 BNT STEEL | ICQ
LC | 123852774 | 004/000 | T2NT DI SALMON CREEK TAP 4/0 RPR INSW | LAKEVLLE | ETL.6981.INSL | 2022-06-15 | 2022-06-06 | 2023-07-14 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 45571278 | T2 DI SALMON CREEK TAP 4/0 RPR INSW | ICW
LC | 129027326 | 000/011 | T2 HAAS-WOODCHUCK 0/11 RPR INSW | FRESNO | ETL.8730.INSL.NCER | 2024-06-06 | 2024-06-06 | 2024-06-06 | Past Due |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46297967 | T2 HAAS-WOODCHUCK 0/11 RPR INSW | ICW
LC | 129028137 | 023/274A | T2 EI DRUM-SMT #2 23/274A RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-06-06 | 2024-06-06 | 2025-05-01 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458329 | T2 EI DRUM-SMT #2 23/274A RPR GYWW | ICW
LC | 129028142 | 021/101 | T2 CALLENDER SW STA-MESA 21/101 TOUCH | PISMOBCH | ETL.1210.TOWR | 2024-06-06 | 2024-06-06 | 2025-04-09 | On-Time |  | 2024-12-06 | 2025-06-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46488933 | T2 CALLENDER SW STA-MESA 21/101 TOUCH | ICQ
LC | 129028349 | 025/305C | T2 EI DRUM-SUMMIT #1 25/305C RPR ANCW | SACTO | ETL.1440.POLE.NWOD | 2024-06-06 | 2024-06-06 | 2024-06-23 | On-Time |  | 2024-12-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46268028 | T2 EI DRUM-SUMMIT #1 25/305C RPR ANCW | ICW
LC | 129028424 | 025/305C | T2 EI DRUM-SUMMIT #1 25/305C RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-06-06 | 2024-06-06 | 2024-06-23 | On-Time |  | 2024-12-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46268020 | T2 EI DRUM-SUMMIT #1 25/305C RPR GYWW | ICW
LC | 129028533 | 025/305B | T2 EI DRUM-SUMMIT #1 25/305B RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-06-06 | 2024-06-06 | 2024-06-22 | On-Time |  | 2024-12-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46267905 | T2 EI DRUM-SUMMIT #1 25/305B RPR GYWW | ICW
LC | 129028586 | 025/305A | T2 EI DRUM-SUMMIT #1 25/305A REGR STRW | SACTO | ETL.1440.POLE.NWOD | 2024-06-06 | 2024-06-06 | 2024-06-22 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46269396 | T2 EI DRUM-SUMMIT #1 25/305A REGR STRW | ICW
LC | 129028722 | 012/009 | T2 EI MENDOCINO-WILLITS 12/009 RPL HRDW | WILLITS | ETL.7540.POLE.WOOD | 2024-06-06 | 2024-06-06 | 2025-01-06 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46310525 | T2 EI MENDOCINO-WILLITS 12/009 RPL HRDW | ICW
LC | 129028753 | 025/304 | T2 EI DRUM-SUMMIT NO. 1_025/304 RPR CRSW | SACTO | ETL.1440.POLE.WDPS | 2024-06-06 | 2024-06-06 | 2025-05-02 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46398063 | T2 EI DRUM-SUMMIT NO. 1_025/304 RPR CRSW | ICW
LC | 129029324 | 019/225C | T2 EI DRUM-SUMMIT #2 19/225C RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-06-06 | 2024-06-06 | 2025-04-30 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458330 | T2 EI DRUM-SUMMIT #2 19/225C RPR GYWW | ICW
LC | 129030430 | 024/290C | T2 EI DRUM-SUMMIT #1 24/290C RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-06-06 | 2024-06-06 | 2024-06-23 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46278105 | T2 EI DRUM-SUMMIT #1 24/290C RPR GYWW | ICW
LC | 129030798 | 019/002 | T2 CLEAR LAKE-KONOCTI 019/002 RPR GYWW | WILLITS | ETL.6852.POLE.NWOD | 2024-06-06 | 2024-06-06 | 2025-03-19 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446914 | T2 CLEAR LAKE-KONOCTI 019/002 RPR GYWW | ICW
LC | 129031395 | 000/007 | T2 KANAKA TAP 0/7R RPL STRW | TABLEMTN | ETL.4223.POLE.STPS | 2024-06-06 | 2024-06-06 | 2024-12-07 | On-Time |  | 2024-09-06 | 2025-06-06 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW NONR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35540817 | T2 KANAKA TAP 01/08 RPL POLES | 70Y
LC | 129031398 | 000/007 | T2 KANAKA TAP 0/7C RPL STRW | TABLEMTN | ETL.4223.POLE.STPS | 2024-06-06 | 2024-06-06 | 2024-12-07 | On-Time |  | 2024-09-06 | 2025-06-06 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW NONR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35540817 | T2 KANAKA TAP 01/08 RPL POLES | 70Y
LC | 129031399 | 000/007 | T2 KANAKA TAP 0/7L RPL STRW | TABLEMTN | ETL.4223.POLE.STPS | 2024-06-06 | 2024-06-06 | 2024-12-07 | On-Time |  | 2024-09-06 | 2025-06-06 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW NONR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35540817 | T2 KANAKA TAP 01/08 RPL POLES | 70Y
LC | 129031413 | 023/200 | T2 EI CASCADE-COTTONWD 23/200 RPR OPGW | TABLEMTN | ETL.1240.POLE.STPS | 2024-06-06 | 2024-06-06 | 2025-04-09 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | OPGW - Wood | Repair | 46383873 | T2 EI CASCADE-COTTONWD 23/200 RPR OPGW | ICW
LC | 129031436 | 029/253 | T2 EI DELTA-COTTONWOOD_029/253 TOUCH | TABLEMTN | ETL.1240.POLE.STPS | 2024-06-06 | 2024-06-06 | 2025-05-22 | On-Time |  | 2024-12-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46486740 | T2 EI DELTA-COTTONWOOD_029/253 TOUCH | ICW
LC | 129031470 | 001/009 | T2 KANAKA TAP 1/9L RPL STRW | TABLEMTN | ETL.4223.POLE.STPS | 2024-06-06 | 2024-06-06 | 2024-12-07 | On-Time |  | 2024-09-06 | 2025-06-06 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW NONR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35540817 | T2 KANAKA TAP 01/08 RPL POLES | 70Y
LC | 129031471 | 001/009 | T2 KANAKA TAP 1/9R RPL STRW | TABLEMTN | ETL.4223.POLE.STPS | 2024-06-06 | 2024-06-06 | 2024-12-07 | On-Time |  | 2024-09-06 | 2025-06-06 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW NONR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35540817 | T2 KANAKA TAP 01/08 RPL POLES | 70Y
LC | 129031475 | 012/001 | T2 EI MENDOCINO-WILLITS 12/001 RPR GYWW | WILLITS | ETL.7540.POLE.NWOD | 2024-06-06 | 2024-06-06 | 2025-01-09 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310523 | T2 EI MENDOCINO-WILLITS 12/001 RPR GYWW | ICW
LC | 129031575 | 012/008 | T2 EI MENDOCINO-WILLITS 12/008 RPR INSW | WILLITS | ETL.7540.INSL.NCER | 2024-06-06 | 2024-06-06 | 2025-01-06 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310524 | T2 EI MENDOCINO-WILLITS 12/008 RPR INSW | ICW
LC | 129032135 | 000/009 | T2 ROCK CREEK POE 0/9 COMPLETE | TABLEMTN | ETL.5630.INSL.CERA | 2024-06-06 | 2024-06-06 | 2025-04-25 | On-Time |  | 2025-06-06 | 2025-06-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46383939 | T2 DI ROCK CREEK POE 0/9 RPR JUMS | ICS
LC | 129032146 | 062/450 | T2NT EI BRDGVLE-COTONWD 62/452 RMV VEG | TABLEMTN | ETL.1110.TOWR | 2024-06-06 | 2024-06-06 | 2024-06-06 | On-Time |  | 2027-06-06 | 2025-06-06 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 129032352 | 013/126 | T2 EI UKH-HPLND-CLVRDL 13/126 RPR WDPKR | WILLITS | ETL.4050.POLE.WOOD | 2024-06-06 | 2024-06-06 | 2025-06-19 | Past Due |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46446913 | T2 EI UKH-HPLND-CLVRDL 13/126 RPR WDPKR | ICW
LC | 129032438 | 006/043 | T2 RE COTTONWOOD#1 6/43 RPL INSS | TABLEMTN | ETL.6620.INSL.CERA | 2024-06-06 | 2024-06-06 | 2025-06-02 | On-Time |  | 2025-06-06 | 2025-06-06 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569574 | T2 DI COTTONWOOD#1 RPL INSS 4 TWRS | 93K
LC | 129033287 | 004/010 | T2 EI CHOWCHILLA-KERCKHOFF 4/10 RPL POLE | FRESNO | ETL.1250.POLE.WOOD | 2024-06-06 | 2024-06-06 | 2025-03-25 | On-Time |  | 2025-06-06 | 2025-06-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573102 | T2 EI CHOWCHILLA-KERCKHOFF 4/10 RPL POLE | 70Y
LC | 129033515 | 004/006 | T2 EI CHOWCHILLA-KERCKHOFF 4/6 RPL POLE | FRESNO | ETL.1250.POLE.WOOD | 2024-06-06 | 2024-06-06 | 2025-03-25 | On-Time |  | 2025-06-06 | 2025-06-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573100 | T2 EI CHOWCHILLA-KERCKHOFF 4/6 RPL POLE | 70Y
LC | 129033856 | 018/223 | T2 EI DRUM-SUMMIT#2 18/223 RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-06-07 | 2024-06-06 | 2025-04-30 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458331 | T2 EI DRUM-SUMMIT#2 18/223 RPR GYWW | ICW
LC | 129033883 | 019/224 | T2 EI DRUM-SUMMIT#2_019/224 RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-06-07 | 2024-06-06 | 2025-04-30 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458332 | T2 EI DRUM-SUMMIT#2_019/224 RPR GYWW | ICW
LC | 129035681 | 000/005A | T2 ROCK CREEK-POE 0/5A UNBURY | TABLEMTN | ETL.5630.POLE.NWOD | 2024-06-07 | 2024-06-06 | 2025-05-28 | On-Time |  | 2025-06-06 | 2025-06-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46382033 | T2 DI ROCK CREEK-POE 00/05A UNBURY | ICQ
LC | 129035806 | 001/010 | T2 ROCK CREEK-POE 01/10 COMPLETE | TABLEMTN | ETL.5630.INSL.NCER | 2024-06-07 | 2024-06-06 | 2025-04-26 | On-Time |  | 2025-06-06 | 2025-06-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46383940 | T2 DI ROCK CREEK-POE 01/10 RPR JUMS | ICS
LC | 129035809 | 014/000 | T2 DI MENDOCINO-WFB 14/0 RMV VEG | WILLITS | ETL.7550.POLE.NWOD | 2024-06-07 | 2024-06-06 | 2025-01-12 | On-Time |  | 2025-06-06 | 2025-06-06 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE SPCR ACCM CNCL OH TR2 PRTO AIR FRAR | Overgrown | Vegetation | Remove
LC | 129035839 | 000/004 | T2 ROCK CREEK-POE 00/04 RPL HRDT | TABLEMTN | ETL.5630.TOWR | 2024-06-07 | 2024-06-06 | 2025-05-28 | On-Time |  | 2025-06-06 | 2025-06-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46382035 | T2 DI ROCK CREEK-POE 00/04 RPL HRDT | ICQ
LC | 129035952 | 062/000 | T2 DI HMBLDT-TRNTY -STL PL 62/0 RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-06-07 | 2024-06-06 | 2024-08-31 | On-Time |  | 2024-09-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46264480 | T2 DI HMBLDT-TRNTY -STL PL 62/0 RPR JUMW | ICW
LC | 129035970 | 062/000 | T2 DI HMLDT-TRNTY -STL PL 62/0 RPR ANCW | EUREKA | ETL.1820.POLE.STPS | 2024-06-07 | 2024-06-06 | 2025-02-21 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46346075 | T2 DI HMLDT-TRNTY -STL PL 62/0 RPR ANCW | ICW
LC | 129036283 | 011/374 | T2 SPAULDING-SUMMIT 11/374 RPR GYWW | SACTO | ETL.8060.POLE.WOOD | 2024-06-07 | 2024-06-06 | 2025-05-30 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46398066 | T2 DI SPAULDING-SUMMIT 11/374 RPR GYWW | ICW
LC | 129036774 | 016/522 | T2 DI SPAULDING-SUMMIT 16/522 RPL INSW | SACTO | ETL.8060.INSL.NCER | 2024-06-07 | 2024-06-06 | 2024-07-30 | On-Time |  | 2025-06-06 | 2025-06-06 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35561433 | T2 DI SPAULDING-SUMMIT 16/522 RPL INSW | 93I
LC | 129036932 | 018/566 | T2 DI SPAULDING-SUMMIT 18/566 RPR GYWW | SACTO | ETL.8060.POLE.WOOD | 2024-06-07 | 2024-06-06 | 2024-07-25 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46284156 | T2 DI SPAULDING-SUMMIT 18/566 RPR GYWW | ICW
LC | 129036934 | 018/566 | T2 DI SPAULDING-SUMMIT 18/566 COTTER | SACTO | ETL.8060.INSL.NCER | 2024-06-07 | 2024-06-06 | 2024-07-25 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46284157 | T2 DI SPAULDING-SUMMIT 18/566 COTTER | ICW
LC | 129224280 | 018/589 | T2 DI SPAULDING-SUMMIT 18/589 RPR INSW | SACTO | ETL.8060.INSL.NCER | 2024-07-15 | 2024-06-06 | 2024-07-30 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46308095 | T2 DI SPAULDING-SUMMIT 18/589 RPR INSW | ICW
LC | 129224447 | 014/465 | T2 DI SPAULDING SUMMIT 14/465 RPR INSW | SACTO | ETL.8060.INSL.NCER | 2024-07-15 | 2024-06-06 | 2025-05-31 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46398103 | T2 DI SPAULDING SUMMIT 14/465 RPR INSW | ICW
LC | 129224544 | 005/102 | T2 DI HAT CREEK #1-WESTWD 5/102 RPL DAMW | TABLEMTN | ETL.7030.INSL.NCER | 2024-07-15 | 2024-06-06 | 2025-05-13 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Damper-Wood | Replace | 46416179 | T2 DI HAT CREEK #1-WESTWD 5/102 RPL DAMW | ICW
LC | 129224594 | 012/243 | T2 DI COLGATE PALERMO 12/243 RPL HRDD | TABLEMTN | ETL.6500.POLE.WOOD | 2024-07-15 | 2024-06-06 | 2025-03-24 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46400342 | T2 DI COLGATE PALERMO 12/243 RPL HRDD | ICW
LC | 129224649 | 021/150 | T2 CARIBOU-TBL MTN 21/150 TOUCH | TABLEMTN | ETL.4440.TOWR | 2024-07-15 | 2024-06-06 | 2024-06-06 | Past Due |  | 2024-09-06 | 2025-06-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478266 | T2 DI CARIBOU-TBL MTN 21/150 TOUCH | ICQ
LC | 129224794 | 023/279 | T2 DI DRM-SMMT # 2 23/279 RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-07-15 | 2024-06-06 | 2025-05-31 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458338 | T2 DI DRM-SMMT # 2 23/279 RPR GYWW | ICW
LC | 129230355 | 021/250 | T2 DRUM-SUMMIT #1 21/250L RPL ANCW | SACTO | ETL.1440.POLE.STPS | 2024-07-16 | 2024-06-06 | 2024-06-06 | Past Due |  | 2025-06-06 | 2025-06-06 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586898 | T2 DI DRM-SMMT #1 27/318L RPL ANCW | 93E
LC | 129230372 | 021/250 | T2 DI DRUM-SUMMIT #1 21/250 COTTER | SACTO | ETL.1440.INSL.NCER | 2024-07-16 | 2024-06-06 | 2025-05-28 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46325987 | T2 DI DRUM-SUMMIT #1 21/250 COTTER | ICW
LC | 129235950 | 015/002 | T2 MNDCNO-WLTS-FRT BRG 15/2 RPR ANCW | WILLITS | ETL.7550.POLE.WOOD | 2024-07-17 | 2024-06-06 | 2024-06-06 | Past Due |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46310526 | T2 DI MNDCNO-WLTS-FRT BRG 15/2 INSPECT | ICW
LC | 129235956 | 035/258 | T2 DI CARIBOU-TBL MTN 035/258 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2024-07-17 | 2024-06-06 | 2025-05-27 | On-Time |  | 2025-06-06 | 2025-06-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46354078 | T2 DI CARIBOU-TBL MTN 035/258 RPL HRDT | ICQ
LC | 129245203 | 021/147 | T2 DI CARIBOU-TBL MTN 021/147 RPR INSS | TABLEMTN | ETL.4440.INSL.CERA | 2024-07-19 | 2024-06-06 | 2025-04-05 | On-Time |  | 2025-06-06 | 2025-06-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46337599 | T2 DI CARIBOU-TBL MTN 021/147 RPR INSS | ICS
LC | 129245421 | 018/571 | T2 DI SPAULDING-SUMMIT 18/571 RPR STRW | SACTO | ETL.8060.POLE.WOOD | 2024-07-19 | 2024-06-06 | 2025-05-31 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401136 | T2 DI SPAULDING-SUMMIT 18/571 RPR STRW | ICW
LC | 129247058 | :020/001 | T2 DI EAGLE ROCK-CORTINA :20/1 RPR ADSS | WILLITS | ETL.1470.POLE.NWOD | 2024-07-19 | 2024-06-06 | 2025-03-13 | On-Time |  | 2024-09-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46305667 | T2 DI EAGLE ROCK-CORTINA 20/1 RPR ADSS | ICW
LC | 129376311 | 005/099 | T2 DI HAT CREEK #1-WSTWD 5/99 RPL ANCW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-08-12 | 2024-06-06 | 2025-05-13 | On-Time |  | 2025-06-06 | 2025-06-06 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586912 | T2 DI HAT CREEK #1-WSTWD 5/99 RPLC ANCW | 93E
LC | 129376316 | 005/099 | T2 DI HAT CREEK #1-WSTWD 5/99 RPR GYWW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-08-12 | 2024-06-06 | 2024-08-28 | On-Time |  | 2024-12-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46303494 | T2 DI HAT CREEK #1-WSTWD 5/99 RPR GYWW | ICW
LC | 129382190 | T002/015 | T2 DI TULUCAY-NAPA #1 T2/15 RPR GYWW | LAKEVLLE | ETL.8180.POLE.NWOD | 2024-08-13 | 2024-06-06 | 2025-04-29 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46401533 | T2 DI TULUCAY-NAPA #1 T2/15 RPR GYWW | ICW
LC | 129382216 | 008/004 | T2 DI TULUCAY NAPA#1 08/004 RPR ANCW | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-08-13 | 2024-06-06 | 2025-01-20 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46401524 | T2 DI TULUCAY NAPA#1 08/004 RPR ANCW | ICW
LC | 129382482 | 010/010 | T2 DI FULTON-HOPLAND 10/10 RPL STRW | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-08-13 | 2024-06-06 | 2025-05-29 | On-Time |  | 2025-06-06 | 2025-06-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586908 | T2 DI FULTON-HOPLAND 10/10 RPL STRW | 70Y
LC | 129382493 | 022/153 | T2 CARIBOU-TBL MTN 22/153 TOUCH | TABLEMTN | ETL.4440.TOWR | 2024-08-13 | 2024-06-06 | 2024-06-06 | Past Due |  | 2024-12-06 | 2025-06-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478268 | T2 DI CARIBOU-TBL MTN 22/153 TOUCH | ICQ
LC | 129382498 | 022/153 | T2 DI CARIBOU TBL MTN 22/153 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2024-08-13 | 2024-06-06 | 2025-05-27 | On-Time |  | 2025-06-06 | 2025-06-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46337137 | T2 DI CARIBOU TBL MTN 22/153 RPR STRT | ICQ
LC | 129382574 | 008/009 | T2 DI TULUCAY-NAPA #1 8/9 RPR ANCW | LAKEVLLE | ETL.8180.POLE.NWOD | 2024-08-13 | 2024-06-06 | 2025-01-22 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46401530 | T2 DI TULUCAY-NAPA #1 8/9 RPR ANCW | ICW
LC | 129382618 | 019/221 | T2 DI DRUM-SUMMIT #1 19/221 RPL ANCW | SACTO | ETL.1440.POLE.WDPS | 2024-08-13 | 2024-06-06 | 2024-11-18 | On-Time |  | 2024-12-06 | 2025-06-06 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35575776 | T1 DI DRUM-SUMMIT #1 16/191C RPLC ANCW | 93E
LC | 129382619 | 023/111 | T2 CORTINA-MENDCN #1 23/111 RPL INSS | WILLITS | ETL.1330.INSL.NCER | 2024-08-13 | 2024-06-06 | 2024-06-06 | Past Due |  | 2025-06-06 | 2025-06-06 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35608975 | T2 DI CORTINA-MENDCN #1 23/111 RPL INSS | 93K
LC | 129382725 | 011/008 | T2 DI FULTON-HOPLAND 11/8 INS HRDD | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-08-13 | 2024-06-06 | 2025-03-19 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Missing | Hardware-Wood | Install | 46401434 | T2 DI FULTON-HOPLAND 11/8 INS HRDD | ICW
LC | 129391409 | 010/361 | T2 SPAULDING-SUMMIT 10/361 RPR INSW | SACTO | ETL.8060.INSL.NCER | 2024-08-15 | 2024-06-06 | 2024-06-06 | Past Due |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46401368 | T2 DI SPLDNG-SUMMIT 010/361 RPR INSW | ICW
LC | 129391539 | 008/066 | T2 DI CARIBOU-TBL MTN 8/066 RPR GYWT | TABLEMTN | ETL.4440.TOWR | 2024-08-15 | 2024-06-06 | 2025-05-22 | On-Time |  | 2025-06-06 | 2025-06-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46337138 | T2 DI CARIBOU-TBL MTN 8/066 RPR GYWT | ICQ
LC | 129391672 | 008/066 | T2 DI CARIBOU-TBL MTN 8/066 RPR INSS | TABLEMTN | ETL.4440.INSL.CERA | 2024-08-15 | 2024-06-06 | 2025-04-01 | On-Time |  | 2025-06-06 | 2025-06-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46337602 | T2 DI CARIBOU-TBL MTN 8/066 RPR INSS | ICS
LC | 129393463 | 015/491 | T2 DI SPAULDING-SUMMIT 15/491 RPR GYWW | SACTO | ETL.8060.POLE.WOOD | 2024-08-15 | 2024-06-06 | 2025-05-31 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46401371 | T2 DI SPAULDING-SUMMIT 15/491 RPR GYWW | ICW
LC | 129393636 | 016/507A | T2 DI SPLDNG-SUMMIT 16/507AL RPR GRWW | SACTO | ETL.8060.POLE.WDPS | 2024-08-15 | 2024-06-06 | 2024-11-14 | On-Time |  | 2024-09-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46305390 | T2 DI SPLDNG-SUMMIT 16/507AL RPR GRWW | ICW
LC | 129394137 | T002/014 | T2 DI TULUCAY-NAPA #1 T002/014 COMPLETE | LAKEVLLE | ETL.8180.TOWR | 2024-08-15 | 2024-06-06 | 2025-03-27 | On-Time |  | 2025-06-06 | 2025-06-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46345550 | T2 DI TULUCAY-NAPA #1 T002/014 RPL HRDT | ICQ
LC | 129394436 | 008/010 | T2 DI TULUCAY-NAPA #1 8/10 RPR ANCW | LAKEVLLE | ETL.8180.POLE.NWOD | 2024-08-15 | 2024-06-06 | 2025-01-22 | On-Time |  | 2025-06-06 | 2025-06-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46401531 | T2 DI TULUCAY-NAPA #1 8/10 RPR ANCW | ICW
LC | 129409070 | 034/256 | T2 DI CARIBOU-TBL MTN 34/256 RPL INSS | TABLEMTN | ETL.4440.INSL | 2024-08-19 | 2024-06-06 | 2025-04-06 | On-Time |  | 2025-06-06 | 2025-06-06 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569572 | T2 DI CARIBOU-TBL MTN RPL INSS | 93K
LC | 129904179 | 315 | T3 BRUNSWICK #1 000/002 RPR SWTC | SACTO | ETL.1422.SWIT | 2024-12-06 | 2024-12-06 | 2025-04-22 | On-Time |  | 2025-06-06 | 2025-06-06 | 623 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH FMOB TR3 PRTO BRIN | Out of Adjustment | Switch | Repair | 46446306 | T3 BRUNSWICK #1 000/002 RPR SWTC | ICE
LC | 123779686 | 001/005 | T2NT EI MENDOCINO-WILLITS 001/5 RPR GYWW | WILLITS | ETL.7540.POLE.WOOD | 2022-06-07 | 2022-06-07 | 2023-05-22 | On-Time |  | 2023-06-07 | 2025-06-07 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45736111 | T2NT EI MENDOCINO-WILLITS 001/5 RPR GYWW | ICW
LC | 123852570 | 007/053 | T3NT DI MRGA-SAN LEANDRO#1 7/53 RPR STRT | CONCORD | ETL.2770.TOWR | 2022-06-15 | 2022-06-07 | 2023-06-14 | On-Time |  | 2025-06-07 | 2025-06-07 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45697875 | T3 DI MRAGA-SAN LEANDRO#1 07/53 RPR STRT | ICQ
LC | 123855570 | 017/156 | T3NT DI MNTA VISTA-BRNS 17/156 RPR HRDW | MOSSLNDG | ETL.7590.POLE.NWOD | 2022-06-16 | 2022-06-07 | 2023-08-16 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR3N PRTO AIR FRAB | Missing | Hardware-Wood | Install | 45618803 | T3 DI MNTA VISTA-BRNS 17/156 RPR HRDW | ICW
LC | 123967293 | 007/052 | T3NT DI MORG-SAN LNDR #1 7/52 RPR STRT | CONCORD | ETL.2770.TOWR | 2022-06-30 | 2022-06-07 | 2023-09-13 | On-Time |  | 2025-06-07 | 2025-06-07 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45699151 | T3 DI MORAGA-SAN LANDR #1- 7/52 RPR STRT | ICQ
LC | 129034566 | 025/225 | T2 EI DELTA-CTTNWD 25/225 RMV DEBRIS | TABLEMTN | ETL.1240.POLE.STPS | 2024-06-07 | 2024-06-07 | 2025-02-04 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Wood | Remove | 46383874 | T2 EI DELTA-CTTNWD 25/225 RMV DEBRIS | ICW
LC | 129035014 | 026/317C | T2 EI DRUM-SUMMIT #2 26/317C RPR INSW | SACTO | ETL.1450.INSL.NCER | 2024-06-07 | 2024-06-07 | 2024-06-23 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46273429 | T2 EI DRUM-SUMMIT #2 26/317C RPR INSW | ICW
LC | 129035161 | 040/347 | T2 DELTA-COTTONWOOD 40/347R RPR GYWW | TABLEMTN | ETL.1240.POLE.STPS | 2024-06-07 | 2024-06-07 | 2025-04-09 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46383875 | T2 EI DELTA-COTTONWOOD 40/347R RPR GYWW | ICW
LC | 129035789 | 009/103 | T2 DRUM-SUMMIT #2 009/103 RPL INSS | SACTO | ETL.1450.INSL | 2024-06-07 | 2024-06-07 | 2024-06-07 | Past Due |  | 2025-06-07 | 2025-06-07 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570802 | T2 EI DRUM-SUMMIT #2 009/103 RPL INSS | 93K
LC | 129035881 | 009/103 | T2NT EI DRUM-SUMMIT #2 09/103 INST ACG | SACTO | ETL.1450.TOWR | 2024-06-07 | 2024-06-07 | 2025-03-25 | On-Time |  | 2027-06-07 | 2025-06-07 | 988 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Anti-Climbing Guard | Structure-Tower | Install | 31712719 | T2NT EI DRUM-SUMMIT #2 09/103 INST ACG | 93A
LC | 129036240 | 016/087 | T2 ROUND MTN-TBLE MTN #1 16/087 COTTER | TABLEMTN | ETL.6060.INSL | 2024-06-07 | 2024-06-07 | 2025-01-22 | On-Time |  | 2025-06-07 | 2025-06-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46306309 | T2 ROUND MTN-TBLE MTN #1 16/087 COTTER | ICS
LC | 129036254 | 006/046 | T2 RE COTTONWOOD #1 6/46 RPL INSS | TABLEMTN | ETL.6620.INSL.CERA | 2024-06-07 | 2024-06-07 | 2025-06-02 | On-Time |  | 2025-06-07 | 2025-06-07 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569574 | T2 DI COTTONWOOD#1 RPL INSS 4 TWRS | 93K
LC | 129036404 | 000/008A | T2 WV COLGATE-SMRTVL #1 0/8A RPL DMPW | SACTO | ETL.6510.INSL.NCER | 2024-06-07 | 2024-06-07 | 2025-01-09 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46337420 | T2 WV COLGATE-SMRTVL #1 0/8A RPL DMPW | ICW
LC | 129036406 | 005/011 | T2 EI CHOWCHILLA-KERCKHOFF 5/11 COTTER | FRESNO | ETL.1250.POLE.NWOD | 2024-06-07 | 2024-06-07 | 2024-10-16 | On-Time |  | 2024-12-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46265371 | T2 EI CHOWCHILLA-KERCKHOFF 5/11 COTTER | ICS
LC | 129036866 | 012/251 | T2 DI CTNWD RED BLUF 12/251 RPR GYWW | TABLEMTN | ETL.6660.POLE.NWOD | 2024-06-07 | 2024-06-07 | 2025-01-10 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311152 | T2 DI CTNWD RED BLUF 12/251 RPR GYWW | ICW
LC | 129036917 | :000/004 | T2 ROCK CREEK-POE :000/004 RMV VEG | TABLEMTN | ETL.5630.TOWR | 2024-06-07 | 2024-06-07 | 2024-06-07 | Past Due |  | 2025-06-07 | 2025-06-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129036963 | 025/219 | T2 EI DELTA-COTTONWOOD 25/219L RMV DBRS | TABLEMTN | ETL.1240.POLE.STPS | 2024-06-07 | 2024-06-07 | 2025-02-07 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Wood | Remove | 46383876 | T2 EI DELTA-COTTONWOOD 25/219L RMV DBRS | ICW
LC | 129036985 | 025/219 | T2 DELTA-CTTNWD 25/219R TOUCH | TABLEMTN | ETL.1240.POLE.STPS | 2024-06-07 | 2024-06-07 | 2024-06-07 | Past Due |  | 2024-12-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46486741 | T2 EI DELTA-CTTNWD 25/219R TOUCH | ICW
LC | 129037131 | 008/110 | T2 EI WTSNVILLE-SALINAS 08/110 RPR GYWW | MOSSLNDG | ETL.8310.POLE.WOOD | 2024-06-07 | 2024-06-07 | 2025-02-28 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391196 | T2 EI WTSNVILLE-SALINAS 08/110 RPR GYWW | ICW
LC | 129037132 | 009/112 | T2 EI WTSNVILLE-SALINAS 09/112 RPR GYWW | MOSSLNDG | ETL.8310.POLE.WOOD | 2024-06-07 | 2024-06-07 | 2025-02-28 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391198 | T2 EI WTSNVILLE-SALINAS 09/112 RPR GYWW | ICW
LC | 129037150 | 024/289A | T2 DRUM-SUMMIT #2 24/289A RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-06-07 | 2024-06-07 | 2025-05-02 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46325984 | T2 EI DRUM-SUMMIT #2 24/289A RPR GYWW | ICW
LC | 129037273 | T002/011 | T2 WV TULUCAY-NAPA #1 T2/11 COMPLETE | LAKEVLLE | ETL.8180.INSL.CERA | 2024-06-07 | 2024-06-07 | 2024-06-07 | Past Due |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install
LC | 129037304 | 014/077 | T2 EI RND MTN-TBL MTN #2 14/77 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2024-06-07 | 2024-06-07 | 2025-01-16 | On-Time |  | 2025-06-07 | 2025-06-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129037305 | 014/076 | T2 EI RND MTN-TBL MTN #2 14/76 UNBURY | TABLEMTN | ETL.6070.TOWR | 2024-06-07 | 2024-06-07 | 2025-04-16 | On-Time |  | 2025-06-07 | 2025-06-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46382036 | T2 EI RND MTN-TBL MTN #2 14/76 UNBURY | ICQ
LC | 129037422 | 035/157 | T2 MTCLF-MSS LNDNG #1 35/157 TOUCH | MOSSLNDG | ETL.5100.TOWR | 2024-06-07 | 2024-06-07 | 2024-06-07 | Past Due |  | 2024-12-07 | 2025-06-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476007 | T2 MTCLF-MSS LNDNG #1 35/157 TOUCH | ICQ
LC | 129037484 | 015/111B | T2 EI HELMS-GREGG #2 015/111B RMV NEST | FRESNO | ETL.4880.TOWR | 2024-06-07 | 2024-06-07 | 2025-04-10 | On-Time |  | 2025-06-07 | 2025-06-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCM COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46297931 | T2 EI HELMS-GREGG #2 015/111B RMV NEST | ICS
LC | 129037827 | 065/274 | T2 EI RND MTN-TBL MTN #1 65/274 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-06-07 | 2024-06-07 | 2025-01-23 | On-Time |  | 2025-06-07 | 2025-06-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306310 | T2 EI RND MTN-TBL MTN #1 65/274 RMV NEST | ICS
LC | 129037848 | 059/429 | T2 BRIDGVIL-COTONWD 59/429 COMPLETE | TABLEMTN | ETL.1110.TOWR | 2024-06-07 | 2024-06-07 | 2025-04-07 | On-Time |  | 2025-06-07 | 2025-06-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46353975 | T2 EI BRIDGVIL-COTONWD 59/429 BNT STEEL | ICQ
LC | 129037871 | 061/444 | T2NT EI BRIDGEVIL-COTONWD 61/444 RMV VEG | TABLEMTN | ETL.1110.TOWR | 2024-06-07 | 2024-06-07 | 2025-03-03 | On-Time |  | 2027-06-07 | 2025-06-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 129037873 | 061/446 | T2NT EI BRIDGVIL-COTONWOD 62/447 RMV VEG | TABLEMTN | ETL.1110.TOWR | 2024-06-07 | 2024-06-07 | 2024-06-07 | On-Time |  | 2027-06-07 | 2025-06-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129038139 | 028/211 | T2 EI MSR FLT-GLD HLL #2 28/211 RPL INSS | SACTO | ETL.2670.INSL.NCER | 2024-06-08 | 2024-06-07 | 2024-06-07 | Past Due |  | 2025-06-07 | 2025-06-07 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570810 | T2 EI MSR FLT-GLD HLL #2 28/211 RPL INSS | 93K
LC | 129054540 | :004/026 | T2 DI ROCK CREEK-POE :4/26 RPR JUMS | TABLEMTN | ETL.5630.INSL.CERA | 2024-06-10 | 2024-06-07 | 2025-04-26 | On-Time |  | 2025-06-07 | 2025-06-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46268460 | T2 DI ROCK CREEK-POE :4/26 RPR JUMP | ICS
LC | 129055192 | 006/017 | T2 DI TULUCAY-NAPA #1 06/17 RPR GYWW | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-06-10 | 2024-06-07 | 2025-03-24 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46403774 | T2 DI TULUCAY-NAPA #1 06/17 RPR GYWW | ICW
LC | 129055193 | 006/017 | T2NT DI TULUCAY-NAPA #1 06/17 RMV VEG | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-06-10 | 2024-06-07 | 2024-06-07 | Past Due |  | 2027-06-07 | 2025-06-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129055252 | 024/176 | T2 DI CARIBOU-TBL MNTN 24/176 COTR KEY | TABLEMTN | ETL.4440.INSL.CERA | 2024-06-10 | 2024-06-07 | 2025-04-02 | On-Time |  | 2025-06-07 | 2025-06-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46337591 | T2 DI CARIBOU-TBL MNTN 24/176 COTR KEY | ICS
LC | 129229937 | A008/168 | T2 DI CSCD-BNTN-DSCHTS A008/168 RPR INSW | TABLEMTN | ETL.6310.INSL.NCER | 2024-07-16 | 2024-06-07 | 2025-04-07 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator-Wood | Repair | 46383921 | T2 DI CSCD-BNTN-DSCHTS A008/168 RPR INSW | ICW
LC | 129230056 | 014/106 | T2 DI CARIBOU-TABLE MTN 14/106 RPR FOND | TABLEMTN | ETL.4440.TOWR | 2024-07-16 | 2024-06-07 | 2025-02-18 | On-Time |  | 2025-06-07 | 2025-06-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46354077 | T2 DI CARIBOU-TABLE MTN 14/106 RPR FOND | ICQ
LC | 129230101 | 020/400 | T2 DI COLGATE-PALERMO 20/400 RPL POLE | TABLEMTN | ETL.6500.POLE.WOOD | 2024-07-16 | 2024-06-07 | 2025-05-20 | On-Time |  | 2025-06-07 | 2025-06-07 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572929 | T2 DI COLGATE-PALERMO 20/400 RPL POLE | 70Y
LC | 129230217 | 013/266 | T2 DI COLGATE-PALERMO 13/266 RPR STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-07-16 | 2024-06-07 | 2025-02-07 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401132 | T2 DI COLGATE-PALERMO 13/266 RPR STRW | ICW
LC | 129230280 | 021/432 | T2 DI COLGATE-PALERMO 21/432 RPR STRW | SACTO | ETL.6500.POLE.NWOD | 2024-07-16 | 2024-06-07 | 2025-02-07 | On-Time |  | 2024-12-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46463504 | T2 DI COLGATE-PALERMO 21/432 RPR STRW | ICW
LC | 129230281 | 021/432 | T2 DI COLGATE-PALERMO 21/432 RPR CNDW | TABLEMTN | ETL.6500.INSL.NCER | 2024-07-16 | 2024-06-07 | 2025-02-07 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46401135 | T2 DI COLGATE-PALERMO 21/432 RPR CNDW | ICW
LC | 129245290 | 003/029 | T2 DI MORAGA-OAKLAND #3 3/29 RPR FOND | CONCORD | ETL.2740.TOWR | 2024-07-19 | 2024-06-07 | 2025-01-17 | On-Time |  | 2025-06-07 | 2025-06-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46289385 | T2 DI MORAGA-OAKLAND #3 3/29 INSP FOND | ICQ
LC | 129245341 | 008/000 | T2 DI TULUCAY-NAPA #1 8/000 RPR STRW | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-07-19 | 2024-06-07 | 2025-04-30 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46403777 | T2 DI TULUCAY-NAPA #1 8/000 RPR STRW | ICW
LC | 129245455 | 048/346 | T2 DI CARIBOU-TBL MTN 048/346 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2024-07-19 | 2024-06-07 | 2025-05-28 | On-Time |  | 2025-06-07 | 2025-06-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Structure-Tower | Repair | 46310433 | T2 DI CARIBOU-TBL MTN 048/346 RPR STRT | ICQ
LC | 129246862 | 007/000 | T2NT DI TULUCAY NAPA #1 07/000 RMV VEG | LAKEVLLE | ETL.8180.POLE.NWOD | 2024-07-19 | 2024-06-07 | 2024-06-07 | Past Due |  | 2027-06-07 | 2025-06-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129246990 | 008/054 | T2 COTTONWOOD #1 008/054 RPR INSS | TABLEMTN | ETL.6620.INSL.NCER | 2024-07-19 | 2024-06-07 | 2025-06-02 | On-Time |  | 2025-06-07 | 2025-06-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46416149 | T2 DI COTTONWOOD #1 008/054 RPR INSS | ICS
LC | 129247103 | 025/302A | T2 DI DRUM-SUMMIT #2 025/302A RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-07-19 | 2024-06-07 | 2025-05-02 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458344 | T2 DI DRUM-SUMMIT #2 025/302A RPR GYWW | ICW
LC | 129247207 | 001/011 | T2 DI MNDCNO-WLTS-FRT BRG 1/11 RPR IBWW | WILLITS | ETL.7550.INSL.CERA | 2024-07-19 | 2024-06-07 | 2025-01-21 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46310527 | T2 DI MNDCNO-WLTS-FRT BRG 1/11 RPR IBWW | ICW
LC | 129247255 | 19 | T2 DI SMARTVILLE-NICOLS#1 7/134 RPR SWTC | SACTO | ETL.7990.SWIT | 2024-07-19 | 2024-06-07 | 2025-05-27 | On-Time |  | 2025-06-07 | 2025-06-07 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Out of Adjustment | Switch | Repair | 46310367 | T2 DI SMARTVILLE-NICOLS#1 7/134 RPR SWTC | ICE
LC | 129247257 | 19 | T2 DI SMARTVILLE-NICOLS#1 7/134 RPR JUMS | SACTO | ETL.7990.SWIT | 2024-07-19 | 2024-06-07 | 2025-05-27 | On-Time |  | 2025-06-07 | 2025-06-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Steel | Repair | 46310253 | T2 DI SMARTVILLE-NICOLS#1 7/134 RPR JUMS | ICS
LC | 129248954 | 018/218B | T2 DI DRUM-SUMMIT #1 18/218B RPR JUMW | SACTO | ETL.1440.INSL.NCER | 2024-07-19 | 2024-06-07 | 2025-06-05 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46398022 | T2 DI DRUM-SUMMIT #1 018/218B RPR JMPW | ICW
LC | 129250108 | 008/143 | T2 DI PIT#1-HAT CK#2-BRNY 8/143 RPR STRW | TABLEMTN | ETL.7040.POLE.WOOD | 2024-07-19 | 2024-06-07 | 2025-05-21 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46454366 | T2 DI PIT#1-HAT CK#2-BRNY 8/143 RPR STRW | ICW
LC | 129250118 | 015/302 | T2 HAT CREEK #1 WESTWOOD 15/302 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-07-19 | 2024-06-07 | 2025-05-17 | On-Time |  | 2025-06-07 | 2025-06-07 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574753 | T2 DI HAT CREEK #1 WSTWD 15/302 RPL POLE | 70Y
LC | 129274457 | 012/245 | T2 DI COLGATE-PALERMO 12/245 TOUCH | TABLEMTN | ETL.6500.POLE.NWOD | 2024-07-22 | 2024-06-07 | 2025-03-03 | On-Time |  | 2024-12-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46463547 | T2 DI COLGATE-PALERMO 12/245 RPR STRW | ICW
LC | 129280315 | :009/050 | T2 DI CRAZY HORSE CANYON 9/50 TOUCH | MOSSLNDG | ETL.2900.TOWR | 2024-07-23 | 2024-06-07 | 2025-03-12 | On-Time |  | 2024-12-07 | 2025-06-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476013 | T2 DI CRAZY HORSE CANYON 9/50 TOUCH | ICQ
LC | 129280316 | :009/050 | T2 DI CRAZY HORSE CANYON-9/50 BNT STEEL | MOSSLNDG | ETL.2900.TOWR | 2024-07-23 | 2024-06-07 | 2025-05-22 | On-Time |  | 2025-06-07 | 2025-06-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416717 | T2 DI CRAZY HORSE CANYON-9/50 BNT STEEL | ICQ
LC | 129284944 | 024/290A | T2 DI DRUM-SUMMIT #1 24/290A RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-07-24 | 2024-06-07 | 2025-05-02 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46401361 | T2 DI DRUM-SUMMIT #1 24/290A RPR GYWW | ICW
LC | 129391209 | 015/156 | T2 DI IGNACIO-ALTO 015/156 RPR INSW | LAKEVLLE | ETL.7150.INSL.NCER | 2024-08-15 | 2024-06-07 | 2025-02-05 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46403778 | T2 DI IGNACIO-ALTO 015/156 RPR INSW | ICW
LC | 129393618 | 014/107C | T2 DI CARIBOU TBL MTN 14/107C RPR GYWT | TABLEMTN | ETL.4440.POLE.NWOD | 2024-08-15 | 2024-06-07 | 2025-02-19 | On-Time |  | 2025-06-07 | 2025-06-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46337220 | T2 DI CARIBOU TBL MTN 14/107C RPR GYWT | ICQ
LC | 129393732 | 014/170 | T2 DI ELK CREEK TAP 14/170 RPL DMPW | TABLEMTN | ETL.6921.INSL.NCER | 2024-08-15 | 2024-06-07 | 2025-05-30 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46383925 | T2 DI ELK CREEK TAP 14/170 RPL DMPW | ICW
LC | 129394208 | B024/554 | T2 DI DRM-GRS VLY-WMR B24/554 RPR INSW | SACTO | ETL.6760.INSL.CERA | 2024-08-15 | 2024-06-07 | 2024-11-09 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46387783 | T2 DI DRM-GRS VLY-WMR B24/554 RPR INSW | ICW
LC | 129394412 | 008/140 | T2 DI PIT #1 HAT CRK #2 8/140 RMV VEGN | TABLEMTN | ETL.7040.POLE.WOOD | 2024-08-15 | 2024-06-07 | 2025-02-06 | On-Time |  | 2025-06-07 | 2025-06-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129394685 | A007/158 | T2 DI CSCD BNT DSCHTS A7/158 RPR STRW | TABLEMTN | ETL.6310.POLE.WOOD | 2024-08-15 | 2024-06-07 | 2025-04-07 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46383927 | T2 DI CSCD BNT DSCHTS A7/158 RPR STRW | ICW
LC | 129394783 | 007/002 | T2 DI TULUCAY NAPA #1 7/2 RPR ANCW | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-08-15 | 2024-06-07 | 2025-01-20 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46401529 | T2 DI TULUCAY NAPA #1 7/2 RPR ANCW | ICW
LC | 129394784 | 007/002 | T2 DI TULUCAY NAPA #1 7/2 RMV VEGN | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-08-15 | 2024-06-07 | 2025-05-20 | On-Time |  | 2025-06-07 | 2025-06-07 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129408361 | 024/179 | T2 DI CARIBOU-TABLE MTN 024/179 RPR JMPS | TABLEMTN | ETL.4440.INSL.CERA | 2024-08-19 | 2024-06-07 | 2024-12-20 | On-Time |  | 2024-09-07 | 2025-06-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46328459 | T2 DI CARIBOU-TABLE MTN 024/179 RPR JMPS | ICS
LC | 129409552 | 024/175 | T2 DI CARIBOU-TBL MTN 24/175 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2024-08-19 | 2024-06-07 | 2025-05-27 | On-Time |  | 2025-06-07 | 2025-06-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46337228 | T2 DI CARIBOU-TBL MTN 24/175 RPR STRT | ICQ
LC | 129410948 | :010/055 | T2 DI CHC-SLNS-SLDAD#1 10/55 RPL RPTS | MOSSLNDG | ETL.2900.TOWR | 2024-08-20 | 2024-06-07 | 2025-04-09 | On-Time |  | 2025-06-07 | 2025-06-07 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46393863 | T2 DI CHC-SLNS-SLDAD#1 10/55 RPL RPTS | ICB
LC | 129419983 | 007/133 | T2 DI SMRTVL NCLUS#1 07/133 RPR INSW | SACTO | ETL.7990.INSL.NCER | 2024-08-21 | 2024-06-07 | 2025-02-10 | On-Time |  | 2025-06-07 | 2025-06-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCH COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46354475 | T2 DI SMRTVL NCLUS#1 07/133 RPR INSW | ICW
LC | 129510325 | 013/101 | T2 DI CARIBOU-TB MT 13/101 RPR FOND | TABLEMTN | ETL.4440.TOWR | 2024-09-10 | 2024-06-07 | 2025-04-02 | On-Time |  | 2024-12-07 | 2025-06-07 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46338969 | T2 DI CARIBOU-TB MT 13/101 RPR FOND | ICQ
LC | 123816711 | 047/234 | T2NT DI MALIN-RND MTN #2 47/234 RPR GYWS | TABLEMTN | ETL.6020.TOWR | 2022-06-10 | 2022-06-08 | 2023-09-11 | On-Time |  | 2025-06-08 | 2025-06-08 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45650743 | T2 DI MALIN-ROUND MTN #2 47/234 RPR GYWS | ICS
LC | 123832637 | 048/240 | T2NT DI MLN RD MN #2 48/240 RPR GYWS | TABLEMTN | ETL.6020.TOWR | 2022-06-13 | 2022-06-08 | 2023-09-11 | On-Time |  | 2025-06-08 | 2025-06-08 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45650741 | T2 DI MLN RND MTN #2 48/240 RPR GYWS | ICS
LC | 123852159 | 026/126 | T2 DI CORTINA-MENDO #1 26/126 BENT STEEL | WILLITS | ETL.1330.TOWR | 2022-06-15 | 2022-06-08 | 2023-05-23 | On-Time |  | 2023-06-08 | 2025-06-08 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Structure-Tower | Repair | 45644804 | T2 DI CORTINA-MENDO #1 26/126 BENT STEEL | ICQ
LC | 129038177 | 009/105B | T2 EI DRUM-SUMMIT #2 009/105B RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-06-08 | 2024-06-08 | 2024-06-16 | On-Time |  | 2024-09-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46265941 | T2 EI DRUM-SUMMIT #2 009/105B RPR GYWW | ICW
LC | 129038222 | 009/105A | T2 EI DRM-SMIT #2 9/105A RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-06-08 | 2024-06-08 | 2024-06-16 | On-Time |  | 2024-09-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46265940 | T2 EI DRM-SMIT #2 9/105A RPR GYWW | ICW
LC | 129038607 | 001/029 | T2 EI APPLE HILL #2 TAP 01/029 RMV VEG | SACTO | ETL.1541.POLE.NWOD | 2024-06-08 | 2024-06-08 | 2025-01-07 | On-Time |  | 2025-06-08 | 2025-06-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129038639 | 001/030 | T2 EI APPLE HILL #2 TAP 01/030 RMV VEG | SACTO | ETL.1541.POLE.WOOD | 2024-06-08 | 2024-06-08 | 2025-01-07 | On-Time |  | 2025-06-08 | 2025-06-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129038770 | 004/003 | T2 EI MENDOCINO-WILLITS 04/003 RPR GYWW | WILLITS | ETL.7540.POLE.NWOD | 2024-06-08 | 2024-06-08 | 2024-11-27 | On-Time |  | 2024-12-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46264538 | T2 EI MENDOCINO-WILLITS 04/003 RPR GYWW | ICW
LC | 129038786 | 011/091 | T2 EI TIGER CREEK-ELCTRA 11/91 RMV VEG | VICTOR | ETL.5780.TOWR | 2024-06-08 | 2024-06-08 | 2024-06-08 | Past Due |  | 2025-06-08 | 2025-06-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 129038976 | 000/004 | T2 EI HAT CREEK #1-PIT #1 0/4 RMV VEG | TABLEMTN | ETL.7020.TOWR | 2024-06-08 | 2024-06-08 | 2025-01-14 | On-Time |  | 2025-06-08 | 2025-06-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129038983 | 001/010 | T2 PIT #1-COTTONWD 1/10 RPR CNDS | TABLEMTN | ETL.5390.INSL.NCER | 2024-06-08 | 2024-06-08 | 2025-04-21 | On-Time |  | 2025-06-08 | 2025-06-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Conductor-Steel | Repair | 46452751 | T2 PIT #1-COTTONWD 1/10 RPR CNDS | ICS
LC | 129038995 | 011/095 | T2 EI CRESTA-RIO OSO 11/95 CGI | TABLEMTN | ETL.4590.TOWR | 2024-06-08 | 2024-06-08 | 2025-04-18 | On-Time |  | 2024-09-08 | 2025-06-08 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 129038997 | 009/081 | T2 EI CRESTA-RIO OSO 9/81 CGI | TABLEMTN | ETL.4590.TOWR | 2024-06-08 | 2024-06-08 | 2025-04-18 | On-Time |  | 2024-09-08 | 2025-06-08 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 129039000 | 011/094 | T2 EI CRESTA-RIO OSO 11/94 CGI | TABLEMTN | ETL.4590.TOWR | 2024-06-08 | 2024-06-08 | 2025-04-18 | On-Time |  | 2024-09-08 | 2025-06-08 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 129039002 | 011/096 | T2 EI CRESTA-RIO OSO 11/96 CGI | TABLEMTN | ETL.4590.TOWR | 2024-06-08 | 2024-06-08 | 2025-04-18 | On-Time |  | 2024-09-08 | 2025-06-08 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 129039003 | 011/093 | T2 EI CRESTA-RIO OSO 11/93 CGI | TABLEMTN | ETL.4590.TOWR | 2024-06-08 | 2024-06-08 | 2025-04-18 | On-Time |  | 2024-09-08 | 2025-06-08 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 129039010 | 010/086 | T2 EI CRESTA-RIO OSO 10/86 CGI | TABLEMTN | ETL.4590.TOWR | 2024-06-08 | 2024-06-08 | 2025-04-18 | On-Time |  | 2024-09-08 | 2025-06-08 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 129039121 | 005/000 | T2 EI MENDOCINO-WILLITS 05/00 RMV NEST | WILLITS | ETL.7540.POLE.NWOD | 2024-06-08 | 2024-06-08 | 2025-01-07 | On-Time |  | 2025-06-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Wood | Remove | 46310528 | T2 EI MENDOCINO-WILLITS 05/00 RMV NEST | ICW
LC | 129039122 | 013/095B | T2 EI HELMS-GREGG #2 13/095B REGRADE | FRESNO | ETL.4880.TOWR | 2024-06-08 | 2024-06-08 | 2025-01-15 | On-Time |  | 2025-06-08 | 2025-06-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46297903 | T2 EI HELMS-GREGG #2 13/095B REGRADE | ICQ
LC | 129049867 | 059/432 | T2 EI BRIDGEVILLE-COTTONWOOD 59/432 CGI | TABLEMTN | ETL.1110.TOWR | 2024-06-10 | 2024-06-08 | 2025-04-21 | On-Time |  | 2024-09-08 | 2025-06-08 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 129054852 | 018/581 | T2 DI SPAULDING-SUMMIT 18/581 RPL INSW | SACTO | ETL.8060.INSL.NCER | 2024-06-10 | 2024-06-08 | 2024-07-30 | On-Time |  | 2025-06-08 | 2025-06-08 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35560426 | T2 DI SPAULDING-SUMMIT 18/581 RPL INSW | 93I
LC | 129055256 | 009/103 | T2 DRUM-SUMMIT #2 09/103 RPR STRT | SACTO | ETL.1450.TOWR | 2024-06-10 | 2024-06-08 | 2025-03-25 | On-Time |  | 2025-06-08 | 2025-06-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46381462 | T2 DI DRUM-SUMMIT #2 09/103 RPR STRT | ICQ
LC | 129061299 | 007/050 | T2 RE COTTONWOOD #1 07/50 RPL INSS | TABLEMTN | ETL.6620.INSL.CERA | 2024-06-11 | 2024-06-08 | 2025-06-02 | On-Time |  | 2025-06-08 | 2025-06-08 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569574 | T2 DI COTTONWOOD#1 RPL INSS 4 TWRS | 93K
LC | 129061346 | 026/308 | T2 DI DRUM SUMMIT #1 26/308C RPL ANCW | SACTO | ETL.1440.POLE.WDPS | 2024-06-11 | 2024-06-08 | 2025-06-08 | On-Time |  | 2025-06-08 | 2025-06-08 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586898 | T2 DI DRM-SMMT #1 27/318L RPL ANCW | 93E
LC | 129061347 | 026/308 | T2 DI DRUM SUMMIT #1 26/308R RPL ANCW | SACTO | ETL.1440.POLE.WDPS | 2024-06-11 | 2024-06-08 | 2024-06-08 | Past Due |  | 2025-06-08 | 2025-06-08 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW ACCH COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586898 | T2 DI DRM-SMMT #1 27/318L RPL ANCW | 93E
LC | 129061720 | 57 | T2 DI DRUM-SPLDNG 9/239 SW#57 COTTER | SACTO | ETL.6770.SWIT | 2024-06-11 | 2024-06-08 | 2024-06-08 | Past Due |  | 2024-12-08 | 2025-06-08 | 623 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | Out of Adjustment | Switch | Repair | 46517406 | T2 DI DRUM-SPLDNG 9/239 SW#57 COTTER | ICE
LC | 129067333 | 329 | T2 DI EL DRDO MSURI FLT#2 4/31 RPR SWTC | SACTO | ETL.1540.SWIT | 2024-06-12 | 2024-06-08 | 2024-09-25 | On-Time |  | 2024-09-08 | 2025-06-08 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | Out of Adjustment | Switch | Repair | 46327655 | T2 DI EL DRDO MSURI FLT#2 4/31 RPR SWTC | ICE
LC | 129067334 | 317 | T2 DI EL DRDO MSURI FLT#1 4/31 RPR SWTC | SACTO | ETL.1530.SWIT | 2024-06-12 | 2024-06-08 | 2024-09-21 | On-Time |  | 2024-09-08 | 2025-06-08 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | Out of Adjustment | Switch | Repair | 46266043 | T2 DI EL DRDO MSURI FLT#1 4/31 RPR SWTC | ICE
LC | 129067335 | 004/031 | T2 DI APPLE HILL #2 TAP 4/31 RPR INSS | SACTO | ETL.1541.INSL.CERA | 2024-06-12 | 2024-06-08 | 2024-09-25 | On-Time |  | 2025-06-08 | 2025-06-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46327656 | T2 DI APPLE HILL #2 TAP 4/31 RPR INSS | ICS
LC | 129067433 | 013/271 | T2 DI COLGATE-PALERMO 13/271 RPR GYWW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-06-12 | 2024-06-08 | 2025-02-07 | On-Time |  | 2025-06-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46398068 | T2 DI COLGATE-PALERMO 13/271 RPR GYWW | ICW
LC | 129067763 | 007/049 | T2 RE COTTONWOOD#1 07/049 RPL INSS | TABLEMTN | ETL.6620.INSL.CERA | 2024-06-12 | 2024-06-08 | 2025-06-02 | On-Time |  | 2025-06-08 | 2025-06-08 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569574 | T2 DI COTTONWOOD#1 RPL INSS 4 TWRS | 93K
LC | 129230245 | 014/276 | T2 DI COLGATE-PALERMO 14/276 RPR CNDW | TABLEMTN | ETL.6500.INSL.NCER | 2024-07-16 | 2024-06-08 | 2025-02-07 | On-Time |  | 2025-06-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46401134 | T2 DI COLGATE-PALERMO 14/276 RPR CNDW | ICW
LC | 129235753 | 017/546 | T2 SPAULDING-SUMMIT 017/546 RPL STRW | SACTO | ETL.8060.POLE.WOOD | 2024-07-17 | 2024-06-08 | 2024-06-08 | Past Due |  | 2025-06-08 | 2025-06-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572882 | T2 DI SPAULDING-SUMMIT 017/546 RPL STRW | 70Y
LC | 129235926 | 018/222B | T2 DRUM-SUMMIT #2 18/222B RPL ANCW | SACTO | ETL.1450.POLE.NWOD | 2024-07-17 | 2024-06-08 | 2025-06-17 | Past Due |  | 2025-06-08 | 2025-06-08 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573632 | T2 EI DRUM-SUMMIT #2 RPL ANCW 4 STRT | 93E
LC | 129235942 | 018/222C | T2 DRUM-SUMMIT #2 18/222C COMPLETE | SACTO | ETL.1450.POLE.NWOD | 2024-07-17 | 2024-06-08 | 2025-04-30 | On-Time |  | 2025-06-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458339 | T2 DI DRUM-SUMMIT #2 18/222C RPR GYWW | ICW
LC | 129235952 | 005/105 | T2 DI COLGATE-PALERMO 5/105 RPL STRW | SACTO | ETL.6500.POLE.WOOD | 2024-07-17 | 2024-06-08 | 2025-03-26 | On-Time |  | 2025-06-08 | 2025-06-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572922 | T2 DI COLGATE-PALERMO 5/105 RPL STRW | 70Y
LC | 129236086 | 017/528 | T2 SPAULDING-SUMMIT 17/528 RPL STRW | SACTO | ETL.8060.POLE.WOOD | 2024-07-17 | 2024-06-08 | 2024-06-08 | Past Due |  | 2025-06-08 | 2025-06-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572881 | T2 DI SPAULDING-SUMMIT 17/528 RPL STRW | 70Y
LC | 129236111 | 026/191 | T2 DI CARIBOU-TBLE MNT 26/191 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2024-07-17 | 2024-06-08 | 2025-05-28 | On-Time |  | 2025-06-08 | 2025-06-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46354079 | T2 DI CARIBOU-TBLE MNT 26/191 RPL HRDT | ICQ
LC | 129250069 | 000/012 | T2 DI CLGT-ALLEGHANY 000/012 RPR STRW | SACTO | ETL.6470.POLE.WOOD | 2024-07-19 | 2024-06-08 | 2025-05-06 | On-Time |  | 2025-06-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46404743 | T2 DI CLGT-ALLEGHANY 000/012 RPR STRW | ICW
LC | 129250102 | 012/237 | T2 DI COLGATE-PALERMO 12/237 RPL STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-07-19 | 2024-06-08 | 2025-05-01 | On-Time |  | 2025-06-08 | 2025-06-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572926 | T2 DI COLGATE-PALERMO 12/237 RPL STRW | 70Y
LC | 129274004 | 019/210 | T2 DI ELK CRK TAP 19/210 RPL ANCW | TABLEMTN | ETL.6921.POLE.NWOD | 2024-07-22 | 2024-06-08 | 2025-05-29 | On-Time |  | 2025-06-08 | 2025-06-08 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35631864 | T2 DI ELK CRK TAP 19/210 RPL ANCW | 93E
LC | 129274839 | 006/121 | T2 DI COLGATE-PALERMO 6/121 RPL STRW | SACTO | ETL.6500.POLE.WOOD | 2024-07-22 | 2024-06-08 | 2025-05-03 | On-Time |  | 2025-06-08 | 2025-06-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572924 | T2 DI COLGATE-PALERMO 6/121 RPL STRW | 70Y
LC | 129274859 | 009/062 | T2 DI COTTONWOOD #2 009/062 COTTER | TABLEMTN | ETL.6630.INSL.CERA | 2024-07-22 | 2024-06-08 | 2024-11-14 | On-Time |  | 2024-12-08 | 2025-06-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46306323 | T2 DI COTTONWOOD #2 009/062 COTTER | ICS
LC | 129292860 | :031/199 | T2 DI NTH TWR MTNZ JT#1 :31/199 RPR INSS | CONCORD | ETL.3130.INSL.NCER | 2024-07-26 | 2024-06-08 | 2025-02-14 | On-Time |  | 2025-06-08 | 2025-06-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46345727 | T2 DI NTH TWR MTNZ JT#1 :31/199 RPR INSS | ICS
LC | 129393278 | 017/545 | T2 DI SPAULDING SUMMIT 17/545 RPR INSW | SACTO | ETL.8060.INSL.NCER | 2024-08-15 | 2024-06-08 | 2025-05-31 | On-Time |  | 2025-06-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46401369 | T2 DI SPAULDING SUMMIT 17/545 RPR INSW | ICW
LC | 129393455 | 006/125 | T2 DI COLGATE PALERMO 6/125 RPL STRW | SACTO | ETL.6500.POLE.WOOD | 2024-08-15 | 2024-06-08 | 2025-05-04 | On-Time |  | 2025-06-08 | 2025-06-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586882 | T2 DI COLGATE PALERMO 6/125 RPL STRW | 70Y
LC | 129393507 | 027/321B | T2 DI DRUM-SUMMIT #2-27/321B RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-08-15 | 2024-06-08 | 2024-09-30 | On-Time |  | 2024-12-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46306362 | T2 DI DRUM-SUMMIT #2-27/321B RPR GYWW | ICW
LC | 129393549 | 003/081 | T2 DI CLGT-ALLGHNY 3/81 RPR INSW | SACTO | ETL.6470.INSL.NCER | 2024-08-15 | 2024-06-08 | 2025-05-05 | On-Time |  | 2025-06-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46404744 | T2 DI CLGT-ALLGHNY 3/81 RPR INSW | ICW
LC | 129393600 | 027/321C | T2 DI DRUM-SUMMIT #2-27/321C RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-08-15 | 2024-06-08 | 2024-09-30 | On-Time |  | 2024-12-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46306363 | T2 DI DRUM-SUMMIT #2-27/321C RPR GYWW | ICW
LC | 129393602 | 027/321C | T2 DI DRUM-SUMMIT #2 27/321C RPR JUMW | SACTO | ETL.1450.INSL.NCER | 2024-08-15 | 2024-06-08 | 2025-06-24 | Past Due |  | 2025-06-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Wood | Repair | 46458350 | T2 DI DRUM-SUMMIT #2 27/321C RPR JUMW | ICW
LC | 129393608 | :010/057 | T2 DI CHC-SALINAS-SOLDD :10/57 RPL RPTS | MOSSLNDG | ETL.2900.TOWR | 2024-08-15 | 2024-06-08 | 2025-04-09 | On-Time |  | 2025-06-08 | 2025-06-08 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46393854 | T2 DI CHC-SALINAS-SOLDD :10/57 RPL RPTS | ICB
LC | 129393702 | 017/554 | T2 DI SPAULDING-SUMMIT 17/554 RPR STRW | SACTO | ETL.8060.POLE.WOOD | 2024-08-15 | 2024-06-08 | 2025-05-31 | On-Time |  | 2025-06-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401376 | T2 DI SPAULDING-SUMMIT 17/554 RPR STRW | ICW
LC | 129393820 | 015/116 | T2 DI CARIBOU TBL MTN 15/116 RPR SHLD | TABLEMTN | ETL.4440.TOWR | 2024-08-15 | 2024-06-08 | 2025-04-02 | On-Time |  | 2025-06-08 | 2025-06-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46337603 | T2 DI CARIBOU TBL MTN 15/116 RPR SHLD | ICS
LC | 129393883 | 017/543 | T2 SPAULDING-SUMMIT 17/543 RPL INSW | SACTO | ETL.8060.INSL.NCER | 2024-08-15 | 2024-06-08 | 2024-06-08 | Past Due |  | 2025-06-08 | 2025-06-08 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35586953 | T2 DI SPAULDING-SUMMIT 17/543 RPL INSW | 93I
LC | 129394041 | 027/318 | T2 DRM-SMMT #1 27/318L RPL ANCW | SACTO | ETL.1440.POLE.WDPS | 2024-08-15 | 2024-06-08 | 2025-06-06 | On-Time |  | 2025-06-08 | 2025-06-08 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586898 | T2 DI DRM-SMMT #1 27/318L RPL ANCW | 93E
LC | 129394043 | 027/318 | T2 DRM-SMMT #1 27/318R RPR GYWW | SACTO | ETL.1440.POLE.WDPS | 2024-08-15 | 2024-06-08 | 2025-05-02 | On-Time |  | 2025-06-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46401378 | T2 DI DRM-SMMT #1 27/318R RPR GYWW | ICW
LC | 129394048 | 027/318 | T2 DI DRM-SMMT #1 27/318R RPR JUMW | SACTO | ETL.1440.INSL.NCER | 2024-08-15 | 2024-06-08 | 2024-11-18 | On-Time |  | 2024-09-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46306365 | T2 DI DRM-SMMT #1 27/318R RPR JUMW | ICW
LC | 129394101 | :011/061 | T2 CHC-SALINAS-SOLEDAD#1 :11/61 RPR STRT | MOSSLNDG | ETL.2900.TOWR | 2024-08-15 | 2024-06-08 | 2025-05-19 | On-Time |  | 2025-06-08 | 2025-06-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416771 | T2 DI CHC-SLNS-SLDAD#1 :11/61 RPR STRT | ICQ
LC | 129394104 | 025/304 | T2 DRUM-SUMMIT #2 25/304C CNCL | SACTO | ETL.1450.POLE.STPS | 2024-08-15 | 2024-06-08 | 2024-06-08 | Past Due |  | 2025-06-08 | 2025-06-08 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586900 | T2 DI DRUM-SUMMIT #2 25/304C RPL ANCW | 93E
LC | 129394108 | 025/304 | T2 DRUM-SUMMIT #2 25/304L CNCL | SACTO | ETL.1450.POLE.STPS | 2024-08-15 | 2024-06-08 | 2024-06-08 | Past Due |  | 2025-06-08 | 2025-06-08 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586900 | T2 DI DRUM-SUMMIT #2 25/304C RPL ANCW | 93E
LC | 129394128 | 007/126 | T2 DI CLGT-PLRMO 7/126 RPL STRW | SACTO | ETL.6500.POLE.WOOD | 2024-08-15 | 2024-06-08 | 2025-05-04 | On-Time |  | 2025-06-08 | 2025-06-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586883 | T2 DI CLGT-PLRMO 7/126 RPL STRW | 70Y
LC | 129394285 | 012/235 | T2 DI COLGATE-PALERMO 12/235 RPR STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-08-15 | 2024-06-08 | 2025-03-24 | On-Time |  | 2025-06-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401380 | T2 DI COLGATE-PALERMO 12/235 RPR STRW | ICW
LC | 129394310 | 025/303 | T2 DRUM-SUMMIT #1 25/303L RPR STRW | SACTO | ETL.1440.POLE.WDPS | 2024-08-15 | 2024-06-08 | 2024-06-08 | Past Due |  | 2025-06-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46545123 | T2 DRUM-SUMMIT #1 25/303L RPR STRW | ICW
LC | 129394317 | 026/190 | T2 DI CARIBOU-TBL MTN 26/190 INS DAMS | TABLEMTN | ETL.4440.INSL.CERA | 2024-08-15 | 2024-06-08 | 2025-04-06 | On-Time |  | 2025-06-08 | 2025-06-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR NTDE | Missing | Damper-Steel | Install | 46337604 | T2 DI CARIBOU-TBL MTN 26/190 INS DAMS | ICS
LC | 129394975 | 006/122 | T2 DI COLGATE-PALERMO 6/122 TOUCH | SACTO | ETL.6500.POLE.NWOD | 2024-08-15 | 2024-06-08 | 2025-03-25 | On-Time |  | 2024-12-08 | 2025-06-08 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46463503 | T2 DI COLGATE-PALERMO 06/122 RPR STRW | ICW
LC | 129410099 | 027/318 | T2 DRUM-SMMT #1 27/318C RPL ANCW | SACTO | ETL.1440.POLE.WDPS | 2024-08-20 | 2024-06-08 | 2025-06-06 | On-Time |  | 2025-06-08 | 2025-06-08 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586898 | T2 DI DRM-SMMT #1 27/318L RPL ANCW | 93E
LC | 129410322 | 027/318 | T2 DRM-SMMT #1 27/318R RPL ANCW | SACTO | ETL.1440.POLE.WDPS | 2024-08-20 | 2024-06-08 | 2025-06-06 | On-Time |  | 2025-06-08 | 2025-06-08 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586898 | T2 DI DRM-SMMT #1 27/318L RPL ANCW | 93E
LC | 129425763 | 008/040A | T2 DI CNTRA CNSTA MRGA #2 8/40A RMV NEST | CONCORD | ETL.5453.POLE.NWOD | 2024-08-22 | 2024-06-08 | 2025-01-15 | On-Time |  | 2025-06-08 | 2025-06-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46404324 | T2 DI CNTRA CNSTA MRGA #2 8/40A RMV NEST | ICS
LC | 129425764 | 008/040A | T2 DI CNTRA CNSTA MRGA #2 8/40A RPL HRDT | CONCORD | ETL.5453.POLE.NWOD | 2024-08-22 | 2024-06-08 | 2025-04-02 | On-Time |  | 2025-06-08 | 2025-06-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46339800 | T2 DI CNTRA CNSTA MRGA #2 8/40A RPL HRDT | ICQ
LC | 123796602 | 030/256 | T3NT EI RND MTN-CTNWD #3 30/256 BNT STL | TABLEMTN | ETL.5650.TOWR | 2022-06-09 | 2022-06-09 | 2023-07-17 | On-Time |  | 2025-06-09 | 2025-06-09 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648237 | T3 EI RND MTN-CTTNWD #3 30/256 BNT STEEL | ICQ
LC | 129039544 | 002/023 | T2 EI HAT CREEK #1-PIT #1 2/023 RPL INSS | TABLEMTN | ETL.7020.INSL.CERA | 2024-06-09 | 2024-06-09 | 2025-05-08 | On-Time |  | 2025-06-09 | 2025-06-09 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570806 | T2 EI HAT CREEK #1-PIT #1 2/023 RPL INSS | 93K
LC | 123814951 | 006/047 | T2NT EI BRUNSWICK #1 TAP 6/47 RMV VEG | SACTO | ETL.1422.TOWR | 2022-06-10 | 2022-06-10 | 2023-09-05 | On-Time |  | 2025-06-10 | 2025-06-10 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2N PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 123819560 | 004/028 | T3NT EI BRUNSWICK #1 TAP 4/028 INS ACG | SACTO | ETL.1422.TOWR | 2022-06-10 | 2022-06-10 | 2025-01-06 | On-Time |  | 2025-06-10 | 2025-06-10 | 988 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3N PRTO FRAB NTDE | Anti-Climbing Guard | Structure-Tower | Install | 31712870 | T3NT EI BRUNSWICK #1 TAP 4/028 INS ACG | 93A
LC | 123821942 | 060/255 | T2NT DI RD MN-TBL MTN #1 60/255 RPR SHLS | TABLEMTN | ETL.6060.TOWR | 2022-06-11 | 2022-06-10 | 2023-11-10 | On-Time |  | 2025-06-10 | 2025-06-10 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire / OPGW-Steel | Repair | 45458954 | T2 DI RND MTN-TBL MTN #1 60/255 RPR SHLS | ICS
LC | 123918894 | 024/198 | T3NT DI PIT #1-CTTNWD 24/198 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2022-06-24 | 2022-06-10 | 2023-10-05 | On-Time |  | 2025-06-10 | 2025-06-10 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45717906 | T3 DI PIT #1-CTTNWD 24/198 BNT STEEL | ICQ
LC | 123923664 | 010/000 | T0 T2NT DI COALINGA #1-SAN MGL 10/0 RPR | FRESNO | ETL.8580.TOWR | 2022-06-25 | 2022-06-10 | 2023-11-20 | On-Time |  | 2025-06-10 | 2025-06-10 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH PRTO AIR FRAA TER0 | No Good/Out of Stdrd | Structure-Tower | Repair | 45639659 | DI COALINGA #1-SAN MGL 10/000 RPR STRT | ICQ
LC | 129049887 | 004/022 | T2 SAN LUIS OBISPO-OCEANO 4/22 TOUCH | PISMOBCH | ETL.3530.TOWR | 2024-06-10 | 2024-06-10 | 2024-06-10 | Past Due |  | 2024-12-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472301 | T2 SAN LUIS OBISPO-OCEANO 4/22 TOUCH | ICQ
LC | 129049892 | C014/059 | T2 MSS LANDING-CBRN C14/59 RPL INSS | MOSSLNDG | ETL.5330.INSL | 2024-06-10 | 2024-06-10 | 2025-04-08 | On-Time |  | 2025-06-10 | 2025-06-10 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35609255 | T2 MSS LANDING-CBRN C14/59 RPL INSS | 93K
LC | 129050099 | 023/282B | T2 EI DRUM-SUMMIT #2 23/282B RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-06-10 | 2024-06-10 | 2024-06-20 | On-Time |  | 2024-09-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46268902 | T2 EI DRUM-SUMMIT #2 23/282B RPR GYWW | ICW
LC | 129050109 | 023/282A | T2 EI DRUM-SUMMIT #2 23/282A RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-06-10 | 2024-06-10 | 2024-06-20 | On-Time |  | 2024-09-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46268818 | T2 EI DRUM-SUMMIT #2 23/282A RPR GYWW | ICW
LC | 129050277 | 023/282C | T2 EI DRUM-SUMMIT #2 23/282C RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-06-10 | 2024-06-10 | 2024-06-20 | On-Time |  | 2024-09-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46268903 | T2 EI DRUM-SUMMIT #2 23/282C RPR GYWW | ICW
LC | 129050355 | 006/028 | T2 WV DIABLO-MESA 6/28 RPR INSS | PISMOBCH | ETL.4620.INSL.NCER | 2024-06-10 | 2024-06-10 | 2025-03-25 | On-Time |  | 2025-06-10 | 2025-06-10 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Insulator-Steel | Install | 35585666 | T2 EI DIABLO-MESA RPL INSS 7 LSTS | 93K
LC | 129051493 | 015/007 | T2 EI CARIBOU-PLUMAS JCT 15/07 RPR GYWW | TABLEMTN | ETL.6290.POLE.NWOD | 2024-06-10 | 2024-06-10 | 2025-03-26 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46397983 | T2 EI CARIBOU-PLUMAS JCT 15/07 RPR GYWW | ICW
LC | 129051715 | 023/279 | T2 EI DRUM-SUMMIT #2 23/279L RPL ANCW | SACTO | ETL.1450.POLE.STPS | 2024-06-10 | 2024-06-10 | 2025-06-19 | Past Due |  | 2025-06-10 | 2025-06-10 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573632 | T2 EI DRUM-SUMMIT #2 RPL ANCW 4 STRT | 93E
LC | 129051723 | 023/279 | T2 EI DRUM-SUMMIT #2 23/279L RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-06-10 | 2024-06-10 | 2024-06-20 | On-Time |  | 2024-12-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46267985 | T2 EI DRUM-SUMMIT #2 23/279L RPR GYWW | ICW
LC | 129052214 | 012/414 | T2 SPAULDING-SUMMIT 12/414 COA | SACTO | ETL.8060.POLE.NWOD | 2024-06-10 | 2024-06-10 | 2025-06-07 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46400323 | T2 EI SPAULDING-SUMMIT 012/414 RPR GYWW | ICW
LC | 129052297 | 066/001X | T2 EI COTONWD-HMBLDT 66/01X RMV VEG | EUREKA | ETL.1820.POLE.WDPS | 2024-06-10 | 2024-06-10 | 2024-12-11 | On-Time |  | 2025-06-10 | 2025-06-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129052518 | 055/236 | T2 EI RND MTN-TBL MTN #1 55/236 RPR JMPS | TABLEMTN | ETL.6060.INSL | 2024-06-10 | 2024-06-10 | 2025-01-23 | On-Time |  | 2025-06-10 | 2025-06-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Jumper-Steel | Repair | 46306311 | T2 EI RND MTN-TBL MTN #1 55/236 RPR JMPS | ICS
LC | 129052562 | 055/236 | T2 EI RND MTN-TBL MTN #1 55/236 RPR INSS | TABLEMTN | ETL.6060.INSL | 2024-06-10 | 2024-06-10 | 2025-01-23 | On-Time |  | 2025-06-10 | 2025-06-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46306312 | T2 EI RND MTN-TBL MTN #1 55/236 RPR INSS | ICS
LC | 129052589 | 066/001X | T2 EI CTONWD-HMBLDT 66/001X RPR ANCW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-10 | 2024-06-10 | 2024-08-28 | On-Time |  | 2024-12-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46268303 | T2 EI CTONWD-HMBLDT 66/001X RPR ANCW | ICW
LC | 129052799 | 032/140 | T2 EI MRRO BY-SLR SS#2 32/140 RPR CNDS | PISMOBCH | ETL.5310.INSL.NCER | 2024-06-10 | 2024-06-10 | 2024-10-28 | On-Time |  | 2024-12-10 | 2025-06-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Conductor-Steel | Repair | 46272340 | T2 EI MORRO BAY-SOLAR SS#2 RPR CNDS | ICS
LC | 129052806 | 023/277 | T2 EI DRUM-SUMMIT #2 23/277C RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-06-10 | 2024-06-10 | 2025-06-08 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458335 | T2 EI DRUM-SUMMIT #2 23/277C RPR GYWW | ICW
LC | 129052912 | 020/188 | T2 EI UKIAH-HPLND-CLVRDL 20/188 RPR GYWW | WILLITS | ETL.4050.POLE.NWOD | 2024-06-10 | 2024-06-10 | 2025-06-20 | Past Due |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446918 | T2 EI UKIAH-HPLND-CLVRDL 20/188 RPR GYWW | ICW
LC | 129053498 | 034/002 | T2 WV PHILO JCT-ELK 034/002 RPL HRDW | WILLITS | ETL.7780.POLE.WOOD | 2024-06-10 | 2024-06-10 | 2025-01-28 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Hardware-Wood | Install | 46340404 | T2 WV PHILO JCT-ELK 034/002 RPL HRDW | ICW
LC | 129053792 | 014/005 | T2 MENDOCINO-HARTLEY 14/5 RPR CNDW | WILLITS | ETL.7510.INSL.NCER | 2024-06-10 | 2024-06-10 | 2024-06-10 | Past Due |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW NONR OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Conductor-Wood | Repair | 46340403 | T2 MENDOCINO-HARTLEY 014/005 RPR CNDW | ICW
LC | 129054387 | 021/196 | T2 EI UKIAH-HPLND-CLVRDL 21/196 RPR GYWW | WILLITS | ETL.4050.POLE.NWOD | 2024-06-10 | 2024-06-10 | 2025-05-12 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446919 | T2 EI UKIAH-HPLND-CLVRDL 21/196 RPR GYWW | ICW
LC | 129054415 | 057/245 | T2 EI RND MTN-TBL MTN #1 57/245 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-06-10 | 2024-06-10 | 2025-01-25 | On-Time |  | 2025-06-10 | 2025-06-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306313 | T2 EI RND MTN-TBL MTN #1 57/245 RMV NEST | ICS
LC | 129054565 | 010/075B | T2 EI HELMS-GREGG#2 10/75B RPR SHLS | FRESNO | ETL.4880.TOWR | 2024-06-10 | 2024-06-10 | 2024-10-29 | On-Time |  | 2025-06-10 | 2025-06-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT SWRK CLR ACCM COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46297933 | T2 EI HELMS-GREGG#2 10/75B RPR SHLS | ICS
LC | 129054753 | 041/269B | T2 DI TRINITY-CTNWD 41/269B RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-06-10 | 2024-06-10 | 2024-08-19 | On-Time |  | 2024-09-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46265954 | T2 DI TRINITY-CTNWD 41/269B RPR JUMW | ICW
LC | 129055899 | 011/081B | T2 EI HELMS-GREGG#2 11/81B RPR INSS | FRESNO | ETL.4880.INSL.CERA | 2024-06-11 | 2024-06-10 | 2024-10-29 | On-Time |  | 2025-06-10 | 2025-06-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297934 | T2 EI HELMS-GREGG#2 11/81B RPR INSS | ICS
LC | 129061248 | 041/269A | T2 DI TRNTY-CTTNWD 41/269A RPR JUMPW | TABLEMTN | ETL.4040.INSL.NCER | 2024-06-11 | 2024-06-10 | 2024-08-19 | On-Time |  | 2024-09-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46265953 | T2 DI TRNTY-CTTNWD 41/269A RPR JUMPW | ICW
LC | 129061284 | 041/269C | T2 DI RND MTN-CTTNWD 41/269C RPR JUMW | TABLEMTN | ETL.4040.INSL.NCER | 2024-06-11 | 2024-06-10 | 2024-08-19 | On-Time |  | 2024-09-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46282254 | T2 DI RND MTN-CTTNWD 41/269C RPR JUMW | ICW
LC | 129061423 | :032/207 | T2 DI NTH TWR MRTN JT#1 :32/207 RPR OPGW | CONCORD | ETL.3130.TOWR | 2024-06-11 | 2024-06-10 | 2025-03-14 | On-Time |  | 2025-06-10 | 2025-06-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46289389 | T2 DI NTH TWR MRTN JT#1 :32/207 RPR OPGW | ICS
LC | 129061424 | 003/024 | T2 OLM-N TOWER-CHRISTIE 3/24 RPR JMPS | CONCORD | ETL.3180.INSL.CERA | 2024-06-11 | 2024-06-10 | 2024-06-10 | Past Due |  | 2025-06-10 | 2025-06-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Steel | Repair | 46289390 | T2 DI OLM-N TOWER-CHRISTIE 3/24 RPR JMPS | ICS
LC | 129061427 | :032/206 | T2 DI NT TR-MTNZ JCT#1 32/206 BNT STEEL | CONCORD | ETL.3130.TOWR | 2024-06-11 | 2024-06-10 | 2025-05-31 | On-Time |  | 2025-06-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46289387 | T2 DI NT TR-MTNZ JCT#1 32/206 BNT STEEL | ICQ
LC | 129061512 | 25 | T2 DI PARDEE#2 TAP 00/01 RPR SWTC | VICTOR | ETL.8251.SWIT | 2024-06-11 | 2024-06-10 | 2025-03-24 | On-Time |  | 2025-06-10 | 2025-06-10 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR NTDE | Out of Adjustment | Switch | Repair | 46325961 | T2 DI PARDEE#2 TAP 00/01 RPR SWTC | ICE
LC | 129061518 | 001/038 | T2 DI SPLDNG SUMMIT 1/38 RPR JUMW | SACTO | ETL.8060.INSL.NCER | 2024-06-11 | 2024-06-10 | 2024-06-21 | On-Time |  | 2024-09-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46265631 | T2 DI SPLDNG SUMMIT 01/038 RPR JUMW | ICW
LC | 129077045 | :032/204 | T2 DI N TWR-MRTNZ JCT#1 :32/204 INS JMPS | CONCORD | ETL.3130.INSL.NCER | 2024-06-14 | 2024-06-10 | 2025-06-10 | On-Time |  | 2025-06-10 | 2025-06-10 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Missing | Insulator-Steel | Install | 35647575 | T2 DI N TWR-MRTNZ JCT#1 :32/204 INS JMPS | 93K
LC | 129224187 | 000/001C | T2 DI BLDN TP - NN WD PL 0/1C RPR GYWT | TABLEMTN | ETL.4441.POLE.NWOD | 2024-07-15 | 2024-06-10 | 2025-01-06 | On-Time |  | 2025-06-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46353977 | T2 DI BLDN TP - NN WD PL 0/1C RPR GYWT | ICQ
LC | 129224433 | 000/001A | T2 DI BELDEN TAP 000/001A RPR GYWT | TABLEMTN | ETL.4441.POLE.NWOD | 2024-07-15 | 2024-06-10 | 2025-01-06 | On-Time |  | 2025-06-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46353978 | T2 DI BELDEN TAP 000/001A RPR GYWT | ICQ
LC | 129224439 | 000/001B | T2 DI BELDEN TAP 000/001B RPR ANCT | TABLEMTN | ETL.4441.POLE.NWOD | 2024-07-15 | 2024-06-10 | 2025-01-06 | On-Time |  | 2025-06-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46354000 | T2 DI BELDEN TAP 000/001B RPR ANCT | ICQ
LC | 129245106 | 007/159 | T2 DI HAMLTN BRNCH-CHSTR 7/159 RPL STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-07-19 | 2024-06-10 | 2025-03-22 | On-Time |  | 2025-06-10 | 2025-06-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574583 | T2 DI HAMLTN BRNCH-CHSTR 7/159 RPL STRW | 70Y
LC | 129245243 | 006/108 | T2 DI CLGT-PALERMO 006/108 RPL STRW | SACTO | ETL.6500.POLE.WOOD | 2024-07-19 | 2024-06-10 | 2025-03-26 | On-Time |  | 2025-06-10 | 2025-06-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572923 | T2 DI CLGT-PALERMO 006/108 RPL STRW | 70Y
LC | 129245555 | 006/016 | T2 DI TULUCAY-NAPA #1 6/16 COTTER | LAKEVLLE | ETL.8180.INSL.NCER | 2024-07-19 | 2024-06-10 | 2025-05-02 | On-Time |  | 2024-12-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46333620 | T2 DI TULUCAY-NAPA #1 6/016 COTTER | ICW
LC | 129245914 | 009/109 | T2 DI DRUM-SUMMIT #2 9/109 RPR GYWW | SACTO | ETL.1450.POLE.WDPS | 2024-07-19 | 2024-06-10 | 2025-04-23 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458343 | T2 DI DRUM-SUMMIT #2 9/109 RPR GYWW | ICW
LC | 129246803 | 015/111 | T2 DI CRIBU TBL MTN 15/111 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2024-07-19 | 2024-06-10 | 2025-04-02 | On-Time |  | 2025-06-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46354100 | T2 DI CRIBU TBL MTN 15/111 RPL HRDT | ICQ
LC | 129246916 | 016/121 | T2 DI CARIBOU-TABLE MNT 16/121 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2024-07-19 | 2024-06-10 | 2025-01-08 | On-Time |  | 2024-09-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Hardware-Tower | Replace | 46323671 | T2 DI CARIBOU-TABLE MNT 16/121 RPL HRDT | ICQ
LC | 129246986 | 027/402 | T2 DI CLAY-MARTEL 27/402 RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-07-19 | 2024-06-10 | 2025-04-30 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46327035 | +T2 DI CLAY-MARTEL 27/402 RPR STRW | ICW
LC | 129247062 | 086/000F | T2 DI HMBLDT-BRDGVLL 86/000F RPR ADSS | EUREKA | ETL.1810.POLE.WOOD | 2024-07-19 | 2024-06-10 | 2025-06-03 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | ADSS - Wood | Repair | 46346081 | T2 DI HMBLDT-BRDGVLL 86/000F RPR ADSS | ICW
LC | 129247318 | 003/066 | T2 DI VALLEY SPRINGS #1 3/66 RPR STRW | VICTOR | ETL.8210.POLE.WOOD | 2024-07-19 | 2024-06-10 | 2025-04-16 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46327515 | T2 DI VALLEY SPRINGS #1 3/66 RPR STRW | ICW
LC | 129249936 | 007/161 | T2 DI HMLTN BRNCH-CHSTR 07/161 RPR STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-07-19 | 2024-06-10 | 2025-01-09 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46311129 | T2 DI HMLTN BRNCH-CHSTR 07/161 RPR STRW | ICW
LC | 129279899 | 039/244 | T2 DI CRZY HRS CNYN-SLNS-S 39/244 RPL HR | MOSSLNDG | ETL.2900.TOWR | 2024-07-23 | 2024-06-10 | 2025-05-22 | On-Time |  | 2025-06-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46416716 | T2 DI CRZY HRS CNYN-SLNS-S 39/244 RPL HR | ICQ
LC | 129280228 | 012/091 | T2NT DI CARIBOU-TBL MTN 012/091 RPR FOND | TABLEMTN | ETL.4440.TOWR | 2024-07-23 | 2024-06-10 | 2025-04-02 | On-Time |  | 2027-06-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46337133 | T2NT DI CARIBOU-TBL MTN 012/091 RPR FOND | ICQ
LC | 129280290 | 012/091 | T2 DI CARIBOU-TBL MTN 12/91 RPR JUMS | TABLEMTN | ETL.4440.INSL.NCER | 2024-07-23 | 2024-06-10 | 2024-12-20 | On-Time |  | 2024-09-10 | 2025-06-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46328454 | T2 DI CARIBOU-TBL MTN 012/091 RPR JUMS | ICS
LC | 129280291 | 004/089 | T2 DI CSCDE-BENT-DESCHUTES 4/89 RPR STRW | TABLEMTN | ETL.6310.POLE.WOOD | 2024-07-23 | 2024-06-10 | 2025-05-16 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46383924 | T2 DI CSCDE-BENT-DESCHUTES 4/89 RPR STRW | ICW
LC | 129280396 | 019/138 | T2 DI CARIBOU-TABLE MTN 19/138 TOUCH | TABLEMTN | ETL.4440.TOWR | 2024-07-23 | 2024-06-10 | 2025-02-19 | On-Time |  | 2024-12-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46474398 | T2 DI CARIBOU-TABLE MTN 19/138 TOUCH | ICQ
LC | 129280431 | 015/113 | T2 DI CARIBOU-TBL MTN 015/113 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2024-07-23 | 2024-06-10 | 2025-04-02 | On-Time |  | 2025-06-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46337134 | T2 DI CARIBOU-TBL MTN 015/113 RPL HRDT | ICQ
LC | 129293691 | :017/090 | T2 DI CZY HS CYN-SLS-SLD#1 17/90 RPL RPT | MOSSLNDG | ETL.2900.TOWR | 2024-07-26 | 2024-06-10 | 2025-04-10 | On-Time |  | 2025-06-10 | 2025-06-10 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46391448 | T2 DI CZY HS CYN-SLS-SLD#1 17/90 RPL RPT | ICB
LC | 129376252 | 000/010 | T2 DI PIT #1-MC ARTHUR-00/10 RPL CRSW | TABLEMTN | ETL.7790.POLE.WOOD | 2024-08-12 | 2024-06-10 | 2025-02-11 | On-Time |  | 2025-06-10 | 2025-06-10 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35586950 | T2 DI PIT #1-MC ARTHUR-00/10 RPL CRSW | 93E
LC | 129376382 | 007/162 | T2 DI HMLTN BRNCH-CHSTR 7/162 RPR STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-08-12 | 2024-06-10 | 2025-01-09 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337217 | T2 DI HMLTN BRNCH-CHSTR 7/162 RPR STRW | ICW
LC | 129376435 | 012/092 | T2 CARIBOU-TBL MTN-12/92 RMV VEG | TABLEMTN | ETL.4440.TOWR | 2024-08-12 | 2024-06-10 | 2024-06-10 | Past Due |  | 2025-06-10 | 2025-06-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129393389 | 010/125C | T2 DI DRUM-SUMMIT #1 10/125C RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-08-15 | 2024-06-10 | 2024-11-18 | On-Time |  | 2024-12-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46306366 | T2 DI DRUM-SUMMIT #1 10/125C RPR GYWW | ICW
LC | 129393415 | 010/124 | T2 DI DRUM-SUMMIT #1 10/124 RPR STRW | SACTO | ETL.1440.POLE.WDPS | 2024-08-15 | 2024-06-10 | 2025-04-24 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401370 | T2 DI DRUM-SUMMIT #1 10/124 RPR STRW | ICW
LC | 129393416 | 010/093 | T2 DI EL DRD-MSSRI FLT #1 10/93 RMV NEST | SACTO | ETL.1530.TOWR | 2024-08-15 | 2024-06-10 | 2025-03-15 | On-Time |  | 2025-06-10 | 2025-06-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46452737 | T2 DI EL DRD-MSSRI FLT #1 10/93 RMV NEST | ICS
LC | 129393425 | 016/322 | T2 HAT CREEK #1 WSTWD 16/322 RPL POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-08-15 | 2024-06-10 | 2025-05-16 | On-Time |  | 2025-06-10 | 2025-06-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586915 | T2 DI HAT CREEK #1 WSTWD 16/322 RPL POLE | 70Y
LC | 129393548 | 026/192A | T2 DI CRBOU-TBL MTN 26/192A RPR GYWT | TABLEMTN | ETL.4440.POLE.NWOD | 2024-08-15 | 2024-06-10 | 2025-02-27 | On-Time |  | 2025-06-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46337139 | T2 DI CRBOU-TBL MTN 26/192A RPR GYWT | ICQ
LC | 129393627 | 027/400 | T2 DI CLAY-MARTEL 27/400 RPR INSW | VICTOR | ETL.8250.INSL.NCER | 2024-08-15 | 2024-06-10 | 2025-05-12 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46339080 | T2 DI CLAY-MARTEL 27/400 RPR INSW | ICW
LC | 129393628 | 027/400 | T2 DI CLAY-MARTEL 27/400 RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-08-15 | 2024-06-10 | 2025-05-12 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46339081 | T2 DI CLAY-MARTEL 27/400 RPR STRW | ICW
LC | 129393675 | 020/143 | T2 DI CARIBOU-TABLE MTN 20/143 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2024-08-15 | 2024-06-10 | 2024-06-10 | Past Due |  | 2025-06-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46337221 | T2 DI CARIBOU-TABLE MTN 20/143 RPR STRT | ICQ
LC | 129393744 | 002/047 | T2 DI HAT CREEK #1-WESTWOOD 2/47 RMV VEG | TABLEMTN | ETL.7030.POLE.WOOD | 2024-08-15 | 2024-06-10 | 2024-12-11 | On-Time |  | 2025-06-10 | 2025-06-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129393747 | 002/047 | T2 DI HAT CREEK #1-WESTWD 2/47 RPR STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-08-15 | 2024-06-10 | 2025-05-13 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46416182 | T2 DI HAT CREEK #1-WESTWD 2/47 RPR STRW | ICW
LC | 129393764 | 003/073 | T2 CASCADE BNTN DSCHTS 3/73 RPL INSW | TABLEMTN | ETL.6310.INSL.NCER | 2024-08-15 | 2024-06-10 | 2024-06-10 | Past Due |  | 2025-06-10 | 2025-06-10 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35586833 | T2 DI CASCADE BNTN DSCHTS 3/73 RPL INSW | 93I
LC | 129393885 | 016/317 | T2 DI COLGATE PALERMO 16/317 RPL STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-08-15 | 2024-06-10 | 2025-02-06 | On-Time |  | 2025-06-10 | 2025-06-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586887 | T2 DI COLGATE PALERMO 16/317 RPL STRW | 70Y
LC | 129393963 | 019/212 | T2 DI ELK CRK TAP 19/212 RPR GYWW | TABLEMTN | ETL.6921.POLE.NWOD | 2024-08-15 | 2024-06-10 | 2024-10-09 | On-Time |  | 2024-09-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46306325 | T2 DI ELK CRK TAP 19/212 RPR GYWW | ICW
LC | 129394092 | 010/121 | T2 DRUM-SUMMIT #1 10/121L COMPLETE | SACTO | ETL.1440.POLE.WDPS | 2024-08-15 | 2024-06-10 | 2025-04-24 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401379 | T2 DI DRUM-SUMMIT #1 10/121L RPR STRW | ICW
LC | 129394103 | 001/025 | T2 DI HAT CREEK #1 WSTWD 1/25 RPR STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-08-15 | 2024-06-10 | 2025-05-13 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46416185 | T2 DI HAT CREEK #1 WSTWD 1/25 RPR STRW | ICW
LC | 129394206 | 004/049B | T2 DI IGNCIO-BLNAS #2 4/49B CANCEL | LAKEVLLE | ETL.7180.POLE.WOOD | 2024-08-15 | 2024-06-10 | 2024-06-10 | Past Due |  | 2025-06-10 | 2025-06-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586946 | T2 DI IGNCIO-BLNS #2 4/49A RPL STRW | 70Y
LC | 129394241 | 007/163 | T2 DI HMLTN BRNCH-CHESTER 7/163 RPR INSW | TABLEMTN | ETL.7000.INSL.NCER | 2024-08-15 | 2024-06-10 | 2025-03-18 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46337241 | T2 DI HMLTN BRNCH-CHESTER 7/163 RPR INSW | ICW
LC | 129394248 | 016/312 | T2 HAT CREEK #1-WSTWD 16/312 RPR CRSW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-08-15 | 2024-06-10 | 2025-05-02 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46416186 | T2 DI HAT CREEK #1-WSTWD 16/312 RPR CRSW | ICW
LC | 129394260 | 002/068 | T2 CSCD-BNTN-DSCHTS 2/68 RPL STRW | TABLEMTN | ETL.6310.POLE.WOOD | 2024-08-15 | 2024-06-10 | 2024-06-10 | Past Due |  | 2025-06-10 | 2025-06-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586832 | T2 DI CSCD-BNTN-DSCHTS 2/68 RPL STRW | 70Y
LC | 129394263 | 033/513 | T2 DI CLY-MRTL 33/513 RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-08-15 | 2024-06-10 | 2025-05-12 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46339082 | T2 DI CLY-MRTL 33/513 RPR STRW | ICW
LC | 129394372 | 004/049A | T2 DI IGNCIO-BLNS #2 4/49A CANCEL | LAKEVLLE | ETL.7180.POLE.WOOD | 2024-08-15 | 2024-06-10 | 2024-06-10 | Past Due |  | 2025-06-10 | 2025-06-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586946 | T2 DI IGNCIO-BLNS #2 4/49A RPL STRW | 70Y
LC | 129394379 | 004/049C | T2 DI IGNCIO-BLNS #2 4/49C CANCEL | LAKEVLLE | ETL.7180.POLE.WOOD | 2024-08-15 | 2024-06-10 | 2024-06-10 | Past Due |  | 2025-06-10 | 2025-06-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586946 | T2 DI IGNCIO-BLNS #2 4/49A RPL STRW | 70Y
LC | 129394404 | 010/125B | T2 DI DRUM SUMMIT #1 10/125B COTTER | SACTO | ETL.1440.INSL.NCER | 2024-08-15 | 2024-06-10 | 2025-04-24 | On-Time |  | 2025-06-15 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46401382 | T2 DI DRUM SUMMIT #1 10/125B COTTER | ICW
LC | 129394590 | 012/097 | T2 DI CARIBOU TBL MTN 12/97 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2024-08-15 | 2024-06-10 | 2025-05-28 | On-Time |  | 2025-06-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46337222 | T2 DI CARIBOU TBL MTN 12/97 RPL HRDT | ICQ
LC | 129394978 | 027/407 | T2 DI CLAY MARTEL 27/407 RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-08-15 | 2024-06-10 | 2025-05-12 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46339084 | T2 DI CLAY MARTEL 27/407 RPR STRW | ICW
LC | 129409396 | :031/200 | T2 DI NTH TWR-MTZ JT #1 :31/200 COMPLETE | CONCORD | ETL.3130.TOWR | 2024-08-19 | 2024-06-10 | 2024-12-16 | On-Time |  | 2024-12-10 | 2025-06-10 | 931 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46345590 | T2 DI NTH TWR-MRTZ JT#1 :31/200 RMV ENCH | CHR
LC | 129409420 | 015/182 | T2 DI ELK CRK TP-WD PL 15/182 RPR INSW | TABLEMTN | ETL.6921.INSL.NCER | 2024-08-19 | 2024-06-10 | 2025-05-30 | On-Time |  | 2025-06-10 | 2025-06-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46383931 | T2 DI ELK CRK TP-WD PL 15/182 RPR INSW | ICW
LC | 131317506 | :032/204 | T2 N TWR-MRTNZ JCT#1 :32/204 HANGER | CONCORD | ETL.3130.INSL.NCER | 2025-06-04 | 2024-06-10 | 2025-06-10 | On-Time |  | 2025-06-10 | 2025-06-10 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46530726 | T2 DI N TWR-MRTNZ JCT#1 :32/204 HANGER | ICQ
LC | 123822097 | 010/099 | T3NT EI DRUM-RIO OSO #2 10/99 BNT STEEL | SACTO | ETL.1430.TOWR | 2022-06-11 | 2022-06-11 | 2023-07-03 | On-Time |  | 2025-06-11 | 2025-06-11 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45600071 | T3 EI DRUM-RIO OSO #2 10/99 BNT STEEL | ICQ
LC | 123823209 | 000/001 | T2NT MELONES-RACETRACK 0/1 RPL INSW | VICTOR | ETL.2400.INSL.CERA | 2022-06-11 | 2022-06-11 | 2023-08-07 | On-Time |  | 2025-06-11 | 2025-06-11 | 508 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 31612297 | T2 EI MELONES-RACETRACK 5/14 RPL INSW | 93I
LC | 123824541 | 000/007 | T3NT EI MIDDLEFORK #1 0/7 RMV VEG | SACTO | ETL.8405.POLE.WOOD | 2022-06-11 | 2022-06-11 | 2023-12-12 | On-Time |  | 2025-06-11 | 2025-06-11 | 564 | TR3N |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR3N PRTO FRAB | Overgrown | Vegetation | Remove
LC | 123825194 | 043/365 | T2NT EI RND MTN-CNWD #3 43/365 BNT STEEL | TABLEMTN | ETL.5650.TOWR | 2022-06-11 | 2022-06-11 | 2023-08-02 | On-Time |  | 2025-06-11 | 2025-06-11 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648253 | T2 EI RND MTN-CONWD #3 43/365 BNT STEEL | ICQ
LC | 123825268 | 008/087 | T3NT EI IGNACIO-BOLINAS #1 8/87 RMV VEG | LAKEVLLE | ETL.7140.POLE.WOOD | 2022-06-11 | 2022-06-11 | 2023-12-01 | On-Time |  | 2025-06-11 | 2025-06-11 | 564 | TR3N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR3N PRTO FRAB | Overgrown | Vegetation | Remove
LC | 123871628 | 007/005C | T2NT DI HUMBOLDT-MAPLE CRK 7/5C RPL STRW | EUREKA | ETL.7130.POLE.WOOD | 2022-06-18 | 2022-06-11 | 2023-11-11 | On-Time |  | 2025-06-11 | 2025-06-11 | 372 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE ACCL COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 31617165 | T2 DI HUMBOLDT-MAPLE CRK 2/5 RPL STRW | 70Y
LC | 123974975 | :008/000 | T2 DI BLT RVRBNK MLNS SS 8/0 INS STEP | VICTOR | ETL.1070.POLE.NWOD | 2022-07-01 | 2022-06-11 | 2023-04-13 | On-Time |  | 2023-06-11 | 2025-06-11 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB NTDE | Missing | Hardware-Wood | Install | 45513987 | T2 DI BLT RVRBNK MLNS SS 8/0 INS STEP | ICW
LC | 129056204 | 008/099B | T2 EI DRUM-SUMMIT #2 08/099B RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-06-11 | 2024-06-11 | 2024-06-16 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46265835 | T2 EI DRUM-SUMMIT #2 08/099B RPR GYWW | ICW
LC | 129056363 | 008/099C | T2 EI DRUM-SUMMIT #2 08/099C RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-06-11 | 2024-06-11 | 2024-06-16 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46265834 | T2 EI DRUM-SUMMIT #2 08/099C RPR GYWW | ICW
LC | 129056634 | 001/022 | T2 WV KESWICK-CASCADE 01/22 RPL DMPW | TABLEMTN | ETL.7260.INSL.NCER | 2024-06-11 | 2024-06-11 | 2024-06-24 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46281077 | T2 WV KESWICK-CASCADE 01/22 RPL DMPW | ICW
LC | 129056983 | 004/028 | T2 EI PTTSBRG-CLYTN #1 4/28 RPL HNGR PL | CONCORD | ETL.3280.INSL.NCER | 2024-06-11 | 2024-06-11 | 2024-09-18 | On-Time |  | 2024-09-11 | 2025-06-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO CLMB DURA BRIN | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46264526 | T2 EI PTTSBRG-CLYTN #1 4/28 RPL HNGR PL | ICQ
LC | 129057088 | 000/009 | T2 EI APPLE HILL #2 TAP 000/009 RPL POLE | SACTO | ETL.1541.POLE.WOOD | 2024-06-11 | 2024-06-11 | 2025-04-18 | On-Time |  | 2025-06-11 | 2025-06-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35571709 | T2 EI APPLE HILL #2 TAP 000/009 RPL POLE | 70Y
LC | 129057498 | 056/241 | T2 EI RND MTN-TBL MTN #1 56/241 RPR SHLD | TABLEMTN | ETL.6060.TOWR | 2024-06-11 | 2024-06-11 | 2025-01-21 | On-Time |  | 2025-06-11 | 2025-06-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46306314 | T2 EI RND MTN-TBL MTN #1 56/241 RPR SHLD | ICS
LC | 129057764 | 056/241 | T2 EI RND MTN-TBL MTN#2 56/241 INS DAMS | TABLEMTN | ETL.6070.INSL | 2024-06-11 | 2024-06-11 | 2025-02-21 | On-Time |  | 2025-06-11 | 2025-06-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Steel | Install | 46306315 | T2 EI RND MTN-TBL MTN#2 56/241 INS DAMS | ICS
LC | 129057797 | 001/031 | T2 EI APPLE HILL #2 TAP 001/031 RPL POLE | SACTO | ETL.1541.POLE.WOOD | 2024-06-11 | 2024-06-11 | 2025-04-18 | On-Time |  | 2025-06-11 | 2025-06-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35571711 | T2 EI APPLE HILL #2 TAP 001/031 RPL POLE | 70Y
LC | 129058639 | 026/002 | T2 HARTLEY-CLEARLAKE 026/002 RPR POLE | WILLITS | ETL.7515.POLE.WOOD | 2024-06-11 | 2024-06-11 | 2024-06-11 | Past Due |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46310531 | T2 EI HARTLEY-CLEARLAKE 026/002 RPR POLE | ICW
LC | 129059144 | 056/240 | T2 EI RND MTN-TBL MTN #2 56/240 COTTER | TABLEMTN | ETL.6070.INSL | 2024-06-11 | 2024-06-11 | 2025-02-21 | On-Time |  | 2024-09-11 | 2025-06-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46272337 | T2 EI RND MTN-TBL MTN#2 56/240 RPR INSS | ICS
LC | 129059148 | 056/240 | T2 EI RND MTN-TBL MTN #1 56/240 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-06-11 | 2024-06-11 | 2025-01-21 | On-Time |  | 2025-06-11 | 2025-06-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306316 | T2 EI RND MTN-TBL MTN #1 56/240 RMV NEST | ICS
LC | 129059149 | 056/240 | T2 RND MTN-TBL MTN #1 56/240 RPL GRND | TABLEMTN | ETL.6060.TOWR | 2024-06-11 | 2024-06-11 | 2024-06-11 | Past Due |  | 2025-06-11 | 2025-06-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Ground Wire-Tower | Replace | 46310401 | T2 EI RND MTN-TBL MTN #1 56/240 RPL GRND | ICQ
LC | 129059150 | 056/242 | T2 EI RND MTN-TBL MTN #1 56/242 RMV NEST | TABLEMTN | ETL.6060.TOWR | 2024-06-11 | 2024-06-11 | 2025-01-21 | On-Time |  | 2025-06-11 | 2025-06-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46306317 | T2 EI RND MTN-TBL MTN #1 56/242 RMV NEST | ICS
LC | 129059198 | 001/011 | T2 BCKS CRK-RCK CRK-CRST 1/11 REGRADE | TABLEMTN | ETL.4430.TOWR | 2024-06-11 | 2024-06-11 | 2025-01-15 | On-Time |  | 2025-06-11 | 2025-06-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46353976 | T2 BCKS CRK-RCK CRK-CRST 1/11 REGRADE | ICQ
LC | 129059301 | 000/013 | T2 WV MNDCNO-WLTS-FRT BRG 0/13 INS DMPW | WILLITS | ETL.7550.INSL.CERA | 2024-06-11 | 2024-06-11 | 2025-03-31 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46310529 | T2 WV MNDCNO-WLTS-FRT BRG 0/13 INS DMPW | ICW
LC | 129060480 | 027/210 | T2 EI MSSRI FLT-GLD HLL #1 27/210 COTTER | SACTO | ETL.2660.INSL.NCER | 2024-06-11 | 2024-06-11 | 2025-06-05 | On-Time |  | 2025-06-11 | 2025-06-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46324620 | T2 EI MSSRI FLT-GLD HLL #1 27/210 COTTER | ICS
LC | 129060820 | 003/001 | T2 EI MAPLE CREEK-HOOPA 3/1 RPL DMPW | EUREKA | ETL.7490.INSL.NCER | 2024-06-11 | 2024-06-11 | 2025-06-11 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Damper-Wood | Replace | 46345977 | T2 EI MAPLE CREEK-HOOPA 3/1 RPL DMPW | ICW
LC | 129060972 | 021/299 | T2 DI CLAY MARTEL 21/299 RPR IBWW | VICTOR | ETL.8250.INSL.CERA | 2024-06-11 | 2024-06-11 | 2024-10-18 | On-Time |  | 2024-09-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46266194 | T2 DI CLAY MARTEL 21/299 RPR IBWW | ICW
LC | 129061138 | :009/067 | T2 DI ROCK CRK-POE :9/67 COTTER | TABLEMTN | ETL.5630.INSL.CERA | 2024-06-11 | 2024-06-11 | 2025-04-26 | On-Time |  | 2025-06-11 | 2025-06-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46383941 | T2 DI ROCK CRK-POE :9/67 COTTER | ICS
LC | 129061338 | 007/168 | T2 DI HMLTN BRNCH-CHSTR 7/168 RPR JUMW | TABLEMTN | ETL.7000.INSL.NCER | 2024-06-11 | 2024-06-11 | 2024-07-24 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46280129 | T2 DI HMLTN BRNCH-CHSTR 7/168 RPR JUMW | ICW
LC | 129061362 | 007/168 | T2 DI HMLTN BRNCH-CHSTR 7/168 RPR CRSW | TABLEMTN | ETL.7000.POLE.NWOD | 2024-06-11 | 2024-06-11 | 2024-07-24 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46286595 | T2 DI HMLTN BRNCH-CHSTR 7/168 RPR CRSW | ICW
LC | 129061556 | 039/240 | T2 INDN FLT-YOSMITE 39/240 RMV VEG | FRESNO | ETL.1112.POLE.NWOD | 2024-06-11 | 2024-06-11 | 2025-01-06 | On-Time |  | 2025-06-11 | 2025-06-11 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW CREW REMT ACCL CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 129061667 | 013/306 | T2 DI DRM-GRSS VLLY-WMR 13/306 RPL TIED | SACTO | ETL.6760.INSL | 2024-06-11 | 2024-06-11 | 2025-01-08 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Tie Wire-Wood | Replace | 46324543 | T2 DI DRM-GRSS VLLY-WMR 13/306 RPL TIED | ICW
LC | 129061901 | :003/019 | T2 ROCK CREEK POE 3/19 BENT STEEL | TABLEMTN | ETL.5630.TOWR | 2024-06-11 | 2024-06-11 | 2025-06-06 | On-Time |  | 2025-06-11 | 2025-06-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46382041 | T2 DI ROCK CREEK POE 3/19 BENT STEEL | ICQ
LC | 129067184 | 018/205 | T2 DI ELK CREEK TAP 18/205 RPR GYWW | TABLEMTN | ETL.6921.POLE.WOOD | 2024-06-12 | 2024-06-11 | 2025-05-28 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46383877 | T2 DI ELK CREEK TAP 18/205 RPR GYWW | ICW
LC | 129067262 | 004/057 | T2 DI CLGATE-SMRTVIL #1-04/57 RPR GYWW | SACTO | ETL.6510.POLE.NWOD | 2024-06-12 | 2024-06-11 | 2025-02-18 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337399 | T2 DI CLGATE-SMRTVIL #1-04/57 RPR GYWW | ICW
LC | 129067429 | 019/207 | T2 DI ELK CREEK TAP 19/207 RPR JUMW | TABLEMTN | ETL.6921.INSL.NCER | 2024-06-12 | 2024-06-11 | 2024-10-09 | On-Time |  | 2024-09-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46269244 | T2 DI ELK CREEK TAP 19/207 RPR JUMW | ICW
LC | 129067523 | 031/004 | T2 DI MNDO-WLTS-FORT BRG 31/04 RPR GYWW | WILLITS | ETL.7550.POLE.NWOD | 2024-06-12 | 2024-06-11 | 2025-03-05 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46310532 | T2 DI MNDO-WLTS-FORT BRG 31/04 RPR GYWW | ICW
LC | 129076779 | 009/206 | T2 DI HMLTN BRNCH CHSTR 09/206 RPL HRDD | TABLEMTN | ETL.7000.POLE.WOOD | 2024-06-14 | 2024-06-11 | 2025-03-19 | On-Time |  | 2024-09-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace | 46311128 | T2 DI HMLTN BRNCH CHSTR 09/206 RPL HRDD | ICW
LC | 129076962 | :009/065 | T2 DI ROCK CREEK POE :9/65 RPR JUMS | TABLEMTN | ETL.5630.INSL.NCER | 2024-06-14 | 2024-06-11 | 2025-04-27 | On-Time |  | 2025-06-11 | 2025-06-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46268461 | T2 DI ROCK CREEK POE :9/65 RPR JUMP | ICS
LC | 129077420 | 085/000 | T2 DI HMBLDT TRNTY 85/0C RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-14 | 2024-06-11 | 2025-04-22 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345978 | T2 DI HMBLDT TRNTY 85/0C RPR GYWW | ICW
LC | 129077422 | 085/000 | T2 DI HMBLDT TRNTY 85/0L RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-14 | 2024-06-11 | 2025-04-22 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345976 | T2 DI HMBLDT TRNTY 85/0L RPR GYWW | ICW
LC | 129077429 | 085/000 | T2 DI HMBLDT TRNTY 85/0R RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-14 | 2024-06-11 | 2025-04-22 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345975 | T2 DI HMBLDT TRNTY 85/0R RPR GYWW | ICW
LC | 129077539 | :008/063 | T2 ROCK CREEK POE :8/63 TOUCH | TABLEMTN | ETL.5630.TOWR | 2024-06-14 | 2024-06-11 | 2024-06-11 | Past Due |  | 2024-12-11 | 2025-06-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478267 | T2 DI ROCK CREEK POE :08/063 TOUCH | ICQ
LC | 129077680 | 021/251B | T2 DI DRUM SUMMIT#1 21/251B RPR GYWW | SACTO | ETL.1440.POLE.NWOD | 2024-06-14 | 2024-06-11 | 2024-07-17 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46284293 | T2 DI DRUM SUMMIT#1 21/251B RPR GYWW | ICW
LC | 129078555 | 004/116 | T2 DI HMLTN BRNCH CHSTR 04/116 RPR JUMW | TABLEMTN | ETL.7000.INSL.NCER | 2024-06-14 | 2024-06-11 | 2024-07-24 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46273549 | T2 DI HMLTN BRNCH CHSTR 04/116 RPR JUMW | ICW
LC | 129078617 | 095/000 | T2 DI HMBLDT TRNTY 95/000 RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-06-14 | 2024-06-11 | 2024-08-28 | On-Time |  | 2024-12-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46268304 | T2 DI HMBLDT TRNTY 95/000 RPR JUMW | ICW
LC | 129078661 | 095/000 | T2 DI HMBLDT TRNTY 95/0L RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-14 | 2024-06-11 | 2024-08-28 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46306446 | T2 DI HMBLDT TRNTY 95/0L RPR GYWW | ICW
LC | 129078697 | 004/031B | T2 DI TRNTY CTTNWD 04/031B RPR GYWW | TABLEMTN | ETL.4040.POLE.NWOD | 2024-06-14 | 2024-06-11 | 2025-01-16 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46455934 | T2 DI TRNTY CTTNWD 04/031B RPR GYWW | ICW
LC | 129083672 | 095/000 | T2 DI HMBLDT TRNTY 95/0R RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-17 | 2024-06-11 | 2024-08-28 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46306446 | T2 DI HMBLDT TRNTY 95/0L RPR GYWW | ICW
LC | 129083675 | 095/000 | T2 DI HMBLDT TRNTY 95/0C RPR GYWW | EUREKA | ETL.1820.POLE.STPS | 2024-06-17 | 2024-06-11 | 2024-08-28 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46306446 | T2 DI HMBLDT TRNTY 95/0L RPR GYWW | ICW
LC | 129274008 | 019/137 | T2 DI CARIBOU--TBL MTN 19/137 RPR JUMS | TABLEMTN | ETL.4440.INSL.NCER | 2024-07-22 | 2024-06-11 | 2024-12-20 | On-Time |  | 2024-09-11 | 2025-06-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46328453 | T2 DI CARIBOU--TBL MTN 19/137 RPR JUMS | ICS
LC | 129274536 | 001/020 | T2 DI COLGATE-PALRMO 1/20 RPR GYWW | SACTO | ETL.6500.POLE.NWOD | 2024-07-22 | 2024-06-11 | 2025-03-25 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337347 | T2 DI COLGATE-PALRMO 1/20 RPR GYWW | ICW
LC | 129280420 | :010/054 | T2 DI CZY HSE CNYN-SLNAS 10/54 BNT STEEL | MOSSLNDG | ETL.2900.TOWR | 2024-07-23 | 2024-06-11 | 2025-04-30 | On-Time |  | 2025-06-11 | 2025-06-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416718 | T2 DI CZY HSE CNYN-SLNAS 10/54 BNT STEEL | ICQ
LC | 129284522 | 076/002A | T2 DI HUMBOLDT-TRINITY 76/2A RPR INSW | EUREKA | ETL.1820.INSL.CERA | 2024-07-24 | 2024-06-11 | 2025-04-22 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46403124 | T2 DI HUMBOLDT-TRINITY 76/2A RPR INSW | ICW
LC | 129284727 | 000/003 | T2 DI PALERMO-PEASE 00/03 RPR INSS | TABLEMTN | ETL.3220.INSL.CERA | 2024-07-24 | 2024-06-11 | 2025-01-08 | On-Time |  | 2025-06-11 | 2025-06-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46337453 | T2 DI PALERMO-PEASE 00/03 RPR INSS | ICS
LC | 129293216 | 012/238 | T2 DI CLGTE-PLMRO 12/238 RMV VEG | TABLEMTN | ETL.6500.POLE.NWOD | 2024-07-26 | 2024-06-11 | 2025-04-10 | On-Time |  | 2025-06-11 | 2025-06-11 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129293729 | 001/023C | T2 DI JOLON TAP 01/023C COTTER | MOSSLNDG | ETL.7321.INSL.NCER | 2024-07-26 | 2024-06-11 | 2025-01-15 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46391189 | T2 DI JOLON TAP 01/023C COTTER | ICW
LC | 129295088 | 016/122 | T2 DI CRBOU-TBL MTN 16/122 RPR SHLS | TABLEMTN | ETL.4440.TOWR | 2024-07-26 | 2024-06-11 | 2025-04-02 | On-Time |  | 2025-06-11 | 2025-06-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46338303 | T2 DI CRBOU-TBL MTN 16/122 RPR SHLS | ICS
LC | 129393438 | 008/182 | T2 DI HMLTN BRNCH-CHSTER 8/182 RPR STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-08-15 | 2024-06-11 | 2025-01-15 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337219 | T2 DI HMLTN BRNCH-CHSTER 8/182 RPR STRW | ICW
LC | 129393776 | 017/338 | T2 DI COLGATE-PALERMO 17/338 RPR STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-08-15 | 2024-06-11 | 2025-05-23 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401377 | T2 DI COLGATE-PALERMO 17/338 RPR STRW | ICW
LC | 129393893 | 003/083 | T2 DI HMLTN BRNCH-CHSTR 3/83 RPR STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-08-15 | 2024-06-11 | 2025-03-19 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337240 | T2 DI HMLTN BRNCH-CHSTR 3/83 RPR STRW | ICW
LC | 129393899 | 012/090 | T2 DI CARIBOU-TABLE MTN 12/90 TOUCH | TABLEMTN | ETL.4440.TOWR | 2024-08-15 | 2024-06-11 | 2025-04-03 | On-Time |  | 2024-12-11 | 2025-06-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478235 | T2 DI CARIBOU-TABLE MTN 12/90 TOUCH | ICQ
LC | 129394243 | 021/298 | T2 DI CLAY-MARTEL 21/298 RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-08-15 | 2024-06-11 | 2025-05-12 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46339095 | T2 DI CLAY-MARTEL 21/298 RPR STRW | ICW
LC | 129394358 | 003/084 | T2 DI HMLTN BRNCH-CHSTR 3/84 RPR STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-08-15 | 2024-06-11 | 2025-03-19 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337242 | T2 DI HMLTN BRNCH-CHSTR 3/84 RPR STRW | ICW
LC | 129394390 | 020/287 | T2 DI CLAY-MARTEL 20/287 RPR STRW | VICTOR | ETL.8250.POLE.WOOD | 2024-08-15 | 2024-06-11 | 2025-05-12 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46339083 | T2 DI CLAY-MARTEL 20/287 RPR STRW | ICW
LC | 129394394 | 032/005 | T2 DI FULTON-HOPLAND 32/5 RPR JMPW | LAKEVLLE | ETL.6890.INSL.NCER | 2024-08-15 | 2024-06-11 | 2025-05-30 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Wood | Repair | 46401436 | T2 DI FULTON-HOPLAND 32/5 RPR JMPW | ICW
LC | 129408647 | 018/206 | T2 DI ELK CREEK TAP 018/206 RPL DAMW | TABLEMTN | ETL.6921.INSL.NCER | 2024-08-19 | 2024-06-11 | 2025-05-28 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46383929 | T2 DI ELK CREEK TAP 018/206 RPL DAMW | ICW
LC | 129408992 | 003/056 | T2 DI CLGTE-PALERMO 03/056 RPR INSW | SACTO | ETL.6500.INSL.NCER | 2024-08-19 | 2024-06-11 | 2024-10-08 | On-Time |  | 2024-12-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46329133 | T2 DI CLGTE-PALERMO 03/056 RPR INSW | ICW
LC | 129408994 | :005/042 | T2 DI PIT #3-PIT #1 :05/042 RPL HRDT | TABLEMTN | ETL.5400.TOWR | 2024-08-19 | 2024-06-11 | 2025-04-24 | On-Time |  | 2025-06-11 | 2025-06-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46404703 | T2 DI PIT #3-PIT #1 :05/042 RPL HRDT | ICQ
LC | 129409040 | 005/097 | T2 DI VALLEY SPRINGS #1 5/97 RPR STRW | VICTOR | ETL.8210.POLE.WOOD | 2024-08-19 | 2024-06-11 | 2025-04-17 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46339014 | T2 DI VALLEY SPRINGS #1 5/97 RPR STRW | ICW
LC | 129409049 | 017/126 | T2 DI CARIBOU-TBL MTN 017/126 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2024-08-19 | 2024-06-11 | 2025-04-03 | On-Time |  | 2025-06-11 | 2025-06-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46337223 | T2 DI CARIBOU-TBL MTN 017/126 RPL HRDT | ICQ
LC | 129409072 | 016/119 | T2 DI CRBU-TBL MTN 16/119 RPR SHLS | TABLEMTN | ETL.4440.TOWR | 2024-08-19 | 2024-06-11 | 2025-04-02 | On-Time |  | 2025-06-11 | 2025-06-11 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46337605 | T2 DI CRBU-TBL MTN 16/119 RPR SHLS | ICS
LC | 129409081 | 016/119 | T2 DI CRBU TBL MTN 16/119 RPR GYWT | TABLEMTN | ETL.4440.TOWR | 2024-08-19 | 2024-06-11 | 2025-05-30 | On-Time |  | 2025-06-11 | 2025-06-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46337224 | T2 DI CRBU TBL MTN 16/119 RPR GYWT | ICQ
LC | 129409084 | 016/119 | T2 DI CRBU-TBL MTN 16/119 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2024-08-19 | 2024-06-11 | 2025-05-30 | On-Time |  | 2025-06-11 | 2025-06-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46337225 | T2 DI CRBU-TBL MTN 16/119 RPL HRDT | ICQ
LC | 129409140 | 003/085 | T2 DI HMLTN BRNCH-CHSTER 3/85 RPR JMPW | TABLEMTN | ETL.7000.INSL.NCER | 2024-08-19 | 2024-06-11 | 2025-03-20 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46337244 | T2 DI HMLTN BRNCH-CHSTER 3/85 RPR JMPW | ICW
LC | 129409142 | 003/085 | T2 DI HMLTON BRNCH-CHSTR 3/85 RPR CRSW | TABLEMTN | ETL.7000.POLE.NWOD | 2024-08-19 | 2024-06-11 | 2025-03-20 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46337245 | T2 DI HMLTON BRNCH-CHSTR 3/85 RPR CRSW | ICW
LC | 129409206 | 001/019 | T2 DI COLGTE-SMRTVLE #1 1/019R RPL ANCW | SACTO | ETL.6510.POLE.STPS | 2024-08-19 | 2024-06-11 | 2024-10-09 | On-Time |  | 2024-12-11 | 2025-06-11 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35576470 | T2 DI COLGTE-SMRTVLE #1 1/019R RPL ANCW | 93E
LC | 129409208 | 008/171 | T2 DI HMLTON BRNCH-CHSTR 8/171 RPL ANCW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-08-19 | 2024-06-11 | 2025-03-21 | On-Time |  | 2025-06-11 | 2025-06-11 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586831 | T2 DI HMLTON BRNCH-CHSTR 8/171 RPL ANCW | 93E
LC | 129409291 | 010/081C | T2 DI CARIBOU-TBL MTN 10/081C RPR GYWT | TABLEMTN | ETL.4440.POLE.NWOD | 2024-08-19 | 2024-06-11 | 2025-04-02 | On-Time |  | 2025-06-11 | 2025-06-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46337226 | T2 DI CARIBOU-TBL MTN 10/081C RPR GYWT | ICQ
LC | 129409297 | 001/057 | T2 DI HMLTN BRNCH-CHSTR 1/057 COTTER | TABLEMTN | ETL.7000.INSL.NCER | 2024-08-19 | 2024-06-11 | 2025-03-18 | On-Time |  | 2025-06-11 | 2025-06-11 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46337246 | T2 DI HMLTN BRNCH-CHSTR 1/057 COTTER | ICW
LC | 129409329 | 006/116 | T2 DI COLGATE-PALERMO 6/116 RPL STRW | SACTO | ETL.6500.POLE.WOOD | 2024-08-19 | 2024-06-11 | 2025-05-03 | On-Time |  | 2025-06-11 | 2025-06-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586881 | T2 DI COLGATE-PALERMO 6/116 RPL STRW | 70Y
LC | 129928095 | 008/057 | T3 OLEUM-G #1 8/57 RPR FOND | CONCORD | ETL.3150.TOWR | 2024-12-11 | 2024-12-11 | 2024-12-16 | On-Time |  | 2025-06-11 | 2025-06-11 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3 FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416101 | T3 OLEUM-G #1 8/57 RPR FOND | ICQ
LC | 129971451 | 000/002 | T2NT SOBRANTE-R #1 000/002 RPR FOND | CONCORD | ETL.3770.TOWR | 2024-12-13 | 2024-06-11 | 2024-06-11 | Past Due |  | 2027-06-11 | 2025-06-11 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair
LC | 123826467 | 004/006 | T3NT EI WISHON-SAN JQN #3 4/6 RPR INSW | FRESNO | ETL.9340.INSL.NCER | 2022-06-12 | 2022-06-12 | 2023-04-27 | On-Time |  | 2025-06-12 | 2025-06-12 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR3 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 45489584 | T3NT EI WISHON-SAN JQN #3 4/6 RPR INSW | ICW
LC | 129063947 | C009/037 | T2 MOSS LANDING-COBURN C9/37 RMV VEG | MOSSLNDG | ETL.5330.TOWR | 2024-06-12 | 2024-06-12 | 2024-06-12 | Past Due |  | 2025-06-12 | 2025-06-12 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 129064715 | 016/523 | T2 EI SPAULDING-SUMMIT 16/523 RPL POLE | SACTO | ETL.8060.POLE.WOOD | 2024-06-12 | 2024-06-12 | 2024-06-12 | Past Due |  | 2025-06-12 | 2025-06-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35638113 | T2 EI SPAULDING-SUMMIT 16/523 RPL POLE | 70Y
LC | 129064812 | 042/335 | T2 EI BRDGVLL-CTTNWD 42/335R RMV VEG | TABLEMTN | ETL.1110.POLE.WDPS | 2024-06-12 | 2024-06-12 | 2024-09-17 | On-Time |  | 2024-09-12 | 2025-06-12 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB DURA BRIN | Overgrown | Vegetation | Trim
LC | 129065221 | C008/035 | T2 EI MOSS LANDING-COBURN C8/35 RMV VEG | MOSSLNDG | ETL.5330.TOWR | 2024-06-12 | 2024-06-12 | 2025-04-18 | On-Time |  | 2025-06-12 | 2025-06-12 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129066017 | 004/032 | T2 VACA-VACAVILLE-JMSN-N 4/32 TOUCH | LAKEVLLE | ETL.4100.TOWR | 2024-06-12 | 2024-06-12 | 2025-03-28 | On-Time |  | 2024-12-12 | 2025-06-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491089 | T2 VACA-VACAVILLE-JMSN-N 4/32 TOUCH | ICQ
LC | 129066270 | 000/005 | T2 COLGATE-SMARTVILLE #2 0/5 CGI VEG | SACTO | ETL.6520.POLE.NWOD | 2024-06-12 | 2024-06-12 | 2025-04-21 | On-Time |  | 2024-09-12 | 2025-06-12 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | Vegetation Overgrown | Other | Access Issue
LC | 129067213 | 002/024 | T2 DI ROCK CREEK-POE 02/024 RPL DAMS | TABLEMTN | ETL.5630.INSL.CERA | 2024-06-12 | 2024-06-12 | 2025-04-27 | On-Time |  | 2025-06-12 | 2025-06-12 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Damper-Steel | Replace | 46383942 | T2 DI ROCK CREEK-POE 02/024 RPL DAMS | ICS
LC | 129067300 | 001/016 | T2 DI ROCK CREEK-POE 1/16 RPR JUMS | TABLEMTN | ETL.5630.INSL.CERA | 2024-06-12 | 2024-06-12 | 2025-04-27 | On-Time |  | 2025-06-12 | 2025-06-12 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46268032 | T2 DI ROCK CREEK-POE 01/016 RPR JUMS | ICS
LC | 129067366 | :001/009 | T2 ROCK CREEK-POE :1/9 COMPLETE | TABLEMTN | ETL.5630.TOWR | 2024-06-12 | 2024-06-12 | 2025-04-03 | On-Time |  | 2025-06-12 | 2025-06-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46382042 | T2 DI ROCK CREEK-POE :1/9 BENT STEEL | ICQ
LC | 129067409 | 002/023 | T2 DI ROCK CREEK-POE 2/23 RPL HRDT | TABLEMTN | ETL.5630.TOWR | 2024-06-12 | 2024-06-12 | 2025-06-06 | On-Time |  | 2025-06-12 | 2025-06-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46382043 | T2 DI ROCK CREEK-POE 2/23 RPL HRDT | ICQ
LC | 129067724 | 001/015 | T2 DI ROCK CREEK-POE 01/015 RPL HRDT | TABLEMTN | ETL.5630.TOWR | 2024-06-12 | 2024-06-12 | 2025-04-27 | On-Time |  | 2025-06-12 | 2025-06-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46382045 | T2 DI ROCK CREEK-POE 01/015 RPL HRDT | ICQ
LC | 129067726 | 001/015 | T2 DI ROCK CREEK-POE 1/15 RPR JUMS | TABLEMTN | ETL.5630.INSL.NCER | 2024-06-12 | 2024-06-12 | 2025-04-27 | On-Time |  | 2025-06-12 | 2025-06-12 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46268022 | T2 DI ROCK CREEK-POE 01/015 RPR JUMS | ICS
LC | 129076830 | 011/087C | T2 DI CARIBOU-TABLE MNT 11/87C RPR GYWT | TABLEMTN | ETL.4440.POLE.NWOD | 2024-06-14 | 2024-06-12 | 2025-02-18 | On-Time |  | 2024-09-12 | 2025-06-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46272323 | T2 DI CARIBOU-TABLE MNT 11/87C RPR GYWT | ICQ
LC | 129077233 | 011/087B | T2 DI CARIBOU-TABLE MTN 11/87B RPR GYWT | TABLEMTN | ETL.4440.POLE.NWOD | 2024-06-14 | 2024-06-12 | 2025-04-02 | On-Time |  | 2025-06-12 | 2025-06-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46517302 | T2 DI CARIBOU-TABLE MTN 11/87B RPR GYWT | ICQ
LC | 129078451 | 004/114 | T2 DI HMLTN BRNCH CHSTR 04/114 RPR STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-06-14 | 2024-06-12 | 2024-07-29 | On-Time |  | 2025-06-12 | 2025-06-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46287726 | T2 DI HMLTN BRNCH CHSTR 04/114 RPR STRW | ICW
LC | 129078493 | 000/025 | T2 DI HMLTN BRNCH CHSTR 00/025 RPR GYWW | TABLEMTN | ETL.7000.POLE.NWOD | 2024-06-14 | 2024-06-12 | 2025-01-08 | On-Time |  | 2025-06-12 | 2025-06-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46311127 | T2 DI HMLTN BRNCH CHSTR 00/025 RPR GYWW | ICW
LC | 129087292 | 004/115 | T2 DI HAMLTN BRNCH-CHSTR 04/115 RPR JUMW | TABLEMTN | ETL.7000.INSL.NCER | 2024-06-17 | 2024-06-12 | 2025-03-19 | On-Time |  | 2025-06-12 | 2025-06-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46311126 | T2 DI HAMLTN BRNCH-CHSTR 04/115 RPR JUMW | ICW
LC | 129224733 | 000/004A | T2 DI COLGATE-SMARTVILLE #2 0/4A RMV VEG | SACTO | ETL.6520.POLE.WOOD | 2024-07-15 | 2024-06-12 | 2024-12-06 | On-Time |  | 2025-06-12 | 2025-06-12 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 129280152 | 019/000 | T2 DI FULTON-HOPLAND 19/0 RPL STRW | LAKEVLLE | ETL.6890.POLE.WOOD | 2024-07-23 | 2024-06-12 | 2025-03-26 | On-Time |  | 2025-06-12 | 2025-06-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | Rotten | Structure-Wood | Replace | 35586909 | T2 DI FULTON-HOPLAND 19/0 RPL STRW | 70Y
LC | 129294226 | 006/136 | T2 DI HMLTN BRNCH-CHSTR 6/136 RPR CNDW | TABLEMTN | ETL.7000.INSL.NCER | 2024-07-26 | 2024-06-12 | 2025-03-18 | On-Time |  | 2025-06-12 | 2025-06-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Wood | Repair | 46337213 | T2 DI HMLTN BRNCH-CHSTR 6/136 RPR CNDW | ICW
LC | 129295652 | 006/134 | T2 DI HAMILTN BRNCH CHSTR 6/134 RPL POLE | TABLEMTN | ETL.7000.POLE.WOOD | 2024-07-26 | 2024-06-12 | 2025-03-19 | On-Time |  | 2025-06-12 | 2025-06-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586830 | T2 DI HAMILTN BRNCH CHSTR 6/134 RPL POLE | 70Y
LC | 129295708 | 008/172 | T2 DI VLY SPNGS#1 08/172 RPR STRW | VICTOR | ETL.8210.POLE.WOOD | 2024-07-26 | 2024-06-12 | 2025-04-21 | On-Time |  | 2025-06-12 | 2025-06-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46339019 | T2 DI VLY SPNGS#1 08/172 RPR STRW | ICW
LC | 129408721 | 001/048 | T2 DI HMLTN BRNCH-CHSTR 1/048 RPR GYWW | TABLEMTN | ETL.7000.POLE.NWOD | 2024-08-19 | 2024-06-12 | 2025-01-08 | On-Time |  | 2025-06-12 | 2025-06-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337243 | T2 DI HMLTN BRNCH-CHSTR 1/048 RPR GYWW | ICW
LC | 129408726 | 000/003 | T2 DI COLGATE-CHALLENGE 0/3 RPR INSW | SACTO | ETL.6480.INSL.NCER | 2024-08-19 | 2024-06-12 | 2025-04-06 | On-Time |  | 2025-06-12 | 2025-06-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46454272 | T2 DI CLGT-CHALLENGE 000/003 RPR INSW | ICW
LC | 129409088 | 039/003 | T2 DI ELK GUALALA 39/3 CANCEL | WILLITS | ETL.8410.INSL.NCER | 2024-08-19 | 2024-06-12 | 2024-06-12 | Past Due |  | 2025-06-12 | 2025-06-12 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCM OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Replace | 35586904 | T2 DI ELK GUALALA 39/003 RPL INSW | 93I
LC | 129409133 | 002/068-GUY | T2 DI HMLTN BRNCH-CHSTR 2/68-G RPL GYPL | TABLEMTN | ETL.7000.POLE.WOOD | 2024-08-19 | 2024-06-12 | 2025-03-19 | On-Time |  | 2025-06-12 | 2025-06-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Rotten | Guy Pole-Wood | Replace | 35586828 | T2 DI HMLTN BRNCH-CHSTR 2/68-GY RPL STRW | 70Y
LC | 129409185 | 000/006 | T2 DI CLGT-CHALLENGE 0/006 RPR INSW | SACTO | ETL.6480.INSL.NCER | 2024-08-19 | 2024-06-12 | 2025-04-06 | On-Time |  | 2025-06-12 | 2025-06-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46454273 | T2 DI CLGT-CHALLENGE 0/006 RPR INSW | ICW
LC | 129409266 | 001/022 | T2 CLGT-PALERMO 001/022 RPL STRW | SACTO | ETL.6500.POLE.WOOD | 2024-08-19 | 2024-06-12 | 2025-05-01 | On-Time |  | 2025-06-12 | 2025-06-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586838 | T2 DI CLGT-PALERMO 001/022 RPL STRW | 70Y
LC | 129409404 | 001/020 | T2 DI CLGTE SMTVIL#2 01/020 RPR ANCW | SACTO | ETL.6520.POLE.STPS | 2024-08-19 | 2024-06-12 | 2025-02-19 | On-Time |  | 2025-06-12 | 2025-06-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46419450 | T2 DI CLGTE SMTVIL#2 01/020 RPR ANCW | ICW
LC | 129409406 | 010/195 | T2 DI VALLEY SPRINGS#1 10/195 RPR STRW | VICTOR | ETL.8210.POLE.WOOD | 2024-08-19 | 2024-06-12 | 2024-06-12 | Past Due |  | 2025-06-12 | 2025-06-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46339085 | T2 DI VALLEY SPRINGS#1 10/195 RPR STRW | ICW
LC | 129409424 | 001/021 | T2 DI COLGTE-PALERMO 001/021 RPR CRSW | SACTO | ETL.6500.POLE.NWOD | 2024-08-19 | 2024-06-12 | 2025-03-25 | On-Time |  | 2025-06-12 | 2025-06-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46401384 | T2 DI COLGTE-PALERMO 001/021 RPR CRSW | ICW
LC | 129420211 | 008/064 | T2 CARIBOU TBL MTN 08/064 RMV VEG | TABLEMTN | ETL.4440.TOWR | 2024-08-21 | 2024-06-12 | 2024-06-12 | Past Due |  | 2025-06-12 | 2025-06-12 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129951335 | ?001/013 | T3 SNEATH LNE-HLF MN BY ?1/13 GO95 CLEAR | METCALF | ETL.7212.POLE.WOOD | 2024-12-12 | 2024-12-12 | 2025-05-05 | On-Time |  | 2025-06-12 | 2025-06-12 | 401T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO CLMB FRAB BRIN | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35606488 | T3 SNEATH LNE-HLF MN BY ?1/13 GO95 CLEAR | 93G
LC | 129951338 | ?004/000 | T3 SNEATH LANE-HLF MN BY ?4/0 GO95 CLEAR | METCALF | ETL.7212.POLE.WOOD | 2024-12-12 | 2024-12-12 | 2025-05-11 | On-Time |  | 2025-06-12 | 2025-06-12 | 401T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO CLMB FRAB BRIN | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35606968 | T3 SNEATH LANE-HLF MN BY ?4/0 GO95 CLEAR | 93G
LC | 123832092 | 001/019 | T2NT EI BRIDGEVLE-CTONWD 1/19 ADSS MRKW | TABLEMTN | ETL.1110.POLE.STPS | 2022-06-13 | 2022-06-13 | 2024-01-08 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 46093197 | T2NT EI BRIDGEVLE-CTONWD 1/19 ADSS MRKW | ICW
LC | 123832124 | 001/018 | T2NT EI BRIDGEVILE-COTNWD 1/18 RPR ADSS | TABLEMTN | ETL.1110.POLE.STPS | 2022-06-13 | 2022-06-13 | 2025-02-06 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | ADSS - Wood | Repair | 46311060 | T2NT EI BRIDGEVILE-COTNWD 1/18 RPR ADSS | ICW
LC | 123852503 | 035/166 | T2NT DI R MTN-T MTN #1 35/166 RMV STEP | TABLEMTN | ETL.6060.TOWR | 2022-06-15 | 2022-06-13 | 2023-08-08 | On-Time |  | 2025-06-13 | 2025-06-13 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 45644455 | T2NT DI R MTN-T MTN #1 35/166 RMV STEP | ICQ
LC | 129069457 | C019/079 | T2 MOSS LANDING-COBURN C19/79 RPL INSS | MOSSLNDG | ETL.5330.INSL | 2024-06-13 | 2024-06-13 | 2025-04-08 | On-Time |  | 2025-06-13 | 2025-06-13 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35610624 | T2 MOSS LANDING-COBURN C19/79 RPL INSS | 93K
LC | 129070056 | 005/066 | T2 BURNS-LONE STAR #1 5/66 RPL INSW | MOSSLNDG | ETL.6230.INSL | 2024-06-13 | 2024-06-13 | 2025-03-14 | On-Time |  | 2025-06-13 | 2025-06-13 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574638 | T2 BURNS-LONE STAR #1 5/66 RPL INSW | 93I
LC | 129070159 | 005/066 | T2 BURNS-LONE STAR #1 5/66 RPR GYWW | MOSSLNDG | ETL.6230.POLE.WOOD | 2024-06-13 | 2024-06-13 | 2025-03-14 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46391302 | T2 BURNS-LONE STAR #1 5/66 RPR GYWW | ICW
LC | 129070204 | 005/068 | T2 BURNS-LONE STAR #1 5/68 RPL INSW | MOSSLNDG | ETL.6230.INSL | 2024-06-13 | 2024-06-13 | 2024-06-13 | Past Due |  | 2025-06-13 | 2025-06-13 | 508 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 31655006 | T2 BURNS-LONE STAR #1 05/65 GO95 | 93G
LC | 129070247 | 043/842 | T2 HAT CREEK #1-WSTWD 43/842 RPR STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-13 | 2024-06-13 | 2025-05-28 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46416163 | T2 EI HAT CREEK #1-WSTWD 43/842 RPR WDPK | ICW
LC | 129070343 | 028/119 | T2 MOSS LANDING-METCALF 28/119 RPR INSS | MOSSLNDG | ETL.6050.INSL | 2024-06-13 | 2024-06-13 | 2025-04-10 | On-Time |  | 2025-06-13 | 2025-06-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46305545 | T2 MOSS LANDING-METCALF 28/119 RPR INSS | ICS
LC | 129071165 | 068/282 | T2 EI RND MT-TBL MTN#2 68/282 RPR INSS | TABLEMTN | ETL.6070.INSL | 2024-06-13 | 2024-06-13 | 2024-10-28 | On-Time |  | 2024-12-13 | 2025-06-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46269322 | T2 EI RND MT-TBL MTN#2 68/282 RPR INSS | ICS
LC | 129071259 | 019/614 | T2 EI SPAULDING-SUMMIT 19/614 COMPLETE | SACTO | ETL.8060.POLE.WOOD | 2024-06-13 | 2024-06-13 | 2024-07-31 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46283561 | T2 EI SPAULDING-SUMMIT 19/614 RPR GYWW | ICW
LC | 129071359 | 019/615 | T2 EI SPAULDING-SUMMIT 19/615 RPR GYWW | SACTO | ETL.8060.POLE.WOOD | 2024-06-13 | 2024-06-13 | 2024-07-25 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46283562 | T2 EI SPAULDING-SUMMIT 19/615 RPR GYWW | ICW
LC | 129071893 | 008/097 | T2 DRUM-SUMMIT #2 008/097 RPL INSW | SACTO | ETL.1450.INSL.CERA | 2024-06-13 | 2024-06-13 | 2024-06-13 | Past Due |  | 2025-06-13 | 2025-06-13 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Wood | Replace | 35611373 | T2 DRUM-SUMMIT #2 008/097 RPL INSW | 93I
LC | 129071978 | 019/616 | T2 EI SPAULDING-SUMMIT 19/616 RPR GYWW | SACTO | ETL.8060.POLE.WOOD | 2024-06-13 | 2024-06-13 | 2024-07-25 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46283564 | T2 EI SPAULDING-SUMMIT 19/616 RPR GYWW | ICW
LC | 129071991 | 019/616 | T2 SPAULDING-SUMMIT 19/616 RPR ANCW | SACTO | ETL.8060.POLE.WOOD | 2024-06-13 | 2024-06-13 | 2025-06-07 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46284431 | T2 EI SPAULDING-SUMMIT 19/616 RPR ANCW | ICW
LC | 129072961 | C012/051 | T2 EI MOSS LANDING-COBURN C12/51 RMV VEG | MOSSLNDG | ETL.5330.TOWR | 2024-06-13 | 2024-06-13 | 2025-05-07 | On-Time |  | 2025-06-13 | 2025-06-13 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 129072962 | C011/049 | T2 EI MOSS LANDING-COBURN C11/49 RMV VEG | MOSSLNDG | ETL.5330.TOWR | 2024-06-13 | 2024-06-13 | 2025-04-21 | On-Time |  | 2025-06-13 | 2025-06-13 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 129072970 | C010/043 | T2 EI MOSS LANDING-CBURN C10/43 COMPLETE | MOSSLNDG | ETL.5330.INSL.NCER | 2024-06-13 | 2024-06-13 | 2024-08-06 | On-Time |  | 2025-06-13 | 2025-06-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46266214 | T2 EI MOSS LANDING-COBURN C10/43 COTTER | ICS
LC | 129072980 | C011/047 | T2 EI MOSS LANDING-COBURN C11/47 RMV VEG | MOSSLNDG | ETL.5330.TOWR | 2024-06-13 | 2024-06-13 | 2025-05-07 | On-Time |  | 2025-06-13 | 2025-06-13 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129073554 | :003/018 | T2 DI RCK CRK-POE 3/18 RPR RETAIN WALL | TABLEMTN | ETL.5630.TOWR | 2024-06-13 | 2024-06-13 | 2025-06-06 | On-Time |  | 2025-06-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46382046 | T2 DI RCK CRK-POE 3/18 RPR RETAIN WALL | ICQ
LC | 129073738 | :009/069 | T2 ROCK CREEK-POE :9/69 RPL HRDT | TABLEMTN | ETL.5630.TOWR | 2024-06-13 | 2024-06-13 | 2025-06-27 | Past Due |  | 2024-12-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Hardware-Tower | Replace | 46382047 | T2 DI ROCK CREEK-POE :9/69 RPL HRDT | ICQ
LC | 129073775 | :003/020A | T2 DI ROCK CREEK-POE :3/20A RPR GYWT | TABLEMTN | ETL.5630.POLE.NWOD | 2024-06-13 | 2024-06-13 | 2024-08-26 | On-Time |  | 2024-09-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46268033 | T2 DI ROCK CREEK-POE :3/20A RPR GYWT | ICQ
LC | 129073823 | :000/003 | T2 RE ROCK CREEK POE 0/3 RPL HRDT | TABLEMTN | ETL.5630.TOWR | 2024-06-13 | 2024-06-13 | 2025-04-26 | On-Time |  | 2025-06-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46382048 | T2 DI ROCK CREEK POE 0/3 RPL HRDT | ICQ
LC | 129073857 | :003/020C | T2 DI ROCK CREEK-POE :3/20C RPR GYWT | TABLEMTN | ETL.5630.POLE.NWOD | 2024-06-13 | 2024-06-13 | 2024-08-26 | On-Time |  | 2024-09-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46267904 | T2 DI ROCK CREEK-POE :3/20C RPR GYWT | ICQ
LC | 129073898 | 003/029 | T2 DI ROCK CREEK POE 3/29 RPR CONS | TABLEMTN | ETL.5630.INSL | 2024-06-13 | 2024-06-13 | 2025-04-27 | On-Time |  | 2025-06-13 | 2025-06-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Conductor-Steel | Repair | 46383943 | T2 DI ROCK CREEK POE 3/29 RPR CONS | ICS
LC | 129075379 | 001/056 | T2 EI SPAULDING-SUMMIT 1/56L RPR GYWW | SACTO | ETL.8060.POLE.STPS | 2024-06-14 | 2024-06-13 | 2025-04-22 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46400325 | T2 EI SPAULDING-SUMMIT 1/56L RPR GYWW | ICW
LC | 129075409 | 001/056 | T2 EI SPAULDING-SUMMIT 1/56R RPR GYWW | SACTO | ETL.8060.POLE.STPS | 2024-06-14 | 2024-06-13 | 2025-04-22 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46400326 | T2 EI SPAULDING-SUMMIT 1/56R RPR GYWW | ICW
LC | 129075421 | 001/056 | T2 EI SPAULDING-SUMMIT 1/56C RPR GYWW | SACTO | ETL.8060.POLE.STPS | 2024-06-14 | 2024-06-13 | 2025-04-22 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46400327 | T2 EI SPAULDING-SUMMIT 1/56C RPR GYWW | ICW
LC | 129075451 | 001/063 | T2 EI SPAULDING-SUMMIT 1/63 RPR GYWW | SACTO | ETL.8060.POLE.WOOD | 2024-06-14 | 2024-06-13 | 2024-06-26 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46271672 | T2 EI SPAULDING-SUMMIT 1/63 RPR GYWW | ICW
LC | 129075456 | 026/204 | T2 EI MSSRI FLT-GLD HLL #1 26/204 COTTER | SACTO | ETL.2660.INSL.NCER | 2024-06-14 | 2024-06-13 | 2025-06-05 | On-Time |  | 2025-06-13 | 2025-06-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46324621 | T2 EI MSSRI FLT-GLD HLL #1 26/204 COTTER | ICS
LC | 129075457 | 001/061 | T2 SPAULDING-SUMMIT 1/61 RPL INSW | SACTO | ETL.8060.INSL.NCER | 2024-06-14 | 2024-06-13 | 2024-06-13 | Past Due |  | 2025-06-13 | 2025-06-13 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572869 | T2 EI SPAULDING-SUMMIT 1/61 RPL INSW | 93I
LC | 129077201 | 009/064 | T2 DI CORTINA-VACA 9/64 RPR OPGW | SACTO | ETL.4540.TOWR | 2024-06-14 | 2024-06-13 | 2024-08-28 | On-Time |  | 2025-06-13 | 2025-06-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46269314 | T2 DI CORTINA-VACA 9/64 RPR OPGW | ICS
LC | 129284463 | 008/162 | T2 DI VALLEY SPRINGS #1 08/162 RPL STRW | VICTOR | ETL.8210.POLE.WOOD | 2024-07-24 | 2024-06-13 | 2025-04-21 | On-Time |  | 2025-06-13 | 2025-06-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35589351 | T2 DI VALLEY SPRINGS #1 08/162 RPL STRW | 70Y
LC | 129284585 | 008/167 | T2 DI VALLEY SPRINGS#1 08/167 RPL STRW | VICTOR | ETL.8210.POLE.WOOD | 2024-07-24 | 2024-06-13 | 2025-04-21 | On-Time |  | 2025-06-13 | 2025-06-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35597544 | T2 DI VALLEY SPRINGS#1 08/167 RPL STRW | 70Y
LC | 129284624 | :019/098 | T2 CHC-SALINAS-SLDAD :19/98 COMPLETE | MOSSLNDG | ETL.2900.TOWR | 2024-07-24 | 2024-06-13 | 2025-05-20 | On-Time |  | 2025-06-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416760 | T2 DI CHC-SALINAS-SLDAD :19/98 BNT STEEL | ICQ
LC | 129284730 | 006/107 | T2 DI CNTRVILLE-TABLE MTN 6/107 RPL STRW | TABLEMTN | ETL.6320.POLE.WOOD | 2024-07-24 | 2024-06-13 | 2025-03-03 | On-Time |  | 2025-06-13 | 2025-06-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586835 | T2 DI CNTRVILLE-TABLE MTN 6/107 RPL STRW | 70Y
LC | 129284826 | :019/101 | T2 DI CHC-SALNS-SLDAD :19/101 RPL RPTS | MOSSLNDG | ETL.2900.TOWR | 2024-07-24 | 2024-06-13 | 2025-04-10 | On-Time |  | 2025-06-13 | 2025-06-13 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46391418 | T2 DI CHC-SALNS-SLDAD :19/101 RPL RPTS | ICB
LC | 129284872 | :019/097 | T2 CHC-SALNS-SLDAD :19/097 COMPLETE | MOSSLNDG | ETL.2900.TOWR | 2024-07-24 | 2024-06-13 | 2025-05-20 | On-Time |  | 2025-06-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416763 | T2 DI CHC-SALNS-SLDAD :19/097 RPR STRT | ICQ
LC | 129292993 | 000/015 | T2 DI CLGT-PALERMO 000/015R RPR GYWW | SACTO | ETL.6500.POLE.STPS | 2024-07-26 | 2024-06-13 | 2025-01-13 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337346 | T2 DI CLGT-PALERMO 000/015R RPR GYWW | ICW
LC | 129293529 | 012/231 | T2 DI VLY SPRNGS#1 12/231 RPL STRW | VICTOR | ETL.8210.POLE.WOOD | 2024-07-26 | 2024-06-13 | 2025-04-24 | On-Time |  | 2025-06-13 | 2025-06-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35597545 | T2 DI VLY SPRNGS#1 12/231 RPL STRW | 70Y
LC | 129293632 | :022/119 | T2 DI CZY HRS CYN SLS SLD 22/119 BNT STL | MOSSLNDG | ETL.2900.TOWR | 2024-07-26 | 2024-06-13 | 2025-05-21 | On-Time |  | 2025-06-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416767 | T2 DI CZY HRS CYN SLS SLD 22/119 BNT STL | ICQ
LC | 129294061 | :020/106 | T2 DI CZY HRS CYN SLS SLD 20/106 BNT STL | MOSSLNDG | ETL.2900.TOWR | 2024-07-26 | 2024-06-13 | 2025-05-21 | On-Time |  | 2025-06-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416768 | T2 DI CZY HRS CYN SLS SLD 20/106 BNT STL | ICQ
LC | 129294064 | :020/106 | T2 DI CZY HRS CYN SLNS SLD 20/106 COTTER | MOSSLNDG | ETL.2900.INSL.CERA | 2024-07-26 | 2024-06-13 | 2024-09-10 | On-Time |  | 2024-09-13 | 2025-06-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46302113 | T2 DI CZY HRS CYN SLNS SLD 20/106 COTTER | ICS
LC | 129408729 | 008/163 | T2 DI VALLEY SPRINGS #1 008/163 RPR INSW | VICTOR | ETL.8210.INSL.NCER | 2024-08-19 | 2024-06-13 | 2025-04-21 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46339018 | T2 DI VALLEY SPRINGS #1 008/163 RPR INSW | ICW
LC | 129408838 | 000/008 | T2 DI PALERMO-WYANDOTTE 0/8 RMV VEG | TABLEMTN | ETL.4315.TOWR | 2024-08-19 | 2024-06-13 | 2025-01-23 | On-Time |  | 2025-06-13 | 2025-06-13 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129408896 | :022/118 | T2 CRAZY HSE CY-SS#1 :22/118 RPR STRT | MOSSLNDG | ETL.2900.TOWR | 2024-08-19 | 2024-06-13 | 2025-05-21 | On-Time |  | 2025-06-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416772 | T2 DI CRAZY HSE CY-SS#1 :22/118 RPR STRT | ICQ
LC | 129408952 | :015/082 | T2 DI CHC-SALINAS-SLDD#2 :15/82 RPL INSS | MOSSLNDG | ETL.2910.INSL.CERA | 2024-08-19 | 2024-06-13 | 2025-05-01 | On-Time |  | 2025-06-13 | 2025-06-13 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE SPCR ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35597755 | T2 DI CRZY HRS CAYN-SLAS 24/124 RPL INSS | 93K
LC | 129408957 | :015/082 | T2 DI CHC-SALINAS-SLDD#2 :15/82 RPL HNGR | MOSSLNDG | ETL.2910.INSL.CERA | 2024-08-19 | 2024-06-13 | 2025-05-01 | On-Time |  | 2025-06-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46416773 | T2 DI CHC-SALINAS-SLDD#2 :15/82 RPL HNGR | ICQ
LC | 129408988 | 017/128 | T2 DI CARIBOU-TABLE MTN 17/128 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2024-08-19 | 2024-06-13 | 2025-04-03 | On-Time |  | 2025-06-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46354101 | T2 DI CARIBOU-TABLE MTN 17/128 RPL HRDT | ICQ
LC | 129409068 | :020/107 | T2 DI CHC-SALINS SLDD#1 :20/107 RPR STRT | MOSSLNDG | ETL.2900.TOWR | 2024-08-19 | 2024-06-13 | 2025-05-21 | On-Time |  | 2025-06-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416774 | T2 DI CHC-SALINS SLDD#1 :20/107 RPR STRT | ICQ
LC | 129409100 | 011/086A | T2 DI CARIBOU-TABLE MTN 11/86A RPR JUMS | TABLEMTN | ETL.4440.INSL.NCER | 2024-08-19 | 2024-06-13 | 2025-04-05 | On-Time |  | 2025-06-13 | 2025-06-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46337606 | T2 DI CARIBOU-TABLE MTN 11/86A RPR JUMS | ICS
LC | 129409163 | :019/100 | T2 CHC SALNAS-SLDD#1 :19/100 COMPLETE | MOSSLNDG | ETL.2900.TOWR | 2024-08-19 | 2024-06-13 | 2025-05-20 | On-Time |  | 2025-06-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416776 | T2 DI CHC SALNAS-SLDD#1 :19/100 RPR STRT | ICQ
LC | 129409195 | 000/010 | T2 DI COLGTE-SMRTVLE #2 0/10 RPR ANCW | SACTO | ETL.6520.POLE.WOOD | 2024-08-19 | 2024-06-13 | 2025-02-20 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46419449 | T2 DI COLGTE-SMRTVLE #2 0/10 RPR ANCW | ICW
LC | 129409242 | 012/078 | T2 DI CRTNA-VACA 12/78 RPR OPGW | SACTO | ETL.4540.TOWR | 2024-08-19 | 2024-06-13 | 2024-08-28 | On-Time |  | 2024-09-13 | 2025-06-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46306134 | T2 DI CRTNA-VACA 12/78 RPR OPGW | ICS
LC | 129409244 | 012/236 | T2 DI VLLY SPRNGS #1 12/236 RPL STRW | VICTOR | ETL.8210.POLE.WOOD | 2024-08-19 | 2024-06-13 | 2025-04-25 | On-Time |  | 2025-06-13 | 2025-06-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35597546 | T2 DI VLLY SPRNGS #1 12/236 RPL STRW | 70Y
LC | 129409415 | :016/086 | T2 DI CHC-SALINAS-SOLDAD#1 :16/86 COTTER | MOSSLNDG | ETL.2900.INSL.CERA | 2024-08-19 | 2024-06-13 | 2024-11-05 | On-Time |  | 2024-09-13 | 2025-06-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46339933 | T2 DI CHC-SALINAS-SOLDAD#1 :16/86 COTTER | ICS
LC | 129409418 | :016/084 | T2 DI CHC-SALNS-SOLDAD#1 :16/84 RPR JUMS | MOSSLNDG | ETL.2900.INSL.NCER | 2024-08-19 | 2024-06-13 | 2025-05-21 | On-Time |  | 2025-06-13 | 2025-06-13 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Steel | Repair | 46393865 | T2 DI CHC-SALNS-SOLDAD#1 :16/84 RPR JUMS | ICS
LC | 129409444 | 011/086B | T2 CARIBOU-TABLE MTN 11/86B RMV VEG | TABLEMTN | ETL.4440.POLE.NWOD | 2024-08-19 | 2024-06-13 | 2024-06-13 | Past Due |  | 2025-06-13 | 2025-06-13 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129409487 | 018/130 | T2 CARIBOU TABLE MTN 18/130 RPR GYWT | TABLEMTN | ETL.4440.TOWR | 2024-08-19 | 2024-06-13 | 2025-06-06 | On-Time |  | 2025-06-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46337227 | T2 DI CARIBOU TABLE MTN 18/130 RPR GYWT | ICQ
LC | 129420213 | 010/199 | T2 DI VALLEY SPRINGS #1 10/199 RPR INSW | VICTOR | ETL.8210.INSL.NCER | 2024-08-21 | 2024-06-13 | 2024-06-13 | Past Due |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46339086 | T2 DI VALLEY SPRINGS #1 10/199 RPR INSW | ICW
LC | 129420217 | A002/044 | T2 DI VALLEY SPRINGS #1 A02/044 RPL STRW | VICTOR | ETL.8210.POLE.WOOD | 2024-08-21 | 2024-06-13 | 2025-05-03 | On-Time |  | 2025-06-13 | 2025-06-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35597547 | T2 DI VALLEY SPRINGS #1 A02/044 RPL STRW | 70Y
LC | 129420261 | 016/333 | T2 DI CLGTE-PLMERO 16/333 RPR STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-08-21 | 2024-06-13 | 2025-02-05 | On-Time |  | 2025-06-13 | 2025-06-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401387 | T2 DI CLGTE-PLMERO 16/333 RPR STRW | ICW
LC | 129615030 | 004/025 | T2 PITTSBURG-CLYTN #3 4/25 REGRADE | CONCORD | ETL.3290.TOWR | 2024-10-01 | 2024-06-13 | 2025-01-07 | On-Time |  | 2025-06-13 | 2025-06-13 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46400052 | T2 PITTSBURG-CLYTN #3 4/25 REGRADE | ICQ
LC | 129971485 | 018/124 | T3 METCALF-GREEN VALLEY 18/124R RPL POLE | MOSSLNDG | ETL.2540.POLE.WDPS | 2024-12-13 | 2024-12-13 | 2025-05-02 | On-Time |  | 2025-06-13 | 2025-06-13 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW TNT SWRK COMP OH FMOB TR3 PRTO BRIN | Rotten | Structure-Wood | Replace | 35606177 | T3 METCALF-GREEN VALLEY 18/124R RPL POLE | 70Y
LC | 130081674 | 018/124 | T3 METCALF-GREEN VALLEY 18/124L RPL POLE | MOSSLNDG | ETL.2540.POLE.WDPS | 2024-12-16 | 2024-12-13 | 2025-05-02 | On-Time |  | 2025-06-13 | 2025-06-13 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW TNT SWRK COMP OH FMOB TR3 PRTO FRAB BRIN | Rotten | Structure-Wood | Replace | 35606177 | T3 METCALF-GREEN VALLEY 18/124R RPL POLE | 70Y
LC | 130541449 | 010/271 | T3 COLGATE-ALLEGHANY 10/271 GO95 | SACTO | ETL.6470.POLE.WOOD | 2024-12-26 | 2024-12-13 | 2024-12-13 | Past Due |  | 2025-06-13 | 2025-06-13 | 401T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR ACCM COMP OH TR3 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35608513 | T3 COLGATE-ALLEGHANY 10/271 GO95 | 93G
LC | 130541681 | 010/272 | T3 COLGATE-ALLEGHANY 10/272 GO95 | SACTO | ETL.6470.POLE.WOOD | 2024-12-26 | 2024-12-13 | 2025-05-13 | On-Time |  | 2025-06-13 | 2025-06-13 | 401T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCM COMP OH TR3 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35608515 | T3 COLGATE-ALLEGHANY 10/272 GO95 | 93G
LC | 123839658 | 001/027 | T3NT EI KESWICK-TRINITY 001/027 RPL ANCW | TABLEMTN | ETL.7270.POLE.NWOD | 2022-06-14 | 2022-06-14 | 2023-05-06 | On-Time |  | 2025-06-14 | 2025-06-14 | 637 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 31620420 | T3 EI KESWICK-TRINITY 001/027 RPL ANCW | 93E
LC | 123901316 | 010/001 | T3NT DI MNT RIO-FLTN-FLTN 10/1 RPR GYWW | LAKEVLLE | ETL.7630.POLE.NWOD | 2022-06-22 | 2022-06-14 | 2023-07-27 | On-Time |  | 2025-06-14 | 2025-06-14 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45575612 | T3 DI MNT RIO-FLTN-FLTN 10/1 RPR GYWW | ICW
LC | 129075973 | 001/042-GUY | T2 EI JFFRSON-STANFORD 1/42-GUY RPR ANCW | METCALF | ETL.7220.POLE.WOOD | 2024-06-14 | 2024-06-14 | 2024-08-23 | On-Time |  | 2025-06-14 | 2025-06-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46271728 | T2 EI JFFRSON-STANFORD 1/42-GUY RPR ANCW | ICW
LC | 129076408 | 025/220 | T2 CASCADE-COTTONWOOD 25/220R RPL STRW | TABLEMTN | ETL.1240.POLE.WDPS | 2024-06-14 | 2024-06-14 | 2025-05-19 | On-Time |  | 2025-06-14 | 2025-06-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35572154 | T2 EI CASCADE-COTN 25/220R RPL PL | 70Y
LC | 129076441 | 025/220 | T2 CASCADE-COTTONWOOD 25/220L RPL STRW | TABLEMTN | ETL.1240.POLE.WDPS | 2024-06-14 | 2024-06-14 | 2025-05-20 | On-Time |  | 2025-06-14 | 2025-06-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35572154 | T2 EI CASCADE-COTN 25/220R RPL PL | 70Y
LC | 129076840 | 65 | T2 SNEATH LAN-HALF MN BAY ;0/1A RMV IDLE | METCALF | ETL.7212.SWIT | 2024-06-14 | 2024-06-14 | 2024-07-17 | On-Time |  | 2025-06-14 | 2025-06-14 | 673T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO NTDE | Idle | Structure-Wood | Remove | 35560738 | T2 SNEATH LAN-HALF MN BAY ;0/1A RMV IDLE | 93J
LC | 129077319 | 004/094 | T2 EI KILARC-DESCHUTES 4/94 RPL POLE | TABLEMTN | ETL.7300.POLE.WOOD | 2024-06-14 | 2024-06-14 | 2025-05-14 | On-Time |  | 2025-06-14 | 2025-06-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573769 | T2 EI KILARC-DESCHUTES 4/94 RPL POLE | 70Y
LC | 129078453 | 003/099 | T2 DI HAMILTON BRC-CHS 3/99 RPR INSW | TABLEMTN | ETL.7000.INSL.CERA | 2024-06-14 | 2024-06-14 | 2024-07-29 | On-Time |  | 2025-06-14 | 2025-06-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46287727 | T2 DI HAMILTON BRC-CHS 3/99 RPR INSW | ICW
LC | 129078457 | 003/099 | T2 DI HAMILTON BRC-CHS 3/99 RPR JUMW | TABLEMTN | ETL.7000.INSL.CERA | 2024-06-14 | 2024-06-14 | 2024-07-29 | On-Time |  | 2024-09-14 | 2025-06-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46273548 | T2 DI HAMILTON BRC-CHS 3/99 RPR JUMW | ICW
LC | 129078533 | 002/109 | T2 EI SPAULDING-SUMMIT 002/109 RPR GYWW | SACTO | ETL.8060.POLE.NWOD | 2024-06-14 | 2024-06-14 | 2024-06-21 | On-Time |  | 2024-09-14 | 2025-06-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46267963 | T2 EI SPAULDING-SUMMIT 002/109 RPR GYWW | ICW
LC | 129078985 | 004/026 | T2 EI PITTSBURG-COLUMBIA 4/26 INS STPS | CONCORD | ETL.3300.TOWR | 2024-06-14 | 2024-06-14 | 2025-02-27 | On-Time |  | 2025-06-14 | 2025-06-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB NTDE | Missing | Hardware-Tower | Install | 46289391 | T2 EI PITTSBURG-COLUMBIA 4/26 INS STPS | ICQ
LC | 129079011 | 004/026 | T2 PITTSBURG-COLUMBIA 4/26 RPR STRT | CONCORD | ETL.3300.TOWR | 2024-06-14 | 2024-06-14 | 2024-09-09 | On-Time |  | 2025-06-14 | 2025-06-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO CLMB FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46268049 | T2 PITTSBURG-COLUMBIA 4/26 RPR STRT | ICQ
LC | 129079281 | 004/145 | T2 SPAULDING-SUMMIT 004/145 RPL HRDW | SACTO | ETL.8060.POLE.WOOD | 2024-06-14 | 2024-06-14 | 2025-06-07 | On-Time |  | 2025-06-14 | 2025-06-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46400328 | T2 EI SPAULDING-SUMMIT 004/145 RPL HRDW | ICW
LC | 129082601 | 004/016 | T2 MELONES-RACETRACK 04/16 RPL POLE | VICTOR | ETL.2400.POLE.WOOD | 2024-06-17 | 2024-06-14 | 2025-02-27 | On-Time |  | 2025-06-14 | 2025-06-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35561653 | T2 MELONES-RACETRACK 04/16 RPL POLE | 70Y
LC | 129087938 | :024/126 | T2 DI CHC-SLNS SLDAD #2 :24/126 RPL HNGR | MOSSLNDG | ETL.2910.INSL.CERA | 2024-06-17 | 2024-06-14 | 2025-05-12 | On-Time |  | 2025-06-14 | 2025-06-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46326012 | T2 DI CHC-SLNS SLDAD #2 :24/126 RPL HNGR | ICQ
LC | 129088020 | :024/126 | T2 DI CHC-SLNS SLDAD #1 :24/126 RPL INSS | MOSSLNDG | ETL.2900.INSL.CERA | 2024-06-17 | 2024-06-14 | 2025-05-20 | On-Time |  | 2025-06-14 | 2025-06-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35591364 | T2 DI CHC-SLNS SLDAD #1 :24/126 RPL INSS | 93K
LC | 129088021 | :024/126 | T2 DI CHC-SLNS SLDAD #1 :24/126 RPL HNGR | MOSSLNDG | ETL.2900.INSL.CERA | 2024-06-17 | 2024-06-14 | 2025-05-19 | On-Time |  | 2025-06-14 | 2025-06-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46416711 | T2 DI CHC-SLNS SLDAD #1 :24/126 RPL HNGR | ICQ
LC | 129088022 | :024/126 | T2 DI CHC-SLNS SLDAD #2 :24/126 RPL INSS | MOSSLNDG | ETL.2910.INSL.CERA | 2024-06-17 | 2024-06-14 | 2025-05-12 | On-Time |  | 2025-06-14 | 2025-06-14 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35597755 | T2 DI CRZY HRS CAYN-SLAS 24/124 RPL INSS | 93K
LC | 129090117 | 002/014 | T2 DVIDE VNDNBRG #2 2/14L GO95 RPL | PISMOBCH | ETL.8630.POLE.WDPS | 2024-06-18 | 2024-06-14 | 2025-01-24 | On-Time |  | 2025-06-14 | 2025-06-14 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35564034 | T2 DVIDE VNDNBRG #2 2/14L GO95 RPL | 93G
LC | 129090119 | 002/014 | T2 DVIDE VNDNBRG #2 2/14R GO95 RPL | PISMOBCH | ETL.8630.POLE.WDPS | 2024-06-18 | 2024-06-14 | 2025-01-24 | On-Time |  | 2025-06-14 | 2025-06-14 | 401 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR FIRE COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35564034 | T2 DVIDE VNDNBRG #2 2/14L GO95 RPL | 93G
LC | 129095196 | 008/115 | T2 DI KESWICK-TRINITY 08/115 RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-06-18 | 2024-06-14 | 2024-09-11 | On-Time |  | 2024-09-14 | 2025-06-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46269247 | T2 DI KESWICK-TRINITY-08/115 RPR JUMW | ICW
LC | 129095260 | :024/125 | T2 DI CHC-SALNS-SOLD #1 :24/125 RPL INSS | MOSSLNDG | ETL.2900.INSL.CERA | 2024-06-18 | 2024-06-14 | 2024-11-05 | On-Time |  | 2024-09-14 | 2025-06-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35563047 | T2 DI CY HS CN-SNS-SD#1 :24/125 RPL INSS | 93K
LC | 129095261 | :024/125 | T2 DI CHC-SALNS-SOLD #1 :24/125 RPL HNGR | MOSSLNDG | ETL.2900.INSL.CERA | 2024-06-18 | 2024-06-14 | 2024-11-05 | On-Time |  | 2024-09-14 | 2025-06-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46269310 | T2 DI CY HS CN-SNS-SD#1 :24/125 RPL HNGR | ICQ
LC | 129095262 | :024/125 | T2 DI CHC-SALNS-SOLD #2 :24/125 RPL HNGR | MOSSLNDG | ETL.2910.INSL.CERA | 2024-06-18 | 2024-06-14 | 2024-11-12 | On-Time |  | 2024-09-14 | 2025-06-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46269433 | T2 DI CY HS CN-SNS-SD#2 :24/125 RPL HNGR | ICQ
LC | 129095263 | :024/125 | T2 DI CHC-SALNS-SOLD #2 :24/125 RPL INSS | MOSSLNDG | ETL.2910.INSL.CERA | 2024-06-18 | 2024-06-14 | 2024-11-12 | On-Time |  | 2024-09-14 | 2025-06-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35563049 | T2 DI CY HS CN-SNS-SD#2 :24/125 RPL INSS | 93K
LC | 129230014 | 000/009 | T2 DI COLGATE-SMARTVLLE #1 0/9C RPR GYWW | SACTO | ETL.6510.POLE.STPS | 2024-07-16 | 2024-06-14 | 2025-02-20 | On-Time |  | 2025-06-14 | 2025-06-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46324542 | T2 DI COLGATE-SMARTVLLE #1 0/9C RPR GYWW | ICW
LC | 129295228 | 016/328 | T2 DI CLGT-PLMRO 16/328 RPL STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-07-26 | 2024-06-14 | 2025-05-22 | On-Time |  | 2025-06-14 | 2025-06-14 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586888 | T2 DI CLGT-PLMRO 16/328 RPL STRW | 70Y
LC | 129295322 | 015/361 | T2 DI DRUM-GRSS VLLY-WMR 15/361 RPL INSW | SACTO | ETL.6760.INSL.NCER | 2024-07-26 | 2024-06-14 | 2024-11-04 | On-Time |  | 2024-09-14 | 2025-06-14 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35575198 | T2 DI DRUM-GRSS VLLY-WMR 15/361 RPL INSW | 93I
LC | 129305656 | :023/123 | T2 DI CZY HRSE CYN-SLNS 23/123 RPL DAMS | MOSSLNDG | ETL.2910.INSL.NCER | 2024-07-29 | 2024-06-14 | 2025-05-16 | On-Time |  | 2025-06-14 | 2025-06-14 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Damper-Steel | Replace | 46393858 | T2 DI CZY HRSE CYN-SLNS 23/123 RPL DAMS | ICS
LC | 129306531 | 016/362 | T2 DI DRM-GRSS VALY-WMR 16/362 RPR ANCW | SACTO | ETL.6760.POLE.WOOD | 2024-07-29 | 2024-06-14 | 2025-02-07 | On-Time |  | 2025-06-14 | 2025-06-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46340504 | T2 DI DRM-GRSS VALY-WMR 16/362 RPR ANCW | ICW
LC | 129311619 | :024/124 | T2 CZY HRS CNYN-SLAS :24/124 RPL INSS | MOSSLNDG | ETL.2910.INSL.CERA | 2024-07-30 | 2024-06-14 | 2024-06-14 | Past Due |  | 2025-06-14 | 2025-06-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35597755 | T2 DI CRZY HRS CAYN-SLAS 24/124 RPL INSS | 93K
LC | 129409127 | :021/110 | T2 DI CHC-SALINS-SLDD#1 :21/110 RPL RPTS | MOSSLNDG | ETL.2900.TOWR | 2024-08-19 | 2024-06-14 | 2025-04-21 | On-Time |  | 2025-06-14 | 2025-06-14 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46393862 | T2 DI CHC-SALINS-SLDD#1 :21/110 RPL RPTS | ICB
LC | 129409333 | :022/117 | T2 CRZY HRS CYN-SNS :22/117 CANCEL | MOSSLNDG | ETL.2900.TOWR | 2024-08-19 | 2024-06-14 | 2025-05-21 | On-Time |  | 2025-06-14 | 2025-06-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416778 | T2 DI CRZY HRS CYN-SNS :22/117 RPR STRT | ICQ
LC | 129409334 | :022/117 | T2 CRZY HRS CYN-SNS :22/117 RPL INSS | MOSSLNDG | ETL.2900.INSL.CERA | 2024-08-19 | 2024-06-14 | 2024-06-14 | Past Due |  | 2025-06-14 | 2025-06-14 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35639341 | T2 DI CRZY HRS CYN-SNS :22/117 RPL INSS | 93K
LC | 129409338 | 000/015A | T2 DI COLGATE-PALERMO 0/15A INST ANMW | SACTO | ETL.6500.POLE.NWOD | 2024-08-19 | 2024-06-14 | 2025-03-25 | On-Time |  | 2025-06-14 | 2025-06-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | Missing | Animal Guard-Wood | Install | 46337345 | T2 DI COLGATE-PALERMO 0/15A INST ANMW | ICW
LC | 129409388 | :022/116 | T2 DI CHC-SALINS-SLDD#1 :22/116 RPR STRT | MOSSLNDG | ETL.2900.TOWR | 2024-08-19 | 2024-06-14 | 2025-05-21 | On-Time |  | 2025-06-14 | 2025-06-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416780 | T2 DI CHC-SALINS-SLDD#1 :22/116 RPR STRT | ICQ
LC | 129409614 | T003/005 | T2 TULUCAY-NAPA #1 T3/5 RPR STRW | LAKEVLLE | ETL.8180.POLE.WOOD | 2024-08-19 | 2024-06-14 | 2024-06-14 | Past Due |  | 2025-06-14 | 2025-06-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401534 | T2 DI TULUCAY-NAPA #1 T003/005 RPR STRW | ICW
LC | 129419978 | 000/009 | T2 DI CLGT-SMRTVLL #2 0/9 RPR GYWW | SACTO | ETL.6520.POLE.STPS | 2024-08-21 | 2024-06-14 | 2024-09-13 | On-Time |  | 2024-12-14 | 2025-06-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46321089 | T2 DI CLGT-SMRTVLL #2 0/9 RPR GYWW | ICW
LC | 123851160 | 004/040 | T2NT EI BRIDGEVILE-COTTNWD 4/40 RPR ADSS | TABLEMTN | ETL.1110.POLE.WDPS | 2022-06-15 | 2022-06-15 | 2024-01-09 | On-Time |  | 2025-06-15 | 2025-06-15 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 46093195 | T2NT EI BRIDGEVILE-COTTNWD 4/40 RPR ADSS | ICW
LC | 123851163 | 004/038 | T2NT EI BRDGVLLE-CTTNWD 4/38 RPR ADSS | TABLEMTN | ETL.1110.POLE.STPS | 2022-06-15 | 2022-06-15 | 2024-01-09 | On-Time |  | 2025-06-15 | 2025-06-15 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 46093196 | T2NT EI BRDGVLLE-CTTNWD 4/38 RPR ADSS | ICW
LC | 123863619 | 052/227 | T2NT DI RND M-TB-MT#1 52/227 BNT STEEL | TABLEMTN | ETL.6060.TOWR | 2022-06-17 | 2022-06-15 | 2023-09-06 | On-Time |  | 2025-06-15 | 2025-06-15 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644487 | T2 DI RND M-TB-MTN#1 052/227 RPR MEMB | ICQ
LC | 123910266 | 054/233 | T2NT DI RND MT-TBL MTN #1 54/233 RMV VEG | TABLEMTN | ETL.6060.TOWR | 2022-06-23 | 2022-06-15 | 2023-08-14 | On-Time |  | 2025-06-15 | 2025-06-15 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 123972208 | 041/303 | T3NT DI CARIBOU-TBL MTN 41/303 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2022-07-01 | 2022-06-15 | 2023-08-28 | On-Time |  | 2025-06-15 | 2025-06-15 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45593303 | T3 DI CARIBOU-TBL MTN 41/303 RPR STRT | ICQ
LC | 123976801 | 005/045 | T2NT DI RCK CRK POE 5/45 BENT STEEL | TABLEMTN | ETL.5630.TOWR | 2022-07-01 | 2022-06-15 | 2023-08-10 | On-Time |  | 2025-06-15 | 2025-06-15 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648209 | T2 DI RCK CRK POE 5/45 BENT STEEL | ICQ
LC | 124002557 | 001/006 | T2NT DI NRTH DBLN CYTN 1/6 RPL INSS | CONCORD | ETL.4500.TOWR | 2022-07-06 | 2022-06-15 | 2023-08-22 | On-Time |  | 2025-06-15 | 2025-06-15 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 31617323 | T2 DI NRTH DBLN CYTN 1/6 RPL INSS | 93K
LC | 124002619 | 001/006 | T2NT DI NRTH DBLN VNYRD 1/6 RPL INSS | CONCORD | ETL.4501.INSL | 2022-07-06 | 2022-06-15 | 2023-08-11 | On-Time |  | 2025-06-15 | 2025-06-15 | 532 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW OTHR FIRE COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 31624214 | T2 DI NORTH DUBLIN-VINEYARD RPL INSS 4TW | 93K
LC | 124003857 | 023/152 | T2NT DI POE-RIO OSO 23/152 BENT STEEL | TABLEMTN | ETL.5540.TOWR | 2022-07-06 | 2022-06-15 | 2023-07-26 | On-Time |  | 2025-06-15 | 2025-06-15 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648166 | T2 DI POE-RIO OSO 23/152 BENT STEEL | ICQ
LC | 129079887 | 002/118 | T2 SPAULDING-SUMMIT 002/118 RPL HRDD | SACTO | ETL.8060.POLE.WOOD | 2024-06-15 | 2024-06-15 | 2025-06-07 | On-Time |  | 2025-06-15 | 2025-06-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46400330 | T2 EI SPAULDING-SUMMIT 002/118 RPL HRDD | ICW
LC | 129080036 | 39 | T2 SPAULDING-SMT 16/507A RPR COND | SACTO | ETL.8060.SWIT | 2024-06-15 | 2024-06-15 | 2024-06-15 | Past Due |  | 2025-06-15 | 2025-06-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Conductor-Wood | Repair | 46400331 | T2 EI SPAULDING-SMT 16/507A RPR COND | ICW
LC | 129080038 | 042/006 | T2 EI ELK-GUALALA 042/006 RMV VEG | WILLITS | ETL.8410.POLE.WOOD | 2024-06-15 | 2024-06-15 | 2025-03-04 | On-Time |  | 2025-06-15 | 2025-06-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129080123 | 002/113 | T2 SPAULDING-SUMMIT 002/113 RPL INSW | SACTO | ETL.8060.INSL.NCER | 2024-06-15 | 2024-06-15 | 2024-06-15 | Past Due |  | 2025-06-15 | 2025-06-15 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572872 | T2 EI SPAULDING-SUMMIT 002/113 RPL INSW | 93I
LC | 129080818 | 003/124 | T2 SPAULDING-SUMMIT 003/124 REGR STRW | SACTO | ETL.8060.POLE.NWOD | 2024-06-15 | 2024-06-15 | 2025-06-07 | On-Time |  | 2025-06-15 | 2025-06-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46400332 | T2 EI SPAULDING-SUMMIT 003/124 REGR STRW | ICW
LC | 129080865 | 003/132 | T2 SPAULDING-SUMMIT 003/132 RPL STRW | SACTO | ETL.8060.POLE.WOOD | 2024-06-15 | 2024-06-15 | 2024-06-15 | Past Due |  | 2025-06-15 | 2025-06-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572873 | T2 EI SPAULDING-SUMMIT 003/132 RPL STRW | 70Y
LC | 129080936 | 023/447 | T2 EI HAT CRK #1-WSTWD 23/447 RPL ANCW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-15 | 2024-06-15 | 2025-06-13 | On-Time |  | 2025-06-15 | 2025-06-15 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35574764 | T2 EI HAT CRK #1-WSTWD 23/447 RPL ANCW | 93E
LC | 129081070 | 028/003 | T2 EI PHILO JCT-ELK 28/3 COTTER | WILLITS | ETL.7780.INSL.CERA | 2024-06-15 | 2024-06-15 | 2025-01-29 | On-Time |  | 2025-06-15 | 2025-06-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46340405 | T2 EI PHILO JCT-ELK 28/3 COTTER | ICW
LC | 129081075 | 033/011 | T2 EI FORT ROSS-GUALALA 33/011 COTTER | LAKEVLLE | ETL.6980.INSL.NCER | 2024-06-15 | 2024-06-15 | 2024-08-19 | On-Time |  | 2024-09-15 | 2025-06-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46268306 | T2 EI FORT ROSS-GUALALA 33/011 RPR INSW | ICW
LC | 129081080 | 028/003 | T2 EI PHILO JCT-ELK 28/3 RPL HRDD | WILLITS | ETL.7780.POLE.WOOD | 2024-06-15 | 2024-06-15 | 2025-01-29 | On-Time |  | 2025-06-15 | 2025-06-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46340406 | T2 EI PHILO JCT-ELK 28/3 RPL HRDD | ICW
LC | 129081188 | 039/008 | T2 EI FORT ROSS-GUALALA 39/8 RPL POLE | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-06-15 | 2024-06-15 | 2024-06-15 | Past Due |  | 2025-06-15 | 2025-06-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574059 | T2 EI FORT ROSS-GUALALA 39/8 RPL PL | 70Y
LC | 129081410 | 015/502 | T2 SPAULDING-SUMMIT 15/502 RPR SPLW | SACTO | ETL.8060.INSL.NCER | 2024-06-16 | 2024-06-15 | 2024-06-15 | Past Due |  | 2025-06-15 | 2025-06-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Splice-Wood | Repair | 46325985 | T2 EI SPAULDING-SUMMIT 15/502 RPR SPLW | ICW
LC | 129087178 | :006/047 | T2 DI ROCK CREEK-POE :6/47 RPR WALL | TABLEMTN | ETL.5630.TOWR | 2024-06-17 | 2024-06-15 | 2024-09-26 | On-Time |  | 2024-12-15 | 2025-06-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46327636 | T2 DI ROCK CREEK-POE :6/47 RPR WALL | ICQ
LC | 129087291 | :006/047 | T2 DI ROCK CREEK-POE 6/47 RPL HRDT | TABLEMTN | ETL.5630.TOWR | 2024-06-17 | 2024-06-15 | 2025-06-02 | On-Time |  | 2025-06-15 | 2025-06-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 46382050 | T2 DI ROCK CREEK-POE 6/47 RPL HRDT | ICQ
LC | 129087429 | 006/123 | T2 DI CORDELIA #2 TAP 006/123 RPR GYWW | SACTO | ETL.8184.POLE.NWOD | 2024-06-17 | 2024-06-15 | 2025-02-03 | On-Time |  | 2025-06-15 | 2025-06-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337353 | T2 DI CORDELIA #2 TAP 006/123 RPR GYWW | ICW
LC | 129087708 | 016/108 | T2 DI NEWARK-LIVERMORE 16/108 RPL STRW | CONCORD | ETL.7660.POLE.WOOD | 2024-06-17 | 2024-06-15 | 2025-04-30 | On-Time |  | 2025-06-15 | 2025-06-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573899 | T2 DI NEWARK-LIVERMORE 16/108 RPL STRW | 70Y
LC | 129087846 | 017/355 | T2 DI COLGATE-PALERMO 17/355 RPL IBWW | TABLEMTN | ETL.6500.INSL.CERA | 2024-06-17 | 2024-06-15 | 2025-05-23 | On-Time |  | 2025-06-15 | 2025-06-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Replace | 46400338 | T2 DI COLGATE-PALERMO 17/355 RPL IBWW | ICW
LC | 129095433 | 007/098B | T2 DI KESWICK-TRINITY 7/98B RPR JUMW | TABLEMTN | ETL.7270.INSL.NCER | 2024-06-18 | 2024-06-15 | 2024-09-12 | On-Time |  | 2024-09-15 | 2025-06-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46269248 | T2 DI KESWICK-TRINITY 7/98 RPR JUMW | ICW
LC | 129292677 | :014/075 | T2 DI CY HS CYN-SLS-SLD#1 14/75 RPL RPTS | MOSSLNDG | ETL.2900.TOWR | 2024-07-26 | 2024-06-15 | 2025-05-01 | On-Time |  | 2025-06-15 | 2025-06-15 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46391449 | T2 DI CY HS CYN-SLS-SLD#1 14/75 RPL RPTS | ICB
LC | 129292679 | :014/075 | T2 CY HS CYN-SLS-SLD#1 :14/75 RMV VEG | MOSSLNDG | ETL.2900.TOWR | 2024-07-26 | 2024-06-15 | 2024-06-15 | Past Due |  | 2025-06-15 | 2025-06-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 129292821 | :014/075 | T2 DI CY HS CYN-SLS-SLD#1 14/75 BNT STL | MOSSLNDG | ETL.2900.TOWR | 2024-07-26 | 2024-06-15 | 2025-04-30 | On-Time |  | 2025-06-15 | 2025-06-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416766 | T2 DI CY HS CYN-SLS-SLD#1 14/75 BNT STL | ICQ
LC | 129293157 | 010/006 | T2 DI FLTN-HOPLAND 10/006 RMV VEG | LAKEVLLE | ETL.6890.POLE.NWOD | 2024-07-26 | 2024-06-15 | 2025-06-09 | On-Time |  | 2025-06-15 | 2025-06-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129306597 | 000/004C | T2 DI COLGATE-PALERMO 0/4C RPL ANCW | SACTO | ETL.6500.POLE.NWOD | 2024-07-29 | 2024-06-15 | 2025-05-03 | On-Time |  | 2024-12-15 | 2025-06-15 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35606138 | T2 DI COLGATE-PALERMO 0/4C RPL ANCW | 93E
LC | 129306598 | 017/350 | T2 DI COLGATE-PALERMO 17/350 RPR STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-07-29 | 2024-06-15 | 2025-05-23 | On-Time |  | 2025-06-15 | 2025-06-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401362 | T2 DI COLGATE-PALERMO 17/350 RPR STRW | ICW
LC | 129312013 | 015/186 | T2 DI KESWICK-TRINITY 015/186 INSP ANCW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-07-30 | 2024-06-15 | 2024-08-21 | On-Time |  | 2025-06-15 | 2025-06-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | Overgrown | Structure-Wood | Inspect | 46305304 | T2 DI KESWICK-TRINITY 015/186 INSP ANCW | ICW
LC | 129420383 | :015/080 | T2NT DI CHC SALINAS SOLDD#1 :15/80 RMV | MOSSLNDG | ETL.2900.TOWR | 2024-08-21 | 2024-06-15 | 2024-06-15 | Past Due |  | 2027-06-15 | 2025-06-15 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE ACCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129420398 | 009/111 | T2 DRUM SUMMIT #2 9/111L RPL STRW | SACTO | ETL.1450.POLE.WDPS | 2024-08-21 | 2024-06-15 | 2024-06-15 | Past Due |  | 2025-06-15 | 2025-06-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35610069 | T2 DI DRUM SUMMIT #2 RPL 2 STRW | 70Y
LC | 129494318 | 007/082 | T2 VEDDER TAP 07/82 RPL DMPW | MIDWAY | ETL.2141.INSL.CERA | 2024-09-09 | 2024-06-15 | 2025-03-04 | On-Time |  | 2025-06-15 | 2025-06-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH RTNR TR2 PRTO AIR | No Good/Out of Stdrd | Damper-Wood | Replace | 46419907 | T2 VEDDER TAP 07/82 RPL DMPW | ICW
LC | 129494340 | 008/093 | T2 VEDDER TAP 08/93 RMV DBRS | MIDWAY | ETL.2141.POLE.WOOD | 2024-09-09 | 2024-06-15 | 2025-03-04 | On-Time |  | 2025-06-15 | 2025-06-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH RTNR TR2 PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 46419908 | T2 VEDDER TAP 08/93 RMV DBRS | ICW
LC | 130110096 | 117 | T2NT EI FULTON-PUEBLO 37/191A RPR SWTC | LAKEVLLE | ETL.1600.SWIT | 2024-12-17 | 2024-12-15 | 2024-12-15 | Past Due |  | 2027-12-15 | 2025-06-15 | 623 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO NTDE | Out of Adjustment | Switch | Repair
LC | 130739306 | 009/111 | T2 DRUM SUMMIT #2 9/111R RPL STRW | SACTO | ETL.1450.POLE.WDPS | 2025-01-14 | 2024-06-15 | 2024-06-15 | Past Due |  | 2025-06-15 | 2025-06-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35610069 | T2 DI DRUM SUMMIT #2 RPL 2 STRW | 70Y
LC | 123857672 | 005/051 | T2NT EI BRIDGEVILLE-CTTNWD 5/51 RPR ADSS | TABLEMTN | ETL.1110.POLE.WDPS | 2022-06-16 | 2022-06-16 | 2023-05-09 | On-Time |  | 2025-06-16 | 2025-06-16 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45644624 | T2 EI BRIDGEVILLE-COTTONWD 5/51 RPR ADSS | ICW
LC | 123859276 | 043/367 | T2NT EI PIT #1-CTNWD 43/367 RMV VEG | TABLEMTN | ETL.5390.TOWR | 2022-06-16 | 2022-06-16 | 2023-08-30 | On-Time |  | 2025-06-16 | 2025-06-16 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR2N PRTO FRAB | Overgrown | Vegetation | Trim
LC | 124002622 | 008/071 | T2NT DI PARADISE-TBL MTN 8/71 BNT STEEL | TABLEMTN | ETL.4316.TOWR | 2022-07-06 | 2022-06-16 | 2023-07-27 | On-Time |  | 2025-06-16 | 2025-06-16 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45617456 | T2 DI PARADISE-TBL MTN 8/71 RPR STRT | ICQ
LC | 124017700 | 020/139 | T3NT DI POE-RIO OSO 020/139 RMV VEG | TABLEMTN | ETL.5540.TOWR | 2022-07-07 | 2022-06-16 | 2023-08-14 | On-Time |  | 2025-06-16 | 2025-06-16 | 564 | TR3N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR3N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 124087158 | 025/496 | T2NT DI HAT CRK #1-WSTWD 25/496 RPR GYWW | TABLEMTN | ETL.7030.POLE.WOOD | 2022-07-15 | 2022-06-16 | 2024-06-24 | On-Time |  | 2025-06-16 | 2025-06-16 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46090803 | T2NT DI HAT CRK #1-WSTWD 25/496 RPR GYWW | ICW
LC | 124093488 | 019/132 | T3NT DI POE-RIO OSO 19/132 RMV VEG | TABLEMTN | ETL.5540.TOWR | 2022-07-15 | 2022-06-16 | 2023-08-29 | On-Time |  | 2025-06-16 | 2025-06-16 | 564 | TR3N |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR3N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 130102669 | 37 | T3 MONTA VSTA-BRNS 14/119 SW#37 RPR SWTC | MOSSLNDG | ETL.7590.SWIT | 2024-12-16 | 2024-12-16 | 2024-12-16 | Past Due |  | 2025-03-16 | 2025-06-16 | 623 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW NONR OH FMOB TR3 PRTO DURA BRIN | Out of Adjustment | Switch | Repair | 46438517 | MONTA VISTA-BURNS 14/119 RPR SWTC | ICE
LC | 123865638 | 008/065 | T3 EI TIGER CREEK-ELECTRA 8/65 BNT STEEL | VICTOR | ETL.5780.TOWR | 2022-06-17 | 2022-06-17 | 2023-05-03 | On-Time |  | 2022-12-17 | 2025-06-17 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3N PRTO FRAB | Anti-Climbing Guard | Structure-Tower | Repair | 45591546 | T3 EI TIGER CREEK-ELECTRA 8/65 BNT STEEL | ICQ
LC | 123977173 | 033/242 | T2NT DI CARIBOU-TBL MTN 33/242 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2022-07-01 | 2022-06-17 | 2023-08-09 | On-Time |  | 2025-06-17 | 2025-06-17 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45593278 | T2 DI CARIBOU-TBL MTN 33/242 RPR STRT | ICQ
LC | 123983121 | 011/045 | T3NT DI PTTSBRG SN RMON 011/045 RPR STRT | CONCORD | ETL.5490.TOWR | 2022-07-02 | 2022-06-17 | 2023-07-21 | On-Time |  | 2025-06-17 | 2025-06-17 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE OH TR3 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Structure-Tower | Repair | 45699244 | T3 DI PTTSBRG SN RMON 011/045 RPR STRT | ICQ
LC | 129083658 | 036/000 | T2 EI BRIDGEVLE-GRBERVLE 36/000 RPL STRW | EUREKA | ETL.6220.POLE.WOOD | 2024-06-17 | 2024-06-17 | 2024-06-17 | Past Due |  | 2025-06-17 | 2025-06-17 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572122 | T2 EI BRIDGEVLE-GRBERVLE 36/000 RPL STRW | 70Y
LC | 129084926 | 001/050 | T2 EI SPAULDING-SUMMIT 1/050 RPR GYWW | SACTO | ETL.8060.POLE.NWOD | 2024-06-17 | 2024-06-17 | 2025-06-08 | On-Time |  | 2025-06-17 | 2025-06-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46400335 | T2 EI SPAULDING-SUMMIT 1/050 RPR GYWW | ICW
LC | 129084927 | 001/049 | T2 EI SPAULDING-SUMMIT 1/49 CNCL | SACTO | ETL.8060.POLE.WOOD | 2024-06-17 | 2024-06-17 | 2024-06-17 | Past Due |  | 2025-06-17 | 2025-06-17 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35572868 | T2 EI SPAULDING-SUMMIT 1/049 RPL STRW | 70Y
LC | 129084949 | 001/037 | T2 EI SPAULDING-SUMMIT 1/37 RPR GYWW | SACTO | ETL.8060.POLE.WOOD | 2024-06-17 | 2024-06-17 | 2025-06-08 | On-Time |  | 2025-06-17 | 2025-06-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46400336 | T2 EI SPAULDING-SUMMIT 1/37 RPR GYWW | ICW
LC | 129087205 | 018/002 | T2 EI PHILO JCT-ELK 18/2 RPL ANCW | WILLITS | ETL.7780.POLE.WOOD | 2024-06-17 | 2024-06-17 | 2025-02-04 | On-Time |  | 2025-06-17 | 2025-06-17 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573317 | T2 EI PHILO JCT-ELK 18/2 RPL ANCW | 93E
LC | 129087218 | 027/010 | T2 EI PHILO JCT-ELK 27/10 RPR INSW | WILLITS | ETL.7780.INSL.CERA | 2024-06-17 | 2024-06-17 | 2025-01-29 | On-Time |  | 2025-06-17 | 2025-06-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46340408 | T2 EI PHILO JCT-ELK 27/10 RPR INSW | ICW
LC | 129088247 | :017/092 | T2 DI CHC-SALINAS SOLEDAD :17/92 COTTER | MOSSLNDG | ETL.2910.INSL.CERA | 2024-06-17 | 2024-06-17 | 2024-07-15 | On-Time |  | 2025-06-17 | 2025-06-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46272334 | T2 DI CHC-SALINAS SOLEDAD :17/92 COTTER | ICS
LC | 129088248 | :017/092 | T2 CHC-SALINAS SLEDAD :17/92 COMPLETE | MOSSLNDG | ETL.2900.TOWR | 2024-06-17 | 2024-06-17 | 2025-05-20 | On-Time |  | 2025-06-17 | 2025-06-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416712 | T2 DI CHC-SALINAS SLEDAD: 17/92 RPR STRT | ICQ
LC | 129089795 | 012/075C | T2 EI CAYUCOS-CAMBRIA_ 12/075R RPL PL | PISMOBCH | ETL.8560.POLE.WDPS | 2024-06-18 | 2024-06-17 | 2025-05-04 | On-Time |  | 2025-06-17 | 2025-06-17 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35572857 | T2 EI CAYUCOS-CAMBRIA_ 12/075R RPL PL | 70Y
LC | 129089874 | 012/075A | T2 EI CAYUCOS-CAMBRIA_ 12/075L RPL PL | PISMOBCH | ETL.8560.POLE.WDPS | 2024-06-18 | 2024-06-17 | 2025-05-04 | On-Time |  | 2025-06-17 | 2025-06-17 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP NOAC CLR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572857 | T2 EI CAYUCOS-CAMBRIA_ 12/075R RPL PL | 70Y
LC | 129089886 | 012/075B | T2 EI CAYUCOS-CAMBRIA_ 12/075C RPL PL | PISMOBCH | ETL.8560.POLE.WDPS | 2024-06-18 | 2024-06-17 | 2025-05-04 | On-Time |  | 2025-06-17 | 2025-06-17 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572857 | T2 EI CAYUCOS-CAMBRIA_ 12/075R RPL PL | 70Y
LC | 129095191 | 000/018 | T2 DI PLUMAS SIERRA TAP 0/18 COTR KEY | TABLEMTN | ETL.6291.INSL.NCER | 2024-06-18 | 2024-06-17 | 2025-01-24 | On-Time |  | 2025-06-17 | 2025-06-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46389183 | T2 DI PLUMAS SIERRA TAP 0/18 COTR KEY | ICW
LC | 129311772 | 008/099C | T2 DRUM-SUMMIT #2 8/99C RPR STRW | SACTO | ETL.1450.POLE.NWOD | 2024-07-30 | 2024-06-17 | 2025-04-23 | On-Time |  | 2025-06-17 | 2025-06-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46458346 | T2 DI DRUM-SUMMIT #2 8/99C RPR STRW | ICW
LC | 129419858 | 011/137C | T2 DI DRUM-SUMMIT #2 11/137C RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2024-08-21 | 2024-06-17 | 2025-04-30 | On-Time |  | 2025-06-17 | 2025-06-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458351 | T2 DI DRUM-SUMMIT #2 11/137C RPR GYWW | ICW
LC | 129420107 | :018/094 | T2 CHC-SALINAS-SLDD#2 :18/94 COMPLETE | MOSSLNDG | ETL.2900.TOWR | 2024-08-21 | 2024-06-17 | 2025-05-20 | On-Time |  | 2025-06-17 | 2025-06-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416782 | T2 DI CHC-SALINAS-SLDD#2 :18/94 RPR STRT | ICQ
LC | 129422222 | 000/007 | T2 DI CLGT-PALERMO 000/007R RPR GYWW | SACTO | ETL.6500.POLE.STPS | 2024-08-22 | 2024-06-17 | 2025-04-28 | On-Time |  | 2025-06-17 | 2025-06-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337344 | T2 DI CLGT-PALERMO 000/007R RPR GYWW | ICW
LC | 123871320 | 009/085 | T2NT EI BRDGVLE-CTNWD 9/85 INS ADSS MKW | TABLEMTN | ETL.1110.POLE.WDPS | 2022-06-18 | 2022-06-18 | 2023-05-09 | On-Time |  | 2025-06-18 | 2025-06-18 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45644635 | T2 EI BRIDGVLE-CTNWD 9/85 INS ADSS MKW | ICW
LC | 124028050 | 005/051 | T2NT DI BUCKS CRK-ROCK CRK 5/51 RPR FOND | TABLEMTN | ETL.4430.TOWR | 2022-07-08 | 2022-06-18 | 2023-08-16 | On-Time |  | 2025-06-18 | 2025-06-18 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45582523 | T2 DI BUCKS CRK-ROCK CRK 5/51 RPR FOND | ICQ
LC | 129090328 | 015/282 | T2 EI FULTON-MLIN-CTTI 015/282 RPL INSW | LAKEVLLE | ETL.6910.INSL.CERA | 2024-06-18 | 2024-06-18 | 2025-02-10 | On-Time |  | 2025-06-18 | 2025-06-18 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35609507 | T2 EI FULTON-MLIN-CTTI 015/282 RPL INSW | 93I
LC | 129090355 | 015/282 | T2 EI FULTON-MLINO-CTTI 015/282 TP HOLD | LAKEVLLE | ETL.6910.POLE.WOOD | 2024-06-18 | 2024-06-18 | 2025-02-11 | On-Time |  | 2025-06-18 | 2025-06-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46306017 | T2 EI FULTON-MLINO-CTTI 015/282 RPL HRDD | ICW
LC | 129091291 | 005/001 | T2 EI MENDOCINO-WILLITS 5/1 RPR INSW | WILLITS | ETL.7540.INSL.NCER | 2024-06-18 | 2024-06-18 | 2025-06-11 | On-Time |  | 2025-06-18 | 2025-06-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310537 | T2 EI MENDOCINO-WILLITS 5/1 RPR INSW | ICW
LC | 129091323 | 003/065 | T2 CARIBOU-PLUMAS JCT 3/065 RPL INSW | TABLEMTN | ETL.6300.INSL.CERA | 2024-06-18 | 2024-06-18 | 2025-03-06 | On-Time |  | 2025-06-18 | 2025-06-18 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572141 | T2 CARIBOU-PLUMAS JCT 3/065 RPL INSW | 93I
LC | 129091392 | 012/010 | T2 EI CARIBOU-PLUMAS JCT 12/010 RPL STRW | TABLEMTN | ETL.6290.POLE.WOOD | 2024-06-18 | 2024-06-18 | 2025-04-29 | On-Time |  | 2025-06-18 | 2025-06-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572132 | T2 EI CARIBOU-PLUMAS JCT 12/010 RPL STRW | 70Y
LC | 129092238 | 027/011 | T2 WV PHILO JCT-ELK 27/11 CANCEL | WILLITS | ETL.7780.POLE.NWOD | 2024-06-18 | 2024-06-18 | 2024-06-18 | Past Due |  | 2024-12-18 | 2025-06-18 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35562653 | T2 WV PHILO JCT-ELK 27/11 RPL ANCW | 93E
LC | 129092559 | 012/097 | T2 WV CARIBOU-TABLE MTN 012/097 RPR INSS | TABLEMTN | ETL.4440.INSL.CERA | 2024-06-18 | 2024-06-18 | 2025-04-01 | On-Time |  | 2025-06-18 | 2025-06-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46337594 | T2 WV CARIBOU-TABLE MTN 012/097 RPR INSS | ICS
LC | 129093595 | 002/015 | T2 HMBLDT-MPL CRK 2/15 RMV VEG | EUREKA | ETL.7130.POLE.WOOD | 2024-06-18 | 2024-06-18 | 2024-06-18 | Past Due |  | 2025-06-18 | 2025-06-18 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129093653 | 002/014-GUY | T2 EI HMBLDT-MPL CRK 2/14-GUY RMV VEG | EUREKA | ETL.7130.POLE.WOOD | 2024-06-18 | 2024-06-18 | 2024-06-18 | Past Due |  | 2025-06-18 | 2025-06-18 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 129093681 | 003/091 | T2 EI HMILTON BRNCH-CHSTR 3/091 RPL STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-06-18 | 2024-06-18 | 2025-03-20 | On-Time |  | 2025-06-18 | 2025-06-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574529 | T2 EI HMILTON BRNCH-CHSTR 3/091 RPL STRW | 70Y
LC | 129093691 | 002/074-GUY | T2 EI HMLTN BRNCH-CHTR 2/74-GUY RPL GYPL | TABLEMTN | ETL.7000.POLE.WOOD | 2024-06-18 | 2024-06-18 | 2025-03-19 | On-Time |  | 2025-06-18 | 2025-06-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | Rotten | Guy Pole-Wood | Replace | 35574528 | T2 EI HMLTN BRNCH-CHTR 2/74-GUY RPL GYPL | 70Y
LC | 129093934 | 030/000 | T2 WV PHILO JCT-ELK 30/0 RPL POLE | WILLITS | ETL.7780.POLE.WOOD | 2024-06-18 | 2024-06-18 | 2024-12-03 | On-Time |  | 2024-12-18 | 2025-06-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35584652 | T2 WV PHILO JCT-ELK 30/0 RPL POLE | 70Y
LC | 129094839 | 010/196 | T2 VALEY SPRINGS #1 10/196 RPL SPLW | VICTOR | ETL.8210.INSL.NCER | 2024-06-18 | 2024-06-18 | 2024-06-18 | Past Due |  | 2025-06-18 | 2025-06-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Splice-Wood | Replace | 46327606 | T2 DI VALEY SPRINGS #1 10/196 RPL SPLW | ICW
LC | 129096054 | 021/296-GUY | T2 CLAY-MARTEL 021/296-GUY RPL POLE | VICTOR | ETL.8250.POLE.WOOD | 2024-06-19 | 2024-06-18 | 2024-06-18 | Past Due |  | 2025-06-18 | 2025-06-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Rotten | Guy Pole-Wood | Replace | 35573184 | +T2 EI CLAY-MARTEL 021/296-GUY RPL POLE | 70Y
LC | 129105365 | :031/198 | T2 NRTH TWR-MRTNZ JCT#1 :31/198 RPR MKBL | CONCORD | ETL.3130.TOWR | 2024-06-20 | 2024-06-18 | 2025-06-06 | On-Time |  | 2025-06-18 | 2025-06-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | FAA Lighting-Steel | Repair | 46452752 | T2 DI NORTH TW-MJ#1 :31/198 RPR MKBL | ICS
LC | 129105369 | :031/198 | T2 N TWER-MRTNZ JCT #1 :31/198 RPR OPGW | CONCORD | ETL.3130.TOWR | 2024-06-20 | 2024-06-18 | 2025-06-06 | On-Time |  | 2024-09-18 | 2025-06-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46270570 | T2 DI NORTH TW-MJ #1 :31/198 RPR OPGW | ICS
LC | 129105453 | 073/003 | T2 DI HMBLDT-TRINITY 73/03C RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-20 | 2024-06-18 | 2025-04-08 | On-Time |  | 2025-06-18 | 2025-06-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345968 | T2 DI HMBLDT-TRINITY 73/03C RPR GYWW | ICW
LC | 129105454 | 073/003 | T2 DI HMBLDT-TRINITY 73/03L RPR GYWW | EUREKA | ETL.1820.POLE.WDPS | 2024-06-20 | 2024-06-18 | 2025-04-21 | On-Time |  | 2025-06-18 | 2025-06-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345974 | T2 DI HMBLDT-TRINITY 73/03L RPR GYWW | ICW
LC | 129139181 | ;009/023 | T2 CARIBOU-PLUMAS JCT ;9/23 RPL POLE | TABLEMTN | ETL.6290.POLE.WOOD | 2024-06-27 | 2024-06-18 | 2024-06-18 | Past Due |  | 2025-06-18 | 2025-06-18 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR TNT OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572130 | T2 CARIBOU-PLUMAS JCT ;9/23 RPL POLE | 70Y
LC | 129306649 | 027/125 | T2 RE TESLA-LOS BANOS #1 27/125 RPR SHLS | VICTOR | ETL.6100.TOWR | 2024-07-29 | 2024-06-18 | 2025-05-27 | On-Time |  | 2025-06-18 | 2025-06-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46339093 | T2 DI TESLA-LOS BANOS #1 27/125 RPR SHLS | ICS
LC | 129311544 | 005/081 | T2 DI COLGATE-PALERMO 5/81 RPR STRW | SACTO | ETL.6500.POLE.WOOD | 2024-07-30 | 2024-06-18 | 2025-04-29 | On-Time |  | 2025-06-18 | 2025-06-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401363 | T2 DI COLGATE-PALERMO 5/81 RPR STRW | ICW
LC | 129311587 | 001/016 | T2 DI COLGATE-PALERMO 1/16L RPR GYWW | SACTO | ETL.6500.POLE.WDPS | 2024-07-30 | 2024-06-18 | 2025-01-13 | On-Time |  | 2025-06-18 | 2025-06-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337343 | T2 DI COLGATE-PALERMO 1/16L RPR GYWW | ICW
LC | 129316277 | 009/204 | T2 DI HMLTN BRNCH-CHSTR 09/204 RPR POLE | TABLEMTN | ETL.7000.POLE.WOOD | 2024-07-31 | 2024-06-18 | 2025-01-14 | On-Time |  | 2025-06-18 | 2025-06-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46337214 | T2 DI HMLTN BRNCH-CHSTR 09/204 RPR POLE | ICW
LC | 129316279 | 009/204 | T2 DI HMLTN BRNCH-CHSTR 09/204 RPL HRDW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-07-31 | 2024-06-18 | 2025-01-14 | On-Time |  | 2024-12-18 | 2025-06-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace | 46328455 | T2 DI HMLTN BRNCH-CHSTR 09/204 RPL HRDW | ICW
LC | 129316464 | 021/143 | T2 DI HELMS GREGG#1 21/143 RPR INSS | FRESNO | ETL.4880.INSL.CERA | 2024-07-31 | 2024-06-18 | 2025-04-10 | On-Time |  | 2024-12-18 | 2025-06-18 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46302565 | T2 DI HELMS GREGG#1 21/143 RPR INSS | ICS
LC | 129316491 | 003/098 | T2 DI HAMLTN BRNCH-CHSTR 3/98 RPR JUMW | TABLEMTN | ETL.7000.INSL.NCER | 2024-07-31 | 2024-06-18 | 2025-03-21 | On-Time |  | 2025-06-18 | 2025-06-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Wood | Repair | 46328456 | T2 DI HMLTN BRNCH-CHSTR 3/098 RPR JUMW | ICW
LC | 129316763 | 004/012 | T2 DI SONOMA PUEBLO 04/012 COTTER | LAKEVLLE | ETL.3810.INSL.CERA | 2024-07-31 | 2024-06-18 | 2025-03-22 | On-Time |  | 2025-06-18 | 2025-06-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46401527 | T2 DI SONOMA PUEBLO 04/012 COTTER | ICW
LC | 129316765 | 004/012 | T2 DI SONOMA PUEBLO 04/012 RPR ANCW | LAKEVLLE | ETL.3810.POLE.WOOD | 2024-07-31 | 2024-06-18 | 2025-03-22 | On-Time |  | 2025-06-18 | 2025-06-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46401528 | T2 DI SONOMA PUEBLO 04/012 RPR ANCW | ICW
LC | 129420172 | 008/174 | T2 DI HMLTN BRNCH-CHSTR 8/174 RPR GYWW | TABLEMTN | ETL.7000.POLE.NWOD | 2024-08-21 | 2024-06-18 | 2025-01-08 | On-Time |  | 2025-06-18 | 2025-06-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337247 | T2 DI HMLTN BRNCH-CHSTR 8/174 RPR GYWW | ICW
LC | 129420174 | 001/008 | T2 MNDCNO-WLTS-FT BRG 1/8 RPR STRW | WILLITS | ETL.7550.POLE.WOOD | 2024-08-21 | 2024-06-18 | 2024-06-18 | Past Due |  | 2025-06-18 | 2025-06-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46544432 | T2 MNDCNO-WLTS-FT BRG 1/8 RPR STRW | ICW
LC | 123875494 | 010/093 | T2NT EI BRDGVILLE-CTNWD 10/93 ADSS MRKW | TABLEMTN | ETL.1110.POLE.WDPS | 2022-06-19 | 2022-06-19 | 2023-08-05 | On-Time |  | 2025-06-19 | 2025-06-19 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45644638 | T2 EI BRIDGEVILLE-CTNWD 10/93 ADSS MRKW | ICW
LC | 129097352 | 000/015 | T2 WV KSWCK-CSCD 0/15 RPL DMPW | TABLEMTN | ETL.7260.INSL.NCER | 2024-06-19 | 2024-06-19 | 2024-07-10 | On-Time |  | 2025-06-19 | 2025-06-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46404760 | T2 WV KSWCK-CSCD 0/15 RPL DMPW | ICW
LC | 129098606 | 018/592 | T2 EI SPAULDING-SUMMIT 18/592 RPR STRT | SACTO | ETL.8060.TOWR | 2024-06-19 | 2024-06-19 | 2024-08-26 | On-Time |  | 2025-06-19 | 2025-06-19 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46299228 | T2 EI SPAULDING-SUMMIT 18/592 RPR STRT | ICQ
LC | 123880512 | 018/064 | T2NT EI EXCHQR-INDIAN FLAT 18/64 RMV VEG | FRESNO | ETL.8650.TOWR | 2022-06-20 | 2022-06-20 | 2023-07-13 | On-Time |  | 2025-06-20 | 2025-06-20 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 123892276 | 054/235 | T2NT DI RND MT-TBL MT#2 54/235 RPR STRT | TABLEMTN | ETL.6070.TOWR | 2022-06-21 | 2022-06-20 | 2023-10-20 | On-Time |  | 2025-06-20 | 2025-06-20 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45647715 | T2 DI R.MTN-T.MTN #2 54/235 BENT STEEL | ICQ
LC | 123901399 | 031/224 | T2NT DI CARIBOU-TBL MTN 31/224 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2022-06-22 | 2022-06-20 | 2023-08-09 | On-Time |  | 2025-06-20 | 2025-06-20 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 45593275 | T2 DI CARIBOU-TBL MTN 31/224 RPL HRDT | ICQ
LC | 124026333 | :008/060 | T2NT DI ROCK CREEK-POE :8/60 BNT STEEL | TABLEMTN | ETL.5630.TOWR | 2022-07-08 | 2022-06-20 | 2023-08-24 | On-Time |  | 2025-06-20 | 2025-06-20 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648200 | T2 DI ROCK CREEK-POE :8/60 BNT STEEL | ICQ
LC | 124031361 | 000/007 | T3NT DI SOBRANTE-""R"" #1+" 0/7 RMV VEG | CONCORD | ETL.3770.TOWR | 2022-07-08 | 2022-06-20 | 2023-11-21 | On-Time |  | 2025-06-20 | 2025-06-20 | 564 | TR3N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR3N PRTO AIR FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 124075427 | ?003/000C | T3NT DI SNTH LN-HLF MN BY ?3/0C RPR POLE | METCALF | ETL.7212.POLE.NWOD | 2022-07-13 | 2022-06-20 | 2024-07-29 | On-Time |  | 2025-06-20 | 2025-06-20 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46080488 | T3NT DI SNTH LN-HLF MN BY ?3/0C RPR POLE | ICW
LC | 129100735 | 022/427 | T2 WV HAT CREEK #1-WSTWD 22/427 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-20 | 2024-06-20 | 2025-04-30 | On-Time |  | 2025-06-20 | 2025-06-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574761 | T2 WV HAT CREEK #1-WSTWD 22/427 RPL POLE | 70Y
LC | 129104275 | 057/245 | T2 METCALF-MOSS LANDNG#1 57/245 TOUCH | MOSSLNDG | ETL.5100.TOWR | 2024-06-20 | 2024-06-20 | 2025-04-28 | On-Time |  | 2024-12-20 | 2025-06-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476008 | T2 METCALF-MOSS LANDNG#1 57/245 TOUCH | ICQ
LC | 129104360 | 014/001 | T2 EI BRDGVLL GRBRVLL 014/001R COMPLETE | EUREKA | ETL.6220.POLE.WDPS | 2024-06-20 | 2024-06-20 | 2025-05-05 | On-Time |  | 2025-06-20 | 2025-06-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345973 | T2 EI BRDGVLL GRBRVLL 014/001R RPR GYWW | ICW
LC | 129105056 | 009/076 | T2 TIGER CREEK-ELECTRA 9/76 RPR FOND | VICTOR | ETL.5780.TOWR | 2024-06-20 | 2024-06-20 | 2024-06-20 | Past Due |  | 2025-06-20 | 2025-06-20 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46416713 | T2 TIGER CREEK-ELECTRA 9/76 EROSION | ICQ
LC | 129116282 | 004/078 | T2 CNTRVLL-TBL MTN 004/078 RPL POLE | TABLEMTN | ETL.6320.POLE.WOOD | 2024-06-24 | 2024-06-20 | 2025-03-01 | On-Time |  | 2025-06-20 | 2025-06-20 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572380 | T2 CNTRVLL-TBL MTN 004/078 RPL POLE | 70Y
LC | 129120258 | 27 | T2 DI SMRTVL-NICLAUS #2 6/134 RPR SWTC | SACTO | ETL.8000.SWIT | 2024-06-24 | 2024-06-20 | 2024-12-21 | On-Time |  | 2024-09-20 | 2025-06-20 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR DURA BRIN | Out of Adjustment | Switch | Repair | 46286539 | T2 DI SMRTVL-NICLAUS #2 6/134 RPR SWIW | ICE
LC | 129120726 | 036/175 | T2 DI CORTINA-MNDNO #1 36/175 RPR JUMS | WILLITS | ETL.1330.INSL.CERA | 2024-06-24 | 2024-06-20 | 2024-06-20 | Past Due |  | 2025-06-20 | 2025-06-20 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW ACCM OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46270531 | T2 DI CORTINA-MNDNO #1 36/175 RPR JUMS | ICS
LC | 129305024 | 001/026-GUY | T2 JEFRSN-STNFRD 01/26-GUY RMV VEG | METCALF | ETL.7220.POLE.WOOD | 2024-07-29 | 2024-06-20 | 2025-05-16 | On-Time |  | 2025-06-20 | 2025-06-20 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Trim
LC | 129311841 | 016/507B | T2 DI SPLDNG-SMMT 16/507BR RPR SWTC | SACTO | ETL.8060.POLE.WDPS | 2024-07-30 | 2024-06-20 | 2025-06-07 | On-Time |  | 2025-06-20 | 2025-06-20 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CUSI COMP OH TR2 PRTO AIR | Out of Adjustment | Switch | Repair | 46398023 | T2 DI SPLDNG-SMMT 16/507BR RPR SWTC | ICE
LC | 129311842 | 016/507B | T2 DI SPLDNG-SUMMIT 16/507BL RPR GRWW | SACTO | ETL.8060.POLE.WDPS | 2024-07-30 | 2024-06-20 | 2025-06-07 | On-Time |  | 2025-06-20 | 2025-06-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46401364 | T2 DI SPLDNG-SUMMIT 16/507BL RPR GRWW | ICW
LC | 129419780 | 000/014 | T2 DI CLGT-SMRTVLL #2 0/014 RPR GYWW | SACTO | ETL.6520.POLE.NWOD | 2024-08-21 | 2024-06-20 | 2025-01-13 | On-Time |  | 2025-06-20 | 2025-06-20 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337342 | T2 DI CLGT-SMRTVLL #2 0/014 RPR GYWW | ICW
LC | 123884930 | 000/005 | T3NT EI EL DRD-MSSRI FLT #1 0/5 RPR FOND | SACTO | ETL.1530.TOWR | 2022-06-21 | 2022-06-21 | 2023-06-30 | On-Time |  | 2025-06-21 | 2025-06-21 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP CPUA COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45600076 | T3 EI EL DRDO-MSSRI FLT #1 0/5 RPR FOND | ICQ
LC | 123970982 | 030/220 | T2NT DI CARIBOU-TBLE MTN 30/220 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2022-07-01 | 2022-06-21 | 2023-08-23 | On-Time |  | 2025-06-21 | 2025-06-21 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 45593273 | T2 DI CARIBOU-TABLE MTN 30/220 RPL HRDT | ICQ
LC | 129109378 | 000/027 | T2 COLLINS PINE TAP 0/027 RMV VEG | TABLEMTN | ETL.7001.POLE.WOOD | 2024-06-21 | 2024-06-21 | 2025-02-12 | On-Time |  | 2025-06-21 | 2025-06-21 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW PATR CNCL OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129110707 | 013/011 | T2 BRDGVLLE-GRBRVLLE 13/11 RPR GYWW | EUREKA | ETL.6220.POLE.NWOD | 2024-06-21 | 2024-06-21 | 2025-05-05 | On-Time |  | 2025-06-21 | 2025-06-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345963 | T2 EI BRDGVLLE-GRBRVLLE 13/11 RPR GYWW | ICW
LC | 129111556 | 013/006 | T2 BRDGVLL-GRBRVLL 13/6 COMPLETE | EUREKA | ETL.6220.POLE.WOOD | 2024-06-21 | 2024-06-21 | 2025-05-05 | On-Time |  | 2025-06-21 | 2025-06-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345971 | T2 EI BRDGVLL-GRBRVLL 13/6 RPR GYWW | ICW
LC | 129115318 | 002/017 | T2 EI HAT CREEK #1-PIT #1 2/017 RPL INSS | TABLEMTN | ETL.7020.INSL.CERA | 2024-06-23 | 2024-06-21 | 2025-05-08 | On-Time |  | 2025-06-21 | 2025-06-21 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570806 | T2 EI HAT CREEK #1-PIT #1 2/023 RPL INSS | 93K
LC | 129115391 | 001/013 | T2 EI HAT CREEK #1-PIT #1 1/013 RPR FOND | TABLEMTN | ETL.7020.TOWR | 2024-06-23 | 2024-06-21 | 2025-01-13 | On-Time |  | 2025-06-21 | 2025-06-21 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46381466 | T2 EI HAT CREEK #1-PIT #1 1/013 RPR FOND | ICQ
LC | 129115392 | 001/016 | T2 EI HAT CREEK #1-PIT #1 1/016 RPL INSS | TABLEMTN | ETL.7020.INSL.CERA | 2024-06-23 | 2024-06-21 | 2025-05-08 | On-Time |  | 2025-06-21 | 2025-06-21 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35570806 | T2 EI HAT CREEK #1-PIT #1 2/023 RPL INSS | 93K
LC | 129120851 | 010/065 | T2 DI CORTINA VACA 10/65 RPR OPGW | SACTO | ETL.4540.TOWR | 2024-06-24 | 2024-06-21 | 2025-01-27 | On-Time |  | 2025-06-21 | 2025-06-21 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46300595 | T2 DI CORTINA VACA 10/65 RPR OPGW | ICS
LC | 129334202 | 016/307 | T2 DI FLTN MLNO COTATI 16/307 RPR POLE | LAKEVLLE | ETL.6910.POLE.WOOD | 2024-08-05 | 2024-06-21 | 2025-01-08 | On-Time |  | 2025-06-21 | 2025-06-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46380894 | T2 DI FLTN MLNO COTATI 16/307 RPR POLE | ICW
LC | 129334427 | 031/000 | T2 DI GARBRVILE LYTONVILE 31/0 RPR GYWW | WILLITS | ETL.8365.POLE.WOOD | 2024-08-05 | 2024-06-21 | 2025-04-16 | On-Time |  | 2025-06-21 | 2025-06-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46402736 | T2 DI GARBRVILE LYTONVILE 31/0 RPR GYWW | ICW
LC | 129334428 | 031/000 | T2 DI GARBRVILE LYTONVILE 31/0 RPR STRW | WILLITS | ETL.8365.POLE.WOOD | 2024-08-05 | 2024-06-21 | 2025-04-16 | On-Time |  | 2025-06-21 | 2025-06-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46402737 | T2 DI GARBRVILE LYTONVILE 31/0 RPR STRW | ICW
LC | 129424949 | 007/185 | T2 DI CTTNWD-BENTON #1 007/185 RPR HRDW | TABLEMTN | ETL.6640.POLE.WOOD | 2024-08-22 | 2024-06-21 | 2025-06-02 | On-Time |  | 2025-06-21 | 2025-06-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Hardware-Wood | Replace | 46463880 | T2 DI CTTNWD-BENTON #1 007/185 RPR HRDW | ICW
LC | 123896267 | 026/112 | T3NT MORRO BAY-MESA 26/112 BNT STEEL | PISMOBCH | ETL.5290.TOWR | 2022-06-22 | 2022-06-22 | 2023-07-12 | On-Time |  | 2025-06-22 | 2025-06-22 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45656545 | T3 MORRO BAY-MESA 26/112 BNT STEEL | ICQ
LC | 123899604 | 039/236 | T2NT EI INDIAN FLT-YSMT 39/236 UNBURY | FRESNO | ETL.1112.POLE.NWOD | 2022-06-22 | 2022-06-22 | 2023-02-15 | On-Time |  | 2025-06-22 | 2025-06-22 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45660340 | T2 EI INDIAN FLT-YSMT 39/236 UNBURY | ICQ
LC | 123913103 | 023/323 | T2NT DI CLAY-MARTEL 23/323 RMV STEP | VICTOR | ETL.8250.POLE.WOOD | 2022-06-24 | 2022-06-22 | 2023-08-30 | On-Time |  | 2025-06-22 | 2025-06-22 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 45519066 | T2 DI CLAY-MARTEL 23/323 RMV STEP | ICW
LC | 124066549 | 029/213 | T2NT DI CARIBOU-TBLE MTN 29/213 RPL HRDT | TABLEMTN | ETL.4440.TOWR | 2022-07-12 | 2022-06-22 | 2023-08-09 | On-Time |  | 2025-06-22 | 2025-06-22 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 45593272 | T2 DI CARIBOU-TABLE MTN 029/213 RPL HRDT | ICQ
LC | 124110582 | 005/085 | T3NT DI MIDDLEFORK #1 5/85 RPR STRW | SACTO | ETL.8405.POLE.NWOD | 2022-07-18 | 2022-06-22 | 2023-08-22 | On-Time |  | 2025-06-22 | 2025-06-22 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 45390665 | T3 DI MIDDLEFORK #1 5/85 RPR STRW | ICW
LC | 129113454 | 013/008 | T2 TRINITY-MAPLE CREEK 13/08 RPR INSW | EUREKA | ETL.8170.INSL.CERA | 2024-06-22 | 2024-06-22 | 2025-03-21 | On-Time |  | 2025-06-22 | 2025-06-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46345964 | T2 TRINITY-MAPLE CREEK 13/08 RPR INSW | ICW
LC | 129113462 | 018/589 | T2 EI SPAULDING-SUMMIT 18/589 REGRADE | SACTO | ETL.8060.POLE.WOOD | 2024-06-22 | 2024-06-22 | 2024-07-30 | On-Time |  | 2025-06-22 | 2025-06-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Regrade | 46286452 | T2 EI SPAULDING-SUMMIT 18/589 REGRADE | ICW
LC | 123906442 | 020/180 | T2NT EI BRDGVLL-CTTNWD 20/180 RPR ADSS | TABLEMTN | ETL.1110.POLE.STPS | 2022-06-23 | 2022-06-23 | 2024-01-15 | On-Time |  | 2025-06-23 | 2025-06-23 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 46093194 | T2NT EI BRDGVLL-CTTNWD 20/180 RPR ADSS | ICW
LC | 123907695 | 018/170 | T2NT EI BRIDGVLLE-CTTNWD 18/170 RPR ADSS | TABLEMTN | ETL.1110.POLE.STPS | 2022-06-23 | 2022-06-23 | 2023-05-10 | On-Time |  | 2025-06-23 | 2025-06-23 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Steel | Repair | 45644673 | T2 EI BRIDGEVILLE-CTTNWD 18/170 RPR ADSS | ICS
LC | 123908350 | 017/119 | T3NT EI POE-RIO OSO -17/119 RMV VEG | TABLEMTN | ETL.5540.TOWR | 2022-06-23 | 2022-06-23 | 2023-08-29 | On-Time |  | 2025-06-23 | 2025-06-23 | 564 | TR3N |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR3N PRTO FRAB | Overgrown | Vegetation | Remove
LC | 123939949 | 006/054 | T2NT DI PARADISE-TBL MTN 6/54 RMV VEG | TABLEMTN | ETL.4316.TOWR | 2022-06-28 | 2022-06-23 | 2023-08-31 | On-Time |  | 2025-06-23 | 2025-06-23 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2N PRTO AIR FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 123912830 | 012/049 | T2NT EI MNT VSTA-JFFRSN #1 12/49 RPR FND | METCALF | ETL.5220.TOWR | 2022-06-24 | 2022-06-24 | 2023-06-21 | On-Time |  | 2025-06-24 | 2025-06-24 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45706620 | T2NT EI MNT VSTA-JFFRSN #1 12/49 RPR FND | ICQ
LC | 123915378 | 015/073 | T2NT EI MS LANDING-CBRN 15/73 RMV VEG | MOSSLNDG | ETL.5330.TOWR | 2022-06-24 | 2022-06-24 | 2023-11-22 | On-Time |  | 2025-06-24 | 2025-06-24 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2N PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 123915839 | 015/072 | T2NT EI MS LNDING-CBURN 15/72 RPR FOND | MOSSLNDG | ETL.5330.TOWR | 2022-06-24 | 2022-06-24 | 2023-08-21 | On-Time |  | 2025-06-24 | 2025-06-24 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 45650227 | T2NT EI MS LNDING-CBURN 15/72 RPR FOND | ICQ
LC | 123915970 | 006/055 | T3NT EI CRAG VIEW-CASCADE 6/55R RPR GYWW | TABLEMTN | ETL.1350.POLE.STPS | 2022-06-24 | 2022-06-24 | 2023-08-22 | On-Time |  | 2025-06-24 | 2025-06-24 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3N PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45461093 | T3 EI CRAG VIEW-CASCADE 6/56R RPR GYWW | ICW
LC | 123945455 | 034/007 | T2NT DI TRINITY-MAPLE CRK 34/7 INS RPTW | EUREKA | ETL.8170.POLE.STPS | 2022-06-28 | 2022-06-24 | 2024-08-05 | On-Time |  | 2025-06-24 | 2025-06-24 | 593 | TR2N | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Raptor Guard-Wood | Replace | 45659246 | T2NT DI TRINITY-MAPLE CRK 34/7 INS RPTW | ICB
LC | 124066595 | 038/283 | T3NT DI CARIBOU-TBL MTN 038/283 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2022-07-12 | 2022-06-24 | 2023-08-09 | On-Time |  | 2025-06-24 | 2025-06-24 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45593300 | T3 DI CARIBOU-TBL MTN 038/283 RPR STRT | ICQ
LC | 124086955 | 023/159A | T2NT DI CARBU-TBL MTN 23/159A RPR GYWS | TABLEMTN | ETL.4440.POLE.NWOD | 2022-07-15 | 2022-06-24 | 2023-08-07 | On-Time |  | 2025-06-24 | 2025-06-24 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45650766 | T2 DI CARBOU-TBL MTN 023/159A RPR GYWS | ICS
LC | 129116241 | 040/770 | T2 HAT CRK #1-WESTWD 40/770 RPL STRW | TABLEMTN | ETL.7030.POLE.NWOD | 2024-06-24 | 2024-06-24 | 2024-06-24 | Past Due |  | 2025-06-24 | 2025-06-24 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Structure-Wood | Replace | 35574688 | T2 HAT CRK #1-WESTWD 40/770 RPL STRW | 70Y
LC | 129116696 | 005/006 | T2 WV HUMBOLDT-MAPLE CREEK 5/6 INS DMPW | EUREKA | ETL.7130.INSL.NCER | 2024-06-24 | 2024-06-24 | 2025-04-02 | On-Time |  | 2025-06-24 | 2025-06-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46345965 | T2 WV HUMBOLDT-MAPLE CREEK 5/6 INS DMPW | ICW
LC | 129119481 | 014/084 | T2 STANISLAUS-MANTECA #2 14/84 RPR STRT | VICTOR | ETL.3820.TOWR | 2024-06-24 | 2024-06-24 | 2024-10-15 | On-Time |  | 2024-09-24 | 2025-06-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46269229 | T2 STANISLAUS-MANTECA #2 14/84 RPR STRT | ICQ
LC | 129119618 | 016/314 | T2 HAT CREEK #1-WSTWD 16/314 RPL POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-24 | 2024-06-24 | 2025-05-03 | On-Time |  | 2025-06-24 | 2025-06-24 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW OTHR COMP FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574754 | T2 WV HAT CREEK #1-WSTWD 16/314 RPL POLE | 70Y
LC | 129121751 | 007/029 | T2 EI MRRO BY-SLR SW ST #2 7/29 INS DMPS | PISMOBCH | ETL.5310.INSL.NCER | 2024-06-25 | 2024-06-24 | 2025-06-18 | On-Time |  | 2025-06-24 | 2025-06-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Steel | Install | 46329547 | T2 EI MRRO BY-SLR SW ST #2 7/29 INS DMPS | ICS
LC | 129126999 | 045/330B | T2 DI CRBU TBL MTN 45/330B RPL INSS | TABLEMTN | ETL.4440.INSL.CERA | 2024-06-25 | 2024-06-24 | 2025-04-07 | On-Time |  | 2025-06-24 | 2025-06-24 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569572 | T2 DI CARIBOU-TBL MTN RPL INSS | 93K
LC | 129236067 | 012/097 | T2 DI CRESTA-RIO OSO 12/097 RPR JUMS | TABLEMTN | ETL.4590.INSL.NCER | 2024-07-17 | 2024-06-24 | 2024-12-10 | On-Time |  | 2024-09-24 | 2025-06-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46332083 | T2 DI CRESTA-RIO OSO 12/097 RPR JUMS | ICS
LC | 129236149 | 009/081 | T2 CRSTA-RIO OSO 9/81 COMPLETE | TABLEMTN | ETL.4590.INSL.NCER | 2024-07-17 | 2024-06-24 | 2025-04-29 | On-Time |  | 2025-06-24 | 2025-06-24 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46337598 | T2 DI CRSTA-RIO OSO 9/81 RPR JUMS | ICS
LC | 129334203 | 007/086 | T2 DI COLGATE SMRTVLE #2 7/86 RPL STRW | SACTO | ETL.6520.POLE.WOOD | 2024-08-05 | 2024-06-24 | 2025-03-06 | On-Time |  | 2025-06-24 | 2025-06-24 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586889 | T2 DI COLGATE SMRTVLE #2 7/86 RPL STRW | 70Y
LC | 130866566 | 045/330A | T2 CRBU TBLE MTN 45/330A RPL INSS | TABLEMTN | ETL.4440.INSL.CERA | 2025-02-18 | 2024-06-24 | 2025-04-07 | On-Time |  | 2025-06-24 | 2025-06-24 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569572 | T2 DI CARIBOU-TBL MTN RPL INSS | 93K
LC | 130866665 | 045/330C | T2 CRBU TBLE MTN 45/330C RPL INSS | TABLEMTN | ETL.4440.INSL.CERA | 2025-02-18 | 2024-06-24 | 2025-04-07 | On-Time |  | 2025-06-24 | 2025-06-24 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569572 | T2 DI CARIBOU-TBL MTN RPL INSS | 93K
LC | 123921471 | 000/009 | T2NT EI PIT #3-CARBEY SWTH 0/9 RPR SPLW | TABLEMTN | ETL.5450.INSL.NCER | 2022-06-25 | 2022-06-25 | 2023-07-27 | On-Time |  | 2025-06-25 | 2025-06-25 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Conductor-Steel | Repair | 45671007 | T2NT EI PIT #3-CARBEY SWTH 0/9 RPR SPLW | ICS
LC | 123922375 | 019/089 | T0 T2NT MNTA VSTA-SRTGA 19/89 COMPLETE | METCALF | ETL.5240.TOWR | 2022-06-25 | 2022-06-25 | 2023-08-14 | On-Time |  | 2025-06-25 | 2025-06-25 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB PRTO FRAA TER0 | Overgrown | Vegetation | Remove
LC | 123926131 | 032/264 | T2NT EI BRIDGEVLL-CTTNWD 32/264 RPR ADSS | TABLEMTN | ETL.1110.TOWR | 2022-06-25 | 2022-06-25 | 2024-06-01 | On-Time |  | 2025-06-25 | 2025-06-25 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Steel | Repair | 46088719 | T2NT EI BRIDGEVLL-CTTNWD 32/264 RPR ADSS | ICS
LC | 123926132 | 031/262 | T2NT EI BRIDGEVLL-CTTNWD 31/262 RPR ADSS | TABLEMTN | ETL.1110.TOWR | 2022-06-25 | 2022-06-25 | 2024-02-02 | On-Time |  | 2025-06-25 | 2025-06-25 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Steel | Repair | 46088717 | T2NT EI BRIDGEVLL-CTTNWD 31/262 RPR ADSS | ICS
LC | 123926180 | 032/263 | T2NT EI BRIDGEVLL-CTTNWD 32/263 RPR ADSS | TABLEMTN | ETL.1110.TOWR | 2022-06-25 | 2022-06-25 | 2024-06-01 | On-Time |  | 2025-06-25 | 2025-06-25 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Steel | Repair | 46088718 | T2NT EI BRIDGEVLL-CTTNWD 32/263 RPR ADSS | ICS
LC | 123932906 | 002/019 | T3NT DI MRG OKLND #3 2/19 RPR STRT | CONCORD | ETL.2740.TOWR | 2022-06-27 | 2022-06-25 | 2023-12-20 | On-Time |  | 2025-06-25 | 2025-06-25 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45697939 | T3 DI MRG OKLND #3 2/19 RPR STRT | ICQ
LC | 124209470 | 006/066 | T3NT DI SNTH LN-PCFCA 6/66 RPR GYWW | METCALF | ETL.7575.POLE.WOOD | 2022-08-02 | 2022-06-25 | 2023-10-25 | On-Time |  | 2025-06-25 | 2025-06-25 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45600933 | T3 DI SNTH LN-PCFCA 6/066 RPR GYWW | ICW
LC | 129121774 | 000/003 | T2 COLGATE PH-COLGATE SW STA 0/3 COTTER | SACTO | ETL.6460.INSL.NCER | 2024-06-25 | 2024-06-25 | 2025-01-27 | On-Time |  | 2025-06-25 | 2025-06-25 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46300522 | T2 COLGATE PH-COLGATE SW STA 0/3 COTTER | ICS
LC | 129121806 | 000/002 | T2 COLGATE-GRASS VALLEY 000/002 RPL POLE | SACTO | ETL.6490.POLE.WOOD | 2024-06-25 | 2024-06-25 | 2025-05-27 | On-Time |  | 2025-06-25 | 2025-06-25 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Structure-Wood | Replace | 35572546 | T2 COLGATE-GRASS VALLEY 000/002 RPL POLE | 70Y
LC | 129124068 | 000/011 | T2 SBRNT-GRZ CLRMT #1 0/11 BNT STEEL | CONCORD | ETL.3740.TOWR | 2024-06-25 | 2024-06-25 | 2025-03-10 | On-Time |  | 2025-06-25 | 2025-06-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46289393 | T2 SBRNT-GRZ CLRMT #1 0/11 BNT STEEL | ICQ
LC | 129126097 | 013/126 | T2 SN LS OBISPO-CYCS 13/126 RPL POLE | PISMOBCH | ETL.9090.POLE.WOOD | 2024-06-25 | 2024-06-25 | 2025-05-05 | On-Time |  | 2025-06-25 | 2025-06-25 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573892 | T2 EI SN LS OBISPO-CYCS 13/126 RPL POLE | 70Y
LC | 129134735 | 015/007 | T2 DI TRINTY-MAPLE CRK 15/07R RPR GYWW | EUREKA | ETL.8170.POLE.STPS | 2024-06-26 | 2024-06-25 | 2025-03-21 | On-Time |  | 2025-06-25 | 2025-06-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46273458 | T2 DI TRINTY-MAPLE CRK 15/07R RPR GYWW | ICW
LC | 129134743 | 015/007 | T2 DI TRINITY-MAPLE CRK-15/07 RPR JUMW | EUREKA | ETL.8170.INSL.NCER | 2024-06-26 | 2024-06-25 | 2025-03-21 | On-Time |  | 2024-09-25 | 2025-06-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46273459 | T2 DI TRINITY-MAPLE CRK-15/07 RPR JUMW | ICW
LC | 129235911 | 016/000 | T2 DI TRNTY-MPL CRK 16/00 RPR GYWW | EUREKA | ETL.8170.POLE.NWOD | 2024-07-17 | 2024-06-25 | 2025-01-22 | On-Time |  | 2025-06-25 | 2025-06-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345966 | T2 DI TRNTY-MPL CRK 16/00 RPR GYWW | ICW
LC | 129235913 | 016/000 | T2 DI TRNTY-MPL CRK 16/0 RPR ANCW | EUREKA | ETL.8170.POLE.NWOD | 2024-07-17 | 2024-06-25 | 2025-01-22 | On-Time |  | 2025-06-25 | 2025-06-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Wood | Repair | 46345877 | T2 DI TRNTY-MPL CRK 16/0 RPR ANCW | ICW
LC | 129444959 | 038/225 | T2 DI INDIAN FLT-YSMT 38/225 RPR FOND | FRESNO | ETL.1112.TOWR | 2024-08-27 | 2024-06-25 | 2024-10-08 | On-Time |  | 2024-12-25 | 2025-06-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46309290 | T2 DI INDIAN FLT-YSMT 38/225 RPR FOND | ICQ
LC | 129444991 | 038/225 | T2 INDIAN FLT-YSMT 38/225 RPL HRDT | FRESNO | ETL.1112.TOWR | 2024-08-27 | 2024-06-25 | 2024-06-25 | Past Due |  | 2025-06-25 | 2025-06-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46399424 | T2 DI INDIAN FLT-YSMT 38/225 RPL HRDT | ICQ
LC | 123927230 | 033/271 | T2NT EI BRIDGEVLL-CTTNWD 33/271 RPR ADSS | TABLEMTN | ETL.1110.POLE.STPS | 2022-06-26 | 2022-06-26 | 2023-04-09 | On-Time |  | 2025-06-26 | 2025-06-26 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 45711378 | T2NT EI BRIDGEVLL-CTTNWD 33/271 RPR ADSS | ICW
LC | 123927423 | 033/273 | T2NT EI BRDGVLL-CTTNWD 33/273 RPR ADSS | TABLEMTN | ETL.1110.POLE.WDPS | 2022-06-26 | 2022-06-26 | 2024-06-01 | On-Time |  | 2025-06-26 | 2025-06-26 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire / OPGW-Wood | Repair | 46093193 | T2NT EI BRDGVLL-CTTNWD 33/273 RPR ADSS | ICW
LC | 123927492 | C000/002 | T2NT EI PALERMO-COLGATE C0/2 RPR SHIELD | SACTO | ETL.5360.TOWR | 2022-06-26 | 2022-06-26 | 2023-06-10 | On-Time |  | 2025-06-26 | 2025-06-26 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Shield Wire / OPGW-Steel | Repair | 45459046 | T2 EI PALERMO-COLGATE C0/2 RPR SHIELD | ICS
LC | 123977086 | 003/065 | T2NT DI HAAS-WOODCHUCK 3/65 RPR GYWW | FRESNO | ETL.8730.POLE.WOOD | 2022-07-01 | 2022-06-26 | 2023-09-19 | On-Time |  | 2025-06-26 | 2025-06-26 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45844796 | T2 DI HAAS-WOODCHUCK 3/65 RPR GYWW | ICW
LC | 124157667 | 004/093C | T2NT DI CORDELIA#1 TAP 4/093C RPL POLE | SACTO | ETL.8182.POLE.WOOD | 2022-07-25 | 2022-06-26 | 2025-04-26 | On-Time |  | 2025-06-26 | 2025-06-26 | 372 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 31619825 | T2 EI CORDELIA #1 TAP 4/093A RPL POLE | 70Y
LC | 129128115 | 013/127 | T2 UKIAH-HPLND-CLVRDLE 13/127 TOUCH | WILLITS | ETL.4050.POLE.NWOD | 2024-06-26 | 2024-06-26 | 2025-05-20 | On-Time |  | 2024-12-26 | 2025-06-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46507787 | T2 UKIAH-HPLND-CLVRDLE 13/127 TOUCH | ICW
LC | 129128551 | 046/002 | T2 WV FORT ROSS-GUALALA 46/2 RPL STRW | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-06-26 | 2024-06-26 | 2025-04-28 | On-Time |  | 2025-06-26 | 2025-06-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574243 | T2 WV FORT ROSS-GUALALA 46/2 RPL STRW | 70Y
LC | 129128789 | C000/001 | T2 PALERMO-COLGATE C0/1 RPR FOND | SACTO | ETL.5360.TOWR | 2024-06-26 | 2024-06-26 | 2025-03-26 | On-Time |  | 2025-06-26 | 2025-06-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46310435 | T2 PALERMO-COLGATE C000/001 RPR FOND | ICQ
LC | 129128846 | 000/009 | T2 SBRNTE-GRZLY-CLMNT#2 0/9 RPR FOND | CONCORD | ETL.3750.TOWR | 2024-06-26 | 2024-06-26 | 2025-04-09 | On-Time |  | 2025-06-26 | 2025-06-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46289394 | T2 SBRNTE-GRZLY-CLMNT#2 0/9 RPR FOND | ICQ
LC | 129130305 | 006/054 | T2 SBRT-GRZZY-CLRMNT #1 6/54 TOUCH | CONCORD | ETL.3740.TOWR | 2024-06-26 | 2024-06-26 | 2025-05-06 | On-Time |  | 2024-12-26 | 2025-06-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAR NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46485460 | T2 SBRT-GRZZY-CLRMNT #1 6/54 TOUCH | ICQ
LC | 129130607 | 011/104 | T2 EI SN LS OBISPO-CYCS 11/104 RPR CRSW | PISMOBCH | ETL.9090.POLE.WOOD | 2024-06-26 | 2024-06-26 | 2025-05-06 | On-Time |  | 2025-06-26 | 2025-06-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46329649 | T2 EI SN LS OBISPO-CYCS 11/104 RPR CRSW | ICW
LC | 129130876 | T035 | T2 MIDWAY-SANTA MARIA T035L RPL POLE | PISMOBCH | ETL.9240.POLE.WDPS | 2024-06-26 | 2024-06-26 | 2025-02-25 | On-Time |  | 2025-06-26 | 2025-06-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO FRAB PGEQ | Rotten | Structure-Wood | Replace | 35573538 | T2 EI MIDWAY-SANTA MARIA T35R RPL POLE | 70Y
LC | 129131641 | T035 | T2 MIDWAY-SANTA MARIA T035C RPL POLE | PISMOBCH | ETL.9240.POLE.WDPS | 2024-06-26 | 2024-06-26 | 2025-02-25 | On-Time |  | 2025-06-26 | 2025-06-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO FRAB PGEQ | Rotten | Structure-Wood | Replace | 35573538 | T2 EI MIDWAY-SANTA MARIA T35R RPL POLE | 70Y
LC | 129134055 | 009/015 | T2 VALLEY SPRNGS-MRTLL #1 9/15 RPR POLE | VICTOR | ETL.8240.POLE.WOOD | 2024-06-26 | 2024-06-26 | 2025-05-14 | On-Time |  | 2025-06-26 | 2025-06-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46325963 | T2 VALLEY SPRNGS-MRTLL #1 9/15 RPR POLE | ICW
LC | 129134741 | 017/109-GUYA | T2 DI NEWARK LVRMORE 17/109-G RPL STRW | CONCORD | ETL.7660.POLE.WOOD | 2024-06-26 | 2024-06-26 | 2025-05-01 | On-Time |  | 2025-06-26 | 2025-06-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573897 | T2 DI NEWARK LVRMORE 17/109-G RPL STRW | 70Y
LC | 129134901 | 017/109-GUYB | T2 DI NWRK-LVRMRE 17/108-GUYB RMV VEG | CONCORD | ETL.7660.POLE.WOOD | 2024-06-26 | 2024-06-26 | 2025-04-29 | On-Time |  | 2025-06-26 | 2025-06-26 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129134907 | 017/109 | T2 DI NWRK-LVRMRE 17/109 RPR GYWW | CONCORD | ETL.7660.POLE.WOOD | 2024-06-26 | 2024-06-26 | 2025-01-26 | On-Time |  | 2025-06-26 | 2025-06-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46289396 | T2 DI NWRK-LVRMRE 17/109 RPR GYWW | ICW
LC | 129134908 | 017/109 | T2 DI NWRK-LVRMRE 17/109 RPR INSW | CONCORD | ETL.7660.INSL.CERA | 2024-06-26 | 2024-06-26 | 2025-01-26 | On-Time |  | 2025-06-26 | 2025-06-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46289397 | T2 DI NWRK-LVRMRE 17/109 RPR INSW | ICW
LC | 129135506 | T027 | T2 EI MIDWAY-SANTA MARIA T027 RPR POLE | PISMOBCH | ETL.9240.POLE.WOOD | 2024-06-27 | 2024-06-26 | 2025-02-21 | On-Time |  | 2025-06-26 | 2025-06-26 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC SWRK ACCL COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46391116 | T2 EI MIDWAY-SANTA MARIA T027 RPR POLE | ICW
LC | 123958544 | 008/039 | T2NT DI FULTON-PUEBLO 8/39 BENT STEEL | LAKEVLLE | ETL.1600.TOWR | 2022-06-29 | 2022-06-27 | 2023-11-15 | On-Time |  | 2025-06-27 | 2025-06-27 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644974 | T2 DI FULTON-PUEBLO 8/39 BENT STEEL | ICQ
LC | 123969358 | 012/087 | T3NT DI ROCK CREEK-POE 12/87 BENT STEEL | TABLEMTN | ETL.5630.TOWR | 2022-07-01 | 2022-06-27 | 2023-08-21 | On-Time |  | 2025-06-27 | 2025-06-27 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648215 | T3 DI ROCK CREEK-POE 12/87 BENT STEEL | ICQ
LC | 124094082 | 005/046 | T3NT DI MDDL FRK-GLD HL 005/046 RPL HRDT | SACTO | ETL.5140.TOWR | 2022-07-15 | 2022-06-27 | 2023-07-11 | On-Time |  | 2025-06-27 | 2025-06-27 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB | Missing | Hardware-Tower | Install | 45600181 | T3 DI MDDL FRK-GLD HL 005/046 RPL HRDT | ICQ
LC | 124177812 | 001/010 | T2NT DI BUTTE VLY-CARIBOU 1/10 RPL HRDT | TABLEMTN | ETL.1180.TOWR | 2022-07-27 | 2022-06-27 | 2023-07-22 | On-Time |  | 2025-06-27 | 2025-06-27 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Tower | Replace | 45582532 | T2 DI BUTTE VALLEY-CARIBOU 1/10 RPL HRDT | ICQ
LC | 124187127 | 014/099 | T2NT DI IGCO-ATO-STO #1 14/99 RMV VEG | LAKEVLLE | ETL.7160.POLE.WOOD | 2022-07-28 | 2022-06-27 | 2023-12-14 | On-Time |  | 2025-06-27 | 2025-06-27 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 127829318 | :020/005 | T2 WV EAGLE ROCK-REDBUD :20/5 INS DMPW | WILLITS | ETL.1480.INSL.NCER | 2023-12-27 | 2023-12-27 | 2024-12-11 | On-Time |  | 2025-06-27 | 2025-06-27 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB XMPT TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46214269 | T2 WV EAGLE ROCK-REDBUD :20/5 INS DMPW | ICW
LC | 129135478 | 013/000 | T2 MENDOCINO-WILLITS 13/0 RPR INSW | WILLITS | ETL.7540.INSL.CERA | 2024-06-27 | 2024-06-27 | 2025-01-06 | On-Time |  | 2025-06-27 | 2025-06-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310539 | T2 MENDOCINO-WILLITS 13/0 RPR INSW | ICW
LC | 129135488 | 059/250 | T2 RND MNTN-TBLE MNTN #2 59/250 RPR INSS | TABLEMTN | ETL.6070.INSL.NCER | 2024-06-27 | 2024-06-27 | 2025-02-19 | On-Time |  | 2025-06-27 | 2025-06-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO NTDE PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46306320 | T2 RND MNTN-TBLE MNTN #2 59/250 RPR INSS | ICS
LC | 129135517 | 007/006 | T2 MENDOCINO-HARTLEY 7/6 RPR GYWW | WILLITS | ETL.7510.POLE.NWOD | 2024-06-27 | 2024-06-27 | 2024-11-18 | On-Time |  | 2024-09-27 | 2025-06-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46282851 | T2 MENDOCINO-HARTLEY 007/006 RPR GYWW | ICW
LC | 129135606 | 009/048 | T2 VACA-LAKEVILLE #1 009/048 TOUCH | LAKEVLLE | ETL.5840.TOWR | 2024-06-27 | 2024-06-27 | 2025-04-23 | On-Time |  | 2024-12-27 | 2025-06-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491090 | T2 VACA-LAKEVILLE #1 009/048 TOUCH | ICQ
LC | 129136148 | 009/014 | T2 WV MELONES-RACETRACK 9/14 INS DAMW | VICTOR | ETL.2400.INSL.NCER | 2024-06-27 | 2024-06-27 | 2025-02-26 | On-Time |  | 2025-06-27 | 2025-06-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46327034 | T2 WV MELONES-RACETRACK 9/14 INS DAMW | ICW
LC | 129136989 | 012/110 | T2 EI SLO-CAYUCOS 12/110R RPL POLE | PISMOBCH | ETL.9090.POLE.WDPS | 2024-06-27 | 2024-06-27 | 2025-05-05 | On-Time |  | 2025-06-27 | 2025-06-27 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35573893 | T2 EI SLO-CAYUCOS 12/110R RPL POLE | 70Y
LC | 129137023 | 012/110 | T2 EI SLO-CAYUCOS 12/110C RPL POLE | PISMOBCH | ETL.9090.POLE.WDPS | 2024-06-27 | 2024-06-27 | 2025-05-05 | On-Time |  | 2025-06-27 | 2025-06-27 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573893 | T2 EI SLO-CAYUCOS 12/110R RPL POLE | 70Y
LC | 129137024 | 012/110 | T2 EI SLO-CAYUCOS 12/110L RPL POLE | PISMOBCH | ETL.9090.POLE.WDPS | 2024-06-27 | 2024-06-27 | 2025-05-05 | On-Time |  | 2025-06-27 | 2025-06-27 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573893 | T2 EI SLO-CAYUCOS 12/110R RPL POLE | 70Y
LC | 129137566 | 016/002 | T2 TRINTY-MPLE CREEK 16/02 RPL BOND | EUREKA | ETL.8170.POLE.WOOD | 2024-06-27 | 2024-06-27 | 2025-03-21 | On-Time |  | 2025-06-27 | 2025-06-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Hardware-Wood | Replace | 46345878 | T2 TRINTY-MPLE CREEK 16/02 RPL BOND | ICW
LC | 129138957 | 043/828 | T2 HAT CRK #1-WESTWD 43/828 RPR GYWW | TABLEMTN | ETL.7030.POLE.NWOD | 2024-06-27 | 2024-06-27 | 2025-05-28 | On-Time |  | 2025-06-27 | 2025-06-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46416168 | T2 EI HAT CRK #1-WESTWD 43/828 RPR GYWW | ICW
LC | 129153717 | 001/013 | T2 DI PIT#3 PIT#1 01/013 RPR STRT | TABLEMTN | ETL.5400.TOWR | 2024-07-01 | 2024-06-27 | 2025-04-23 | On-Time |  | 2025-06-27 | 2025-06-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46382054 | T2 DI PIT#3 PIT#1 01/013 RPR STRT | ICQ
LC | 129153718 | 001/013 | T2 DI PIT#3 PIT#1 01/013 RPR JUMS | TABLEMTN | ETL.5400.INSL.NCER | 2024-07-01 | 2024-06-27 | 2024-08-23 | On-Time |  | 2025-06-26 | 2025-06-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46273979 | T2 DI PIT#3 PIT#1 01/013 RPR JUMS | ICS
LC | 129153719 | 028/139 | T2 DI EXCHQR INDN FLT 28/139 RPR JUMS | FRESNO | ETL.8650.INSL.NCER | 2024-07-01 | 2024-06-27 | 2024-06-27 | Past Due |  | 2025-06-27 | 2025-06-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46272124 | T2 DI EXCHQR INDN FLT 28/139 RPR JUMS | ICS
LC | 129187381 | 028/138 | T2 DI EXCHQUR-INDN FLT 28/138 RPR GYWT | FRESNO | ETL.8650.POLE.NWOD | 2024-07-08 | 2024-06-27 | 2024-06-27 | Past Due |  | 2025-06-27 | 2025-06-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46297904 | T2 DI EXCHQUR-INDN FLT 28/138 RPR GYWT | ICQ
LC | 129444935 | 054/002B | T2 DI HUMBOLDT-TRINITY 54/02B RPR GYWW | EUREKA | ETL.1820.POLE.WOOD | 2024-08-27 | 2024-06-27 | 2025-06-04 | On-Time |  | 2025-06-27 | 2025-06-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46403125 | T2 DI HUMBOLDT-TRINITY 54/02B RPR GYWW | ICW
LC | 124109347 | 044/321 | T3NT DI CARIBOU-TBL MTN 044/321 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2022-07-18 | 2022-06-28 | 2023-07-27 | On-Time |  | 2025-06-28 | 2025-06-28 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45593304 | T3 DI CARIBOU-TBL MTN 044/321 RPR STRT | ICQ
LC | 124167239 | 004/043B | T3NT DI SLY CREEK TAP 4/43B RMV VEG | TABLEMTN | ETL.4221.POLE.NWOD | 2022-07-26 | 2022-06-28 | 2023-08-30 | On-Time |  | 2025-06-28 | 2025-06-28 | 564 | TR3N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR3N PRTO AIR FRAB | Overgrown | Vegetation | Trim
LC | 124184486 | 034/172 | T3NT DI FULTON-PUEBLO 34/172 BNT STEEL | LAKEVLLE | ETL.1600.TOWR | 2022-07-28 | 2022-06-28 | 2023-07-17 | On-Time |  | 2025-06-28 | 2025-06-28 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45645041 | T3 DI FULTON-PUEBLO 34/172 BNT STEEL | ICQ
LC | 129141225 | 065/274 | T2 RND MTN-TBLE MTN #1 65/274 RPR SHIELD | TABLEMTN | ETL.6060.TOWR | 2024-06-28 | 2024-06-28 | 2025-01-23 | On-Time |  | 2025-06-28 | 2025-06-28 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46306321 | T2 RND MTN-TBLE MTN #1 65/274 RPR SHIELD | ICS
LC | 129143907 | 045/006 | T2 WV FORT ROSS-GUALALA 45/006 RPL STRW | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-06-28 | 2024-06-28 | 2025-04-28 | On-Time |  | 2025-06-28 | 2025-06-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574242 | T2 WV FORT ROSS-GUALALA 45/006 RPL STRW | 70Y
LC | 129144203 | 021/410 | T2 HAT CRK #1-WESTWD 21/410 COMPLETE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-28 | 2024-06-28 | 2025-05-01 | On-Time |  | 2025-06-28 | 2025-06-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574758 | T2 EI HAT CRK #1-WESTWD 21/410 RPL STRW | 70Y
LC | 129144205 | 025/481 | T2 HAT CRK #1-WESTWD 25/481 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-28 | 2024-06-28 | 2025-06-18 | On-Time |  | 2025-06-28 | 2025-06-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574765 | T2 EI HAT CRK #1-WESTWD 25/481 RPL STRW | 70Y
LC | 129144220 | 022/431 | T2 EI HAT CRK #1-WESTWD 22/431 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-28 | 2024-06-28 | 2025-06-15 | On-Time |  | 2025-06-28 | 2025-06-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574762 | T2 EI HAT CRK #1-WESTWD 22/431 RPL STRW | 70Y
LC | 129144235 | 021/412 | T2 HAT CRK #1-WESTWOOD 21/412 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-28 | 2024-06-28 | 2025-05-01 | On-Time |  | 2025-06-28 | 2025-06-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574760 | T2 EI HAT CRK #1-WESTWD 21/412 RPL STRW | 70Y
LC | 129144237 | 028/543 | T2 EI HAT CRK #1-WESTWD 28/543 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-28 | 2024-06-28 | 2025-06-18 | On-Time |  | 2025-06-28 | 2025-06-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574767 | T2 EI HAT CRK #1-WESTWD 28/543 RPL STRW | 70Y
LC | 129144443 | 028/545 | T2 WV HAT CRK #1-WESTWD 28/545 INS DAMW | TABLEMTN | ETL.7030.INSL.NCER | 2024-06-28 | 2024-06-28 | 2025-06-17 | On-Time |  | 2025-06-28 | 2025-06-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46416172 | T2 WV HAT CRK #1-WESTWD 28/545 INS DAMW | ICW
LC | 129144501 | 029/562 | T2 WV HAT CRK #1-WESTWD 29/562 INS DAMW | TABLEMTN | ETL.7030.INSL.NCER | 2024-06-28 | 2024-06-28 | 2025-06-17 | On-Time |  | 2025-06-28 | 2025-06-28 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46416173 | T2 WV HAT CRK #1-WESTWD 29/562 INS DAMW | ICW
LC | 129224589 | 035/200 | T2 XCHQUR-INDIAN FLT 35/200 RPR JUMS | FRESNO | ETL.8650.INSL.NCER | 2024-07-15 | 2024-06-28 | 2024-06-28 | Past Due |  | 2024-12-28 | 2025-06-28 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46297965 | T2 DI XCHQUR-INDIAN FLT 35/200 RPR JUMS | ICS
LC | 129311774 | 001/013 | T2 DI PIT #1-COTTONWOOD 1/13 COTTER | TABLEMTN | ETL.5390.INSL.NCER | 2024-07-30 | 2024-06-28 | 2025-04-21 | On-Time |  | 2025-06-28 | 2025-06-28 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46452721 | T2 DI PIT #1-COTTONWOOD 1/13 COTTER | ICS
LC | 123956921 | 009/147 | T3NT ATSCDR-SNLS-OBSPO 9/147 BNT STEEL | PISMOBCH | ETL.8490.TOWR | 2022-06-29 | 2022-06-29 | 2023-07-11 | On-Time |  | 2025-06-29 | 2025-06-29 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45656551 | T3 ATSCDRO-SAN LUS OBSPO 9/147 BNT STEEL | ICQ
LC | 124066144 | 014/272 | T2NT DI SMRTVL-CMP FAR W 14/272 RMV BUTT | SACTO | ETL.7970.POLE.WOOD | 2022-07-12 | 2022-06-29 | 2023-08-27 | On-Time |  | 2025-06-29 | 2025-06-29 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 TR2N PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Wood | Remove | 45657176 | T2 DI SMRTVL-CMP FR WST 14/272 RMV BUTT | ICW
LC | 124088014 | 040/295 | T3NT DI CARIBOU-TBL MTN 040/295 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2022-07-15 | 2022-06-29 | 2023-07-28 | On-Time |  | 2025-06-29 | 2025-06-29 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45593301 | T3 DI CARIBOU-TBL MTN 040/295 RPR STRT | ICQ
LC | 129146153 | 012/010 | T2 BRIDGEVILLE-GRBRVLE 12/10 RPL INSW | EUREKA | ETL.6220.INSL.CERA | 2024-06-29 | 2024-06-29 | 2024-06-29 | Past Due |  | 2025-06-29 | 2025-06-29 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572071 | T2 EI BRIDGEVILLE-GRBRVLE 12/10 RPL INSW | 93I
LC | 129146166 | 030/583 | T2 EI HAT CRK #1-WESTWD 30/583 CNCL | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-29 | 2024-06-29 | 2024-06-29 | Past Due |  | 2025-06-29 | 2025-06-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35574770 | T2 EI HAT CRK #1-WESTWD 30/583 RPL STRW | 70Y
LC | 129146185 | 033/649 | T2 EI HAT CRK #1-WESTWD 33/649 RPR GYWW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-06-29 | 2024-06-29 | 2025-03-29 | On-Time |  | 2025-06-29 | 2025-06-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46416174 | T2 EI HAT CRK #1-WESTWD 33/649 RPR GYWW | ICW
LC | 129146238 | 012/015 | T2 BRIDGEVILLE-GRBRVLE 12/15 RPL POLE | EUREKA | ETL.6220.POLE.WOOD | 2024-06-29 | 2024-06-29 | 2024-06-29 | Past Due |  | 2025-06-29 | 2025-06-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572072 | T2 EI BRIDGEVILLE-GRBRVLE 12/15 RPL POLE | 70Y
LC | 129146450 | 017/547 | T2 SPAULDING-SUMMIT 17/547 RPL STRW | SACTO | ETL.8060.POLE.WOOD | 2024-06-29 | 2024-06-29 | 2024-06-29 | Past Due |  | 2025-06-29 | 2025-06-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572883 | T2 EI SPAULDING-SUMMIT 17/547 RPL STRW | 70Y
LC | 129152455 | 015/493 | T2 SPAULDING-SUMMIT 15/493 RPL STRW | SACTO | ETL.8060.POLE.WOOD | 2024-07-01 | 2024-06-29 | 2024-06-29 | Past Due |  | 2025-06-29 | 2025-06-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572879 | T2 EI SPAULDING-SUMMIT 15/493 RPL STRW | 70Y
LC | 129152457 | 015/492 | T2 SPAULDING-SUMMIT 15/492 RPL STRW | SACTO | ETL.8060.POLE.WOOD | 2024-07-01 | 2024-06-29 | 2024-06-29 | Past Due |  | 2025-06-29 | 2025-06-29 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572878 | T2 EI SPAULDING-SUMMIT 15/492 RPL STRW | 70Y
LC | 123985008 | 003/087 | T3NT DI DEER CREEK-DRUM 003/087 RPR INSW | SACTO | ETL.6690.INSL.NCER | 2022-07-02 | 2022-06-30 | 2023-06-19 | On-Time |  | 2025-06-30 | 2025-06-30 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 45684649 | T3 DI DEER CREEK-DRUM 003/087 RPR INSW | ICW
LC | 123982492 | 028/231 | T2NT DI CRESTA RIO OSO 28/231 RPR STRT | TABLEMTN | ETL.4590.TOWR | 2022-07-02 | 2022-07-01 | 2024-08-29 | On-Time |  | 2025-07-01 | 2025-07-01 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB SR23 | No Good/Out of Stdrd | Structure-Tower | Repair | 46128012 | T2NT DI CRESTA RIO OSO 28/231 RPR STRT | ICQ
LC | 123984440 | 013/089 | T2NT DI CTRA CSTA-LS PSTS 13/89 RMV NEST | CONCORD | ETL.4510.TOWR | 2022-07-02 | 2022-07-01 | 2023-08-31 | On-Time |  | 2025-07-01 | 2025-07-01 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 45515586 | T2 DI CTRA CSTA-LS PSTAS 13/89 RMV NEST | ICS
LC | 124196128 | 007/036 | T2NT DI CNTR CSTA-MRG #1 7/36 RPR STRT | CONCORD | ETL.5452.TOWR | 2022-07-29 | 2022-07-01 | 2023-07-26 | On-Time |  | 2025-07-01 | 2025-07-01 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45515606 | *CANC*DI T2 CNTRA CSTA-MRGA #1 07/36 RPR | ICS
LC | 129151017 | 004/100 | T2 EI COLGATE-GRSS VLLY 004/100 RPL POLE | SACTO | ETL.6490.POLE.WOOD | 2024-07-01 | 2024-07-01 | 2025-05-31 | On-Time |  | 2025-07-01 | 2025-07-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572551 | T2 EI COLGATE-GRSS VLLY 004/100 RPL POLE | 70Y
LC | 129151087 | 004/101 | T2 EI COLGATE-GRSS VLLY 004/101 RPR INSW | SACTO | ETL.6490.INSL | 2024-07-01 | 2024-07-01 | 2025-02-27 | On-Time |  | 2025-07-01 | 2025-07-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Repair | 46400339 | T2 EI COLGATE-GRSS VLLY 004/101 RPR INSW | ICW
LC | 129151207 | 004/103 | T2 EI COLGATE-GRSS VLLY 004/103 RPL POLE | SACTO | ETL.6490.POLE.WOOD | 2024-07-01 | 2024-07-01 | 2025-05-31 | On-Time |  | 2025-07-01 | 2025-07-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572552 | T2 EI COLGATE-GRSS VLLY 004/103 RPL POLE | 70Y
LC | 129151563 | 000/006 | T2 VLY SPRNGS-CLVRS CMNT 0/6 RPL ANCW | VICTOR | ETL.8220.POLE.WOOD | 2024-07-01 | 2024-07-01 | 2025-05-06 | On-Time |  | 2025-07-01 | 2025-07-01 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR SWRK SPCR ACCH USA COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573397 | T2 VLY SPRNGS-CLVRS CMNT 0/6 RPL ANCW | 93E
LC | 129151977 | 029/000 | T2 WV PHILO JCT-ELK 29/000 INS DAMW | WILLITS | ETL.7780.INSL.NCER | 2024-07-01 | 2024-07-01 | 2025-01-29 | On-Time |  | 2025-07-01 | 2025-07-01 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46340413 | T2 WV PHILO JCT-ELK 29/000 INS DAMW | ICW
LC | 129153029 | 007/182 | T2 EI COLGATE-GRSS VLLY 007/182 RPL POLE | SACTO | ETL.6490.POLE.WOOD | 2024-07-01 | 2024-07-01 | 2025-05-30 | On-Time |  | 2025-07-01 | 2025-07-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572553 | T2 EI COLGATE-GRSS VLLY 007/182 RPL POLE | 70Y
LC | 130704026 | 020/140 | T3 METCALF-GREEN VALLEY 20/140C RPR GYWW | MOSSLNDG | ETL.2540.POLE.STPS | 2025-01-02 | 2024-12-31 | 2025-02-07 | On-Time |  | 2025-03-31 | 2025-07-01 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46451934 | T3 METCALF-GREEN VALLEY 20/140C RPR GYWW | ICW
LC | 130709749 | 020/140 | T3 METCALF-GREEN VALLEY 20/140R RPR GYWW | MOSSLNDG | ETL.2540.POLE.STPS | 2025-01-06 | 2024-12-31 | 2025-02-07 | On-Time |  | 2025-03-30 | 2025-07-01 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46451932 | T3 METCALF-GREEN VALLEY 20/140R RPR GYWW | ICW
LC | 130709800 | 020/140 | T3 METCALF-GREEN VALLEY 20/140L RPR GYWW | MOSSLNDG | ETL.2540.POLE.STPS | 2025-01-06 | 2024-12-31 | 2025-02-07 | On-Time |  | 2025-03-30 | 2025-07-01 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46451933 | T3 METCALF-GREEN VALLEY 20/140L RPR GYWW | ICW
LC | 128014750 | 000/018 | T2 HALSEY-PLACER 000/018 GO95 | SACTO | ETL.6990.POLE.WOOD | 2024-01-09 | 2024-01-02 | 2024-01-02 | TBC |  | 2025-07-02 | 2025-07-02 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR FIRE ACCH COMP OH XMPT TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35522536 | T2 HALSEY-PLACER 000/018 GO95 | 93G
LC | 129156252 | 009/071 | T2 EI EL DRAD-MSURI FLT #2 9/71 RPR GYWW | SACTO | ETL.1540.POLE.NWOD | 2024-07-02 | 2024-07-02 | 2024-08-26 | On-Time |  | 2024-10-02 | 2025-07-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46305384 | T2 EI EL DRAD-MSURI FLT #2 9/71 RPR GYWW | ICW
LC | 129156331 | 008/103 | T2 WV DIVIDE-CABRILLO #1 08/103 GO95 | PISMOBCH | ETL.1380.POLE.WOOD | 2024-07-02 | 2024-07-02 | 2024-07-02 | TBC |  | 2025-07-02 | 2025-07-02 | 401 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35587433 | T2 WV DIVIDE-CABRILLO #1 08/103 GO95 | 93G
LC | 129156839 | 000/003 | T2 EI BLACK TAP 0/3 CGI | TABLEMTN | ETL.5431.TOWR | 2024-07-02 | 2024-07-02 | 2025-04-21 | On-Time |  | 2024-10-02 | 2025-07-02 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 129156930 | 009/162 | T2 TEJON-LEBEC 009/162 RPR INSW | MIDWAY | ETL.9250.INSL.NCER | 2024-07-02 | 2024-07-02 | 2025-05-09 | On-Time |  | 2025-07-02 | 2025-07-02 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46302709 | T2 TEJON-LEBEC 009/162 RPR INSW | ICW
LC | 129158039 | C005/023 | T2 MOSS LANDING-COBURN C5/23 TOUCH | MOSSLNDG | ETL.5330.TOWR | 2024-07-02 | 2024-07-02 | 2024-07-02 | TBC |  | 2025-01-02 | 2025-07-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46478234 | T2 MOSS LANDING-COBURN C005/023 TOUCH | ICQ
LC | 129159652 | 091/001 | T2 HUMBOLDT-TRINITY 91/1L RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-07-02 | 2024-07-02 | 2024-07-02 | TBC |  | 2025-07-02 | 2025-07-02 | 401T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR FIRE SPCR OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35564635 | T2 HUMBOLDT-TRINITY 91/1L RPL STRW | 93G
LC | 129159654 | 091/001 | T2 HUMBOLDT-TRINITY 91/1R RPL STRW | EUREKA | ETL.1820.POLE.WDPS | 2024-07-02 | 2024-07-02 | 2024-07-02 | TBC |  | 2025-07-02 | 2025-07-02 | 401T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR FIRE SPCR OH TR2 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35564635 | T2 HUMBOLDT-TRINITY 91/1L RPL STRW | 93G
LC | 129162002 | 065/273 | T2 ROUND MNTN-TBL MNTN#1 65/273 RPL INSS | TABLEMTN | ETL.6060.INSL | 2024-07-03 | 2024-07-03 | 2025-01-23 | On-Time |  | 2025-07-03 | 2025-07-03 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569940 | T2 EI RND MTN-TBL MTN #1 RPL INSS 9 TWRS | 93K
LC | 129162712 | 000/007 | T2 WV RACETRACK TAP 000/007 INS DMPW | VICTOR | ETL.2393.INSL.NCER | 2024-07-03 | 2024-07-03 | 2025-06-18 | On-Time |  | 2025-07-03 | 2025-07-03 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46325964 | T2 WV RACETRACK TAP 000/007 INS DMPW | ICW
LC | 129164068 | 003/019A | T2 PITTSBURG-CLAYTON #3 3/19A RPR FOND | CONCORD | ETL.3290.TOWR | 2024-07-03 | 2024-07-03 | 2024-08-30 | On-Time |  | 2025-01-03 | 2025-07-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR REMT COMP OH FMOB TR2 PRTO FRAB DURA | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46272858 | T2 PITTSBURG-CLAYTON #3 3/19A RPR FOND | ICQ
LC | 129164083 | 056/239 | T2 ROUND MNTN-TABLE MNTN 56/239 COTTER | TABLEMTN | ETL.6070.INSL | 2024-07-03 | 2024-07-03 | 2025-02-21 | On-Time |  | 2025-07-03 | 2025-07-03 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46306322 | T2 ROUND MNTN-TABLE MNTN 56/239 COTTER | ICS
LC | 129164097 | 003/019B | T2 PITTSBURG-CLAYTON #4 3/19B RPR FOND | CONCORD | ETL.3291.TOWR | 2024-07-03 | 2024-07-03 | 2025-06-17 | On-Time |  | 2025-01-03 | 2025-07-03 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46272857 | T2 PITTSBURG-CLAYTON #4 3/19B RPR FOND | ICQ
LC | 129167090 | 002/020 | T2 PIT #7 TAP 2/20L RPL STRW | TABLEMTN | ETL.5442.POLE.WDPS | 2024-07-03 | 2024-07-03 | 2025-06-17 | On-Time |  | 2025-07-03 | 2025-07-03 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35607191 | T2 WV PIT #7 TAP 2/20 RPL STRW | 70Y
LC | 129179053 | 002/020 | T2 PIT #7 TAP 2/20R RPL STRW | TABLEMTN | ETL.5442.POLE.WDPS | 2024-07-08 | 2024-07-03 | 2025-06-17 | On-Time |  | 2025-07-03 | 2025-07-03 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CREW COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35607191 | T2 WV PIT #7 TAP 2/20 RPL STRW | 70Y
LC | 129187117 | 030/163 | T2 EXCHQUR INDN FLT 30/163 COTTER | FRESNO | ETL.8650.INSL.NCER | 2024-07-08 | 2024-07-04 | 2024-07-04 | TBC |  | 2025-07-04 | 2025-07-04 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297939 | T2 DI EXCHQUR INDN FLT 30/163 COTTER | ICS
LC | 124023205 | 023/171 | T2NT DI CRBU-TBLE MNTN 23/171 RPR STRT | TABLEMTN | ETL.4440.TOWR | 2022-07-07 | 2022-07-05 | 2023-08-23 | On-Time |  | 2025-07-05 | 2025-07-05 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45593037 | T2 DI CARIB-TBLE MNTN 23/171 RPR STRT | ICQ
LC | 124063618 | 025/184 | T2NT DI CARB-TBL MTN 25/184 BNT STL | TABLEMTN | ETL.4440.TOWR | 2022-07-12 | 2022-07-05 | 2023-08-23 | On-Time |  | 2025-07-05 | 2025-07-05 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45593263 | T2 DI CARIBOU-TBL MTN 25/184 BNT STEEL | ICQ
LC | 124218723 | :006/043A | T2NT DI ROCK CREEK-POE :6/43A RMV VEG | TABLEMTN | ETL.5630.POLE.NWOD | 2022-08-03 | 2022-07-05 | 2023-08-16 | On-Time |  | 2025-07-05 | 2025-07-05 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129173467 | 034/007 | T2 WV PHILO JCT-ELK_034/007C RPL GYWW | WILLITS | ETL.7780.POLE.WDPS | 2024-07-05 | 2024-07-05 | 2025-01-27 | On-Time |  | 2025-07-05 | 2025-07-05 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | Missing | Guy Wire-Wood | Install | 46340414 | T2 WV PHILO JCT-ELK_034/007C RPL GYWW | ICW
LC | 129174278 | A001/015 | T2 FULTON-PUEBLO :1/15 RPL INSW | LAKEVLLE | ETL.1600.INSL.NCER | 2024-07-05 | 2024-07-05 | 2024-09-03 | On-Time |  | 2024-10-05 | 2025-07-05 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW NONR COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573726 | T2 FULTON-PUEBLO :1/13 RPL INSW | 93I
LC | 129175433 | A001/013 | T2 FULTON-PUEBLO :1/13 RPL INSW | LAKEVLLE | ETL.1600.INSL.NCER | 2024-07-05 | 2024-07-05 | 2024-08-17 | On-Time |  | 2024-10-05 | 2025-07-05 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573726 | T2 FULTON-PUEBLO :1/13 RPL INSW | 93I
LC | 124062000 | 010/073 | T2NT DI ROCK CREEK-POE 010/073 RMV VEG | TABLEMTN | ETL.5630.TOWR | 2022-07-12 | 2022-07-07 | 2023-08-30 | On-Time |  | 2025-07-07 | 2025-07-07 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE CNCL OH TR2N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 124228472 | 010/085 | T2NT DI CRESTA RIO OSO 10/085 RMV VEG | TABLEMTN | ETL.4590.TOWR | 2022-08-04 | 2022-07-07 | 2023-11-22 | On-Time |  | 2025-07-07 | 2025-07-07 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129393807 | 015/304 | T2 DI HAT CREEK #1-WSTWD 15/304 RPR INSW | TABLEMTN | ETL.7030.INSL.NCER | 2024-08-15 | 2024-07-07 | 2025-05-17 | On-Time |  | 2025-07-07 | 2025-07-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46416183 | T2 DI HAT CREEK #1-WSTWD 15/304 RPR INSW | ICW
LC | 130735011 | 006/077A | T3 GEYSERS #3-CLOVERDALE 6/077A GO95 | LAKEVLLE | ETL.1650.POLE.NWOD | 2025-01-13 | 2025-01-07 | 2025-04-15 | On-Time |  | 2025-07-07 | 2025-07-07 | 401T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35610082 | T3 GEYSERS #3-CLOVERDALE 6/077A GO95 | 93G
LC | 130735015 | 006/077B | T3 GEYSERS #3-CLOVERDALE 6/077B GO95 | LAKEVLLE | ETL.1650.POLE.NWOD | 2025-01-13 | 2025-01-07 | 2025-04-15 | On-Time |  | 2025-07-07 | 2025-07-07 | 401T | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35610082 | T3 GEYSERS #3-CLOVERDALE 6/077A GO95 | 93G
LC | 130735081 | 006/077C | T3 GEYSERS #3-CLOVERDALE 6/077C GO95 | LAKEVLLE | ETL.1650.POLE.NWOD | 2025-01-13 | 2025-01-07 | 2025-04-15 | On-Time |  | 2025-07-07 | 2025-07-07 | 401T | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35610082 | T3 GEYSERS #3-CLOVERDALE 6/077A GO95 | 93G
LC | 124067207 | 019/129 | T3NT DI POE-RIO OSO-RIO 19/129 RMV VEG | TABLEMTN | ETL.5540.TOWR | 2022-07-12 | 2022-07-08 | 2023-08-14 | On-Time |  | 2025-07-08 | 2025-07-08 | 564 | TR3N |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR3N PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129180003 | 043/008 | T2 WV FORT ROSS-GUALALA 43/8 RPL INSW | LAKEVLLE | ETL.6980.INSL.NCER | 2024-07-08 | 2024-07-08 | 2025-04-28 | On-Time |  | 2025-07-08 | 2025-07-08 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574241 | T2 WV FORT ROSS-GUALALA 43/8 RPL INSW | 93I
LC | 129185628 | 003/000 | T2 RIO DEL TAP 003/000C RPL POLE | EUREKA | ETL.7851.POLE.WDPS | 2024-07-08 | 2024-07-08 | 2024-07-08 | TBC |  | 2025-07-08 | 2025-07-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572960 | T2 EI RIO DEL TAP 003/000R RPL POLE | 70Y
LC | 129185690 | 003/000 | T2 RIO DEL TAP 003/000R RPL POLE | EUREKA | ETL.7851.POLE.WDPS | 2024-07-08 | 2024-07-08 | 2024-07-08 | TBC |  | 2025-07-08 | 2025-07-08 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35572960 | T2 EI RIO DEL TAP 003/000R RPL POLE | 70Y
LC | 129187461 | 022/083 | T2 DI EXCHQUR INDN FLTS 22/083 RPR JUMS | FRESNO | ETL.8650.INSL.NCER | 2024-07-08 | 2024-07-08 | 2024-07-08 | TBC |  | 2025-07-08 | 2025-07-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46297960 | T2 DI EXCHQUR INDN FLTS 22/083 RPR JUMS | ICS
LC | 129187468 | 019/070 | T2 DI EXCHQUR-INDN FLTS 19/070 COMPLETE | FRESNO | ETL.8650.INSL.NCER | 2024-07-08 | 2024-07-08 | 2025-04-01 | On-Time |  | 2025-07-08 | 2025-07-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46297961 | T2 DI EXCHQUR-INDN FLTS 19/070 RPR JUMS | ICS
LC | 129187537 | 023/087 | T2 DI EXCHQUR INDN FLTS 23/087 RMV VEG | FRESNO | ETL.8650.TOWR | 2024-07-08 | 2024-07-08 | 2025-04-07 | On-Time |  | 2025-07-08 | 2025-07-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129187583 | 026/115 | T2 EXCHQUER INDIAN FLAT 26/115 RPR JUMS | FRESNO | ETL.8650.INSL.NCER | 2024-07-08 | 2024-07-08 | 2024-07-08 | TBC |  | 2025-07-08 | 2025-07-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46274018 | T2 DI EXCHQUR INDN FLTS 26/115 RPR JUMS | ICS
LC | 129187669 | 030/160 | T2 EXCHQUR-INDIN FLTS 30/160 COTTER | FRESNO | ETL.8650.INSL.NCER | 2024-07-08 | 2024-07-08 | 2024-07-08 | TBC |  | 2025-07-08 | 2025-07-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297962 | T2 DI EXCHQUR-INDIN FLTS 30/160 COTTER | ICS
LC | 129187683 | 021/082 | T2 EXCHQUR-INDIAN FLT 21/82 RPR JUMS | FRESNO | ETL.8650.INSL.NCER | 2024-07-08 | 2024-07-08 | 2024-07-08 | TBC |  | 2025-07-08 | 2025-07-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46274017 | T2 DI EXCHQUR-INDIAN FLT 21/82 RPR JUMS | ICS
LC | 129193369 | 031/167A | T2 EXCHEQUR INDIAN FLAT 31/167A RPR JUMS | FRESNO | ETL.8650.INSL.NCER | 2024-07-09 | 2024-07-08 | 2024-07-08 | TBC |  | 2025-07-08 | 2025-07-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46280430 | T2 DI EXCHQUR INDN FLT 31/167A RPR JUMS | ICS
LC | 129193740 | 016/054 | T2 DI EXCHEQUER-IDN FLT 16/054 RMV VEG | FRESNO | ETL.8650.TOWR | 2024-07-09 | 2024-07-08 | 2025-04-14 | On-Time |  | 2025-07-08 | 2025-07-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW CNCL OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129193780 | 027/129 | T3 DI EXCHEQUER-IDN FLT 27/129 RPR STRT | FRESNO | ETL.8650.POLE.NWOD | 2024-07-09 | 2024-07-08 | 2024-07-08 | TBC |  | 2025-07-08 | 2025-07-08 | 543 | TR3 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46292625 | T3 DI EXCHEQUER-IDN FLT 27/129 RPR STRT | ICQ
LC | 129230112 | 019/072 | T2 DI EXCHQUR-INDIAN FLAT 19/72 RPR STRT | FRESNO | ETL.8650.TOWR | 2024-07-16 | 2024-07-08 | 2025-04-23 | On-Time |  | 2025-07-08 | 2025-07-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46297905 | T2 DI EXCHQUR-INDIAN FLAT 19/72 RPR STRT | ICQ
LC | 129230240 | 016/057 | T2 DI EXCHQUR-INDIAN FLAT 16/57 RMV VEG | FRESNO | ETL.8650.TOWR | 2024-07-16 | 2024-07-08 | 2025-03-28 | On-Time |  | 2025-07-08 | 2025-07-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 129235688 | 030/161 | T2 DI EXCHQR-INDN FLT 30/161 RPR JUMS | FRESNO | ETL.8650.INSL.NCER | 2024-07-17 | 2024-07-08 | 2024-07-08 | TBC |  | 2025-07-08 | 2025-07-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46297966 | T2 DI EXCHQR-INDN FLT 30/161 RPR JUMS | ICS
LC | 129235744 | 018/063 | T2 DI EXCHQUR-INDAN FLT 18/63 RMV VEG | FRESNO | ETL.8650.TOWR | 2024-07-17 | 2024-07-08 | 2024-07-08 | TBC |  | 2025-07-08 | 2025-07-08 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 129614783 | 011/078 | T2 IGNACIO-ALTO-SLTO #1 11/78 RPR FOND | LAKEVLLE | ETL.7160.TOWR | 2024-10-01 | 2024-07-08 | 2025-03-11 | On-Time |  | 2025-07-08 | 2025-07-08 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46419550 | T2 IGNACIO-ALTO-SLTO #1 11/78 RPR FOND | ICQ
LC | 130748025 | 005/005 | T3 DIABLO UNIT #2 05/05 RPR INSS | PISMOBCH | ETL.5950.INSL | 2025-01-16 | 2025-01-08 | 2025-01-08 | TBC |  | 2025-07-08 | 2025-07-08 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46460943 | T3 DIABLO UNIT #2 05/05 RPR INSS | ICS
LC | 124235652 | 018/085 | T0 T2NT DI MONTA VISTA-SARATOG 18/85 RPR | METCALF | ETL.5240.TOWR | 2022-08-05 | 2022-07-09 | 2024-02-08 | On-Time |  | 2025-07-09 | 2025-07-09 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH PRTO AIR FRAA TER0 | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46147367 | T0 DI MONTA VISTA-SARATOG 18/85 RPR FOND | ICQ
LC | 129188241 | C007/031 | T2 COBURN-LAS AGLS SS C7/31 COTTER | MOSSLNDG | ETL.4460.INSL.NCER | 2024-07-09 | 2024-07-09 | 2024-07-09 | TBC |  | 2025-07-09 | 2025-07-09 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46391447 | T2 CBRN-LS AGULS S ST-PNCHE C7/31 COTTER | ICS
LC | 129189169 | 013/260-GUY | T2 EI COLGATE-PALRMO 13/260-GUY RPL STRW | TABLEMTN | ETL.6500.POLE.WOOD | 2024-07-09 | 2024-07-09 | 2025-03-03 | On-Time |  | 2025-07-09 | 2025-07-09 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572927 | T2 EI COLGATE-PALRMO 13/260-GUY RPL STRW | 70Y
LC | 129191344 | 016/073 | T2 SN LS OBISPO-SNTA MRIA 16/73 RPL INSS | PISMOBCH | ETL.3540.INSL.CERA | 2024-07-09 | 2024-07-09 | 2025-05-29 | On-Time |  | 2025-01-09 | 2025-07-09 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR RESD REAR CLR ACCH COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 31528665 | DI SN LS OBSPO-SNT MARIA 25/135 RPL INSS | 93K
LC | 129193462 | :012/063 | T2 CZY HRS CN SLNS #1 :12/63 COMPLETE | MOSSLNDG | ETL.2900.TOWR | 2024-07-09 | 2024-07-09 | 2025-04-30 | On-Time |  | 2025-07-09 | 2025-07-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416715 | T2 DI CZY HRS CN SLNS #1 12/63 RPR STRT | ICQ
LC | 129246746 | 014/004 | T2 DI TRINITY MAPLE CREEK 14/4 RPR GYWW | EUREKA | ETL.8170.POLE.WOOD | 2024-07-19 | 2024-07-09 | 2025-03-22 | On-Time |  | 2025-07-09 | 2025-07-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46345960 | T2 DI TRINITY MAPLE CREEK 14/4 RPR GYWW | ICW
LC | 129246781 | 014/004 | T2 DI TRINITY MAPLE CREEK 14/4 RPR JUMW | EUREKA | ETL.8170.INSL.NCER | 2024-07-19 | 2024-07-09 | 2025-03-22 | On-Time |  | 2024-10-09 | 2025-07-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46338675 | T2 DI TRINITY MAPLE CREEK 14/4 RPR JUMW | ICW
LC | 129445025 | 024/286 | T2 DI DRUM-SUMMIT #1 24/286L RPR STRW | SACTO | ETL.1440.POLE.WDPS | 2024-08-27 | 2024-07-09 | 2025-05-02 | On-Time |  | 2025-07-09 | 2025-07-09 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46401389 | T2 DI DRUM-SUMMIT #1 24/286L RPR STRW | ICW
LC | 124090725 | 001/015 | T2NT DI BCKS CREEK-ROCK CREK 1/15 UNBURY | TABLEMTN | ETL.4430.TOWR | 2022-07-15 | 2022-07-10 | 2023-08-12 | On-Time |  | 2025-07-10 | 2025-07-10 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2N PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45582473 | T2 DI BUCKS CREEK-ROCK CREEK 1/15 FONT R | ICQ
LC | 129205337 | 015/485 | T2 SPAULDING-SUMMIT 015/485 RPR GYWW | SACTO | ETL.8060.POLE.WOOD | 2024-07-10 | 2024-07-10 | 2024-07-10 | TBC |  | 2025-01-10 | 2025-07-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46400340 | T2 SPAULDING-SUMMIT 015/485 RPR GYWW | ICW
LC | 129205722 | 038/249 | T2 TRINITY-COTTONWOOD 38/249 RMV VEG | TABLEMTN | ETL.4040.POLE.STPS | 2024-07-10 | 2024-07-10 | 2024-07-10 | TBC |  | 2025-07-10 | 2025-07-10 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW PATR OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129205752 | 021/327 | T2 KESWICK-TRINITY 021/327 RPL POLE | TABLEMTN | ETL.7270.POLE.WOOD | 2024-07-10 | 2024-07-10 | 2025-04-12 | On-Time |  | 2025-07-10 | 2025-07-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573318 | T2 KESWICK-TRINITY 021/327 RPL POLE | 70Y
LC | 129209898 | 002/055 | T2 JEFF-STNFRD-STNFRD 2/55 RPL POLE | METCALF | ETL.7220.POLE.WOOD | 2024-07-11 | 2024-07-10 | 2024-07-10 | TBC |  | 2025-07-10 | 2025-07-10 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW TNT COMP OH TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35573650 | T2 JEFF-STNFRD-STNFRD 2/55 RPL POLE | 70Y
LC | 129450610 | 018/099A | T2 LONE TREE-CAYETANO 18/99A RPL INSS | CONCORD | ETL.6160.INSL.NCER | 2024-08-28 | 2024-07-10 | 2024-07-10 | TBC |  | 2025-07-10 | 2025-07-10 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35609139 | T2 DI LN TR-CYTNO 18/99A RPL INSS | 93K
LC | 124256530 | 001/015 | T2NT DI ROCK CREEK-POE 01/15 RPR STRT | TABLEMTN | ETL.5630.TOWR | 2022-08-09 | 2022-07-11 | 2023-11-28 | On-Time |  | 2025-07-11 | 2025-07-11 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45648203 | T2 DI ROCK CREEK-POE 01/15 RPR STRT | ICQ
LC | 129209959 | 004/000 | T3 EI BRDGVLLE-GARBERVILLE 4/0 RPL STRW | EUREKA | ETL.6220.POLE.WOOD | 2024-07-11 | 2024-07-11 | 2024-07-11 | TBC |  | 2025-07-11 | 2025-07-11 | 372T | TR3 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35566372 | T3 EI BRDGVLLE-GARBERVILLE 4/0 RPL POLE | 70Y
LC | 129316743 | 17 | T2 DI KSWCK-TRINITY 011/151 RPR SWITCH | TABLEMTN | ETL.7270.SWIT | 2024-07-31 | 2024-07-11 | 2025-04-24 | On-Time |  | 2025-07-11 | 2025-07-11 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | Out of Adjustment | Switch | Repair | 46337215 | T2 DI KSWCK-TRINITY 011/151 RPR SWITCH | ICE
LC | 124090772 | 082/419C | T2NT DI MLN-RND MTN #2 082/419C RPR GYWS | TABLEMTN | ETL.6020.TOWR | 2022-07-15 | 2022-07-12 | 2023-08-22 | On-Time |  | 2025-07-12 | 2025-07-12 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45650765 | T2 DI MLN-RND MTN #2 082/419C RPR GYWS | ICS
LC | 124091463 | 082/419B | T2NT DI MLN-RND MTN #2 82/419B RPR GYWS | TABLEMTN | ETL.6020.TOWR | 2022-07-15 | 2022-07-12 | 2023-08-22 | On-Time |  | 2025-07-12 | 2025-07-12 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45650764 | T2 DI MLN-RND MTN #2 82/419B RPR GYWS | ICS
LC | 124091569 | 082/419A | T2NT DI MLN-RND MTN #2 082/419A RPR GYWS | TABLEMTN | ETL.6020.TOWR | 2022-07-15 | 2022-07-12 | 2023-08-22 | On-Time |  | 2025-07-12 | 2025-07-12 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 45650763 | T2 DI MLN-RND MTN #2 082/419A RPR GYWS | ICS
LC | 124092507 | 002/047 | T3NT DI MIDDLEFORK #1 2/47 RPR CRSW | SACTO | ETL.8405.POLE.WOOD | 2022-07-15 | 2022-07-12 | 2023-08-20 | On-Time |  | 2025-07-12 | 2025-07-12 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3N PRTO AIR FRAB | No Good/Out of Stdrd | Crossarm-Wood | Repair | 45740192 | T3 DI MIDDLEFORK #1 2/47 RPR CRSW | ICW
LC | 129213924 | A007/087 | T2 WV PALERMO-OROVILLE #2 A7/87 INS DMPW | TABLEMTN | ETL.7740.INSL.NCER | 2024-07-12 | 2024-07-12 | 2025-06-18 | On-Time |  | 2025-07-12 | 2025-07-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46463719 | T2 WV PALERMO-OROVILLE #2 A7/87 INS DMPW | ICW
LC | 129217379 | 013/002 | T2 MENDOCINO-WILLITS 013/002 RPL STRW | WILLITS | ETL.7540.POLE.WOOD | 2024-07-12 | 2024-07-12 | 2025-01-10 | On-Time |  | 2025-07-12 | 2025-07-12 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574336 | T2 MENDOCINO-WILLITS 013/002 RPL POLE | 70Y
LC | 124077012 | 002/025 | T2NT DI BCKS CRK-RCK CRK 2/25 RPR STRT | TABLEMTN | ETL.4430.TOWR | 2022-07-14 | 2022-07-13 | 2024-04-29 | On-Time |  | 2025-07-13 | 2025-07-13 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46090891 | T2NT DI BCKS CRK-RCK CRK 2/25 RPR STRT | ICQ
LC | 124121775 | 022/169 | T2NT DI DRUM-RIO OSO #1 22/169 RMV VEG | SACTO | ETL.1420.TOWR | 2022-07-19 | 2022-07-13 | 2023-12-08 | On-Time |  | 2025-07-13 | 2025-07-13 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH TR2N PRTO AIR FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 124273236 | 012/099 | T3NT DI CRESTA RIO OSO 12/99 UNBURY | TABLEMTN | ETL.4590.TOWR | 2022-08-10 | 2022-07-15 | 2023-08-19 | On-Time |  | 2025-07-15 | 2025-07-15 | 543 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3N PRTO AIR FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 45597622 | T3 DI CRESTA RIO OSO 12/099 RPR FOND | ICQ
LC | 129220202 | 014/359 | T2 COTTONWOOD-BENTON #1 014/359 RPL POLE | TABLEMTN | ETL.6640.POLE.WOOD | 2024-07-15 | 2024-07-15 | 2025-04-28 | On-Time |  | 2025-07-15 | 2025-07-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572992 | T2 COTTONWOOD-BENTON #1 014/359 RPL POLE | 70Y
LC | 129221942 | :002/014 | T2 WV CARIBOU #2 :002/014 INS DMPW | TABLEMTN | ETL.6280.INSL.CERA | 2024-07-15 | 2024-07-15 | 2024-07-17 | On-Time |  | 2025-07-15 | 2025-07-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46284464 | T2 WV CARIBOU #2 :002/014 INS DMPW | ICW
LC | 129222167 | 005/008 | T2 MENDOCINO-WILLITS 05/008 RPR INSW | WILLITS | ETL.7540.INSL.NCER | 2024-07-15 | 2024-07-15 | 2024-07-15 | TBC |  | 2025-07-15 | 2025-07-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46310557 | T2 MENDOCINO-WILLITS 05/008 RPR INSW | ICW
LC | 129222946 | 003/094 | T2 COLGATE-GRASS VALLEY 03/94 RPR INSW | SACTO | ETL.6490.INSL | 2024-07-15 | 2024-07-15 | 2025-03-01 | On-Time |  | 2025-07-15 | 2025-07-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46400341 | T2 COLGATE-GRASS VALLEY 03/94 RPR INSW | ICW
LC | 129223187 | 037/161 | T2 MRRO BY-SLR SW STA #2 37/161 COTTER | PISMOBCH | ETL.5310.INSL | 2024-07-15 | 2024-07-15 | 2025-04-29 | On-Time |  | 2025-07-15 | 2025-07-15 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329546 | T2 MRRO BY-SLR SW STA #2 37/161 COTTER | ICS
LC | 129333893 | 137 | T2 DI HUMBOLDT TRINITY 81/4 RPR SWTC | EUREKA | ETL.1820.SWIT | 2024-08-05 | 2024-07-15 | 2024-11-08 | On-Time |  | 2024-10-15 | 2025-07-15 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR2 PRTO AIR DURA BRIN | Out of Adjustment | Switch | Repair | 46302077 | T2 DI HUMBOLDT TRINITY 81/4 RPR SWTC | ICE
LC | 129456832 | 082/004 | T2 DI HUMBOLDT-TRINITY 82/4L RPL POLE | EUREKA | ETL.1820.POLE.WDPS | 2024-08-29 | 2024-07-15 | 2025-04-21 | On-Time |  | 2025-07-15 | 2025-07-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35586919 | T2 DI HUMBOLDT-TRINITY 82/4L RPL POLE | 70Y
LC | 129456833 | 082/004 | T2 DI HUMBOLDT-TRINITY 82/4R RPL POLE | EUREKA | ETL.1820.POLE.WDPS | 2024-08-29 | 2024-07-15 | 2025-04-21 | On-Time |  | 2025-07-15 | 2025-07-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586919 | T2 DI HUMBOLDT-TRINITY 82/4L RPL POLE | 70Y
LC | 129469580 | :015/081 | T2 DI CRZY HRS CNY SLN #1 15/81 RPR STRT | MOSSLNDG | ETL.2900.TOWR | 2024-09-03 | 2024-07-15 | 2025-04-30 | On-Time |  | 2025-07-15 | 2025-07-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416784 | T2 DI CRZY HRS CNY SLN #1 15/81 RPR STRT | ICQ
LC | 124141533 | 040/185 | T2NT DI RD MT-TB MT #2 40/185 RPL INSS | TABLEMTN | ETL.6070.INSL | 2022-07-22 | 2022-07-16 | 2024-05-06 | On-Time |  | 2025-07-16 | 2025-07-16 | 532 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 31661877 | T2NT DI RD MT-TB MT #2 40/185 RPL INSS | 93K
LC | 124277138 | 047/208 | T2NT DI RND MTN TBL MT#1 47/208 BNT STEL | TABLEMTN | ETL.6060.TOWR | 2022-08-11 | 2022-07-16 | 2023-09-05 | On-Time |  | 2025-07-16 | 2025-07-16 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644474 | T2 DI RND MTN TBL MTN #1 47/208 BENT STL | ICQ
LC | 124279273 | 052/226 | T2NT DI RND MT TBL MN #1 52/226 BENT STL | TABLEMTN | ETL.6060.TOWR | 2022-08-11 | 2022-07-16 | 2023-09-06 | On-Time |  | 2025-07-16 | 2025-07-16 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45644483 | T2 DI RND MTN TBL MNT #1 52/226 BENT STL | ICQ
LC | 129225554 | 37 | T2 SPAULDING-SUMMIT 016/506 COTTER | SACTO | ETL.8060.SWIT | 2024-07-16 | 2024-07-16 | 2024-07-16 | TBC |  | 2025-07-16 | 2025-07-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46400344 | T2 SPAULDING-SUMMIT 016/506 COTTER | ICW
LC | 129227405 | 013/451 | T2 SPAULDING-SUMMIT- 013/451 RPR INSW | SACTO | ETL.8060.INSL.NCER | 2024-07-16 | 2024-07-16 | 2024-07-16 | TBC |  | 2025-07-16 | 2025-07-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Wood | Repair | 46401131 | T2 SPAULDING-SUMMIT- 013/451 RPR INSW | ICW
LC | 129228519 | 013/125 | T2 SAN LUIS OBISPO-CYCS 13/125 RMV DBRW | PISMOBCH | ETL.9090.INSL | 2024-07-16 | 2024-07-16 | 2024-08-22 | On-Time |  | 2024-10-16 | 2025-07-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ DURA BRIN | Debris/Nest/etc. | Conductor-Wood | Remove | 46303797 | T2 SAN LUIS OBISPO-CYCS 13/125 RMV DBRW | ICW
LC | 129228672 | 014/006 | T2 COALINGA #1-SAN MIGUEL 14/6 RPL HNGR | FRESNO | ETL.8580.INSL.CERA | 2024-07-16 | 2024-07-16 | 2024-10-16 | On-Time |  | 2024-10-16 | 2025-07-16 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 PRTO PGEQ DURA BRIN | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46297909 | T2 COALINGA #1-SAN MIGUEL 14/6 RPL HNGR | ICQ
LC | 129246887 | 014/009 | T2 DI TRINITY MAPLE CREEK 14/9 RPR JMPW | EUREKA | ETL.8170.INSL.NCER | 2024-07-19 | 2024-07-16 | 2025-03-22 | On-Time |  | 2024-10-16 | 2025-07-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46338676 | T2 DI TRINITY MAPLE CREEK 14/9 RPR JMPW | ICW
LC | 129469674 | 031/009 | T2 DI MENDNO WITS FT BRG 31/9 RPR GYWW | WILLITS | ETL.7550.POLE.WOOD | 2024-09-03 | 2024-07-16 | 2025-03-05 | On-Time |  | 2025-07-16 | 2025-07-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46402749 | T2 DI MENDNO WITS FT BRG 31/9 RPR GYWW | ICW
LC | 129469675 | 008/175 | T2 DI HAM BRANCH CHESTER 8/175 RPR GYWW | TABLEMTN | ETL.7000.POLE.NWOD | 2024-09-03 | 2024-07-16 | 2025-01-08 | On-Time |  | 2025-07-16 | 2025-07-16 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337248 | T2 DI HAM BRANCH CHESTER 8/175 RPR GYWW | ICW
LC | 128049802 | 038/734 | T2 HAT CREEK #1-WESTWOOD 038/734 GO95 | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-17 | 2024-01-17 | 2025-05-27 | On-Time |  | 2025-07-17 | 2025-07-17 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35524483 | T2 HAT CREEK #1-WESTWOOD 038/734 GO95 | 93G
LC | 128049806 | 032/617 | T2 HAT CREEK #1-WESTWOOD 032/617 GO95 | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-17 | 2024-01-17 | 2025-06-15 | On-Time |  | 2025-07-17 | 2025-07-17 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35524487 | T2 HAT CREEK #1-WESTWOOD 032/617 GO95 | 93G
LC | 129230646 | 043/253 | T2 COTTLE-MELONES 043/253 TOUCH | VICTOR | ETL.4530.POLE.NWOD | 2024-07-17 | 2024-07-17 | 2024-07-17 | TBC |  | 2025-01-17 | 2025-07-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR2 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Steel | Repair | 46477463 | T2 COTTLE-MELONES 043/253 TOUCH | ICS
LC | 129232349 | 012/015 | T2 WV BRDGEVLLE-GRBERVLLE 12/15 INS DAMW | EUREKA | ETL.6220.INSL.CERA | 2024-07-17 | 2024-07-17 | 2024-07-17 | TBC |  | 2025-07-17 | 2025-07-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46403126 | T2 WV BRDGEVLLE-GRBERVLLE 12/15 INS DAMW | ICW
LC | 129235968 | 029/149 | T2 DI EXCHQR-INDN FLT 29/149 COTTER | FRESNO | ETL.8650.INSL.NCER | 2024-07-17 | 2024-07-17 | 2024-07-17 | TBC |  | 2025-07-17 | 2025-07-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46297927 | T2 DI EXCHQR-INDN FLT 29/149 COTTER | ICS
LC | 129247512 | 028/140 | T2 DI EXCHQR INDIAN FLAT 28/140 RPR JUMS | FRESNO | ETL.8650.INSL.NCER | 2024-07-19 | 2024-07-17 | 2024-07-17 | TBC |  | 2025-07-17 | 2025-07-17 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46297928 | T2 DI EXCHQR INDN FLT 28/140 RPR JMPS | ICS
LC | 129475662 | 013/115 | T2 DI CRAG VIEW-CASCADE 13/115 TOUCH | TABLEMTN | ETL.1350.TOWR | 2024-09-04 | 2024-07-17 | 2024-07-17 | TBC |  | 2025-01-17 | 2025-07-17 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46463299 | T2 DI CRAG VIEW-CASCADE 13/115 RPR STRT | ICQ
LC | 129475664 | 013/115 | T2 DI CRAG VIEW-CASCADE 13/115 RPL MKBL | TABLEMTN | ETL.1350.TOWR | 2024-09-04 | 2024-07-17 | 2024-07-17 | TBC |  | 2025-07-17 | 2025-07-17 | 671T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | FAA Lighting-Steel | Replace | 35586894 | T2 DI CRAG VIEW-CASCADE 13/115 RPL MRKB | 93P
LC | 129240534 | A001/015 | T2 WV KM GREEN TAP A001/015 RPL INSS | VICTOR | ETL.3505.INSL.NCER | 2024-07-18 | 2024-07-18 | 2025-05-30 | On-Time |  | 2025-07-18 | 2025-07-18 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35610461 | T2 WV KM GREEN TAP A001/015 RPL INSS | 93K
LC | 129243199 | 009/069 | T2 EI CARIBOU-TABLE MTN 9/069 CGI | TABLEMTN | ETL.4440.TOWR | 2024-07-18 | 2024-07-18 | 2025-04-18 | On-Time |  | 2024-10-18 | 2025-07-18 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 129243257 | 009/068 | T2 EI CARIBOU-TABLE MTN 9/068 CGI | TABLEMTN | ETL.4440.TOWR | 2024-07-18 | 2024-07-18 | 2025-04-18 | On-Time |  | 2024-10-18 | 2025-07-18 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB DURA BRIN | Land/Enviro Issue | Other | Access Issue
LC | 129292830 | A032/007A | T2 DI FLTN-CALISTOGA A032/007A RPR INSW | LAKEVLLE | ETL.6880.INSL.NCER | 2024-07-26 | 2024-07-18 | 2025-06-27 | On-Time |  | 2025-07-18 | 2025-07-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46401432 | T2 DI FLTN-CALISTOGA A032/007A RPR INSW | ICW
LC | 129292838 | 064/000B | T2 DI HUMBLDT-TRINITY 64/000B RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-07-26 | 2024-07-18 | 2025-04-19 | On-Time |  | 2024-10-18 | 2025-07-18 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46308612 | T2 DI HUMBLDT-TRINITY 64/000B RPR JUMW | ICW
LC | 129250356 | 011/259 | T2 WV SALINAS-LAURELES 11/259 INS DMPW | MOSSLNDG | ETL.7930.INSL.NCER | 2024-07-19 | 2024-07-19 | 2025-04-07 | On-Time |  | 2025-07-19 | 2025-07-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Damper-Wood | Replace | 46329996 | T2 WV SALINAS-LAURELES 11/259 INS DMPW | ICW
LC | 130775078 | 016/002 | T3 WV MONTE RIO-FORT ROSS 16/2 INS DAMW | LAKEVLLE | ETL.6979.INSL.NCER | 2025-01-19 | 2025-01-19 | 2025-06-18 | On-Time |  | 2025-07-19 | 2025-07-19 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | Missing | Damper-Wood | Install | 46459986 | T3 WV MONTE RIO-FORT ROSS 16/2 INS DAMW | ICW
LC | 130775243 | 17 | T3 WV BURNS-LONE STAR #2 A0/2 RPR SWTC | MOSSLNDG | ETL.6240.SWIT | 2025-01-20 | 2025-01-20 | 2025-03-08 | On-Time |  | 2025-07-20 | 2025-07-20 | 623 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO | Out of Adjustment | Switch | Repair | 46488657 | T3 WV BURNS-LONE STAR #2 A0/2 RPR SWTC | ICE
LC | 130776511 | 002/037 | T3 WV WST PNT-VLLY SPRNGS 2/37 RPR STRW | VICTOR | ETL.8350.POLE.WOOD | 2025-01-21 | 2025-01-21 | 2025-02-13 | On-Time |  | 2025-07-21 | 2025-07-21 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46460673 | T3 WV WST PNT-VLLY SPRNGS 2/37 RPR STRW | ICW
LC | 128071199 | 013/004 | T2 WV TRINITY-MAPLE CREEK 13/04 REFRAME | EUREKA | ETL.8170.POLE.WOOD | 2024-01-22 | 2024-01-22 | 2025-03-22 | On-Time |  | 2025-07-22 | 2025-07-22 | 637T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35568301 | T2 WV TRINITY-MAPLE CREEK 13/04 REFRAME | 93E
LC | 129262687 | 043/003 | T2 TRINITY-MAPLE CREEK 43/003 INS GYWW | EUREKA | ETL.8170.POLE.WOOD | 2024-07-22 | 2024-07-22 | 2024-07-22 | On-Time |  | 2025-07-22 | 2025-07-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Guy Wire-Wood | Install | 46283447 | T2 TRINITY-MAPLE CREEK 43/003 INS GYWW | ICW
LC | 129268701 | 000/011 | T2 WV LAURELES-OTTER 00/011 INS DMPW | MOSSLNDG | ETL.7380.INSL.NCER | 2024-07-22 | 2024-07-22 | 2025-03-23 | On-Time |  | 2025-07-22 | 2025-07-22 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46393876 | T2 WV LAURELES-OTTER 00/011 INS DMPW | ICW
LC | 129272117 | 011/374 | T2 SPLDING-SUMMIT 11/374 RPL INSS | SACTO | ETL.8060.INSL.NCER | 2024-07-22 | 2024-07-22 | 2024-07-22 | TBC |  | 2025-07-22 | 2025-07-22 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572876 | T2 SPAULDING-SUMMIT 11/374 RPL INS | 93I
LC | 129272201 | 012/422 | T2 SPAULDING-SUMMIT 12/422 INS JUMPER | SACTO | ETL.8060.POLE.WOOD | 2024-07-22 | 2024-07-22 | 2024-07-22 | TBC |  | 2025-07-22 | 2025-07-22 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572877 | T2 SPAULDING-SUMMIT 12/422 INS JUMPER | 93I
LC | 129276834 | 013/011 | T2 WV BRDGEVLLE-GRBERVLLE 13/11 INS DAMW | EUREKA | ETL.6220.INSL.NCER | 2024-07-23 | 2024-07-23 | 2024-07-23 | TBC |  | 2025-07-23 | 2025-07-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46403127 | T2 WV BRDGEVLLE-GRBERVLLE 13/11 INS DAMW | ICW
LC | 129277441 | 008/149 | T2 WV CARIBOU-WESTWOOD 008/149 RPL INSW | TABLEMTN | ETL.6300.INSL.CERA | 2024-07-23 | 2024-07-23 | 2025-03-10 | On-Time |  | 2025-07-23 | 2025-07-23 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35586825 | T2 WV CARIBOU-WESTWOOD 008/149 RPL INSW | 93I
LC | 129886537 | 010/076 | T2 VACA-VCVLLE-JMSN N TWR 10/76 RPR STRT | SACTO | ETL.4100.TOWR | 2024-12-02 | 2024-07-23 | 2024-07-23 | TBC |  | 2025-01-23 | 2025-07-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46504396 | T2 VACA-VCVL-JMSN 010/076 RPR STRT | ICQ
LC | 130785444 | 009/062 | T3 WV OLEUM-G #1 9/62 RPR FOND | CONCORD | ETL.3150.TOWR | 2025-01-23 | 2025-01-23 | 2025-05-21 | On-Time |  | 2025-07-23 | 2025-07-23 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46460546 | T3 WV OLEUM-G #1 9/62 RPR FOND | ICQ
LC | 129283753 | 012/242 | T2 WV CARIBOU-WESTWOOD 12/242 RPR GYWW | TABLEMTN | ETL.6300.POLE.WOOD | 2024-07-24 | 2024-07-24 | 2025-01-21 | On-Time |  | 2025-07-24 | 2025-07-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46337452 | T2 WV CARIBOU-WESTWOOD 12/242 RPR GYWW | ICW
LC | 129284173 | 014/336 | T2 WV DRM-GRS VLEY-WIMAR 14/336 RPR GYWW | SACTO | ETL.6760.POLE.WOOD | 2024-07-24 | 2024-07-24 | 2024-09-30 | On-Time |  | 2025-01-24 | 2025-07-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB DURA | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46323929 | T2 WV DRM-GRS VLEY-WIMAR 14/336 RPR GYWW | ICW
LC | 129301111 | 033/191 | T2 TEMBLOR-SAN LS OBISPO 33/191 RPL INSS | PISMOBCH | ETL.3960.INSL.CERA | 2024-07-29 | 2024-07-24 | 2025-01-30 | On-Time |  | 2025-07-24 | 2025-07-24 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW CREW COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35585152 | T2 DI TEMBLOR-SLO-TWR 50/284 RPL INSS | 93K
LC | 129347677 | 059/432 | T2 DI BRIDGEVILLE-CTTNWD 59/432 RPR STRT | TABLEMTN | ETL.1110.TOWR | 2024-08-07 | 2024-07-24 | 2024-07-24 | TBC |  | 2025-07-24 | 2025-07-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46337136 | T2 DI BRIDGEVILLE-CTTNWD 59/432 RPR STRT | ICQ
LC | 129993500 | 007/058 | T2 VACA-VCVLL-JMSN 7/058 RPR STRT | SACTO | ETL.4100.TOWR | 2024-12-13 | 2024-07-24 | 2025-01-13 | On-Time |  | 2025-07-24 | 2025-07-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46446332 | T2 VACA-VCVLL-JMSN 7/058 RPR STRT | ICQ
LC | 129288330 | 003/088 | T2 WV HMLTON BRNCH-CHESTER 3/88 RPL STRW | TABLEMTN | ETL.7000.POLE.WOOD | 2024-07-25 | 2024-07-25 | 2025-03-20 | On-Time |  | 2025-07-25 | 2025-07-25 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586829 | T2 WV HMLTON BRNCH-CHESTER 3/88 RPL STRW | 70Y
LC | 129290487 | 000/003 | T2 BRIDGEVILLE-GARBERVILLE 0/3 INS GYWW | EUREKA | ETL.6220.POLE.NWOD | 2024-07-25 | 2024-07-25 | 2024-07-25 | TBC |  | 2025-07-25 | 2025-07-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB | Missing | Guy Wire-Wood | Install | 46403128 | T2 WV BRDGEVLLE-GARBERVILLE 0/3 INS GYWW | ICW
LC | 129291229 | 017/002 | T2 PHILO JCT-ELK 017/002 RPL INSW | WILLITS | ETL.7780.INSL.NCER | 2024-07-25 | 2024-07-25 | 2025-04-26 | On-Time |  | 2025-07-25 | 2025-07-25 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR REMT REAR SWRK CLR ACCH COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35586949 | T2 PHILO JCT-ELK 017/002 RPL INSW | 93I
LC | 129291520 | 017/001 | T2 PHILO JCT-ELK 17/001 RPL INSW | WILLITS | ETL.7780.INSL.NCER | 2024-07-25 | 2024-07-25 | 2025-04-26 | On-Time |  | 2025-07-25 | 2025-07-25 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR REMT REAR SWRK CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35586948 | T2 PHILO JCT-ELK 17/001 RPL INSW | 93I
LC | 129356536 | 009/223 | T2 COTONWD-BENTON #1 9/223 RPL POLE | TABLEMTN | ETL.6640.POLE.WOOD | 2024-08-09 | 2024-07-25 | 2024-07-25 | TBC |  | 2025-07-25 | 2025-07-25 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586890 | T2 COTONWD-BENTON #1 9/223 RPL POLE | 70Y
LC | 129783357 | 008/062 | T2 VACA-VCVLL-JMSN 8/062 RPR STRT | SACTO | ETL.4100.TOWR | 2024-11-06 | 2024-07-25 | 2024-07-25 | TBC |  | 2025-07-25 | 2025-07-25 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416692 | T2 VACA-VCVLL-JMSN 8/062 RPR STRT | ICQ
LC | 128087310 | 044/860 | T2 HAT CREEK #1-WESTWOOD 044/860 GO95 | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-26 | 2024-01-26 | 2025-05-29 | On-Time |  | 2025-07-26 | 2025-07-26 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR SWRK ACCM COMP OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35526643 | T2 HAT CREEK #1-WESTWOOD 044/860 GO95 | 93G
LC | 130791688 | 012/006 | T3 WV MONTE RIO-FULTON 12/6 RPL POLE | LAKEVLLE | ETL.7630.POLE.WOOD | 2025-01-26 | 2025-01-26 | 2025-06-05 | On-Time |  | 2025-07-26 | 2025-07-26 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3 PRTO FRAB BRIN | Rotten | Structure-Wood | Replace | 35612022 | T3 WV MONTE RIO-FULTON 12/6 RPL POLE | 70Y
LC | 130797323 | 000/001C | T3 EI DIABLO-GATES #1 0/1C RPR FOND | PISMOBCH | ETL.5960.TOWR | 2025-01-28 | 2025-01-27 | 2025-01-27 | TBC |  | 2025-07-27 | 2025-07-27 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46459731 | T3 EI DIABLO-GATES #1 0/1C RPR FOND | ICQ
LC | 130797176 | 000/004 | T3 DIABLO-GATES #1 0/4 RPR FOND | PISMOBCH | ETL.5960.TOWR | 2025-01-28 | 2025-01-28 | 2025-01-28 | TBC |  | 2025-07-28 | 2025-07-28 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 PRTO CLMB FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46459732 | T3 EI DIABLO-GATES #1 0/4 RPR FOND | ICQ
LC | 130798084 | 000/005 | T3 DIABLO-GATES #1 000/005 RPR STRT | PISMOBCH | ETL.5960.TOWR | 2025-01-28 | 2025-01-28 | 2025-01-28 | TBC |  | 2025-07-28 | 2025-07-28 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 PRTO CLMB FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472266 | T3 EI DIABLO-GATES #1 000/005 RPR STRT | ICQ
LC | 130798427 | 000/006 | T3 EI DIABLO-GATES #1 0/6 RPR GYWT | PISMOBCH | ETL.5960.TOWR | 2025-01-28 | 2025-01-28 | 2025-05-09 | On-Time |  | 2025-07-28 | 2025-07-28 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO CLMB FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46472293 | T3 EI DIABLO-GATES #1 0/6 RPR GYWT | ICQ
LC | 130798891 | 001/007 | T3 DIABLO-GATES #1 1/7 RPR FOND | PISMOBCH | ETL.5960.TOWR | 2025-01-28 | 2025-01-28 | 2025-01-28 | TBC |  | 2025-07-28 | 2025-07-28 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 PRTO CLMB FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46460460 | T3 DIABLO-GATES #1 1/7 RPR FOND | ICQ
LC | 124269788 | 020/082 | T2NT DI DIABLO-MIDWAY #2 20/82 RPR INSS | PISMOBCH | ETL.5970.INSL.NCER | 2022-08-10 | 2022-07-29 | 2023-11-20 | On-Time |  | 2025-07-29 | 2025-07-29 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 45670550 | T2 DI DIABLO-MIDWAY #2 20/82 RPR INSS | ICS
LC | 128097373 | 016/320 | T2 HAT CREEK #1-WSTWD 16/320 GO95 | TABLEMTN | ETL.7030.POLE.WOOD | 2024-01-29 | 2024-01-29 | 2025-05-02 | On-Time |  | 2025-07-29 | 2025-07-29 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35528627 | T2 HAT CREEK #1-WSTWD 16/320 GO95 | 93G
LC | 128142664 | 037/728 | T2 HAT CREEK #1 37/728 GO95 RPL | TABLEMTN | ETL.7030.POLE.WOOD | 2024-02-07 | 2024-01-29 | 2025-05-27 | On-Time |  | 2025-07-29 | 2025-07-29 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35529923 | T2 HAT CREEK #1 37/728 GO95 RPL | 93G
LC | 128142665 | 023/442 | T2 HAT CREEK #1 23/442 GO95 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-02-07 | 2024-01-29 | 2025-06-15 | On-Time |  | 2025-07-29 | 2025-07-29 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35529925 | T2 HAT CREEK #1 23/442 GO95 RPL STRW | 93G
LC | 128142667 | 023/451 | T2 HAT CREEK #1 23/451 GO95 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-02-07 | 2024-01-29 | 2025-06-16 | On-Time |  | 2025-07-29 | 2025-07-29 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35529926 | T2 HAT CREEK #1 23/451 GO95 RPL STRW | 93G
LC | 128142668 | 024/477 | T2 HAT CREEK #1 24/477 GO95 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-02-07 | 2024-01-29 | 2025-06-17 | On-Time |  | 2025-07-29 | 2025-07-29 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35529927 | T2 HAT CREEK #1 24/477 GO95 RPL STRW | 93G
LC | 128142669 | 025/479 | T2 HAT CREEK #1 25/479 GO95 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-02-07 | 2024-01-29 | 2025-06-17 | On-Time |  | 2025-07-29 | 2025-07-29 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35529928 | T2 HAT CREEK #1 25/479 GO95 RPL STRW | 93G
LC | 129303823 | 008/062 | T2 MORAGA-SN LEANDRO #2 8/62 GO95 CLEAR | CONCORD | ETL.2780.INSL | 2024-07-29 | 2024-07-29 | 2024-10-31 | On-Time |  | 2025-07-29 | 2025-07-29 | 400 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH TR2 PRTO NTDE | Clearance | GO95 Clear Infract-Tower | To Be Corrected | 35523645 | T3 MRAGA-SN LEANDRO #2 6/44 GO95 CLEAR | 93T
LC | 129510704 | :021/111 | T2 DI CHC-SLNS-SOLEDAD :21/111 RPL RPTS | MOSSLNDG | ETL.2900.TOWR | 2024-09-10 | 2024-07-29 | 2025-04-21 | On-Time |  | 2025-07-29 | 2025-07-29 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46393861 | T2 DI CHC-SLNS-SOLEDAD :21/111 RPL RPTS | ICB
LC | 130802539 | 004/010 | T3 EI BRDGVLLE-GRBRVLLE 4/10 RPR GYWW | EUREKA | ETL.6220.POLE.NWOD | 2025-01-29 | 2025-01-29 | 2025-01-29 | TBC |  | 2025-07-29 | 2025-07-29 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46477333 | T3 EI BRDGVLLE-GRBRVLLE 4/10 RPR GYWW | ICW
LC | 130804391 | 014/109 | T3 MONTA VISTA-BURNS 14/109 RPL STRW | MOSSLNDG | ETL.7590.POLE.WOOD | 2025-01-29 | 2025-01-29 | 2025-01-29 | TBC |  | 2025-07-29 | 2025-07-29 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35617266 | T3 WV MONTA VISTA-BURNS 14/109 RPL STRW | 70Y
LC | 130804568 | 006/002 | T3 BRDGVL-GRBRVL 6/2 RPL CRSW | EUREKA | ETL.6220.POLE.WOOD | 2025-01-29 | 2025-01-29 | 2025-01-29 | TBC |  | 2025-07-29 | 2025-07-29 | 637T | TR3 |  | E - Schd Compl Yr 0 | Open | REGW OTHR OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35526864 | T3 DI BRIDGEVILL-GRBR 6/2 RPL POLE | 70Y
LC | 128103325 | 003/020 | T2 SOBRNTE-STNDRD O SW STA 3/20 RPL INSS | CONCORD | ETL.3800.INSL | 2024-01-30 | 2024-01-30 | 2025-04-29 | On-Time |  | 2025-07-30 | 2025-07-30 | 532 | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574948 | T0 DI SBRT-STD OIL SS#1 RPL INSS IN 9 T | 93K
LC | 129308433 | 042/824 | T2 HT CREEK #1-WSTWD 42/824 RPL STRW | TABLEMTN | ETL.7030.POLE.WOOD | 2024-07-30 | 2024-07-30 | 2025-05-30 | On-Time |  | 2025-07-30 | 2025-07-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586916 | T2 WV HT CREEK #1-WSTWD 42/824 RPL STRW | 70Y
LC | 129309036 | 001/016 | T2 EI TRINITY-MAPLE CREEK 1/16 RMV VEG | EUREKA | ETL.8170.POLE.WOOD | 2024-07-30 | 2024-07-30 | 2024-07-30 | TBC |  | 2025-07-30 | 2025-07-30 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 129311112 | 057/004 | T2 EI COTTONWD-HUMBOLDT#1 57/4 RPR JUMW | EUREKA | ETL.1820.INSL.NCER | 2024-07-30 | 2024-07-30 | 2025-04-09 | On-Time |  | 2025-01-30 | 2025-07-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46308613 | T2 EI COTTONWD-HUMBOLDT#1 57/4 RPR JUMW | ICW
LC | 130808324 | 005/005 | T3 EI BRDGVL-GRBRVL 5/5 RPR CRSW | EUREKA | ETL.6220.POLE.WOOD | 2025-01-30 | 2025-01-30 | 2025-01-30 | TBC |  | 2025-07-30 | 2025-07-30 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46477334 | T3 EI BRDGVL-GRBRVL 5/5 RPR CRSW | ICW
LC | 128171407 | 035/007 | T2 FORT ROSS-GUALALA 35/07 GO95 CLEAR | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-02-14 | 2024-02-14 | 2024-02-14 | TBC |  | 2025-07-31 | 2025-07-31 | 401 | TR2 | YES | E - Schd Compl Yr 0 | Open | REGW OTHR CLR USA OH FMOB XMPT TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 31653342 | T2 FORT ROSS-GUALALA 035/008 GO95 CLEAR | 93G
LC | 128171578 | 035/005 | T2 FORT ROSS-GUALALA 35/5 GO95 CLEAR | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-02-14 | 2024-02-14 | 2024-02-14 | TBC |  | 2025-07-31 | 2025-07-31 | 401 | TR2 | YES | E - Schd Compl Yr 0 | Open | REGW OTHR CLR USA OH FMOB XMPT TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 31654781 | T2 FORT ROSS-GUALALA 35/006 GO95 | 93G
LC | 129313816 | 014/335 | T2 WV DRUM-GRSS VLY-WMR 14/335 INS DAMW | SACTO | ETL.6760.INSL.NCER | 2024-07-31 | 2024-07-31 | 2024-12-10 | On-Time |  | 2025-07-31 | 2025-07-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46340505 | T2 WV DRUM-GRSS VLY-WMR 14/335 INS DAMW | ICW
LC | 129316191 | 004/002 | T2NT DI MLNS-CRTS 004/002R GO95 CLEAR | VICTOR | ETL.2390.POLE.WDPS | 2024-07-31 | 2024-07-31 | 2024-07-31 | TBC |  | 2027-07-31 | 2025-07-31 | 401 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW OTHR OH FMOB TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35522263 | T2 DI MLNS-CRTS 004/002 MITIGATION | 93G
LC | 129316996 | 009/045 | T2 SILVERADO-FULTON 9/45 GRND WASH | LAKEVLLE | ETL.1610.INSL.NCER | 2024-07-31 | 2024-07-31 | 2024-07-31 | TBC |  | 2025-01-31 | 2025-07-31 | 622 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB DURA BRIN | Contaminated | Insulator | Ground Wash | 46401525 | T2 DI SILVERADO-FULTON 9/45 GRND WASH | ICD
LC | 129316997 | 009/045 | T2 FULTON-PUEBLO 9/45 GRND WASH | LAKEVLLE | ETL.1600.INSL.NCER | 2024-07-31 | 2024-07-31 | 2024-07-31 | TBC |  | 2025-01-31 | 2025-07-31 | 622 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB DURA BRIN | Contaminated | Insulator | Ground Wash | 46542257 | T2 DI FULTON-PUEBLO 9/45 GRND WASH | ICD
LC | 129325151 | 029/008 | T2 DI FRT RSS-GUALALA 29/008 RPR GYWW | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-08-02 | 2024-07-31 | 2024-07-31 | TBC |  | 2025-07-31 | 2025-07-31 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46401431 | T2 DI FRT RSS-GUALALA 29/008 RPR GYWW | ICW
LC | 129320500 | 002/036 | T2 SMARTVILLE-NICOLAUS #1 2/36 RPL PL | SACTO | ETL.7990.POLE.WOOD | 2024-08-01 | 2024-08-01 | 2025-05-27 | On-Time |  | 2025-08-01 | 2025-08-01 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW TNT COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35586952 | T2 SMARTVILLE-NICOLAUS #1 2/36 RPL PL | 70Y
LC | 129321638 | 000/011 | T2 JEFFERSON-STANFORD 00/011 COMPLETE | METCALF | ETL.7220.INSL.CERA | 2024-08-01 | 2024-08-01 | 2025-03-30 | On-Time |  | 2025-08-01 | 2025-08-01 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH FMOB TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35587535 | T2 JEFFERSON-STANFORD 00/011 RPL INSW | 93I
LC | 129342227 | 014/005 | T2 COALINGA #1-SAN MIGUEL 14/5 RPL HNGR | FRESNO | ETL.8580.INSL.CERA | 2024-08-07 | 2024-08-01 | 2024-10-16 | On-Time |  | 2025-08-01 | 2025-08-01 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46340184 | T2 COALINGA #1-SAN MIGUEL 14/5 RPL HNGR | ICQ
LC | 129342264 | 014/005 | T2 COALINGA #1-SAN MIGUEL 14/5 RPL INSS | PISMOBCH | ETL.8580.INSL.CERA | 2024-08-07 | 2024-08-01 | 2025-04-28 | On-Time |  | 2025-08-01 | 2025-08-01 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Replace | 35596442 | T2 COALINGA #1-SAN MIGUEL 14/5 RPL INSS | 93K
LC | 129342486 | 009/115A | T2 WATSONVILLE-SALINAS 9/115A G095 CLEAR | MOSSLNDG | ETL.8310.POLE.WOOD | 2024-08-07 | 2024-08-01 | 2025-06-20 | On-Time |  | 2025-08-01 | 2025-08-01 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35608148 | T2 WATSONVILLE-SALINAS 9/115A G095 CLEAR | 93G
LC | 129342644 | 009/115B | T2 WATSONVILLE-SALINAS 9/115B GO95 | MOSSLNDG | ETL.8310.POLE.WOOD | 2024-08-07 | 2024-08-01 | 2025-06-20 | On-Time |  | 2025-08-01 | 2025-08-01 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35608148 | T2 WATSONVILLE-SALINAS 9/115A G095 CLEAR | 93G
LC | 129342648 | 009/115C | T2 WATSONVILLE-SALINAS 9/115C GO95 | MOSSLNDG | ETL.8310.POLE.WOOD | 2024-08-07 | 2024-08-01 | 2025-06-20 | On-Time |  | 2025-08-01 | 2025-08-01 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35608148 | T2 WATSONVILLE-SALINAS 9/115A G095 CLEAR | 93G
LC | 130814072 | 003/013 | T3 EI BRDGVLLE-GARBERVILLE 3/13 RPL HRDW | EUREKA | ETL.6220.POLE.WOOD | 2025-02-03 | 2025-02-03 | 2025-02-03 | TBC |  | 2025-08-03 | 2025-08-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace | 46477336 | T3 EI BRDGVLLE-GARBERVILLE 3/13 RPL HRDW | ICW
LC | 130814568 | 007/008 | T3 WV MNDCNO-WLTS-FRT BRG 07/08 RPL STRW | WILLITS | ETL.7550.POLE.WOOD | 2025-02-03 | 2025-02-03 | 2025-04-03 | On-Time |  | 2025-08-03 | 2025-08-03 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35617198 | T3 WV MNDCNO-WLTS-FRT BRG 07/08 RPL STRW | 70Y
LC | 130816664 | ?001/012 | T3 WV SNTH LNE-HLF MN BY ?1/12 INS DMPW | METCALF | ETL.7212.POLE.NWOD | 2025-02-03 | 2025-02-03 | 2025-03-30 | On-Time |  | 2025-08-03 | 2025-08-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | Missing | Damper-Wood | Install | 46477432 | T3 WV SNTH LNE-HLF MN BY ?1/12 INS DMPW | ICW
LC | 130821697 | 018/009 | T3 EI MI-WUK-CURTIS 18/09L RPL STRW | VICTOR | ETL.1073.POLE.WDPS | 2025-02-04 | 2025-02-04 | 2025-02-04 | TBC |  | 2025-08-04 | 2025-08-04 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP RESD SWRK CLR ACCH USA OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35616391 | T3 EI MI-WUK-CURTIS 18/09L RPL STRW | 70Y
LC | 130821756 | 018/009 | T3 MI-WUK-CURTIS 18/09R RPL STRW | VICTOR | ETL.1073.POLE.WDPS | 2025-02-04 | 2025-02-04 | 2025-02-04 | TBC |  | 2025-08-04 | 2025-08-04 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35616391 | T3 EI MI-WUK-CURTIS 18/09L RPL STRW | 70Y
LC | 130823498 | 003/035A | T3 WV SLY CREEK TAP 003/035A INS DMPW | TABLEMTN | ETL.4221.INSL.NCER | 2025-02-04 | 2025-02-04 | 2025-02-04 | TBC |  | 2025-08-04 | 2025-08-04 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR3 PRTO FRAB NTDE BRIN | Missing | Damper-Wood | Install | 46494186 | T3 WV SLY CREEK TAP 003/035A INS DMPW | ICW
LC | 130823600 | 001/008A | T3 WV SLY CREEK TAP 001/008A INS DMPW | TABLEMTN | ETL.4221.INSL.NCER | 2025-02-04 | 2025-02-04 | 2025-02-04 | TBC |  | 2025-08-04 | 2025-08-04 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR3 PRTO NTDE BRIN | Missing | Damper-Wood | Install | 46494185 | T3 WV SLY CREEK TAP 001/008A INS DMPW | ICW
LC | 129406486 | 032/002 | T2 GRBRVLE LAYTONVLE 32/2 RPL POLE | WILLITS | ETL.8365.POLE.WOOD | 2024-08-19 | 2024-08-05 | 2025-06-24 | On-Time |  | 2025-08-05 | 2025-08-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586911 | T2 GRBRVLE LAYTONVLE 32/2 RPL POLE | 70Y
LC | 130825805 | ?010/007 | T3 EI SNTH LNE-HLF MN BY ?10/7 CGI | METCALF | ETL.7212.POLE.NWOD | 2025-02-05 | 2025-02-05 | 2025-05-22 | On-Time |  | 2025-05-05 | 2025-08-05 | 625 | TR3 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | Vegetation Overgrown | Other | Access Issue
LC | 130825887 | 001/041 | T3 WV DEER CREEK-DRUM 001/041 REFRAME | SACTO | ETL.6690.POLE.WOOD | 2025-02-05 | 2025-02-05 | 2025-02-05 | TBC |  | 2025-08-05 | 2025-08-05 | 637T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35617199 | T3 WV DEER CREEK-DRUM 001/041 REFRAME | 93E
LC | 130826379 | 008/216 | T3 EI COLGATE-ALLEGHANY 8/216 INS DMPW | SACTO | ETL.6470.INSL.NCER | 2025-02-05 | 2025-02-05 | 2025-05-13 | On-Time |  | 2025-08-05 | 2025-08-05 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | Missing | Damper-Wood | Install | 46477091 | T3 EI COLGATE-ALLEGHANY 8/216 INS DMPW | ICW
LC | 130827282 | 020/140 | T3 WV METCLF-GRN VALY 20/140 INS DMPW | MOSSLNDG | ETL.2540.INSL.NCER | 2025-02-05 | 2025-02-05 | 2025-06-09 | On-Time |  | 2025-08-05 | 2025-08-05 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | Missing | Damper-Wood | Install | 46488658 | T3 WV METCLF-GRN VALY 20/140 INS DMPW | ICW
LC | 128134787 | 047/006 | T2 TRINITY-MAPLE CRK 47/6 GO95 RPL STRW | EUREKA | ETL.8170.POLE.WOOD | 2024-02-06 | 2024-02-06 | 2025-06-17 | On-Time |  | 2025-08-06 | 2025-08-06 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE ACCM COMP OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35529366 | T2 TRINITY-MAPLE CRK 47/6 GO95 RPL STRW | 93G
LC | 128135774 | 027/004A | T2 MONTE RIO-FRT RSS 27/4A GO95 | LAKEVLLE | ETL.6979.POLE.WOOD | 2024-02-06 | 2024-02-06 | 2025-05-22 | On-Time |  | 2025-08-06 | 2025-08-06 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW OTHR FIRE SPCR ACCL COMP OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35521357 | T2 EI MONTE RIO-FORT ROSS 27/4B RPL POLE | 93G
LC | 129335061 | 034/006 | T2 TRINITY-MAPLE CREEK 34/6 RPL STRW | EUREKA | ETL.8170.POLE.WOOD | 2024-08-06 | 2024-08-06 | 2024-08-06 | TBC |  | 2025-08-06 | 2025-08-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586955 | T2 TRINITY-MAPLE CREEK 34/6 RPL STRW | 70Y
LC | 129340099 | 000/009 | T2 TOCALOMA TAP 00/09 RPR ROAD | LAKEVLLE | ETL.7721.POLE.NWOD | 2024-08-06 | 2024-08-06 | 2024-08-09 | On-Time |  | 2025-08-06 | 2025-08-06 | 932 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2 FRAB ETRI | No Good/Out of Stdrd | Road | Repair | 46298218 | T2 TOCALOMA TAP 00/09 RPR ROAD | CHS
LC | 129341977 | 016/069 | T2 TESLA-METCALF 16/69 RPR SHLS | METCALF | ETL.6110.TOWR | 2024-08-07 | 2024-08-06 | 2025-03-21 | On-Time |  | 2025-08-06 | 2025-08-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46333531 | T2 TESLA-METCALF 16/69 RPR SHLS | ICS
LC | 129341993 | 008/034 | T2 TESLA-METCALF 8/34 RPR SHLD | CONCORD | ETL.6110.TOWR | 2024-08-07 | 2024-08-06 | 2025-02-20 | On-Time |  | 2025-08-06 | 2025-08-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46345732 | T2 TESLA-METCALF 8/34 RPR SHLS | ICS
LC | 129713324 | 003/014 | T2 MORRO BAY-MESA 03/14 RMV VEG | PISMOBCH | ETL.5290.TOWR | 2024-10-22 | 2024-08-06 | 2024-08-06 | TBC |  | 2025-08-06 | 2025-08-06 | 564 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW CREW OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation-Tower | Cage Clearing
LC | 130828944 | 007/150 | T3 EI VOLTA-DESCHUTES 007/150 RPL STRW | TABLEMTN | ETL.8290.POLE.WOOD | 2025-02-06 | 2025-02-06 | 2025-02-06 | TBC |  | 2025-08-06 | 2025-08-06 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35617481 | T3 EI VOLTA-DESCHUTES 007/150 RPL STRW | 70Y
LC | 130829096 | 007/151 | T3 EI VOLTA-DESCHUTES 007/151 RPL STRW | TABLEMTN | ETL.8290.POLE.WOOD | 2025-02-06 | 2025-02-06 | 2025-02-06 | TBC |  | 2025-08-06 | 2025-08-06 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35617483 | T3 EI VOLTA-DESCHUTES 007/151 RPL STRW | 70Y
LC | 130830101 | 007/064 | T3 MNTA VSTA-BRNS 7/64L RPR SPLW | MOSSLNDG | ETL.7590.INSL.NCER | 2025-02-06 | 2025-02-06 | 2025-05-13 | On-Time |  | 2025-08-06 | 2025-08-06 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Splice-Wood | Repair | 46478353 | T3 MNTA VSTA-BRNS 7/64L RPR SPLW | ICW
LC | 129347240 | 004/013 | T2 VLLY SPRNGS-CLVRS CMNT 04/13 GO95 RPL | VICTOR | ETL.8220.POLE.WOOD | 2024-08-07 | 2024-08-07 | 2025-03-08 | On-Time |  | 2025-08-07 | 2025-08-07 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35571930 | T2 VLLY SPRNGS-CLVRS CMNT 04/13 GO95 RPL | 93G
LC | 129351371 | 006/092 | T2 VALLEY SPRINGS-CLAY 6/92 RMV NEST | VICTOR | ETL.8264.POLE.WOOD | 2024-08-08 | 2024-08-07 | 2024-09-17 | On-Time |  | 2024-11-07 | 2025-08-07 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH TR2 PRTO FRAB DURA BRIN | Debris/Nest/etc. | Structure-Wood | Remove | 46308843 | T2 VALLEY SPRINGS-CLAY 6/92 RMV NEST | ICW
LC | 129351590 | 006/092 | T2 VALLEY SPRINGS-CLAY 6/92 RPL POLE | VICTOR | ETL.8264.POLE.WOOD | 2024-08-08 | 2024-08-07 | 2024-11-05 | On-Time |  | 2025-08-07 | 2025-08-07 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35580041 | T2 VALLEY SPRINGS-CLAY 6/92 RPL POLE | 70Y
LC | 130832511 | 006/004 | T3 WV BRDGVL-GRBRVL 6/4 RPR SPLW | EUREKA | ETL.6220.INSL.CERA | 2025-02-07 | 2025-02-07 | 2025-02-07 | TBC |  | 2025-08-07 | 2025-08-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR3 PRTO NTDE BRIN | No Good/Out of Stdrd | Splice-Wood | Repair | 46477337 | T3 WV BRDGVL-GRBRVL 6/4 RPR SPLW | ICW
LC | 130833021 | 000/001A | T3 DIABLO PP STANDBY SPPLY 0/1A RPR ADSS | PISMOBCH | ETL.4610.POLE.NWOD | 2025-02-07 | 2025-02-07 | 2025-03-29 | On-Time |  | 2025-05-07 | 2025-08-07 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCM COMP OH FMOB TR3 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Steel | Repair | 46488759 | T3 DIABLO PP STANDBY SPPLY 0/1A RPR ADSS | ICS
LC | 130833210 | 000/001 | T3 WV KESWICK-TRINITY 00/01 INS HRDW | TABLEMTN | ETL.7270.POLE.WOOD | 2025-02-07 | 2025-02-07 | 2025-04-23 | On-Time |  | 2025-08-07 | 2025-08-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | Missing | Hardware-Wood | Install | 46507929 | T3 WV KESWICK-TRINITY 00/01 INS HRDW | ICW
LC | 130833719 | 013/118B | T3 EI CTTNWD-BNTN #2 013/118B-L RPR ANCW | TABLEMTN | ETL.6650.POLE.WDPS | 2025-02-07 | 2025-02-07 | 2025-02-07 | TBC |  | 2025-08-07 | 2025-08-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46489533 | T3 EI CTTNWD-BNTN #2 013/118B-L RPR ANCW | ICW
LC | 130835295 | 017/161 | T3 WV MONTA VISTA-BURNS 17/161 RPL INSW | MOSSLNDG | ETL.7590.INSL.NCER | 2025-02-09 | 2025-02-09 | 2025-02-09 | TBC |  | 2025-08-09 | 2025-08-09 | 508T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35619248 | T3 WV MONTA VISTA-BURNS 17/161 RPL INSW | 93I
LC | 130845421 | 018/006 | T3 MI-WUK-CURTIS 18/6R RPR GYWW | VICTOR | ETL.1073.POLE.STPS | 2025-02-10 | 2025-02-10 | 2025-03-12 | On-Time |  | 2025-08-10 | 2025-08-10 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46485190 | T3 MI-WUK-CURTIS 18/6R RPR GYWW | ICW
LC | 130848342 | 017/081 | T3 DI MOSS LNDING METCALF 17/81 RPR SHLS | MOSSLNDG | ETL.6050.TOWR | 2025-02-10 | 2025-02-10 | 2025-04-25 | On-Time |  | 2025-08-10 | 2025-08-10 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46472302 | T3 DI MOSS LNDING METCALF 17/81 RPR SHLS | ICS
LC | 130848375 | 016/076 | T3 DI MOSS LANDING-METCALF 16/76 TOUCH | MOSSLNDG | ETL.6050.TOWR | 2025-02-10 | 2025-02-10 | 2025-02-10 | TBC |  | 2025-08-10 | 2025-08-10 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW ACCM OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46472262 | T3 DI MOSS LANDING-METCALF 16/76 TOUCH | ICQ
LC | 130851605 | 014/067 | T3 DI MOSS LANDING-METCALF 14/67 TOUCH | MOSSLNDG | ETL.6050.TOWR | 2025-02-11 | 2025-02-10 | 2025-02-10 | TBC |  | 2025-08-10 | 2025-08-10 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46525766 | T3 DI MOSS LANDING-METCALF 14/67 TOUCH | ICQ
LC | 130856079 | 018/082 | T3 DI MOSS LANDING-METCALF-18/82 TOUCH | MOSSLNDG | ETL.6050.TOWR | 2025-02-12 | 2025-02-10 | 2025-04-28 | On-Time |  | 2025-05-10 | 2025-08-10 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46474267 | T3 DI MOSS LANDING-METCALF-18/82 TOUCH | ICQ
LC | 130851461 | 004/057B | T3 EI DRUM-SUMMIT#2 4/57L RPR JUMPW | SACTO | ETL.1450.INSL.NCER | 2025-02-11 | 2025-02-11 | 2025-06-20 | On-Time |  | 2025-08-11 | 2025-08-11 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46484973 | T3 EI DRUM-SUMMIT#2 4/57L RPR JUMPW | ICW
LC | 130871728 | ?009/000 | T3 SNEATH LNE-HLF MN BY ?9/0R RMV VEG | METCALF | ETL.7212.POLE.WDPS | 2025-02-19 | 2025-02-11 | 2025-06-25 | On-Time |  | 2025-08-11 | 2025-08-11 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH FMOB TR3 PRTO BRIN ETRI | Overgrown | Vegetation | Remove
LC | 130871760 | ?008/008 | T3 EI SNEATH LNE-HLF MN BY ?8/8R RMV VEG | METCALF | ETL.7212.POLE.WDPS | 2025-02-19 | 2025-02-11 | 2025-03-18 | On-Time |  | 2025-08-11 | 2025-08-11 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW INSP CNCL OH FMOB TR3 PRTO FRAB BRIN ETRI | Overgrown | Vegetation | Remove
LC | 130871761 | ?008/005 | T3 EI SNEATH LNE-HLF MN BY ?8/5L RMV VEG | METCALF | ETL.7212.POLE.WDPS | 2025-02-19 | 2025-02-11 | 2025-03-07 | On-Time |  | 2025-08-11 | 2025-08-11 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW INSP CNCL OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Remove
LC | 130921221 | ?009/009 | T3 SNEATH LANE-HALF MN BY ?9/9 RMV BRSH | METCALF | ETL.7212.POLE.WOOD | 2025-03-03 | 2025-02-11 | 2025-03-18 | On-Time |  | 2025-08-11 | 2025-08-11 | 932 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR3 PRTO FRAB BRIN | Brush Fuel | Road | Remove | 44306463 | SNEATH LANE-HMB :001/010 FIX ROAD | CHS
LC | 130921222 | ?009/008 | T3 SNEATH LANE-HALF MN BY ?9/8 RMV BRSH | METCALF | ETL.7212.POLE.WOOD | 2025-03-03 | 2025-02-11 | 2025-03-18 | On-Time |  | 2025-08-11 | 2025-08-11 | 932 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR3 PRTO FRAB BRIN | Brush Fuel | Road | Remove | 44306463 | SNEATH LANE-HMB :001/010 FIX ROAD | CHS
LC | 130921224 | ?009/007 | T3 SNEATH LANE-HALF MN BY ?9/7 RMV BRSH | METCALF | ETL.7212.POLE.WOOD | 2025-03-03 | 2025-02-11 | 2025-03-18 | On-Time |  | 2025-08-11 | 2025-08-11 | 932 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR3 PRTO FRAB BRIN | Brush Fuel | Road | Remove | 44306463 | SNEATH LANE-HMB :001/010 FIX ROAD | CHS
LC | 130921225 | ?009/004 | T3 SNEATH LANE-HALF MN BY ?9/4 RMV BRSH | METCALF | ETL.7212.POLE.WOOD | 2025-03-03 | 2025-02-11 | 2025-03-19 | On-Time |  | 2025-08-11 | 2025-08-11 | 932 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR3 PRTO FRAB BRIN | Brush Fuel | Road | Remove | 44306463 | SNEATH LANE-HMB :001/010 FIX ROAD | CHS
LC | 130921226 | ?009/001 | T3 SNEATH LANE-HALF MN BY ?9/1 RMV BRSH | METCALF | ETL.7212.POLE.NWOD | 2025-03-03 | 2025-02-11 | 2025-03-19 | On-Time |  | 2025-08-11 | 2025-08-11 | 932 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR3 PRTO FRAB BRIN | Brush Fuel | Road | Remove | 44306463 | SNEATH LANE-HMB :001/010 FIX ROAD | CHS
LC | 130921228 | ?008/004B | T3 SNEATH LANE-HLF MN BY ?8/4B RMV BRSH | METCALF | ETL.7212.POLE.NWOD | 2025-03-03 | 2025-02-11 | 2025-03-24 | On-Time |  | 2025-08-11 | 2025-08-11 | 932 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR3 PRTO FRAB BRIN | Brush Fuel | Road | Remove | 44306463 | SNEATH LANE-HMB :001/010 FIX ROAD | CHS
LC | 130921229 | ?008/003 | T3 SNEATH LANE-HALF MN BY ?8/3 RMV BRSH | METCALF | ETL.7212.POLE.WOOD | 2025-03-03 | 2025-02-11 | 2025-03-24 | On-Time |  | 2025-08-11 | 2025-08-11 | 932 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH FMOB TR3 PRTO FRAB BRIN ETRI | Brush Fuel | Road | Remove | 44306463 | SNEATH LANE-HMB :001/010 FIX ROAD | CHS
LC | 130921305 | ?008/002 | T3 SNEATH LANE-HALF MN BY ?8/2 RMV BRSH | METCALF | ETL.7212.POLE.WOOD | 2025-03-03 | 2025-02-11 | 2025-03-24 | On-Time |  | 2025-08-11 | 2025-08-11 | 932 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH FMOB TR3 PRTO FRAB BRIN ETRI | Brush Fuel | Road | Remove | 44306463 | SNEATH LANE-HMB :001/010 FIX ROAD | CHS
LC | 130921352 | ?008/000 | T3 SNEATH LANE-HALF MN BY ?8/0 RMV BRSH | METCALF | ETL.7212.POLE.WOOD | 2025-03-03 | 2025-02-11 | 2025-03-25 | On-Time |  | 2025-08-11 | 2025-08-11 | 932 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH FMOB TR3 PRTO FRAB BRIN ETRI | Brush Fuel | Road | Remove | 44306463 | SNEATH LANE-HMB :001/010 FIX ROAD | CHS
LC | 130921358 | ?007/009 | T3 SNEATH LANE-HALF MN BY ?7/9 RMV BRSH | METCALF | ETL.7212.POLE.NWOD | 2025-03-03 | 2025-02-11 | 2025-03-28 | On-Time |  | 2025-08-11 | 2025-08-11 | 932 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW COMP OH FMOB TR3 PRTO FRAB BRIN ETRI | Brush Fuel | Road | Remove | 44306463 | SNEATH LANE-HMB :001/010 FIX ROAD | CHS
LC | 130921370 | ?007/008 | T3 SNEATH LANE-HALF MN BY ?7/8 RMV BRSH | METCALF | ETL.7212.POLE.NWOD | 2025-03-03 | 2025-02-11 | 2025-04-02 | On-Time |  | 2025-08-11 | 2025-08-11 | 932 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR3 PRTO FRAB BRIN | Brush Fuel | Road | Remove | 44306463 | SNEATH LANE-HMB :001/010 FIX ROAD | CHS
LC | 130921371 | ?007/006 | T3 SNTH LANE-HLF MN BAY ?7/6 RMV BRSH | METCALF | ETL.7212.POLE.NWOD | 2025-03-03 | 2025-02-11 | 2025-03-17 | On-Time |  | 2025-08-11 | 2025-08-11 | 932 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR3 PRTO FRAB BRIN | Brush Fuel | Road | Remove | 44306463 | SNEATH LANE-HMB :001/010 FIX ROAD | CHS
LC | 130921377 | ?001/008 | T3 SNEATH LANE-HALF MN BY ?1/8 RMV BRSH | METCALF | ETL.7212.POLE.WOOD | 2025-03-03 | 2025-02-12 | 2025-05-28 | On-Time |  | 2025-08-12 | 2025-08-12 | 932 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB TR3 PRTO FRAB BRIN | Brush Fuel | Road | Remove | 44306463 | SNEATH LANE-HMB :001/010 FIX ROAD | CHS
LC | 129380144 | 009/044 | T2 SN LUIS OBISPO-SNT MRIA 9/44 RPL INSS | PISMOBCH | ETL.3540.INSL.CERA | 2024-08-13 | 2024-08-13 | 2025-05-31 | On-Time |  | 2025-08-13 | 2025-08-13 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574155 | T2 SN LUIS OBISPO-SNT MRIA 9/43 RPL INSS | 93K
LC | 129380674 | 009/043 | T2 SN LUIS OBISPO-SNT MRIA 9/43 RPL INSS | PISMOBCH | ETL.3540.INSL.CERA | 2024-08-13 | 2024-08-13 | 2025-05-27 | On-Time |  | 2025-08-13 | 2025-08-13 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574155 | T2 SN LUIS OBISPO-SNT MRIA 9/43 RPL INSS | 93K
LC | 129421821 | 047/010 | T2 TRNTY-MPL CRK 47/10 RPL ANCW | EUREKA | ETL.8170.POLE.WOOD | 2024-08-22 | 2024-08-13 | 2024-08-13 | TBC |  | 2025-08-13 | 2025-08-13 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP FIRE ACCH COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586956 | T2 EI TRNTY-MPL CRK 47/10 RPL ANCW | 93E
LC | 130859044 | 003/079 | T3 EI VOLTA-DESCHUTES 03/079 TOUCH | TABLEMTN | ETL.8290.POLE.NWOD | 2025-02-13 | 2025-02-13 | 2025-02-13 | TBC |  | 2025-08-13 | 2025-08-13 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46478092 | T3 EI VOLTA-DESCHUTES 03/079 TOUCH | ICW
LC | 130859713 | 025/111 | T3NT MRO BY SLR SWSTA#1 25/111 RMV VEG | PISMOBCH | ETL.5300.TOWR | 2025-02-13 | 2025-02-13 | 2025-02-13 | TBC |  | 2028-02-13 | 2025-08-13 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 PRTO AIR FRAB | Overgrown | Vegetation | Remove
LC | 130859790 | 025/109 | T3 DI MORRO BY MESA 25/109 TOUCH | PISMOBCH | ETL.5290.TOWR | 2025-02-13 | 2025-02-13 | 2025-05-14 | On-Time |  | 2025-08-13 | 2025-08-13 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46486178 | T3 DI MORRO BY MESA 25/109 TOUCH | ICQ
LC | 128172805 | 002/027 | T2 EI GRANITE ROCK TAP 2/27 RPL INSW | MOSSLNDG | ETL.8311.INSL.NCER | 2024-02-14 | 2024-02-14 | 2025-04-06 | On-Time |  | 2025-08-14 | 2025-08-14 | 508T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMC REMT SWRK SPCR CLR ACCL ACCM ACCH COMP OH FMOB XMPT TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35611215 | T2 EI GRANITE ROCK TAP 2/27 RPL INSW | 93I
LC | 128173198 | 023/001 | T2 EI COPPERMINE-TIVY VLY 23/01 RPL STRW | FRESNO | ETL.8590.POLE.WOOD | 2024-02-14 | 2024-02-14 | 2025-03-31 | On-Time |  | 2025-08-14 | 2025-08-14 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP REMT ACCM ACCH COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35554464 | T2 EI COPPERMINE-TIVY VLY 23/01 RPL STRW | 70Y
LC | 128173322 | 022/014 | T2 EI COPPERMINE-TIVY VLY 22/14 RPL POLE | FRESNO | ETL.8590.POLE.WOOD | 2024-02-14 | 2024-02-14 | 2025-03-31 | On-Time |  | 2025-08-14 | 2025-08-14 | 372 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP REMT ACCL ACCM ACCH COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35554463 | T2 EI COPPERMINE-TIVY VLY 22/14 RPL PL | 70Y
LC | 128173943 | 054/1046 | T2 HAT CREEK#1-WSTWD 54/1046 RPL POLE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-02-14 | 2024-02-14 | 2025-05-27 | On-Time |  | 2025-08-14 | 2025-08-14 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35536591 | T2 EI HAT CREEK#1-WSTWD 54/1046 RPL POLE | 70Y
LC | 128189517 | 002/027 | T2 DI CHRISTIE-WILLOW PSS 2/27 RPL STRW | CONCORD | ETL.6370.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2025-04-09 | On-Time |  | 2025-08-14 | 2025-08-14 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573113 | T2 DI CHRISTIE-WILLOW PSS 2/27 RPL STRW | 70Y
LC | 128189952 | 003/034 | T2 DI CHRISTIE-WILLOW PSS 3/34 RPL STRW | CONCORD | ETL.6370.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2025-04-11 | On-Time |  | 2025-08-14 | 2025-08-14 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573117 | T2 DI CHRISTIE-WILLOW PSS 3/34 RPL STRW | 70Y
LC | 128190468 | 003/032 | T2 DI CHRISTIE-WILLOW PSS 3/32 RPL POLE | CONCORD | ETL.6370.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2025-04-10 | On-Time |  | 2025-08-14 | 2025-08-14 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573116 | T2 DI CHRISTIE-WILLOW PSS 3/32 RPL POLE | 70Y
LC | 128191065 | 003/031 | T2 DI CHRISTIE-WILLOW PSS 3/31 RPR GYWW | CONCORD | ETL.6370.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2025-04-11 | On-Time |  | 2025-08-14 | 2025-08-14 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46286502 | T2 DI CHRISTIE-WILLOW PSS 3/31 RPR GYWW | ICW
LC | 129386669 | 19 | COLGATE-SMARTVILLE #1 11/134 RPR SWTC | SACTO | ETL.6510.SWIT | 2024-08-14 | 2024-08-14 | 2025-01-09 | On-Time |  | 2024-11-14 | 2025-08-14 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Switch-Wood | Repair | 46323930 | COLGATE-SMARTVILLE #1 11/134 RPR SWTC | ICW
LC | 130862232 | 012/112 | T3 EI CTTNWD-BENTON #2 12/112R RPR POLE | TABLEMTN | ETL.6650.POLE.WDPS | 2025-02-14 | 2025-02-14 | 2025-02-14 | TBC |  | 2025-08-14 | 2025-08-14 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46489536 | T3 EI CTTNWD-BENTON #2 12/112R RPR POLE | ICW
LC | 130862877 | 000/008 | T3 EI VOLTA-DESCHUTES 0/008 RPL STRW | TABLEMTN | ETL.8290.POLE.WOOD | 2025-02-14 | 2025-02-14 | 2025-02-14 | TBC |  | 2025-08-14 | 2025-08-14 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35619951 | T3 EI VOLTA-DESCHUTES 0/008 RPL STRW | 70Y
LC | 130863403 | 010/151A | T3 EI WEIMAR #1 10/151A RPL HRDW | SACTO | ETL.7560.POLE.NWOD | 2025-02-14 | 2025-02-14 | 2025-04-08 | On-Time |  | 2025-08-14 | 2025-08-14 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace | 46484878 | T3 EI WEIMAR #1 10/151A RPL HRDW | ICW
LC | 130863539 | 000/020 | T3 EI VOLTA-DESCHUTES 0/020 RPL STRW | TABLEMTN | ETL.8290.POLE.WOOD | 2025-02-14 | 2025-02-14 | 2025-02-14 | TBC |  | 2025-08-14 | 2025-08-14 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35619596 | T3 EI VOLTA-DESCHUTES 0/020 RPL STRW | 70Y
LC | 130863650 | 014/191 | T3 EI WEIMAR #1 14/191 RMV STEP | SACTO | ETL.7560.POLE.NWOD | 2025-02-14 | 2025-02-14 | 2025-04-08 | On-Time |  | 2025-08-14 | 2025-08-14 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Hardware-Steel | Replace | 46484960 | T3 EI WEIMAR #1 14/191 RMV STEP | ICS
LC | 130871110 | 010/041 | T3 DI MRO BAY SLR SWST #1 10/41 MASTIC | PISMOBCH | ETL.5300.TOWR | 2025-02-18 | 2025-02-14 | 2025-02-14 | TBC |  | 2025-08-14 | 2025-08-14 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46486400 | T3 DI MRO BAY SLR SWST #1 10/41 MASTIC | ICQ
LC | 130921374 | ?002/002 | T3 SNEATH LANE-HALF MN BY ?2/2 RMV BRSH | METCALF | ETL.7212.POLE.NWOD | 2025-03-03 | 2025-02-14 | 2025-02-14 | TBC |  | 2025-08-14 | 2025-08-14 | 932 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH FMOB TR3 PRTO FRAB BRIN | Brush Fuel | Road | Remove | 44306463 | SNEATH LANE-HMB :001/010 FIX ROAD | CHS
LC | 130865798 | 001/034 | T3 EI VOLTA-DESCHUTES 001/034 RPR STRW | TABLEMTN | ETL.8290.POLE.WOOD | 2025-02-17 | 2025-02-17 | 2025-02-17 | TBC |  | 2025-08-17 | 2025-08-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46485451 | T3 EI VOLTA-DESCHUTES 001/034 RPR STRW | ICW
LC | 130870724 | 001/020 | T3 DI WST PNT-VLLY SPRNGS 1/20 RPL STRW | VICTOR | ETL.8350.POLE.WOOD | 2025-02-18 | 2025-02-18 | 2025-02-18 | TBC |  | 2025-08-18 | 2025-08-18 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35617273 | T3 DI WST PNT-VLLY SPRNGS 1/20 RPL STRW | 70Y
LC | 130871013 | 001/007 | T3 DI TIGER CREEK ELECTRA 1/7 TOUCH | VICTOR | ETL.5780.TOWR | 2025-02-18 | 2025-02-18 | 2025-05-12 | On-Time |  | 2025-08-18 | 2025-08-18 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491561 | T3 DI TIGER CREEK ELECTRA 1/7 TOUCH | ICQ
LC | 130871101 | 001/023 | T3 DI WST PNT-VLLY SPRNGS 1/23 RPL STRW | VICTOR | ETL.8350.POLE.WOOD | 2025-02-18 | 2025-02-18 | 2025-02-18 | TBC |  | 2025-08-18 | 2025-08-18 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35617274 | T3 DI WST PNT-VLLY SPRNGS 1/23 RPL STRW | 70Y
LC | 130874363 | 006/094 | T3 EI WEIMAR #1 006/094 RPR STRW | SACTO | ETL.7560.POLE.WOOD | 2025-02-19 | 2025-02-18 | 2025-05-05 | On-Time |  | 2025-08-18 | 2025-08-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46484972 | T3 EI WEIMAR #1 006/094 RPR STRW | ICW
LC | 130874988 | 002/021 | T3 DI TGR CRK-VLLY SPRNGS 2/21 BNT STEEL | VICTOR | ETL.5790.TOWR | 2025-02-19 | 2025-02-18 | 2025-05-12 | On-Time |  | 2025-08-18 | 2025-08-18 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46493444 | T3 DI TGR CRK-VLLY SPRNGS 2/21 BNT STEEL | ICQ
LC | 130871864 | 002/015 | T3 WV SOBRANTE-R #1 002/015 GO95 CLEAR | CONCORD | ETL.3770.TOWR | 2025-02-19 | 2025-02-19 | 2025-02-19 | TBC |  | 2025-08-19 | 2025-08-19 | 400 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW OTHR OH FMOB TR3 PRTO FRAB BRIN | Clearance | GO95 Clear Infract-Tower | To Be Corrected | 31739471 | T3 WV SOBRANTE-R #1 002/015 GO95 CLEAR | 93T
LC | 130875147 | 003/028 | T3 DI TGR CRK VLY SPNGS 03/028 RPL INSS | VICTOR | ETL.5790.INSL.CERA | 2025-02-19 | 2025-02-19 | 2025-02-19 | TBC |  | 2025-08-19 | 2025-08-19 | 532T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35642499 | T3 DI TGR CRK VLY SPNGS 03/028 RPL INSS | 93K
LC | 130875167 | 004/032 | T3 DI TGR CRK-VLLY SPRNGS 4/32 COTTER | VICTOR | ETL.5790.INSL.CERA | 2025-02-19 | 2025-02-19 | 2025-05-05 | On-Time |  | 2025-08-19 | 2025-08-19 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46488867 | T3 DI TGR CRK-VLLY SPRNGS 4/32 COTTER | ICS
LC | 130875192 | 001/008 | T3 DI TGR CRK ELCTRA 01/008 RPL INSW | VICTOR | ETL.5780.INSL.CERA | 2025-02-19 | 2025-02-19 | 2025-05-10 | On-Time |  | 2025-08-19 | 2025-08-19 | 508T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35627955 | T3 DI TGR CRK ELCTRA 01/008 RPL INSW | 93I
LC | 130877862 | 008/036 | T3 DI MORO BAY-SLR SS #1-08/36 RPR JUMS | PISMOBCH | ETL.5300.INSL.NCER | 2025-02-20 | 2025-02-19 | 2025-04-10 | On-Time |  | 2025-08-19 | 2025-08-19 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46488821 | T3 DI MORO BAY-SLR SS #1-08/36 RPR JUMS | ICS
LC | 128197351 | 005/042 | T2 EI DIVIDE-VANDENBERG #1 5/42 RPL STRW | PISMOBCH | ETL.8620.POLE.WOOD | 2024-02-20 | 2024-02-20 | 2024-02-20 | TBC |  | 2025-08-20 | 2025-08-20 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573266 | T2 EI DIVIDE-VANDENBERG #1 5/42 RPL STRW | 70Y
LC | 128197538 | 005/043 | T2 DIVIDE-VANDENBERG #1 5/43 RPL STRW | PISMOBCH | ETL.8620.POLE.WOOD | 2024-02-20 | 2024-02-20 | 2024-02-20 | TBC |  | 2025-08-20 | 2025-08-20 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573267 | T2 EI DIVIDE-VANDENBERG #1 5/43 RPL STRW | 70Y
LC | 130876698 | 009/141 | T3 EI WEIMAR #1 9/141 TOUCH | SACTO | ETL.7560.POLE.NWOD | 2025-02-20 | 2025-02-20 | 2025-04-08 | On-Time |  | 2025-05-20 | 2025-08-20 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAR DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46484875 | T3 EI WEIMAR #1 9/141 TOUCH | ICW
LC | 130877586 | 003/075 | T3 EI VOLTA-DESCHUTES 03/075 RPR CNDW | TABLEMTN | ETL.8290.INSL.NCER | 2025-02-20 | 2025-02-20 | 2025-02-20 | TBC |  | 2025-08-20 | 2025-08-20 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46477694 | T3 EI VOLTA-DESCHUTES 03/075 RPR CNDW | ICW
LC | 130877709 | 026/103 | T3 IR PITTSBURG-EASTSHRE 26/103 RPR SPLS | CONCORD | ETL.5462.INSL.NCER | 2025-02-20 | 2025-02-20 | 2025-02-20 | TBC |  | 2025-05-20 | 2025-08-20 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW IR OH TR3 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Splice-Steel | Repair | 46475931 | T3 DI PITTSBURG-EASTSHRE 26/103 RPL SPLS | ICS
LC | 130877987 | 000/016 | T3 DI PINE GROVE TAP-00/16 TOUCH | VICTOR | ETL.8351.POLE.WOOD | 2025-02-20 | 2025-02-20 | 2025-06-02 | On-Time |  | 2025-08-20 | 2025-08-20 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46477451 | T3 DI PINE GROVE TAP-00/16 TOUCH | ICW
LC | 130896527 | 001/026 | T3 DI WEST PT VALY SPRINGS 1/26 RPL STRW | VICTOR | ETL.8350.POLE.WOOD | 2025-02-24 | 2025-02-20 | 2025-02-20 | TBC |  | 2025-08-20 | 2025-08-20 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35618532 | T3 DI WEST PT VALY SPRINGS 1/26 RPL STRW | 70Y
LC | 128200141 | 000/004 | T2 EI GRANITE ROCK TP 00/04 GRND WASH | MOSSLNDG | ETL.8311.INSL.CERA | 2024-02-21 | 2024-02-21 | 2025-04-05 | On-Time |  | 2025-08-21 | 2025-08-21 | 622 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP REMT NOAC SWRK COMP OH FMOB XMPT TR2 PRTO | Contaminated | Insulator | Ground Wash | 46305517 | T2 EI GRANITE ROCK TP 00/04 GRND WASH | ICD
LC | 129415046 | 001/027 | T2 VALLEY SPRINGS #1 1/27 RPL STRW | VICTOR | ETL.8210.POLE.WOOD | 2024-08-21 | 2024-08-21 | 2025-04-19 | On-Time |  | 2025-08-21 | 2025-08-21 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW TNT COMP OH FMOB TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35587672 | T2 VALLEY SPRINGS #1 1/27 RPL POLE | 70Y
LC | 128206012 | 038/008 | T2 TRINITY-MAPLE CREEK 38/8 GO95 | EUREKA | ETL.8170.POLE.WOOD | 2024-02-22 | 2024-02-22 | 2024-02-22 | TBC |  | 2025-08-22 | 2025-08-22 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR FIRE ACCM OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35533318 | -RINITY-MAPLE CREEK 38/8 OVERLOADED POLE | 93G
LC | 129423013 | 018/307 | T2 ARCO-POLNIO PASS PP 18/307 RPL ANCW | MIDWAY | ETL.8450.POLE.WOOD | 2024-08-22 | 2024-08-22 | 2025-01-24 | On-Time |  | 2025-02-22 | 2025-08-22 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW REMT TRAF ACCH USA COMP OH FMOB TR2 PRTO FRAB DURA | No Good/Out of Stdrd | Anchor-Wood | Replace | 35578693 | T2 EI ARCO-POLNIO PSS PP 18/307 RPL ANCW | 93E
LC | 129423044 | 014/237 | T2 ARCO-POLONIO PASS PP 014/237 RPL ANCW | MIDWAY | ETL.8450.POLE.WOOD | 2024-08-22 | 2024-08-22 | 2025-04-02 | On-Time |  | 2025-02-22 | 2025-08-22 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW REMT USA COMP OH FMOB TR2 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35578692 | T2 ARCO-POLONIO PASS PP 014/237 RPL ANCW | 93E
LC | 128213983 | 009/173 | T2 MNTA VSTA-LS GTS 009/173 GO95 | METCALF | ETL.7610.POLE.WOOD | 2024-02-26 | 2024-02-23 | 2025-04-30 | On-Time |  | 2025-08-23 | 2025-08-23 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR2 PRTO FRAR | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35592193 | T2 MNTA VSTA-LS GTS 009/173 GO95 | 93G
LC | 128217518 | 025/002 | T2 TRINTY-MPLE CRK 25/2 COMPLETE | EUREKA | ETL.8170.POLE.WOOD | 2024-02-27 | 2024-02-23 | 2025-04-13 | On-Time |  | 2025-08-23 | 2025-08-23 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE COMP OH XMPT TR2 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35534253 | T2 TRINTY-MPLE CRK 25/2 OVERLOADED POLE | 93G
LC | 129886421 | 005/021 | T2 PITTSBURG-TESLA #1 005/021 RPR STRT | CONCORD | ETL.5510.TOWR | 2024-12-02 | 2024-08-23 | 2025-02-06 | On-Time |  | 2025-08-23 | 2025-08-23 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46441172 | T2 PITTSBURG-TESLA #1 005/021 RPR STRT | ICQ
LC | 130930271 | 005/045 | T3 DI TIGER CRK VLY SPRNGS 5/45 TOUCH | VICTOR | ETL.5790.TOWR | 2025-03-04 | 2025-02-24 | 2025-05-12 | On-Time |  | 2025-08-24 | 2025-08-24 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46493451 | T3 DI TIGER CRK VLY SPRNGS 5/45 TOUCH | ICQ
LC | 130901319 | 021/088 | T3 DI MRR BY-SLR SW ST #1 21/88 TOUCH | PISMOBCH | ETL.5300.TOWR | 2025-02-25 | 2025-02-25 | 2025-06-03 | On-Time |  | 2025-08-25 | 2025-08-25 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46491148 | T3 DI MRR BY-SLR SW ST #1 21/88 TOUCH | ICQ
LC | 130901506 | 004/033 | T3 MORAGA-OAKLAND J 4/033 RPL SPLS | CONCORD | ETL.2760.INSL | 2025-02-25 | 2025-02-25 | 2025-05-22 | On-Time |  | 2025-08-25 | 2025-08-25 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW IR COMP OH TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Splice-Steel | Replace | 46485067 | T3 DI MORAGA-OAKLAND J 4/033 RPL SPLS | ICS
LC | 128213254 | 010/116 | T2 DRUM-SUMMIT #2 10/116 RPR INSS | SACTO | ETL.1450.INSL.NCER | 2024-02-26 | 2024-02-26 | 2025-06-19 | On-Time |  | 2025-08-26 | 2025-08-26 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB XMPT TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Insulator-Steel | Repair | 46443292 | T2 DRUM-SUMMIT #2 10/116 RPR INSS | ICS
LC | 128231615 | 022/147 | T2 DI POE-RIO OSO RIO OS 22/147 RPL INSS | TABLEMTN | ETL.5540.INSL | 2024-03-01 | 2024-02-26 | 2025-04-15 | On-Time |  | 2025-08-26 | 2025-08-26 | 532 | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW COMP OH XMPT TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35571205 | T2 DI POE-RIO OSO RIO OS 22/147 RPL INSS | 93K
LC | 129435913 | 008/068 | T2 DI TRNTY-CTTNWD 008/068L RPL POLE | TABLEMTN | ETL.4040.POLE.WDPS | 2024-08-26 | 2024-08-26 | 2024-08-26 | TBC |  | 2025-08-26 | 2025-08-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572430 | T2 DI TRNTY-CTTNWD 008/068R RPL POLE | 70Y
LC | 129436084 | 69 | T2NT TRINITY-MAPLE CREEK 42/03D RPR SWTC | EUREKA | ETL.8170.SWIT | 2024-08-26 | 2024-08-26 | 2024-08-26 | TBC |  | 2027-08-26 | 2025-08-26 | 623 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO | Out of Adjustment | Switch | Repair | 46343731 | T2 TRINITY-MAPLE CREEK 42/03D RPR SWTC | ICE
LC | 129436259 | 010/078 | T2 VACA-SUISUN-JAMESON 10/78 INS RPTS | SACTO | ETL.4080.INSL.NCER | 2024-08-26 | 2024-08-26 | 2024-12-30 | On-Time |  | 2024-11-26 | 2025-08-26 | 530 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO DURA BRIN | Missing | Raptor Guard-Steel | Install | 31706644 | T2 VACA-SUISUN-JAMESON 10/78 INS RPTS | 93R
LC | 129436513 | 033/268 | T2 DI BRIDGEVIL-CTTNWD 33/268R RPL STRW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-08-26 | 2024-08-26 | 2025-04-07 | On-Time |  | 2025-08-26 | 2025-08-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35572065 | T2 DI BRIDGEVIL-CTTNWD 33/268C RPL STRW | 70Y
LC | 129436516 | 033/268 | T2 DI BRIDGEVIL-CTTNWD 33/268C RPL STRW | TABLEMTN | ETL.1110.POLE.WDPS | 2024-08-26 | 2024-08-26 | 2025-04-07 | On-Time |  | 2025-08-26 | 2025-08-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35572065 | T2 DI BRIDGEVIL-CTTNWD 33/268C RPL STRW | 70Y
LC | 129437922 | 007/034 | T2 DI SAN LS OBSPO-OCNO 7/34 RPL SPLS | PISMOBCH | ETL.3530.INSL.CERA | 2024-08-26 | 2024-08-26 | 2025-06-24 | On-Time |  | 2025-08-26 | 2025-08-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Splice-Steel | Replace | 46380794 | T2 DI SAN LS OBSPO-OCNO 7/34 RPL SPLS | ICS
LC | 129437954 | 007/036 | T2 DI SAN LUIS OBISPO-OCNO 7/36 RPR CNDS | PISMOBCH | ETL.3540.INSL.NCER | 2024-08-26 | 2024-08-26 | 2025-05-28 | On-Time |  | 2025-08-26 | 2025-08-26 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Conductor-Steel | Repair | 46380795 | T2 DI SAN LUIS OBISPO-OCNO 7/36 RPR CNDS | ICS
LC | 129444626 | 004/021 | T2 DI SN LUIS OBSPO-OCENO 4/21 TOUCH | PISMOBCH | ETL.3530.TOWR | 2024-08-27 | 2024-08-26 | 2025-03-05 | On-Time |  | 2025-02-26 | 2025-08-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46475654 | T2 DI SN LUIS OBSPO-OCENO 4/21 TOUCH | ICQ
LC | 129444627 | 004/021 | T2NT DI SN LUIS OBSP OCENO 4/21 RPR STRT | PISMOBCH | ETL.3530.TOWR | 2024-08-27 | 2024-08-26 | 2024-08-26 | TBC |  | 2027-08-26 | 2025-08-26 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE ACCM OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair
LC | 129450608 | 006/031 | T2 DI SN LS OBSPO-STA MRA 6/31 RPL INSS | PISMOBCH | ETL.3540.INSL.CERA | 2024-08-28 | 2024-08-26 | 2025-05-28 | On-Time |  | 2024-11-26 | 2025-08-26 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35587174 | T2 DI SN LS OBSPO-SNTA MRA RPL INSS 2 LS | 93K
LC | 129450682 | 004/022 | T2 DI SN LS OBSPO-SNTA MRA 4/22 RPL INSS | PISMOBCH | ETL.3540.INSL.CERA | 2024-08-28 | 2024-08-26 | 2025-05-28 | On-Time |  | 2025-08-26 | 2025-08-26 | 532T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35587174 | T2 DI SN LS OBSPO-SNTA MRA RPL INSS 2 LS | 93K
LC | 129450912 | 046/008 | T2 FORT ROSS-GUALALA 46/008 RPL STRW | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-08-28 | 2024-08-26 | 2025-04-29 | On-Time |  | 2025-08-26 | 2025-08-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW FIRE SPCR ACCM COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586907 | T2 FORT ROSS-GUALALA 46/008 RPL STRW | 70Y
LC | 129452610 | 044/005 | T2 FORT ROSS-GUALALA 44/5C RPL STRW | LAKEVLLE | ETL.6980.POLE.WDPS | 2024-08-29 | 2024-08-26 | 2025-04-29 | On-Time |  | 2025-08-26 | 2025-08-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW FIRE COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586905 | T2 FORT ROSS-GUALALA 44/5C RPL STRW | 70Y
LC | 129452894 | 045/007 | T2 FORT ROSS-GUALALA 45/7 RPL 129452894 | LAKEVLLE | ETL.6980.POLE.WOOD | 2024-08-29 | 2024-08-26 | 2025-04-29 | On-Time |  | 2025-08-26 | 2025-08-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW FIRE SPCR ACCM COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586906 | T2 FORT ROSS-GUALALA 45/7 RPL STRW | 70Y
LC | 129453403 | 044/005 | T2 FORT ROSS-GUALALA 44/5L RPL STRW | LAKEVLLE | ETL.6980.POLE.WDPS | 2024-08-29 | 2024-08-26 | 2025-04-29 | On-Time |  | 2025-08-26 | 2025-08-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR FIRE COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586905 | T2 FORT ROSS-GUALALA 44/5C RPL STRW | 70Y
LC | 129453406 | 044/005 | T2 FORT ROSS-GUALALA 44/5R RPL STRW | LAKEVLLE | ETL.6980.POLE.WDPS | 2024-08-29 | 2024-08-26 | 2025-04-29 | On-Time |  | 2025-08-26 | 2025-08-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW OTHR FIRE COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35586905 | T2 FORT ROSS-GUALALA 44/5C RPL STRW | 70Y
LC | 129626304 | 009/109 | T2 COLGTE-SMRTVLLE #1 9/109 RPL STRW | SACTO | ETL.6510.POLE.WOOD | 2024-10-03 | 2024-08-26 | 2025-04-09 | On-Time |  | 2025-08-26 | 2025-08-26 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35604412 | T2 COLGTE-SMRTVLLE #1 9/109 RPL POLE | 70Y
LC | 130913380 | 009/034 | T3 DI DIABLO-MIDWAY #3 09/34 RPR INSS | PISMOBCH | ETL.5980.INSL.NCER | 2025-02-27 | 2025-02-26 | 2025-04-16 | On-Time |  | 2025-08-26 | 2025-08-26 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46496906 | T3 DI DIABLO-MIDWAY #3 09/34 RPR INSS | ICS
LC | 130924995 | 002/012 | T3 DI DIABLO-MDWY #2 2/12 TOUCH | PISMOBCH | ETL.5970.TOWR | 2025-03-03 | 2025-02-26 | 2025-02-26 | TBC |  | 2025-08-26 | 2025-08-26 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46493076 | T3 DI DIABLO-MDWY #2 2/12 TOUCH | ICQ
LC | 128218085 | 015/294 | T2 HAT CRK #1-WSTWD 015/294 GO95 RPL | TABLEMTN | ETL.7030.POLE.WOOD | 2024-02-27 | 2024-02-27 | 2025-05-02 | On-Time |  | 2025-08-27 | 2025-08-27 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35534333 | T2 HAT CRK #1-WSTWD 015/294 GO95 RPL | 93G
LC | 128254833 | 051/362 | T2 DI CARIBOU-TABLE MNTN 51/362 RPL INSS | TABLEMTN | ETL.4440.INSL.CERA | 2024-03-08 | 2024-02-27 | 2025-04-09 | On-Time |  | 2025-08-27 | 2025-08-27 | 532 | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569572 | T2 DI CARIBOU-TBL MTN RPL INSS | 93K
LC | 128259056 | 050/359 | T2 DI CARIBOU-TABLE MTN 50/359 RPL INSS | TABLEMTN | ETL.4440.INSL.CERA | 2024-03-09 | 2024-02-27 | 2025-04-09 | On-Time |  | 2025-08-27 | 2025-08-27 | 532 | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569572 | T2 DI CARIBOU-TBL MTN RPL INSS | 93K
LC | 129441818 | 008/001 | T2 WV HUMBOLDT-MAPLE CREEK 8/1R TOUCH | EUREKA | ETL.7130.POLE.WDPS | 2024-08-27 | 2024-08-27 | 2024-08-27 | TBC |  | 2025-02-27 | 2025-08-27 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46496188 | T2 WV HUMBOLDT-MAPLE CREEK 8/1R TOUCH | ICW
LC | 130911437 | X001/008 | T3 EI DIABLO-MESA X001/008 RPR FOND | PISMOBCH | ETL.4620.TOWR | 2025-02-27 | 2025-02-27 | 2025-03-25 | On-Time |  | 2025-08-27 | 2025-08-27 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46491143 | T3 EI DIABLO-MESA X001/008 RPR FOND | ICQ
LC | 130911537 | X001/007 | T3 EI DIABLO-MESA X001/007 RPR FOND | PISMOBCH | ETL.4620.TOWR | 2025-02-27 | 2025-02-27 | 2025-03-25 | On-Time |  | 2025-08-27 | 2025-08-27 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46491142 | T3 EI DIABLO-MESA X001/007 RPR FOND | ICQ
LC | 130913328 | 006/028 | T3 DI MORRO BAY-TMPLTN 6/28 COTTER | PISMOBCH | ETL.5933.INSL.NCER | 2025-02-27 | 2025-02-27 | 2025-02-27 | TBC |  | 2025-08-27 | 2025-08-27 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46496150 | T3 DI MORRO BAY-TMPLTN 6/28 COTTER | ICS
LC | 130913463 | 007/033 | T3 MORROO BAY TEMPLETON 7/33 RPR JUMS | PISMOBCH | ETL.5933.INSL.CERA | 2025-02-27 | 2025-02-27 | 2025-02-27 | TBC |  | 2025-08-27 | 2025-08-27 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46493126 | T3 DI MORROO BAY TEMPLETON 7/33 RPR JUMS | ICS
LC | 130934057 | 008/235 | T3 DI COLGATE-ALLEGHANY 8/235 RPL STRW | SACTO | ETL.6470.POLE.WOOD | 2025-03-05 | 2025-02-27 | 2025-05-14 | On-Time |  | 2025-08-27 | 2025-08-27 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35620295 | T3 DI COLGATE-ALLEGHANY 8/235 RPL STRW | 70Y
LC | 130934326 | 005/133 | T3 DI COLGATE-ALLEGHANY 5/133 RPR CRSW | SACTO | ETL.6470.POLE.WOOD | 2025-03-05 | 2025-02-27 | 2025-05-12 | On-Time |  | 2025-08-27 | 2025-08-27 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46491485 | T3 DI COLGATE-ALLEGHANY 5/133 RPR CRSW | ICW
LC | 128224988 | 000/002 | T2 PIT #7 TAP 0/2 RPR SHLS | TABLEMTN | ETL.5442.POLE.STPS | 2024-02-28 | 2024-02-28 | 2025-06-20 | On-Time |  | 2025-08-28 | 2025-08-28 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO | No Good/Out of Stdrd | Shield Wire - Wood | Repair | 46332407 | T2 EI PIT #7 TAP 0/2 RPR SHLS | ICW
LC | 128229796 | 047/341 | T2 DI CARIBOU-TABLE MTN 47/341 RPL INSS | TABLEMTN | ETL.4440.INSL.CERA | 2024-02-29 | 2024-02-28 | 2025-04-08 | On-Time |  | 2025-08-28 | 2025-08-28 | 532 | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569572 | T2 DI CARIBOU-TBL MTN RPL INSS | 93K
LC | 128254527 | 046/336 | T2 DI CARIBOU TBL MTN 46/336 RPL INSS | TABLEMTN | ETL.4440.INSL.CERA | 2024-03-08 | 2024-02-28 | 2025-04-09 | On-Time |  | 2025-08-28 | 2025-08-28 | 532 | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569572 | T2 DI CARIBOU-TBL MTN RPL INSS | 93K
LC | 129445592 | 011/140 | T2 KESWICK-TRINITY 011/140 RPL STRW | TABLEMTN | ETL.7270.POLE.WOOD | 2024-08-28 | 2024-08-28 | 2025-04-25 | On-Time |  | 2025-08-28 | 2025-08-28 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Replace | 35586947 | T2 KESWICK-TRINITY 011/140 RPL STRW | 70Y
LC | 130921217 | 026/103 | T3 PITTSBURG-SAN MATEO 26/103 RPR CNDS | CONCORD | ETL.5462.INSL.NCER | 2025-03-03 | 2025-02-28 | 2025-02-28 | TBC |  | 2025-08-28 | 2025-08-28 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Conductor-Steel | Repair | 46516555 | T3 PITTSBURG-SAN MATEO 26/103 RPR CNDS | ICS
LC | 130924899 | 005/063B | T3 DI WST PNT VLLY SRNGS 5/63B RPR CNDW | VICTOR | ETL.8350.INSL.NCER | 2025-03-03 | 2025-02-28 | 2025-02-28 | TBC |  | 2025-08-28 | 2025-08-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46484270 | T3 DI WST PNT VLLY SRNGS 5/63B RPR CNDW | ICW
LC | 130924961 | 005/063B | T3 DI PINE GROVE TAP 5/63B RPR INSW | VICTOR | ETL.8351.INSL.NCER | 2025-03-03 | 2025-02-28 | 2025-02-28 | TBC |  | 2025-08-28 | 2025-08-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46528322 | T3 DI PINE GROVE TAP 5/63B RPR INSW | ICW
LC | 130924962 | 002/033 | T3 DI W POINT VALLEY SRNGS 2/33 GO95 | VICTOR | ETL.8350.POLE.WOOD | 2025-03-03 | 2025-02-28 | 2025-02-28 | TBC |  | 2025-08-28 | 2025-08-28 | 401 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | Overloaded | GO95 Clear Infract-Wood | Replace | 35624587 | T3 DI W POINT VALLEY SRNGS 2/33 GO95 | 93G
LC | 130924964 | 005/063A | T3 PINE GROVE TAP 5/63A RPR INSW | VICTOR | ETL.8351.INSL.NCER | 2025-03-03 | 2025-02-28 | 2025-02-28 | TBC |  | 2025-08-28 | 2025-08-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46528321 | T3 PINE GROVE TAP 5/63A RPR INSW | ICW
LC | 130924965 | 005/063A | T3 DI W POINT VALLEY SRNG 5/63A RPR BOND | VICTOR | ETL.8350.INSL.CERA | 2025-03-03 | 2025-02-28 | 2025-02-28 | TBC |  | 2025-05-28 | 2025-08-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46493895 | T3 DI W POINT VALLEY SRNG 5/63A RPR BOND | ICW
LC | 130924966 | 005/063C | T3 DI W POINT VALLEY SRNG 5/63C RPR ANCW | VICTOR | ETL.8350.POLE.WOOD | 2025-03-03 | 2025-02-28 | 2025-02-28 | TBC |  | 2025-08-28 | 2025-08-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46493896 | T3 DI W POINT VALLEY SRNG 5/63C RPR ANCW | ICW
LC | 130930273 | 005/062 | T3 DI WST PNT VLLY SPRNGS 5/62 RPR SWTC | VICTOR | ETL.8350.POLE.NWOD | 2025-03-04 | 2025-02-28 | 2025-02-28 | TBC |  | 2025-05-28 | 2025-08-28 | 623 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB DURA BRIN | Out of Adjustment | Switch | Repair | 46484273 | T3 DI WST PNT VLLY SPRNGS 5/62 RPR SWTC | ICE
LC | 130930280 | 007/203 | T3 DI COLGTE-ALLEGHANY 7/203 RPR INSW | SACTO | ETL.6470.INSL.NCER | 2025-03-04 | 2025-02-28 | 2025-05-13 | On-Time |  | 2025-08-28 | 2025-08-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46491480 | T3 DI COLGTE-ALLEGHANY 7/203 RPR INSW | ICW
LC | 130934055 | 018/486 | T3 DI COLGATE-ALLEGHANY 18/486 RPR JUMW | SACTO | ETL.6470.INSL.NCER | 2025-03-05 | 2025-02-28 | 2025-05-14 | On-Time |  | 2025-08-28 | 2025-08-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46491482 | T3 DI COLGATE-ALLEGHANY 18/486 RPR JUMW | ICW
LC | 130934059 | 006/160 | T3 DI COLGATE-ALLEGHANY 6/160 RPR JUMW | SACTO | ETL.6470.INSL.NCER | 2025-03-05 | 2025-02-28 | 2025-05-13 | On-Time |  | 2025-08-28 | 2025-08-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46491483 | T3 DI COLGATE-ALLEGHANY 6/160 RPR JUMW | ICW
LC | 130934103 | 006/157 | T3 DI CLGT-ALLEGHANY 6/157 RPL STRW | SACTO | ETL.6470.POLE.WOOD | 2025-03-05 | 2025-02-28 | 2025-05-13 | On-Time |  | 2025-08-28 | 2025-08-28 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35620293 | T3 DI CLGT-ALLEGHANY 6/157 RPL STRW | 70Y
LC | 130934201 | 010/291 | T3 DI CLGT-ALLEGHANY 10/291 RPR JUMW | SACTO | ETL.6470.INSL.NCER | 2025-03-05 | 2025-02-28 | 2025-05-13 | On-Time |  | 2025-08-28 | 2025-08-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46491484 | T3 DI CLGT-ALLEGHANY 10/291 RPR JUMW | ICW
LC | 130934263 | 007/206 | T3 DI COLGATE-ALLEGHANY 7/206 RPL STRW | SACTO | ETL.6470.POLE.WOOD | 2025-03-05 | 2025-02-28 | 2025-05-13 | On-Time |  | 2025-08-28 | 2025-08-28 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35620294 | T3 DI COLGATE-ALLEGHANY 7/206 RPL STRW | 70Y
LC | 130934358 | 005/046 | T3 DI TGR CRK-ELECTRA 05/46 TOUCH | VICTOR | ETL.5780.TOWR | 2025-03-05 | 2025-02-28 | 2025-05-12 | On-Time |  | 2025-08-28 | 2025-08-28 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46496147 | T3 DI TGR CRK-ELECTRA 05/46 TOUCH | ICQ
LC | 130938143 | 002/018 | T3 DI TGR CRK ELCTRA 02/18 TOUCH | VICTOR | ETL.5780.TOWR | 2025-03-06 | 2025-02-28 | 2025-05-12 | On-Time |  | 2025-08-28 | 2025-08-28 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46496148 | T3 DI TGR CRK ELCTRA 02/18 TOUCH | ICQ
LC | 130938168 | 004/051 | T3 DI WEST PNT LLEY SPRNGS 4/51 RPL STRW | VICTOR | ETL.8350.POLE.WOOD | 2025-03-06 | 2025-02-28 | 2025-02-28 | TBC |  | 2025-08-28 | 2025-08-28 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35633713 | T3 DI WEST PNT LLEY SPRNGS 4/51 RPL STRW | 70Y
LC | 129469438 | 009/170 | T2 SMARTVILLE-MARYSVILE 9/170 RPR POLE | SACTO | ETL.7980.POLE.WOOD | 2024-09-03 | 2024-08-29 | 2025-04-25 | On-Time |  | 2025-08-29 | 2025-08-29 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46354476 | T2 SMARTVILLE-MARYSVILE 9/170 RPR POLE | ICW
LC | 124406818 | B016/380 | T2NT DRUM-GRSS VLLY-WMR B16/380 BACKFIL | SACTO | ETL.6760.POLE.NWOD | 2022-08-30 | 2022-08-30 | 2023-03-19 | On-Time |  | 2025-08-30 | 2025-08-30 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 45683634 | T2 DRUM-GRSS VLLY-WEIMAR B16/380 BACKFIL | ICW
LC | 126313372 | 017/083 | T3 CRTNA MNDCNO#1 17/83 RPR OPGW | WILLITS | ETL.1330.TOWR | 2023-06-07 | 2023-05-31 | 2023-05-31 | TBC |  | 2025-08-31 | 2025-08-31 | 628 | TR3 | YES | E - Schd Compl Yr 0 | Open | RELW FIRE OH XMPT TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 45845929 | T3 DI CRTNA MNDCNO#1 17/083 RPR SHLS | ICS
LC | 128137583 | 048/002 | T2 WV FORT ROSS-GUALALA 48/2 INST DMPW | LAKEVLLE | ETL.6980.INSL.NCER | 2024-02-06 | 2024-02-06 | 2024-02-06 | TBC |  | 2025-08-31 | 2025-08-31 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB XMPT TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46305572 | T2 WV FORT ROSS-GUALALA 48/2 INST DMPW | ICW
LC | 128142662 | 012/424 | T2 SPAULDING-SUMMIT 12/424 GO95 RPL | SACTO | ETL.8060.POLE.WOOD | 2024-02-07 | 2024-02-07 | 2024-02-07 | TBC |  | 2025-09-01 | 2025-09-01 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR CUSI CGI OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35529922 | T2 SPAULDING-SUMMIT 12/424 GO95 RPL | 93G
LC | 129539864 | 031/007 | T2 GOLD HILL #1 31/7 RPL POLE | VICTOR | ETL.6950.POLE.WOOD | 2024-09-16 | 2024-09-02 | 2025-04-12 | On-Time |  | 2025-09-02 | 2025-09-02 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35587536 | T2 GOLD HILL #1 31/7 RPL POLE | 70Y
LC | 129469352 | 025/006 | T2 WV RIO DLL JCT-BRDGEVLE 25/06 RPL RPT | EUREKA | ETL.7850.POLE.NWOD | 2024-09-03 | 2024-09-03 | 2024-09-03 | TBC |  | 2025-09-03 | 2025-09-03 | 593 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Raptor Guard-Wood | Replace | 46403129 | T2 WV RIO DLL JCT-BRDGEVLE 25/06 RPL RPT | ICB
LC | 130924180 | 005/059 | T3 GEYSERS #3-CLOVERDL 5/59L OVERLOAD | LAKEVLLE | ETL.1650.POLE.WDPS | 2025-03-03 | 2025-03-03 | 2025-03-03 | TBC |  | 2025-09-03 | 2025-09-03 | 401T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR SPCR ACCM OH TR3 PRTO NTDE BRIN | Overloaded | GO95 Clear Infract-Wood | Replace | 35619956 | T3 GEYSERS #3-CLOVERDL 5/59L OVERLOAD | 93G
LC | 130924183 | 005/059 | T3 GEYSERS #3-CLOVERDL 5/59R OVERLOAD | LAKEVLLE | ETL.1650.POLE.WDPS | 2025-03-03 | 2025-03-03 | 2025-03-03 | TBC |  | 2025-09-03 | 2025-09-03 | 401T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OTHR SPCR ACCM OH TR3 PRTO NTDE BRIN | Overloaded | GO95 Clear Infract-Wood | Replace | 35619956 | T3 GEYSERS #3-CLOVERDL 5/59L OVERLOAD | 93G
LC | 130929266 | 005/001 | T3 DI DIABLO UNIT #1 005/001 TOUCH | PISMOBCH | ETL.5940.TOWR | 2025-03-04 | 2025-03-03 | 2025-03-03 | TBC |  | 2025-09-03 | 2025-09-03 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46493074 | T3 DI DIABLO UNIT #1 005/001 TOUCH | ICQ
LC | 130929292 | X000/001A | T3 DI DIABLO MESA 0/001A RRP ADSS | PISMOBCH | ETL.4620.POLE.WOOD | 2025-03-04 | 2025-03-03 | 2025-04-14 | On-Time |  | 2025-06-03 | 2025-09-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46494655 | T3 DI DIABLO MESA 0/001A RRP ADSS | ICW
LC | 130929349 | 004/058 | T3 DI DESABLA-CNTRVLL 4/058 RPL INSW | TABLEMTN | ETL.6720.INSL.NCER | 2025-03-04 | 2025-03-03 | 2025-04-15 | On-Time |  | 2025-09-03 | 2025-09-03 | 508T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35624217 | T3 DI DESABLA-CNTRVLL 4/058 RPL INSW | 93I
LC | 130929385 | 004/052 | T3 DI WST PNT-VLLY SPNGS 4/52 RPL STRW | VICTOR | ETL.8350.POLE.WOOD | 2025-03-04 | 2025-03-03 | 2025-03-03 | TBC |  | 2025-09-03 | 2025-09-03 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35624588 | T3 DI WST PNT-VLLY SPNGS 4/52 RPL STRW | 70Y
LC | 130929410 | 001/015 | T3 DI WST PT VLY SPNGS 1/015 RPR JMPW | VICTOR | ETL.8350.INSL.NCER | 2025-03-04 | 2025-03-03 | 2025-03-03 | TBC |  | 2025-09-03 | 2025-09-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46484271 | T3 DI WST PT VLY SPNGS 1/015 RPR JMPW | ICW
LC | 130934262 | 005/002 | T3 DI DIABLO UNIT #1 5/2 RPR OPGW | PISMOBCH | ETL.5940.TOWR | 2025-03-05 | 2025-03-03 | 2025-03-03 | TBC |  | 2025-09-03 | 2025-09-03 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46493127 | T3 DI DIABLO UNIT #1 5/2 RPR OPGW | ICS
LC | 130938241 | 005/060 | T3 DI DESABLA CENTERVLE 5/60 RPR STRW | TABLEMTN | ETL.6720.POLE.NWOD | 2025-03-06 | 2025-03-03 | 2025-04-15 | On-Time |  | 2025-09-03 | 2025-09-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46497256 | T3 DI DESABLA CENTERVLE 5/60 RPR STRW | ICW
LC | 130938285 | 003/042 | T3 DI W POINT VALLEY SPRNG 3/42 RPL POLE | VICTOR | ETL.8350.POLE.WOOD | 2025-03-06 | 2025-03-03 | 2025-03-03 | TBC |  | 2025-09-03 | 2025-09-03 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35624589 | T3 DI W POINT VALLEY SPRNG 3/42 RPL POLE | 70Y
LC | 130940078 | 000/011 | T3 DI WST PNT-VLY SPRNGS-00/11 RPL STRW | VICTOR | ETL.8350.POLE.WOOD | 2025-03-07 | 2025-03-03 | 2025-03-03 | TBC |  | 2025-09-03 | 2025-09-03 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35625456 | T3 DI WST PNT-VLY SPRNGS-00/11 RPL STRW | 70Y
LC | 130940079 | 000/011 | T3 DI WST PNT-VLY SPRNGS-00/11 RPR JUMW | VICTOR | ETL.8350.INSL.CERA | 2025-03-07 | 2025-03-03 | 2025-03-03 | TBC |  | 2025-09-03 | 2025-09-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46494872 | T3 DI WST PNT-VLY SPRNGS-00/11 RPR JUMW | ICW
LC | 130940129 | 008/064 | T3 DI TGR CRK-VLY SPRNGS 8/64 TOUCH | VICTOR | ETL.5790.TOWR | 2025-03-07 | 2025-03-03 | 2025-05-13 | On-Time |  | 2025-09-03 | 2025-09-03 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46493449 | T3 DI TGR CRK-VLY SPRNGS 8/64 TOUCH | ICQ
LC | 130940276 | 006/047 | T3 DI TGR CRK-ELECTRA 06/47 COTR KEY | VICTOR | ETL.5780.INSL | 2025-03-07 | 2025-03-03 | 2025-05-10 | On-Time |  | 2025-09-03 | 2025-09-03 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46494873 | T3 DI TGR CRK-ELECTRA 06/47 COTR KEY | ICS
LC | 130940754 | 008/065 | T3 DI TGR CRK-ELECTRA 08/65 TOUCH | VICTOR | ETL.5780.TOWR | 2025-03-07 | 2025-03-03 | 2025-05-13 | On-Time |  | 2025-09-03 | 2025-09-03 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46496149 | T3 DI TGR CRK-ELECTRA 08/65 TOUCH | ICQ
LC | 129471849 | 025/008 | T2NT WV RIO DL JCT-BRDGVLE 25/8 RPL INSW | EUREKA | ETL.7850.INSL.NCER | 2024-09-04 | 2024-09-04 | 2024-09-04 | TBC |  | 2027-09-04 | 2025-09-04 | 508 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW OTHR OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Insulator-Wood | Replace
LC | 129471980 | 025/008 | T2 WV RIO DL JCT-BRDGVLLE 25/08 INS DMPW | EUREKA | ETL.7850.INSL.NCER | 2024-09-04 | 2024-09-04 | 2025-06-05 | On-Time |  | 2025-09-04 | 2025-09-04 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46403130 | T2 WV RIO DL JCT-BRDGVLLE 25/08 INS DMPW | ICW
LC | 130927689 | 006/159 | T3 EI COLGATE-GRASS VLLY 6/159 RPL HRDW | SACTO | ETL.6490.POLE.WOOD | 2025-03-04 | 2025-03-04 | 2025-05-29 | On-Time |  | 2025-09-04 | 2025-09-04 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace | 46485461 | T3 EI COLGATE-GRASS VLLY 6/159 RPL HRDW | ICW
LC | 130927971 | 001/014 | T3 EL DRDO-MSSRI FLT #2 1/14 RPL INSS | SACTO | ETL.1540.INSL | 2025-03-04 | 2025-03-04 | 2025-03-16 | On-Time |  | 2025-09-04 | 2025-09-04 | 532T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35619176 | T3 EL DRDO-MSSRI FLT #2 1/14 RPL INSS | 93K
LC | 130928124 | 003/051 | T3 KESWICK-TRINITY 03/051 RPR INSW | TABLEMTN | ETL.7270.INSL.NCER | 2025-03-04 | 2025-03-04 | 2025-04-08 | On-Time |  | 2025-09-04 | 2025-09-04 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46494193 | T3 KESWICK-TRINITY 03/051 RPR INSW | ICW
LC | 130928510 | 008/005 | T3 EI MONTE RIO-FULTON 008/005 TOUCH | LAKEVLLE | ETL.7630.POLE.NWOD | 2025-03-04 | 2025-03-04 | 2025-03-04 | TBC |  | 2025-09-04 | 2025-09-04 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46493807 | T3 EI MONTE RIO-FULTON 008/005 TOUCH | ICW
LC | 130934058 | X001/011 | T3 DI DIABLO MESA X001/11 RPR OPGW | PISMOBCH | ETL.4620.TOWR | 2025-03-05 | 2025-03-04 | 2025-04-14 | On-Time |  | 2025-09-04 | 2025-09-04 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46488748 | T3 DI DIABLO MESA X001/11 RPR OPGW | ICS
LC | 130934372 | 005/060 | T3 DI WEST PINT-VLY SPRGS 5/60 RPR JUMW | VICTOR | ETL.8350.INSL.NCER | 2025-03-05 | 2025-03-04 | 2025-03-04 | TBC |  | 2025-09-04 | 2025-09-04 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46494871 | T3 DI WEST PINT-VLY SPRGS 5/60 RPR JUMW | ICW
LC | 130959407 | 003/046 | T3 DI WST PT-VLY SPNGS 3/046 BACKFILL | VICTOR | ETL.8350.POLE.NWOD | 2025-03-10 | 2025-03-04 | 2025-05-17 | On-Time |  | 2025-09-04 | 2025-09-04 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | Debris/Nest/etc. | Structure-Wood | Remove | 46494874 | T3 DI WST PT-VLY SPNGS 3/046 BACKFILL | ICW
LC | 130959411 | 003/046 | T3 DI WST PT-VLY SPNGS 3/046 TOUCH | VICTOR | ETL.8350.POLE.NWOD | 2025-03-10 | 2025-03-04 | 2025-05-17 | On-Time |  | 2025-09-04 | 2025-09-04 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46494875 | T3 DI WST PT-VLY SPNGS 3/046 TOUCH | ICW
LC | 130959532 | 005/046 | T3 DI TIGER CREEK VLY SPRN 5/46 TOUCH | VICTOR | ETL.5790.TOWR | 2025-03-10 | 2025-03-04 | 2025-05-13 | On-Time |  | 2025-09-04 | 2025-09-04 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46493453 | T3 DI TIGER CREEK VLY SPRN 5/46 TOUCH | ICQ
LC | 130959552 | 005/040 | T3 DI TIGER CREEK ELECTRA 5/40 TOUCH | VICTOR | ETL.5780.TOWR | 2025-03-10 | 2025-03-04 | 2025-05-29 | On-Time |  | 2025-09-04 | 2025-09-04 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46496902 | T3 DI TIGER CREEK ELECTRA 5/40 TOUCH | ICQ
LC | 130959606 | 005/042 | T3 DI TIGER CREEK ELECTRA 5/42 TOUCH | VICTOR | ETL.5780.TOWR | 2025-03-10 | 2025-03-04 | 2025-05-13 | On-Time |  | 2025-09-04 | 2025-09-04 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46496903 | T3 DI TIGER CREEK ELECTRA 5/42 TOUCH | ICQ
LC | 129476665 | 016/134 | T2 CRBRY SS-ROUND MTN 16/134 CANCEL | TABLEMTN | ETL.5410.INSL | 2024-09-05 | 2024-09-05 | 2024-09-05 | TBC |  | 2025-09-05 | 2025-09-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Splice-Steel | Replace | 46416226 | T2 EI CRBRY SS-ROUND MTN 16/134 RPL SPLS | ICS
LC | 129607979 | 008/073 | T2 DI PIT #3 PIT #1 8/73 MASTIC | TABLEMTN | ETL.5400.TOWR | 2024-09-30 | 2024-09-05 | 2025-06-04 | On-Time |  | 2025-09-05 | 2025-09-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46404705 | T2 DI PIT #3 PIT #1 8/73 MASTIC | ICQ
LC | 129614357 | 009/076 | T2 DI PIT #1-CTNWD 09/76 RPL HRDT | TABLEMTN | ETL.5390.TOWR | 2024-10-01 | 2024-09-05 | 2025-06-04 | On-Time |  | 2025-09-05 | 2025-09-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46452476 | T2 DI PIT #1-CTNWD 09/76 RPL HRDT | ICQ
LC | 129614396 | 009/076 | T2 DI PIT #1-CTNWD 09/76 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-10-01 | 2024-09-05 | 2025-06-04 | On-Time |  | 2025-09-05 | 2025-09-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46452740 | T2 DI PIT #1-CTNWD 09/76 RPR STRT | ICQ
LC | 130931914 | 012/105 | T3 CTTNWD-BENTON #2 12/105R RPL POLE | TABLEMTN | ETL.6650.POLE.WDPS | 2025-03-05 | 2025-03-05 | 2025-03-05 | TBC |  | 2025-09-05 | 2025-09-05 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | REGW OH FMOB TR3 PRTO FRAB PGEQ BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35624578 | T3 CTTNWD-BENTON #2 12/105L RPL POLE | 70Y
LC | 130932901 | 008/007 | T3 EI MONTE RIO-FULTON 008/007 RPR GYWW | LAKEVLLE | ETL.7630.POLE.NWOD | 2025-03-05 | 2025-03-05 | 2025-04-21 | On-Time |  | 2025-09-05 | 2025-09-05 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46493806 | T3 EI MONTE RIO-FULTON 008/007 RPR GYWW | ICW
LC | 130934190 | 010/001 | T3 EI MONTE RIO-FULTON 010/001 RMV VEG | LAKEVLLE | ETL.7630.POLE.NWOD | 2025-03-05 | 2025-03-05 | 2025-03-05 | TBC |  | 2025-09-05 | 2025-09-05 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Remove
LC | 130934461 | 043/191 | T3 DI MTCLF-MSS LNDNG #1 43/191 RPR STRT | MOSSLNDG | ETL.5100.TOWR | 2025-03-05 | 2025-03-05 | 2025-03-05 | TBC |  | 2025-09-05 | 2025-09-05 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46493243 | T3 DI MTCLF-MSS LNDNG #1 43/191 RPR STRT | ICQ
LC | 130934462 | 043/191 | T3 DI MTCLF-MSS LNDNG #1 43/191 TOUCH | MOSSLNDG | ETL.5100.TOWR | 2025-03-05 | 2025-03-05 | 2025-03-05 | TBC |  | 2025-09-05 | 2025-09-05 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46493252 | T3 DI MTCLF-MSS LNDNG #1 43/191 TOUCH | ICQ
LC | 130959457 | 012/128 | T3 DI IGNACIO BOLINAS #1 12/128 RPL DMPW | LAKEVLLE | ETL.7140.INSL.NCER | 2025-03-10 | 2025-03-05 | 2025-03-05 | TBC |  | 2025-09-05 | 2025-09-05 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCL OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Damper-Wood | Replace | 46499059 | T3 DI IGNACIO BOLINAS #1 12/128 RPL DMPW | ICW
LC | 130959467 | 045/195 | T3 DI METCALF MSS LNDNG#1 45/195 TOUCH | MOSSLNDG | ETL.5100.TOWR | 2025-03-10 | 2025-03-05 | 2025-03-05 | TBC |  | 2025-09-05 | 2025-09-05 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE CGI ACCL OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46493246 | T3 DI METCALF MSS LNDNG#1 45/195 TOUCH | ICQ
LC | 130959519 | 023/115 | T3 DI RND MTN TBL MTN#2 23/115 RPL INSS | TABLEMTN | ETL.6070.INSL | 2025-03-10 | 2025-03-05 | 2025-03-05 | TBC |  | 2025-09-05 | 2025-09-05 | 532 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35626538 | T2 DI RND MTN TBL MTN #2 10/54 RPL INSS | 93K
LC | 130959539 | 023/115 | T3 DI RND MTN TBL MTN#2 23/115 RPR SHLS | TABLEMTN | ETL.6060.TOWR | 2025-03-10 | 2025-03-05 | 2025-05-22 | On-Time |  | 2025-09-05 | 2025-09-05 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46493163 | T3 DI RND MTN TBL MTN#2 23/115 RPR SHLS | ICS
LC | 131013756 | 012/105 | T3 CTTNWD-BENTON #2 12/105L RPL POLE | TABLEMTN | ETL.6650.POLE.WDPS | 2025-03-26 | 2025-03-05 | 2025-03-05 | TBC |  | 2025-09-05 | 2025-09-05 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 PRTO PGEQ BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35624578 | T3 CTTNWD-BENTON #2 12/105L RPL POLE | 70Y
LC | 128255853 | A001/014 | T2 DI FULTON-PUEBLO :001/014 RPR POLE | LAKEVLLE | ETL.1600.POLE.WOOD | 2024-03-08 | 2024-03-06 | 2024-03-06 | TBC |  | 2025-09-06 | 2025-09-06 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46403099 | T2 DI FULTON-PUEBLO :001/014 RPR POLE | ICW
LC | 128281234 | 005/025 | T2 DI DIABLO-GATES #1 5/25 RPR SHLD | PISMOBCH | ETL.5960.TOWR | 2024-03-13 | 2024-03-06 | 2024-03-06 | TBC |  | 2025-09-06 | 2025-09-06 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW ACCM OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329568 | T2 DI DIABLO-GATES #1 5/25 RPR SHLD | ICS
LC | 128469478 | 025/145 | T2 STANISLAUS-MNTC #2 25/145 RMV NEST | VICTOR | ETL.3820.TOWR | 2024-04-06 | 2024-04-06 | 2024-04-06 | TBC |  | 2025-09-06 | 2025-09-06 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46299709 | T2 EI STANISLAUS-MNTC #2 25/145 RMV NEST | ICS
LC | 129482863 | 003/094 | T2 COLGATE-ALLEGHANY 03/94 RPL POLE | SACTO | ETL.6470.POLE.WOOD | 2024-09-06 | 2024-09-06 | 2024-10-17 | On-Time |  | 2025-09-06 | 2025-09-06 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35579660 | T2 COLGATE-ALLEGHANY 03/94 RPL POLE | 70Y
LC | 129595204 | 008/066 | T2 DI PIT #1-CTTNWD 8/66 RMV NEST | TABLEMTN | ETL.5390.TOWR | 2024-09-26 | 2024-09-06 | 2024-09-06 | TBC |  | 2025-09-06 | 2025-09-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46452764 | T2 DI PIT #1-CTTNWD 8/66 RMV NEST | ICS
LC | 129595206 | 008/066 | T2 DI PIT #1-CTTNWD 8/66 RPR FOND | TABLEMTN | ETL.5390.TOWR | 2024-09-26 | 2024-09-06 | 2025-06-04 | On-Time |  | 2025-09-06 | 2025-09-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46452758 | T2 DI PIT #1-CTTNWD 8/66 RPR FOND | ICQ
LC | 129595208 | 008/066 | T2 DI PIT #1-CTTNWD 8/66 RPR STRT | TABLEMTN | ETL.5390.TOWR | 2024-09-26 | 2024-09-06 | 2025-03-07 | On-Time |  | 2024-12-06 | 2025-09-06 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46452750 | T2 DI PIT #1-CTTNWD 8/66 RPR STRT | ICQ
LC | 129621753 | 006/056 | T2 DI PIT #1-COTTONWOOD 6/56 RMV NEST | TABLEMTN | ETL.5390.TOWR | 2024-10-02 | 2024-09-06 | 2024-09-06 | TBC |  | 2025-09-06 | 2025-09-06 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46452759 | T2 DI PIT #1-COTTONWOOD 6/56 RMV NEST | ICS
LC | 130937353 | 011/006 | T3 EI MONTE RIO-FULTON 011/006 RMV VEG | LAKEVLLE | ETL.7630.POLE.WOOD | 2025-03-06 | 2025-03-06 | 2025-03-06 | TBC |  | 2025-09-06 | 2025-09-06 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Remove
LC | 130937468 | 005/002 | T3 EI DIABLO UNIT #1 5/002 RPR STRT | PISMOBCH | ETL.5940.TOWR | 2025-03-06 | 2025-03-06 | 2025-03-06 | TBC |  | 2025-09-06 | 2025-09-06 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 PRTO CLMB FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46493077 | ET3 EI DIABLO UNIT #1 5/002 RPR STRT | ICQ
LC | 130937661 | 017/068 | T3 DIABLO-GATES #1 017/068 RPR INSS | PISMOBCH | ETL.5960.INSL | 2025-03-06 | 2025-03-06 | 2025-03-06 | TBC |  | 2025-09-06 | 2025-09-06 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR3 PRTO PGEQ BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46488852 | T3 DIABLO-GATES #1 017/068 RPR INSS | ICS
LC | 130938480 | B022/507 | T3 DI DRM-GRS VLY-WMR B022/507 RPL STRW | SACTO | ETL.6760.POLE.WOOD | 2025-03-06 | 2025-03-06 | 2025-06-23 | On-Time |  | 2025-09-06 | 2025-09-06 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35625455 | T3 DI DRM-GRS VLY-WMR B022/507 RPL STRW | 70Y
LC | 130959857 | 021/107 | T3 DI ROUND MTN 21/107 RPR SHLS | TABLEMTN | ETL.6070.TOWR | 2025-03-10 | 2025-03-06 | 2025-06-18 | On-Time |  | 2025-09-06 | 2025-09-06 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46493164 | T3 DI ROUND MTN 21/107 RPR SHLS | ICS
LC | 128250393 | 036/001 | T2 RIO DELL JCT-BRIDGEVILE 36/1 RPL PL | EUREKA | ETL.7850.POLE.WOOD | 2024-03-07 | 2024-03-07 | 2025-06-18 | On-Time |  | 2025-09-07 | 2025-09-07 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR SPCR ACCL COMP OH XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35537121 | T2 RIO DELL JCT-BRIDGEVILE 36/1 RPL PL | 70Y
LC | 130941412 | 005/072 | T3 EI KESWICK-TRINITY 05/072 RPR JMPW | TABLEMTN | ETL.7270.INSL.NCER | 2025-03-07 | 2025-03-07 | 2025-04-23 | On-Time |  | 2025-09-07 | 2025-09-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO PGEQ BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46494198 | T3 EI KESWICK-TRINITY 05/072 RPR JMPW | ICW
LC | 130941510 | 005/003B | T3 EI DIABLO UNIT #1 5/003B RPR STRT | PISMOBCH | ETL.5940.TOWR | 2025-03-07 | 2025-03-07 | 2025-04-24 | On-Time |  | 2025-09-07 | 2025-09-07 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH FMOB TR3 PRTO CLMB FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46479478 | T3 EI DIABLO UNIT #1 5/003B RPR STRT | ICQ
LC | 130959522 | 001/027 | T3 DI COLGATE-CHALLENGE 01/27 RPL STRW | SACTO | ETL.6480.POLE.WOOD | 2025-03-10 | 2025-03-07 | 2025-04-06 | On-Time |  | 2025-09-07 | 2025-09-07 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35624214 | T3 DI COLGATE-CHALLENGE 01/27 RPL STRW | 70Y
LC | 130959592 | 011/301 | T3 DI COLGATE-ALLEGHANY 11/301 RPL STRW | SACTO | ETL.6470.POLE.WOOD | 2025-03-10 | 2025-03-07 | 2025-05-14 | On-Time |  | 2025-09-07 | 2025-09-07 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35623061 | T3 DI COLGATE-ALLEGHANY 11/301 RPL STRW | 70Y
LC | 130965175 | 042/185 | T3 DI MTCLF-MSS LNDNG#1 42/185 RPR FOND | MOSSLNDG | ETL.5100.TOWR | 2025-03-11 | 2025-03-07 | 2025-03-07 | TBC |  | 2025-09-07 | 2025-09-07 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW ACCL OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46493249 | T3 DI MTCLF-MSS LNDNG#1 42/185 RPR FOND | ICQ
LC | 128294209 | 037/156 | T2 DI TEMPLETON-GATES 37/156 RPR OPGW | PISMOBCH | ETL.5934.TOWR | 2024-03-15 | 2024-03-08 | 2025-04-17 | On-Time |  | 2025-09-08 | 2025-09-08 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | OPGW - Steel | Repair | 46329551 | T2 DI TEMPLETON-GATES 37/156 RPR OPGW | ICS
LC | 128294734 | 039/163 | T2 DI TEMPLETON-GATES 39/163 RPR OPGW | PISMOBCH | ETL.5934.TOWR | 2024-03-15 | 2024-03-08 | 2025-04-17 | On-Time |  | 2025-09-08 | 2025-09-08 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46329552 | T2 DI TEMPLETON-GATES 39/163 RPR OPGW | ICS
LC | 128305360 | 023/320-GUY | T2 DI CLAY-MARTEL 23/320 RPL GYPL | VICTOR | ETL.8250.POLE.WOOD | 2024-03-19 | 2024-03-08 | 2024-03-08 | TBC |  | 2025-09-08 | 2025-09-08 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR2 PRTO AIR FRAB | Rotten | Guy Pole-Wood | Replace | 35574399 | +T2 DI CLAY-MARTEL 23/320 RPL GYPL | 70Y
LC | 128336183 | 001/014 | T2 DI CHRISTIE-WLLW PSS 01/014L RPL STRW | CONCORD | ETL.6370.POLE.WDPS | 2024-03-20 | 2024-03-08 | 2025-04-14 | On-Time |  | 2025-09-08 | 2025-09-08 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35573110 | T2 DI CHRISTIE-WLLW PSS 01/014L RPL STRW | 70Y
LC | 128336185 | 001/014 | T2 DI CHRISTIE-WLLW PSS 01/014R RPL STRW | CONCORD | ETL.6370.POLE.WDPS | 2024-03-20 | 2024-03-08 | 2025-04-11 | On-Time |  | 2025-09-08 | 2025-09-08 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW COMP OH XMPT TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35573110 | T2 DI CHRISTIE-WLLW PSS 01/014L RPL STRW | 70Y
LC | 129489773 | 041/196 | T2 IGNACIO-SOBRANTE 41/196 DUP CNCL | CONCORD | ETL.4920.TOWR | 2024-09-09 | 2024-09-08 | 2024-09-08 | TBC |  | 2025-09-08 | 2025-09-08 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW CREW REMT OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46320339 | T2 IGNACIO-SOBRANTE 41/196 RMV NEST | ICS
LC | 128274696 | 002/025 | T2 CW MONTA VISTA-BURNS 2/25 RPR POLE | MOSSLNDG | ETL.7590.POLE.NWOD | 2024-03-11 | 2024-03-09 | 2025-05-12 | On-Time |  | 2025-09-09 | 2025-09-09 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW CREW RESD TRAF CLR ACCH FLAG COMP OH FMOB XMPT TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Repair | 46329989 | T2 CW MONTA VISTA-BURNS 2/25 RPR POLE | ICW
LC | 129493405 | 024/003 | T2NT WV RIO DL JCT-BRDGVLE 24/3 RPL INSW | EUREKA | ETL.7850.INSL.NCER | 2024-09-09 | 2024-09-09 | 2024-09-09 | TBC |  | 2027-09-09 | 2025-09-09 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Insulator-Wood | Replace | 35586951 | T2NT WV RIO DL JCT-BRDGVLE 24/3 RPL INSW | 93I
LC | 129621644 | 007/064 | T2 DI PIT #3-PIT #1 7/64 TOUCH | TABLEMTN | ETL.5400.TOWR | 2024-10-02 | 2024-09-09 | 2025-02-26 | On-Time |  | 2025-03-09 | 2025-09-09 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46476139 | T2 DI PIT #3-PIT #1 7/64 TOUCH | ICQ
LC | 129539404 | :017/014 | T2 EAGLE ROCK-CORTINA :17/14 GO95 RPL | WILLITS | ETL.1470.POLE.WOOD | 2024-09-16 | 2024-09-10 | 2024-09-10 | TBC |  | 2025-09-10 | 2025-09-10 | 508T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35604413 | T2 EAGLE ROCK-CORTINA :17/014 RPL INSW | 93I
LC | 129632240 | 005/044 | T2 DI PIT #3-PIT #1 5/44 RPR INSS | TABLEMTN | ETL.5400.INSL.NCER | 2024-10-04 | 2024-09-10 | 2025-02-13 | On-Time |  | 2025-09-10 | 2025-09-10 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Insulator-Steel | Repair | 46452733 | T2 DI PIT #3-PIT #1 5/44 RPR INSS | ICS
LC | 130958240 | 014/002 | T3 EI MONTE RIO-FULTON 014/002 RMV VEG | LAKEVLLE | ETL.7630.POLE.WOOD | 2025-03-10 | 2025-03-10 | 2025-03-10 | TBC |  | 2025-09-10 | 2025-09-10 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Remove
LC | 130958992 | 014/004 | T3 EI MONTE RIO-FULTON 014/004 RPR POLE | LAKEVLLE | ETL.7630.POLE.WOOD | 2025-03-10 | 2025-03-10 | 2025-06-03 | On-Time |  | 2025-09-10 | 2025-09-10 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46493804 | T3 EI MONTE RIO-FULTON 014/004 RPR POLE | ICW
LC | 130962922 | 026/118 | T3 EI EXCHEQR-INDN FLT 26/118 UNBURY | FRESNO | ETL.8650.POLE.NWOD | 2025-03-11 | 2025-03-10 | 2025-03-10 | TBC |  | 2025-09-10 | 2025-09-10 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46486770 | T3 EI EXCHEQR-INDN FLT 26/118 UNBURY | ICQ
LC | 130965122 | 011/292 | T3 DI COLGATE ALLEGHANY 11/292C RPL STRW | SACTO | ETL.6470.POLE.WDPS | 2025-03-11 | 2025-03-10 | 2025-05-14 | On-Time |  | 2025-09-10 | 2025-09-10 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35623191 | T3 DI COLGATE-ALLEGHANY 11/292L RPL STRW | 70Y
LC | 130965125 | 011/292 | T3 DI COLGATE-ALLEGHANY 11/292R RPL STRW | SACTO | ETL.6470.POLE.WDPS | 2025-03-11 | 2025-03-10 | 2025-05-14 | On-Time |  | 2025-09-10 | 2025-09-10 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35623191 | T3 DI COLGATE-ALLEGHANY 11/292L RPL STRW | 70Y
LC | 130965172 | 011/292 | T3 DI COLGATE-ALLEGHANY 11/292L RPL STRW | SACTO | ETL.6470.POLE.WDPS | 2025-03-11 | 2025-03-10 | 2025-05-14 | On-Time |  | 2025-09-10 | 2025-09-10 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35623191 | T3 DI COLGATE-ALLEGHANY 11/292L RPL STRW | 70Y
LC | 130971074 | 009/050 | T3 DI RND MTN-TBL MTN #1 9/50 RPR SHLS | TABLEMTN | ETL.6060.TOWR | 2025-03-12 | 2025-03-10 | 2025-05-22 | On-Time |  | 2025-09-10 | 2025-09-10 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46493036 | T3 DI RND MTN-TBL MTN #1 9/50 RPR SHLS | ICS
LC | 130971259 | 009/051 | T3 DI RND MTN TBL MTN #1 9/51 RPR SHLS | TABLEMTN | ETL.6060.TOWR | 2025-03-12 | 2025-03-10 | 2025-05-23 | On-Time |  | 2025-09-10 | 2025-09-10 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46493035 | T3 DI RND MTN TBL MTN #1 9/51 RPR SHLS | ICS
LC | 128336181 | 006/049 | T2 DI TRINITY-COTTONWOOD 6/49 RPL POLE | TABLEMTN | ETL.4040.POLE.WDPS | 2024-03-20 | 2024-03-11 | 2024-03-11 | TBC |  | 2025-09-11 | 2025-09-11 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW FIRE OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572435 | T2 DI TRINITY-COTTONWOOD 6/49 RPL POLE | 70Y
LC | 128336184 | 006/049 | T2 DI TRINITY-COTTONWOOD 6/49 RPL POLE | TABLEMTN | ETL.4040.POLE.WDPS | 2024-03-20 | 2024-03-11 | 2024-03-11 | TBC |  | 2025-09-11 | 2025-09-11 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | POHW FIRE OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572435 | T2 DI TRINITY-COTTONWOOD 6/49 RPL POLE | 70Y
LC | 129516011 | 002/049 | T2 WV PINE GROVE TAP 02/49 RPL POLE | VICTOR | ETL.8351.POLE.WOOD | 2024-09-11 | 2024-09-11 | 2024-09-11 | TBC |  | 2025-09-11 | 2025-09-11 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAR | No Good/Out of Stdrd | Structure-Wood | Replace | 35587663 | T2 WV PINE GROVE TAP 02/49 RPL POLE | 70Y
LC | 130971104 | 005/003B | T3 DI DIABLO UNIT #1 5/003B RPR OPGW | PISMOBCH | ETL.5940.TOWR | 2025-03-12 | 2025-03-11 | 2025-03-11 | TBC |  | 2025-09-11 | 2025-09-11 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCH OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46493079 | T3 DI DIABLO UNIT #1 5/003B RPR OPGW | ICS
LC | 130974715 | 026/122 | T3 EI EXCHQUER-INDIAN FLAT 26/122 UNBURY | FRESNO | ETL.8650.POLE.NWOD | 2025-03-13 | 2025-03-11 | 2025-03-11 | TBC |  | 2025-09-11 | 2025-09-11 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46493069 | T3 EI EXCHQUER-INDIAN FLAT 26/122 UNBURY | ICQ
LC | 130758086 | 004/002 | T2 PTTR VLLY-MNDCNO 004/002 RPR STRT | WILLITS | ETL.7810.POLE.NWOD | 2025-01-16 | 2024-09-12 | 2025-03-18 | On-Time |  | 2025-09-12 | 2025-09-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46459998 | T2 PTTR VLLY-MNDCNO 004/002 RPR STRT | ICQ
LC | 130969268 | 000/004 | T3 KESWICK-TRINITY 000/004 TOUCH | TABLEMTN | ETL.7270.POLE.NWOD | 2025-03-12 | 2025-03-12 | 2025-04-08 | On-Time |  | 2025-09-12 | 2025-09-12 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO FRAB NTDE PGEQ BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46494220 | T3 KESWICK-TRINITY 000/004 TOUCH | ICW
LC | 130971047 | 020/103 | T3 DI ROUND MT-TBL MNT 20/103 RPR INST | TABLEMTN | ETL.6070.INSL | 2025-03-12 | 2025-03-12 | 2025-06-17 | On-Time |  | 2025-09-12 | 2025-09-12 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46493161 | T3 DI ROUND MT-TBL MNT 20/103 RPR INST | ICS
LC | 130971161 | 005/003C | T3 DI DIABLO UNIT#1 5/003C RPR SHLD | PISMOBCH | ETL.5940.TOWR | 2025-03-12 | 2025-03-12 | 2025-03-12 | TBC |  | 2025-09-12 | 2025-09-12 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCH OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46493128 | T3 DI DIABLO UNIT#1 5/003C RPR SHLD | ICS
LC | 130975825 | 020/103 | T3 DI ROUND MOUNTAIN 20/103 TOUCH | TABLEMTN | ETL.6060.TOWR | 2025-03-13 | 2025-03-12 | 2025-06-05 | On-Time |  | 2025-09-12 | 2025-09-12 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46517301 | T3 DI ROUND MOUNTAIN 20/103 TOUCH | ICQ
LC | 130975855 | 019/101 | T3 DI ROUND MOUNTAIN 19/101 RPR SHLS | TABLEMTN | ETL.6070.TOWR | 2025-03-13 | 2025-03-12 | 2025-06-18 | On-Time |  | 2025-09-12 | 2025-09-12 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46493034 | T3 DI ROUND MOUNTAIN 19/101 RPR SHLS | ICS
LC | 130975879 | 046/202 | T3 DI METCLF MSS LNDING#1 46/202 TOUCH | MOSSLNDG | ETL.5100.TOWR | 2025-03-13 | 2025-03-12 | 2025-03-12 | TBC |  | 2025-09-12 | 2025-09-12 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46493244 | T3 DI METCLF MSS LNDING#1 46/202 TOUCH | ICQ
LC | 130975963 | 020/102 | T3 DI RND MTN TBL MTN 20/102 RPR SHLS | TABLEMTN | ETL.6070.TOWR | 2025-03-13 | 2025-03-12 | 2025-06-18 | On-Time |  | 2025-09-12 | 2025-09-12 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46493039 | T3 DI RND MTN TBL MTN 20/102 RPR SHLS | ICS
LC | 128205910 | 007/078 | T2 DI IGNACIO-BOLINAS #1 7/78 RPL STRW | LAKEVLLE | ETL.7140.POLE.WOOD | 2024-02-22 | 2024-02-21 | 2024-02-21 | TBC |  | 2025-09-13 | 2025-09-13 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW FIRE ACCL OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573793 | T2 DI IGNACIO-BOLINAS #1 7/78 RPL STRW | 70Y
LC | 128214840 | 004/052 | T2 DI IGNACIO-BOLINAS #1-04/52 RPL STRW | LAKEVLLE | ETL.7140.POLE.WOOD | 2024-02-26 | 2024-02-26 | 2024-02-26 | TBC |  | 2025-09-13 | 2025-09-13 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW ACCL OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573792 | T2 DI IGNACIO-BOLINAS #1-04/52 RPL STRW | 70Y
LC | 130975823 | 054/302 | T3 DI TEMBLOR-SLO 054/302 RPR FOND | PISMOBCH | ETL.3960.TOWR | 2025-03-13 | 2025-03-13 | 2025-03-24 | On-Time |  | 2025-09-13 | 2025-09-13 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46493078 | T3 DI TEMBLOR-SLO 054/302 RPR FOND | ICQ
LC | 130975962 | 008/045 | T3 DI RND MTN-TBL MTN #1 8/45 RPR SHLS | TABLEMTN | ETL.6060.TOWR | 2025-03-13 | 2025-03-13 | 2025-05-22 | On-Time |  | 2025-09-13 | 2025-09-13 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46493162 | T3 DI RND MTN-TBL MTN #1 8/45 RPR SHLS | ICS
LC | 130986214 | 011/264 | T3 DI DRM GRS-VLY WMR 11/264 RPL POLE | SACTO | ETL.6760.POLE.WOOD | 2025-03-17 | 2025-03-13 | 2025-06-17 | On-Time |  | 2025-09-13 | 2025-09-13 | 372T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCH COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35625454 | T3 DI DRM GRS-VLY WMR 11/264 RPL POLE | 70Y
LC | 124501897 | :006/046 | T2NT WV ROCK CREEK-POE :06/46 RPR STRT | TABLEMTN | ETL.5630.TOWR | 2022-09-14 | 2022-09-14 | 2023-08-24 | On-Time |  | 2025-09-14 | 2025-09-14 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45717912 | T2 WV ROCK CREEK-POE :06/46 RPP STRT | ICQ
LC | 128289476 | 008/151 | T2 EI TEJON-LEBEC 008/151 RPR GYWW | MIDWAY | ETL.9250.POLE.NWOD | 2024-03-14 | 2024-03-14 | 2025-05-09 | On-Time |  | 2025-09-14 | 2025-09-14 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46302346 | T2 EI TEJON-LEBEC 008/151 RPR GYWW | ICW
LC | 128289910 | 003/005A | T2 EI HUMBOLDT-MAPLE CREEK 3/5A RPL INSW | EUREKA | ETL.7130.INSL | 2024-03-14 | 2024-03-14 | 2025-04-02 | On-Time |  | 2025-09-14 | 2025-09-14 | 508T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO | No Good/Out of Stdrd | Insulator-Wood | Replace | 35574642 | T2 EI HUMBOLDT-MAPLE CREEK 3/5A RPL INSW | 93I
LC | 128289912 | 003/007 | T2 EI HUMBOLDT-MAPLE CREEK 3/7 RPL STRW | EUREKA | ETL.7130.POLE.WOOD | 2024-03-14 | 2024-03-14 | 2025-04-01 | On-Time |  | 2025-09-14 | 2025-09-14 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574645 | T2 EI HUMBOLDT-MAPLE CREEK 3/7 RPL STRW | 70Y
LC | 129533785 | 029/002 | T2 EI TRINTY-MPLE CREEK 29/02 RPL ANCW | EUREKA | ETL.8170.POLE.WOOD | 2024-09-14 | 2024-09-14 | 2025-04-14 | On-Time |  | 2025-09-14 | 2025-09-14 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586954 | T2 EI TRINTY-MPLE CREEK 29/02 RPL ANCW | 93E
LC | 130985706 | 006/124 | T3 DI COLGATE-CHALLENGE 6/124 RPL INSW | SACTO | ETL.6480.INSL.NCER | 2025-03-17 | 2025-03-14 | 2025-04-06 | On-Time |  | 2025-09-14 | 2025-09-14 | 508T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35624216 | T3 DI COLGATE-CHALLENGE 6/124 RPL INSW | 93I
LC | 130985982 | 010/174 | T3 DI CLGT-CHALLENGE 010/174 RPR JUMW | SACTO | ETL.6480.INSL.NCER | 2025-03-17 | 2025-03-14 | 2025-04-06 | On-Time |  | 2025-09-14 | 2025-09-14 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46494376 | T3 DI CLGT-CHALLENGE 010/174 RPR JUMW | ICW
LC | 130986059 | 012/116 | T3 DI DRUM-HIGGINS 012/116R TOUCH | SACTO | ETL.4393.POLE.STPS | 2025-03-17 | 2025-03-14 | 2025-03-14 | TBC |  | 2025-09-14 | 2025-09-14 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH TR3 PRTO AIR NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46498567 | T3 DI DRUM-HIGGINS 012/116R TOUCH | ICW
LC | 130986140 | 012/116 | T3 DI DRUM-HIGGINS 012/116L TOUCH | SACTO | ETL.4393.POLE.STPS | 2025-03-17 | 2025-03-14 | 2025-06-29 | On-Time |  | 2025-09-14 | 2025-09-14 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46498568 | T3 DI DRUM-HIGGINS 012/116L TOUCH | ICW
LC | 130986221 | 009/169 | T3 DI CLGT-CHALLENGE 9/169 RPR JUMW | SACTO | ETL.6480.INSL.NCER | 2025-03-17 | 2025-03-14 | 2025-04-06 | On-Time |  | 2025-09-14 | 2025-09-14 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46494377 | T3 DI CLGT-CHALLENGE 9/169 RPR JUMW | ICW
LC | 130990458 | 001/010 | T3 DI MORAGA-OAKLAND #1 1/10 RPL HRDT | CONCORD | ETL.2720.TOWR | 2025-03-18 | 2025-03-14 | 2025-06-12 | On-Time |  | 2025-09-14 | 2025-09-14 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Hardware-Tower | Replace | 46499170 | T3 DI MORAGA-OAKLAND #1 1/10 RPL HRDT | ICQ
LC | 128293844 | 012/069 | T2 EI LONE TREE CAYENTANO 12/69 RPL INSS | CONCORD | ETL.6160.INSL.CERA | 2024-03-15 | 2024-03-15 | 2024-03-15 | TBC |  | 2025-09-15 | 2025-09-15 | 532 | TR2 | YES | E - Schd Compl Yr 0 | Open | REGW INSP REMT SWRK CLR OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575002 | T2 EI LONE TREE-CAYETANO RPL INSS IN 2 T | 93K
LC | 128294408 | 027/118 | T2 DIABLO-MESA 27/118 RPL INSS | PISMOBCH | ETL.4620.INSL | 2024-03-15 | 2024-03-15 | 2024-03-15 | TBC |  | 2025-09-15 | 2025-09-15 | 532T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP CLR OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35585666 | T2 EI DIABLO-MESA RPL INSS 7 LSTS | 93K
LC | 130986074 | 014/116 | T3 DI MONTA VISTA-BURNS 14/116 RPL INSW | MOSSLNDG | ETL.7590.INSL.NCER | 2025-03-17 | 2025-03-17 | 2025-05-10 | On-Time |  | 2025-09-17 | 2025-09-17 | 508T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35630424 | T3 DI MONTA VISTA-BURNS 14/116 RPL INSW | 93I
LC | 130986077 | 014/119 | T3 DI MONTA VISTA-BURNS 14/119 TOUCH | MOSSLNDG | ETL.7590.POLE.NWOD | 2025-03-17 | 2025-03-17 | 2025-05-10 | On-Time |  | 2025-09-17 | 2025-09-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW ACCH COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46498560 | T3 DI MONTA VISTA-BURNS 14/119 TOUCH | ICW
LC | 130986082 | 002/020 | T3 DI CASTRO VALLEY NEWARK 2/20 TOUCH | CONCORD | ETL.4450.TOWR | 2025-03-17 | 2025-03-17 | 2025-05-19 | On-Time |  | 2025-06-17 | 2025-09-17 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR3 PRTO AIR FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46494333 | T3 DI CASTRO VALLEY NEWARK 2/20 TOUCH | ICQ
LC | 130990236 | 000/011 | T3 DI VOLTA SOUTH 0/11 RPR ADSS | TABLEMTN | ETL.8300.POLE.NWOD | 2025-03-18 | 2025-03-17 | 2025-06-04 | On-Time |  | 2025-06-17 | 2025-09-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46494183 | T3 DI VOLTA SOUTH 0/11 RPR ADSS | ICW
LC | 130990239 | 39 | T3 MONTA VISTA BURNS 14/121 RPR SWTCH | MOSSLNDG | ETL.7590.SWIT | 2025-03-18 | 2025-03-17 | 2025-05-13 | On-Time |  | 2025-06-17 | 2025-09-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB DURA BRIN | Out of Adjustment | Switch | Repair | 46497618 | T3 DI MONTA VISTA BURNS 14/121 RPR SWTCH | ICW
LC | 130994404 | T-116 | T3 DI MDWY-SNT MRA T-116 RPR STRT | PISMOBCH | ETL.9240.TOWR | 2025-03-19 | 2025-03-17 | 2025-03-17 | TBC |  | 2025-09-17 | 2025-09-17 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46496102 | T3 DI MDWY-SNT MRA T-116 RPR STRT | ICQ
LC | 130994483 | 000/018 | T3 DI VOLTA SOUTH 0/18 TOUCH | TABLEMTN | ETL.8300.POLE.NWOD | 2025-03-19 | 2025-03-17 | 2025-06-04 | On-Time |  | 2025-09-17 | 2025-09-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46498711 | T3 DI VOLTA SOUTH 0/18 TOUCH | ICW
LC | 130994519 | 009/216 | T3 DI DRUM-GRAS VLY WEIMAR 9/216 RMV VEG | SACTO | ETL.6760.POLE.WOOD | 2025-03-19 | 2025-03-17 | 2025-03-17 | TBC |  | 2025-09-17 | 2025-09-17 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE SPCR OH TR3 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 128299704 | X008/038 | T2 EI DIABLO-MESA X008/038 COMPLETE | PISMOBCH | ETL.4620.INSL | 2024-03-18 | 2024-03-18 | 2025-03-25 | On-Time |  | 2025-09-18 | 2025-09-18 | 532 | TR2 | YES | E - Schd Compl Yr 0 | Closed | REGW INSP REMT SPCR ACCH COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35585666 | T2 EI DIABLO-MESA RPL INSS 7 LSTS | 93K
LC | 128300321 | 046/225 | T2 EI LAKEVLLE-SBRNTE #2 46/225 RPR INSS | CONCORD | ETL.4960.INSL | 2024-03-18 | 2024-03-18 | 2025-05-09 | On-Time |  | 2025-09-18 | 2025-09-18 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46403184 | T2 EI LAKEVLLE-SBRNTE #2 46/225 RPR INSS | ICS
LC | 128304046 | 006/048 | T2 DI IGNCO-ALTO-SLTO #1 6/48 BNT STEEL | LAKEVLLE | ETL.7160.TOWR | 2024-03-18 | 2024-03-18 | 2025-04-26 | On-Time |  | 2025-09-18 | 2025-09-18 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46289543 | T2 DI IGNCO-ALTO-SLTO #1 6/48 BNT STEEL | ICQ
LC | 128304207 | 051/003 | T2 TRINITY-MAP CRK 51/3 GO95 | EUREKA | ETL.8170.POLE.WOOD | 2024-03-18 | 2024-03-18 | 2025-06-19 | On-Time |  | 2025-09-18 | 2025-09-18 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR FIRE SPCR ACCM COMP OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35538394 | T2 TRINITY-MAP CRK 51/3 REFRAME | 93G
LC | 128322169 | 007/050 | T2 DI IGNC-ALTO-SLT #2 70/50 RPR CNDS | LAKEVLLE | ETL.7170.INSL.CERA | 2024-03-19 | 2024-03-18 | 2024-03-18 | TBC |  | 2025-09-18 | 2025-09-18 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW FIRE OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Conductor-Steel | Repair | 46403182 | T2 DI IGNC-ALTO-SLT #2 70/50 RPR CNDS | ICS
LC | 128322255 | 006/047 | T2 DI IGNC-ALTO-SLT #2 6/47 RPR INSS | LAKEVLLE | ETL.7170.INSL.CERA | 2024-03-19 | 2024-03-18 | 2025-05-01 | On-Time |  | 2025-09-18 | 2025-09-18 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46403181 | T2 DI IGNC-ALTO-SLT #2 6/47 RPR INSS | ICS
LC | 128389124 | 006/046 | T2 DI IGNCO-ALT-SLTO #1 6/46 RPR STRT | LAKEVLLE | ETL.7160.TOWR | 2024-03-29 | 2024-03-18 | 2025-04-26 | On-Time |  | 2025-09-18 | 2025-09-18 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46289542 | T2 DI IGNCO-ALT-SLTO #1 6/46 RPR STRT | ICQ
LC | 129556112 | 009/179 | T2 MONTA VISTA LOS GATOS 9/179 RPL STRW | METCALF | ETL.7610.POLE.WOOD | 2024-09-19 | 2024-09-18 | 2024-09-18 | TBC |  | 2025-09-18 | 2025-09-18 | 401 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR2 PRTO FRAR | Overloaded | GO95 Clear Infract-Wood | Replace | 35513224 | T2 EI MNTA VSTA-LS GTOS 8/163 RPL STRW | 93G
LC | 129556113 | 008/163 | T2 MONTA VISTA LOS GATOS 8/163 RPL STRW | METCALF | ETL.7610.POLE.WOOD | 2024-09-19 | 2024-09-18 | 2024-09-18 | TBC |  | 2025-09-18 | 2025-09-18 | 401 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR2 PRTO FRAB | Overloaded | GO95 Clear Infract-Wood | Replace | 35513224 | T2 EI MNTA VSTA-LS GTOS 8/163 RPL STRW | 93G
LC | 130989107 | 007/086 | T3 EI GRN VLLEY-CAMP VERS 7/086L RMV VEG | MOSSLNDG | ETL.1710.POLE.WDPS | 2025-03-18 | 2025-03-18 | 2025-06-18 | On-Time |  | 2025-09-18 | 2025-09-18 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR3 PRTO BRIN | Overgrown | Vegetation | Remove
LC | 130989177 | 012/101 | T3 CRESTA-RIO OSO 12/101 STAT HOLD | TABLEMTN | ETL.4590.TOWR | 2025-03-18 | 2025-03-18 | 2025-03-18 | TBC |  | 2025-06-18 | 2025-09-18 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW NONR OH FMOB TR3 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46505519 | T3 CRESTA-RIO OSO 12/101 STAT HOLD | ICQ
LC | 130989254 | 012/100 | T3 CRESTA-RIO OSO 12/100 STAT HOLD | TABLEMTN | ETL.4590.TOWR | 2025-03-18 | 2025-03-18 | 2025-03-18 | TBC |  | 2025-06-18 | 2025-09-18 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW NONR OH FMOB TR3 PRTO FRAB DURA BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46505522 | T3 CRESTA-RIO OSO 12/100 STAT HOLD | ICQ
LC | 130989871 | 007/064 | T3 WV MONTA VISTA-BURNS 7/64 INS DMPW | MOSSLNDG | ETL.7590.INSL.NCER | 2025-03-18 | 2025-03-18 | 2025-05-13 | On-Time |  | 2025-09-18 | 2025-09-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | Missing | Damper-Wood | Install | 46498561 | T3 WV MONTA VISTA-BURNS 7/64 INS DMPW | ICW
LC | 130989974 | 007/064 | T3 WV MONTA VISTA-BURNS 7/64R INS GYWW | MOSSLNDG | ETL.7590.POLE.STPS | 2025-03-18 | 2025-03-18 | 2025-05-13 | On-Time |  | 2025-09-18 | 2025-09-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO NTDE BRIN | Missing | Guy Wire-Wood | Install | 46510154 | T3 WV MONTA VISTA-BURNS 7/64R INS GYWW | ICW
LC | 130991493 | Z003/001 | T3NT FULTON-CALISTOGA Z3/1 TOUCH | LAKEVLLE | ETL.6880.POLE.NWOD | 2025-03-19 | 2025-03-18 | 2025-05-13 | On-Time |  | 2025-09-18 | 2025-09-18 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46503929 | T3NT FULTON-CALISTOGA Z3/1 TOUCH | ICQ
LC | 130994498 | 005/044 | T3 DI DRUM-RIO OSO #1 05/44 RPR OPGW | SACTO | ETL.1420.POLE.NWOD | 2025-03-19 | 2025-03-18 | 2025-05-05 | On-Time |  | 2025-06-18 | 2025-09-18 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46493353 | T3 DI DRUM-RIO OSO #1 05/44 RPR OPGW | ICS
LC | 130994510 | 015/130 | T3 DI MNTA VSTA-BRNS 15/130 RPR INSW | MOSSLNDG | ETL.7590.INSL.NCER | 2025-03-19 | 2025-03-18 | 2025-03-18 | TBC |  | 2025-09-18 | 2025-09-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW ACCL OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46497720 | T3 DI MNTA VSTA-BRNS 15/130 RPR INSW | ICW
LC | 130994517 | 010/240 | T3 DI DRM-GRSS VLLY-WMR 10/240 RPR JUMW | SACTO | ETL.6760.INSL.NCER | 2025-03-19 | 2025-03-18 | 2025-03-18 | TBC |  | 2025-09-18 | 2025-09-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW ACCL OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46496951 | T3 DI DRM-GRSS VLLY-WMR 10/240 RPR JUMW | ICW
LC | 130994518 | 010/240 | T3 DI DRM-GRSS VLLY-WMR 10/240 RPR GYWW | SACTO | ETL.6760.POLE.NWOD | 2025-03-19 | 2025-03-18 | 2025-03-18 | TBC |  | 2025-09-18 | 2025-09-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW ACCL OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46496952 | T3 DI DRM-GRSS VLLY-WMR 10/240 RPR GYWW | ICW
LC | 130997755 | 005/043 | T3 DI TIGER CREEK-ELECTRA 5/43 TOUCH | VICTOR | ETL.5780.TOWR | 2025-03-20 | 2025-03-18 | 2025-05-13 | On-Time |  | 2025-09-18 | 2025-09-18 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46505503 | T3 DI TIGER CREEK-ELECTRA 5/43 TOUCH | ICQ
LC | 131040118 | 007/064 | T3 WV MONTA VISTA-BURNS 7/64C INS GYWW | MOSSLNDG | ETL.7590.POLE.STPS | 2025-04-02 | 2025-03-18 | 2025-05-13 | On-Time |  | 2025-09-18 | 2025-09-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO NTDE BRIN | Missing | Guy Wire-Wood | Install | 46510153 | T3 WV MONTA VISTA-BURNS 7/64C INS GYWW | ICW
LC | 124528416 | 003/016A | T3NT EGL RK-FLTN-SLVRDO 3/16A JUMPR POLE | LAKEVLLE | ETL.4392.TOWR | 2022-09-19 | 2022-09-19 | 2024-10-24 | On-Time |  | 2025-09-19 | 2025-09-19 | 372 | TR3 | YES | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB XMPT TR3 PRTO FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Replace | 31616582 | T3 EAGLE RK-FLTN-SLVRDO 3/16A JUMPR POLE | 70Y
LC | 128305173 | 042/200 | T2 EI IGNACIO-SOBRNTE 42/200 RMV NEST | CONCORD | ETL.4920.TOWR | 2024-03-19 | 2024-03-19 | 2024-03-19 | TBC |  | 2025-09-19 | 2025-09-19 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46403186 | T2 EI IGNACIO-SOBRNTE 42/200 RMV NEST | ICS
LC | 128306321 | 041/196 | T2 IGNACIO-SOBRANTE 41/196 RMV NEST | CONCORD | ETL.4920.TOWR | 2024-03-19 | 2024-03-19 | 2024-03-19 | TBC |  | 2025-09-19 | 2025-09-19 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46403185 | T2 EI IGNACIO-SOBRANTE 41/196 RMV NEST | ICS
LC | 128308163 | 012/004 | T2 EI PHILO JCT-ELK 12/4 RPL STRW | WILLITS | ETL.7780.POLE.WOOD | 2024-03-19 | 2024-03-19 | 2024-03-19 | TBC |  | 2025-09-19 | 2025-09-19 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573316 | T2 EI PHILO JCT-ELK 12/4 RPL STRW | 70Y
LC | 129557756 | 012/082 | T2 CAYUCOS-CAMBRIA 012/082 CGI | PISMOBCH | ETL.8560.POLE.WOOD | 2024-09-19 | 2024-09-19 | 2025-04-18 | On-Time |  | 2024-12-19 | 2025-09-19 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW TNT CGI COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Customer Refusal
LC | 129557757 | 012/079 | T2 CAYUCOS-CAMBRIA 012/079 CGI | PISMOBCH | ETL.8560.POLE.WOOD | 2024-09-19 | 2024-09-19 | 2025-04-18 | On-Time |  | 2024-12-19 | 2025-09-19 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW TNT CGI COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Customer Refusal
LC | 129557806 | 012/080 | T2 CAYUCOS-CAMBRIA 012/080 CGI | PISMOBCH | ETL.8560.POLE.WOOD | 2024-09-19 | 2024-09-19 | 2025-04-18 | On-Time |  | 2024-12-19 | 2025-09-19 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW TNT COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Customer Refusal
LC | 129557807 | 013/086 | T2 CAYUCOS-CAMBRIA 013/086 CGI | PISMOBCH | ETL.8560.POLE.WOOD | 2024-09-19 | 2024-09-19 | 2025-04-18 | On-Time |  | 2024-12-19 | 2025-09-19 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW TNT CGI COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Customer Refusal
LC | 129557808 | 013/087 | T2 CAYUCOS-CAMBRIA 013/087 CGI | PISMOBCH | ETL.8560.POLE.WOOD | 2024-09-19 | 2024-09-19 | 2025-04-18 | On-Time |  | 2024-12-19 | 2025-09-19 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW TNT CGI COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Customer Refusal
LC | 129557809 | 012/081 | T2 CAYUCOS-CAMBRIA 012/081 CGI | PISMOBCH | ETL.8560.POLE.WOOD | 2024-09-19 | 2024-09-19 | 2025-04-18 | On-Time |  | 2024-12-19 | 2025-09-19 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW TNT CGI COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Customer Refusal
LC | 129557811 | 014/091 | T2 CAYUCOS-CAMBRIA 014/091 CGI | PISMOBCH | ETL.8560.POLE.WOOD | 2024-09-19 | 2024-09-19 | 2025-04-18 | On-Time |  | 2024-12-19 | 2025-09-19 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW TNT CGI COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Customer Refusal
LC | 129557820 | 013/085 | T2 CAYUCOS-CAMBRIA 013/085 CGI | PISMOBCH | ETL.8560.POLE.WOOD | 2024-09-19 | 2024-09-19 | 2025-04-18 | On-Time |  | 2024-12-19 | 2025-09-19 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW TNT CGI COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Customer Refusal
LC | 130991923 | 003/012 | T3 BRIDGEVILLE-GARBERVILLE 3/12 CGI | EUREKA | ETL.6220.POLE.WOOD | 2025-03-19 | 2025-03-19 | 2025-03-19 | TBC |  | 2025-06-19 | 2025-09-19 | 625 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW TNT CGI OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | Land/Enviro Issue | Other | Access Issue | 46506040 | T3 BRIDGEVILLE-GARBERVILLE 3/12 CGI | ICH
LC | 130993620 | 007/064 | T3 WV MONTA VISTA-BURNS 7/64L INS GYWW | MOSSLNDG | ETL.7590.POLE.STPS | 2025-03-19 | 2025-03-19 | 2025-05-13 | On-Time |  | 2025-09-19 | 2025-09-19 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO NTDE BRIN | Missing | Guy Wire-Wood | Install | 46498563 | T3 WV MONTA VISTA-BURNS 7/64L INS GYWW | ICW
LC | 130994400 | 014/125 | T3 DI MONTA VISTA-BURNS-14/125 RPR JUMW | MOSSLNDG | ETL.7590.INSL.NCER | 2025-03-19 | 2025-03-19 | 2025-03-19 | TBC |  | 2025-09-19 | 2025-09-19 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46497721 | T3 DI MONTA VISTA-BURNS-14/125 RPR JUMW | ICW
LC | 130997618 | 003/036 | T3 DI IGNAGIO BOLINAS #1 3/36L RPL HRDD | LAKEVLLE | ETL.7140.POLE.STPS | 2025-03-20 | 2025-03-19 | 2025-03-19 | TBC |  | 2025-09-19 | 2025-09-19 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace | 46499102 | T3 DI IGNAGIO BOLINAS #1 3/36L RPL HRDD | ICW
LC | 130997723 | 047/268 | T3 DI TEMBLOR-SLO 047/268 TOUCH | PISMOBCH | ETL.3960.TOWR | 2025-03-20 | 2025-03-19 | 2025-06-03 | On-Time |  | 2025-09-19 | 2025-09-19 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46496107 | T3 DI TEMBLOR-SLO 047/268 TOUCH | ICQ
LC | 131008078 | 000/003 | T3 DI VOLTA-SOUTH 00/03 COTTER | TABLEMTN | ETL.8300.INSL.NCER | 2025-03-24 | 2025-03-19 | 2025-06-04 | On-Time |  | 2025-09-19 | 2025-09-19 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46498712 | T3 DI VOLTA-SOUTH 00/03 COTTER | ICW
LC | 131008189 | 002/033 | T3 DI IGNCIO-BLNS #1 2/33 COTTER | LAKEVLLE | ETL.7140.INSL.NCER | 2025-03-24 | 2025-03-19 | 2025-03-19 | TBC |  | 2025-09-19 | 2025-09-19 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW ACCL OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46499101 | T3 DI IGNCIO-BLNS #1 2/33 COTTER | ICW
LC | 131008216 | 004/039 | T3 DI DRM-RIO OSO #1 4/39 RPR OPGW | SACTO | ETL.1420.POLE.NWOD | 2025-03-24 | 2025-03-19 | 2025-05-05 | On-Time |  | 2025-09-19 | 2025-09-19 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46495045 | T3 DI DRM-RIO OSO #1 4/39 RPR OPGW | ICS
LC | 131008351 | 043/244 | T3 DI TEMBLOR-SL OBSPO 43/244 RMV VEG | PISMOBCH | ETL.3960.TOWR | 2025-03-24 | 2025-03-19 | 2025-03-19 | TBC |  | 2025-09-19 | 2025-09-19 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 128366707 | 011/078 | T2 DI IGNCIO-ALT-SLTO #2 11/078 RPR CNDS | LAKEVLLE | ETL.7170.INSL.NCER | 2024-03-25 | 2024-03-20 | 2025-05-01 | On-Time |  | 2025-09-20 | 2025-09-20 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Conductor-Steel | Repair | 46403424 | T2 DI IGNCIO-ALT-SLTO #2 11/078 RPR CNDS | ICS
LC | 128389153 | 008/062 | T2 DI TRNTY-CTTNWD 008/062R RPL POLE | TABLEMTN | ETL.4040.POLE.WDPS | 2024-03-29 | 2024-03-20 | 2024-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572433 | T2 DI TRNTY-CTTNWD 008/062R RPL POLE | 70Y
LC | 128389155 | 008/062 | T2 DI TRNTY-CTTNWD 008/062L RPL POLE | TABLEMTN | ETL.4040.POLE.WDPS | 2024-03-29 | 2024-03-20 | 2024-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 372 | TR2 | YES | E - Schd Compl Yr 0 | Open | POHW OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572433 | T2 DI TRNTY-CTTNWD 008/062R RPL POLE | 70Y
LC | 128395528 | 008/068 | T2 DI TRNTY-CTTNWD 008/068R RPL POLE | TABLEMTN | ETL.4040.POLE.WDPS | 2024-03-31 | 2024-03-20 | 2024-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572430 | T2 DI TRNTY-CTTNWD 008/068R RPL POLE | 70Y
LC | 128395534 | 003/009 | T2 DI LWR LK-HMSTK 003/009 RPL HRDD | WILLITS | ETL.1481.POLE.WOOD | 2024-03-31 | 2024-03-20 | 2025-05-06 | On-Time |  | 2025-09-20 | 2025-09-20 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46333921 | T2 DI LWR LK-HMSTK 003/009 RPL HRDD | ICW
LC | 129612486 | 012/128 | T3 WV IGNACIO-BOLINAS #1 12/128 RPL HRDW | LAKEVLLE | ETL.7140.POLE.NWOD | 2024-10-01 | 2024-09-30 | 2024-09-30 | TBC |  | 2025-09-20 | 2025-09-20 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB XMPT TR3 PRTO FRAB NTDE | Missing | Hardware-Wood | Install | 46345553 | T3 WV IGNACIO-BOLINAS #1 12/128 RPL HRDW | ICW
LC | 130995717 | 006/084 | T3 GRN VLEY-CAMP EVRS 06/084L ANTI SPLIT | MOSSLNDG | ETL.1710.POLE.WDPS | 2025-03-20 | 2025-03-20 | 2025-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46505757 | T3 GRN VLEY-CAMP EVRS 06/084L ANTI SPLIT | ICW
LC | 130996896 | 003/024 | T3 DORADO-MISSOURI FLT #2 3/024 RPL COND | SACTO | ETL.1540.INSL.CERA | 2025-03-20 | 2025-03-20 | 2025-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 531 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW OTHR OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Conductor-Steel | Replace | 35633481 | T3 EL DORADO-MISSRI FLT #2 1/14 RPL COND | 93C
LC | 130996909 | 003/024 | T3 DORADO-MISSOURI FLT #1 3/024 RPL COND | SACTO | ETL.1530.INSL.CERA | 2025-03-20 | 2025-03-20 | 2025-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 531 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW OTHR OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Conductor-Steel | Replace | 35633239 | T3 EL DORADO-MISSRI FLT #1 1/14 RPL COND | 93C
LC | 130996959 | 001/014 | T3 EL DORADO-MISSRI FLT #1 1/14 RPL COND | SACTO | ETL.1530.INSL.NCER | 2025-03-20 | 2025-03-20 | 2025-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 531T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW CREW CLR OH FMOB TR3 PRTO DURA BRIN | No Good/Out of Stdrd | Conductor-Steel | Replace | 35633239 | T3 EL DORADO-MISSRI FLT #1 1/14 RPL COND | 93C
LC | 130997031 | 001/014 | T3 EL DORADO-MISSRI FLT #2 1/14 RPL COND | SACTO | ETL.1540.INSL | 2025-03-20 | 2025-03-20 | 2025-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 531T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Conductor-Steel | Replace | 35633481 | T3 EL DORADO-MISSRI FLT #2 1/14 RPL COND | 93C
LC | 130997032 | 000/010 | T3 TNT KILARC-DESCHUTES 0/10 RPL POLE | TABLEMTN | ETL.7300.POLE.WOOD | 2025-03-20 | 2025-03-20 | 2025-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW TNT OH FMOB TR3 PRTO FRAB BRIN | Rotten | Structure-Wood | Replace | 35624300 | T3 TNT KILARC-DESCHUTES 0/10 RPL POLE | 70Y
LC | 130997656 | 010/106 | T3 GRN VLEY-CAMP EVERS 10/106R RPR GYWW | MOSSLNDG | ETL.1710.POLE.STPS | 2025-03-20 | 2025-03-20 | 2025-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46525767 | T3 GRN VLEY-CAMP EVERS 10/106R RPR GYWW | ICW
LC | 130997657 | 010/106 | T3 GRN VLEY-CAMP EVERS 10/106R RMV VEG | MOSSLNDG | ETL.1710.POLE.STPS | 2025-03-20 | 2025-03-20 | 2025-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO BRIN | Overgrown | Vegetation | Remove
LC | 130997749 | 008/159 | T3 KESWICK-CASCADE 008/159C RPL ANCW | TABLEMTN | ETL.7260.POLE.WDPS | 2025-03-20 | 2025-03-20 | 2025-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 637T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP REMT CLR ACCM OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35631867 | T3 KESWICK-CASCADE 008/159C RPL ANCW | 93E
LC | 131008220 | 008/071B | T3 DI DRUM-RIO OSO #1 8/071B RPR OPGW | SACTO | ETL.1420.POLE.NWOD | 2025-03-24 | 2025-03-20 | 2025-05-05 | On-Time |  | 2025-09-20 | 2025-09-20 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46495044 | T3 DI DRUM-RIO OSO #1 8/071B RPR OPGW | ICS
LC | 131016958 | 005/048 | T3 DI MONTA VST BURNS 5/48 RPL INSW | MOSSLNDG | ETL.7590.INSL | 2025-03-26 | 2025-03-20 | 2025-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 508T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35630421 | T3 DI MONTA VST BURNS 5/48 RPL INSW | 93I
LC | 131017025 | 008/195 | T3 RE DRUM-GRS VLY 8/195 RPL INSW | SACTO | ETL.6760.INSL.NCER | 2025-03-26 | 2025-03-20 | 2025-06-17 | On-Time |  | 2025-09-20 | 2025-09-20 | 508T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35633488 | T3 RE DRUM-GRS VLY 8/195 RPL INSW | 93I
LC | 131267183 | 008/159 | T3 KESWICK-CASCADE 008/159L RPL ANCW | TABLEMTN | ETL.7260.POLE.WDPS | 2025-05-21 | 2025-03-20 | 2025-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 637T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW INSP REMT CLR ACCM OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35631867 | T3 KESWICK-CASCADE 008/159C RPL ANCW | 93E
LC | 131267188 | 008/159 | T3 KESWICK-CASCADE 008/159R RPL ANCW | TABLEMTN | ETL.7260.POLE.WDPS | 2025-05-21 | 2025-03-20 | 2025-03-20 | TBC |  | 2025-09-20 | 2025-09-20 | 637T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW INSP REMT CLR ACCM OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35631867 | T3 KESWICK-CASCADE 008/159C RPL ANCW | 93E
LC | 128337503 | 015/087 | T2 EI BAHIA-MORAGA 15/87 RPL INSS | CONCORD | ETL.4340.INSL.NCER | 2024-03-21 | 2024-03-21 | 2024-03-21 | TBC |  | 2025-09-21 | 2025-09-21 | 532T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575029 | T2 EI BAHIA-MORAGA RPL INSS IN 2 TWRS | 93K
LC | 128342247 | 030/003A | T2 TRINITY-MPL CRK 30/3A GO95 RPL | EUREKA | ETL.8170.POLE.WOOD | 2024-03-21 | 2024-03-21 | 2024-03-21 | TBC |  | 2025-09-21 | 2025-09-21 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR FIRE OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35539221 | T2 TRINITY-MPL CRK 30/3A OVERLOADED POLE | 93G
LC | 128342350 | 014/083 | T2 BAHIA-MORAGA 014/083 RPL HNGT | CONCORD | ETL.4340.INSL.NCER | 2024-03-21 | 2024-03-21 | 2024-03-21 | TBC |  | 2025-09-21 | 2025-09-21 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46286748 | T2 EI BAHIA-MORAGA 014/083 HANGER | ICQ
LC | 128343172 | 014/081 | T2 BAHIA-MORAGA 014/081 RPL HNGT | CONCORD | ETL.4340.INSL.NCER | 2024-03-21 | 2024-03-21 | 2024-03-21 | TBC |  | 2025-09-21 | 2025-09-21 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46286747 | T2 EI BAHIA-MORAGA 014/081 HANGER | ICQ
LC | 128343191 | 014/080 | T2 BAHIA-MORAGA 014/080 RPL HNGT | CONCORD | ETL.4340.INSL | 2024-03-21 | 2024-03-21 | 2024-03-21 | TBC |  | 2025-09-21 | 2025-09-21 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP REMT OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46286746 | T2 EI BAHIA-MORAGA 014/080 HANGER | ICQ
LC | 128343470 | 038/002 | T2 EI RIO DLL JCT-BRDGVLL 38/2L RPR INSW | EUREKA | ETL.7850.INSL.NCER | 2024-03-21 | 2024-03-21 | 2025-06-21 | On-Time |  | 2025-09-21 | 2025-09-21 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46345705 | T2 EI RIO DLL JCT-BRDGVLL 38/2L RPR INSW | ICW
LC | 128344437 | 013/078 | T2 BAHIA-MORAGA 13/78 HANGER | CONCORD | ETL.4340.INSL.NCER | 2024-03-21 | 2024-03-21 | 2024-03-21 | TBC |  | 2025-09-21 | 2025-09-21 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46286745 | T2 EI BAHIA-MORAGA 013/078 HANGER | ICQ
LC | 128429917 | A001/003 | T2 DI FULTON-PUEBLO :001/003 RPR POLE | LAKEVLLE | ETL.1600.POLE.WOOD | 2024-04-02 | 2024-03-21 | 2025-04-16 | On-Time |  | 2025-09-21 | 2025-09-21 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46403455 | T2 DI FULTON-PUEBLO :001/003 RPR POLE | ICW
LC | 131000577 | 000/009 | T3 EI CNTRVL-TBL MTN-ORVLE 0/9 RPL STRW | TABLEMTN | ETL.6330.POLE.WOOD | 2025-03-21 | 2025-03-21 | 2025-03-21 | TBC |  | 2025-09-21 | 2025-09-21 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35630624 | T3 EI CNTRVL-TBL MTN-ORVLE 0/9 RPL STRW | 70Y
LC | 131001735 | 003/065 | T3 CNTRVLLE-TBLE MTN-ORVLLE 3/65 RMV VEG | TABLEMTN | ETL.6330.POLE.WOOD | 2025-03-21 | 2025-03-21 | 2025-03-21 | TBC |  | 2028-03-21 | 2025-09-21 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 131001738 | 003/065 | T3 CNTRVLLE-TBLE MTN-ORVLLE 3/65 COTTER | TABLEMTN | ETL.6330.INSL.CERA | 2025-03-21 | 2025-03-21 | 2025-03-21 | TBC |  | 2025-09-21 | 2025-09-21 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46498714 | T3 CNTRVLLE-TBLE MTN-ORVLLE 3/65 COTTER | ICW
LC | 131017052 | 005/050 | T3 DI MONTA VISTA-BURNS 5/50 RPR CNDW | MOSSLNDG | ETL.7590.INSL.NCER | 2025-03-26 | 2025-03-21 | 2025-05-08 | On-Time |  | 2025-09-21 | 2025-09-21 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46504086 | T3 DI MONTA VISTA-BURNS 5/50 RPR CNDW | ICW
LC | 128350747 | 039/181 | T2 EI LAKEVLLE-SBRNTE #2 39/181 RPL INSS | CONCORD | ETL.4960.INSL | 2024-03-22 | 2024-03-22 | 2025-05-06 | On-Time |  | 2025-09-22 | 2025-09-22 | 532T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35608525 | T2 EI LAKEVLLE-SBRNTE #2 39/181 RPL INSS | 93K
LC | 128351609 | 038/180 | T2 LAKEVLLE-SBRNTE #2 38/180 RMV NEST | CONCORD | ETL.4920.TOWR | 2024-03-22 | 2024-03-22 | 2024-03-22 | TBC |  | 2025-09-22 | 2025-09-22 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46403456 | T2 EI LAKEVLLE-SBRNTE #2 38/180 RMV NEST | ICS
LC | 128351967 | 011/068 | T2 EI BAHIA-MORAGA 011/068 HANGER | CONCORD | ETL.4340.INSL | 2024-03-22 | 2024-03-22 | 2024-03-22 | TBC |  | 2025-09-22 | 2025-09-22 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46286750 | T2 EI BAHIA-MORAGA 011/068 HANGER | ICQ
LC | 128351968 | 011/068 | T2 EI BAHIA-MORAGA 011/068 RPL INSS | CONCORD | ETL.4340.INSL | 2024-03-22 | 2024-03-22 | 2024-03-22 | TBC |  | 2025-09-22 | 2025-09-22 | 532 | TR2 | YES | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35575029 | T2 EI BAHIA-MORAGA RPL INSS IN 2 TWRS | 93K
LC | 128353456 | X007/031 | T2 DI DIABLO-MESA X7/31 RPL INSS | PISMOBCH | ETL.4620.INSL.CERA | 2024-03-23 | 2024-03-22 | 2025-03-25 | On-Time |  | 2025-09-22 | 2025-09-22 | 532 | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35585666 | T2 EI DIABLO-MESA RPL INSS 7 LSTS | 93K
LC | 128366368 | 035/203 | T2 EXCHQR INDN FLT 35/203 BNT STEEL | FRESNO | ETL.8650.TOWR | 2024-03-25 | 2024-03-22 | 2024-03-22 | TBC |  | 2025-09-22 | 2025-09-22 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW FIRE OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46292637 | T2 DI EXCHQR INDN FLT 35/203 BNT STEEL | ICQ
LC | 129574622 | 000/006 | T2 GRANITE ROCK TAP 00/06 COMPLETE | MOSSLNDG | ETL.8311.INSL.CERA | 2024-09-23 | 2024-09-23 | 2025-04-05 | On-Time |  | 2025-09-23 | 2025-09-23 | 622 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO | Contaminated | Insulator | Ground Wash | 46327628 | T2 GRANITE ROCK TAP 00/06 WASH INSW | ICD
LC | 129575939 | 004/032 | T2 DI MORAGA CLRMNT #1 4/32 RPL INSS | CONCORD | ETL.2700.INSL | 2024-09-23 | 2024-09-23 | 2024-09-23 | TBC |  | 2025-09-23 | 2025-09-23 | 532T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW IR OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Replace | 35620844 | T2 DI MORAGA CLRMNT #1 4/32 RPL INSS | 93K
LC | 131007681 | 001/005 | T3 DIABLO-MIDWAY #3 1/5 RPR GYWT | PISMOBCH | ETL.5980.TOWR | 2025-03-24 | 2025-03-24 | 2025-03-24 | TBC |  | 2025-09-24 | 2025-09-24 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 PRTO CLMB FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Tower | Replace | 46505370 | T3 DIABLO-MIDWAY #3 1/5 RPR GYWT | ICQ
LC | 131007811 | 002/049 | T3NT CNTRVILLE-TABLE MTN 2/49 RMV VEG | TABLEMTN | ETL.6330.POLE.NWOD | 2025-03-24 | 2025-03-24 | 2025-03-24 | TBC |  | 2028-03-24 | 2025-09-24 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 131008393 | 007/073 | T3 DRUM-HIGGINS 007/073 RPR JUMS | SACTO | ETL.4393.INSL.NCER | 2025-03-24 | 2025-03-24 | 2025-03-24 | TBC |  | 2025-09-24 | 2025-09-24 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46505508 | T3 DRUM-HIGGINS 007/073 RPR JUMS | ICS
LC | 131017178 | 008/081 | T3 DRUM HIGGINS+ 8/81 TOUCH | SACTO | ETL.4393.TOWR | 2025-03-26 | 2025-03-24 | 2025-06-18 | On-Time |  | 2025-09-24 | 2025-09-24 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46499039 | T3 DRUM HIGGINS+ 8/81 TOUCH | ICQ
LC | 131032190 | 009/091 | T3 DRUM-HIGGINS 09/91 RPR STRW | SACTO | ETL.4393.POLE.WDPS | 2025-03-31 | 2025-03-24 | 2025-03-24 | TBC |  | 2025-09-24 | 2025-09-24 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46507592 | T3 DRUM-HIGGINS 09/91 RPR STRW | ICW
LC | 128365039 | 008/151 | T2 TEJON-LEBEC 008/151 RPL HRDW | MIDWAY | ETL.9250.POLE.NWOD | 2024-03-25 | 2024-03-25 | 2025-05-09 | On-Time |  | 2025-09-25 | 2025-09-25 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB XMPT TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Hardware-Wood | Replace | 46302363 | T2 TEJON-LEBEC 008/151 RPL HRDW | ICW
LC | 129587587 | 009/153 | T2 WV TEJON-LEBEC 09/153 TOUCH | MIDWAY | ETL.9250.POLE.NWOD | 2024-09-25 | 2024-09-25 | 2025-05-05 | On-Time |  | 2025-03-25 | 2025-09-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46489440 | T2 WV TEJON-LEBEC 09/153 TOUCH | ICW
LC | 129605694 | 025/277 | T3 WV IGNACIO-BOLINAS #2 25/277 INS DMPW | LAKEVLLE | ETL.7180.INSL.CERA | 2024-09-30 | 2024-09-30 | 2024-09-30 | TBC |  | 2025-09-25 | 2025-09-25 | 630 | TR3 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB XMPT TR3 PRTO FRAB NTDE BRIN | Missing | Damper-Wood | Install | 46381775 | T3 WV IGNACIO-BOLINAS #2 25/277 INS DMPW | ICW
LC | 131009026 | 019/005C | T3 EI MI-WUK-CURTIS 19/005C RPR GYWW | VICTOR | ETL.1073.POLE.NWOD | 2025-03-25 | 2025-03-25 | 2025-06-27 | On-Time |  | 2025-09-25 | 2025-09-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD NOAC ACCL COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46496208 | T3 EI MI-WUK-CURTIS 19/005C RPR GYWW | ICW
LC | 131009058 | 019/005A | T3 EI MI-WUK-CURTIS 19/005A RPR GYWW | VICTOR | ETL.1073.POLE.NWOD | 2025-03-25 | 2025-03-25 | 2025-06-27 | On-Time |  | 2025-09-25 | 2025-09-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD NOAC ACCL COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46496209 | T3 EI MI-WUK-CURTIS 19/005A RPR GYWW | ICW
LC | 131009062 | 019/005B | T3 EI MI-WUK-CURTIS 19/005B RPR GYWW | VICTOR | ETL.1073.POLE.NWOD | 2025-03-25 | 2025-03-25 | 2025-06-27 | On-Time |  | 2025-09-25 | 2025-09-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP RESD NOAC ACCL COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46496210 | T3 EI MI-WUK-CURTIS 19/005B RPR GYWW | ICW
LC | 131009176 | 019/004 | T3 MI-WUK-CURTIS 019/004L RPR GYWW | VICTOR | ETL.1073.POLE.STPS | 2025-03-25 | 2025-03-25 | 2025-03-25 | TBC |  | 2025-09-25 | 2025-09-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46499421 | T3 MI-WUK-CURTIS 019/004L RPR GYWW | ICW
LC | 131010201 | 019/010C | T3 EI MI-WUK-CURTIS 19/010C RPR COND | VICTOR | ETL.1073.INSL.NCER | 2025-03-25 | 2025-03-25 | 2025-03-25 | TBC |  | 2025-09-25 | 2025-09-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP RESD SWRK CLR ACCM OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46496211 | T3 EI MI-WUK-CURTIS 19/010C RPR COND | ICW
LC | 131016990 | Z013/006 | T3 FULTON-CALISTOGA Z013/006 RPR JUMW | LAKEVLLE | ETL.6880.INSL.NCER | 2025-03-26 | 2025-03-25 | 2025-03-25 | TBC |  | 2025-09-25 | 2025-09-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46507839 | T3 FULTON-CALISTOGA Z013/006 RPR JUMW | ICW
LC | 131016991 | 000/003 | T3 DI BRUNSWICK #1 TAP 0/003 BNT STEEL | SACTO | ETL.1422.TOWR | 2025-03-26 | 2025-03-25 | 2025-06-23 | On-Time |  | 2025-09-25 | 2025-09-25 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46505477 | T3 DI BRUNSWICK #1 TAP 0/003 BNT STEEL | ICQ
LC | 131017146 | 009/131 | T3 DI MIDDLE FORK #1 9/131 RPR JMPW | SACTO | ETL.8405.INSL.NCER | 2025-03-26 | 2025-03-25 | 2025-03-25 | TBC |  | 2025-09-25 | 2025-09-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46503818 | T3 DI MIDDLE FORK #1 9/131 RPR JMPW | ICW
LC | 131017262 | 007/065 | T3 MIDDLE FK GOLD HILL 7/65 RPR JUMS | SACTO | ETL.5140.INSL.NCER | 2025-03-26 | 2025-03-25 | 2025-05-10 | On-Time |  | 2025-09-25 | 2025-09-25 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46503819 | T3 MIDDLE FK GOLD HILL 7/65 RPR JUMS | ICS
LC | 131017280 | 024/099 | T3 DI EXCHQUR INDN FLT 24/099 RPR JUMS | FRESNO | ETL.8650.INSL.NCER | 2025-03-26 | 2025-03-25 | 2025-03-25 | TBC |  | 2025-09-25 | 2025-09-25 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46498659 | T3 DI EXCHQUR INDN FLT 24/099 RPR JUMS | ICS
LC | 131032289 | 001/016A | T3 DRUM-HIGGINS 001/016A RPL STRW | SACTO | ETL.4393.POLE.WOOD | 2025-03-31 | 2025-03-25 | 2025-03-25 | TBC |  | 2025-09-25 | 2025-09-25 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35633480 | T3 DRUM-HIGGINS 001/016A RPL STRW | 70Y
LC | 131032311 | 001/028 | T3 PINE GROVE TAP 1/28 RPR GYWW | VICTOR | ETL.8351.POLE.NWOD | 2025-03-31 | 2025-03-25 | 2025-06-07 | On-Time |  | 2025-09-25 | 2025-09-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46499420 | T3 PINE GROVE TAP 1/28 RPR GYWW | ICW
LC | 131032318 | 005/019 | T3 EAGLE RCK FLTN SLVR 5/19 RPR STRT | LAKEVLLE | ETL.4392.TOWR | 2025-03-31 | 2025-03-25 | 2025-03-25 | TBC |  | 2025-09-25 | 2025-09-25 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46505455 | T3 EAGLE RCK FLTN SLVR 5/19 RPR STRT | ICQ
LC | 131032340 | 001/016B | T3 DRUM-HIGGINS 001/016B RPL STRW | SACTO | ETL.4393.POLE.WOOD | 2025-03-31 | 2025-03-25 | 2025-03-25 | TBC |  | 2025-09-25 | 2025-09-25 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35633480 | T3 DRUM-HIGGINS 001/016A RPL STRW | 70Y
LC | 131032342 | 001/016C | T3 DRUM-HIGGINS 001/016C RPL STRW | SACTO | ETL.4393.POLE.WOOD | 2025-03-31 | 2025-03-25 | 2025-03-25 | TBC |  | 2025-09-25 | 2025-09-25 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35633480 | T3 DRUM-HIGGINS 001/016A RPL STRW | 70Y
LC | 131032356 | 029/219 | T3 MIDDLE FORK GOLD HILL 29/219L TOUCH | SACTO | ETL.5140.POLE.STPS | 2025-03-31 | 2025-03-25 | 2025-03-25 | TBC |  | 2025-09-25 | 2025-09-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46503980 | T3 MIDDLE FORK GOLD HILL 29/219L TOUCH | ICW
LC | 131032358 | 009/128 | T3 MIDDLEFORK #1 9/128 RPR JUMW | SACTO | ETL.8405.INSL.NCER | 2025-03-31 | 2025-03-25 | 2025-03-25 | TBC |  | 2025-09-25 | 2025-09-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46503820 | T3 MIDDLEFORK #1 9/128 RPR JUMW | ICW
LC | 131057269 | 008/065 | T3 TIGER CRK VALLEY SPNGS 8/065 TOUCH | VICTOR | ETL.5790.TOWR | 2025-04-07 | 2025-03-25 | 2025-05-12 | On-Time |  | 2025-09-25 | 2025-09-25 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46505521 | T3 TIGER CRK VALLEY SPNGS 8/065 TOUCH | ICQ
LC | 131057385 | 001/008 | T3 BRUNSWICK #2 TAP 1/008 RPR JUMS | SACTO | ETL.1431.INSL.CERA | 2025-04-07 | 2025-03-25 | 2025-03-25 | TBC |  | 2025-09-25 | 2025-09-25 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46503823 | T3 BRUNSWICK#1 TAP 1/008 RPR JUMS | ICS
LC | 131062151 | 004/071 | T3 SISQUOC-GAREY 004/071 RPR GYWW | PISMOBCH | ETL.3690.POLE.WOOD | 2025-04-08 | 2025-03-25 | 2025-05-20 | On-Time |  | 2025-09-25 | 2025-09-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46505997 | T3 SISQUOC-GAREY 004/071 RPR GYWW | ICW
LC | 128368299 | 018/097 | T2 VACA-BAHIA 18/97 RPL INSS | SACTO | ETL.5810.INSL | 2024-03-26 | 2024-03-26 | 2024-03-26 | TBC |  | 2025-09-26 | 2025-09-26 | 532 | TR2 | YES | E - Schd Compl Yr 0 | Open | REGW OH FMOB XMPT TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574253 | T2 DI VACA-BAHIA RPL INSS 2 TWRS | 93K
LC | 128368370 | 005/003 | T2 PHILO JCT-ELK 05/003 RPR STRW | WILLITS | ETL.7780.POLE.WOOD | 2024-03-26 | 2024-03-26 | 2024-03-26 | TBC |  | 2025-09-26 | 2025-09-26 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW COMP OH FMOB XMPT TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Structure-Wood | Repair | 46333933 | T2 PHILO JCT-ELK 05/003 RPR STRW | ICW
LC | 128369352 | :001/002 | T2 CARIBOU #2 :1/2 GO95 RPL | TABLEMTN | ETL.6280.POLE.WOOD | 2024-03-26 | 2024-03-26 | 2025-06-23 | On-Time |  | 2025-09-26 | 2025-09-26 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35540746 | T2 CARIBOU #2 :1/2 GO95 RPL | 93G
LC | 128369355 | :004/008 | T2 CARIBOU #2 :4/8 GO95 RPL | TABLEMTN | ETL.6280.POLE.WOOD | 2024-03-26 | 2024-03-26 | 2025-06-22 | On-Time |  | 2025-09-26 | 2025-09-26 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35540744 | T2 CARIBOU #2 :4/8 GO95 RPL | 93G
LC | 128369357 | :004/010 | T2 CARIBOU #2 :4/10 GO95 RPL | TABLEMTN | ETL.6280.POLE.WOOD | 2024-03-26 | 2024-03-26 | 2025-06-22 | On-Time |  | 2025-09-26 | 2025-09-26 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35540745 | T2 CARIBOU #2 :4/10 GO95 RPL | 93G
LC | 128388452 | 007/000 | T2 DI LYTNVLL-CVLO 007/0L RPL POLE | WILLITS | ETL.7390.POLE.WDPS | 2024-03-29 | 2024-03-26 | 2025-06-11 | On-Time |  | 2025-09-26 | 2025-09-26 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574141 | T2 DI LYTNVLL-CVLO 007/0L RPL POLE | 70Y
LC | 128388454 | 007/000 | T2 DI LYTNVLL-CVLO 7/0C RPL POLE | WILLITS | ETL.7390.POLE.WDPS | 2024-03-29 | 2024-03-26 | 2025-06-11 | On-Time |  | 2025-09-26 | 2025-09-26 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW COMP OH XMPT TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574141 | T2 DI LYTNVLL-CVLO 007/0L RPL POLE | 70Y
LC | 128388505 | 007/000 | T2 DI LYTNVLL-CVLO 7/0R RPL POLE | WILLITS | ETL.7390.POLE.WDPS | 2024-03-29 | 2024-03-26 | 2024-03-26 | TBC |  | 2025-09-26 | 2025-09-26 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | POHW COMP OH XMPT TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574141 | T2 DI LYTNVLL-CVLO 007/0L RPL POLE | 70Y
LC | 131016112 | 001/023 | T3 IGNACIO-BOLINAS #2 001/023 RPR INSW | LAKEVLLE | ETL.7180.INSL.NCER | 2025-03-26 | 2025-03-26 | 2025-03-26 | TBC |  | 2025-09-26 | 2025-09-26 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46507961 | T3 IGNACIO-BOLINAS #2 001/023 RPR INSW | ICW
LC | 131016148 | ?002/005 | T3NT SNTH LN-HLF MN BAY ?2/5 RPR STRW | METCALF | ETL.7212.POLE.NWOD | 2025-03-26 | 2025-03-26 | 2025-03-26 | TBC |  | 2028-03-26 | 2025-09-26 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Repair
LC | 131016412 | ?002/006 | T3 SNTH LN-HLF MN BAY ?2/6 RPR GYWW | METCALF | ETL.7212.POLE.NWOD | 2025-03-26 | 2025-03-26 | 2025-04-22 | On-Time |  | 2025-09-26 | 2025-09-26 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46508046 | T3 SNTH LN-HLF MN BAY ?2/6 RPR GYWW | ICW
LC | 131017164 | :004/016 | T3 EAGLE RCK-FLTN-SLVRD :4/16 RPL INSS | LAKEVLLE | ETL.4392.INSL.CERA | 2025-03-26 | 2025-03-26 | 2025-03-26 | TBC |  | 2025-09-26 | 2025-09-26 | 532T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace | 35642406 | T3 EAGLE RCK-FLTN-SLVRD :4/16 RPL INSS | 93K
LC | 131017317 | 017/147 | T3 DRUM-HIGGINS+ 17/147 TOUCH | SACTO | ETL.4393.TOWR | 2025-03-26 | 2025-03-26 | 2025-06-23 | On-Time |  | 2025-09-26 | 2025-09-26 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46507767 | T3 DRUM-HIGGINS+ 17/147 TOUCH | ICQ
LC | 131021414 | 127 | T3 DUTCH FLAT #2 TAP 0/1 RPR JUMS | SACTO | ETL.1421.SWIT | 2025-03-27 | 2025-03-26 | 2025-03-26 | TBC |  | 2025-09-26 | 2025-09-26 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46503814 | T3 DUTCH FLAT #2 TAP 0/1 RPR JUMS | ICS
LC | 131021415 | 129 | T3 DUTCH FLAT #2 TAP 0/1 RPR JUMS | SACTO | ETL.1421.SWIT | 2025-03-27 | 2025-03-26 | 2025-03-26 | TBC |  | 2025-09-26 | 2025-09-26 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46503815 | T3 DUTCH FLAT #2 TAP 0/1 RPR JUMS | ICS
LC | 131036788 | B023/527 | T3 DRUM-GRASS VALLY-WEIMAR B23/527 TOUCH | SACTO | ETL.6760.POLE.NWOD | 2025-04-01 | 2025-03-26 | 2025-06-22 | On-Time |  | 2025-09-26 | 2025-09-26 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46503816 | T3 DRUM-GRASS VALLY-WEIMAR B23/527 TOUCH | ICW
LC | 131037132 | B022/505 | T3 DRM-GRS VLY-WMR B022/505 RPR INSW | SACTO | ETL.6760.INSL.NCER | 2025-04-01 | 2025-03-26 | 2025-06-23 | On-Time |  | 2025-09-26 | 2025-09-26 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46506582 | T3 DRM-GRS VLY-WMR B022/505 RPR INSW | ICW
LC | 131057517 | 325 | T3 BRUNSWICK #2 TAP 0/2 RPR SWTCH | SACTO | ETL.1431.SWIT | 2025-04-07 | 2025-03-26 | 2025-03-26 | TBC |  | 2025-09-26 | 2025-09-26 | 623 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | Out of Adjustment | Switch | Repair | 46503817 | T3 BRUNSWICK #2 TAP 0/2 RPR SWTCH | ICE
LC | 131062146 | 027/127 | T3 EXCHEQUER-INDIAN FLAT-27/127 RPR STRT | FRESNO | ETL.8650.POLE.NWOD | 2025-04-08 | 2025-03-26 | 2025-03-26 | TBC |  | 2025-09-26 | 2025-09-26 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46505372 | T3 EXCHEQUER-INDIAN FLAT-27/127 RPR STRT | ICQ
LC | 128376394 | 039/002 | T2 EI ELK-GUALALA 039/002 RMV VEG | WILLITS | ETL.8410.POLE.WOOD | 2024-03-27 | 2024-03-27 | 2024-03-27 | On-Time |  | 2025-09-27 | 2025-09-27 | 564 | TR2 | YES | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 128380168 | 000/009 | T2 EI BCKS CRK-RCK CRK-CRST 0/9 RPR ROAD | TABLEMTN | ETL.4430.TOWR | 2024-03-27 | 2024-03-27 | 2024-03-27 | TBC |  | 2025-09-27 | 2025-09-27 | 932 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | Grade Change | Road | Repair | 46308255 | T2 EI BCKS CRK-RCK CRK-CRST 0/9 RPR ROAD | CHS
LC | 128494553 | 013/008 | T2 DI HMBLDT BAY-RIO DELL 13/8 RPR STRW | EUREKA | ETL.7100.POLE.WOOD | 2024-04-09 | 2024-03-27 | 2025-04-29 | On-Time |  | 2025-09-27 | 2025-09-27 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW SPCR ACCL COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46345708 | T2 DI HMBLDT BAY-RIO DELL 13/8 RPR STRW | ICW
LC | 129604025 | 011/073 | T2 CAYUCOS-CAMBRIA 011/073 CGI | PISMOBCH | ETL.8560.POLE.WOOD | 2024-09-30 | 2024-09-27 | 2025-04-18 | On-Time |  | 2024-12-27 | 2025-09-27 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW TNT CGI COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Access Issue
LC | 129604055 | 011/072 | T2 CAYUCOS-CAMBRIA 011/072 CGI | PISMOBCH | ETL.8560.POLE.WOOD | 2024-09-30 | 2024-09-27 | 2025-04-18 | On-Time |  | 2024-12-27 | 2025-09-27 | 625 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW TNT CGI COMP OH FMOB TR2 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Access Issue
LC | 129614209 | :011/061 | T2 DI CRAZY HS C-SS#1 :11/61 COTTER | MOSSLNDG | ETL.2910.INSL.CERA | 2024-10-01 | 2024-09-27 | 2024-11-04 | On-Time |  | 2024-12-27 | 2025-09-27 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46340100 | T2 DI CRAZY HS C-SS#1 :11/61 COTTER | ICS
LC | 129614228 | :013/068 | T2 DI CRAZY HS C-SS#1 :13/68 RPR STRT | MOSSLNDG | ETL.2900.TOWR | 2024-10-01 | 2024-09-27 | 2025-04-29 | On-Time |  | 2025-09-27 | 2025-09-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46387609 | T2 DI CRAZY HS C-SS#1 :13/68 RPR STRT | ICQ
LC | 129614285 | :012/065 | T2 DI CRAZY HS C-SS#1 :12/65 RPR STRT | MOSSLNDG | ETL.2900.TOWR | 2024-10-01 | 2024-09-27 | 2025-04-29 | On-Time |  | 2025-09-27 | 2025-09-27 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46387608 | T2 DI CRAZY HS C-SS#1 :12/65 RPR STRT | ICQ
LC | 131020683 | 000/006 | T3 CENTERVLLE-TBL MTN-ORVLL 0/6 RPR STRW | TABLEMTN | ETL.6330.POLE.WOOD | 2025-03-27 | 2025-03-27 | 2025-03-27 | TBC |  | 2025-09-27 | 2025-09-27 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 PRTO FRAB PGEQ BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46499512 | T3 CENTERVLLE-TBL MTN-ORVLL 0/6 RPR STRW | ICW
LC | 131020845 | 008/047 | T3 EI FULTON-IGNACIO #1 008/047 TOUCH | LAKEVLLE | ETL.4680.TOWR | 2025-03-27 | 2025-03-27 | 2025-04-30 | On-Time |  | 2025-09-27 | 2025-09-27 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46503928 | T3 EI FULTON-IGNACIO #1 008/047 TOUCH | ICQ
LC | 131021007 | 009/102 | T3 GREEN VALLEY-CMP EVERS 9/102 RPR GYWW | MOSSLNDG | ETL.1710.POLE.STPS | 2025-03-27 | 2025-03-27 | 2025-03-27 | TBC |  | 2025-09-27 | 2025-09-27 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46529923 | T3 GREEN VALLEY-CMP EVERS 9/102 RPR GYWW | ICW
LC | 131021248 | Z014/003 | T3 DI FULTON CALISTOGA Z14/3 TOUCH | LAKEVLLE | ETL.6880.POLE.NWOD | 2025-03-27 | 2025-03-27 | 2025-03-27 | TBC |  | 2025-09-27 | 2025-09-27 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Steel | Repair | 46505513 | T3 DI FULTON CALISTOGA Z14/3 TOUCH | ICS
LC | 131046023 | 005/044 | T3 TGR CRK-VALLEY SPRNGS 5/044 TOUCH | VICTOR | ETL.5790.TOWR | 2025-04-03 | 2025-03-27 | 2025-05-13 | On-Time |  | 2025-09-27 | 2025-09-27 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46505533 | T3 TGR CRK-VALLEY SPRNGS 5/044 TOUCH | ICQ
LC | 131046068 | 016/140 | T3 MISSOURI FLT-GLD HL #1 16/140 TOUCH | SACTO | ETL.2660.TOWR | 2025-04-03 | 2025-03-27 | 2025-03-27 | TBC |  | 2025-09-27 | 2025-09-27 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46507686 | T3 MISSOURI FLT-GLD HL #1 16/140 TOUCH | ICQ
LC | 131080252 | 015/136 | T3 MSURI FLT-GLD HIL #2 15/136 COTTER | SACTO | ETL.2670.INSL | 2025-04-10 | 2025-03-27 | 2025-06-04 | On-Time |  | 2025-09-27 | 2025-09-27 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46506290 | T3 MSURI FLT-GLD HIL #1 15/136 COTTER | ICS
LC | 131080388 | 000/004 | T3 BEAR CANYON TAP 000/004 TOUCH | LAKEVLLE | ETL.1182.TOWR | 2025-04-10 | 2025-03-27 | 2025-03-27 | TBC |  | 2025-09-27 | 2025-09-27 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46515148 | T3 BEAR CANYON TAP 000/004 TOUCH | ICQ
LC | 128385754 | 008/050 | T2 EI SBRNT-STNDRD OIL #2 08/50 HANGER | CONCORD | ETL.3790.INSL | 2024-03-28 | 2024-03-28 | 2025-05-20 | On-Time |  | 2025-09-28 | 2025-09-28 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46286916 | T2 EI SBRNT-STNDRD OIL #2 08/50 HANGER | ICQ
LC | 131022684 | 006/023 | T3 DIABLO-MIDWAY #3 6/23 RPR ZENA | PISMOBCH | ETL.5980.TOWR | 2025-03-28 | 2025-03-28 | 2025-04-17 | On-Time |  | 2025-09-28 | 2025-09-28 | 593 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 FRAB PGEQ BRIN | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46505991 | T3 DIABLO-MIDWAY #3 6/23 RPR ZENA | ICB
LC | 131024030 | ?006/008 | T3 SNTH LN-HLF MN BAY ?6/8 RPR GYWW | METCALF | ETL.7212.POLE.WOOD | 2025-03-28 | 2025-03-28 | 2025-04-21 | On-Time |  | 2025-09-28 | 2025-09-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46503430 | T3 SNTH LN-HLF MN BAY ?6/8 RPR GYWW | ICW
LC | 131024032 | ?006/008 | T3 SNTH LN-HLF MN BAY ?6/8 RMV VEG | METCALF | ETL.7212.POLE.WOOD | 2025-03-28 | 2025-03-28 | 2025-04-28 | On-Time |  | 2025-09-28 | 2025-09-28 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | REGW INSP PATR CNCL OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131024605 | 014/005A | T3 EI LAURELES-OTTER 14/005A RPR GYWW | MOSSLNDG | ETL.7380.POLE.NWOD | 2025-03-28 | 2025-03-28 | 2025-03-28 | TBC |  | 2025-09-28 | 2025-09-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46505759 | T3 EI LAURELES-OTTER 14/005A RPR GYWW | ICW
LC | 131024608 | 014/006 | T3 LAURELES-OTTER 014/006L RMV VEG | MOSSLNDG | ETL.7380.POLE.WDPS | 2025-03-28 | 2025-03-28 | 2025-03-28 | TBC |  | 2025-09-28 | 2025-09-28 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO BRIN | Overgrown | Vegetation | Trim
LC | 131024964 | 001/031 | T3 CENTRVLLE-TBL MTN-ORVLL 1/31 RPL INSW | TABLEMTN | ETL.6330.INSL | 2025-03-28 | 2025-03-28 | 2025-03-28 | TBC |  | 2025-09-28 | 2025-09-28 | 508T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35633487 | T3 CENTRVLLE-TBL MTN-ORVLL 1/31 RPL INSW | 93I
LC | 131028276 | 016/083 | T3 EI FULTON-IGNACIO #1 16/083 TOUCH | LAKEVLLE | ETL.4680.TOWR | 2025-03-31 | 2025-03-28 | 2025-04-15 | On-Time |  | 2025-09-28 | 2025-09-28 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46503927 | T3 EI FULTON-IGNACIO #1 16/083 TOUCH | ICQ
LC | 131032298 | C014/004 | T3 FULTON-CALISTGA C014/004 RPR GYWW | LAKEVLLE | ETL.6880.POLE.NWOD | 2025-03-31 | 2025-03-28 | 2025-05-06 | On-Time |  | 2025-09-28 | 2025-09-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46507962 | T3 DI FULTON-CALISTGA C014/004 RPR GYWW | ICW
LC | 131046043 | :003/019 | T3 GEYSERS #9-FULTON 3/19 RPR INSS | LAKEVLLE | ETL.4780.INSL.NCER | 2025-04-03 | 2025-03-28 | 2025-03-28 | TBC |  | 2025-09-28 | 2025-09-28 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46505509 | T3 GEYSERS #9-FULTON 3/19 RPR INSS | ICS
LC | 131106570 | 018/001 | T3 MONTE RIO-FORT ROSS 18/1 RMV VEG | LAKEVLLE | ETL.6979.POLE.WOOD | 2025-04-14 | 2025-03-28 | 2025-03-28 | TBC |  | 2025-09-28 | 2025-09-28 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE ACCM OH TR3 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131116449 | T049 | T3 MIDWAY-SANTA MARIA T049 RMV VEG | PISMOBCH | ETL.9240.TOWR | 2025-04-16 | 2025-03-28 | 2025-03-28 | TBC |  | 2025-09-28 | 2025-09-28 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131116500 | T049 | T3 MIDWAY-SANTA MARIA T049 RPR STRT | PISMOBCH | ETL.9240.TOWR | 2025-04-16 | 2025-03-28 | 2025-03-28 | TBC |  | 2025-09-28 | 2025-09-28 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46508200 | T3 MIDWAY-SANTA MARIA T049 RPR STRT | ICQ
LC | 131028791 | 016/187 | T3 IGNCIO-BOLNAS #2 16/187 TOUCH | LAKEVLLE | ETL.7180.POLE.NWOD | 2025-03-31 | 2025-03-29 | 2025-06-19 | On-Time |  | 2025-06-29 | 2025-09-29 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB NTDE DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46507958 | T3 IGNCIO-BOLNAS #2 16/187 TOUCH | ICW
LC | 129605124 | 030/007 | T2 WV GARBERVILLE-LYTNVLLE 30/7 INS DAMW | WILLITS | ETL.8365.INSL.NCER | 2024-09-30 | 2024-09-30 | 2025-04-16 | On-Time |  | 2025-09-30 | 2025-09-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46402735 | T2 WV GARBERVILLE-LYTNVLLE 30/7 INS DAMW | ICW
LC | 129606048 | 040/005 | T2 WV RIO DLL JCT-BRDGVLLE 40/5 INS DAMW | EUREKA | ETL.7850.INSL.NCER | 2024-09-30 | 2024-09-30 | 2025-06-21 | On-Time |  | 2025-09-30 | 2025-09-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46403131 | T2 WV RIO DLL JCT-BRDGVLLE 40/5 INS DAMW | ICW
LC | 129607768 | 15 | T2 EI DRM-GRSS VLLY-WMR B15/354 RPR SWTC | SACTO | ETL.6760.SWIT | 2024-09-30 | 2024-09-30 | 2025-05-07 | On-Time |  | 2025-09-30 | 2025-09-30 | 623 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO | Out of Adjustment | Switch | Repair | 46459930 | T2 EI DRM-GRSS VLLY-WMR B15/354 RPR SWTC | ICE
LC | 129608262 | :012/067 | T2 DI CHC-SALNAS-SLDAD#1 :12/67 RPR JUMS | MOSSLNDG | ETL.2900.INSL.CERA | 2024-09-30 | 2024-09-30 | 2025-05-21 | On-Time |  | 2025-09-30 | 2025-09-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Steel | Repair | 46393869 | T2 DI CHC-SALNAS-SLDAD#1 :12/67 RPR JUMS | ICS
LC | 129608263 | :012/067 | T2 DI CHC-SALINAS-SLDD#1 :12/67 RPR STRW | MOSSLNDG | ETL.2900.TOWR | 2024-09-30 | 2024-09-30 | 2025-04-29 | On-Time |  | 2025-09-30 | 2025-09-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46387611 | T2 DI CHC-SALINAS-SLDD#1 :12/67 RPR STRW | ICQ
LC | 129608265 | :012/067 | T2 DI CHC-SALINAS-SOLEDD#2 :12/67 COTTER | MOSSLNDG | ETL.2910.INSL.CERA | 2024-09-30 | 2024-09-30 | 2025-05-13 | On-Time |  | 2025-09-30 | 2025-09-30 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46393868 | T2 DI CHC-SALINAS-SOLEDD#1 :12/67 COTTER | ICS
LC | 129614132 | :012/066 | T2 DI CHC-SS#1 :12/66 RPR STRT | MOSSLNDG | ETL.2900.TOWR | 2024-10-01 | 2024-09-30 | 2025-04-29 | On-Time |  | 2025-09-30 | 2025-09-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46387610 | T2 DI CHC-SS#1 :12/66 RPR STRT | ICQ
LC | 129614136 | :012/066 | T2 DI CHS-SS#1 :12/66 RPL INSS | MOSSLNDG | ETL.2910.INSL.CERA | 2024-10-01 | 2024-09-30 | 2025-05-13 | On-Time |  | 2025-09-30 | 2025-09-30 | 532 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE SPCR ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35597755 | T2 DI CRZY HRS CAYN-SLAS 24/124 RPL INSS | 93K
LC | 129614629 | :015/078 | T2 DI CRAZY HS C-SS#1 :15/78 RPR STRT | MOSSLNDG | ETL.2900.TOWR | 2024-10-01 | 2024-09-30 | 2025-04-30 | On-Time |  | 2025-09-30 | 2025-09-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46387612 | T2 DI CRAZY HS C-SS#1 :15/78 RPR STRT | ICQ
LC | 129614695 | :014/077 | T2 DI CRAZY HS C-SS#1 :14/77 RPL RPTS | MOSSLNDG | ETL.2900.TOWR | 2024-10-01 | 2024-09-30 | 2025-04-30 | On-Time |  | 2025-09-30 | 2025-09-30 | 593 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH TR2 PRTO AIR FRAB NTDE | No Good/Out of Stdrd | Raptor Guard-Steel | Replace | 46393873 | T2 DI CRAZY HS C-SS#1 :14/77 RPL RPTS | ICB
LC | 128500602 | 011/014 | T2 LWR LAKE HOMESTK 11/14 COMPLETE | WILLITS | ETL.1481.POLE.WOOD | 2024-04-09 | 2024-04-01 | 2025-05-06 | On-Time |  | 2025-10-01 | 2025-10-01 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574452 | T2 DI LWR LAKE HOMESTK 11/14 RPL POLE | 70Y
LC | 129610475 | 77 | T2 TRNTY-MPLE CREEK 47/18 SW#77 RPL SWTC | EUREKA | ETL.8170.SWIT | 2024-10-01 | 2024-10-01 | 2025-06-23 | On-Time |  | 2025-10-01 | 2025-10-01 | 427 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Switch-Wood | Replace | 35604481 | T2 TRINITY-MAPLE CREEK 47/018 RPL SWITCH | 93H
LC | 131029906 | ?010/001 | T3 SNTH LN-HLF MN BAY ?10/1 RMV VEG | METCALF | ETL.7212.POLE.WOOD | 2025-03-31 | 2025-03-31 | 2025-05-29 | On-Time |  | 2025-09-30 | 2025-10-01 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131031019 | 013/017 | T3 EI LAURELES-OTTER 13/17 RMV VEG | MOSSLNDG | ETL.7380.POLE.WOOD | 2025-03-31 | 2025-03-31 | 2025-03-31 | TBC |  | 2025-09-30 | 2025-10-01 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Trim
LC | 131031037 | 013/011 | T3 EI LAURELES-OTTER 13/11 RMV VEG | MOSSLNDG | ETL.7380.POLE.WOOD | 2025-03-31 | 2025-03-31 | 2025-03-31 | TBC |  | 2025-09-30 | 2025-10-01 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Trim
LC | 131031038 | 013/012 | T3 EI LAURELES-OTTER 13/012 RMV VEG | MOSSLNDG | ETL.7380.POLE.WOOD | 2025-03-31 | 2025-03-31 | 2025-03-31 | TBC |  | 2025-09-30 | 2025-10-01 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Trim
LC | 131032015 | 013/013 | T3 EI LAURELES-OTTER 13/013 RMV VEG | MOSSLNDG | ETL.7380.POLE.WOOD | 2025-03-31 | 2025-03-31 | 2025-03-31 | TBC |  | 2025-09-30 | 2025-10-01 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Trim
LC | 131033205 | 013/005 | T3 EI LAURELES-OTTER 13/05 RMV VEG | MOSSLNDG | ETL.7380.POLE.WOOD | 2025-04-01 | 2025-04-01 | 2025-04-01 | TBC |  | 2025-10-01 | 2025-10-01 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Trim
LC | 131036828 | 026/103 | T3 DIABLO-MIDWAY #2 026/103 RPR GYWT | PISMOBCH | ETL.5970.TOWR | 2025-04-01 | 2025-04-01 | 2025-04-01 | TBC |  | 2025-10-01 | 2025-10-01 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 PRTO CLMB FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46505373 | T3 DIABLO-MIDWAY #2 026/103 RPR GYWT | ICQ
LC | 131036986 | 017/001A | T3 MNT RIOFRT RSS 17/1A RPL STRW | LAKEVLLE | ETL.6979.POLE.WOOD | 2025-04-01 | 2025-04-01 | 2025-04-01 | TBC |  | 2025-10-01 | 2025-10-01 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35636426 | T3 T2NT DI MNT RIOFRT RSS 17/1A RPL STRW | 70Y
LC | 131045930 | 013/066A | T3 CNTRA COSTA MORAGA#1 13/066A TOUCH | CONCORD | ETL.5452.POLE.NWOD | 2025-04-03 | 2025-04-01 | 2025-04-01 | TBC |  | 2025-10-01 | 2025-10-01 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Steel | Repair | 46505514 | T3 CNTRA COSTA MORAGA#1 13/066A TOUCH | ICS
LC | 131057421 | 017/002 | T3 MONTE RIO-FORT ROSS 17/02L RPL POLE | LAKEVLLE | ETL.6979.POLE.WDPS | 2025-04-07 | 2025-04-01 | 2025-04-01 | TBC |  | 2025-10-01 | 2025-10-01 | 372 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35636426 | T3 T2NT DI MNT RIOFRT RSS 17/1A RPL STRW | 70Y
LC | 131062142 | 013/067 | T3 CONTRA COSTA-MORAGA #1 13/67 TOUCH | CONCORD | ETL.5452.TOWR | 2025-04-08 | 2025-04-01 | 2025-04-01 | TBC |  | 2025-10-01 | 2025-10-01 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46505523 | T3 CONTRA COSTA-MORAGA #1 13/67 TOUCH | ICQ
LC | 131111876 | T042 | T3 MIDWAY-SANTA MARIA T042 RMV VEG | PISMOBCH | ETL.9240.TOWR | 2025-04-15 | 2025-03-31 | 2025-03-31 | TBC |  | 2025-09-30 | 2025-10-01 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131111930 | T046 | T3 MIDWAY-SANTA MARIA T46 RMV VEG | PISMOBCH | ETL.9240.TOWR | 2025-04-15 | 2025-03-31 | 2025-03-31 | TBC |  | 2025-09-30 | 2025-10-01 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131116405 | C014/003 | T3 FULTON-CALISTOGA C014/3 RPR INSW | LAKEVLLE | ETL.6880.INSL.NCER | 2025-04-16 | 2025-03-31 | 2025-05-06 | On-Time |  | 2025-09-30 | 2025-10-01 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW SPCR COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46507954 | T3 FULTON-CALISTOGA C014/3 RPR INSW | ICW
LC | 131185840 | 000/001 | T3 RINCON #1 TAP 000/001 TOUCH | LAKEVLLE | ETL.1601.POLE.NWOD | 2025-05-01 | 2025-04-01 | 2025-04-01 | TBC |  | 2025-10-01 | 2025-10-01 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Steel | Repair | 46515149 | T3 RINCON #1 TAP 000/001 TOUCH | ICS
LC | 131377095 | 017/002A | T3 MONTE RIO-FORT ROSS 17/02A RPL POLE | LAKEVLLE | ETL.6979.POLE.WOOD | 2025-06-17 | 2025-04-01 | 2025-04-01 | TBC |  | 2025-10-01 | 2025-10-01 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35636426 | T3 T2NT DI MNT RIOFRT RSS 17/1A RPL STRW | 70Y
LC | 128418521 | 008/158 | T2 WV VALLEY SPRINGS #1 08/158 RPL STRW | VICTOR | ETL.8210.POLE.WOOD | 2024-04-02 | 2024-04-02 | 2024-04-02 | TBC |  | 2025-10-02 | 2025-10-02 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB XMPT TR2 PRTO FRAB | Rotten | Structure-Wood | Replace | 35573566 | T2 WV VALLEY SPRINGS #1 08/158 RPL STRW | 70Y
LC | 128429442 | 018/149 | T2 CRBRY SS-RND MTN 18/149 RPR JMPS | TABLEMTN | ETL.5410.INSL | 2024-04-02 | 2024-04-02 | 2024-04-02 | TBC |  | 2025-10-02 | 2025-10-02 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Jumper-Steel | Repair | 46332469 | T2 EI CRBRY SS-RND MTN 18/149 RPR JMPS | ICS
LC | 128429444 | 018/149 | T2 CRBRY SS-RND MTN 18/149 RPL INSS | TABLEMTN | ETL.5410.INSL | 2024-04-02 | 2024-04-02 | 2024-04-02 | TBC |  | 2025-10-02 | 2025-10-02 | 532 | TR2 | YES | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35569571 | T2 EI CARBRY SS-RND MTN RPL INSS 6 TWRS. | 93K
LC | 128499516 | 003/012 | T3 BRIDGEVILLE-GARBERVILLE 3/12 RPL POLE | EUREKA | ETL.6220.POLE.WOOD | 2024-04-09 | 2024-04-02 | 2024-04-02 | TBC |  | 2025-10-02 | 2025-10-02 | 372T | TR3 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR OH XMPT TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35543853 | T3 BRIDGEVILLE-GARBERVILLE 3/12 RPL POLE | 70Y
LC | 129686722 | 004/042 | T2NT DI PIT#1-COTTONWOOD 4/42 RMV NEST | TABLEMTN | ETL.5390.TOWR | 2024-10-14 | 2024-10-02 | 2024-10-02 | TBC |  | 2027-10-02 | 2025-10-02 | 628 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR FRAB | Debris/Nest/etc. | Structure-Steel | Remove
LC | 129691939 | 005/048 | T2NT DI PT #1-CTTNWD 5/48 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2024-10-15 | 2024-10-02 | 2024-10-02 | TBC |  | 2027-10-02 | 2025-10-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair
LC | 129692508 | 005/045 | T2 DI PIT #1 COTTONWOOD 5/45 BNT STEEL | TABLEMTN | ETL.5390.TOWR | 2024-10-15 | 2024-10-02 | 2024-10-02 | TBC |  | 2025-10-02 | 2025-10-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46452771 | T2 DI PIT #1 COTTONWOOD 5/45 BNT STEEL | ICQ
LC | 129692622 | 005/044 | T2 DI PIT #1 COTTONWOOD 5/44 UNBURY | TABLEMTN | ETL.5390.TOWR | 2024-10-15 | 2024-10-02 | 2025-01-14 | On-Time |  | 2025-10-02 | 2025-10-02 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46452743 | T2 DI PIT #1 COTTONWOOD 5/44 UNBURY | ICQ
LC | 131039025 | 019/000 | T3 MI-WUK-CURTIS 019/000R RPL STRW | VICTOR | ETL.1073.POLE.WDPS | 2025-04-02 | 2025-04-02 | 2025-04-02 | TBC |  | 2025-10-02 | 2025-10-02 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | REGW CREW OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35636263 | T3 DI MI WUK CURTIS 19/0 RPL STRW | 70Y
LC | 131039488 | ?009/000 | T3 SNTH LNE-HLF MN BY ?009/000 RPR GYWW | METCALF | ETL.7212.POLE.WDPS | 2025-04-02 | 2025-04-02 | 2025-06-19 | On-Time |  | 2025-10-02 | 2025-10-02 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46525762 | T3 SNTH LNE-HLF MN BY ?009/000 RPR GYWW | ICW
LC | 131039798 | 004/013 | T3 KONOCTI-EAGLE ROCK 004/013 RPR GYWW | WILLITS | ETL.6861.POLE.WOOD | 2025-04-02 | 2025-04-02 | 2025-06-05 | On-Time |  | 2025-10-02 | 2025-10-02 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46522538 | T3 KONOCTI-EAGLE ROCK 004/013 RPR GYWW | ICW
LC | 131040298 | ?004/003 | T3 SNTH LN-HLF MN BAY ?4/3 RPR GYWW | METCALF | ETL.7212.POLE.NWOD | 2025-04-02 | 2025-04-02 | 2025-05-27 | On-Time |  | 2025-10-02 | 2025-10-02 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46503434 | T3 SNTH LN-HLF MN BAY ?4/3 RPR GYWW | ICW
LC | 131041693 | 007/008 | T3 LAURELES-OTTER 007/008C RPR GYWW | MOSSLNDG | ETL.7380.POLE.WDPS | 2025-04-02 | 2025-04-02 | 2025-04-02 | TBC |  | 2025-10-02 | 2025-10-02 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Replace | 46504678 | T3 LAURELES-OTTER 007/008C RPR GYWW | ICW
LC | 131041781 | 012/006 | T3 LAURELES-OTTER 12/06 RMV VEG | MOSSLNDG | ETL.7380.POLE.WOOD | 2025-04-02 | 2025-04-02 | 2025-04-02 | TBC |  | 2025-10-02 | 2025-10-02 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Trim
LC | 131202125 | 014/130 | T3 MISSR FLT-GLD HLL #1 14/130 RMV NEST | SACTO | ETL.2660.POLE.NWOD | 2025-05-06 | 2025-04-02 | 2025-06-04 | On-Time |  | 2025-10-02 | 2025-10-02 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | Debris/Nest/etc. | Structure-Steel | Remove | 46525051 | T3 MISSR FLT-GLD HLL #1 14/130 RMV NEST | ICS
LC | 131215106 | 022/180 | T3 MISSOURI FLT-GOLD HL #2 22/180 COTTER | SACTO | ETL.2670.INSL.NCER | 2025-05-08 | 2025-04-02 | 2025-06-05 | On-Time |  | 2025-10-02 | 2025-10-02 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46523349 | T3 MISSOURI FLT-GOLD HL #2 22/180 COTTER | ICS
LC | 131215107 | 022/180 | T3 MISSOURI FLT-GOLD HL #1 22/180 COTTER | SACTO | ETL.2660.INSL.NCER | 2025-05-08 | 2025-04-02 | 2025-06-05 | On-Time |  | 2025-10-02 | 2025-10-02 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46523350 | T3 MISSOURI FLT-GOLD HL #1 22/180 COTTER | ICS
LC | 131215112 | 000/004-GUY | T3 MSSN PWR TP 0/4G RPR GYWW | LAKEVLLE | ETL.1651.POLE.NWOD | 2025-05-08 | 2025-04-02 | 2025-04-02 | TBC |  | 2025-10-02 | 2025-10-02 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46525496 | T3 MSSN PWR TP 0/4G RPR GYWW | ICW
LC | 131215116 | 000/002 | T3 GYSRS #16 TP 0/2 RPR JUMS | LAKEVLLE | ETL.4760.INSL.CERA | 2025-05-08 | 2025-04-02 | 2025-04-02 | TBC |  | 2025-10-02 | 2025-10-02 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW SPCR ACCL OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46525494 | T3 GYSRS #16 TP 0/2 RPR JUMS | ICS
LC | 131215119 | 000/002 | T3 GYSRS #5-GYRS #3 0/2 RPR STRW | LAKEVLLE | ETL.1670.POLE.WOOD | 2025-05-08 | 2025-04-02 | 2025-05-27 | On-Time |  | 2025-10-02 | 2025-10-02 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46525495 | T3 GYSRS #5-GYRS #3 0/2 RPR STRW | ICW
LC | 131215161 | 000/005 | T3 MSSN PWR TP 0/5 TOUCH | LAKEVLLE | ETL.1651.POLE.NWOD | 2025-05-08 | 2025-04-02 | 2025-04-02 | TBC |  | 2025-10-02 | 2025-10-02 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46525497 | T3 MSSN PWR TP 0/5 TOUCH | ICW
LC | 131236750 | 000/004 | T3 GYSRS #5-GYSRS #3 0/4 RPL STRW | LAKEVLLE | ETL.1670.POLE.WOOD | 2025-05-12 | 2025-04-02 | 2025-04-02 | TBC |  | 2025-10-02 | 2025-10-02 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW CUST ACCM OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35641758 | T3 GYSRS #5-GYSRS #3 0/4 RPL STRW | 70Y
LC | 131241238 | 000/001 | T3 MSSN PWR TAP 0/1 RPR GYWW | LAKEVLLE | ETL.1651.POLE.WOOD | 2025-05-13 | 2025-04-02 | 2025-04-02 | TBC |  | 2025-10-02 | 2025-10-02 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW ACCM OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46525492 | T3 MSSN PWR TAP 0/1 RPR GYWW | ICW
LC | 124637408 | 006/045 | T0 NEWARK-JARVIS #1 6/45 RPR STRT | CONCORD | ETL.3020.TOWR | 2022-10-06 | 2022-10-03 | 2025-06-16 | On-Time |  | 2025-10-03 | 2025-10-03 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR ZNE1 FRAR | No Good/Out of Stdrd | Structure-Tower | Repair | 46410906 | T0 DI NEWARK-JARVIS #1 006/045 RPR STRT | ICQ
LC | 128541518 | 004/011 | T2 DI LOWER LAKE-HOMESTAKE 4/11 RPL STRW | WILLITS | ETL.1481.POLE.WOOD | 2024-04-12 | 2024-04-03 | 2025-05-06 | On-Time |  | 2025-10-03 | 2025-10-03 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35617060 | T2 DI LOWER LAKE-HOMESTAKE 4/11 RPL STRW | 70Y
LC | 128548518 | 005/006 | T2 DI LWR LAKE-HOMESTAKE 5/6 RPL STRW | WILLITS | ETL.1481.POLE.WOOD | 2024-04-15 | 2024-04-03 | 2025-05-06 | On-Time |  | 2025-10-03 | 2025-10-03 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574448 | T2 DI LWR LAKE-HOMESTAKE 5/6 RPL STRW | 70Y
LC | 128548622 | 003/013 | T2 DI LOWER LAKE-HMSTK 3/13 RPL STRW | WILLITS | ETL.1481.POLE.WOOD | 2024-04-15 | 2024-04-03 | 2025-05-06 | On-Time |  | 2025-10-03 | 2025-10-03 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574447 | T2 DI LOWER LAKE-HMSTK 3/13 RPL STRW | 70Y
LC | 128548776 | 003/015 | T2 DI LOWER LAKE-HOMESTAKE 3/15 RPR STRW | WILLITS | ETL.1481.POLE.WOOD | 2024-04-15 | 2024-04-03 | 2025-05-06 | On-Time |  | 2025-10-03 | 2025-10-03 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46340105 | T2 DI LOWER LAKE-HOMESTAKE 3/15 RPR STRW | ICW
LC | 131042877 | ?005/001 | T3 SNTH LN-HLF MN BAY ?5/1 RPR GRWW | METCALF | ETL.7212.POLE.NWOD | 2025-04-03 | 2025-04-03 | 2025-05-27 | On-Time |  | 2025-10-03 | 2025-10-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Ground Wire-Wood | Repair | 46503442 | T3 SNTH LN-HLF MN BAY ?5/1 RPR GRWW | ICW
LC | 131044636 | 014/115 | T3 GRN VALLEY-CAMP EVERS 14/115 RMV ENCR | MOSSLNDG | ETL.1710.TOWR | 2025-04-03 | 2025-04-03 | 2025-04-03 | TBC |  | 2025-10-03 | 2025-10-03 | 931 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Encroachment | Right of Way | Remove
LC | 131044737 | 017/125 | T3 GRN VALLEY-CAMP EVERS 17/125 RMV VEG | MOSSLNDG | ETL.1710.TOWR | 2025-04-03 | 2025-04-03 | 2025-04-03 | TBC |  | 2025-10-03 | 2025-10-03 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131045493 | 006/076 | T3 GREEN VALLEY-CAMP EVERS 06/76 RMV VEG | MOSSLNDG | ETL.1710.POLE.STPS | 2025-04-03 | 2025-04-03 | 2025-04-03 | TBC |  | 2025-10-03 | 2025-10-03 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO BRIN | Overgrown | Vegetation | Remove
LC | 131045626 | 006/076 | T3 GREEN VALLEY-CAMP EVERS 06/76 RMV VEG | MOSSLNDG | ETL.1710.POLE.STPS | 2025-04-03 | 2025-04-03 | 2025-04-03 | TBC |  | 2025-10-03 | 2025-10-03 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO BRIN | Overgrown | Vegetation | Remove
LC | 131045663 | 006/076 | T3GREEN VALLEY-CAMP EVERS 06/76 RMV VEG | MOSSLNDG | ETL.1710.POLE.STPS | 2025-04-03 | 2025-04-03 | 2025-04-03 | TBC |  | 2025-10-03 | 2025-10-03 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO BRIN | Overgrown | Vegetation | Remove
LC | 131045694 | 007/001 | T3 LAURELES-OTTER 7/1 RPR GYWW | MOSSLNDG | ETL.7380.POLE.WOOD | 2025-04-03 | 2025-04-03 | 2025-04-03 | TBC |  | 2025-10-03 | 2025-10-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Replace | 46516573 | T3 LAURELES-OTTER 7/1 RPR GYWW | ICW
LC | 131045705 | 007/000 | T3 LAURELES-OTTER 7/0 RPR GYWW | MOSSLNDG | ETL.7380.POLE.NWOD | 2025-04-03 | 2025-04-03 | 2025-04-03 | TBC |  | 2025-10-03 | 2025-10-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46516574 | T3 LAURELES-OTTER 7/0 RPR GYWW | ICW
LC | 131046149 | 012/009 | T3NT LAURELES-OTTER 12/009 RMV VEG | MOSSLNDG | ETL.7380.POLE.WOOD | 2025-04-03 | 2025-04-03 | 2025-04-03 | TBC |  | 2028-04-03 | 2025-10-03 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB | Overgrown | Vegetation | Trim
LC | 131046260 | 012/004 | T3 LAURELES-OTTER 12/004 RPR STRW | MOSSLNDG | ETL.7380.POLE.WOOD | 2025-04-03 | 2025-04-03 | 2025-04-03 | TBC |  | 2025-10-03 | 2025-10-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46516575 | T3 LAURELES-OTTER 12/004 RPR STRW | ICW
LC | 131046432 | ?007/006 | T3 SNTH LN-HLF MN BAY ?7/6 RPR GYWW | METCALF | ETL.7212.POLE.NWOD | 2025-04-03 | 2025-04-03 | 2025-04-21 | On-Time |  | 2025-10-03 | 2025-10-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46503445 | T3 SNTH LN-HLF MN BAY ?7/6 RPR GYWW | ICW
LC | 131057392 | 002/023B | T3 DRUM-RIO OSO #1-02/23B RPR STRS | SACTO | ETL.1420.POLE.NWOD | 2025-04-07 | 2025-04-03 | 2025-06-25 | On-Time |  | 2025-10-03 | 2025-10-03 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Steel | Repair | 46507768 | T3 DRUM-RIO OSO #1-02/23B RPR STRS | ICS
LC | 131057434 | 000/002 | T3 GYSRS #11-EAGLE RCK 00/02 TOUCH | LAKEVLLE | ETL.4391.POLE.NWOD | 2025-04-07 | 2025-04-03 | 2025-04-03 | TBC |  | 2025-10-03 | 2025-10-03 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Steel | Repair | 46507955 | T3 GYSRS #11-EAGLE RCK 00/02 TOUCH | ICS
LC | 131057454 | 000/005 | T3 GEYSERS #3-EAGLE ROCK 0/5 COTTER | LAKEVLLE | ETL.1660.INSL.CERA | 2025-04-07 | 2025-04-03 | 2025-05-27 | On-Time |  | 2025-10-03 | 2025-10-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46507963 | T3 GEYSERS #3-EAGLE ROCK 0/5 COTTER | ICW
LC | 131062199 | 000/004C | T3 GEYSERS #3-EAGLE ROCK 0/4C RPR ADSS | LAKEVLLE | ETL.1660.POLE.NWOD | 2025-04-08 | 2025-04-03 | 2025-05-27 | On-Time |  | 2025-07-03 | 2025-10-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46507956 | T3 GEYSERS #3-EAGLE ROCK 0/4C RPR ADSS | ICW
LC | 131080076 | 000/005C | T3 GYSRS #7-EAGLE ROCK 00/05C RPR SHLD | LAKEVLLE | ETL.1680.POLE.WOOD | 2025-04-10 | 2025-04-03 | 2025-05-09 | On-Time |  | 2025-10-03 | 2025-10-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Wood | Repair | 46507957 | T3 GYSRS #7-EAGLE ROCK 00/05C RPR SHLD | ICW
LC | 131080078 | 000/005B | T3 GYSRS #7-EAGLE ROCK 00/05B RMV VEG | LAKEVLLE | ETL.1680.POLE.WOOD | 2025-04-10 | 2025-04-03 | 2025-04-03 | TBC |  | 2025-10-03 | 2025-10-03 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131185716 | 000/007 | T3 GEYSERS #3 EAGLE RCK 0/7 RPR JUMS | LAKEVLLE | ETL.1660.INSL.NCER | 2025-05-01 | 2025-04-03 | 2025-05-27 | On-Time |  | 2025-10-03 | 2025-10-03 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46515150 | T3 GEYSERS #3 EAGLE RCK 0/7 RPR JUMS | ICS
LC | 131185865 | B008/007 | T3 FULTON CALISTOGA B08/07 TOUCH | LAKEVLLE | ETL.6880.POLE.NWOD | 2025-05-01 | 2025-04-03 | 2025-04-03 | TBC |  | 2025-10-03 | 2025-10-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46515151 | T3 FULTON CALISTOGA B08/07 TOUCH | ICW
LC | 131215045 | 000/011A | T3 CALPINE WEST FORD FLAT 0/11A TOUCH | LAKEVLLE | ETL.1183.POLE.NWOD | 2025-05-08 | 2025-04-03 | 2025-04-03 | TBC |  | 2025-10-03 | 2025-10-03 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46529554 | T3 CALPINE WEST FORD FLAT 0/11A TOUCH | ICQ
LC | 128449452 | 042/170 | T2 EI DIABLO-MIDWAY #2 42/170 COTTER | PISMOBCH | ETL.5970.INSL.NCER | 2024-04-04 | 2024-04-04 | 2025-04-11 | On-Time |  | 2025-10-04 | 2025-10-04 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329576 | T2 EI DIABLO-MIDWAY #2 42/170 COTTER | ICS
LC | 129635753 | 006/090 | T2 EI KESWICK-TRINITY 06/90 RMV VEG | TABLEMTN | ETL.7270.POLE.NWOD | 2024-10-04 | 2024-10-04 | 2024-11-14 | On-Time |  | 2025-10-04 | 2025-10-04 | 564 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW INSP COMP OH FMOB TR2 PRTO FRAB | Overgrown | Vegetation | Remove
LC | 131049001 | ?007/001 | T3 SNTH LN-HLF MN BAY ?7/1 RMV VEG | METCALF | ETL.7212.POLE.WOOD | 2025-04-04 | 2025-04-04 | 2025-05-08 | On-Time |  | 2025-10-04 | 2025-10-04 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | REGW INSP CNCL OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131053117 | 016/182 | T3 IGNACIO-BOLINAS #2 16/182 RPR STRW | LAKEVLLE | ETL.7180.POLE.WOOD | 2025-04-06 | 2025-04-04 | 2025-04-04 | TBC |  | 2025-10-04 | 2025-10-04 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46507964 | T3 IGNACIO-BOLINAS #2 16/182 RPR STRW | ICW
LC | 131053134 | 017/128 | T3 GRN VALLEY-CAMP EVERS 17/128 RMV VEG | MOSSLNDG | ETL.1710.POLE.NWOD | 2025-04-06 | 2025-04-04 | 2025-04-04 | TBC |  | 2025-10-04 | 2025-10-04 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131062193 | 001/001B | T3 BEARDSLEY TAP 001/001B RPR IBWW | VICTOR | ETL.1401.INSL.NCER | 2025-04-08 | 2025-04-04 | 2025-06-20 | On-Time |  | 2025-07-04 | 2025-10-04 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46505261 | T3 BEARDSLEY TAP 001/001B RPR IBWW | ICW
LC | 131062197 | 001/001C | T3 BEARDSLEY TAP 001/001C RPR STRW | VICTOR | ETL.1401.POLE.WOOD | 2025-04-08 | 2025-04-04 | 2025-06-20 | On-Time |  | 2025-10-04 | 2025-10-04 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46506506 | T3 BEARDSLEY TAP 001/001C RPR STRW | ICW
LC | 131080383 | 000/007 | T3 DONNELLS-MI-WUK 00/07L RPR GYWS | VICTOR | ETL.1400.POLE.WDPS | 2025-04-10 | 2025-04-04 | 2025-04-04 | TBC |  | 2025-10-04 | 2025-10-04 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Guy Wire-Steel | Repair | 46508075 | T3 DONNELLS-MI-WUK 00/07L RPR GYWS | ICS
LC | 131185940 | 020/136 | T3 POE RIO OSO 20/136 RPR JUMS | TABLEMTN | ETL.5540.INSL.NCER | 2025-05-01 | 2025-04-04 | 2025-04-04 | TBC |  | 2025-10-04 | 2025-10-04 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46526599 | T3 POE RIO OSO 20/136 RPR JUMS | ICS
LC | 131215076 | 000/011C | T3 CALPINE WEST FORD FLAT 0/11C TOUCH | LAKEVLLE | ETL.1183.POLE.NWOD | 2025-05-08 | 2025-04-04 | 2025-04-04 | TBC |  | 2025-10-04 | 2025-10-04 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46529555 | T3 CALPINE WEST FORD FLAT 0/11C TOUCH | ICQ
LC | 131215146 | 014/076 | T3 MONTA VISTA CYT SWST 14/76 RPR SHLS | MOSSLNDG | ETL.5090.TOWR | 2025-05-08 | 2025-04-04 | 2025-04-04 | TBC |  | 2025-10-04 | 2025-10-04 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46529927 | T3 MONTA VISTA CYT SWST 14/76 RPR SHLS | ICS
LC | 124691817 | 001/031-GUY | T2NT DI PLACER-DEL MAR 1/31-GY RMV VEG | SACTO | ETL.7800.POLE.WOOD | 2022-10-11 | 2022-10-05 | 2023-12-21 | On-Time |  | 2025-10-05 | 2025-10-05 | 564 | TR2N |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR2N PRTO AIR FRAR | Overgrown | Vegetation | Remove
LC | 128459262 | 020/339 | T2 EI ARCO-PLONIO PSS PP 20/339 RPL POLE | MIDWAY | ETL.8450.POLE.WOOD | 2024-04-05 | 2024-04-05 | 2025-04-16 | On-Time |  | 2025-10-05 | 2025-10-05 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35554110 | T2 EI ARCO-PLONIO PSS PP 20/339 RPL POLE | 70Y
LC | 128464316 | 020/335 | T2 EI ARCO-PLONIO PSS PP 20/335 RPR HRDW | MIDWAY | ETL.8450.POLE.WOOD | 2024-04-05 | 2024-04-05 | 2025-04-16 | On-Time |  | 2025-10-05 | 2025-10-05 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46302367 | T2 EI ARCO-PLONIO PSS PP 20/335 RPR HRDW | ICW
LC | 131052814 | 024/269 | T3 IGNACIO-BOLINAS #2 24/269 RPR INSW | LAKEVLLE | ETL.7180.INSL.NCER | 2025-04-05 | 2025-04-05 | 2025-04-05 | TBC |  | 2025-10-05 | 2025-10-05 | 508 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW OTHR OH FMOB TR3 PRTO NTDE BRIN | Missing | Insulator-Wood | Install | 31617012 | T3 EI IGNACIO-BOLINAS #2 24/276 RPL STRW | 70Y
LC | 124757689 | 014/090 | T0 T2NT DI NEWARK-LIVERMORE 014/090 RMV | CONCORD | ETL.7660.TOWR | 2022-10-21 | 2022-10-06 | 2024-01-22 | On-Time |  | 2025-10-06 | 2025-10-06 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH PRTO AIR FRAA TER0 | No Good/Out of Stdrd | Hardware-Tower | Replace | 46160961 | T0 DI NEWARK-LIVERMORE 014/090 RMV STEP | ICQ
LC | 124781889 | 014/092 | T0 T2NT DI NWRK-LVRMRE 14/092 RPR STRT | CONCORD | ETL.7660.TOWR | 2022-10-26 | 2022-10-06 | 2024-01-24 | On-Time |  | 2025-10-06 | 2025-10-06 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCH COMP OH PRTO AIR FRAA TER0 | No Good/Out of Stdrd | Structure-Tower | Repair | 46160964 | T0 DI NWRK-LVRMRE 14/092 RPR STRT | ICQ
LC | 127994329 | 033/182 | T2 EXCHQR-INDN FLT 33/182 RPR STRT | FRESNO | ETL.8650.POLE.NWOD | 2024-01-02 | 2024-01-02 | 2024-01-02 | TBC |  | 2025-10-07 | 2025-10-07 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46272336 | T2 WV EXCHQR-INDN FLT 33/182 RPR STRT | ICQ
LC | 129648543 | 35 | T2 BURNS-LONE STAR #2 005/112 RPR SWTC | MOSSLNDG | ETL.6240.SWIT | 2024-10-07 | 2024-10-07 | 2024-10-07 | TBC |  | 2025-10-07 | 2025-10-07 | 623 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW PATR REMT SWRK ACCL ACCM OH FMOB TR2 PRTO NTDE | Out of Adjustment | Switch | Repair | 46419870 | T2 BURNS-LONE STAR #2 005/112 RPR SWTC | ICE
LC | 131056488 | 016/186 | T3 IGNACIO-BOLINAS #2 016/186 TOUCH | LAKEVLLE | ETL.7180.POLE.NWOD | 2025-04-07 | 2025-04-07 | 2025-06-19 | On-Time |  | 2025-10-07 | 2025-10-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46507966 | T3 IGNACIO-BOLINAS #2 016/186 TOUCH | ICW
LC | 131056531 | 016/185 | T3 IGNACIO-BOLINAS #2 16/185 TOUCH | LAKEVLLE | ETL.7180.POLE.NWOD | 2025-04-07 | 2025-04-07 | 2025-06-19 | On-Time |  | 2025-10-07 | 2025-10-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46507965 | T3 IGNACIO-BOLINAS #2 16/185 TOUCH | ICW
LC | 131056582 | 017/193 | T3 IGNACIO-BOLINAS#2 17/193 RPR INSW | LAKEVLLE | ETL.7180.INSL.CERA | 2025-04-07 | 2025-04-07 | 2025-04-07 | TBC |  | 2025-10-07 | 2025-10-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46507959 | T3 IGNACIO-BOLINAS#2 17/193 RPR INSW | ICW
LC | 131056895 | :001/007 | T3 EAGLE ROCK-CORTINA :001/007 COTR KEY | WILLITS | ETL.1470.INSL.NCER | 2025-04-07 | 2025-04-07 | 2025-06-11 | On-Time |  | 2025-10-07 | 2025-10-07 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46505506 | T3 EAGLE ROCK-CORTINA :001/007 COTR KEY | ICS
LC | 131056992 | 023/264 | T3 IGNACIO-BOLINAS #2 23/264 RPL DAMW | LAKEVLLE | ETL.7180.INSL.CERA | 2025-04-07 | 2025-04-07 | 2025-04-07 | TBC |  | 2025-10-07 | 2025-10-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Damper-Wood | Replace | 46508282 | T3 IGNACIO-BOLINAS #2 23/264 RPL DAMW | ICW
LC | 131062019 | 001/006C | T3 BEARDSLEY TAP 1/6C RPR JUMW | VICTOR | ETL.1401.INSL.NCER | 2025-04-08 | 2025-04-07 | 2025-04-07 | TBC |  | 2025-10-07 | 2025-10-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46506504 | T3 BEARDSLEY TAP 1/6C RPR JUMW | ICW
LC | 131062226 | 001/006A | T3 BEARDSLEY TAP 1/6A RPR JMPW | VICTOR | ETL.1401.INSL.NCER | 2025-04-08 | 2025-04-07 | 2025-04-07 | TBC |  | 2025-10-07 | 2025-10-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46505262 | T3 BEARDSLEY TAP 1/6A RPR JMPW | ICW
LC | 131106399 | 014/122 | T3 CRESTA-RIO OSO 14/122 RPR JUMS | TABLEMTN | ETL.4590.INSL.NCER | 2025-04-14 | 2025-04-07 | 2025-04-30 | On-Time |  | 2025-10-07 | 2025-10-07 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46508286 | T3 CRESTA-RIO OSO 14/122 RPR JUMS | ICS
LC | 131106537 | 012/098 | T3 CRESTA-RIO OSO 12/098 RPR JUMS | TABLEMTN | ETL.4590.INSL.NCER | 2025-04-14 | 2025-04-07 | 2025-04-29 | On-Time |  | 2025-10-07 | 2025-10-07 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46507800 | T3 CRESTA-RIO OSO 12/098 RPR JUMS | ICS
LC | 131112074 | 021/140 | T3 POE-RIO OSO 21/140 RPR JUMPS | TABLEMTN | ETL.5540.INSL.NCER | 2025-04-15 | 2025-04-07 | 2025-04-07 | TBC |  | 2025-10-07 | 2025-10-07 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46510291 | T3 POE-RIO OSO 21/140 RPR JUMPS | ICS
LC | 131197353 | 018/146 | T3 CRSTA-RIO OSO 18/146 TOUCH | TABLEMTN | ETL.4590.TOWR | 2025-05-05 | 2025-04-07 | 2025-04-07 | TBC |  | 2025-10-07 | 2025-10-07 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair
LC | 131197356 | 013/111 | T3 CRSTA-RIO OSO 13/111 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2025-05-05 | 2025-04-07 | 2025-04-07 | TBC |  | 2025-10-07 | 2025-10-07 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46539225 | T3 CRSTA-RIO OSO 13/111 RPR FOND | ICQ
LC | 131197359 | 016/130 | T3 CRSTA-RIO OSO 16/130 RPR FOND | TABLEMTN | ETL.4590.TOWR | 2025-05-05 | 2025-04-07 | 2025-04-07 | TBC |  | 2025-10-07 | 2025-10-07 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46539226 | T3 CRSTA-RIO OSO 16/130 RPR FOND | ICQ
LC | 131214919 | 013/094 | T3 ROCK CREEK-POE 13/94 RPR JMPS | TABLEMTN | ETL.5630.INSL.NCER | 2025-05-08 | 2025-04-07 | 2025-04-07 | TBC |  | 2025-10-07 | 2025-10-07 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW COMC FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46526620 | T3 ROCK CREEK-POE 13/94 RPR JMPS | ICS
LC | 131261052 | 013/107 | T3 CRESTA-RIO OSO 13/107 RPR JMPS | TABLEMTN | ETL.4590.INSL.NCER | 2025-05-19 | 2025-04-07 | 2025-04-07 | TBC |  | 2025-10-07 | 2025-10-07 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46530502 | T3 CRESTA-RIO OSO 13/107 RPR JMPS | ICS
LC | 131261057 | 013/110 | T3 CRESTA-RIO OSO 13/110 RPR STRT | TABLEMTN | ETL.4590.TOWR | 2025-05-19 | 2025-04-07 | 2025-04-07 | TBC |  | 2025-10-07 | 2025-10-07 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46528183 | T3 CRESTA-RIO OSO 13/110 RPR STRT | ICQ
LC | 131261094 | 015/126 | T3 CRESTA RIO OSO 15/126 RPR JUMS | TABLEMTN | ETL.4590.INSL.CERA | 2025-05-19 | 2025-04-07 | 2025-04-07 | TBC |  | 2025-10-07 | 2025-10-07 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46530503 | T3 CRESTA RIO OSO 15/126 RPR JUMS | ICS
LC | 128479828 | 004/059 | T2 DI GRN VLY-PAUL SWEET 4/59R RPL POLE | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-04-08 | 2024-04-08 | 2025-05-28 | On-Time |  | 2025-10-08 | 2025-10-08 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35573565 | T2 DI GRN VLY-PAUL SWEET 4/59R RPL POLE | 70Y
LC | 128479829 | 004/059 | T2 DI GRN VLY-PAUL SWEET 4/59L RPL POLE | MOSSLNDG | ETL.1730.POLE.WDPS | 2024-04-08 | 2024-04-08 | 2025-05-28 | On-Time |  | 2025-10-08 | 2025-10-08 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW COMP OH XMPT TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35573565 | T2 DI GRN VLY-PAUL SWEET 4/59R RPL POLE | 70Y
LC | 129670790 | 004/049 | T2 SNEATH LANE-PACIFICA 4/49 RPL INSW | METCALF | ETL.7575.INSL.CERA | 2024-10-10 | 2024-10-08 | 2025-01-31 | On-Time |  | 2025-04-08 | 2025-10-08 | 508T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35592997 | T2 SNEATH LANE-PACIFICA 4/49 RPL INSW | 93I
LC | 131059320 | 016/124 | T3 GRN VALLEY-CAMP EVERS 16/124 RMV VEG | MOSSLNDG | ETL.1710.TOWR | 2025-04-08 | 2025-04-08 | 2025-04-08 | TBC |  | 2025-10-08 | 2025-10-08 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131060072 | 016/122 | T3 GRN VALLEY-CAMP EVERS 16/122 RMV VEG | MOSSLNDG | ETL.1710.TOWR | 2025-04-08 | 2025-04-08 | 2025-04-08 | TBC |  | 2025-10-08 | 2025-10-08 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131060124 | 016/121 | T3 GRN VALLEY-CAMP EVERS 16/121 RMV VEG | MOSSLNDG | ETL.1710.TOWR | 2025-04-08 | 2025-04-08 | 2025-04-08 | TBC |  | 2025-10-08 | 2025-10-08 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131061891 | 025/278 | T3 IGNACIO-BOLINAS #2 025/278 RPR GYWW | LAKEVLLE | ETL.7180.POLE.WOOD | 2025-04-08 | 2025-04-08 | 2025-05-02 | On-Time |  | 2025-10-08 | 2025-10-08 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46508283 | T3 IGNACIO-BOLINAS #2 025/278 RPR GYWW | ICW
LC | 131062210 | X000/001 | T3 DIABLO-MESA X00/01 RPR OPGW | PISMOBCH | ETL.4620.TOWR | 2025-04-08 | 2025-04-08 | 2025-06-12 | On-Time |  | 2025-07-08 | 2025-10-08 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46505511 | T3 DIABLO-MESA X00/01 RPR OPGW | ICS
LC | 131062309 | 014/114 | T3 GRN VALLEY-CAMP EVERS 14/114 RMV VEG | MOSSLNDG | ETL.1710.TOWR | 2025-04-09 | 2025-04-08 | 2025-04-08 | TBC |  | 2025-10-08 | 2025-10-08 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Trim
LC | 131080371 | 000/004 | T3 DIABLO MIDWAY #2 0/4 TOUCH | PISMOBCH | ETL.5970.TOWR | 2025-04-10 | 2025-04-08 | 2025-04-08 | TBC |  | 2025-10-08 | 2025-10-08 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46505375 | T3 DIABLO MIDWAY #2 0/4 TOUCH | ICQ
LC | 128498861 | 010/167 | T2 EI TEJON-LEBEC 010/167 GO95 | MIDWAY | ETL.9250.POLE.WOOD | 2024-04-09 | 2024-04-09 | 2025-05-09 | On-Time |  | 2025-10-09 | 2025-10-09 | 401 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35573706 | T2 EI TEJON-LEBEC 010/167 RPL INSW | 93G
LC | 131066236 | 009/077 | T3 MONTA VISTA-BURNS 9/077 RPR GYWW | MOSSLNDG | ETL.7590.POLE.STPS | 2025-04-09 | 2025-04-09 | 2025-05-13 | On-Time |  | 2025-10-09 | 2025-10-09 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46505572 | T3 MONTA VISTA-BURNS 9/077 RPR GYWW | ICW
LC | 131106573 | 019/091 | T3 CORTINA-MENDO #1 19/91 RPR OPGW | WILLITS | ETL.1330.TOWR | 2025-04-14 | 2025-04-09 | 2025-04-09 | TBC |  | 2025-10-09 | 2025-10-09 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46522561 | T3 CORTINA-MENDO #1 19/91 RPR OPGW | ICS
LC | 131106574 | 019/091 | T3 CORTINA-MENDO #1 19/91 RPR JUMS | WILLITS | ETL.1330.INSL.CERA | 2025-04-14 | 2025-04-09 | 2025-04-09 | TBC |  | 2025-10-09 | 2025-10-09 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46522562 | T3 CORTINA-MENDO #1 19/91 RPR JUMS | ICS
LC | 131106650 | 000/005 | T3 BEARDSLEY TAP 000/005R RPR STRW | VICTOR | ETL.1401.POLE.WDPS | 2025-04-14 | 2025-04-09 | 2025-06-20 | On-Time |  | 2025-10-09 | 2025-10-09 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46509369 | T3 BEARDSLEY TAP 000/005 RPR STRW | ICW
LC | 131106713 | 002/028 | T3 DESABLA CENTERVILLE 2/28L RPL HRDW | TABLEMTN | ETL.6720.POLE.WDPS | 2025-04-14 | 2025-04-09 | 2025-04-09 | TBC |  | 2025-10-09 | 2025-10-09 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace | 46508542 | T3 DESABLA CENTERVILLE 2/28L RPL HRDW | ICW
LC | 131106714 | 002/028 | T3 DESABLA CENTERVILLE 2/28R RPL HRDW | TABLEMTN | ETL.6720.POLE.WDPS | 2025-04-14 | 2025-04-09 | 2025-04-09 | TBC |  | 2025-10-09 | 2025-10-09 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace | 46508543 | T3 DESABLA CENTERVILLE 2/28R RPL HRDW | ICW
LC | 131214322 | 011/082 | T3 ROCK CREEK-POE 11/82 TOUCH | TABLEMTN | ETL.5630.TOWR | 2025-05-08 | 2025-04-09 | 2025-04-09 | TBC |  | 2025-10-09 | 2025-10-09 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46522419 | T3 ROCK CREEK-POE 11/82 TOUCH | ICQ
LC | 131261080 | 019/131 | T3 POE RIO OSO 19/131 RPR JUMS | TABLEMTN | ETL.5540.INSL.NCER | 2025-05-19 | 2025-04-09 | 2025-04-09 | TBC |  | 2025-10-09 | 2025-10-09 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46528640 | T3 POE RIO OSO 19/131 RPR JUMS | ICS
LC | 124765642 | 016/109 | T0 T2NT DI TESLA-NEWARK #2 16/109 RPR ST | CONCORD | ETL.5354.TOWR | 2022-10-24 | 2022-10-10 | 2024-02-26 | On-Time |  | 2025-10-10 | 2025-10-10 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH PRTO AIR FRAA TER0 NTDE | No Good/Out of Stdrd | Structure-Tower | Repair | 46176458 | T0 DI TESLA-NEWARK #2 16/109 RPR STRT | ICQ
LC | 124833381 | 016/108 | T0 T2NT DI TESLA-NEWARK #2 016/108 RPR S | CONCORD | ETL.5354.TOWR | 2022-11-04 | 2022-10-10 | 2024-02-22 | On-Time |  | 2025-10-10 | 2025-10-10 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH PRTO AIR FRAA TER0 NTDE | No Good/Out of Stdrd | Structure-Tower | Repair | 46176459 | T0 DI TESLA-NEWARK #2 016/108 RPR STRT | ICQ
LC | 128577888 | 003/030 | T2 DI MONTA VISTA-BURNS 03/30 RPL STRW | MOSSLNDG | ETL.7590.POLE.WOOD | 2024-04-18 | 2024-04-10 | 2025-05-11 | On-Time |  | 2025-10-10 | 2025-10-10 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH XMPT TR2 PRTO AIR FRAB | Rotten | Structure-Wood | Replace | 35573539 | T2 DI MONTA VISTA-BURNS 03/30 RPL STRW | 70Y
LC | 128577889 | 005/006 | T2 DI PHILO JCT-ELK 005/006 RPL STRW | WILLITS | ETL.7780.POLE.WOOD | 2024-04-18 | 2024-04-10 | 2024-04-10 | TBC |  | 2025-10-10 | 2025-10-10 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW FIRE ACCM COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573314 | T2 DI PHILO JCT-ELK 005/006 RPL STRW | 70Y
LC | 131078981 | 008/010 | T3 LAURELES-OTTER 8/010 RPR JMPW | MOSSLNDG | ETL.7380.INSL.CERA | 2025-04-10 | 2025-04-10 | 2025-04-10 | TBC |  | 2025-10-10 | 2025-10-10 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 PRTO PGEQ BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46516763 | T3 LAURELES-OTTER 8/010 RPR JMPW | ICW
LC | 131111808 | 000/003 | T3 GEYSERS #18 TAP 0/3 RPR STRT | LAKEVLLE | ETL.4784.TOWR | 2025-04-15 | 2025-04-10 | 2025-05-22 | On-Time |  | 2025-10-10 | 2025-10-10 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46510553 | T3 GEYSERS #18 TAP 0/3 RPR STRT | ICQ
LC | 131116466 | 000/001 | T3 FORKS OF THE BUT TAP 0/1 RPR JUMW | TABLEMTN | ETL.6722.INSL.NCER | 2025-04-16 | 2025-04-10 | 2025-04-10 | TBC |  | 2025-10-10 | 2025-10-10 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46512141 | T3 FORKS OF THE BUT TAP 0/1 RPR JUMW | ICW
LC | 131215156 | 000/000 | T3 DESABLA-CENTERVILLE 0/0 TOUCH | TABLEMTN | ETL.6720.TOWR | 2025-05-08 | 2025-04-10 | 2025-04-10 | TBC |  | 2025-10-10 | 2025-10-10 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46523123 | T3 DESABLA-CENTERVILLE 0/0 RPR STRT | ICQ
LC | 131261000 | 012/061 | T3 MONTA VISTA CYT SW 12/61 RPR SHLD | MOSSLNDG | ETL.5090.TOWR | 2025-05-19 | 2025-04-10 | 2025-04-10 | TBC |  | 2025-10-10 | 2025-10-10 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46529926 | T3 MONTA VISTA CYT SW 12/61 RPR SHLD | ICS
LC | 124858503 | 013/079 | T0 T2NT DI NEWARK-LIVERMORE 13/79 BNT ST | CONCORD | ETL.7660.TOWR | 2022-11-09 | 2022-10-11 | 2024-01-25 | On-Time |  | 2025-10-11 | 2025-10-11 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCL COMP OH PRTO AIR FRAA TER0 | No Good/Out of Stdrd | Structure-Tower | Repair | 46160972 | T0 DI NEWARK-LIVERMORE 13/79 BNT STEEL | ICQ
LC | 124887154 | 013/084 | T0 T2NT DI NEWARK-LIVERMORE 13/84 RPR ST | CONCORD | ETL.7660.TOWR | 2022-11-14 | 2022-10-11 | 2024-01-29 | On-Time |  | 2025-10-11 | 2025-10-11 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCH COMP OH PRTO AIR FRAA TER0 | No Good/Out of Stdrd | Structure-Tower | Repair | 46160974 | T0 DI NEWARK-LIVERMORE 13/84 RPR STRT | ICQ
LC | 124887878 | 014/097 | T0 T2NT DI TESLA-NEWARK #2 14/97 RPR STR | CONCORD | ETL.5354.TOWR | 2022-11-14 | 2022-10-11 | 2024-06-12 | On-Time |  | 2025-10-11 | 2025-10-11 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH PRTO AIR FRAA TER0 NTDE | No Good/Out of Stdrd | Structure-Tower | Repair | 46190346 | T0 DI TESLA-NEWARK #2 14/97 RPR STRT | ICQ
LC | 128535258 | 022/007 | T2 TRINITY-MAPLE CREEK 22/07 COMPLETE | EUREKA | ETL.8170.POLE.NWOD | 2024-04-11 | 2024-04-11 | 2025-04-12 | On-Time |  | 2025-10-11 | 2025-10-11 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572086 | T2 EI TRINITY-MAPLE CREEK 22/07 RPL STRW | 70Y
LC | 131099114 | 016/131C | T3 MIDDLE FORK-GLD HILL 16/131C RPL GYWW | SACTO | ETL.5140.POLE.WOOD | 2025-04-11 | 2025-04-11 | 2025-05-08 | On-Time |  | 2025-10-11 | 2025-10-11 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Replace | 46511948 | T3 MIDDLE FORK-GLD HILL 16/131C RPL GYWW | ICW
LC | 131116436 | 017/002 | T3 OAKHURST TAP 17/002 RPR JUMPW | FRESNO | ETL.1252.INSL.NCER | 2025-04-16 | 2025-04-11 | 2025-04-11 | TBC |  | 2025-10-11 | 2025-10-11 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCM OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46508661 | T3 OAKHURST TAP 17/002 RPR JUMPW | ICW
LC | 131116438 | 017/002 | T3 OAKHURST TAP 17/002 RPR GYWW | FRESNO | ETL.1252.POLE.NWOD | 2025-04-16 | 2025-04-11 | 2025-04-11 | TBC |  | 2025-10-11 | 2025-10-11 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCM OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46508663 | T3 OAKHURST TAP 17/002 RPR GYWW | ICW
LC | 131116464 | 014/068 | T3 CORTINA MEWNDOCINO#1 14/68 RPR INSS | WILLITS | ETL.1330.INSL.CERA | 2025-04-16 | 2025-04-11 | 2025-04-11 | TBC |  | 2025-10-11 | 2025-10-11 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46522567 | T3 CORTINA MEWNDOCINO#1 14/68 RPR INSS | ICS
LC | 131119934 | 011/005 | T3 UKIAH-HOPLAND-CLVRDL 11/5 RPR JUMW | WILLITS | ETL.4050.INSL.NCER | 2025-04-17 | 2025-04-11 | 2025-06-18 | On-Time |  | 2025-10-11 | 2025-10-11 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46522563 | T3 UKIAH-HOPLAND-CLVRDL 11/5 RPR JUMW | ICW
LC | 131119935 | 011/005 | T3 UKIAH-HOPLAND-CLVRDL 11/5 RPR ANCW | WILLITS | ETL.4050.POLE.WOOD | 2025-04-17 | 2025-04-11 | 2025-06-18 | On-Time |  | 2025-10-11 | 2025-10-11 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Anchor-Wood | Repair | 46522566 | T3 UKIAH-HOPLAND-CLVRDL 11/5 RPR ANCW | ICW
LC | 131236716 | 012/001 | T3 UKH-HPLND-CLVRDLE 12/1L RMV VEG | WILLITS | ETL.4050.POLE.STPS | 2025-05-12 | 2025-04-11 | 2025-04-11 | TBC |  | 2025-10-11 | 2025-10-11 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW ACCL OH TR3 PRTO AIR BRIN | Overgrown | Vegetation | Remove
LC | 131236717 | 012/001 | T3 UKH-HPLND-CLVRDLE 12/1C RMV VEG | WILLITS | ETL.4050.POLE.STPS | 2025-05-12 | 2025-04-11 | 2025-04-11 | TBC |  | 2025-10-11 | 2025-10-11 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW ACCL OH TR3 PRTO AIR BRIN | Overgrown | Vegetation | Remove
LC | 131236752 | 019/133 | T3 POE-RIO OSO 19/133 RPR JMPS | TABLEMTN | ETL.5540.INSL.NCER | 2025-05-12 | 2025-04-11 | 2025-04-11 | TBC |  | 2025-10-11 | 2025-10-11 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46528641 | T3 POE-RIO OSO 19/133 RPR JMPS | ICS
LC | 131241168 | 011/003 | T3 UKIAH-HOPLAND-CLOVERDALE 11/3 TOUCH | WILLITS | ETL.4050.POLE.NWOD | 2025-05-13 | 2025-04-11 | 2025-06-06 | On-Time |  | 2025-10-11 | 2025-10-11 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46537986 | T3 UKIAH-HOPLAND-CLOVERDALE 11/3 TOUCH | ICW
LC | 131241438 | 008/063 | T3 TGR CRK-VLLY SPRNGS 8/63 RMV VEG | VICTOR | ETL.5790.TOWR | 2025-05-13 | 2025-04-11 | 2025-04-11 | TBC |  | 2025-10-11 | 2025-10-11 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 129685145 | 002/050 | T2 HAT CREEK #1-WESTWOOD 002/050 GO95 | TABLEMTN | ETL.7030.INSL | 2024-10-14 | 2024-10-14 | 2025-06-24 | On-Time |  | 2025-10-14 | 2025-10-14 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCL COMP OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35604416 | T2 HAT CREEK #1-WESTWOOD 002/050 GO95 | 93G
LC | 129685224 | 002/056 | T2 HAT CREEK #1-WESTWOOD 002/056 GO95 | TABLEMTN | ETL.7030.INSL | 2024-10-14 | 2024-10-14 | 2024-10-14 | TBC |  | 2025-10-14 | 2025-10-14 | 401T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR ACCL OH TR2 PRTO FRAB NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35604417 | T2 HAT CREEK #1-WESTWOOD 002/056 GO95 | 93G
LC | 130759954 | 038/164 | T2 CBRN-LAS AGUILAS SS 038/164 RPR STRT | MOSSLNDG | ETL.4460.TOWR | 2025-01-16 | 2024-10-14 | 2024-10-14 | TBC |  | 2025-10-14 | 2025-10-14 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46472258 | T2 CBRN-LAS AGUILAS SS 038/164 RPR STRT | ICQ
LC | 131146885 | 007/061 | T3 TIGER CREEK ELECTRA 7/061 RMV VEG | VICTOR | ETL.5780.TOWR | 2025-04-21 | 2025-04-14 | 2025-04-14 | TBC |  | 2025-10-14 | 2025-10-14 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131151188 | 016/115 | T3 ROCK CREEK POE 16/115 RPR JUMS | TABLEMTN | ETL.5630.INSL.NCER | 2025-04-22 | 2025-04-14 | 2025-04-14 | TBC |  | 2025-10-14 | 2025-10-14 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46526621 | T3 ROCK CREEK POE 16/115 RPR JUMS | ICS
LC | 131196832 | 004/054 | T3 WST PT VLY SPNGS 4/054 RPR CNDW | VICTOR | ETL.8350.INSL.NCER | 2025-05-05 | 2025-04-14 | 2025-04-14 | TBC |  | 2025-10-14 | 2025-10-14 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46528146 | T3 WST PT VLY SPNGS 4/054 RPR CNDW | ICW
LC | 131241014 | 023/106 | T3 CONTRA COSTA-MRGA #1 23/106 RPL HRDT | CONCORD | ETL.5452.TOWR | 2025-05-13 | 2025-04-14 | 2025-04-14 | TBC |  | 2025-10-14 | 2025-10-14 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Hardware-Tower | Replace | 46525669 | T3 CONTRA COSTA-MRGA #1 23/106 RPL HRDT | ICQ
LC | 131246282 | 000/002 | T3 DRUM RIO OSO #1 0/2R RPR ADSS | SACTO | ETL.1420.POLE.STPS | 2025-05-14 | 2025-04-14 | 2025-06-03 | On-Time |  | 2025-07-15 | 2025-10-14 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR DURA BRIN | No Good/Out of Stdrd | ADSS - Steel | Repair | 46526271 | T3 DRUM RIO OSO #1 0/2R RPR ADSS | ICS
LC | 128548355 | 082/419C | T2 MALIN-ROUND MTN #2 82/419C RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-04-15 | 2024-04-15 | 2025-06-17 | On-Time |  | 2025-10-15 | 2025-10-15 | 93Z | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716778 | T2 DI MLN RD MTN#2 RPL ANCT 10 TWRS | 93Z
LC | 128581970 | 040/163 | T2 DI DIABLO-MWY #3 40/163 RPR SHLD | PISMOBCH | ETL.5980.TOWR | 2024-04-19 | 2024-04-15 | 2025-04-11 | On-Time |  | 2025-10-15 | 2025-10-15 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46329621 | T2 DI DIABLO-MWY #3 40/163 RPR SHLS | ICS
LC | 129688229 | 030/007-GUY | T2 RIO DELL JCT-BRDGVLLE 30/7-G RPL GYPL | EUREKA | ETL.7850.POLE.WOOD | 2024-10-15 | 2024-10-15 | 2024-10-15 | TBC |  | 2025-10-15 | 2025-10-15 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB | Rotten | Guy Pole-Wood | Replace | 35604419 | T2 EI RO DLL JCT-BRDGVLL 30/7-G RPL STRW | 70Y
LC | 130745312 | 028/173 | T2 HELMS-GREGG #1 028/173 RPR STRT | FRESNO | ETL.4870.TOWR | 2025-01-15 | 2024-10-15 | 2025-03-24 | On-Time |  | 2025-10-15 | 2025-10-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46469066 | T2 HELMS-GREGG #1 028/173 RPR STRT | ICQ
LC | 131107911 | 006/103 | T3 DELTA-CASCADE 006/103 RPR POLE | TABLEMTN | ETL.6750.POLE.WDPS | 2025-04-15 | 2025-04-15 | 2025-05-13 | On-Time |  | 2025-10-15 | 2025-10-15 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46511373 | T3 DELTA-CASCADE 006/103 RPR POLE | ICW
LC | 131108993 | 020/014 | T3 MAPLE CREEK-HOOPA 20/014 RPL STRW | EUREKA | ETL.7490.POLE.WOOD | 2025-04-15 | 2025-04-15 | 2025-04-15 | TBC |  | 2025-10-15 | 2025-10-15 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35637744 | T3 MAPLE CREEK-HOOPA 20/014 RPL STRW | 70Y
LC | 131109279 | 005/004 | T3 LAURELES-OTTER 5/004 RPR STRW | MOSSLNDG | ETL.7380.POLE.WOOD | 2025-04-15 | 2025-04-15 | 2025-04-15 | TBC |  | 2025-10-15 | 2025-10-15 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 PRTO FRAB PGEQ BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46516764 | T3 LAURELES-OTTER 5/004 RPR STRW | ICW
LC | 131265676 | 017/121 | T3 POE-RIO OSO 17/121 COTR KEY | TABLEMTN | ETL.5540.INSL.CERA | 2025-05-20 | 2025-04-15 | 2025-04-15 | TBC |  | 2025-10-15 | 2025-10-15 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46539961 | T3 POE-RIO OSO 17/121 COTR KEY | ICS
LC | 128550389 | 016/011 | T2 OAKHURST TAP 16/11 COTTER | FRESNO | ETL.1252.INSL.NCER | 2024-04-16 | 2024-04-16 | 2025-05-19 | On-Time |  | 2025-10-16 | 2025-10-16 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298281 | T2 EI OAKHURST TAP 016/011 RPR INSW | ICW
LC | 129695575 | 106/002 | T2 HUMBOLDT-TRINITY 106/002 INS MKBL | EUREKA | ETL.1820.INSL.NCER | 2024-10-16 | 2024-10-16 | 2024-10-16 | TBC |  | 2025-04-16 | 2025-10-16 | 671T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO NTDE DURA | Missing | FAA Lighting-Wood | Install | 35590399 | T2 HUMBOLDT-MAPLE CRK 8/2A INS MKBL | 93P
LC | 131113135 | 005/091 | T3 DELTA-MTN GATE JCT 05/091 RPL ANCW | TABLEMTN | ETL.6750.POLE.WOOD | 2025-04-16 | 2025-04-16 | 2025-04-16 | TBC |  | 2025-10-16 | 2025-10-16 | 637T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35638306 | T3 DELTA-MTN GATE JCT 05/091 RPL ANCW | 93E
LC | 131116469 | 004/103 | T3 DRUM GRASS VALEY WMR 4/103 RPR ADSS | SACTO | ETL.6760.POLE.NWOD | 2025-04-16 | 2025-04-16 | 2025-05-16 | On-Time |  | 2025-07-16 | 2025-10-16 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46510483 | T3 DRUM GRASS VALEY WMR 4/103 RPR ADSS | ICW
LC | 131132389 | 002/011 | T3 DIABLO-MIDWAY #2 2/011 RPR GYWT | PISMOBCH | ETL.5970.TOWR | 2025-04-21 | 2025-04-16 | 2025-04-16 | TBC |  | 2025-10-16 | 2025-10-16 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 PRTO CLMB FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46512015 | T3 DIABLO-MIDWAY #2 2/011 RPR GYWT | ICQ
LC | 131147172 | 017/149 | T3 MISSURI FLT GOLD HILL #1 17/149 TOUCH | SACTO | ETL.2660.TOWR | 2025-04-21 | 2025-04-16 | 2025-04-16 | TBC |  | 2025-10-16 | 2025-10-16 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46530738 | T3 MISSURI FLT GOLD HILL #1 17/149 TOUCH | ICQ
LC | 131250004 | 003/033 | T3 DRUM HIGGINS 3/33 RPR JUMW | SACTO | ETL.4393.INSL.NCER | 2025-05-15 | 2025-04-16 | 2025-04-16 | TBC |  | 2025-10-16 | 2025-10-16 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46532363 | T3 DRUM HIGGINS 3/33 RPR JUMW | ICW
LC | 128296356 | 046/224 | T2 EI IGNACIO-SOBRANTE 46/224 RPR CNDS | CONCORD | ETL.4920.INSL.NCER | 2024-03-15 | 2024-03-15 | 2024-03-15 | TBC |  | 2025-10-17 | 2025-10-17 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP CLR OH FMOB XMPT TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Conductor-Steel | Repair | 46403180 | T2 EI IGNACIO-SOBRANTE 46/224 RPR CNDS | ICS
LC | 128300311 | 046/225 | T2 EI IGNACIO-SOBRANTE 46/225 RPR INSS | CONCORD | ETL.4920.INSL.CERA | 2024-03-18 | 2024-03-18 | 2024-03-18 | TBC |  | 2025-10-17 | 2025-10-17 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair | 46403183 | T2 EI IGNACIO-SOBRANTE 46/225 RPR INSS | ICS
LC | 128561138 | 015/001B | T2 EI OAKHURST TAP 015/001B RPL ANCW | FRESNO | ETL.1252.POLE.NWOD | 2024-04-17 | 2024-04-17 | 2025-05-19 | On-Time |  | 2025-10-17 | 2025-10-17 | 637T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573817 | T2 EI OAKHURST TAP 015/001B RPL ANCW | 93E
LC | 128567790 | 048/240 | T2 MALIN-RUND MTN #2 048/240 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-04-17 | 2024-04-17 | 2025-05-14 | On-Time |  | 2025-10-17 | 2025-10-17 | 93Z | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716724 | T2 EI MALIN-RND MTN #2 RPL ANCT 7 TWRS | 93Z
LC | 128585114 | 029/177 | T2 DI HELMS-GREGG #1 29/177 RMV NEST | FRESNO | ETL.4870.TOWR | 2024-04-19 | 2024-04-17 | 2024-04-17 | TBC |  | 2025-10-17 | 2025-10-17 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR OH XMPT TR2 PRTO AIR FRAB NTDE | Debris/Nest/etc. | Structure-Steel | Remove | 46298233 | T2 DI HELMS-GREGG #1 29/177 RMV NEST | ICS
LC | 128585376 | 009/057 | T2 DI BALCH-SANGER 9/57 RPR STRT | FRESNO | ETL.1050.TOWR | 2024-04-19 | 2024-04-17 | 2024-04-17 | TBC |  | 2025-10-17 | 2025-10-17 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW FIRE OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46292642 | T2 DI BALCH-SANGER 9/57 RPR STRT | ICQ
LC | 129699038 | 000/012 | T2 CARIBOU-WESTWOOD 000/012 O/L INSULATO | TABLEMTN | ETL.6300.INSL.NCER | 2024-10-17 | 2024-10-17 | 2025-03-05 | On-Time |  | 2025-10-17 | 2025-10-17 | 401T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR ACCL COMP OH TR2 PRTO NTDE | Overloaded | GO95 Clear Infract-Wood | Replace | 35604411 | CARIBOU-WESTWOOD 000/012 O/L INSULATOR | 93G
LC | 129700419 | 012/098 | T3 CRESTA-RIO OSO 12/098 RPR STRT | TABLEMTN | ETL.4590.TOWR | 2024-10-17 | 2024-10-17 | 2024-10-17 | TBC |  | 2025-10-17 | 2025-10-17 | 543 | TR3 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB XMPT TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46397756 | T3 CRESTA-RIO OSO 12/098 RPR STRT | ICQ
LC | 131117497 | ?006/010 | T3 SNEATH LANE-HALF MN BY ?6/10 RPR STRW | METCALF | ETL.7212.POLE.WOOD | 2025-04-17 | 2025-04-17 | 2025-04-17 | TBC |  | 2025-10-17 | 2025-10-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 PRTO FRAB PGEQ BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46510149 | T3 SNEATH LANE-HALF MN BY ?6/10 RPR STRW | ICW
LC | 131118002 | 000/011B | T3 DONNELLS-MI-WUK 00/11B RPR GYWW | VICTOR | ETL.1400.POLE.NWOD | 2025-04-17 | 2025-04-17 | 2025-04-17 | TBC |  | 2025-10-17 | 2025-10-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46510381 | T3 DONNELLS-MI-WUK 00/11B RPR GYWW | ICW
LC | 131118192 | 319 | T3 CORTINA-MENDOCINA #1 18/090A RPR SWTC | WILLITS | ETL.1330.SWIT | 2025-04-17 | 2025-04-17 | 2025-04-17 | TBC |  | 2025-10-17 | 2025-10-17 | 623 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW PATR OH FMOB TR3 PRTO BRIN | Out of Adjustment | Switch | Repair | 46522570 | T3 CORTINA-MENDOCINA #1 18/090A RPR SWTC | ICE
LC | 131119936 | 018/000A | T3 OAKHURST TAP 018/000A RPR JUMW | FRESNO | ETL.1252.INSL.NCER | 2025-04-17 | 2025-04-17 | 2025-04-17 | TBC |  | 2025-10-17 | 2025-10-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46508662 | T3 OAKHURST TAP 018/000A RPR JUMW | ICW
LC | 131147105 | 000/007 | T3 DRUM-GRASS VLY WEIMAR 0/7 RPR JUMW | SACTO | ETL.6760.INSL.NCER | 2025-04-21 | 2025-04-17 | 2025-04-17 | TBC |  | 2025-10-17 | 2025-10-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46510482 | T3 DRUM-GRASS VLY WEIMAR 0/7 RPR JUMW | ICW
LC | 131147148 | 000/004 | T3 GYSRS #17-FLTN 0/4 RPL HRDT | LAKEVLLE | ETL.4770.TOWR | 2025-04-21 | 2025-04-17 | 2025-05-22 | On-Time |  | 2025-10-17 | 2025-10-17 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW ACCM COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Hardware-Tower | Replace | 46515155 | T3 GYSRS #17-FLTN 0/4 RPL HRDT | ICQ
LC | 131147177 | 004/048 | T3 DRUM HIGGINS 4/048 RPR JUMW | SACTO | ETL.4393.INSL.NCER | 2025-04-21 | 2025-04-17 | 2025-04-17 | TBC |  | 2025-10-17 | 2025-10-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46515137 | T3 DRUM HIGGINS 4/048 RPR JUMW | ICW
LC | 131249976 | 001/030 | T3 DRUM GRS VLY WEMR 1/030 TOUCH | SACTO | ETL.6760.POLE.NWOD | 2025-05-15 | 2025-04-17 | 2025-06-11 | On-Time |  | 2025-10-17 | 2025-10-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46526269 | T3 DRUM GRS VLY WEMR 1/030 TOUCH | ICW
LC | 131270125 | 000/008 | T3 DRUM-GRS VLY-WEIMR 0/8 RPR ADSS | SACTO | ETL.6760.POLE.NWOD | 2025-05-21 | 2025-04-17 | 2025-06-03 | On-Time |  | 2025-07-17 | 2025-10-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46528485 | T3 DRUM-GRS VLY-WEIMR 0/8 RPR ADSS | ICW
LC | 131270282 | 001/025 | T3 DRUM-GRS VLY-WEIMR 1/25 RPR ADSS | SACTO | ETL.6760.POLE.WOOD | 2025-05-21 | 2025-04-17 | 2025-06-03 | On-Time |  | 2025-07-17 | 2025-10-17 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCM COMP OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | ADSS - Wood | Repair | 46528486 | T3 DRUM-GRS VLY-WEIMR 1/25 RPR ADSS | ICW
LC | 131286418 | 001/008 | T3 EAGLE-RK-FUL-SILV 1/8 TOUCH | LAKEVLLE | ETL.4392.TOWR | 2025-05-27 | 2025-04-17 | 2025-04-17 | TBC |  | 2025-10-17 | 2025-10-17 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR ACCM OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46530709 | T3 EAGLE-RK-FUL-SILV 1/8 TOUCH | ICQ
LC | 128569969 | 001/013 | T2 SBRNT-STRD OIL SS #1 01/013 RPL HNGR | CONCORD | ETL.3800.INSL | 2024-04-18 | 2024-04-18 | 2024-04-29 | On-Time |  | 2025-10-18 | 2025-10-18 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB XMPT TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46287407 | T2 SBRNT-STRD OIL SS #1 01/013 RPL HNGR | ICQ
LC | 128570004 | 001/013 | T2 SBRNT-STRD OIL SS #1 01/13 RPL INSS | CONCORD | ETL.3800.INSL | 2024-04-18 | 2024-04-18 | 2025-04-28 | On-Time |  | 2025-10-18 | 2025-10-18 | 532T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB XMPT TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Steel | Replace | 35636121 | T2 SBRNT-STRD OIL SS #1 01/13 RPL INSS | 93K
LC | 128583127 | 049/244 | T2 MLN RND MTN#2 49/244 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-04-19 | 2024-04-18 | 2025-05-14 | On-Time |  | 2025-10-18 | 2025-10-18 | 93Z | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716724 | T2 EI MALIN-RND MTN #2 RPL ANCT 7 TWRS | 93Z
LC | 131124606 | 011/110 | T3 GREEN VALLEY-CAMP EVERS 11/110 TOUCH | MOSSLNDG | ETL.1710.POLE.STPS | 2025-04-18 | 2025-04-18 | 2025-06-04 | On-Time |  | 2025-10-18 | 2025-10-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW RESD NOAC ACCL COMP OH FMOB TR3 PRTO NTDE PGEQ BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46529924 | T3 GREEN VALLEY-CAMP EVERS 11/110 TOUCH | ICW
LC | 131171074 | 016/128 | T3 SALT SPRINGS-TIGER CREEK 16/128 TOUCH | VICTOR | ETL.3500.TOWR | 2025-04-28 | 2025-04-18 | 2025-04-18 | TBC |  | 2025-10-18 | 2025-10-18 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46530228 | T3 SALT SPRINGS-TIGER CREEK 16/128 TOUCH | ICQ
LC | 131171134 | 029/006 | T3 FULTON-HOPLAND 29/6 RPR STRW | LAKEVLLE | ETL.6890.POLE.WOOD | 2025-04-28 | 2025-04-18 | 2025-06-11 | On-Time |  | 2025-10-18 | 2025-10-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46532357 | T3 FULTON-HOPLAND 29/6 RPR STRW | ICW
LC | 131176355 | 004/041B | T3 SLY CRK TAP 04/041B RPR JUMW | TABLEMTN | ETL.4221.INSL.NCER | 2025-04-29 | 2025-04-18 | 2025-04-18 | TBC |  | 2025-10-18 | 2025-10-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46526598 | T3 SLY CRK TAP 04/041B RPR JUMW | ICW
LC | 131236569 | 004/067 | T3 KESWICK TRINITY 4/67 RPL STRW | TABLEMTN | ETL.7270.POLE.WOOD | 2025-05-12 | 2025-04-18 | 2025-04-18 | TBC |  | 2025-10-18 | 2025-10-18 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35642633 | T3 KESWICK TRINITY 4/67 RPL STRW | 70Y
LC | 131260629 | 015/119 | T3 SLT SPRNG-TGR CRK 15/119 RPL HRDT | VICTOR | ETL.3500.TOWR | 2025-05-19 | 2025-04-18 | 2025-04-18 | TBC |  | 2025-10-18 | 2025-10-18 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Hardware-Tower | Replace | 46530226 | T3 SLT SPRNG-TGR CRK 15/119 RPL HRDT | ICQ
LC | 131260644 | 004/040A | T3 SLY CRK TAP 4/40A RPR JUMW | TABLEMTN | ETL.4221.INSL.NCER | 2025-05-19 | 2025-04-18 | 2025-04-18 | TBC |  | 2025-10-18 | 2025-10-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46539851 | T3 SLY CRK TAP 4/40A RPR JUMW | ICW
LC | 131260662 | 015/117 | T3 SALT SPRNGS TIGER CRK 15/117 TOUCH | VICTOR | ETL.3500.TOWR | 2025-05-19 | 2025-04-18 | 2025-04-18 | TBC |  | 2025-10-18 | 2025-10-18 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46530225 | T3 SALT SPRNGS TIGER CRK 15/117 TOUCH | ICQ
LC | 131260717 | 004/040B | T3 SLY CRK TAP 4/40B RPR JUMW | TABLEMTN | ETL.4221.INSL.NCER | 2025-05-19 | 2025-04-18 | 2025-04-18 | TBC |  | 2025-10-18 | 2025-10-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46539852 | T3 SLY CRK TAP 4/40B RPR JUMW | ICW
LC | 131260726 | 029/001 | T3 FULTON-HOPLAND-29/01 TOUCH | LAKEVLLE | ETL.6890.POLE.NWOD | 2025-05-19 | 2025-04-18 | 2025-06-23 | On-Time |  | 2025-10-18 | 2025-10-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46532430 | T3 FULTON-HOPLAND-29/01 TOUCH | ICW
LC | 131260812 | 017/118 | T3 ROCK CREEK POE 17/118 TOUCH | TABLEMTN | ETL.5630.TOWR | 2025-05-19 | 2025-04-18 | 2025-04-18 | TBC |  | 2025-10-18 | 2025-10-18 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46539234 | T3 ROCK CREEK POE 17/118 TOUCH | ICQ
LC | 131260928 | 004/040C | T3 SLY CRK TAP 4/40C RPR JUMW | TABLEMTN | ETL.4221.INSL.NCER | 2025-05-19 | 2025-04-18 | 2025-04-18 | TBC |  | 2025-10-18 | 2025-10-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46539854 | T3 SLY CRK TAP 4/40C RPR JUMW | ICW
LC | 131274702 | T061 | T3 MDWY-SNTA MRIA T61 RPL HRDT | PISMOBCH | ETL.9240.TOWR | 2025-05-22 | 2025-04-18 | 2025-04-18 | TBC |  | 2025-10-18 | 2025-10-18 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Hardware-Tower | Replace | 46528305 | T3 MDWY-SNTA MRIA T61 RPL HRDT | ICQ
LC | 128588625 | 007/003A | T2 DUNLAP TAP 7/3A SW#47 RMV NEST | FRESNO | ETL.9061.POLE.NWOD | 2024-04-19 | 2024-04-19 | 2024-04-19 | TBC |  | 2025-10-19 | 2025-10-19 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB DURA BRIN | Debris/Nest/etc. | Structure-Steel | Remove | 46298236 | T2 EI DUNLAP TAP 007/003A RMV NEST | ICS
LC | 128618505 | 091/464 | T2 MALIN-RND MNTN #2 91/464 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-19 | 2025-06-16 | On-Time |  | 2025-10-19 | 2025-10-19 | 93Z | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716778 | T2 DI MLN RD MTN#2 RPL ANCT 10 TWRS | 93Z
LC | 128618750 | 091/463 | T2 DI MALIN-RND MNTN#2 91/463 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-04-22 | 2024-04-19 | 2025-06-16 | On-Time |  | 2025-10-19 | 2025-10-19 | 93Z | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716778 | T2 DI MLN RD MTN#2 RPL ANCT 10 TWRS | 93Z
LC | 128698735 | 007/086C | T2 DI DRUM-SUMMIT #2 7/086C RPL STRW | SACTO | ETL.1450.POLE.WOOD | 2024-05-01 | 2024-04-19 | 2025-06-26 | On-Time |  | 2025-10-19 | 2025-10-19 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | POHW FIRE SPCR COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557677 | T2 DI DRUM-SMMT#2 RPL 4 STRW | 70Y
LC | 128698770 | 007/086A | T2 DI DRUM-SMMT#2 7/86A RPL STRW | SACTO | ETL.1450.POLE.WOOD | 2024-05-01 | 2024-04-19 | 2025-06-26 | On-Time |  | 2025-10-19 | 2025-10-19 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557677 | T2 DI DRUM-SMMT#2 RPL 4 STRW | 70Y
LC | 128698819 | 007/086B | T2 DI DRUM-SMMT#2 7/86B RPL STRW | SACTO | ETL.1450.POLE.WOOD | 2024-05-01 | 2024-04-19 | 2024-04-19 | TBC |  | 2025-10-19 | 2025-10-19 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | POHW FIRE SPCR COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35557677 | T2 DI DRUM-SMMT#2 RPL 4 STRW | 70Y
LC | 129707303 | 013/247 | T2 SMARTVL-CMP FR WST 13/247 RMV NEST | SACTO | ETL.7970.POLE.NWOD | 2024-10-19 | 2024-10-19 | 2024-11-01 | On-Time |  | 2025-10-19 | 2025-10-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW NONR COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Wood | Remove | 46381282 | T2 SMARTVL-CMP FR WST 13/247 RMV NEST | ICW
LC | 128608309 | 012/000C | T2 OAKHURST TAP 012/000C RPR INSW | FRESNO | ETL.1252.INSL.NCER | 2024-04-20 | 2024-04-20 | 2024-04-20 | TBC |  | 2025-10-20 | 2025-10-20 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46298193 | T2 EI OAKHURST TAP 012/000C RPR INSW | ICW
LC | 128609268 | :004/001 | T2 CARIBOU #2 :4/1 GO95 RPL | TABLEMTN | ETL.6280.POLE.WOOD | 2024-04-20 | 2024-04-20 | 2024-04-20 | TBC |  | 2025-10-20 | 2025-10-20 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW COMP OH FMOB XMPT TR2 PRTO FRAB PGEQ | Overloaded | GO95 Clear Infract-Wood | Replace | 35556123 | T2 CARIBOU #2 :004/001 GO95 | 93G
LC | 128612129 | 027/109A | T2 DIABLO MIDWAY #3 27/109A RPR INSS | PISMOBCH | ETL.5980.INSL.NCER | 2024-04-22 | 2024-04-20 | 2025-04-12 | On-Time |  | 2025-10-20 | 2025-10-20 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Steel | Repair | 46329604 | T2 DI DIABLO MIDWAY #3 27/109A RPR INSS | ICS
LC | 128628820 | 016/085 | T2 DI BALCH-SANGER 16/85 RPR STRT | FRESNO | ETL.1050.TOWR | 2024-04-23 | 2024-04-20 | 2024-04-20 | TBC |  | 2025-10-20 | 2025-10-20 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW FIRE OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46292652 | T2 DI BALCH-SANGER 16/85 RPR STRT | ICQ
LC | 128698852 | 015/083 | T2 DI BALCH-SANGER 15/83 RPR STRT | FRESNO | ETL.1050.TOWR | 2024-05-01 | 2024-04-20 | 2024-04-20 | TBC |  | 2025-10-20 | 2025-10-20 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46292651 | T2 DI BALCH-SANGER 15/83 RPR STRT | ICQ
LC | 129710418 | 55 | T2 EI UNION CHEMICAL TAP 00/08 RPR SWTCH | CONCORD | ETL.6351.SWIT | 2024-10-21 | 2024-10-21 | 2024-10-21 | TBC |  | 2025-10-21 | 2025-10-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP COMC TRAF SPCR CLR ACCL ACCM ACCH FLAG OH FMOB TR2 PRTO | No Good/Out of Stdrd | Switch-Wood | Repair | 46477531 | T2 EI UNION CHEMICAL TAP 00/08 RPR SWTCH | ICW
LC | 129711680 | 011/005 | T2 MELONES-CURTIS 011/005 RPL HRDW | VICTOR | ETL.2390.POLE.WDPS | 2024-10-21 | 2024-10-21 | 2024-10-21 | TBC |  | 2025-10-21 | 2025-10-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE | Missing | Hardware-Wood | Install | 46410870 | T2 MELONES-CURTIS 011/005 RPL HRDW | ICW
LC | 129768113 | 011/005 | T2 MELONES-CURTIS 011/005 RPL HRDW | VICTOR | ETL.2390.POLE.WDPS | 2024-11-04 | 2024-10-21 | 2024-10-21 | TBC |  | 2025-10-21 | 2025-10-21 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE | Missing | Hardware-Wood | Install | 46410872 | T2 MELONES-CURTIS 011/005 RPL HRDW | ICW
LC | 131144785 | 018/075 | T3 DIABLO-GATES #1 018/075 RMV VEG | PISMOBCH | ETL.5960.TOWR | 2025-04-21 | 2025-04-21 | 2025-04-21 | TBC |  | 2025-10-21 | 2025-10-21 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW REMT ACCL OH FMOB TR3 PRTO CLMB FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131146149 | 021/001B | T3 DONNELLS-CURTIS 021/001B-R RPR STRW | VICTOR | ETL.1073.POLE.WDPS | 2025-04-21 | 2025-04-21 | 2025-04-21 | TBC |  | 2025-10-21 | 2025-10-21 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46526222 | T3 DONNELLS-CURTIS 021/001B-R RPR STRW | ICW
LC | 131146155 | 021/002B | T3 MI-WUK-CURTIS 021/002B RPL STRW | VICTOR | ETL.1073.POLE.WOOD | 2025-04-21 | 2025-04-21 | 2025-04-21 | TBC |  | 2025-10-21 | 2025-10-21 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35639294 | T3 MI-WUK-CURTIS 021/002A RPL STRW | 70Y
LC | 131146170 | 021/002C | T3 MI-WUK-CURTIS 021/002C RPL STRW | VICTOR | ETL.1073.POLE.WOOD | 2025-04-21 | 2025-04-21 | 2025-04-21 | TBC |  | 2025-10-21 | 2025-10-21 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35639294 | T3 MI-WUK-CURTIS 021/002A RPL STRW | 70Y
LC | 131146415 | 017/196 | T3 IGNACIO-BOLINAS #2 17/196 TOUCH | LAKEVLLE | ETL.7180.POLE.NWOD | 2025-04-21 | 2025-04-21 | 2025-05-23 | On-Time |  | 2025-07-21 | 2025-10-21 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO FRAB NTDE PGEQ DURA BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46515147 | T3 IGNACIO-BOLINAS #2 17/196 TOUCH | ICW
LC | 131146805 | 011/087 | T3 MONTA VISTA BURNS 11/87 RPR GYWW | MOSSLNDG | ETL.7590.POLE.NWOD | 2025-04-21 | 2025-04-21 | 2025-04-21 | TBC |  | 2025-10-21 | 2025-10-21 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46525769 | T3 MONTA VISTA BURNS 11/87 RPR GYWW | ICW
LC | 131147106 | 013/104 | T3 MNTA VSTA-BRNS 13/104 RMV VEG | MOSSLNDG | ETL.7590.POLE.NWOD | 2025-04-21 | 2025-04-21 | 2025-04-21 | TBC |  | 2025-10-21 | 2025-10-21 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW ACCL OH TR3 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131176207 | 002/017 | T3 ROUND MNTAIN-TBLE MTN #2 2/17 RMV VEG | TABLEMTN | ETL.6070.TOWR | 2025-04-29 | 2025-04-21 | 2025-04-21 | TBC |  | 2025-10-21 | 2025-10-21 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131177825 | 021/002A | T3 MI-WUK-CURTIS 021/002A RPL STRW | VICTOR | ETL.1073.POLE.WOOD | 2025-04-30 | 2025-04-21 | 2025-04-21 | TBC |  | 2025-10-21 | 2025-10-21 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35639294 | T3 MI-WUK-CURTIS 021/002A RPL STRW | 70Y
LC | 131185918 | 001/009 | T3 TIGER CRK VALLEY SPRGS 1/9 TOUCH | VICTOR | ETL.5790.TOWR | 2025-05-01 | 2025-04-21 | 2025-04-21 | TBC |  | 2025-10-21 | 2025-10-21 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46530229 | T3 TIGER CRK VALLEY SPRGS 1/9 TOUCH | ICQ
LC | 131196939 | 001/012 | T3 TIGER CRK VALLEY SPRGS 1/12 RMV VEGN | VICTOR | ETL.5790.TOWR | 2025-05-05 | 2025-04-21 | 2025-04-21 | TBC |  | 2025-10-21 | 2025-10-21 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131261054 | 002/017 | T3 ROUND MTN TABLE MTN 2/17 COTTER | TABLEMTN | ETL.6060.INSL.NCER | 2025-05-19 | 2025-04-21 | 2025-06-18 | On-Time |  | 2025-07-21 | 2025-10-21 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46540913 | T3 ROUND MTN TABLE MTN 2/17 COTTER | ICS
LC | 131286355 | 000/003 | T3 EL DORADO MISOURI FLT #1 0/3 RPR JUMS | SACTO | ETL.1540.INSL.NCER | 2025-05-27 | 2025-04-21 | 2025-04-21 | TBC |  | 2025-10-21 | 2025-10-21 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46532374 | T3 EL DORADO MISOURI FLT #1 0/3 RPR JUMS | ICS
LC | 131324051 | 008/048 | T3 ROUND MT-TBL MT#2 8/48 RPR INSS | TABLEMTN | ETL.6070.INSL.CERA | 2025-06-05 | 2025-04-21 | 2025-06-18 | On-Time |  | 2025-10-21 | 2025-10-21 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46540907 | T3 ROUND MT-TBL MT#2 8/48 RPR INSS | ICS
LC | 128617977 | 010/003 | T2 OAKHURST TAP 010/003 RPL ANCW | FRESNO | ETL.1252.POLE.NWOD | 2024-04-22 | 2024-04-22 | 2025-05-19 | On-Time |  | 2025-10-22 | 2025-10-22 | 637T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573815 | T2 EI OAKHURST TAP 010/003 RPL ANCW | 93E
LC | 129770927 | 000/001 | T3 WV GEYSERS#5-GEYSERS#3 0/1 RPL INSW | LAKEVLLE | ETL.1670.INSL.NCER | 2024-11-05 | 2024-10-22 | 2025-05-27 | On-Time |  | 2025-10-22 | 2025-10-22 | 508 | TR3 | YES | E - Schd Compl Yr 0 | Closed | POHW OTHR COMP OH FMOB XMPT TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 31651345 | T3 WV GEYSERS #3-CLOVERDALE 0/1 RPL POLE | 70Y
LC | 131147672 | 016/120 | T3 CAMP EVERS-PAUL SWEET 16/120 RPR CNDS | MOSSLNDG | ETL.1220.INSL.NCER | 2025-04-22 | 2025-04-22 | 2025-04-22 | TBC |  | 2025-10-22 | 2025-10-22 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 PRTO FRAB PGEQ BRIN | No Good/Out of Stdrd | Conductor-Steel | Repair | 46525776 | T3 CAMP EVERS-PAUL SWEET 16/120 RPR CNDS | ICS
LC | 131150463 | :001/011 | T3 EAGLE ROCK-REDBUD :001/011 COTTER | WILLITS | ETL.1480.INSL.NCER | 2025-04-22 | 2025-04-22 | 2025-06-11 | On-Time |  | 2025-10-22 | 2025-10-22 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO FRAB PGEQ BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46529810 | T3 EAGLE ROCK-REDBUD :001/011 COTTER | ICS
LC | 131151150 | 010/153 | T3 ATASCADERO-SN LS OBSP 10/153 RPR STRT | PISMOBCH | ETL.8490.TOWR | 2025-04-22 | 2025-04-22 | 2025-04-22 | TBC |  | 2025-10-22 | 2025-10-22 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46510545 | T3 ATASCADERO-SN LS OBSP 10/153 RPR STRT | ICQ
LC | 131160930 | 002/018 | T3 ROUND MTN-TABLE MTN #1 2/18 RPR SHLS | TABLEMTN | ETL.6060.TOWR | 2025-04-24 | 2025-04-22 | 2025-05-22 | On-Time |  | 2025-10-22 | 2025-10-22 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46523732 | T3 ROUND MTN-TABLE MTN #1 2/18 RPR SHLS | ICS
LC | 131171241 | 003/021 | T3 RND MTN-TBL MTN #2 3/21 RPR INSS | TABLEMTN | ETL.6070.INSL | 2025-04-28 | 2025-04-22 | 2025-04-22 | TBC |  | 2025-10-22 | 2025-10-22 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46525104 | T3 RND MTN-TBL MTN #2 3/21 RPR INSS | ICS
LC | 131176564 | 003/020 | T3 ROUND MNTAIN TBL MTN #2 3/20 RPR FOND | TABLEMTN | ETL.6070.TOWR | 2025-04-29 | 2025-04-22 | 2025-04-22 | TBC |  | 2025-10-22 | 2025-10-22 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46525268 | T3 ROUND MOUNTAIN TBLE MTN 3/20 RPR FOND | ICQ
LC | 131261029 | 003/021 | T3 ROUND MTN TABLE MTN 3/21 RPR FOND | TABLEMTN | ETL.6060.TOWR | 2025-05-19 | 2025-04-22 | 2025-04-22 | TBC |  | 2025-10-22 | 2025-10-22 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46528184 | T3 ROUND MTN TABLE MTN 3/21 RPR FOND | ICQ
LC | 131261099 | 003/019 | T3 ROUND MTN TBL MTN #2 003/019 RPR FOND | TABLEMTN | ETL.6070.TOWR | 2025-05-19 | 2025-04-22 | 2025-04-22 | TBC |  | 2025-10-22 | 2025-10-22 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46527535 | T3 ROUND MTN TBL MTN #2 003/019 RPR FOND | ICQ
LC | 128624141 | 010/000 | T2 EI OAKHURST TAP 010/000 RPL ANCW | FRESNO | ETL.1252.POLE.NWOD | 2024-04-23 | 2024-04-23 | 2025-05-19 | On-Time |  | 2025-10-23 | 2025-10-23 | 637T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Wood | Replace | 35573814 | T2 EI OAKHURST TAP 010/000 RPL ANCW | 93E
LC | 128625652 | :001/001 | T2 BELLT-RVRBNK-MLNS SS :1/1 RPR STRW | VICTOR | ETL.1070.POLE.WOOD | 2024-04-23 | 2024-04-23 | 2025-06-03 | On-Time |  | 2025-10-23 | 2025-10-23 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46531172 | T2 BELLT-RVRBNK-MLNS SS :1/1 RPR STRW | ICW
LC | 128628511 | :000/011 | T2 EI BLLT-RVRBNK-MLNS SS :0/11 RPL STRW | VICTOR | ETL.1070.POLE.WOOD | 2024-04-23 | 2024-04-23 | 2025-06-03 | On-Time |  | 2025-10-23 | 2025-10-23 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35554199 | T2 EI BLLT-RVRBNK-MLNS SS :0/11 RPL STRW | 70Y
LC | 128679417 | 019/603 | T2 SPAULDING-SMT 19/603 RPL INSW | SACTO | ETL.8060.INSL.NCER | 2024-04-29 | 2024-04-23 | 2024-04-23 | TBC |  | 2025-10-23 | 2025-10-23 | 508T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572884 | T2 DI SPAULDING-SMT 19/603 RPL INSW | 93I
LC | 131155274 | 020/010 | T3 MI-WUK-CURTIS 20/10 RPL STRW | VICTOR | ETL.1073.POLE.WDPS | 2025-04-23 | 2025-04-23 | 2025-04-23 | TBC |  | 2025-10-23 | 2025-10-23 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35639295 | T3 MI-WUK-CURTIS 20/10 RPL STRW | 70Y
LC | 131177446 | 020/010 | T3 MI-WUK-CURTIS 20/10 RPL STRW | VICTOR | ETL.1073.POLE.WDPS | 2025-04-30 | 2025-04-23 | 2025-04-23 | TBC |  | 2025-10-23 | 2025-10-23 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW INSP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35639295 | T3 MI-WUK-CURTIS 20/10 RPL STRW | 70Y
LC | 128631124 | :006/006 | T2 CARIBOU #2 :6/6 GO95 RPL | TABLEMTN | ETL.6280.POLE.WOOD | 2024-04-24 | 2024-04-24 | 2025-06-23 | On-Time |  | 2025-10-24 | 2025-10-24 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB XMPT TR2 PRTO FRAB PGEQ | Overloaded | GO95 Clear Infract-Wood | Replace | 35556124 | T2 CARIBOU #2 :006/006 GO95 | 93G
LC | 128636941 | 020/119 | T2 STANSLS-MNTC #2 20/119 RMV NEST | VICTOR | ETL.3820.TOWR | 2024-04-24 | 2024-04-24 | 2024-04-24 | TBC |  | 2025-10-24 | 2025-10-24 | 628 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB BRIN | Debris/Nest/etc. | Structure-Steel | Remove | 46325896 | T2 EI STANSLS-MNTC #2 20/119 RMV NEST | ICS
LC | 128768366 | 007/044 | T2 BALCH-SANGER 7/44 RPR STRT | FRESNO | ETL.1050.POLE.NWOD | 2024-05-13 | 2024-04-24 | 2024-04-24 | TBC |  | 2025-10-24 | 2025-10-24 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46303929 | T2 DI BALCH-SANGER 7/44 RPR STRT | ICQ
LC | 128774014 | 014/072 | T2 DI BALCH-SANGER 014/072 RPR STRT | FRESNO | ETL.1050.TOWR | 2024-05-14 | 2024-04-24 | 2024-04-24 | TBC |  | 2025-10-24 | 2025-10-24 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46297865 | T2 DI BALCH-SANGER 014/072 RPR STRT | ICQ
LC | 128774293 | 013/070 | T2 DI BALCH-SANGER 13/70 RPR STRT | FRESNO | ETL.1050.TOWR | 2024-05-14 | 2024-04-24 | 2024-04-24 | TBC |  | 2025-10-24 | 2025-10-24 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW FIRE OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46292657 | T2 DI BALCH-SANGER 13/70 RPR STRT | ICQ
LC | 130746648 | 007/031 | T2 PITTSBURG-SAN MATEO 7/031 RPR STRT | CONCORD | ETL.5463.TOWR | 2025-01-15 | 2024-10-24 | 2025-06-05 | On-Time |  | 2025-10-24 | 2025-10-24 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46463760 | T2 PITTSBURG-SAN MATEO 7/031 RPR STRT | ICQ
LC | 128656898 | 004/119 | T2 DEL MONTE-VIEJO 4/119 GO95 | MOSSLNDG | ETL.6710.POLE.WOOD | 2024-04-25 | 2024-04-25 | 2024-04-25 | TBC |  | 2025-10-25 | 2025-10-25 | 401T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR COMP OH FMOB XMPT TR2 PRTO FRAB NTDE | Clearance | GO95 Clear Infract-Wood | To Be Corrected | 35555544 | T2 DEL MONTE-VIEJO 4/119 GO95 | 93G
LC | 128768436 | 006/039 | T2 BALCH-SANGER 6/39 RPL HRDT | FRESNO | ETL.1050.POLE.NWOD | 2024-05-13 | 2024-04-25 | 2024-04-25 | TBC |  | 2025-10-25 | 2025-10-25 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Hardware-Tower | Replace | 46297873 | T2 DI BALCH-SANGER 6/39 RPL HRDT | ICQ
LC | 131168287 | ?003/000B | T3 SNEATH LANE HMB ?3/0B INST ANCW | METCALF | ETL.7212.POLE.NWOD | 2025-04-28 | 2025-04-25 | 2025-05-10 | On-Time |  | 2025-10-25 | 2025-10-25 | 637T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB BRIN | Missing | Anchor-Wood | Install | 35637996 | T3 SNEATH LANE HMB ?3/0B INST ANCW | 93E
LC | 131168476 | ?003/000A | T3 SNEATH LANE HMB ?3/0A RPR CNDW | METCALF | ETL.7212.INSL.NCER | 2025-04-28 | 2025-04-25 | 2025-05-05 | On-Time |  | 2025-10-25 | 2025-10-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46511089 | T3 SNEATH LANE HMB ?3/0A RPR CNDW | ICW
LC | 131168477 | ?003/000B | T3 SNEATH LANE HMB ?3/0B RPR CNDW | METCALF | ETL.7212.INSL.NCER | 2025-04-28 | 2025-04-25 | 2025-05-05 | On-Time |  | 2025-10-25 | 2025-10-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46511090 | T3 SNEATH LANE HMB ?3/0B RPR CNDW | ICW
LC | 131168504 | ?003/000C | T3 SNEATH LANE HMB ?3/0C RPR CNDW | METCALF | ETL.7212.INSL.NCER | 2025-04-28 | 2025-04-25 | 2025-05-05 | On-Time |  | 2025-10-25 | 2025-10-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46511091 | T3 SNEATH LANE HMB ?3/0C RPR CNDW | ICW
LC | 131168828 | ?002/007 | T3 SNEATH LANE HMB ?2/7R INST ANCW | METCALF | ETL.7212.POLE.STPS | 2025-04-28 | 2025-04-25 | 2025-05-10 | On-Time |  | 2025-10-25 | 2025-10-25 | 637T | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO BRIN | Missing | Anchor-Wood | Install | 35637995 | T3 SNEATH LANE HMB ?2/7R INST ANCW | 93E
LC | 131171141 | 005/051 | T3 MONTA VISTA-BURNS 5/51 RPR GYWW | MOSSLNDG | ETL.7590.POLE.WOOD | 2025-04-28 | 2025-04-25 | 2025-04-25 | TBC |  | 2025-10-25 | 2025-10-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46525775 | T3 MONTA VISTA-BURNS 5/51 RPR GYWW | ICW
LC | 124777992 | :031/202 | T2NT N TWR-MRTNEZ JCT#1 :31/202 RPR STRT | CONCORD | ETL.3130.TOWR | 2022-10-26 | 2022-10-26 | 2023-06-14 | On-Time |  | 2025-10-26 | 2025-10-26 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45699346 | T2 N TWR-MARTINEZ JCT#1 31/202 RPR STRT | ICQ
LC | 124778622 | :032/204 | T2NT N TWR-MRTNEZ JCT#1 :32/204 RPR STRT | CONCORD | ETL.3130.TOWR | 2022-10-26 | 2022-10-26 | 2023-06-14 | On-Time |  | 2025-10-26 | 2025-10-26 | 628 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Steel | Repair | 45682106 | T2 N TWR-MARTINEZ JCT#1 :32/204 RPR STRT | ICS
LC | 128662562 | 031/224 | T2 DI DRUM RIO OSO #1 31/224 RPR STRT | SACTO | ETL.1420.TOWR | 2024-04-26 | 2024-04-26 | 2024-04-26 | TBC |  | 2025-10-26 | 2025-10-26 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46327683 | T2 DI DRUM RIO OSO #1 3/224 RPR STRT | ICQ
LC | 128679008 | 024/185 | T2 DI DRUM-RIO OSO #1 24/185 RPR STRT | SACTO | ETL.1420.TOWR | 2024-04-29 | 2024-04-26 | 2024-04-26 | TBC |  | 2025-10-26 | 2025-10-26 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46327684 | T2 DI DRUM-RIO OSO #1 24/185 RPR STRT | ICQ
LC | 128769026 | 024/183 | T2 DI DRUM-RIO OSO #1 24/183 RPR STRT | SACTO | ETL.1420.TOWR | 2024-05-13 | 2024-04-26 | 2024-04-26 | TBC |  | 2025-10-26 | 2025-10-26 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW FIRE OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46327690 | T2 DI DRUM-RIO OSO #1 24/183 RPR STRT | ICQ
LC | 129737204 | 57 | T2 IGNCIO-BLNAS #2 15/175 SW#57 RPR SWTC | LAKEVLLE | ETL.7180.SWIT | 2024-10-28 | 2024-10-28 | 2024-10-28 | TBC |  | 2025-04-28 | 2025-10-28 | 623 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO FRAB DURA BRIN | Out of Adjustment | Switch | Repair | 46401522 | T2 EI IGNACIO-BOLINAS #2 15/175 RPR SWTC | ICE
LC | 129743221 | 003/026 | T2 MORAGA-OAKLAND #3 3/26 RPL HNGR | CONCORD | ETL.2740.INSL.NCER | 2024-10-29 | 2024-10-28 | 2025-06-09 | On-Time |  | 2025-10-28 | 2025-10-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW CLR COMP OH TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46399495 | T2 MORAGA-OAKLAND #3 3/26 RPL HNGR | ICQ
LC | 130736890 | 006/028 | T2NT PTSBRG-SN MATEO 006/028 RPR FOND | CONCORD | ETL.5463.TOWR | 2025-01-13 | 2024-10-28 | 2024-10-28 | TBC |  | 2027-10-28 | 2025-10-28 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair
LC | 131170319 | 010/000 | T3 MAPLE CREEK-HOOPA 10/00 RPR INSW | EUREKA | ETL.7490.INSL.NCER | 2025-04-28 | 2025-04-28 | 2025-04-28 | TBC |  | 2025-10-28 | 2025-10-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46525607 | T3 MAPLE CREEK-HOOPA 10/00 RPR INSW | ICW
LC | 128716745 | 021/164 | T2 DI DRM RIO OSO #1 21/164 RPR STRT | SACTO | ETL.1420.TOWR | 2024-05-06 | 2024-04-29 | 2024-04-29 | TBC |  | 2025-10-29 | 2025-10-29 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46327687 | T2 DI DRM RIO OSO #1 21/164 RPR STRT | ICQ
LC | 128685250 | 011/065 | T2 BAHIA-MORAGA 11/65 RPL HNGR | CONCORD | ETL.4340.INSL.NCER | 2024-04-30 | 2024-04-30 | 2024-04-30 | TBC |  | 2025-10-30 | 2025-10-30 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46287415 | T2 WV BAHIA-MORAGA 11/65 RPL HNGR | ICQ
LC | 128818887 | 004/001 | T2 DI POTER VALY-MENDO-04/01 BNT STEEL | WILLITS | ETL.7810.POLE.NWOD | 2024-05-20 | 2024-04-30 | 2025-06-03 | On-Time |  | 2025-10-30 | 2025-10-30 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46290422 | T2 DI POTER VALY-MENDO-04/01 BNT STEEL | ICQ
LC | 129747164 | 003/018 | T2 MORRO BAY-SLO #1 3/18 RPR STRT | PISMOBCH | ETL.2810.TOWR | 2024-10-30 | 2024-10-30 | 2024-11-05 | On-Time |  | 2025-10-30 | 2025-10-30 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW NOAC COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46351466 | T2 MORRO BAY-SLO #1 3/18 RPR STRT | ICQ
LC | 129760656 | 001/041 | T2 PINE GROVE TAP 01/41 RPL STRW | VICTOR | ETL.8351.POLE.WOOD | 2024-11-01 | 2024-10-30 | 2024-10-30 | TBC |  | 2025-10-30 | 2025-10-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35611216 | T2 DI PINE GROVE TAP 01/41 RPL STRW | 70Y
LC | 129760784 | 001/041-GUYB | T2 PINE GROVE TAP 1/41 RPR GYWW | VICTOR | ETL.8351.POLE.WOOD | 2024-11-01 | 2024-10-30 | 2025-06-07 | On-Time |  | 2025-10-30 | 2025-10-30 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46410871 | T2 DI PINE GROVE TAP 1/41-GUYB RPR GYWW | ICW
LC | 129760853 | 001/041-GUYA | T2 PINE GROVE TAP 1/41 RPL GYPL | VICTOR | ETL.8351.POLE.WOOD | 2024-11-01 | 2024-10-30 | 2024-10-30 | TBC |  | 2025-10-30 | 2025-10-30 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR2 PRTO AIR FRAB | Rotten | Guy Pole-Wood | Replace | 35611216 | T2 DI PINE GROVE TAP 01/41 RPL STRW | 70Y
LC | 131185951 | ?003/009 | T3 SNTH LANE-HLF MN BAY ?3/9 RPL POLE | METCALF | ETL.7212.POLE.WOOD | 2025-05-01 | 2025-04-30 | 2025-04-30 | TBC |  | 2025-10-30 | 2025-10-30 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35641822 | T3 SNTH LANE-HLF MN BAY ?3/9 RPL POLE | 70Y
LC | 128393840 | 108/002 | T2 DI HMBLDT-TRINITY 108/002L RPL POLE | EUREKA | ETL.1820.POLE.WDPS | 2024-03-29 | 2024-03-20 | 2024-03-20 | TBC |  | 2025-10-31 | 2025-10-31 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR2 PRTO AIR | No Good/Out of Stdrd | Structure-Wood | Replace | 35574487 | T2 DI HMBLDT-TRINITY 108/002L RPL POLE | 70Y
LC | 128482874 | 108/002 | T2 DI HUMBOLDT-TRINITY 108/002 RPL POLE | EUREKA | ETL.1820.POLE.WDPS | 2024-04-08 | 2024-03-20 | 2024-03-20 | TBC |  | 2025-10-31 | 2025-10-31 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | POHW OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574487 | T2 DI HMBLDT-TRINITY 108/002L RPL POLE | 70Y
LC | 129751832 | 030/004 | T2 MENDOCINO-WILLTS-FRT BRG 30/4 REFRAME | WILLITS | ETL.7550.POLE.NWOD | 2024-10-31 | 2024-10-31 | 2025-04-08 | On-Time |  | 2025-10-31 | 2025-10-31 | 637T | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW NONR REMT REAR SWRK CLR ACCH COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Crossarm-Wood | Replace | 35574305 | T2 DI MNDCNO-WLTS-FRT BRG 30/3 REFRAME | 93E
LC | 129756141 | 003/094 | T2 COLGATE-ALLEGHANY 003/094 RPR FOND | SACTO | ETL.6470.POLE.NWOD | 2024-10-31 | 2024-10-31 | 2025-05-12 | On-Time |  | 2025-10-31 | 2025-10-31 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46446152 | T2 COLGATE-ALLEGHANY 003/094 RPR FOND | ICQ
LC | 128699126 | 006/099 | T3 DLT-MTN GT JCT-MNTN 6/99R RPL POLE | TABLEMTN | ETL.6750.POLE.WDPS | 2024-05-01 | 2024-05-01 | 2024-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 372T | TR3 | YES | E - Schd Compl Yr 0 | Open | RELW INSP COMP OH FMOB XMPT TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35552636 | T3 EI DLT-MTN GT JCT-MNTN 6/99R RPL POLE | 70Y
LC | 128699147 | 006/099 | T3 DLT-MTN GT JCT-MNTN 6/99L RPL POLE | TABLEMTN | ETL.6750.POLE.WDPS | 2024-05-01 | 2024-05-01 | 2024-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 372T | TR3 | YES | E - Schd Compl Yr 0 | Open | REGW INSP COMP OH FMOB XMPT TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35552636 | T3 EI DLT-MTN GT JCT-MNTN 6/99R RPL POLE | 70Y
LC | 128901842 | 032/006 | T2 DI GARBRVL-LAYTNVL 32/06 RPR JMPW | WILLITS | ETL.8365.INSL.NCER | 2024-05-28 | 2024-05-01 | 2025-06-23 | On-Time |  | 2025-11-01 | 2025-11-01 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Wood | Repair | 46446656 | T2 DI GARBRVL-LAYTNVL 32/06 RPR JMPW | ICW
LC | 131184348 | :007/041 | T3 EAGLE ROCK-CORTINA :007/041 RPR CNDT | WILLITS | ETL.1470.INSL.NCER | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-08-01 | 2025-11-01 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 PRTO FRAB PGEQ DURA BRIN | No Good/Out of Stdrd | Conductor-Steel | Repair | 46522531 | T3 EAGLE ROCK-CORTINA :007/041 RPR CNDT | ICS
LC | 131185445 | 022/003 | T3 MAPLE CREEK-HOOPA 22/003 RPL STRW | EUREKA | ETL.7490.POLE.WOOD | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35646584 | T3 MAPLE CREEK-HOOPA 22/003 RPL STRW | 70Y
LC | 131185508 | 010/004 | T3 BRIDGEVILLE-GARBERVILLE 10/4 RPL HRDW | EUREKA | ETL.6220.POLE.WOOD | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | Missing | Hardware-Wood | Install | 46525578 | T3 BRIDGEVILLE-GARBERVILLE 10/4 RPL HRDW | ICW
LC | 131185645 | 17 | T3 WEST POINT-VALEY SPRINGS 0/2 RPR SWCH | VICTOR | ETL.8350.SWIT | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 623 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | Out of Adjustment | Switch | Repair | 46528138 | T3 WEST POINT-VALEY SPRINGS 0/2 RPR SWCH | ICE
LC | 131185658 | 011/083 | T3 ROCK CREEK-POE 11/083 RPR JMPT | TABLEMTN | ETL.5630.INSL.NCER | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP REMT TRAF ACCH OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46516940 | T3 ROCK CREEK-POE 11/083 RPR JMPT | ICS
LC | 131185674 | ?001/004 | T3 SNTH LANE-HLF MN BAY ?1/4 RPR CNDW | METCALF | ETL.7212.INSL.NCER | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46522215 | T3 SNTH LANE-HLF MN BAY ?1/4 RPR CNDW | ICW
LC | 131185751 | ?003/001 | T3SNTH LANE-HLF MN BAY ?3/1L RPL STRW | METCALF | ETL.7212.POLE.WDPS | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35643358 | T3SNTH LANE-HLF MN BAY ?3/1L RPL STRW | 70Y
LC | 131185752 | ?003/001 | T3 SNTH LANE-HLF MN BAY ?3/1R RPL STRW | METCALF | ETL.7212.POLE.WDPS | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35643358 | T3SNTH LANE-HLF MN BAY ?3/1L RPL STRW | 70Y
LC | 131185845 | 000/001B | T3 WST PNT-VALLEY SPRNGS 0/1B RPR JUMW | VICTOR | ETL.8350.INSL.NCER | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46528139 | T3 WST PNT-VALLEY SPRNGS 0/1B RPR JUMW | ICW
LC | 131185867 | 000/001A | T3 WST POINT-VALLEY SPRNGS 0/1A RPR JMPW | VICTOR | ETL.8350.INSL.NCER | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46528140 | T3 WST POINT-VALLEY SPRNGS 0/1A RPR JMPW | ICW
LC | 131185868 | 000/001A | T3 WST POINT-VALLEY SPRNGS 0/1A RPR STRW | VICTOR | ETL.8350.POLE.WOOD | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46528141 | T3 WST POINT-VALLEY SPRNGS 0/1A RPR STRW | ICW
LC | 131185889 | 001/015 | T3 WST PT VLY SPNGS 1/015 RPL STRW | VICTOR | ETL.8350.POLE.WOOD | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35643359 | T3 WST PT VLY SPNGS 1/015 RPL STRW | 70Y
LC | 131185912 | 000/008 | T3 WST POINT-VALLEY SPRINGS 0/8 RPR CRSW | VICTOR | ETL.8350.POLE.WOOD | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46528143 | T3 WST POINT-VALLEY SPRINGS 0/8 RPR CRSW | ICW
LC | 131185916 | 000/001 | T3 WST POINT-VALLEY SPRINGS 0/1 RPR JMPW | VICTOR | ETL.8350.INSL.NCER | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46528144 | T3 WST POINT-VALLEY SPRINGS 0/1 RPR JMPW | ICW
LC | 131185941 | 000/003 | T3 WST POINT-VALLEY SPRINGS 0/3 RPL SPLC | VICTOR | ETL.8350.INSL.NCER | 2025-05-01 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Splice-Wood | Repair | 46528145 | T3 WST POINT-VALLEY SPRINGS 0/3 RPL SPLC | ICW
LC | 131197176 | 005/047 | T3 MONTA VISTA-BURNS 5/47 RPR INSW | MOSSLNDG | ETL.7590.INSL.NCER | 2025-05-05 | 2025-05-01 | 2025-05-01 | TBC |  | 2025-11-01 | 2025-11-01 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46525773 | T3 MONTA VISTA-BURNS 5/47 RPR INSW | ICW
LC | 129773682 | 011/083 | T2 GREEN VALLEY-LLAGAS 11/83L RPL POLE | MOSSLNDG | ETL.1720.POLE.STPS | 2024-11-05 | 2024-11-05 | 2024-11-05 | TBC |  | 2025-11-05 | 2025-11-05 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35596356 | T2 GREEN VALLEY-LLAGAS 11/83L RPL POLE | 70Y
LC | 129782072 | 011/083 | T2 GREEN VALLEY-LLAGAS 11/83R RPL POLE | MOSSLNDG | ETL.1720.POLE.STPS | 2024-11-06 | 2024-11-05 | 2024-11-05 | TBC |  | 2025-11-05 | 2025-11-05 | 372 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35596356 | T2 GREEN VALLEY-LLAGAS 11/83L RPL POLE | 70Y
LC | 131195545 | 000/001B | T3 DIABLO PP STDBY SUPLY 00/01B RMV VEG | PISMOBCH | ETL.4610.POLE.NWOD | 2025-05-05 | 2025-05-05 | 2025-05-05 | TBC |  | 2025-11-05 | 2025-11-05 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 PRTO FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131196196 | 002/026 | T3 HILLSDALE JCT-HALF MOON BAY 2/26 CGI | METCALF | ETL.7060.POLE.WOOD | 2025-05-05 | 2025-05-05 | 2025-05-05 | TBC |  | 2025-08-05 | 2025-11-05 | 625 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW TNT COMP OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Access Issue
LC | 131196223 | 002/027 | T3 HILLSDALE JCT-HALF MOON BAY 2/27 CGI | METCALF | ETL.7060.POLE.WOOD | 2025-05-05 | 2025-05-05 | 2025-05-05 | TBC |  | 2025-08-05 | 2025-11-05 | 625 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW TNT COMP OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Access Issue
LC | 131196234 | 002/025 | T3 HILLSDALE JCT-HALF MOON BAY 2/25 CGI | METCALF | ETL.7060.POLE.WOOD | 2025-05-05 | 2025-05-05 | 2025-05-05 | TBC |  | 2025-08-05 | 2025-11-05 | 625 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW TNT COMP OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Access Issue
LC | 131196315 | 001/024 | T3 HILLSDALE JCT-HLF MN BY 01/24 CGI | METCALF | ETL.7060.POLE.WOOD | 2025-05-05 | 2025-05-05 | 2025-05-05 | TBC |  | 2025-08-05 | 2025-11-05 | 625 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW TNT COMP OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Access Issue
LC | 131196318 | 001/023 | T3 HILLSDALE JCT-HLF MN BY 01/23 CGI | METCALF | ETL.7060.POLE.WOOD | 2025-05-05 | 2025-05-05 | 2025-05-05 | TBC |  | 2025-08-05 | 2025-11-05 | 625 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW TNT OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Access Issue
LC | 131196328 | 001/021 | T3 HILLSDALE JCT-HALF MN BY - 6 1/21 CGI | METCALF | ETL.7060.POLE.WOOD | 2025-05-05 | 2025-05-05 | 2025-05-05 | TBC |  | 2025-08-05 | 2025-11-05 | 625 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW TNT CGI COMP OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Access Issue
LC | 131196338 | 001/018 | T3 HILLSDALE JCT-HALF MOON BAY 1/18 CGI | METCALF | ETL.7060.POLE.WOOD | 2025-05-05 | 2025-05-05 | 2025-05-05 | TBC |  | 2025-08-05 | 2025-11-05 | 625 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW TNT COMP OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Access Issue
LC | 131196342 | 001/022 | T3 HILLSDALE JCT-HALF MOON BAY 01/22 CGI | METCALF | ETL.7060.POLE.WOOD | 2025-05-05 | 2025-05-05 | 2025-05-05 | TBC |  | 2025-08-05 | 2025-11-05 | 625 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW TNT COMP OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Access Issue
LC | 131196347 | 001/020 | T3 HILLSDALE JCT-HALF MOON BAY 1/20 CGI | METCALF | ETL.7060.POLE.WOOD | 2025-05-05 | 2025-05-05 | 2025-05-05 | TBC |  | 2025-08-05 | 2025-11-05 | 625 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW TNT COMP OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Access Issue
LC | 131196348 | 001/019 | T3 HILLSDALE JCT-HALF MOON BAY 1/19 CGI | METCALF | ETL.7060.POLE.WOOD | 2025-05-05 | 2025-05-05 | 2025-05-05 | TBC |  | 2025-08-05 | 2025-11-05 | 625 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW TNT COMP OH FMOB TR3 PRTO FRAB NTDE DURA BRIN | Customer Issue | Other | Access Issue
LC | 131201046 | ?001/013 | T3 SNEATH LANE HMB ?1/13 RPR CNDW | METCALF | ETL.7212.INSL.NCER | 2025-05-06 | 2025-05-05 | 2025-05-07 | On-Time |  | 2025-11-05 | 2025-11-05 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 NTDE BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46516890 | T3 SNEATH LANE HMB ?1/13 RPR CNDW | ICW
LC | 131286396 | 004/026 | T3 RND MTN TBL MTN#1 4/026 RPR SHLS | TABLEMTN | ETL.6060.TOWR | 2025-05-27 | 2025-05-05 | 2025-06-18 | On-Time |  | 2025-11-05 | 2025-11-05 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46539674 | T3 RND MTN TBL MTN#1 4/026 RPR SHLS | ICS
LC | 131286397 | 004/026 | T3 RND MTN TBL MTN#1 4/026 RPR INSS | TABLEMTN | ETL.6060.INSL.NCER | 2025-05-27 | 2025-05-05 | 2025-05-05 | TBC |  | 2025-11-05 | 2025-11-05 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46539675 | T3 RND MTN TBL MTN#1 4/026 RPR INSS | ICS
LC | 131324293 | 006/038 | T3 RND MTN-TBL MTN #1 006/038 RPR SHLS | TABLEMTN | ETL.6060.TOWR | 2025-06-05 | 2025-05-05 | 2025-06-21 | On-Time |  | 2025-11-05 | 2025-11-05 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46540908 | T3 RND MTN-TBL MTN #1 006/038 RPR SHLS | ICS
LC | 128957024 | 062/005 | T2 DI GRBRVLL-LYTNVLL 062/005 RPL STRW | WILLITS | ETL.8365.POLE.WOOD | 2024-05-31 | 2024-05-06 | 2024-05-06 | TBC |  | 2025-11-06 | 2025-11-06 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574358 | T2 DI GRBRVLL-LYTNVLL 062/005 RPL STRW | 70Y
LC | 131201418 | 008/003 | T3 BRIDGEVILLE-GARBERVILLE 8/3 TOUCH | EUREKA | ETL.6220.POLE.NWOD | 2025-05-06 | 2025-05-06 | 2025-06-05 | On-Time |  | 2025-11-06 | 2025-11-06 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46525576 | T3 BRIDGEVILLE-GARBERVILLE 8/3 TOUCH | ICW
LC | 131201450 | 008/002 | T3 BRIDGEVILLE-GARBERVILLE 8/2 RPL HRDW | EUREKA | ETL.6220.POLE.WOOD | 2025-05-06 | 2025-05-06 | 2025-05-06 | TBC |  | 2025-11-06 | 2025-11-06 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | Missing | Hardware-Wood | Install | 46525575 | T3 BRIDGEVILLE-GARBERVILLE 8/2 RPL HRDW | ICW
LC | 131201982 | 004/023 | T3 ROUND MT-TBLE MT #2 4/23 RPR SHLS | TABLEMTN | ETL.6070.TOWR | 2025-05-06 | 2025-05-06 | 2025-06-21 | On-Time |  | 2025-11-06 | 2025-11-06 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46528650 | T3 ROUND MT-TBLE MT #2 4/23 RPR SHLS | ICS
LC | 131293081 | X000/003 | T3 DIABLO MESA 0/003 RPR OPGW | PISMOBCH | ETL.4620.TOWR | 2025-05-28 | 2025-05-06 | 2025-06-11 | On-Time |  | 2025-11-06 | 2025-11-06 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE ACCM COMP OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46529919 | T3 DIABLO MESA 0/003 RPR OPGW | ICS
LC | 131297160 | 004/026 | T3 ROUND MTN-TABLE MTN #2 4/26 RPR SHLS | TABLEMTN | ETL.6070.TOWR | 2025-05-29 | 2025-05-06 | 2025-06-21 | On-Time |  | 2025-11-06 | 2025-11-06 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46540904 | T3 ROUND MTN-TABLE MTN #2 4/26 RPR SHLS | ICS
LC | 131297165 | 007/040 | T3 ROUND MTN-TABLE MTN #2 7/40 RPR SHLS | TABLEMTN | ETL.6070.TOWR | 2025-05-29 | 2025-05-06 | 2025-05-06 | TBC |  | 2025-11-06 | 2025-11-06 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46540905 | T3 ROUND MTN-TABLE MTN #2 7/40 RPR SHLS | ICS
LC | 131297167 | 007/040 | T3 ROUND MTN-TABLE MTN #2 7/40 COTTER | TABLEMTN | ETL.6070.INSL | 2025-05-29 | 2025-05-06 | 2025-06-21 | On-Time |  | 2025-11-06 | 2025-11-06 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46540906 | T3 ROUND MTN-TABLE MTN #2 7/40 COTTER | ICS
LC | 129786862 | 025/167 | T2 POE-RIO OSO 25/167 RMV NEST | TABLEMTN | ETL.5540.TOWR | 2024-11-07 | 2024-11-07 | 2025-03-24 | On-Time |  | 2025-11-07 | 2025-11-07 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMP OH FMOB TR2 PRTO FRAB | Debris/Nest/etc. | Structure-Steel | Remove | 46452734 | T2 POE-RIO OSO 25/167 RMV NEST | ICS
LC | 129802129 | 008/169 | T2 VALLEY SPRINGS #1 8/169 RPL POLE | VICTOR | ETL.8210.POLE.WOOD | 2024-11-12 | 2024-11-07 | 2024-11-07 | TBC |  | 2025-11-07 | 2025-11-07 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35641821 | T2 VALLEY SPRINGS #1 8/169 RPL POLE | 70Y
LC | 131205972 | ?004/000 | T3 SNEATH LANE HMB ?4/0 RPR CNDW | METCALF | ETL.7212.INSL.CERA | 2025-05-07 | 2025-05-07 | 2025-05-11 | On-Time |  | 2025-11-07 | 2025-11-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46522213 | T3 SNEATH LANE HMB ?4/0 RPR CNDW | ICW
LC | 131207365 | 021/007 | T3 MAPLE CREEK-HOOPA 21/007 RPR JMPW | EUREKA | ETL.7490.INSL.NCER | 2025-05-07 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46525612 | T3 MAPLE CREEK-HOOPA 21/007 RPR JMPW | ICW
LC | 131207464 | 033/165 | T3 FULTON-PUEBLO 33/165 RPR INSW | LAKEVLLE | ETL.1600.INSL.NCER | 2025-05-07 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46532359 | T3 FULTON-PUEBLO 33/165 RPR INSW | ICS
LC | 131209299 | 021/006 | T3 MAPLE CREEK-HOOPA 21/006 RPR JMPW | EUREKA | ETL.7490.INSL.NCER | 2025-05-07 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46525611 | T3 MAPLE CREEK-HOOPA 21/006 RPR JMPW | ICW
LC | 131240956 | 005/079 | T3 MIDDLE FORK #1 5/79 RPR JMPW | SACTO | ETL.8405.INSL.NCER | 2025-05-13 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46526268 | T3 MIDDLE FORK #1 5/79 RPR JMPW | ICW
LC | 131246400 | 003/035C | T3 SLY CREEK TAP 3/35C RPR JUMW | TABLEMTN | ETL.4221.INSL.NCER | 2025-05-14 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46539594 | T3 SLY CREEK TAP 3/35C RPR JUMW | ICW
LC | 131246413 | 008/066 | T3 MIDDLE FORK GLD HL 8/066 RPR JUMS | SACTO | ETL.5140.INSL | 2025-05-14 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46526483 | T3 MIDDLE FORK GLD HL 8/066 RPR JUMS | ICS
LC | 131246414 | 008/066 | T3 MIDDLE FORK GLD HL 8/066 RPR STRT | SACTO | ETL.5140.TOWR | 2025-05-14 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46539919 | T3 MIDDLE FORK GLD HL 8/066 RPR STRT | ICQ
LC | 131249895 | 008/112 | T3 MIDDLEFORK #1 8/112 RPL STRW | SACTO | ETL.8405.POLE.WOOD | 2025-05-15 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35643950 | T3 MIDDLEFORK #1 8/112 RPL STRW | 70Y
LC | 131249957 | 003/039 | T3 GEYSERS #3-CLOVERDALE 3/39 RPR INSW | LAKEVLLE | ETL.1650.INSL.NCER | 2025-05-15 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46532358 | T3 GEYSERS #3-CLOVERDALE 3/39 RPR INSW | ICW
LC | 131250047 | 000/013 | T3 ORO FINO TAP 000/013 RPR STRW | TABLEMTN | ETL.6721.POLE.WOOD | 2025-05-15 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46526193 | T3 ORO FINO TAP 000/013 RPR STRW | ICW
LC | 131292757 | 005/045 | T3 MIDDLE FORK-GOLD HILL 5/45 RPR JUMS | SACTO | ETL.5140.INSL.NCER | 2025-05-28 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46532368 | T3 MIDDLE FORK-GOLD HILL 5/45 RPR JUMS | ICS
LC | 131292876 | 017/117 | T3 ROCK CREEK POE 17/117 TOUCH | TABLEMTN | ETL.5630.TOWR | 2025-05-28 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair
LC | 131292966 | 004/095 | T3 DRM-SPLDNG 4/95 RPL HRDW | SACTO | ETL.6770.POLE.NWOD | 2025-05-28 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace | 46532606 | T3 DRM-SPLDNG 4/95 RPL HRDW | ICW
LC | 131293030 | 008/117 | T3 MIDDLE FORK #1 8/117 TOUCH | SACTO | ETL.8405.POLE.NWOD | 2025-05-28 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46530492 | T3 MIDDLE FORK #1 8/117 TOUCH | ICQ
LC | 131297190 | 000/015 | T3 ORO FINO TAP 000/015 RPR JUMW | TABLEMTN | ETL.6721.INSL.NCER | 2025-05-29 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46537285 | T3 ORO FINO TAP 000/015 RPR JUMW | ICW
LC | 131297396 | 004/074 | T3 MIDDLEFORK #1 004/074 RPR JUMW | SACTO | ETL.8405.INSL.NCER | 2025-05-29 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46532608 | T3 MIDDLEFORK #1 004/074 RPR JUMW | ICW
LC | 131297422 | 003/038 | T3 GEYSERS #3-CLOVERDALE 3/38 RPR JUMW | LAKEVLLE | ETL.1650.INSL.NCER | 2025-05-29 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46539735 | T3 GEYSERS #3-CLOVERDALE 3/38 RPR JUMW | ICW
LC | 131336521 | 003/036B | T3 SLY CREEK TAP-03/36B RPR JUMW | TABLEMTN | ETL.4221.INSL.NCER | 2025-06-09 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46541728 | T3 SLY CREEK TAP-03/36B RPR JUMW | ICW
LC | 131336636 | 003/036A | T3 SLY CREEK TAP 3/36A RPR JUMW | TABLEMTN | ETL.4221.INSL.NCER | 2025-06-09 | 2025-05-07 | 2025-05-07 | TBC |  | 2025-11-07 | 2025-11-07 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46541729 | T3 SLY CREEK TAP 3/36A RPR JUMW | ICW
LC | 131215192 | 012/270 | T3 KILARC CEDAR CRK 12/270 RPR STRW | TABLEMTN | ETL.7290.POLE.NWOD | 2025-05-08 | 2025-05-08 | 2025-05-08 | TBC |  | 2025-11-08 | 2025-11-08 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46528459 | T3 KILARC CEDAR CRK 12/270 RPR STRW | ICW
LC | 131250068 | 005/064 | T3 GEYSERS #3 CLOVERDALE 5/64 RMV VEG | LAKEVLLE | ETL.1650.POLE.WOOD | 2025-05-15 | 2025-05-08 | 2025-05-08 | TBC |  | 2025-11-08 | 2025-11-08 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131297280 | 017/086 | T3 MONTA VISTA-COYOTE SS 17/86 RPR SHLS | MOSSLNDG | ETL.5090.TOWR | 2025-05-29 | 2025-05-08 | 2025-06-20 | On-Time |  | 2025-11-08 | 2025-11-08 | 628 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46538196 | T3 MONTA VISTA-COYOTE SS 17/86 RPR SHLS | ICS
LC | 131336694 | 017/083 | T3 MONTA VISTA COYOTE SW 17/83 RPR SHLS | METCALF | ETL.5090.TOWR | 2025-06-09 | 2025-05-08 | 2025-05-08 | TBC |  | 2025-11-08 | 2025-11-08 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE COMP OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46540845 | T3 MONTA VISTA COYOTE SW 17/83 RPR SHLS | ICS
LC | 128730688 | 009/117 | T2 IGNACIO-BOLINAS #2 09/117 RPL INSW | LAKEVLLE | ETL.7180.INSL.NCER | 2024-05-09 | 2024-05-09 | 2024-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 508T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH FMOB XMPT TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573788 | T2 IGNACIO-BOLINAS #2 09/117 RPL INSW | 93I
LC | 128733427 | 072/367 | T2 MALIN-ROUND MTN #2 72/367 RPR ANCT | TABLEMTN | ETL.6020.TOWR | 2024-05-09 | 2024-05-09 | 2024-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH FMOB XMPT TR2 PRTO CLMB FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46381412 | T2 EI MALIN-ROUND MTN#2 72/367 RPR ANCT | ICQ
LC | 131236688 | 000/002 | T3 BEARDSLEY TAP 00/02R RPR STRW | VICTOR | ETL.1401.POLE.WDPS | 2025-05-12 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46530938 | T3 BEARDSLEY TAP 00/02R RPR STRW | ICW
LC | 131260716 | 002/015 | T3 MORAGA OAKLAND #1 2/15 TOUCH | CONCORD | ETL.2720.TOWR | 2025-05-19 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46530063 | T3 MORAGA OAKLAND #1 2/15 TOUCH | ICQ
LC | 131260771 | T071 | T3 MIDWAY SANTA MARIA T071 RMV VEG | PISMOBCH | ETL.9240.TOWR | 2025-05-19 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 PRTO AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131260780 | 002/015 | T3 MORAGA-OAKLAND #1 2/15 RPR STRT | CONCORD | ETL.2720.TOWR | 2025-05-19 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46527534 | T3 MORAGA-OAKLAND #1 2/15 RPR STRT | ICQ
LC | 131260814 | 000/003 | T3 MORAGA OAKLAND #1 0/3 TOUCH | CONCORD | ETL.2720.TOWR | 2025-05-19 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46530061 | T3 MORAGA OAKLAND #1 0/3 TOUCH | ICQ
LC | 131260951 | 000/004 | T3 MORAGA OAKLAND #1 0/4 TOUCH | CONCORD | ETL.2720.TOWR | 2025-05-19 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46530062 | T3 MORAGA OAKLAND #1 0/4 TOUCH | ICQ
LC | 131274687 | 011/043 | T3 PITTSBURG SAN MATEO 11/43 RPR INSS | CONCORD | ETL.5463.INSL | 2025-05-22 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46529986 | T3 PITTSBURG SAN MATEO 11/43 RPR INSS | ICS
LC | 131297289 | T070 | T3 MIDWAY-SANTA MARIA T070 RMV VEG | PISMOBCH | ETL.9240.TOWR | 2025-05-29 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB BRIN | Overgrown | Vegetation-Tower | Cage Clearing
LC | 131300215 | 000/001 | T3 MORAGA-OAKLAND #2 00/01 RPR JUMS | CONCORD | ETL.2730.INSL | 2025-05-30 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46532265 | T3 MORAGA-OAKLAND #2 00/01 RPR JUMS | ICS
LC | 131300217 | T056 | T3 MIDWAY-SANTA MARIA T056 RMV VEG | PISMOBCH | ETL.9240.TOWR | 2025-05-30 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 AIR FRAB BRIN | Overgrown | Vegetation-Tower | Cage Clearing
LC | 131300219 | T056 | T3 MIDWAY-SANTA MARIA T056 RPR STRT | PISMOBCH | ETL.9240.TOWR | 2025-05-30 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46532460 | T3 MIDWAY-SANTA MARIA T056 RPR STRT | ICQ
LC | 131300303 | T055 | T3 MIDWAY-SANTA MARIA T055 RMV VEG | PISMOBCH | ETL.9240.TOWR | 2025-05-30 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 AIR FRAB BRIN | Overgrown | Vegetation-Tower | Cage Clearing
LC | 131307624 | 002/017 | T3 MORAGA OAKLAND #2 02/016 RPR CRST | CONCORD | ETL.2730.INSL.NCER | 2025-06-02 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Crossarm-Tower | Repair | 46537573 | T3 MORAGA OAKLAND#1 02/016 RPR CRST | ICQ
LC | 131307763 | 000/005 | T3 MRGA-OKLND #3 0/5 RPR JUMS | CONCORD | ETL.2750.INSL.NCER | 2025-06-02 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46532266 | T3 MRGA-OKLND #3 0/5 RPR JUMS | ICS
LC | 131307783 | 012/089 | T3 MRGA-LKWK 12/89 RPR CRST | CONCORD | ETL.3741.INSL | 2025-06-02 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Crossarm-Tower | Repair | 46537571 | T3 MRGA-LKWK 12/89 RPR CRST | ICQ
LC | 131350228 | 002/017 | T3 CW MORAGA-OAKLAND #3 2/17 TOUCH | CONCORD | ETL.2740.TOWR | 2025-06-10 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair
LC | 131350496 | 005/047 | T3 SLY CREEK TAP 005/047 RPR INSW | TABLEMTN | ETL.4221.INSL.CERA | 2025-06-10 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46541731 | T3 SLY CREEK TAP 005/047 RPR INSW | ICW
LC | 131392627 | 002/017 | T3 MORAGA OAKLAND #1 02/017 RPR CRST | CONCORD | ETL.2720.INSL.NCER | 2025-06-23 | 2025-05-09 | 2025-05-09 | TBC |  | 2025-11-09 | 2025-11-09 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Crossarm-Tower | Repair | 46545312 | T3 MORAGA OAKLAND #1 02/017 RPR CRST | ICQ
LC | 128743216 | :001/010 | T2 BLLTA-RVRBNK-MLN SW ST :1/10 RPL POLE | VICTOR | ETL.1070.POLE.WOOD | 2024-05-10 | 2024-05-10 | 2025-06-04 | On-Time |  | 2025-11-10 | 2025-11-10 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB XMPT TR2 PRTO FRAB PGEQ | No Good/Out of Stdrd | Structure-Wood | Replace | 35554199 | T2 EI BLLT-RVRBNK-MLNS SS :0/11 RPL STRW | 70Y
LC | 131233703 | 016/123 | T3 TRINTY-COTTNWD 16/123L TOUCH | TABLEMTN | ETL.4040.POLE.STPS | 2025-05-12 | 2025-05-10 | 2025-05-10 | TBC |  | 2025-11-10 | 2025-11-10 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR3 NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46539591 | T3 TRINTY-COTTNWD 16/123L TOUCH | ICW
LC | 131236665 | ?009/000 | T3 SNEATH LANE-HLF MN BAY ?9/0C RMV VEG | METCALF | ETL.7212.POLE.WDPS | 2025-05-12 | 2025-05-10 | 2025-06-05 | On-Time |  | 2025-11-10 | 2025-11-10 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR3 PRTO AIR BRIN | Overgrown | Vegetation | Remove
LC | 131236692 | ?009/000 | T3 SNEATH LANE-HLF MN BAY ?9/0L RMV VEG | METCALF | ETL.7212.POLE.WDPS | 2025-05-12 | 2025-05-10 | 2025-06-05 | On-Time |  | 2025-11-10 | 2025-11-10 | 564 | TR3 |  | E - Schd Compl Yr 0 | Closed | POHW FIRE COMP OH TR3 PRTO AIR BRIN | Overgrown | Vegetation | Remove
LC | 131261008 | 005/048 | T3 SLY CRK TAP 5/48L TOUCH | TABLEMTN | ETL.4221.POLE.STPS | 2025-05-19 | 2025-05-10 | 2025-05-10 | TBC |  | 2025-11-10 | 2025-11-10 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46541720 | T3 SLY CRK TAP 5/48L TOUCH | ICW
LC | 131261009 | 003/039 | T3 DRUM-SUMMIT #1 003/039L RPL STRW | SACTO | ETL.1440.POLE.WDPS | 2025-05-19 | 2025-05-10 | 2025-05-10 | TBC |  | 2025-11-10 | 2025-11-10 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35643247 | T3 DRUM-SUMMIT #1 003/039L RPL STRW | 70Y
LC | 131261011 | 003/039 | T3 DRUM-SUMMIT #1 003/039R RPL STRW | SACTO | ETL.1440.POLE.WDPS | 2025-05-19 | 2025-05-10 | 2025-05-10 | TBC |  | 2025-11-10 | 2025-11-10 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35643247 | T3 DRUM-SUMMIT #1 003/039L RPL STRW | 70Y
LC | 131261036 | 005/048 | T3 SLY CRK TAP 5/48C TOUCH | TABLEMTN | ETL.4221.POLE.STPS | 2025-05-19 | 2025-05-10 | 2025-05-10 | TBC |  | 2025-11-10 | 2025-11-10 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46541721 | T3 SLY CRK TAP 5/48C TOUCH | ICW
LC | 131261037 | 005/048 | T3 MIDDLE FORK GOLD HILL 5/48L RPR SHLD | SACTO | ETL.5140.POLE.STPS | 2025-05-19 | 2025-05-10 | 2025-05-10 | TBC |  | 2025-11-10 | 2025-11-10 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR BRIN | No Good/Out of Stdrd | Shield Wire - Wood | Repair | 46532371 | T3 MIDDLE FORK GOLD HILL 5/48L RPR SHLD | ICW
LC | 131307454 | 004/039 | T3 SLY CREEK TAP 4/039 RPR JUMW | TABLEMTN | ETL.4221.INSL.NCER | 2025-06-02 | 2025-05-10 | 2025-05-10 | TBC |  | 2025-11-10 | 2025-11-10 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46541722 | T3 SLY CREEK TAP 4/039 RPR JUMW | ICW
LC | 131307628 | 001/034 | T3 FRNCH MDOW MDDL FRK 1/34 RPR GYWW | SACTO | ETL.6870.POLE.NWOD | 2025-06-02 | 2025-05-10 | 2025-05-10 | TBC |  | 2025-11-10 | 2025-11-10 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46532610 | T3 FRNCH MDOW MDDL FRK 1/34 RPR GYWW | ICW
LC | 129807100 | 050/284 | T2 DI TEMBLOR-SLO 50/284 RPL HNGR | MIDWAY | ETL.3960.INSL.NCER | 2024-11-13 | 2024-11-12 | 2024-11-12 | TBC |  | 2025-11-12 | 2025-11-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46394483 | T2 DI TEMBLOR-SLO 50/284 HANGER | ICQ
LC | 129807101 | 055/308 | T2 DI TEMBLOR-SLO 55/308 HANGER | MIDWAY | ETL.3960.INSL.NCER | 2024-11-13 | 2024-11-12 | 2024-11-12 | TBC |  | 2025-11-12 | 2025-11-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46393966 | T2 DI TEMBLOR-SLO 55/308 HANGER | ICQ
LC | 129808682 | 015/114 | T2 CARIBOU-TABLE MTN 15/114 RPL STRT | TABLEMTN | ETL.4440.TOWR | 2024-11-13 | 2024-11-12 | 2024-11-12 | TBC |  | 2025-11-12 | 2025-11-12 | 426 | TR2 |  | E - Schd Compl Yr 0 | Open | POHW CREW OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Tower | Replace | 31712967 | T2 CARIBOU-TABLE MTN 15/114 RPL TWR & RD | 70S
LC | 129848624 | 038/330 | T2 CASCADE-CTNWD 38/330 RPR JUMW | TABLEMTN | ETL.1240.INSL.NCER | 2024-11-21 | 2024-11-12 | 2025-05-01 | On-Time |  | 2025-05-12 | 2025-11-12 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46463882 | T2 CASCADE-CTNWD 38/330 RPR JUMW | ICW
LC | 130747452 | 018/098 | T2 RND MTN-TBL MTN #1 18/98 RPR STRT | TABLEMTN | ETL.6060.TOWR | 2025-01-15 | 2024-11-12 | 2024-11-12 | TBC |  | 2025-11-12 | 2025-11-12 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR CNCL OH TR2 FRAB | No Good/Out of Stdrd | Structure-Tower | Repair
LC | 131236387 | 005/050 | T3 MONTA VISTA-BURNS 5/50 CNCL | MOSSLNDG | ETL.7590.INSL.NCER | 2025-05-12 | 2025-05-12 | 2025-05-12 | TBC |  | 2025-11-12 | 2025-11-12 | 638T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Conductor-Wood | Replace | 35645990 | T3 MONTA VISTA-BURNS 5/50 RPL CNDW | 93C
LC | 131236671 | ?008/000 | T3 SNTH LN-HLF MN BY ?8/0 RPR JUMW | METCALF | ETL.7212.INSL.NCER | 2025-05-12 | 2025-05-12 | 2025-05-12 | TBC |  | 2025-11-12 | 2025-11-12 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46528086 | T3 SNTH LN-HLF MN BY ?8/0 RPR JUMW | ICW
LC | 131237206 | 013/001 | T3 MAPLE CREEK-HOOPA 013/001 RPR GYWW | EUREKA | ETL.7490.POLE.NWOD | 2025-05-13 | 2025-05-12 | 2025-05-12 | TBC |  | 2025-11-12 | 2025-11-12 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46525608 | T3 MAPLE CREEK-HOOPA 013/001 RPR GYWW | ICW
LC | 131241009 | 012/095 | T3 MNTA VSTA-BRNS 12/95 RPR CRSW | MOSSLNDG | ETL.7590.POLE.WOOD | 2025-05-13 | 2025-05-12 | 2025-05-12 | TBC |  | 2025-11-12 | 2025-11-12 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46530405 | T3 MNTA VSTA-BRNS 12/95 RPR CRSW | ICW
LC | 131241090 | 012/095 | T3 T2NT MNTA VSTA-BRNS 12/95 RPR GYWW | MOSSLNDG | ETL.7590.POLE.WOOD | 2025-05-13 | 2025-05-12 | 2025-05-12 | TBC |  | 2025-11-12 | 2025-11-12 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46530406 | T3 T2NT MNTA VSTA-BRNS 12/95 RPR GYWW | ICW
LC | 131265601 | 008/116 | T3 MIDDLE FORK #1 8/116 TOUCH | SACTO | ETL.8405.POLE.NWOD | 2025-05-20 | 2025-05-12 | 2025-06-04 | On-Time |  | 2025-11-12 | 2025-11-12 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46529671 | T3 MIDDLE FORK #1 8/116 TOUCH | ICQ
LC | 131307388 | 002/049 | T3 FRNCH MEDWS-MIDL FORK 02/49 COTTER | SACTO | ETL.6870.INSL.NCER | 2025-06-02 | 2025-05-12 | 2025-05-12 | TBC |  | 2025-11-12 | 2025-11-12 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46532609 | T3 FRNCH MEDWS-MIDL FORK 02/49 COTTER | ICW
LC | 131307632 | 008/114A | T3 MIDDLEFORK #1 008/114A RPR JUMS | SACTO | ETL.8405.INSL.NCER | 2025-06-02 | 2025-05-12 | 2025-05-12 | TBC |  | 2025-11-12 | 2025-11-12 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46532435 | T3 MIDDLEFORK #1 008/114A RPR JUMS | ICS
LC | 131307637 | 001/022 | T3 GEYSERS #3-CLOVERDALE 01/22 RPL STRW | LAKEVLLE | ETL.1650.POLE.WOOD | 2025-06-02 | 2025-05-12 | 2025-05-12 | TBC |  | 2025-11-12 | 2025-11-12 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35646583 | T3 GEYSERS #3-CLOVERDALE 01/22 RPL STRW | 70Y
LC | 131307671 | 013/001A | T3 UKIAH-HPLND-CLVRDL 13/1A RPR BOND | WILLITS | ETL.4050.INSL.NCER | 2025-06-02 | 2025-05-12 | 2025-05-12 | TBC |  | 2025-11-12 | 2025-11-12 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46544433 | T3 UKIAH-HPLND-CLVRDL 13/1A RPR BOND | ICW
LC | 131313737 | 000/001 | T3 EL DORADO-MISURI FLT#1-0/1 TOUCH | SACTO | ETL.1530.TOWR | 2025-06-03 | 2025-05-12 | 2025-05-12 | TBC |  | 2025-11-12 | 2025-11-12 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46539251 | T3 EL DORADO-MISURI FLT#1-0/1 TOUCH | ICQ
LC | 131359234 | 005/119 | T3 DRUM-SPAULDING 5/119 RPL INSW | SACTO | ETL.6770.INSL.NCER | 2025-06-12 | 2025-05-12 | 2025-05-12 | TBC |  | 2025-08-12 | 2025-11-12 | 508T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB DURA BRIN | No Good/Out of Stdrd | Insulator-Wood | Replace | 35648304 | T3 DRUM-SPAULDING 5/119 RPL INSW | 93I
LC | 128759435 | 066/333 | T2 MALIN-ROUND MTN#2 66/333 RPR GYWT | TABLEMTN | ETL.6020.TOWR | 2024-05-13 | 2024-05-13 | 2024-05-13 | TBC |  | 2025-11-13 | 2025-11-13 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Guy Wire-Tower | Repair | 46381422 | T2 EI MALIN-ROUND MTN#2 66/333 RPR GYWT | ICQ
LC | 128759580 | 066/334 | T2 MALIN-ROUND MTN#2 66/334 UNBURY | TABLEMTN | ETL.6020.TOWR | 2024-05-13 | 2024-05-13 | 2024-05-13 | TBC |  | 2025-11-13 | 2025-11-13 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | Earth Covered Tower | Foundation/Concrete-Tower | Repair | 46381425 | T2 EI MALIN-ROUND MTN#2 66/334 UNBURY | ICQ
LC | 129810010 | 129 | T2 DI SANTA YNEZ TAP A0/2 RPL SWITCH | PISMOBCH | ETL.3701.SWIT | 2024-11-13 | 2024-11-13 | 2025-04-17 | On-Time |  | 2025-11-13 | 2025-11-13 | 427 | TR2 |  | E - Schd Compl Yr 0 | Closed | REGW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Switch-Wood | Replace | 35511202 | T2 DI SANTA YNEZ TAP A0/2 RPL INSW | 93I
LC | 131240529 | 010/002A | T3 LAURELES-OTTER_010/002A RPR GYWW | MOSSLNDG | ETL.7380.POLE.WDPS | 2025-05-13 | 2025-05-13 | 2025-05-13 | TBC |  | 2025-11-13 | 2025-11-13 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46530407 | T3 LAURELES-OTTER_010/002A RPR GYWW | ICW
LC | 131240688 | 015/002 | T3 MAPLE CREEK-HOOPA 015/002 RPR GYWW | EUREKA | ETL.7490.POLE.NWOD | 2025-05-13 | 2025-05-13 | 2025-05-13 | TBC |  | 2025-11-13 | 2025-11-13 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46525609 | T3 MAPLE CREEK-HOOPA 015/002 RPR GYWW | ICW
LC | 131240715 | 015/004 | T3 MAPLE CREEK-HOOPA 15/004 RPL ANCW | EUREKA | ETL.7490.POLE.NWOD | 2025-05-13 | 2025-05-13 | 2025-05-13 | TBC |  | 2025-11-13 | 2025-11-13 | 637 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB NTDE BRIN | No Good/Out of Stdrd | Anchor-Wood | Replace | 35645018 | T3 MAPLE CREEK-HOOPA 15/004 RPL ANCW | 93E
LC | 131265539 | 005/136 | T3 DRUM-SPAULDING 5/136 RPR STRW | SACTO | ETL.6770.POLE.WOOD | 2025-05-20 | 2025-05-13 | 2025-06-22 | On-Time |  | 2025-11-13 | 2025-11-13 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46532603 | T3 DRUM-SPAULDING 5/136 RPR STRW | ICW
LC | 131270037 | 000/001 | T3 ORO FINO TAP 0/1 TOUCH | TABLEMTN | ETL.6721.POLE.NWOD | 2025-05-21 | 2025-05-13 | 2025-05-13 | TBC |  | 2025-11-13 | 2025-11-13 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 PRTO AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46530504 | T3 ORO FINO TAP 0/1 TOUCH | ICW
LC | 131274684 | 021/153A | T3 TRINITY COTTONWOOD 21/153A RPR GYWW | TABLEMTN | ETL.4040.POLE.NWOD | 2025-05-22 | 2025-05-13 | 2025-05-13 | TBC |  | 2025-11-13 | 2025-11-13 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46539580 | T3 TRINITY COTTONWOOD 21/153A RPR GYWW | ICW
LC | 131274751 | 021/153B | T3 TRINITY COTTONWOOD 21/153B RPR GYWW | TABLEMTN | ETL.4040.POLE.NWOD | 2025-05-22 | 2025-05-13 | 2025-05-13 | TBC |  | 2025-11-13 | 2025-11-13 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46539581 | T3 TRINITY COTTONWOOD 21/153B RPR GYWW | ICW
LC | 131313424 | 000/005 | T3 ORO FINO TAP 0/5 TOUCH | TABLEMTN | ETL.6721.POLE.NWOD | 2025-06-03 | 2025-05-13 | 2025-05-13 | TBC |  | 2025-11-13 | 2025-11-13 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46539582 | T3 ORO FINO TAP 0/5 TOUCH | ICW
LC | 131313499 | 002/027 | T3 GEYSERS #3 CLOVERDALE 2/27 RPR JUMW | LAKEVLLE | ETL.1650.INSL.NCER | 2025-06-03 | 2025-05-13 | 2025-05-13 | TBC |  | 2025-11-13 | 2025-11-13 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW ACCM OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46539736 | T3 GEYSERS #3 CLOVERDALE 2/27 RPR JUMW | ICW
LC | 131324222 | 000/000 | T3 EL DRDO-MISSOURI FLT #2 0/0R TOUCH | SACTO | ETL.1540.POLE.STPS | 2025-06-05 | 2025-05-13 | 2025-05-13 | TBC |  | 2025-11-13 | 2025-11-13 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 AIR NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair
LC | 131359055 | 005/137 | T3 DRUM-SPAULDING 5/137 RPR CRSW | SACTO | ETL.6770.POLE.WOOD | 2025-06-12 | 2025-05-13 | 2025-05-13 | TBC |  | 2025-11-13 | 2025-11-13 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Crossarm-Wood | Repair | 46542556 | T3 DRUM-SPAULDING 5/137 RPR CRSW | ICW
LC | 131370173 | 020/147B | T3 TRINITY COTNWD 20/147B RPR GYWW | TABLEMTN | ETL.4040.POLE.NWOD | 2025-06-16 | 2025-05-13 | 2025-05-13 | TBC |  | 2025-11-13 | 2025-11-13 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair
LC | 131242393 | ?001/000 | T3 SNEATH LANE-HLF MN BAY ?1/0 RPL STRW | METCALF | ETL.7212.POLE.WOOD | 2025-05-14 | 2025-05-14 | 2025-05-14 | TBC |  | 2025-11-14 | 2025-11-14 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW TNT OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35647513 | T3 SNEATH LANE-HLF MN BAY ?1/0 RPL STRW | 70Y
LC | 131242522 | 39 | T3 MONTA VISTA-BURNS 014/121 RPR SWTC | MOSSLNDG | ETL.7590.SWIT | 2025-05-14 | 2025-05-14 | 2025-05-14 | TBC |  | 2025-11-14 | 2025-11-14 | 623 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB TR3 FRAB BRIN | Out of Adjustment | Switch | Repair | 46530408 | T3 MONTA VISTA-BURNS 014/121 RPR SWTC | ICE
LC | 131244785 | 005/047 | T3 ATASCADERO-CAYUCOS 005/047 RPR STRW | PISMOBCH | ETL.8480.POLE.WOOD | 2025-05-14 | 2025-05-14 | 2025-05-14 | TBC |  | 2025-11-14 | 2025-11-14 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP RESD REAR SWRK CLR ACCL OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46529916 | T3 ATASCADERO-CAYUCOS 005/047 RPR STRW | ICW
LC | 131246146 | 012/011 | T3 LAURELES-OTTER 012/011 CGI | MOSSLNDG | ETL.7380.POLE.WOOD | 2025-05-14 | 2025-05-14 | 2025-05-14 | TBC |  | 2025-08-14 | 2025-11-14 | 625 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 FRAB NTDE DURA BRIN | Vegetation Overgrown | Other | Access Issue
LC | 131274785 | 008/069 | T3 MIDDLE FORK-GOLD HILL 8/69 TOUCH | SACTO | ETL.5140.TOWR | 2025-05-22 | 2025-05-14 | 2025-06-04 | On-Time |  | 2025-11-14 | 2025-11-14 | 543 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46530493 | T3 MIDDLE FORK-GOLD HILL 8/69 TOUCH | ICQ
LC | 131286276 | 016/005 | T3 UKIAH HOPLAND CLVRDL 16/5 RPL STRW | WILLITS | ETL.4050.POLE.WOOD | 2025-05-27 | 2025-05-14 | 2025-05-14 | TBC |  | 2025-11-14 | 2025-11-14 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCM OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35645435 | T3 UKIAH HOPLAND CLVRDL 16/5 RPL STRW | 70Y
LC | 131324055 | 016/002 | T3 UKIAH-HOPLAND-CLVRDLE 16/2 RPR JMPW | WILLITS | ETL.4050.INSL.NCER | 2025-06-05 | 2025-05-14 | 2025-05-14 | TBC |  | 2025-11-14 | 2025-11-14 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46544435 | T3 UKIAH-HOPLAND-CLVRDLE 16/2 RPR JMPW | ICW
LC | 131324098 | 010/120 | T3 GEYERS #3 CLOVERDALE 10/120 RPR INSS | LAKEVLLE | ETL.1650.INSL.CERA | 2025-06-05 | 2025-05-14 | 2025-05-14 | TBC |  | 2025-11-14 | 2025-11-14 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46544483 | T3 GEYERS #3 CLOVERDALE 10/120 RPR INSS | ICS
LC | 131324267 | 006/165 | T3 DRUM-SPAULDING 006/165 RPL STRW | SACTO | ETL.6770.POLE.WOOD | 2025-06-05 | 2025-05-14 | 2025-05-14 | TBC |  | 2025-11-14 | 2025-11-14 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35646826 | T3 DRUM-SPAULDING 006/165 RPL STRW | 70Y
LC | 131370271 | 006/158 | T3 DRUM-SPAULDING 06/158 RPR WDPKR | SACTO | ETL.6770.POLE.WOOD | 2025-06-16 | 2025-05-14 | 2025-05-14 | TBC |  | 2025-11-14 | 2025-11-14 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46543516 | T3 DRUM-SPAULDING 06/158 RPR WDPKR | ICW
LC | 131377951 | 008/067 | T3 MIDDLE FORK GOLD HILL 8/67 RPR JUMP | SACTO | ETL.5140.INSL | 2025-06-17 | 2025-05-14 | 2025-05-14 | TBC |  | 2025-11-14 | 2025-11-14 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46543518 | T3 MIDDLE FORK GOLD HILL 8/67 RPR JUMP | ICS
LC | 131377958 | 005/066 | T3 DRUM SUMMIT #1 5/66 RPR JUMW | SACTO | ETL.1440.INSL.NCER | 2025-06-17 | 2025-05-14 | 2025-05-14 | TBC |  | 2025-11-14 | 2025-11-14 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair
LC | 131378259 | 008/113 | T3 MIDDLEFORK #1 8/113 RPR JUMW | SACTO | ETL.8405.INSL.CERA | 2025-06-17 | 2025-05-14 | 2025-05-14 | TBC |  | 2025-11-14 | 2025-11-14 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair
LC | 131380362 | 75 | T3 DESABLA-CENTERVILLE 00/01B RPR JUMW | TABLEMTN | ETL.6720.SWIT | 2025-06-18 | 2025-05-14 | 2025-05-14 | TBC |  | 2025-11-14 | 2025-11-14 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46545118 | T3 DESABLA-CENTERVILLE 00/01B RPR JUMW | ICW
LC | 129829147 | 024/160 | T2 DI POE-RIO OSO 024/160 BNT STEEL | TABLEMTN | ETL.5540.TOWR | 2024-11-18 | 2024-11-15 | 2024-11-15 | TBC |  | 2025-11-15 | 2025-11-15 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46416695 | T2 DI POE-RIO OSO 024/160 BNT STEEL | ICQ
LC | 129830426 | 011/201 | T2 DI TEJON-LEBEC 011/201 RPR GYWW | MIDWAY | ETL.9250.POLE.WOOD | 2024-11-18 | 2024-11-15 | 2025-02-10 | On-Time |  | 2025-11-15 | 2025-11-15 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46452948 | T2 DI TEJON-LEBEC 011/201 RPR GYWW | ICW
LC | 131249344 | 022/011 | T3 MAPLE CREEK-HOOPA 22/011 RPL STRW | EUREKA | ETL.7490.POLE.WOOD | 2025-05-15 | 2025-05-15 | 2025-05-15 | TBC |  | 2025-11-15 | 2025-11-15 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35642891 | T3 MAPLE CREEK-HOOPA 22/011 RPL STRW | 70Y
LC | 131260512 | 017/002 | T3 MONTE RIO-FORT ROSS 17/02R RPL POLE | LAKEVLLE | ETL.6979.POLE.WDPS | 2025-05-19 | 2025-05-15 | 2025-05-15 | TBC |  | 2025-11-15 | 2025-11-15 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OTHR FIRE OH TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35636426 | T3 T2NT DI MNT RIOFRT RSS 17/1A RPL STRW | 70Y
LC | 131260516 | 017/002 | T3 MONTE RIO-FORT ROSS 17/02C RPL POLE | LAKEVLLE | ETL.6979.POLE.WDPS | 2025-05-19 | 2025-05-15 | 2025-05-15 | TBC |  | 2025-11-15 | 2025-11-15 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OTHR FIRE OH TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35636426 | T3 T2NT DI MNT RIOFRT RSS 17/1A RPL STRW | 70Y
LC | 131261821 | 017/001 | T3 MONTE RIO-FORT ROSS 17/1L RPL POLE | LAKEVLLE | ETL.6979.POLE.WDPS | 2025-05-20 | 2025-05-15 | 2025-05-15 | TBC |  | 2025-11-15 | 2025-11-15 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OTHR FIRE OH TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35636426 | T3 T2NT DI MNT RIOFRT RSS 17/1A RPL STRW | 70Y
LC | 131261823 | 017/001 | T3 MONTE RIO-FORT ROSS 17/1C RPL POLE | LAKEVLLE | ETL.6979.POLE.WDPS | 2025-05-20 | 2025-05-15 | 2025-05-15 | TBC |  | 2025-11-15 | 2025-11-15 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OTHR FIRE OH TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35636426 | T3 T2NT DI MNT RIOFRT RSS 17/1A RPL STRW | 70Y
LC | 131261824 | 017/001 | T3 MONTE RIO-FORT ROSS 17/1R RPL POLE | LAKEVLLE | ETL.6979.POLE.WDPS | 2025-05-20 | 2025-05-15 | 2025-05-15 | TBC |  | 2025-11-15 | 2025-11-15 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OTHR FIRE OH TR3 PRTO BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35636426 | T3 T2NT DI MNT RIOFRT RSS 17/1A RPL STRW | 70Y
LC | 131292984 | 003/026 | T3 MORAGA-CLAREMONT #1 003/026 TOUCH | CONCORD | ETL.2700.TOWR | 2025-05-28 | 2025-05-15 | 2025-05-15 | TBC |  | 2025-11-15 | 2025-11-15 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46539822 | T3 MORAGA-CLAREMONT #1 003/026 TOUCH | ICQ
LC | 131324382 | 000/012 | T3 DESABLA-CENTERVILLE 000/012 TOUCH | TABLEMTN | ETL.6720.POLE.NWOD | 2025-06-05 | 2025-05-15 | 2025-05-15 | TBC |  | 2025-11-15 | 2025-11-15 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46540281 | T3 DESABLA-CENTERVILLE 000/012 TOUCH | ICW
LC | 131251668 | 27 | T3 DRUM-GRASS VLLY-WMR B017/385 RPR SWTC | SACTO | ETL.6760.SWIT | 2025-05-16 | 2025-05-16 | 2025-05-16 | TBC |  | 2025-08-16 | 2025-11-16 | 623 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB TR3 FRAB DURA BRIN | Out of Adjustment | Switch | Repair | 46539205 | T3 DRUM-GRASS VLLY-WMR B017/385 RPR SWTC | ICE
LC | 129078065 | :006/002 | T2 DI CARIBOU#2 :6/2 RPR IBWW | TABLEMTN | ETL.6280.INSL.CERA | 2024-06-14 | 2024-05-17 | 2025-06-23 | On-Time |  | 2025-11-17 | 2025-11-17 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46337211 | T2 DI CARIBOU#2 :6/2 RPR IBWW | ICW
LC | 124932150 | 087/440 | T2NT DI MALIN-RND MTN #2 87/440 RPR STRT | TABLEMTN | ETL.6020.TOWR | 2022-11-23 | 2022-11-18 | 2023-08-21 | On-Time |  | 2025-11-18 | 2025-11-18 | 543 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH TR2N PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45717902 | T2 DI MALIN-RND MTN #2 087/440 RPR STRT | ICQ
LC | 130759116 | 001/010 | T2 BUTT VALLEY-CARIBOU 1/10 RPR STRT | TABLEMTN | ETL.1180.TOWR | 2025-01-16 | 2024-11-18 | 2024-11-18 | TBC |  | 2025-11-18 | 2025-11-18 | 543 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR2 FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46472257 | T2 BUTT VALLEY-CARIBOU 001/010 RPR STRT | ICQ
LC | 131257393 | 017/197 | T3 IGNACIO-BOLINAS #2 17/197 TOUCH | LAKEVLLE | ETL.7180.POLE.NWOD | 2025-05-19 | 2025-05-19 | 2025-05-19 | TBC |  | 2025-11-19 | 2025-11-19 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW OH FMOB TR3 FRAB NTDE PGEQ BRIN | No Good/Out of Stdrd | Structure-Wood | Repair
LC | 131257839 | 001/021 | T3 ORO FINO TAP 001/021 GO95 | TABLEMTN | ETL.6721.POLE.WOOD | 2025-05-19 | 2025-05-19 | 2025-05-19 | TBC |  | 2025-11-19 | 2025-11-19 | 401T | TR3 |  | E - Schd Compl Yr 0 | Open | POHW INSP OH FMOB TR3 PRTO FRAB NTDE SR22 BRIN | Overloaded | GO95 Clear Infract-Wood | Replace | 35642483 | T3 ORO FINO TAP 001/019 GO95 | 93G
LC | 131258128 | 006/055 | T3 ATASCADERO-CAYUCOS 006/055 RPL RPTW | PISMOBCH | ETL.8480.POLE.NWOD | 2025-05-19 | 2025-05-19 | 2025-05-19 | TBC |  | 2025-11-19 | 2025-11-19 | 593 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP REMT SWRK ACCL OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Raptor Guard-Wood | Replace | 46529917 | T3 ATASCADERO-CAYUCOS 006/055 RPL RPTW | ICB
LC | 131258129 | 006/055 | T3 ATASCADERO-CAYUCOS 006/055 RPR GYWW | PISMOBCH | ETL.8480.POLE.NWOD | 2025-05-19 | 2025-05-19 | 2025-05-19 | TBC |  | 2025-11-19 | 2025-11-19 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP REMT SWRK ACCL OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46529918 | T3 ATASCADERO-CAYUCOS 006/055 RPR GYWW | ICW
LC | 131258828 | 006/094 | T3 WEIMAR #1 06/094 RPL STRW | SACTO | ETL.7560.POLE.WOOD | 2025-05-19 | 2025-05-19 | 2025-05-19 | TBC |  | 2025-11-19 | 2025-11-19 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | REGW CREW OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 74032504 | WEIMAR #1 60 KV RECONDUCTOR | 93P
LC | 131259884 | 005/042 | T3 TIGER CREEK-ELECTRA 005/042 TOUCH | VICTOR | ETL.5780.TOWR | 2025-05-19 | 2025-05-19 | 2025-05-19 | TBC |  | 2025-11-19 | 2025-11-19 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR3 FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46530701 | T3 TIGER CREEK-ELECTRA 005/042 TOUCH | ICQ
LC | 131260376 | 008/065 | T3 TIGER CREEK-VALLEY SPRINGS 8/65 TOUCH | VICTOR | ETL.5790.TOWR | 2025-05-19 | 2025-05-19 | 2025-05-19 | TBC |  | 2025-11-19 | 2025-11-19 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR3 FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46530704 | T3 TIGER CREEK-VALLEY SPRINGS 8/65 TOUCH | ICQ
LC | 131264472 | 002/021 | T3 TIGER CRK-VALLEY SPRGS 2/21 RPR STRT | VICTOR | ETL.5790.TOWR | 2025-05-20 | 2025-05-20 | 2025-05-20 | TBC |  | 2025-11-20 | 2025-11-20 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR3 FRAB DURA | Missing | Hardware-Tower | Install | 46538226 | T3 TIGER CRK-VALLEY SPRGS 2/21 RPR STRT | ICQ
LC | 128824844 | 011/138 | T2 DRUM-SUMMIT#2 11/138L RPL STRW | SACTO | ETL.1450.POLE.WDPS | 2024-05-21 | 2024-05-21 | 2025-06-27 | On-Time |  | 2025-11-21 | 2025-11-21 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO | No Good/Out of Stdrd | Structure-Wood | Replace | 35631087 | T2 DRUM-SUMMIT #2 11/138R RPL STRW | 70Y
LC | 131269140 | 024/010 | T3 MAPLE CREEK-HOOPA 024/010 RPR STRW | EUREKA | ETL.7490.POLE.WOOD | 2025-05-21 | 2025-05-21 | 2025-05-21 | TBC |  | 2025-11-21 | 2025-11-21 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46531224 | T3 MAPLE CREEK-HOOPA 024/010 RPR STRW | ICW
LC | 128839052 | 058/247B | T2 EI RND MTN-TBL MN #1 58/247B RPR ANCT | TABLEMTN | ETL.6060.POLE.NWOD | 2024-05-22 | 2024-05-22 | 2024-05-22 | TBC |  | 2025-11-22 | 2025-11-22 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46310392 | T2 EI RND MTN-TBL MN #1 58/247B RPR ANCT | ICQ
LC | 128839564 | 007/086 | T2 EI DRUM-SUMMIT #1_007/086 RPL INSW | SACTO | ETL.1440.INSL | 2024-05-22 | 2024-05-22 | 2025-06-03 | On-Time |  | 2025-11-22 | 2025-11-22 | 508T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35573503 | T2 EI DRUM-SUMMIT #1_007/086 RPL INSW | 93I
LC | 131272158 | 017/202 | T3 IGNACIO-BOLINAS #2 017/202 TOUCH | LAKEVLLE | ETL.7180.POLE.NWOD | 2025-05-22 | 2025-05-22 | 2025-05-22 | TBC |  | 2025-11-22 | 2025-11-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 FRAB NTDE PGEQ BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46542258 | T3 IGNACIO-BOLINAS #2 017/202 TOUCH | ICW
LC | 131273664 | 012/013 | T3 MAPLE CREEK-HOOPA 012/013 RPL HRDD | EUREKA | ETL.7490.POLE.NWOD | 2025-05-22 | 2025-05-22 | 2025-05-22 | TBC |  | 2025-11-22 | 2025-11-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 PRTO FRAB BRIN | No Good/Out of Stdrd | Hardware-Wood | Replace | 46531197 | T3 MAPLE CREEK-HOOPA 012/013 RPL HRDD | ICW
LC | 131286412 | 003/024 | T3 MORAGA-CLAREMT #1 3/24 TOUCH | CONCORD | ETL.2700.TOWR | 2025-05-27 | 2025-05-22 | 2025-05-22 | TBC |  | 2025-11-22 | 2025-11-22 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46539823 | T3 MORAGA-CLAREMT #1 3/24 TOUCH | ICQ
LC | 131286413 | 003/024 | T3 MORAGA-CLAREMT #1 3/24 RPR JUMS | CONCORD | ETL.2700.INSL | 2025-05-27 | 2025-05-22 | 2025-05-22 | TBC |  | 2025-08-22 | 2025-11-22 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB DURA BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46544945 | T3 MORAGA-CLAREMT #1 3/24 RPR JUMS | ICS
LC | 131286414 | 003/024 | T3 MORAGA-CLAREMT #1 3/24 RPL HRDT | CONCORD | ETL.2700.TOWR | 2025-05-27 | 2025-05-22 | 2025-05-22 | TBC |  | 2025-11-22 | 2025-11-22 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Hardware-Tower | Replace | 46539821 | T3 MORAGA-CLAREMT #1 3/24 RPL HRDT | ICQ
LC | 131307498 | 005/046 | T3 SOBRANTE-GRZLY CLRMNT #1 5/046 TOUCH | CONCORD | ETL.3740.TOWR | 2025-06-02 | 2025-05-22 | 2025-05-22 | TBC |  | 2025-11-22 | 2025-11-22 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46539825 | T3 SOBRANTE-GRZLY CLRMNT #1 5/046 TOUCH | ICQ
LC | 131307566 | 000/005C | T3 DRUM-SMMT #2 0/5C RPR GYWW | SACTO | ETL.1450.POLE.NWOD | 2025-06-02 | 2025-05-22 | 2025-06-20 | On-Time |  | 2025-11-22 | 2025-11-22 | 630 | TR3 |  | E - Schd Compl Yr 0 | Closed | RELW FIRE SPCR ACCL COMP OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46539204 | T3 DRUM-SMMT #2 0/5C RPR GYWW | ICW
LC | 131307643 | 024/198 | T3 CRBRY SWSTA RND MTN 24/198 RPL HRDT | TABLEMTN | ETL.5410.TOWR | 2025-06-02 | 2025-05-22 | 2025-05-22 | TBC |  | 2025-11-22 | 2025-11-22 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Hardware-Tower | Replace | 46539254 | T3 CRBRY SWSTA RND MTN 24/198 RPL HRDT | ICQ
LC | 131370251 | 020/191 | T3 ROUND MTN-CTONWOD #2 20/191 RPR OPGW | TABLEMTN | ETL.5640.TOWR | 2025-06-16 | 2025-05-22 | 2025-05-22 | TBC |  | 2025-11-22 | 2025-11-22 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46545202 | T3 ROUND MTN-CTONWOD #2 20/191 RPR OPGW | ICS
LC | 131307664 | 000/010 | T3 GEYSERS #5-GEYSERS #3 0/010 RPL STRW | LAKEVLLE | ETL.1670.POLE.WOOD | 2025-06-02 | 2025-05-23 | 2025-05-23 | TBC |  | 2025-11-23 | 2025-11-23 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35647223 | T3 GEYSERS #5-GEYSERS #3 0/010 RPL STRW | 70Y
LC | 131378076 | 000/004 | T3 GEYSERS #13 TAP 0/4 TOUCH | LAKEVLLE | ETL.4781.TOWR | 2025-06-17 | 2025-05-23 | 2025-05-23 | TBC |  | 2025-11-23 | 2025-11-23 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCL OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46544486 | T3 GEYSERS #13 TAP 0/4 TOUCH | ICQ
LC | 128896332 | 053/1026 | T2 HT CRK #1-WSTWD 53/1026 COMPLETE | TABLEMTN | ETL.7030.POLE.WOOD | 2024-05-28 | 2024-05-24 | 2025-05-21 | On-Time |  | 2025-11-24 | 2025-11-24 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35574722 | T2 EI HT CRK #1-WSTWD 53/1026 RPL POLE | 70Y
LC | 128891459 | 000/002 | T2 EI SPAULDING-SUMMIT 0/2 RPL INSW | SACTO | ETL.8060.INSL.NCER | 2024-05-25 | 2024-05-25 | 2024-05-25 | TBC |  | 2025-11-25 | 2025-11-25 | 508T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Replace | 35572861 | T2 EI SPAULDING-SUMMIT 000/002 RPL INSW | 93I
LC | 129121003 | 004/139 | T2 SPAULDNG-SUMMIT 4/139 RPR STRW | SACTO | ETL.8060.POLE.WOOD | 2024-06-24 | 2024-05-25 | 2025-05-29 | On-Time |  | 2025-11-25 | 2025-11-25 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46398070 | T2 DI SPAULDNG-SUMMIT 4/139 RPR WDPK | ICW
LC | 129879508 | 027/007 | T2 DI RIO DLL JCT-BRDGVLLE 27/7 RPL SPLW | EUREKA | ETL.7850.INSL.NCER | 2024-11-27 | 2024-11-25 | 2024-11-25 | TBC |  | 2025-11-25 | 2025-11-25 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OH TR2 PRTO AIR NTDE | No Good/Out of Stdrd | Splice-Wood | Replace | 46419584 | T2 DI RIO DLL JCT-BRDGVLLE 27/7 RPL SPLW | ICW
LC | 129879520 | 019/012-GUY | T2 DI FRT BRGG-ELK 19/12-GUY RPL STRW | WILLITS | ETL.2060.POLE.WOOD | 2024-11-27 | 2024-11-27 | 2025-02-24 | On-Time |  | 2025-11-27 | 2025-11-27 | 372T | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | Rotten | Guy Pole-Wood | Replace | 35604414 | T2 DI FRT BRGG-ELK 19/12-GUY RPL STRW | 70Y
LC | 131313687 | 018/173 | T3 ROUND MNTN-CTNWD #2 18/173 RPR OPGW | TABLEMTN | ETL.5640.TOWR | 2025-06-03 | 2025-05-27 | 2025-05-27 | TBC |  | 2025-11-27 | 2025-11-27 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46539213 | T3 ROUND MNTN-CTNWD #2 18/173 RPR OPGW | ICS
LC | 131395651 | 017/170 | T3 RND MTN-CTTNWD #2 17/170 RPR OPGW | TABLEMTN | ETL.5640.TOWR | 2025-06-23 | 2025-05-27 | 2025-05-27 | TBC |  | 2025-11-27 | 2025-11-27 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB | No Good/Out of Stdrd | OPGW - Steel | Repair | 46545201 | T3 RND MTN-CTTNWD #2 17/170 RPR OPGW | ICS
LC | 124953836 | 023/126 | T3NT WV EI PARKWY-MORAGA 23/126 RPR INSS | CONCORD | ETL.4340.INSL.NCER | 2022-11-30 | 2022-11-28 | 2024-04-27 | On-Time |  | 2025-11-28 | 2025-11-28 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3N PRTO NTDE | No Good/Out of Stdrd | Insulator-Steel | Repair | 46078367 | T3NT WV EI PARKWY-MORAGA 23/126 RPR INSS | ICS
LC | 124953837 | 022/125 | T3NT WV PARKWAY-MORAGA 22/125 RPR INSS | CONCORD | ETL.4340.INSL.NCER | 2022-11-30 | 2022-11-28 | 2024-04-27 | On-Time |  | 2025-11-28 | 2025-11-28 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3N PRTO NTDE | No Good/Out of Stdrd | Insulator-Steel | Repair | 46078368 | T3NT WV PARKWAY-MORAGA 22/125 RPR INSS | ICS
LC | 128173214 | 022/003 | T2 EI COPPERMINE-TIVY VLY 22/3 RPR BOND | FRESNO | ETL.8590.INSL.NCER | 2024-02-14 | 2024-02-14 | 2024-02-14 | TBC |  | 2025-11-28 | 2025-11-28 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Insulator Bond Wire-Wood | Repair | 46298333 | T2 EI COPPERMINE-TIVY VLY 22/3 RPR BOND | ICW
LC | 128899489 | 022/267 | T2 EI DRUM-SUMMIT #1_022/267 RPR INSW | SACTO | ETL.1440.INSL | 2024-05-28 | 2024-05-28 | 2025-05-29 | On-Time |  | 2025-11-28 | 2025-11-28 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46398033 | T2 EI DRUM-SUMMIT #1_022/267 RPR INSW | ICW
LC | 131324337 | 001/009 | T3 GEYSERS #13 TAP 001/009 TOUCH | LAKEVLLE | ETL.4781.TOWR | 2025-06-05 | 2025-05-28 | 2025-05-28 | TBC |  | 2025-11-28 | 2025-11-28 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46539738 | T3 GEYSERS #13 TAP 001/009 TOUCH | ICQ
LC | 131395239 | B004/003 | T3 FULTON-CALISTOGA B4/3 TOUCH | LAKEVLLE | ETL.6880.POLE.NWOD | 2025-06-23 | 2025-05-28 | 2025-05-28 | TBC |  | 2025-11-28 | 2025-11-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair
LC | 131395251 | 037/191A | T3 FULTON-PUEBLO 37/191A RPR SWTC | LAKEVLLE | ETL.1600.TOWR | 2025-06-23 | 2025-05-28 | 2025-05-28 | TBC |  | 2025-11-28 | 2025-11-28 | 623 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE SPCR ACCL OH TR3 AIR FRAB BRIN | Out of Adjustment | Switch | Repair
LC | 131395438 | B004/002 | T3 FULTON-CALISTOGA B4/2 SPLIT BOLT | LAKEVLLE | ETL.6880.POLE.WOOD | 2025-06-23 | 2025-05-28 | 2025-05-28 | TBC |  | 2025-11-28 | 2025-11-28 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB BRIN | Missing | Hardware-Wood | Install
LC | 131399453 | 002/011B | T3 GEYSERS #12-FULTON 02/11B COTR KEY | LAKEVLLE | ETL.4750.INSL.NCER | 2025-06-24 | 2025-05-28 | 2025-05-28 | TBC |  | 2025-11-28 | 2025-11-28 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Repair
LC | 128910474 | 072/364 | T2 MALIN RND MTN #2 72/364 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-05-29 | 2024-05-29 | 2024-05-29 | TBC |  | 2025-11-29 | 2025-11-29 | 93Z | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716724 | T2 EI MALIN-RND MTN #2 RPL ANCT 7 TWRS | 93Z
LC | 128959976 | 072/365 | T2 MLN-RND MTN #2 072/365 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-05-31 | 2024-05-29 | 2024-05-29 | TBC |  | 2025-11-29 | 2025-11-29 | 93Z | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716724 | T2 EI MALIN-RND MTN #2 RPL ANCT 7 TWRS | 93Z
LC | 128961174 | 072/364A | T2 MLIN-RND MNTAIN #2 72/364 RPR STRT | TABLEMTN | ETL.6020.TOWR | 2024-05-31 | 2024-05-29 | 2024-05-29 | TBC |  | 2025-11-29 | 2025-11-29 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 46452739 | T2 DI MLIN-RND MNTAIN #2 72/364 RPR STRT | ICQ
LC | 129134867 | 015/080 | T2 VACA-BAHIA 15/80 RPL INSS | SACTO | ETL.5810.INSL | 2024-06-26 | 2024-05-29 | 2024-05-29 | TBC |  | 2025-11-29 | 2025-11-29 | 532T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Steel | Replace | 35574253 | T2 DI VACA-BAHIA RPL INSS 2 TWRS | 93K
LC | 129280399 | 071/362 | T2 MALIN-RND MNTN #2 71/362 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-07-23 | 2024-05-29 | 2024-05-29 | TBC |  | 2025-11-29 | 2025-11-29 | 93Z | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31712420 | T2 DI MALIN-RND MNTN #2 71/362 RPL ANCT | 93Z
LC | 131296905 | 002/017 | T3 MORAGA-OAKLAND J 02/17 HANGER | CONCORD | ETL.2760.INSL.NCER | 2025-05-29 | 2025-05-29 | 2025-05-29 | TBC |  | 2025-11-29 | 2025-11-29 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46539651 | T3 MORAGA-OAKLAND J 02/17 HANGER | ICQ
LC | 131399866 | 020/098 | T3 MONTA VISTA-COYOTE SS 20/98 RPR SHLS | METCALF | ETL.5090.TOWR | 2025-06-24 | 2025-05-29 | 2025-05-29 | TBC |  | 2025-11-29 | 2025-11-29 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair
LC | 128924984 | 002/088 | T2 EI SPAULDING-SUMMIT 002/088 RPR POLE | SACTO | ETL.8060.POLE.NWOD | 2024-05-30 | 2024-05-30 | 2025-06-03 | On-Time |  | 2025-11-30 | 2025-11-30 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Repair | 46398039 | T2 EI SPAULDING-SUMMIT 002/088 RPR POLE | ICW
LC | 128961280 | 015/109 | T2 IGNCO ALTO SUSLTO#1 15/109 RPR STRT | LAKEVLLE | ETL.7160.TOWR | 2024-05-31 | 2024-05-30 | 2024-05-30 | TBC |  | 2025-11-30 | 2025-11-30 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW FIRE OH XMPT TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46261890 | T2 DI IGCO ALTO SUSLTO#1 15/109 RPR STRT | ICQ
LC | 128964381 | 001/063 | T2 SPLDING SUMMIT 01/063 RPL POLE | SACTO | ETL.8060.POLE.WOOD | 2024-06-01 | 2024-05-31 | 2024-05-31 | TBC |  | 2025-11-30 | 2025-11-30 | 372 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW FIRE OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35572870 | T2 DI SPLDING SUMMIT 01/063 RPL POLE | 70Y
LC | 129015756 | 070/355 | T2 MALIN-ROUND MNTAIN #2 70/355 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-06-03 | 2024-05-31 | 2025-06-18 | On-Time |  | 2025-11-30 | 2025-11-30 | 93Z | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716724 | T2 EI MALIN-RND MTN #2 RPL ANCT 7 TWRS | 93Z
LC | 129215432 | 070/353 | T2 DI MALIN-ROUND MNT #2 70/353 RPL ANCT | TABLEMTN | ETL.6020.TOWR | 2024-07-12 | 2024-05-31 | 2025-06-18 | On-Time |  | 2025-11-30 | 2025-11-30 | 93Z | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Anchor-Tower | Replace | 31716724 | T2 EI MALIN-RND MTN #2 RPL ANCT 7 TWRS | 93Z
LC | 129340041 | 011/129 | T2 DRUM SUMMIT #1 11/129 RPL ANCW | SACTO | ETL.1440.POLE.WDPS | 2024-08-06 | 2024-05-31 | 2025-06-04 | On-Time |  | 2025-11-30 | 2025-11-30 | 637T | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW FIRE COMP OH XMPT TR2 PRTO AIR | No Good/Out of Stdrd | Anchor-Wood | Replace | 35586895 | T2 DI DRUM SUMMIT #1 11/129 RPL ANCW | 93E
LC | 131302137 | 008/068B | T3 MONTA VISTA-BURNS 8/68 RMV DEBRIS | MOSSLNDG | ETL.7590.INSL.NCER | 2025-05-30 | 2025-05-30 | 2025-05-30 | TBC |  | 2025-11-30 | 2025-11-30 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR3 FRAB BRIN | Debris/Nest/etc. | Conductor-Wood | Remove | 46543522 | T3 MONTA VISTA-BURNS 8/68 RMV DEBRIS | ICW
LC | 131324096 | 010/010 | T3 UKIAH HOPLND CLOVERDALE 10/10 RMV VEG | WILLITS | ETL.4050.POLE.NWOD | 2025-06-05 | 2025-05-30 | 2025-05-30 | TBC |  | 2025-11-30 | 2025-11-30 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE SPCR OH TR3 AIR FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131407265 | B010/005 | T3 FULTON-CALISTOGA B010/005 RPR CRSW | LAKEVLLE | ETL.6880.POLE.WOOD | 2025-06-26 | 2025-05-30 | 2025-05-30 | TBC |  | 2025-11-30 | 2025-11-30 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Crossarm-Wood | Repair
LC | 131306588 | 337 | T3 DRUM-HIGGINS 00/001 SW 337 RPR SWTC | SACTO | ETL.4393.SWIT | 2025-06-02 | 2025-06-02 | 2025-06-02 | TBC |  | 2025-09-02 | 2025-12-02 | 623 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB DURA BRIN | Out of Adjustment | Switch | Repair | 46532376 | T3 DRUM-HIGGINS 00/001 SW 337 RPR SWTC | ICE
LC | 131306750 | 337 | T3 DRUM-HIGGINS 00/001 RPR JUMS | SACTO | ETL.4393.SWIT | 2025-06-02 | 2025-06-02 | 2025-06-02 | TBC |  | 2025-12-02 | 2025-12-02 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46539200 | T3 DRUM-HIGGINS 00/001 RPR JUMS | ICS
LC | 131306754 | 000/001 | T3 DRUM-HIGGINS 00/001 TOUCH | SACTO | ETL.4393.TOWR | 2025-06-02 | 2025-06-02 | 2025-06-02 | TBC |  | 2025-12-02 | 2025-12-02 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair
LC | 131313764 | 022/001 | T3 MONTE RIO-FORT ROSS 22/1 TOUCH | LAKEVLLE | ETL.6979.POLE.NWOD | 2025-06-03 | 2025-06-02 | 2025-06-02 | TBC |  | 2025-12-02 | 2025-12-02 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Steel | Repair | 46544481 | T3 MONTE RIO-FORT ROSS 22/1 TOUCH | ICS
LC | 131313765 | 97 | T3 MNTE RIO-FRT ROSS 22/1 SW 97 RPR SWTC | LAKEVLLE | ETL.6979.SWIT | 2025-06-03 | 2025-06-02 | 2025-06-02 | TBC |  | 2025-12-02 | 2025-12-02 | 623 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | Out of Adjustment | Switch | Repair | 46544482 | T3 MNTE RIO-FRT ROSS 22/1 SW 97 RPR SWTC | ICE
LC | 131350402 | 007/064 | T3 WOODLEAF-PALERMO 7/64R RMV VEG | TABLEMTN | ETL.4220.POLE.STPS | 2025-06-10 | 2025-06-02 | 2025-06-02 | TBC |  | 2025-12-02 | 2025-12-02 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 AIR BRIN | Overgrown | Vegetation | Remove
LC | 131399387 | 000/002A | T3 DRUM PH #2 TAP 000/002A TOUCH | SACTO | ETL.6375.POLE.NWOD | 2025-06-24 | 2025-06-02 | 2025-06-02 | TBC |  | 2025-12-02 | 2025-12-02 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair
LC | 131399508 | 000/002B | T3 DRUM PH #2 TAP 0/002B TOUCH | SACTO | ETL.6375.POLE.NWOD | 2025-06-24 | 2025-06-02 | 2025-06-02 | TBC |  | 2025-12-02 | 2025-12-02 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair
LC | 131399534 | 000/002C | T3 DRUM PH #2 TAP 2/2C TOUCH | SACTO | ETL.6375.POLE.NWOD | 2025-06-24 | 2025-06-02 | 2025-06-02 | TBC |  | 2025-12-02 | 2025-12-02 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair
LC | 131399921 | 000/005 | T3 DRM-SPLDNG 0/5 RPR JUMW | SACTO | ETL.6770.INSL.NCER | 2025-06-24 | 2025-06-02 | 2025-06-02 | TBC |  | 2025-12-02 | 2025-12-02 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair
LC | 131399954 | 000/001 | T3 DRUM-SPAULDING 0/1 RPR STRW | SACTO | ETL.6770.POLE.NWOD | 2025-06-24 | 2025-06-02 | 2025-06-02 | TBC |  | 2025-12-02 | 2025-12-02 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW ACCM OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair
LC | 131406891 | 009/109 | T3 GEYSERS #3 CLOVERDALE 9/109 RPR JUMW | LAKEVLLE | ETL.1650.INSL.NCER | 2025-06-26 | 2025-06-02 | 2025-06-02 | TBC |  | 2025-12-02 | 2025-12-02 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair
LC | 128189115 | 003/040 | T2 DI CHRISTIE-WILLOW PSS 3/40 RPR STRW | CONCORD | ETL.6370.POLE.WOOD | 2024-02-16 | 2024-02-14 | 2024-02-14 | TBC |  | 2025-12-03 | 2025-12-03 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW FIRE OH XMPT TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Structure-Wood | Repair | 46286504 | T2 DI CHRISTIE-WILLOW PSS 3/40 RPR STRW | ICW
LC | 131309776 | 018/274 | T3 GOLD HILL #1 18/274 RPR STRW | SACTO | ETL.6950.POLE.WOOD | 2025-06-03 | 2025-06-03 | 2025-06-03 | TBC |  | 2025-12-03 | 2025-12-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair
LC | 131312708 | 002/023 | T3 WOODLEAF-PALERMO 2/23R RPR CNDW | TABLEMTN | ETL.4220.INSL.NCER | 2025-06-03 | 2025-06-03 | 2025-06-03 | TBC |  | 2025-12-03 | 2025-12-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP REMT SWRK CLR ACCM OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair
LC | 131313618 | ?004/002 | T3 SNEATH LN-HMB ?004/002R RPR CNDW | METCALF | ETL.7212.INSL.NCER | 2025-06-03 | 2025-06-03 | 2025-06-03 | TBC |  | 2025-12-03 | 2025-12-03 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46544573 | T3 SNEATH LN-HMB ?004/002R RPR CNDW | ICW
LC | 131407267 | 317 | T3 CORTINA-MNDCNO #1 18/92A RPR JUMS | WILLITS | ETL.1330.SWIT | 2025-06-26 | 2025-06-03 | 2025-06-03 | TBC |  | 2025-12-03 | 2025-12-03 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair
LC | 129019364 | 071/361 | T2 MALIN-RND MTN #2 71/361 RPR ANCT | TABLEMTN | ETL.6020.TOWR | 2024-06-04 | 2024-06-04 | 2024-06-04 | TBC |  | 2025-12-04 | 2025-12-04 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Anchor-Tower | Repair | 46381456 | T2 EI MALIN-RND MTN #2 71/361 RPR ANCT | ICQ
LC | 131350049 | 015/117A | T3 TRINITY-COTTONWOOD 15/117A TOUCH | TABLEMTN | ETL.4040.POLE.NWOD | 2025-06-10 | 2025-06-04 | 2025-06-04 | TBC |  | 2025-12-04 | 2025-12-04 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46543512 | T3 TRINITY-COTTONWOOD 15/117A TOUCH | ICW
LC | 131350222 | 016/122 | T3 TRINITY-COTNWD 16/122L RPR GYWW | TABLEMTN | ETL.4040.POLE.STPS | 2025-06-10 | 2025-06-04 | 2025-06-04 | TBC |  | 2025-12-04 | 2025-12-04 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair
LC | 131350223 | 016/122 | T3 TRNTY-CTNWD 16/122R RPR GYWW | TABLEMTN | ETL.4040.POLE.STPS | 2025-06-10 | 2025-06-04 | 2025-06-04 | TBC |  | 2025-12-04 | 2025-12-04 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair
LC | 131350357 | 007/012 | T3 MENDOCINO WILLITIS 7/12 RPL STRW | WILLITS | ETL.7540.POLE.WOOD | 2025-06-10 | 2025-06-04 | 2025-06-04 | TBC |  | 2025-12-04 | 2025-12-04 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCM OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35649397 | T3 MENDOCINO WILLITIS 7/12 RPL STRW | 70Y
LC | 129897935 | 030/222 | T2 DRUM RIO OSO #2 30/222 RPL HNGR | SACTO | ETL.1430.INSL.CERA | 2024-12-05 | 2024-12-05 | 2025-04-21 | On-Time |  | 2025-12-05 | 2025-12-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH TR2 PRTO | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46452723 | T2 DRUM RIO OSO #2 30/222 RPL HNGR | ICQ
LC | 129898003 | 003/026 | T2 MORAGA-OAKLAND#4 3/26 RPL HNGR | CONCORD | ETL.2750.INSL.NCER | 2024-12-05 | 2024-12-05 | 2025-06-17 | On-Time |  | 2025-12-05 | 2025-12-05 | 543 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Hanger Plate - Tower | Replace | 46441173 | T2 MORAGA-OAKLAND#4 3/26 RPL HNGR | ICQ
LC | 129903599 | 071/291 | T2 ROUND MTN-TABLE MTN#2 71/291 RPR INSS | TABLEMTN | ETL.6070.INSL.CERA | 2024-12-06 | 2024-12-05 | 2025-02-19 | On-Time |  | 2025-12-05 | 2025-12-05 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW PATR COMP OH FMOB TR2 PRTO NTDE | No Good/Out of Stdrd | Insulator-Steel | Repair | 46460886 | T2 ROUND MTN-TABLE MTN#2 71/291 RPR INSS | ICS
LC | 131322710 | 008/113 | T3 GOLD HILL #1 008/113 RPR POLE | SACTO | ETL.6950.POLE.WOOD | 2025-06-05 | 2025-06-05 | 2025-06-05 | TBC |  | 2025-12-05 | 2025-12-05 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair
LC | 131350427 | 008/001 | T3 PTR VLY-WILLITS 8/001 RPR STRW | WILLITS | ETL.7820.POLE.WOOD | 2025-06-10 | 2025-06-05 | 2025-06-05 | TBC |  | 2025-12-05 | 2025-12-05 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair
LC | 131350467 | 008/002 | T3 POTTER VALLEY-WILLITS 8/2 RPR JUMW | WILLITS | ETL.7820.INSL.NCER | 2025-06-10 | 2025-06-05 | 2025-06-05 | TBC |  | 2025-12-05 | 2025-12-05 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair
LC | 131350469 | 019/001 | T3 MONTE RIO-FORT ROSS 19/1L RPR GYWW | LAKEVLLE | ETL.6979.POLE.STPS | 2025-06-10 | 2025-06-05 | 2025-06-05 | TBC |  | 2025-12-05 | 2025-12-05 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair
LC | 131350480 | 008/007 | T3 POTTER VLY-WILLITS 8/007 RPR JUMW | WILLITS | ETL.7820.INSL.NCER | 2025-06-10 | 2025-06-05 | 2025-06-05 | TBC |  | 2025-12-05 | 2025-12-05 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair
LC | 131350499 | 018/008 | T3 MONTE RIO-FORT ROSS 18/008 WASH INSW | LAKEVLLE | ETL.6979.INSL.NCER | 2025-06-10 | 2025-06-05 | 2025-06-05 | TBC |  | 2025-12-05 | 2025-12-05 | 622 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | Contaminated | Insulator | Ground Wash | 46544484 | T3 MONTE RIO-FORT ROSS 18/008 WASH INSW | ICD
LC | 131359321 | 000/004 | T3 DESABLA CENTERVILLE 0/4 RPR STRW | TABLEMTN | ETL.6720.POLE.WOOD | 2025-06-12 | 2025-06-05 | 2025-06-05 | TBC |  | 2025-12-05 | 2025-12-05 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair | 46540282 | T3 DESABLA CENTERVILLE 0/4 RPR STRW | ICW
LC | 129901553 | A002/050 | T2 WV VALLEY SPRINGS#1 A2/50 RPL SPLW | VICTOR | ETL.8210.INSL.NCER | 2024-12-06 | 2024-12-06 | 2024-12-06 | TBC |  | 2025-12-06 | 2025-12-06 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Splice-Wood | Replace | 46460671 | T2 WV VALLEY SPRINGS#1 A2/50 RPL SPLW | ICW
LC | 131328733 | 009/117 | T3 GOLD HILL #1 009/117 RMV VEG | SACTO | ETL.6950.POLE.WOOD | 2025-06-06 | 2025-06-06 | 2025-06-06 | TBC |  | 2025-12-06 | 2025-12-06 | 564 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 FRAB BRIN | Overgrown | Vegetation | Remove
LC | 131328734 | 009/117 | T3 GOLD HILL #1 009/117 RPL POLE | SACTO | ETL.6950.POLE.WOOD | 2025-06-06 | 2025-06-06 | 2025-06-06 | TBC |  | 2025-12-06 | 2025-12-06 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35647573 | T3 GOLD HILL #1 009/117 RPL POLE | 70Y
LC | 131328735 | 008/114 | T3 GOLD HILL #1 008/114 RPR POLE | SACTO | ETL.6950.POLE.WOOD | 2025-06-06 | 2025-06-06 | 2025-06-06 | TBC |  | 2025-12-06 | 2025-12-06 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair
LC | 131329558 | 023/341 | T3 GOLD HILL #1 23/341 RPR INSW | SACTO | ETL.6950.INSL.NCER | 2025-06-06 | 2025-06-06 | 2025-06-06 | TBC |  | 2025-12-06 | 2025-12-06 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair
LC | 131329616 | 047/205 | T3 MTCALF-MSS LANDING #1 47/205 RPR INSS | METCALF | ETL.5100.TOWR | 2025-06-06 | 2025-06-06 | 2025-06-06 | TBC |  | 2025-12-06 | 2025-12-06 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR3 FRAB NTDE BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46544559 | T3 MTCALF-MSS LANDING #1 47/205 RPR INSS | ICS
LC | 131336710 | 005/032 | T3 CASTRO VALLEY NEWARK 5/32 RPR OPGW | CONCORD | ETL.4450.TOWR | 2025-06-09 | 2025-06-06 | 2025-06-06 | TBC |  | 2025-09-06 | 2025-12-06 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE ACCH OH TR3 AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46544948 | T3 CASTRO VALLEY NEWARK 5/32 RPR OPGW | ICS
LC | 131350350 | ?005/001 | T3 SNETH LN-HALF MN BAY-?05/01 RPR GYWW | METCALF | ETL.7212.POLE.NWOD | 2025-06-10 | 2025-06-06 | 2025-06-06 | TBC |  | 2025-12-06 | 2025-12-06 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46544574 | T3 SNETH LN-HALF MN BAY-?05/01 RPR GYWW | ICW
LC | 131370168 | 008/003 | T3 MENDOCINO-WILLITS 8/3 RPR GYWW | WILLITS | ETL.7540.POLE.NWOD | 2025-06-16 | 2025-06-06 | 2025-06-06 | TBC |  | 2025-12-06 | 2025-12-06 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46544426 | T3 MENDOCINO-WILLITS 8/3 RPR GYWW | ICW
LC | 131370246 | 006/035 | T3 CASTRO VALLEY NEWARK 6/35 RPR OPGW | CONCORD | ETL.4450.TOWR | 2025-06-16 | 2025-06-06 | 2025-06-06 | TBC |  | 2025-12-06 | 2025-12-06 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46544756 | T3 CASTRO VALLEY NEWARK 6/35 RPR OPGW | ICS
LC | 124998997 | 005/049 | T3NT DRUM-RIO OSO #2 5/49 RPR JMPS | SACTO | ETL.1430.INSL.NCER | 2022-12-09 | 2022-12-09 | 2024-01-10 | On-Time |  | 2025-12-09 | 2025-12-09 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR3 PRTO PGEQ | No Good/Out of Stdrd | Jumper-Steel | Repair | 46101302 | T3NT DRUM-RIO OSO #2 5/49 RPR JMPS | ICS
LC | 129911006 | 033/244 | T2 DI CARIBOU-TBL MTN 33/244 RPR JUMS | TABLEMTN | ETL.4440.TOWR | 2024-12-09 | 2024-12-09 | 2025-04-07 | On-Time |  | 2025-12-09 | 2025-12-09 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Jumper-Steel | Repair | 46452772 | T2 DI CARIBOU-TBL MTN 33/244 RPR JUMS | ICS
LC | 131350581 | 002/021 | T3 MRGA-OKLND #1 2/21 RPR STRT | CONCORD | ETL.2720.TOWR | 2025-06-10 | 2025-06-09 | 2025-06-09 | TBC |  | 2025-12-09 | 2025-12-09 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Tower | Repair
LC | 131369997 | 009/001 | T3 POTTER VALLEY-WILLITS 9/1 RPR CRSW | WILLITS | ETL.7820.POLE.WOOD | 2025-06-16 | 2025-06-09 | 2025-06-09 | TBC |  | 2025-12-09 | 2025-12-09 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Crossarm-Wood | Repair
LC | 131370062 | 009/009 | T3 POTTER VALLEY-WILLITS 9/9 RPL STRW | WILLITS | ETL.7820.POLE.WOOD | 2025-06-16 | 2025-06-09 | 2025-06-09 | TBC |  | 2025-12-09 | 2025-12-09 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35650686 | T3 POTTER VALLEY-WILLITS 9/9 RPL STRW | 70Y
LC | 131370089 | 009/000 | T3 POTTER VALLEY-WILLITS 9/0 PRL STRW | WILLITS | ETL.7820.POLE.WOOD | 2025-06-16 | 2025-06-09 | 2025-06-09 | TBC |  | 2025-12-09 | 2025-12-09 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35650147 | T3 POTTER VALLEY-WILLITS 9/0 PRL STRW | 70Y
LC | 131370212 | 009/002 | T3 POTTER VALLEY-WILLITS 9/2 RPL STRW | WILLITS | ETL.7820.POLE.WOOD | 2025-06-16 | 2025-06-09 | 2025-06-09 | TBC |  | 2025-12-09 | 2025-12-09 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35650149 | T3 POTTER VALLEY-WILLITS 9/2 RPL STRW | 70Y
LC | 131370284 | 009/060 | T3 OLEUM "G" #1 9/060 RPR JUMS | CONCORD | ETL.3160.INSL.NCER | 2025-06-16 | 2025-06-09 | 2025-06-09 | TBC |  | 2025-12-09 | 2025-12-09 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46544757 | T3 OLEUM "G" #1 9/060 RPR JUMS | ICS
LC | 129052623 | 023/277 | T2 EI DRUM-SUMMIT #2 23/277L RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-06-10 | 2024-06-10 | 2025-06-08 | On-Time |  | 2025-12-10 | 2025-12-10 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458334 | T2 EI DRUM-SUMMIT #2 23/277L RPR GYWW | ICW
LC | 129053021 | 023/277 | T2 EI DRUM-SUMMIT #2 23/277R RPR GYWW | SACTO | ETL.1450.POLE.STPS | 2024-06-10 | 2024-06-10 | 2025-06-08 | On-Time |  | 2025-12-10 | 2025-12-10 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB XMPT TR2 PRTO | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46458337 | T2 EI DRUM-SUMMIT #2 23/277R RPR GYWW | ICW
LC | 129054410 | 057/243 | T2 EI RND MTN-TBL MTN #1 57/243 REGRADE | TABLEMTN | ETL.6060.TOWR | 2024-06-10 | 2024-06-10 | 2024-06-10 | TBC |  | 2025-12-10 | 2025-12-10 | 543 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46310399 | T2 EI RND MTN-TBL MTN #1 57/243 REGRADE | ICQ
LC | 129922961 | 129 | T2 EI DIVIDE-CABRILLO#2 008/106 RPR SWTC | PISMOBCH | ETL.1370.SWIT | 2024-12-10 | 2024-12-10 | 2024-12-10 | TBC |  | 2025-12-10 | 2025-12-10 | 623 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | Out of Adjustment | Switch | Repair | 46478010 | T2 EI DIVIDE-CABRILLO#2 008/106 RPR SWTC | ICE
LC | 129923587 | 004/004 | T2 DI LYTNVL-CVLO 4/4 RPR JUMW | WILLITS | ETL.7390.INSL.NCER | 2024-12-10 | 2024-12-10 | 2025-06-10 | On-Time |  | 2025-03-10 | 2025-12-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB DURA | No Good/Out of Stdrd | Jumper-Wood | Repair | 46438396 | T2 DI LYTNVL-CVLO 4/4 RPR JUMW | ICW
LC | 129923720 | 004/004 | T2 DI LYTNVL-CVLO 4/4 RPR GYWW | WILLITS | ETL.7390.POLE.NWOD | 2024-12-10 | 2024-12-10 | 2025-04-14 | On-Time |  | 2025-12-10 | 2025-12-10 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW ACCL COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46446951 | T2 DI LYTNVL-CVLO 4/4 RPR GYWW | ICW
LC | 131349338 | 024/352 | T3 GOLD HILL #1 24/352 RPR INSW | SACTO | ETL.6950.INSL.CERA | 2025-06-10 | 2025-06-10 | 2025-06-10 | TBC |  | 2025-12-10 | 2025-12-10 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Insulator-Wood | Repair | 46539999 | T3 GOLD HILL #1 24/352 RPR INSW | ICW
LC | 131349773 | 024/359 | T3 GOLD HILL #1 24/359 RPR STRW | SACTO | ETL.6950.POLE.WOOD | 2025-06-10 | 2025-06-10 | 2025-06-10 | TBC |  | 2025-12-10 | 2025-12-10 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair
LC | 131369951 | 014/059 | T3 MNT VST-JFFRSN #2 14/59 RPR JUMS | METCALF | ETL.5230.INSL.NCER | 2025-06-16 | 2025-06-10 | 2025-06-10 | TBC |  | 2025-12-10 | 2025-12-10 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair | 46544567 | T3 MNT VST-JFFRSN #2 14/59 RPR JUMS | ICS
LC | 131395812 | 008/045 | T3 DI CASTRO VALLEY-NEWARK 8/45 OPGW | CONCORD | ETL.4450.TOWR | 2025-06-23 | 2025-06-10 | 2025-06-10 | TBC |  | 2025-12-10 | 2025-12-10 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46544758 | T3 DI CASTRO VALLEY-NEWARK 8/45 OPGW | ICS
LC | 131354992 | 025/373 | T3 GOLD HILL #1 025/373 RPL POLE | SACTO | ETL.6950.POLE.WOOD | 2025-06-11 | 2025-06-11 | 2025-06-11 | TBC |  | 2025-12-11 | 2025-12-11 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35648305 | T3 GOLD HILL #1 025/373 RPL POLE | 70Y
LC | 131355264 | 011/003 | T3 MONTE RIO-FULTON 11/3 INS DMPW | LAKEVLLE | ETL.7630.INSL.NCER | 2025-06-11 | 2025-06-11 | 2025-06-11 | TBC |  | 2025-12-11 | 2025-12-11 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW OTHR OH FMOB TR3 FRAB NTDE BRIN | Missing | Damper-Wood | Install
LC | 131378017 | 002/021 | T3 MRGA-OKLND #3 2/21 TOUCH | CONCORD | ETL.2740.POLE.NWOD | 2025-06-17 | 2025-06-11 | 2025-06-11 | TBC |  | 2025-12-11 | 2025-12-11 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Steel | Repair
LC | 129930532 | 47 | T2 EI KONOCTI-MIDDLETOWN 12/00A RPR SWTC | WILLITS | ETL.6380.SWIT | 2024-12-12 | 2024-12-12 | 2024-12-12 | TBC |  | 2025-12-12 | 2025-12-12 | 623 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | Out of Adjustment | Switch | Repair | 46446952 | T2 EI KONOCTI-MIDDLETOWN 12/00A RPR SWTC | ICE
LC | 131357618 | 000/002 | T3 MORAGA-SAN LEANDRO #3 0/2 RPL INSLS | CONCORD | ETL.2790.INSL | 2025-06-12 | 2025-06-12 | 2025-06-12 | TBC |  | 2025-09-12 | 2025-12-12 | 532 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW PATR OH FMOB TR3 MBSF FRAB DURA BRIN | No Good/Out of Stdrd | Insulator-Steel | Replace
LC | 131358058 | 021/106 | T3 RND MTN-TABLE MTN #1 21/106 RPR FOND | TABLEMTN | ETL.6060.TOWR | 2025-06-12 | 2025-06-12 | 2025-06-12 | TBC |  | 2025-12-12 | 2025-12-12 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Foundation/Concrete-Tower | Repair | 46543610 | T3 RND MTN-TABLE MTN #1 21/106 RPR FOND | ICQ
LC | 131358986 | ?007/008 | T3 SNEATH LN HLF MOOD BAY ?7/8 RPR GYWW | METCALF | ETL.7212.POLE.NWOD | 2025-06-12 | 2025-06-12 | 2025-06-12 | TBC |  | 2025-12-12 | 2025-12-12 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE SPCR OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 46544575 | T3 SNEATH LN HLF MOOD BAY ?7/8 RPR GYWW | ICW
LC | 131370154 | 020/112 | T3 PARKWAY-MORAGA 20/112 RPR OPGW | CONCORD | ETL.5930.TOWR | 2025-06-16 | 2025-06-12 | 2025-06-12 | TBC |  | 2025-09-12 | 2025-12-12 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB DURA BRIN | No Good/Out of Stdrd | OPGW - Steel | Repair | 46544752 | T3 PARKWAY-MORAGA 20/112 RPR OPGW | ICS
LC | 129972082 | 005/139 | T2 WEIMAR-HALSEY 5/139 RPL CNDW | SACTO | ETL.8340.INSL.NCER | 2024-12-13 | 2024-12-13 | 2024-12-13 | TBC |  | 2025-12-13 | 2025-12-13 | 638T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO | No Good/Out of Stdrd | Conductor-Wood | Replace | 35608965 | T2 WEIMAR-HALSEY 5/139 RPL CNDW | 93C
LC | 129972172 | 005/139 | T2 WEIMAR-HALSEY 5/139 RPL STRW | SACTO | ETL.8340.POLE.WOOD | 2024-12-13 | 2024-12-13 | 2024-12-13 | TBC |  | 2025-12-13 | 2025-12-13 | 372T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Replace | 35623063 | T2 WEIMAR-HALSEY 5/139 RPL STRW | 70Y
LC | 130052168 | 79 | T2 EI SAN LUIS OBSPO-CYCS 5/32A RPR SWTC | PISMOBCH | ETL.9090.SWIT | 2024-12-13 | 2024-12-13 | 2025-05-21 | On-Time |  | 2025-12-13 | 2025-12-13 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW INSP COMP OH FMOB TR2 PRTO FRAB | No Good/Out of Stdrd | Switch-Wood | Repair | 46478011 | T2 EI SAN LUIS OBSPO-CYCS 5/32A RPR SWTC | ICW
LC | 125023520 | 017/121 | T3NT WV METCALF-GRN VLY 17/121 RPR STRW | MOSSLNDG | ETL.2540.POLE.WOOD | 2022-12-14 | 2022-12-14 | 2024-04-09 | On-Time |  | 2025-12-14 | 2025-12-14 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3N PRTO FRAB NTDE | No Good/Out of Stdrd | Structure-Wood | Repair | 46081119 | T3NT WV METCALF-GRN VLY 17/121 RPR STRW | ICW
LC | 125025708 | 000/022 | T2NT WV CSCD-BNTN-DSCHTS 0/22 RPL HRDD | TABLEMTN | ETL.6310.INSL.CERA | 2022-12-14 | 2022-12-14 | 2024-05-22 | On-Time |  | 2025-12-14 | 2025-12-14 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2N FRAB NTDE | No Good/Out of Stdrd | Hardware-Wood | Replace | 46092049 | T2NT WV CSCD-BNTN-DSCHTS 0/22 RPL HRDD | ICW
LC | 125029705 | 004/010 | T2NT CLEAR LAKE-HOPLAND 4/10 RPL POLE | WILLITS | ETL.6390.POLE.WOOD | 2022-12-15 | 2022-12-15 | 2024-06-26 | On-Time |  | 2025-12-15 | 2025-12-15 | 372 | TR2N | YES | E - Schd Compl Yr 0 | Closed | REGW COMP OH FMOB XMPT TR2N FRAB PGEQ | No Good/Out of Stdrd | Structure-Wood | Replace | 31629256 | T2 CLEAR LAKE-HOPLAND 004/011 RPL POLE | 70Y
LC | 125031475 | 004/005B | T2NT CLEAR LAKE-HOPLAND 4/005B RPR GYWW | WILLITS | ETL.6390.POLE.WOOD | 2022-12-15 | 2022-12-15 | 2023-12-13 | On-Time |  | 2025-12-15 | 2025-12-15 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH FMOB TR2N FRAB PGEQ | No Good/Out of Stdrd | Guy Wire-Wood | Repair | 45749376 | T2NT CLEAR LAKE-HOPLAND 4/005B RPR GYWW | ICW
LC | 125079858 | 002/034 | T3NT WV GEYSERS#3-CLVRDL 2/34 INS DAMW | LAKEVLLE | ETL.1650.POLE.WOOD | 2022-12-16 | 2022-12-16 | 2024-09-17 | On-Time |  | 2025-12-16 | 2025-12-16 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO FRAB NTDE | Missing | Damper-Wood | Install | 46204241 | T3NT WV GEYSERS#3-CLVRDL 2/34 INS DAMW | ICW
LC | 131368079 | 015/007 | T3 MONTE RIO-FT ROSS 15/07 RPL POLE | LAKEVLLE | ETL.6979.POLE.WOOD | 2025-06-16 | 2025-06-16 | 2025-06-16 | TBC |  | 2025-12-16 | 2025-12-16 | 372T | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH TR3 FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Replace | 35650685 | T3 MONTE RIO-FT ROSS 15/07 RPL POLE | 70Y
LC | 131368663 | 014/219 | T3 GOLD HILL #1 014/219 RPR STRW | SACTO | ETL.6950.POLE.WOOD | 2025-06-16 | 2025-06-16 | 2025-06-16 | TBC |  | 2025-12-16 | 2025-12-16 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Structure-Wood | Repair
LC | 131368859 | :001/011 | T3 EAGLE ROCK-REDBUD :001/011 COTR KEY | WILLITS | ETL.1480.INSL.NCER | 2025-06-16 | 2025-06-16 | 2025-06-16 | TBC |  | 2025-12-16 | 2025-12-16 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW CREW OH FMOB TR3 FRAB BRIN | No Good/Out of Stdrd | Hardware-Tower | Replace
LC | 131369656 | 011/056 | T3 MONTA VISTA-CYTE SS 11/56 BENT STL | METCALF | ETL.5090.TOWR | 2025-06-16 | 2025-06-16 | 2025-06-16 | TBC |  | 2025-12-16 | 2025-12-16 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OH FMOB TR3 CLMB FRAB BRIN | No Good/Out of Stdrd | Structure-Tower | Repair | 46545387 | T3 MONTA VISTA-CYTE SS 11/56 BENT STL | ICQ
LC | 131383265 | 010/017 | T3 BRIDGEVLLE-GARBERVILLE 10/17 RPR GYWW | EUREKA | ETL.6220.POLE.NWOD | 2025-06-18 | 2025-06-16 | 2025-06-16 | TBC |  | 2025-12-16 | 2025-12-16 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair
LC | 131383266 | 010/017 | T3 BRIDGEVLLE-GARBERVILLE 10/17 RPR JMPW | EUREKA | ETL.6220.INSL.NCER | 2025-06-18 | 2025-06-16 | 2025-06-16 | TBC |  | 2025-12-16 | 2025-12-16 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair
LC | 130111751 | 040/005 | T2 FRT RSS-GUALLA-GLLA 40/5R RPL ANCW | LAKEVLLE | ETL.6980.POLE.WDPS | 2024-12-17 | 2024-12-17 | 2024-12-17 | TBC |  | 2025-12-17 | 2025-12-17 | 93Z | TR2 |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR2 PRTO | No Good/Out of Stdrd | Anchor-Wood | Replace | 31722218 | T2 FRT RSS-GUALLA-GLLA 40/5R RPL ANCW | 93Z
LC | 130111842 | 004/055 | T2 DI CLGT-SMRTVLL #2 4/055 RPR CNDW | SACTO | ETL.6520.INSL | 2024-12-17 | 2024-12-17 | 2025-03-05 | On-Time |  | 2025-06-17 | 2025-12-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA | No Good/Out of Stdrd | Conductor-Wood | Repair | 46459931 | T2 DI CLGT-SMRTVLL #2 4/055 RPR CNDW | ICW
LC | 130112082 | 007/087 | T2 DI COLGATE-SMARTVLLE #2 7/87 RPR INSW | SACTO | ETL.6520.INSL | 2024-12-17 | 2024-12-17 | 2025-03-06 | On-Time |  | 2025-12-17 | 2025-12-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Insulator-Wood | Repair | 46459932 | T2 DI COLGATE-SMARTVLLE #2 7/87 RPR INSW | ICW
LC | 130112085 | 007/087 | T2 DI CLGT-SMRTVLL #2 7/087 RPR CNDW | SACTO | ETL.6520.INSL | 2024-12-17 | 2024-12-17 | 2025-03-06 | On-Time |  | 2025-06-17 | 2025-12-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA | No Good/Out of Stdrd | Conductor-Wood | Repair | 46459933 | T2 DI CLGT-SMRTVLL #2 7/087 RPR CNDW | ICW
LC | 130116518 | 031/602 | T2 DI HAT CRK #1-WSTWD 31/602 RPR INSW | TABLEMTN | ETL.7030.INSL | 2024-12-18 | 2024-12-17 | 2025-06-16 | On-Time |  | 2025-12-17 | 2025-12-17 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair | 46463884 | T2 DI HAT CRK #1-WSTWD 31/602 RPR INSW | ICW
LC | 131386973 | 003/056A | T3 GRIZZLY-BUCKS CREEK 03/56A RPR JUMS | TABLEMTN | ETL.2395.INSL.NCER | 2025-06-20 | 2025-06-18 | 2025-06-18 | TBC |  | 2025-12-18 | 2025-12-18 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Steel | Repair
LC | 131394683 | 017/002 | T3 MONTE RIO-FT ROSS 17/02 RPR CNDW | LAKEVLLE | ETL.6979.INSL.NCER | 2025-06-23 | 2025-06-18 | 2025-06-18 | TBC |  | 2025-12-18 | 2025-12-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR FIRE OH TR3 FRAB BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46543143 | T3 MONTE RIO-FT ROSS 17/02 RPR CNDW | ICW
LC | 131394743 | 017/003 | T3 MONTE RIO-FT ROSS 17/03 RPR CNDW | LAKEVLLE | ETL.6979.INSL.NCER | 2025-06-23 | 2025-06-18 | 2025-06-18 | TBC |  | 2025-12-18 | 2025-12-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR FIRE OH TR3 FRAB BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46543144 | T3 MONTE RIO-FT ROSS 17/03 RPR CNDW | ICW
LC | 131394746 | 018/000 | T3 MONTE RIO-FT ROSS 18/00 RPR CNDW | LAKEVLLE | ETL.6979.INSL.NCER | 2025-06-23 | 2025-06-18 | 2025-06-18 | TBC |  | 2025-12-18 | 2025-12-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR FIRE OH TR3 FRAB BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46543145 | T3 MONTE RIO-FT ROSS 18/00 RPR CNDW | ICW
LC | 131394748 | 018/001 | T3 MONTE RIO-FT ROSS 18/01 RPR CNDW | LAKEVLLE | ETL.6979.INSL.NCER | 2025-06-23 | 2025-06-18 | 2025-06-18 | TBC |  | 2025-12-18 | 2025-12-18 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW OTHR FIRE OH TR3 FRAB BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46543146 | T3 MONTE RIO-FT ROSS 18/01 RPR CNDW | ICW
LC | 131395616 | 001/007 | T3 MORAGA-CLAREMONT #2 1/7 COTTER | CONCORD | ETL.2710.INSL.NCER | 2025-06-23 | 2025-06-18 | 2025-06-18 | TBC |  | 2025-12-18 | 2025-12-18 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair
LC | 130118083 | 147 | T0 WOODLEAF-PALERMO 6/053 RPR SWTC | TABLEMTN | ETL.4220.SWIT | 2024-12-19 | 2024-12-19 | 2025-03-11 | On-Time |  | 2025-03-19 | 2025-12-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW CREW COMP OH FMOB TR2 PRTO DURA BRIN | No Good/Out of Stdrd | Switch-Wood | Repair | 46463886 | T0 WOODLEAF-PALERMO 6/053 RPR SWTC | ICW
LC | 130118233 | 027/007 | T2 WV RIO DLL JCT-BRDGVLLE 27/7 INS ANCW | EUREKA | ETL.7850.POLE.NWOD | 2024-12-19 | 2024-12-19 | 2024-12-19 | TBC |  | 2025-12-19 | 2025-12-19 | 637T | TR2 |  | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB TR2 PRTO FRAB NTDE | Missing | Anchor-Wood | Install | 35607632 | T2 WV RIO DLL JCT-BRDGVLLE 27/7 INS ANCW | 93E
LC | 130118261 | 027/007 | T2 WV RIO DLL JCT-BRDGVLLE 27/7 INS DAMP | EUREKA | ETL.7850.INSL.NCER | 2024-12-19 | 2024-12-19 | 2024-12-19 | TBC |  | 2025-12-19 | 2025-12-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 PRTO NTDE | Missing | Damper-Wood | Install | 46446430 | T2 WV RIO DLL JCT-BRDGVLLE 27/7 INS DAMP | ICW
LC | 130132479 | 029/208 | T2 DI CARIBOU-TBL MTN 29/208 RPR JMPS | TABLEMTN | ETL.4440.INSL.NCER | 2024-12-19 | 2024-12-19 | 2025-04-06 | On-Time |  | 2025-12-19 | 2025-12-19 | 628 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR | No Good/Out of Stdrd | Jumper-Steel | Repair | 46452753 | T2 DI CARIBOU-TBL MTN 29/208 RPR JMPS | ICS
LC | 130208256 | 010/127 | T2 DI COLGATE-SMRTVLE #2 10/127 RPR JUMW | SACTO | ETL.6520.INSL.NCER | 2024-12-19 | 2024-12-19 | 2025-03-05 | On-Time |  | 2025-03-19 | 2025-12-19 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR DURA BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46452876 | T2 DI COLGATE-SMRTVLE #2 10/127 RPR JMPW | ICW
LC | 131385028 | 015/000 | T3 LAURELES-OTTER 15/000L RPR GYWW | MOSSLNDG | ETL.7380.POLE.WDPS | 2025-06-19 | 2025-06-19 | 2025-06-19 | TBC |  | 2025-12-19 | 2025-12-19 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair
LC | 131385029 | 015/000 | T3 LAURELES-OTTER 015/000 RPR GYWW | MOSSLNDG | ETL.7380.POLE.WDPS | 2025-06-19 | 2025-06-19 | 2025-06-19 | TBC |  | 2025-12-19 | 2025-12-19 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 BRIN | No Good/Out of Stdrd | Guy Wire-Wood | Repair
LC | 125148558 | 026/125 | T2NT CRTINA-MNDCN#1 26/125 INS DAMS | WILLITS | ETL.1330.INSL.NCER | 2022-12-20 | 2022-12-20 | 2022-12-20 | TBC |  | 2025-12-20 | 2025-12-20 | 628 | TR2N |  | E - Schd Compl Yr 0 | Open | RELW OTHR OH FMOB TR2 TR2N PRTO FRAB NTDE | No Good/Out of Stdrd | Damper-Steel | Replace | 45983215 | T2NT WV CORTINA-MENDCN#1 26/125 INS DAMS | ICS
LC | 125154037 | 003/020 | T3NT WV SOBRANTE-""G"" #1" 3/20 RPR DAMW | CONCORD | ETL.3720.INSL.NCER | 2022-12-20 | 2022-12-20 | 2024-10-20 | On-Time |  | 2025-12-20 | 2025-12-20 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 PRTO NTDE | Missing | Damper-Steel | Install | 46289966 | T3NT WV SOBRANTE-""G"" #1" 3/20 RPR DAMW | ICS
LC | 125170549 | 078/319 | T2NT RND MT-TB MT #2 78/319 RPR STRT | TABLEMTN | ETL.6070.TOWR | 2022-12-20 | 2022-12-20 | 2022-12-20 | TBC |  | 2025-12-20 | 2025-12-20 | 543 | TR2N |  | E - Schd Compl Yr 0 | Open | RELW CREW OH FMOB TR2 FRAB | No Good/Out of Stdrd | Structure-Tower | Repair | 45699366 | T2NT RND MT-TB MT #2 78/319 RPR STRT | ICQ
LC | 128698292 | 031/009 | T2 RIO DL JCT-BRDGVLE 31/9 RPL STRW | EUREKA | ETL.7850.POLE.WOOD | 2024-05-01 | 2024-05-01 | 2024-05-01 | TBC |  | 2025-12-20 | 2025-12-20 | 372T | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35573120 | T2 EI RIO DL JCT-BRDGVLE 31/9 RPL STRW | 70Y
LC | 128703707 | 031/005 | T2 EI RIO DL JCT-BRDGVLE 31/5 RPL SPLW | EUREKA | ETL.7850.INSL.NCER | 2024-05-02 | 2024-05-02 | 2024-05-02 | TBC |  | 2025-12-20 | 2025-12-20 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO | No Good/Out of Stdrd | Splice-Wood | Replace | 46345840 | T2 EI RIO DL JCT-BRDGVLE 31/5 RPL SPLW | ICW
LC | 131387989 | 002/027 | T3 BURNS-LONE STAR #1 02/27 RMV BRSH | MOSSLNDG | ETL.6230.POLE.NWOD | 2025-06-20 | 2025-06-20 | 2025-06-20 | TBC |  | 2025-12-20 | 2025-12-20 | 932 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH FMOB TR3 FRAB BRIN ETRI | Brush Fuel | Road | Remove | 46544724 | T3 BURNS-LONE STAR #1 02/27 RMV BRSH | CHS
LC | 131387996 | 001/023 | T3 BURNS-LONE STAR #1 01/23 RMV BRSH | MOSSLNDG | ETL.6230.POLE.STPS | 2025-06-20 | 2025-06-20 | 2025-06-20 | TBC |  | 2025-12-20 | 2025-12-20 | 932 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW COMP OH FMOB TR3 BRIN ETRI | Brush Fuel | Road | Remove | 46544724 | T3 BURNS-LONE STAR #1 02/27 RMV BRSH | CHS
LC | 131395425 | ?009/008 | T3 SNTH LN-HLF MN BY ?9/8 RPR INSW | METCALF | ETL.7212.INSL.NCER | 2025-06-23 | 2025-06-20 | 2025-06-20 | TBC |  | 2025-12-20 | 2025-12-20 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW SPCR ACCL OH TR3 AIR FRAB | No Good/Out of Stdrd | Insulator-Wood | Repair
LC | 131399435 | 022/126 | T3 PARKWAY MORAGA 22/126 RPR SHLS | CONCORD | ETL.5930.TOWR | 2025-06-24 | 2025-06-20 | 2025-06-20 | TBC |  | 2025-12-20 | 2025-12-20 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46544943 | T3 PARKWAY MORAGA 22/126 RPR SHLS | ICS
LC | 131399685 | 021/120 | T3 PARKWAY MORAGA 21/120 RPR SHLS | CONCORD | ETL.5930.TOWR | 2025-06-24 | 2025-06-20 | 2025-06-20 | TBC |  | 2025-12-20 | 2025-12-20 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Shield Wire - Steel | Repair | 46544940 | T3 PARKWAY MORAGA 21/120 RPR SHLS | ICS
LC | 131399687 | 021/120 | T3 PARKWAY MORAGA 21/120 COTTER | CONCORD | ETL.5930.INSL.NCER | 2025-06-24 | 2025-06-20 | 2025-06-20 | TBC |  | 2025-12-20 | 2025-12-20 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | RELW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Insulator-Steel | Repair | 46544942 | T3 PARKWAY MORAGA 21/120 COTTER | ICS
LC | 131406842 | 003/027 | T3 MORAGA-SAN LEANDRO #3 3/27 INS HRDT | CONCORD | ETL.2790.TOWR | 2025-06-26 | 2025-06-20 | 2025-06-20 | TBC |  | 2025-12-20 | 2025-12-20 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB NTDE BRIN | Missing | Hardware-Tower | Install
LC | 125191390 | 025/004 | T2NT HARTLEY-CLEARLAKE 25/04 RPL POLE | WILLITS | ETL.7515.POLE.WOOD | 2022-12-21 | 2022-12-21 | 2022-12-21 | TBC |  | 2025-12-21 | 2025-12-21 | 372 | TR2N |  | E - Schd Compl Yr 0 | Open | POHW OTHR OH TR2N PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 31633606 | T0 HARTLEY CLEARLAKE 24/12 RPL POLE | 70Y
LC | 130522012 | 77 | T2 EI SAN LUIS OBISPO-CYCS 4/28 RPR SWTC | PISMOBCH | ETL.9090.SWIT | 2024-12-21 | 2024-12-21 | 2024-12-21 | TBC |  | 2025-12-21 | 2025-12-21 | 623 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB TR2 PRTO | Out of Adjustment | Switch | Repair | 46478013 | T2 EI SAN LUIS OBISPO-CYCS 4/28 RPR SWTC | ICE
LC | 131395384 | 019/109 | T3 PARKWAY-MORAGA 19/109 RPL HNGR | CONCORD | ETL.5930.TOWR | 2025-06-23 | 2025-06-22 | 2025-06-22 | TBC |  | 2025-12-22 | 2025-12-22 | 543 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE SPCR OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Hanger Plate - Tower | Replace
LC | 131407100 | 000/003 | T3 SPNG GAP TAP 0/3L RPL STRW | VICTOR | ETL.1402.POLE.WDPS | 2025-06-26 | 2025-06-22 | 2025-06-22 | TBC |  | 2025-12-22 | 2025-12-22 | 372 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW ACCL OH TR3 AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Replace
LC | 131407106 | 000/003 | T3 SPNG GAP TAP 0/3C RPL STRW | VICTOR | ETL.1402.POLE.WDPS | 2025-06-26 | 2025-06-22 | 2025-06-22 | TBC |  | 2025-12-22 | 2025-12-22 | 372 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW SPCR ACCL OH TR3N AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Replace
LC | 131407107 | 000/003 | T3 SPNG GAP TAP 0/3R RPL STRW | VICTOR | ETL.1402.POLE.WDPS | 2025-06-26 | 2025-06-22 | 2025-06-22 | TBC |  | 2025-12-22 | 2025-12-22 | 372 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW SPCR ACCL OH TR3 AIR BRIN | No Good/Out of Stdrd | Structure-Wood | Replace
LC | 130534651 | 25 | T2NT EI SLO CAYUCOS 3/17A RPR SWTC | PISMOBCH | ETL.9090.SWIT | 2024-12-23 | 2024-12-23 | 2024-12-23 | TBC |  | 2027-12-23 | 2025-12-23 | 623 | TR2 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR2 PRTO | Out of Adjustment | Switch | Repair
LC | 130535338 | 010/203 | T2 DI HAT CREEK #1-WSTWD 10/203 RPR JUMW | TABLEMTN | ETL.7030.INSL.NCER | 2024-12-23 | 2024-12-23 | 2025-06-26 | On-Time |  | 2025-12-23 | 2025-12-23 | 630 | TR2 |  | E - Schd Compl Yr 0 | Closed | RELW COMP OH TR2 PRTO AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair | 46463887 | T2 DI HTCRK#1-WSTWD 10/203 RPR JUMP | ICW
LC | 131406931 | 004/007 | T3 PTR VLY WILTS 4/007 RPR JUMW | WILLITS | ETL.7820.INSL.NCER | 2025-06-26 | 2025-06-23 | 2025-06-23 | TBC |  | 2025-12-23 | 2025-12-23 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE OH TR3 AIR FRAB BRIN | No Good/Out of Stdrd | Jumper-Wood | Repair
LC | 131407084 | 000/005 | T3 GEYSERS #11 EAGLE ROCK 0/5 TOUCH | LAKEVLLE | ETL.4391.POLE.NWOD | 2025-06-26 | 2025-06-23 | 2025-06-23 | TBC |  | 2025-12-23 | 2025-12-23 | 628 | TR3 |  | E - Schd Compl Yr 0 | Open | POHW FIRE ACCH OH TR3 AIR FRAB NTDE BRIN | No Good/Out of Stdrd | Structure-Steel | Repair
LC | 130545186 | 032/625 | T2 HAT CREEK #1-WESTWOOD 32/625 RPR CNDW | TABLEMTN | ETL.7030.INSL.NCER | 2024-12-26 | 2024-12-24 | 2024-12-24 | TBC |  | 2025-06-24 | 2025-12-24 | 630 | TR2 |  | E - Schd Compl Yr 0 | Open | RELW COMP OH TR2 PRTO AIR FRAB DURA BRIN | No Good/Out of Stdrd | Conductor-Wood | Repair | 46463888 | T2 DI HAT CRK #1-WSTWD 32/625 RPR CNDW | ICW
LC | 128703588 | 031/004 | T2 EI RIO DL JCT-BRDGVLE 31/4 RPL SPLW | EUREKA | ETL.7850.INSL.NCER | 2024-05-02 | 2024-05-02 | 2024-05-02 | TBC |  | 2025-12-25 | 2025-12-25 | 630 | TR2 | YES | E - Schd Compl Yr 0 | Open | RELW INSP OH FMOB XMPT TR2 PRTO | No Good/Out of Stdrd | Splice-Wood | Replace | 46345799 | T2 EI RIO DL JCT-BRDGVLE 31/4 RPL SPLW | ICW
LC | 131401745 | 008/006 | T3 MONTE RIO-FULTON 8/6 INS DMPW | LAKEVLLE | ETL.7630.INSL.CERA | 2025-06-25 | 2025-06-25 | 2025-06-25 | TBC |  | 2025-12-25 | 2025-12-25 | 630 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW OTHR OH FMOB TR3 FRAB NTDE BRIN | Missing | Damper-Wood | Install
LC | 131406209 | 001/013 | T3 MORAGA-OAKLAND #2 1/13 GROUNDWASH | CONCORD | ETL.2730.INSL | 2025-06-26 | 2025-06-26 | 2025-06-26 | TBC |  | 2025-12-26 | 2025-12-26 | 622 | TR3 |  | E - Schd Compl Yr 0 | Open | REGW NONR OH FMOB TR3 MBSF FRAB BRIN | Contaminated | Insulator | Ground Wash
LC | 131406259 | 006/149 | T3 DEER CREEK-DRUM 006/149 RPL ANCT | SACTO | ETL.6690.POLE.NWOD | 2025-06-26 | 2025-06-26 | 2025-06-26 | TBC |  | 2025-12-26 | 2025-12-26 | 93Z | TR3 |  | E - Schd Compl Yr 0 | Open | REGW INSP OH FMOB TR3 FRAB BRIN | Missing | Anchor-Tower | Install
LC | 125255219 | 008/075 | T2NT WV CRAG VIEW-CASCADE 8/075 RPR SPLW | TABLEMTN | ETL.1350.INSL.CERA | 2022-12-27 | 2022-12-27 | 2024-02-27 | On-Time |  | 2025-12-27 | 2025-12-27 | 630 | TR2N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR2N NTDE | No Good/Out of Stdrd | Splice-Wood | Repair | 45698563 | T2NT WV CRAG VIEW-CASCADE 8/075 RPR SPLW | ICW
LC | 125255277 | T041 | T3NT WV MIDWAY-SNTA ARI T041 RPR DMPS | PISMOBCH | ETL.9240.TOWR | 2022-12-27 | 2022-12-27 | 2024-10-28 | On-Time |  | 2025-12-27 | 2025-12-27 | 628 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3 FRAB NTDE | No Good/Out of Stdrd | Damper-Steel | Replace | 46089982 | T3NT WV MIDWAY-SNTA ARI T041 RPR DMPS | ICS
LC | 125267700 | 003/080 | T3NT WV KILARC-CEDAR CREEK 9/80 RPR SPLW | TABLEMTN | ETL.7290.INSL.NCER | 2022-12-30 | 2022-12-30 | 2024-03-20 | On-Time |  | 2025-12-30 | 2025-12-30 | 630 | TR3N |  | E - Schd Compl Yr 0 | Closed | RELW OTHR COMP OH FMOB TR3N FRAB NTDE | Missing | Damper-Wood | Install | 46092048 | T3NT WV KILARC-CEDAR CREEK 9/80 RPR SPLW | ICW
LC | 130579404 | 011/151A | T2 JOLON TAP 011/151A RPL POLE | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-12-31 | 2024-12-31 | 2025-01-19 | On-Time |  | 2025-12-31 | 2025-12-31 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW TNT COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35587537 | T2 DI JOLON TAP 011/151C RPL PL | 70Y
LC | 130579406 | 011/151B | T2 JOLON TAP 011/151B RPL POLE | MOSSLNDG | ETL.7321.POLE.WOOD | 2024-12-31 | 2024-12-31 | 2025-01-19 | On-Time |  | 2025-12-31 | 2025-12-31 | 372 | TR2 |  | E - Schd Compl Yr 0 | Closed | POHW TNT COMP OH TR2 PRTO FRAB | No Good/Out of Stdrd | Structure-Wood | Replace | 35587537 | T2 DI JOLON TAP 011/151C RPL PL | 70Y
Formulas:
SOMS DUE Date = DATE(YEAR([Notification date])+1,MONTH([Notification date]),DAY([Notification date]))
SOMS DUE Date = DATE(YEAR([Notification date]),MONTH([Notification date])+6,DAY([Notification date]))