## Master Data
MDF ID | In EMT | In ProntoForms | In GCM | DiRT Investigation Documents on Sharepoint | Event Date | Month Name | Month | Year | EMT # | PM Number | Notification/Leak# | County | PG&E Region | PG&E Division | DiRT Division | City | ARCHIVED Valid for STIP (Yes/No) | Dig-in Description | Coating/Wrap Damage | Facility Type | Gas Release? | Excavation Method | Work Performed Type | Root Cause | Valid USA? | USA Ticket # | Contact Type | Damage Caused By | Contractor Name | Line Use | ARCHIVED PG&E At-Fault | L&M Error? | At-Fault Error Type | At-Fault Comment | Quarter | Within Last 12 Months? | Mapping Color | PG&E Group | Late Ticket Dig-In | Exclusion Reason | Reporting Type | Reported in Year | Date Discovered | Pipe Size | Depth of Facility | Minutes of Gas Release | Reason for No USA | Date Discovered Month | Date Discovered Month Name | Date Discovered Year | Locator Status | CLSB # | Hand Tools | New Region | Regions 2025
23295 |  | x |  | x | 2025-04-01 | Apr | 4 | 2025 | 119121 |  |  | Fresno | Central Valley | Fresno | South | Selma | Yes | Eagle Concrete damaged a 1/2" plastic gas service with a pickaxe while doing Curb/Sidewalk Work. No 811 Ticket. | No | Gas Line | Yes | Pickaxe | Curb/Sidewalk Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Eagle Concrete | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-01 | ½” | 31 | 108 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 4 | Apr | 2025 |  | 913898 | Yes | Central Valley | Central Valley
23296 | x | x |  | x | 2025-04-01 | Apr | 4 | 2025 | 119191 |  |  | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | City of San Jose damaged a 1 1/4" plastic gas main and a 1/2" plastic gas service with a backhoe while doing sewer work. Valid 811 ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025030600270 | Dig-In to PG&E Underground | 3rd Party-Contractor | City of San Jose | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-01 | 1 ¼” | 33 | 80 | N/A | 4 | Apr | 2025 |  |  | No | South Bay & Central Coast | South Bay & Central Coast
23297 | x | x | x | x | 2025-04-02 | Apr | 4 | 2025 | 119211 |  | 131039425 | Marin | North Coast | Marin | North | Sausalito | Yes | Maggiora & Ghilotti damaged a 1/2" aldyl-a gas service stub with a excavator while doing water main install. Valid 811 Ticket. PG&E At Fault. Wire Error. Locating Wire Missing or Broken | No | Gas Line | Yes | Excavator | Water | Locating Wire Missing or Broken | Yes | 2024111401114 | Dig-In to PG&E Underground | 3rd Party-Contractor | Maggiora & Ghilotti Inc | Distribution Service |  | Yes | Locator Error - No Mark | Did not mark locatable facility | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-02 | ½” | 12 | 24 | N/A | 4 | Apr | 2025 | Bargaining Unit | 226767 | No | North Coast | North Coast
23298 | x | x | x | x | 2025-04-02 | Apr | 4 | 2025 | 119221 |  | 131040392 | Butte | Northern | North Valley | North | Oroville | Yes | Homeowner damaged a 1/2" plastic gas service with a excavator while doing sewer and septic work. No 811 Ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-02 | ½” | 36 | 37 | Believed they knew where underground utility was from previous knowledge | 4 | Apr | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23299 | x | x |  | x | 2025-04-02 | Apr | 4 | 2025 | 119217 |  |  | Butte | Northern | North Valley | North | Chico | Yes | Morello Construction damaged a 2" plastic gas main and a 4" electric conduit with a Horizontal Directional Drill while doing telecommunication work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Drilling Equipment | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025032702824 | Dig-In to PG&E Underground | 3rd Party-Contractor | Morello Construction | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-02 | 2” | 32 | 60 | N/A | 4 | Apr | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23300 | x | x | x | x | 2025-04-02 | Apr | 4 | 2025 | 119237 |  | 131041536 | Merced | Central Valley | Yosemite | South | Merced | Yes | Jerry's Trenching Service damaged a 2" plastic gas main with boring equipment while doing telecommunications work. Valid 811 Ticket. Excavator Failed to Maintain Clearance After Verifying Marks | No | Gas Line | Yes | Boring Equipment | Telecommunications | Excavator Failed to Maintain Clearance After Verifying Marks | Yes | 2025022002544 | Dig-In to PG&E Underground | 3rd Party-Contractor | Jerry’s Trenching Service | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-02 | 2” | 42 | 86 | N/A | 4 | Apr | 2025 |  | 228083 | No | Central Valley | Central Valley
23301 | x | x | x | x | 2025-04-03 | Apr | 4 | 2025 | 119276 |  | 131044112 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Florez Paving damaged a 1" plastic gas service with a backhoe while doing water main install. Valid 811 Ticket. Excavated prior to receiving a positive response | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Excavated Prior to Receiving a Positive Response From All Utilities | Yes | 2025032800129 | Dig-In to PG&E Underground | 3rd Party-Contractor | Florez Paving | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-03 | 1” | 58 | 24 | N/A | 4 | Apr | 2025 |  | 766999 | No | North Valley & Sierra | North Valley & Sierra
23302 | x | x |  | x | 2025-04-03 | Apr | 4 | 2025 | 119268 |  |  | Contra Costa | Bay Area | Diablo | South | Moraga | Yes | Alamo Landscape and maintenance damaged a 3/4" steel gas service with a skid steer while doing drive way work. Valid 811 ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | No | Skid Steer | Driveway Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025032701054 | Dig-In to PG&E Underground | 3rd Party-Contractor | Alamo Landscape and Maintenance | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-03 | ¾” | 12 | 1 | N/A | 4 | Apr | 2025 |  | 992321 | No | Bay Area | Bay Area
23303 | x | x | x | x | 2025-04-04 | Apr | 4 | 2025 | 119331 |  | 131051507 | San Mateo | Central Coast | Belmont | Central | San Carlos | Yes | Kerex Engineering, Inc. damaged a 1/2" plastic gas service with a backhoe with doing curb/sidewalk work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation or Boring Equipment | No | Gas Line | Yes | Backhoe/Trackhoe | Curb/Sidewalk Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025031902571 | Dig-In to PG&E Underground | 3rd Party-Contractor | Kerex Engineering, Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-04 | ½” | 36 | 7 | N/A | 4 | Apr | 2025 |  | 1002913 | No | Bay Area | Bay Area
23304 | x | x | x | x | 2025-04-04 | Apr | 4 | 2025 | 119336 |  | 131051682 | Shasta | Northern | North Valley | North | Redding | Yes | Unlicensed Contractor damaged a 3/4" steel gas service with a skid steer while doing blading/lot grading work. No 811 Ticket. | No | Gas Line | Yes | Skid Steer | Blading/Lot Grading | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-04 | ¾” | 24 | 32 | No Knowledge of USA Ticketing Process | 4 | Apr | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23305 |  | x |  | x | 2025-04-04 | Apr | 4 | 2025 | OIS 2753623 |  |  | El Dorado | Northern | Sacramento | North | Placerville | No | Dars Cox Construction damaged an electric 4/0 Triplex 3" Conduit with a excavator with doing electric work. Valid 811 Ticket. Excavated outside of delineated area. Electric Dig In, Not valid for STIP. | No | Electric Line | No | Excavator | Electric Work | Excavated outside delineated area | Yes | 202502101479 | Dig-In to PG&E Underground | 2nd Party-Contractor | Dars Cox Construction | Electric |  | No | N/A |  | 2025 Q2 | Yes | Orange | PG&E GC Electric |  |  | 2nd Party Electric | Yes | 2025-04-04 |  | 33 | 0 | N/A | 4 | Apr | 2025 |  | 1063607 | No | North Valley & Sierra | North Valley & Sierra
23306 | x | x | x | x | 2025-04-04 | Apr | 4 | 2025 | 119317 |  | 131050913 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | DC Construction damaged a 1/2" plastic gas service line with a wooden stake while doing foundation work. No 811 Ticket. | No | Gas Line | Yes | Stake | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | DC Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-04 | ½” | 30 | 26 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  | 995488 | Yes | South Bay & Central Coast | South Bay & Central Coast
23307 | x | x | x | x | 2025-04-05 | Apr | 4 | 2025 | 119350 |  | 131052512 | San Joaquin | Central Valley | Stockton | South | Stockton | Yes | Homeowner damaged a 1/2" plastic gas service with a shovel while doing tree work. No 811 Ticket. | No | Gas Line | Yes | Shovel | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-05 | ½” | 18 | 22 | No Knowledge of USA Ticketing Process | 4 | Apr | 2025 |  |  | Yes | Central Valley | Central Valley
23308 | x | x | x | x | 2025-04-05 | Apr | 4 | 2025 | 119351 |  | 131052553 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Homeowner damaged a 1/2" plastic gas service with a post hole digger while doing fence work. No 811 Ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-05 | ½” | 30 | 15 | Excavator Did Not Believe a USA Ticket was Required | 4 | Apr | 2025 |  |  | Yes | Central Valley | Central Valley
23309 | x | x | x | x | 2025-04-05 | Apr | 4 | 2025 | 119348 |  | 131052336 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Jarco Land Inc. damaged a 1" plastic gas service with a stake while doing curb/sidewalk concrete work. No 811 Ticket. | No | Gas Line | Yes | Stake | Curb/Sidewalk Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Jarco Land Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-05 | 1” | 20 | 1 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  | 1062523 | Yes | North Coast | North Coast
23310 | x | x | x | x | 2025-04-05 | Apr | 4 | 2025 | 119357 |  | 131052727 | Alameda | Bay Area | Mission | South | Pleasanton | Yes | SU Construction Sudio Inc. damaged a 1/2" plastic gas service with a shovel while doing water work. Valid 811 Ticket. Excavated Prior to Receiving a Positive Response From All Utilities | No | Gas Line | Yes | Shovel | Water | Excavated Prior to Receiving a Positive Response From All Utilities | Yes | 2025040500190 | Dig-In to PG&E Underground | 3rd Party-Contractor | SU Construction Studio Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-05 | ½” | 48 | 88 | N/A | 4 | Apr | 2025 |  | 1083081 | Yes | Bay Area | Bay Area
23311 | x | x | x | x | 2025-04-06 | Apr | 4 | 2025 | 119373 |  | 131053102 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Krufal Construction damaged a 1/2" plastic gas service line with a shovel while doing building demo work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Building Demolition | Failed to Dig with Care | Yes | 2025031101023 | Dig-In to PG&E Underground | 3rd Party-Contractor | Krufal Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-06 | ½” | 24 | 11 | N/A | 4 | Apr | 2025 |  |  | Yes | Central Valley | Central Valley
23312 | x | x | x | x | 2025-04-06 | Apr | 4 | 2025 | 119377 |  | 131053301 | Solano | Northern | North Bay | North | Rio Vista | Yes | Homeowner damaged a 3/4" Steel Gas Service inserted into a 2" Steel Gas Main with a backhoe while doing water work. No 811 Ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-06 | ¾” | 32 | 78 | No Knowledge of USA Ticketing Process | 4 | Apr | 2025 |  |  | No | North Coast | North Coast
23313 | x | x | x | x | 2025-04-07 | Apr | 4 | 2025 | 119426 |  | 131056696 | Contra Costa | Bay Area | Diablo | South | Danville | Yes | Olwin Landscape Design & Construction Inc. damaged a 1/2" plastic gas service with a excavator while doing irrigation work. No 811 Ticket. | No | Gas Line | Yes | Excavator | Irrigation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Olwin Landscape Design & Construction Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-07 | ½” | 36 | 27 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 4 | Apr | 2025 |  | 752929 | No | Bay Area | Bay Area
23314 | x | x | x | x | 2025-04-07 | Apr | 4 | 2025 | 119403 |  | 131055401 | Santa Clara | Central Coast | San Jose | Central | Santa Clara | Yes | Peninsula Demolition and Deconstruction damaged a 1/2" plastic gas service with a excavator while doing tree demo work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Excavator | Tree Removal/Stump Grinding | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2024121801463 | Dig-In to PG&E Underground | 3rd Party-Contractor | Peninsula Demolition and Deconstruction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-07 | ½” | 18 | 9 | N/A | 4 | Apr | 2025 |  | 1081696 | No | South Bay & Central Coast | South Bay & Central Coast
23315 | x | x | x | x | 2025-04-07 | Apr | 4 | 2025 | 119410 |  | 131055777 | Merced | Central Valley | Yosemite | South | Merced | Yes | Ranchwood Contractors damaged a 1/2" plastic gas service with a mini excavator while doing site development work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Excavator | Site Development | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025040203044 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ranchwood Contractors | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-07 | ½” | 40 | 26 | N/A | 4 | Apr | 2025 |  | 708848 | No | Central Valley | Central Valley
23316 | x | x | x | x | 2025-04-07 | Apr | 4 | 2025 | 119406 |  | 131055606 | Sacramento | Northern | Sacramento | North | Citrus Heights | Yes | Express Sewer and Drain damaged a 1/2" aldyl-a gas service with a mini excavator while doing sewer work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025032601471 | Dig-In to PG&E Underground | 3rd Party-Contractor | Express Sewer and Drain | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-07 | ½” | 36 | 10 | N/A | 4 | Apr | 2025 |  | 882660 | No | North Valley & Sierra | North Valley & Sierra
23317 |  | x |  | x | 2025-04-07 | Apr | 4 | 2025 | OIS 2755462 |  |  | Solano | Northern | North Bay | North | Vacaville | No | Homeowner damaged a secondary electric line with a excavator while doing stump removal. No 811 Ticket. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Excavator | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Electric |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Electric | Yes | 2025-04-07 |  |  | 0 | No Knowledge of USA Ticketing Process | 4 | Apr | 2025 |  |  | No | North Coast | North Coast
23318 | x | x | x | x | 2025-04-08 | Apr | 4 | 2025 | 119477 |  | 131061513 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Chavez Concrete and Landscaping damaged a 1/2-inch Aldyl-A gas service with a trencher while doing landscape work. No 811 Ticket. | No | Gas Line | Yes | Trencher | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Chavez Concrete and landscaping | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-08 | ½” | 15 | 25 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  | 1008455 | No | North Valley & Sierra | North Valley & Sierra
23319 |  | x |  | x | 2025-04-08 | Apr | 4 | 2025 | OIS 35619904 |  |  | Santa Barbara | Central Coast | Los Padres | South | Lompoc | No | William Rieck Plumbing damaged a residential secondary service with a high-pressure power water jetter while cleaning out a sewer lateral. No 811 Ticket. Electric Dig In, Not valid for STIP. | No | Electric Line | No | Other Hand Machinery | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Main Line Engineering | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-04-08 |  |  | 0 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  | 805755 | No | South Bay & Central Coast | South Bay & Central Coast
23320 | x | x | x | x | 2025-04-08 | Apr | 4 | 2025 | 119475 |  | 131061205 | Contra Costa | Bay Area | Diablo | South | Danville | Yes | Juan Rios Landscaping damaged a 1" plastic gas service with a front loader while doing landscape work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Front Loader | Landscaping | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025012600395 | Dig-In to PG&E Underground | 3rd Party-Contractor | Juan Rios Landscaping | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-08 | 1” | 36 | 20 | N/A | 4 | Apr | 2025 |  | 948480 | No | Bay Area | Bay Area
23321 | x | x | x | x | 2025-04-08 | Apr | 4 | 2025 | 119452 |  | 131059695 | Solano | Northern | North Bay | North | Fairfield | Yes | Sunrun damaged a 1/2" plastic gas service with a shovel while doing solar install. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | 2025040200821 | Dig-In to PG&E Underground | 3rd Party-Contractor | Sunrun | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-08 | ½” | 32 | 27 | N/A | 4 | Apr | 2025 |  | 750184 | Yes | North Coast | North Coast
23322 |  | x |  | x | 2025-04-09 | Apr | 4 | 2025 | OIS 2756892 |  |  | Santa Clara | Central Coast | De Anza | Central | Saratoga | No | Lindco Energy Division Inc damaged a secondary electric line with a cutting machine while doing electric work. No 811 Ticket. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Cutting Machine | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Lindco Energy Division | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-04-09 |  | 16 | 0 | Excavator Asserted They Could Not Wait | 4 | Apr | 2025 |  | 948387 | No | South Bay & Central Coast | South Bay & Central Coast
23323 | x | x | x | x | 2025-04-09 | Apr | 4 | 2025 | 119516 |  | 131066539 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | The Electric Company damaged a 1/2" plastic gas service with a shovel while doing electric work to upgrade a panel for a customer. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | 2025032402652 | Dig-In to PG&E Underground | 3rd Party-Contractor | The Electric Company | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-09 | ½” | 39 | 30 | N/A | 4 | Apr | 2025 |  | 1050612 | Yes | Central Valley | Central Valley
23324 | x | x | x | x | 2025-04-09 | Apr | 4 | 2025 | 119489 |  | 131064750 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Florez Paving damaged a 3/4" steel gas service with a mini excavator while doing water main install. Valid 811 Ticket. PG&E At Fault. Locator Error - No Mark. Facility was not Located or Marked | No | Gas Line | Yes | Excavator | Water | Facility was not Located or Marked | Yes | 2025032800129 | Dig-In to PG&E Underground | 3rd Party-Contractor | Florez Paving | Distribution Service |  | Yes | Locator Error - No Mark | Did not count services | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-09 | ¾” | 20 | 29 | N/A | 4 | Apr | 2025 | Bargaining Unit | 766999 | No | North Valley & Sierra | North Valley & Sierra
23325 | x | x |  | x | 2025-04-10 | Apr | 4 | 2025 | 119584 |  |  | Contra Costa | Bay Area | Diablo | South | Martinez | Yes | Homeowner damaged a 1/2" plastic gas service with a excavator while doing electric work. No 811 Ticket. | No | Gas Line | Yes | Excavator | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-10 | ½” | 24 | 22 | Believed they knew where underground utility was from previous knowledge | 4 | Apr | 2025 |  |  | No | Bay Area | Bay Area
23326 | x | x |  | x | 2025-04-10 | Apr | 4 | 2025 | 119552 |  |  | Butte | Northern | North Valley | North | Chico | Yes | West Coast Pipeline Solutions damaged a 1/2" plastic gas service with a shovel while doing telecommunication work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Dig with Care | Yes | 2025032702824 | Dig-In to PG&E Underground | 3rd Party-Contractor | West Coast Pipeline Solution Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-10 | ½” | 32 | 21 | N/A | 4 | Apr | 2025 |  | 1054122 | Yes | North Valley & Sierra | North Valley & Sierra
23327 | x | x | x | x | 2025-04-11 | Apr | 4 | 2025 | 119615 |  | 131108725 | Santa Clara | Central Coast | De Anza | Central | Sunnyvale | Yes | Jaz Builders damaged a 1/2" plastic gas service with a shovel while doing landscaping work. No 811 Ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Jaz Builders Inc | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-11 | ½” | 30 | 11 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 4 | Apr | 2025 |  | 1089478 | Yes | South Bay & Central Coast | South Bay & Central Coast
23328 | x | x | x | x | 2025-04-11 | Apr | 4 | 2025 | 119609 |  | 131098834 | Contra Costa | Bay Area | Diablo | South | Pleasant Hill | Yes | Custom Fire Protection Inc damaged a 1/2" plastic gas service with a shovel while doing site development. No 811 Ticket. | No | Gas Line | Yes | Shovel | Site Development | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Custom Fire Protection Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-11 | ½” | 36 | 54 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 4 | Apr | 2025 |  | 1044448 | Yes | Bay Area | Bay Area
23329 | x | x | x | x | 2025-04-11 | Apr | 4 | 2025 | 119621 |  | 131100115 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service with a shovel while doing work to dig a trench for a homeowner for electric upgrade. No 811 Ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-11 | ½” | 36 | 27 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 4 | Apr | 2025 |  |  | Yes | South Bay & Central Coast | South Bay & Central Coast
23330 | x | x | x | x | 2025-04-12 | Apr | 4 | 2025 | 119639 |  | 131102234 | Contra Costa | Bay Area | Diablo | South | Pittsburg | Yes | Homeowner damaged a 1/2" plastic gas service with a shovel while doing fence work. No 811 Ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-12 | ½” | 18 | 22 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  |  | Yes | Bay Area | Bay Area
23331 |  | x |  | x | 2025-04-12 | Apr | 4 | 2025 | OIS 2759509 |  |  | Placer | Northern | Sierra | North | Gold Run | No | Homeowner damaged a 4/0 secondary electric line with a tractor while doing landscape work. No 811 Ticket. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Tractor | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Electric |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Electric | Yes | 2025-04-12 |  |  | 0 | No Knowledge of USA Ticketing Process | 4 | Apr | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23332 |  | x |  | x | 2025-04-14 | Apr | 4 | 2025 | OIS 2760350 |  |  | Contra Costa | Bay Area | Diablo | South | Discovery Bay | No | Unlicensed Contractor damaged a streetlight electric line with a shovel while doing tree removal and stump grinding. No 811 Ticket. Electric Dig IN, Not Valid for STIP. | No | Electric Line | No | Shovel | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-04-14 |  | 24 | 0 | No Knowledge of USA Ticketing Process | 4 | Apr | 2025 |  |  | Yes | Bay Area | Bay Area
23333 | x | x | x | x | 2025-04-14 | Apr | 4 | 2025 | 119691 |  | 131105415 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Skytek General Engineering damaged a 1/2" plastic gas service line with a shovel while doing foundation work. No 811 Ticket. | No | Gas Line | Yes | Shovel | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Skytec General Engineering | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-14 | ½” | 22 | 25 | No Knowledge of USA Ticketing Process | 4 | Apr | 2025 |  | 1103936 | Yes | Bay Area | Bay Area
23334 | x | x | x | x | 2025-04-14 | Apr | 4 | 2025 | 119675 |  | 131103878 | San Mateo | Central Coast | Belmont | Central | Portola Valley | Yes | Adorno Construction Inc. damaged a 1/2" plastic gas service with a shovel while doing foundation work. No 811 Ticket. | No | Gas Line | Yes | Shovel | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Adorno Construction Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-14 | ½” | 20 | 31 | Believed they knew where underground utility was from previous knowledge | 4 | Apr | 2025 |  | 743749 | Yes | Bay Area | Bay Area
23335 | x | x | x | x | 2025-04-14 | Apr | 4 | 2025 | 119690 |  | 131105368 | Sonoma | Northern | Sonoma | North | Petaluma | Yes | Serres Corporation damaged a 1 1/4" plastic gas service with a excavator while doing site development work. Valid 811 Ticket. Excavated outside delineated area | No | Gas Line | Yes | Excavator | Site Development | Excavated outside delineated area | Yes | 2025031900789 | Dig-In to PG&E Underground | 3rd Party-Contractor | Serres Corporation | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-14 | 1 ¼” | 34 | 73 | N/A | 4 | Apr | 2025 |  | 471196 | No | North Coast | North Coast
23336 | x | x |  | x | 2025-04-14 | Apr | 4 | 2025 | 119688 |  |  | San Mateo | Central Coast | Belmont | Central | San Carlos | Yes | Black Diamond Paver Stone & Landscaping damaged a 3/4" steel gas service with a skid steer while doing driveway work to install new pavers. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Skid Steer | Driveway Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025040802428 | Dig-In to PG&E Underground | 3rd Party-Contractor | Black Diamond Paver Stones & Landscape | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-14 | ¾” | 18 | 0 | N/A | 4 | Apr | 2025 |  | 841042 | No | Bay Area | Bay Area
23337 |  | x |  | x | 2025-04-14 | Apr | 4 | 2025 | OIS 9124142 |  |  | Contra Costa | Bay Area | Diablo | South | Concord | No | EJ Masonay Inc damaged an electric line with an excavator while doing a new drainage system. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment. Electric Dig In, Not valid for STIP. | No | Electric Line | No | Excavator | Drainage Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025032300453 | Dig-In to PG&E Underground | 3rd Party-Contractor | E J Masonry Inc. | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-04-14 |  | 36 | 0 | N/A | 4 | Apr | 2025 |  |  | No | Bay Area | Bay Area
23338 | x | x | x | x | 2025-04-15 | Apr | 4 | 2025 | 119733 | 47203364 | 131109042 | Contra Costa | Bay Area | Diablo | South | Pleasant Hill | Yes | Bay Side Fencing damaged a 1/2" plastic gas service with a shovel while doing fence work. Valid 811 Ticket. Excavated outside delineated area | No | Gas Line | Yes | Shovel | Fencing | Excavated outside delineated area | Yes | 2025040900235 | Dig-In to PG&E Underground | 3rd Party-Contractor | Bay Side Fencing Company | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-15 | ½” | 30 | 50 | N/A | 4 | Apr | 2025 |  | 1042534 | Yes | Bay Area | Bay Area
23339 | x | x | x | x | 2025-04-15 | Apr | 4 | 2025 | 119758 |  | 131111304 | Humboldt | Northern | Humboldt | North | Arcata | Yes | Tim’s Plumbing damaged a 1/2" plastic gas service with a shovel while doing sewer work. No 811 Ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Tim’s Plumbing | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-15 | ½” | 20 | 27 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  | 701392 | Yes | North Coast | North Coast
23340 | x | x | x | x | 2025-04-15 | Apr | 4 | 2025 | 119727 |  | 131109187 | Napa | Bay Area | North Bay | North | Calistoga | Yes | Arktos Inc. damaged a 1" plastic gas service with a post hole digger while doing fence work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Post-Hole Digger | Fencing | Failed to Dig with Care | Yes | 2025040201068 | Dig-In to PG&E Underground | 3rd Party-Contractor | Arktos Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-15 | 1” | 24 | 38 | N/A | 4 | Apr | 2025 |  | 855272 | Yes | North Coast | North Coast
23341 | x | x | x | x | 2025-04-15 | Apr | 4 | 2025 | 119738 |  | 131109419 | Alameda | Bay Area | Richmond | North | Berkeley | Yes | EBMUD damaged a1/2" plastic gas service with a backhoe while doing water main install. Valid 811 Ticket. Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | 2025030700385 | Dig-In to PG&E Underground | 3rd Party-Government Entity | EBMUD | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2025-04-15 | ½” | 31 | 14 | N/A | 4 | Apr | 2025 |  |  | No | Bay Area | Bay Area
23342 | x | x | x | x | 2025-04-15 | Apr | 4 | 2025 | 119736 |  | 131109087 | Sonoma | Northern | Sonoma | North | Sonoma | Yes | E K Excavating damaged a 3/4" steel gas service line with a excavator while doing site development work. No 811 Ticket. | No | Gas Line | Yes | Excavator | Site Development | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | EK Excavating | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-15 | ¾” | 24 | 62 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 4 | Apr | 2025 |  | 275372 | No | North Coast | North Coast
23343 | x | x | x | x | 2025-04-15 | Apr | 4 | 2025 | 119761 |  | 131112076 | Shasta | Northern | North Valley | North | Anderson | Yes | Homeowner damaged a 1/2" gas service with a shovel while doing tree removal. Valid 811 Ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Tree Removal/Stump Grinding | Failed to Dig with Care | Yes | 2025040903328 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-15 | ½” | 26 | 58 | N/A | 4 | Apr | 2025 |  |  | Yes | North Valley & Sierra | North Valley & Sierra
23344 | x | x | x | x | 2025-04-16 | Apr | 4 | 2025 | 119797 |  | 131115393 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service with a shovel while doing electric work for homeowner. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | 2025040702387 | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-16 | ½” | 30 | 19 | N/A | 4 | Apr | 2025 |  |  | Yes | Central Valley | Central Valley
23345 |  | x |  | x | 2025-04-16 | Apr | 4 | 2025 | OIS 2762212 |  |  | Fresno | Central Valley | Fresno | South | Fresno | No | Nolan Thomas Construction damaged an electric secondary line with a excavator while doing building demo work to remove a plumbing line. No 811 Ticket. Electric Dig In, Not valid for STIP. | No | Electric Line | No | Excavator | Building Demolition | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Nolan Thomas Construction | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-04-16 |  |  | 0 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  | 384104 | No | Central Valley | Central Valley
23346 | x | x |  | x | 2025-04-16 | Apr | 4 | 2025 | 119782 |  |  | Contra Costa | Bay Area | Diablo | South | Lafayette | Yes | Cratus Inc. damaged a 1/2" plastic gas service with a shovel while doing sewer work. Valid 811 Ticket. PG&E At Fault. Locator Error - Mismark. Incorrect Information or Marks | No | Gas Line | Yes | Shovel | Sewer | Incorrect Information or Marks | Yes | 2025022101299 | Dig-In to PG&E Underground | 3rd Party-Contractor | Cratus Inc | Distribution Service |  | Yes | Records Error | Incorrect GSR | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-16 | ½” | 36 | 16 | N/A | 4 | Apr | 2025 |  | 987888 | Yes | Bay Area | Bay Area
23347 | x | x |  | x | 2025-04-16 | Apr | 4 | 2025 | 119792 |  |  | Fresno | Central Valley | Fresno | South | Fresno | Yes | Haydon Construction Inc damaged a 3/4" steel gas service with a excavator while doing storm drain work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | No | Excavator | Drainage Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025011001071 | Dig-In to PG&E Underground | 3rd Party-Contractor | Haydon Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-16 | ¾” | 12 | 0 | N/A | 4 | Apr | 2025 |  | 458977 | No | Central Valley | Central Valley
23348 | x | x | x | x | 2025-04-16 | Apr | 4 | 2025 | 119778 |  | 131114171 | Contra Costa | Bay Area | Richmond | North | Richmond | Yes | Hudson Excavation Inc damaged a 1/2" plastic gas service with a excavator while doing electric work. Valid 811 Ticket. PG&E At Fault. Records Error. Incorrect Facility Records / Maps. | No | Gas Line | Yes | Excavator | Electric Work | Incorrect Facility Records / Maps | Yes | 2025040700127 | Dig-In to PG&E Underground | 3rd Party-Contractor | Hudson Excavation | Distribution Service |  | Yes | Records Error | Unmapped Stub | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-16 | ½” | 36 | 18 | N/A | 4 | Apr | 2025 |  | 599907 | No | Bay Area | Bay Area
23349 | x | x |  | x | 2025-04-17 | Apr | 4 | 2025 | 119847 |  |  | Solano | Bay Area | North Bay | North | Vallejo | Yes | Homeowner damaged a 1/2" plastic gas service with a pneumatic hammer while doing fence work. No 811 ticket. | No | Gas Line | Yes | Other Hand Tools | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-17 | ½” | 1 | 46 | No Knowledge of USA Ticketing Process | 4 | Apr | 2025 |  |  | Yes | North Coast | North Coast
23350 | x | x | x | x | 2025-04-17 | Apr | 4 | 2025 | 119842 |  | 131118266 | San Joaquin | Central Valley | Stockton | South | Lathrop | Yes | Roto Rooter damaged a 1/2" plastic gas service with a probe while doing work for plumbing for a septic tank. No 811 Ticket. | No | Gas Line | Yes | Probing Tool | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Roto Rooter | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-17 | ½” | 33 | 35 | Excavator Did Not Believe a USA Ticket was Required | 4 | Apr | 2025 |  |  | Yes | Central Valley | Central Valley
23351 | x | x | x | x | 2025-04-17 | Apr | 4 | 2025 | 119853 |  | 131119576 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Phoenix Electric Company damaged a 3" plastic gas main with a skid steer while doing electric work. Valid 811 Ticket. Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | No | Gas Line | Yes | Skid Steer | Electric Work | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | 2025031101955 | Dig-In to PG&E Underground | 3rd Party-Contractor | Phoenix Electric Co | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-17 | 3" | 25 | 69 | N/A | 4 | Apr | 2025 |  | 811031 | No | Bay Area | Bay Area
23352 | x | x |  | x | 2025-04-17 | Apr | 4 | 2025 | 119844 |  |  | San Mateo | Central Coast | Colma | Central | San Bruno | Yes | JMB Construction damaged a 1/2" plastic inserted in a 3/4" steel gas service with a backhoe while doing sewer work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | No | Backhoe/Trackhoe | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2024120301710 | Dig-In to PG&E Underground | 3rd Party-Contractor | JMB Construction Inc | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-17 | ¾” | 20 | 0 | N/A | 4 | Apr | 2025 |  | 715324 | No | Bay Area | Bay Area
23353 | x | x |  | x | 2025-04-17 | Apr | 4 | 2025 | 119855 |  |  | Alameda | Bay Area | Oakland | North | Piedmont | Yes | FCO-S Concrete Construction Company damaged a 1/2" plastic inserted into a 3/4" steel gas service line with a shovel while doing foundation work. Valid 811 Ticket. Excavated Prior to Receiving a Positive Response From All Utilities | No | Gas Line | Yes | Shovel | Foundation Work | Excavated Prior to Receiving a Positive Response From All Utilities | Yes | 2025041701839 | Dig-In to PG&E Underground | 3rd Party-Contractor | FCO-S Concrete Construction Company | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-17 | ¾” | 18 | 74 | N/A | 4 | Apr | 2025 |  | 808853 | Yes | Bay Area | Bay Area
23354 | x | x |  | x | 2025-04-18 | Apr | 4 | 2025 | 119890 |  |  | Placer | Northern | Sierra | North | Roseville | Yes | Mountain Cascade damaged a 3/4" steel gas service line with a excavator while doing sewer work. Valid 811 Ticket. Excavator Failed to Maintain Clearance After Verifying Marks | No | Gas Line | Yes | Excavator | Sewer | Excavator Failed to Maintain Clearance After Verifying Marks | Yes | 2024121002906 | Dig-In to PG&E Underground | 3rd Party-Contractor | Mountain Cascade Inc | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-18 | ¾” | 28 | 5 | N/A | 4 | Apr | 2025 |  | 422496 | No | North Valley & Sierra | North Valley & Sierra
23355 | x | x | x | x | 2025-04-18 | Apr | 4 | 2025 | 119892 |  | 131129663 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | Gator Rooting & Plumbing Inc damaged a 1" plastic gas service with a excavator while doing sewer work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025032700832 | Dig-In to PG&E Underground | 3rd Party-Contractor | Gator Rooting & Plumbing Inc | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-18 | 1” | 30 | 8 | N/A | 4 | Apr | 2025 |  | 1073039 | No | South Bay & Central Coast | South Bay & Central Coast
23356 | x | x | x | x | 2025-04-18 | Apr | 4 | 2025 | 119886 |  | 131125405 | Alameda | Bay Area | Richmond | North | Berkeley | Yes | Bay Area Home Builders damaged a 1/2" gas service aldyl-a line with a mini excavator while doing electric work for a new ADU. No 811 Ticket. | No | Gas Line | Yes | Excavator | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Bay Area Home Builders | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-18 | ½” | 6 | 19 | Didn’t think they were digging deep enough to damage an underground utility | 4 | Apr | 2025 |  | 1039108 | No | Bay Area | Bay Area
23357 |  | x |  | x | 2025-04-18 | Apr | 4 | 2025 | OIS 2763559 |  |  | Santa Clara | Central Coast | De Anza | Central | Saratoga | No | Villalobos & Associates Inc damaged a primary electric line with a auger while doing pole/post install for the city. Valid 811 Ticket. Failed to Delineate Work Site With Required Markings. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Auger | Pole/Post Installation | Failed to Delineate Work Site With Required Markings | Yes | 2025041603462 | Dig-In to PG&E Underground | 3rd Party-Contractor | Villalobos & Associates | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-04-18 |  |  | 0 | N/A | 4 | Apr | 2025 |  | 1017098 | No | South Bay & Central Coast | South Bay & Central Coast
23358 |  | x |  | x | 2025-04-18 | Apr | 4 | 2025 | OIS 2763775 |  |  | Yuba | Northern | Sierra | North | Wheatland | No | Homeowner damaged a secondary electric line with a excavator while Tree Removal/Stump Grinding. No 811 Ticket. Electric Dig In, Not Valid For STIP. | No | Electric Line | No | Excavator | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Electric |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Electric | Yes | 2025-04-18 |  | 30 | 0 | No Knowledge of USA Ticketing Process | 4 | Apr | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23359 | x | x | x | x | 2025-04-19 | Apr | 4 | 2025 | 119919 |  | 131131951 | San Joaquin | Central Valley | Stockton | South | Banta | Yes | Homeowner damaged a 1" plastic gas service with a hammer while excavating for sewer work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Other Hand Tools | Sewer | Failed to Dig with Care | Yes | 2025041701122 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-19 | 1” | 26 | 1 | N/A | 4 | Apr | 2025 |  |  | Yes | Central Valley | Central Valley
23360 | x | x | x | x | 2025-04-19 | Apr | 4 | 2025 | 119918 |  | 131131924 | Kern | Central Valley | Kern | South | Bakersfield | Yes | Homeowner damaged a 1/2" plastic gas servicer line with a shovel while doing sewer work. No 811 Ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-19 | 1” | 24 | 26 | No Knowledge of USA Ticketing Process | 4 | Apr | 2025 |  |  | Yes | Central Valley | Central Valley
23361 | x | x |  | x | 2025-04-19 | Apr | 4 | 2025 | 119914 |  |  | Sonoma | Northern | Sonoma | North | Windsor | Yes | Homeowner damaged a 3/4" steel gas service with a excavator while doing tree removal and stump grinding. No 811 Ticket. | No | Gas Line | No | Excavator | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-19 | ¾” | 12 | 0 | No Knowledge of USA Ticketing Process | 4 | Apr | 2025 |  |  | No | North Coast | North Coast
23362 | x |  | x | x | 2025-04-21 | Apr | 4 | 2025 | 119959 |  | 131145426 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Fast Response Plumbing & Rooter damaged a 1/2" plastic gas service with a shovel while doing sewer work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | 2025040703585 | Dig-In to PG&E Underground | 3rd Party-Contractor | Fast Response Plumbing & Rooter | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-21 | ½” | 26 | 46 | N/A | 4 | Apr | 2025 |  | 1024971 | Yes | Bay Area | Bay Area
23363 | x | x | x | x | 2025-04-21 | Apr | 4 | 2025 | 119975 |  | 131145923 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Homeowner damaged a 1/2" plastic gas service with a excavator while doing curb/sidewalk concrete work. No 811 Ticket. | No | Gas Line | Yes | Excavator | Curb/Sidewalk Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-21 | ½” | 24 | 6 | No Knowledge of USA Ticketing Process | 4 | Apr | 2025 |  |  | No | Central Valley | Central Valley
23364 | x | x | x | x | 2025-04-21 | Apr | 4 | 2025 | 119952 |  | 131145562 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | J. Flores Construction damaged a 1/2" plastic gas service with a backhoe while doing sewer work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025041602279 | Dig-In to PG&E Underground | 3rd Party-Contractor | J Flores Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-21 | ½” | 30 | 23 | N/A | 4 | Apr | 2025 |  | 705393 | No | Bay Area | Bay Area
23365 | x | x | x | x | 2025-04-21 | Apr | 4 | 2025 | 119964 |  | 131145514 | Humboldt | Northern | Humboldt | North | Fortuna | Yes | Fortuna Cemetery District damaged a 1" plastic gas service with a backhoe while doing water line repair. No 811 Ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Government Entity | Fortuna Cemetery District | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2025-04-21 | 1” | 36 | 65 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  |  | No | North Coast | North Coast
23366 | x | x | x | x | 2025-04-22 | Apr | 4 | 2025 | 120019 |  | 131150103 | Solano | Bay Area | North Bay | North | Vallejo | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service with a skid steer while doing landscape, tree removal and stump grinding work for the homeowner. No 811 Ticket. | No | Gas Line | Yes | Skid Steer | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-22 | ½” | 28 | 66 | No Knowledge of USA Ticketing Process | 4 | Apr | 2025 |  |  | No | North Coast | North Coast
23367 | x | x | x | x | 2025-04-22 | Apr | 4 | 2025 | 120021 |  | 131150173 | Placer | Northern | Sierra | North | Roseville | Yes | TW Enterprises damaged a 1/2" plastic gas service with a excavator while doing water work. No 811 Ticket. | No | Gas Line | Yes | Excavator | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | TWC Enterprises | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-22 | ½” | 30 | 13 | Excavator Did Not Believe a USA Ticket was Required | 4 | Apr | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23368 | x | x | x | x | 2025-04-22 | Apr | 4 | 2025 | 120032 |  | 131150676 | Santa Clara | Central Coast | De Anza | Central | Cupertino | Yes | Dryco damaged a 2" plastic gas main with a excavator while doing landscape work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Excavator | Landscaping | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025021200236 | Dig-In to PG&E Underground | 3rd Party-Contractor | DRYCO Construction | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-22 | 2” | 22 | 43 | N/A | 4 | Apr | 2025 |  | 540379 | No | South Bay & Central Coast | South Bay & Central Coast
23369 | x | x | x | x | 2025-04-22 | Apr | 4 | 2025 | 120044 |  | 131151433 | Sonoma | Northern | Sonoma | North | Sebastopol | Yes | Homeowner hired workers who damaged a 1" plastic gas service with a stake while doing drainage work. No 811 Ticket. | No | Gas Line | Yes | Stake | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-22 | 1” | 33 | 62 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  |  | Yes | North Coast | North Coast
23370 | x | x | x | x | 2025-04-22 | Apr | 4 | 2025 | 120040 |  | 131151095 | Alameda | Bay Area | Mission | South | Livermore | Yes | KS Construction and Developers Inc. damaged a 1/2" plastic gas service line with a shovel while doing sewer work. No 811 Ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | KS Construction and Developers Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-22 | ½” | 28 | 21 | Believed they knew where underground utility was from previous knowledge | 4 | Apr | 2025 |  | 955547 | Yes | Bay Area | Bay Area
23371 | x | x | x | x | 2025-04-22 | Apr | 4 | 2025 | 120050 |  | 131151339 | Nevada | Northern | Sierra | North | Grass Valley | Yes | Blacktop Always Paving damaged a 2" aldyl-A inserted in 4" plastic gas main with an excavator while doing sewer work. No 811 Ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Blacktop Asphalt | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-22 | 2” | 48 | 207 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 4 | Apr | 2025 |  | 1036777 | No | North Valley & Sierra | North Valley & Sierra
23372 |  |  |  | x | 2025-04-22 | Apr | 4 | 2025 | OIS 2764043 |  |  | Santa Clara | Central Coast | San Jose | Central | San Jose | No | Unknown party damaged secondary electric. No 811 ticket. Investigation was unable to determine who caused the damage or when. | No | Electric Line | No | Shovel | Unknown | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unknown | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-04-22 |  |  |  | Other | 4 | Apr | 2025 |  |  | Yes | South Bay & Central Coast | South Bay & Central Coast
23373 |  | x |  | x | 2025-04-23 | Apr | 4 | 2025 | 120085 |  |  | San Mateo | Central Coast | Colma | Central | San Bruno | Yes | U A Hotels Construction Inc. damaged a 1/2" plastic gas service with a sawzall while doing water work. No 811 Ticket. | No | Gas Line | Yes | Cutting Machine | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | U A Hotels Construction Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-23 | ½” | 23 | 267 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  | 707819 | No | Bay Area | Bay Area
23374 | x | x | x | x | 2025-04-23 | Apr | 4 | 2025 | 120087 | 47206413 | 131156830 | Madera | Central Valley | Yosemite | South | Madera | Yes | Homeowner damaged a 1/2" plastic gas service with a post hole digger while doing fence work. No 811 Ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-23 | ½” | 26 | 30 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  |  | Yes | Central Valley | Central Valley
23375 | x | x | x | x | 2025-04-23 | Apr | 4 | 2025 | 120082 |  | 131156634 | San Mateo | Central Coast | Colma | Central | El Granada | Yes | Delaney Construction damaged a 1/2" plastic gas service with a backhoe while doing gas trench for a new generator. No 811 Ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Gas | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Delaney Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-23 | ½” | 21 | 39 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  | 830405 | No | Bay Area | Bay Area
23376 | x | x | x | x | 2025-04-23 | Apr | 4 | 2025 | 120056 |  | 131153679 | San Joaquin | Central Valley | Stockton | South | Manteca | Yes | Evergreen Landscape damaged a 1" plastic gas service with a trencher while doing landscape work. Valid 811 ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Trencher | Landscaping | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025040301449 | Dig-In to PG&E Underground | 3rd Party-Contractor | Evergreen Landscape Company | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-23 | 1” | 26 | 32 | N/A | 4 | Apr | 2025 |  | 1021111 | No | Central Valley | Central Valley
23377 | x | x | x | x | 2025-04-23 | Apr | 4 | 2025 | 120077 |  | 131155898 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Homeowner damaged a 1/2" plastic gas service with a shovel while doing sewer work. No 811 Ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-23 | ½” | 24 | 25 | No Knowledge of USA Ticketing Process | 4 | Apr | 2025 |  |  | Yes | Central Valley | Central Valley
23378 | x |  | x | x | 2025-04-24 | Apr | 4 | 2025 | 120131 |  | 131160679 | Monterey | Central Coast | Central Coast | South | Seaside | Yes | Homeowner damaged a 1/2" plastic gas service with a post hole digger while doing fence work. No 811 Ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-24 | ½” | 18 | 26 | Other | 4 | Apr | 2025 |  |  | Yes | South Bay & Central Coast | South Bay & Central Coast
23379 | x | x | x | x | 2025-04-24 | Apr | 4 | 2025 | 120107 |  | 131158994 | Kern | Central Valley | Kern | South | Ridgecrest | Yes | Indian Wells Water District damaged a 1/2" plastic gas service with a backhoe while doing water install. Valid 811 Ticket. Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | No | Gas Line | Yes | Shovel | Water | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | 2025040701460 | Dig-In to PG&E Underground | 3rd Party-Government Entity | Indian Wells Water District | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2025-04-24 | ½” | 36 | 6 | N/A | 4 | Apr | 2025 |  |  | Yes | Central Valley | Central Valley
23380 | x | x | x | x | 2025-04-24 | Apr | 4 | 2025 | 120108 |  | 131159115 | Merced | Central Valley | Yosemite | South | Atwater | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service with a shovel while doing landscape work. No 811 Ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-24 | ½” | 30 | 2 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  |  | Yes | Central Valley | Central Valley
23381 | x |  | x | x | 2025-04-24 | Apr | 4 | 2025 | 120114 |  | 131159554 | Alameda | Bay Area | Mission | South | Hayward | Yes | Pavement Data Group damaged a 3/4" steel gas service with a boring machine while doing telecommunications work. Valid 811 ticket. PG&E At Fault - Other Error - Construction Error | No | Gas Line | Yes | Boring Equipment | Telecommunications | Other Error | Yes | 2025040402737 | Dig-In to PG&E Underground | 3rd Party-Contractor | Pavement Data Group | Distribution Service |  | Yes | Other Error | Construction Error | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-24 | ¾” | 34 | 37 | N/A | 4 | Apr | 2025 |  | 927168 | No | Bay Area | Bay Area
23382 | x |  | x | x | 2025-04-24 | Apr | 4 | 2025 | 120121 |  | 131159696 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Mid-Cal Pipeline & Utilities damaged a 1/2" plastic gas service with a excavator while doing water main install. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation or Boring Equipment | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025032403059 | Dig-In to PG&E Underground | 3rd Party-Contractor | Mid-Cal Pipeline & Utilities | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-24 | ½” | 31 | 9 | N/A | 4 | Apr | 2025 |  | 4551138 | No | Central Valley | Central Valley
23383 | x | x | x | x | 2025-04-24 | Apr | 4 | 2025 | 120100 |  | 131158473 | Sonoma | Northern | Sonoma | North | Sebastopol | Yes | Mountain General Engineering damaged a 1" plastic gas service with a excavator while doing driveway work. Expired 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Excavator | Driveway Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No (expired) | 2025021200111 | Dig-In to PG&E Underground | 3rd Party-Contractor | Mountain General Engineering | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-24 | 1” | 36 | 3 | Expired USA Ticket | 4 | Apr | 2025 |  | 1080909 | No | North Coast | North Coast
23384 |  | x |  | x | 2025-04-25 | Apr | 4 | 2025 | OIS 2768882 |  |  | Marin | North Coast | Marin | North | Kentfield | No | Linscott Engineering damaged two 2/0 direct buried cables with a shovel while doing electric work. Valid 811 Ticket. PG&E At Fault. Locator Error - Mismark. Incorrect Information or Marks. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Shovel | Electric Work | Incorrect Information or Marks | Yes | 2025040101533 | Dig-In to PG&E Underground | 3rd Party-Contractor | Linscott Engineering | Electric |  | Yes | Locator Error - No Mark | Did Not Locate A to B and B to A | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-04-25 |  | 26 | 0 | N/A | 4 | Apr | 2025 | Bargaining Unit | 477476 | Yes | North Coast | North Coast
23385 | x | x | x | x | 2025-04-25 | Apr | 4 | 2025 | 120143 |  | 131163229 | Stanislaus | Central Valley | Yosemite | South | Turlock | Yes | Property Owner damaged a 1/2" plastic gas service with a auger while doing fence work. No 811 Ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-25 | ½” | 24 | 43 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  |  | No | Central Valley | Central Valley
23386 | x | x | x | x | 2025-04-25 | Apr | 4 | 2025 | 120155 |  | 131163814 | Santa Cruz | Central Coast | Central Coast | South | Soquel | Yes | KJ Woods Construction damaged a 1/2" plastic gas service with a shovel while doing water work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Water | Failed to Dig with Care | Yes | 2025031101242 | Dig-In to PG&E Underground | 3rd Party-Contractor | KJ Woods Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-25 | ½” | 24 | 19 | N/A | 4 | Apr | 2025 |  | 701797 | Yes | South Bay & Central Coast | South Bay & Central Coast
23387 | x | x | x | x | 2025-04-25 | Apr | 4 | 2025 | 120167 |  | 131164719 | Alameda | Bay Area | Oakland | North | Alameda | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service with a shovel while doing water work for an ADU. Expired 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Water | Failed to Dig with Care | No (expired) | 2025022500938 | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-25 | ½” | 18 | 21 | Expired USA Ticket | 4 | Apr | 2025 |  |  | Yes | Bay Area | Bay Area
23388 | x | x | x | x | 2025-04-25 | Apr | 4 | 2025 | 120174 |  | 131165058 | San Mateo | Central Coast | Colma | Central | Moss Beach | Yes | Homeowner damaged a 1/2" plastic gas service with a possible shovel, unconfirmed by investigator. The damage was done while doing tree removal. No 811 Ticket. | No | Gas Line | Yes | Shovel | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-04-25 | ½” | 24 | 45 | Knew about USA ticket requirement but chose not to call | 4 | Apr | 2025 |  |  | No | Bay Area | Bay Area
23389 | x | x |  | x | 2025-04-26 | Apr | 4 | 2025 | 120188 |  |  | Sacramento | Northern | Sacramento | North | Fair Oaks | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service with a shovel while doing electric work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | 2025040303239 | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-26 | ½” | 30 | 23 | N/A | 4 | Apr | 2025 |  |  | Yes | North Valley & Sierra | North Valley & Sierra
23390 | x | x | x | x | 2025-04-26 | Apr | 4 | 2025 | 120185 | 47207283 | 131166069 | Placer | Northern | Sierra | North | Rocklin | Yes | Ryan Lynch Construction damaged a 1/2" plastic gas service with a mini excavator while doing sewer work. Valid 811 Ticket. Failed to Delineate Work Site With Required Markings | No | Gas Line | Yes | Excavator | Sewer | Failed to Delineate Work Site With Required Markings | Yes | 2025022200225 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ryan Lynch Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-26 | ½” | 36 | 29 | N/A | 4 | Apr | 2025 |  | 1036581 | No | North Valley & Sierra | North Valley & Sierra
23391 | x | x | x | x | 2025-04-28 | Apr | 4 | 2025 | 120260 |  | 131173111 | Sutter | Northern | Sierra | North | Yuba City | Yes | USA Directional Bore an affiliate of Gigawave (RG3) damaged a 1/2" plastic gas service with a shovel while doing telecommunications work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Dig with Care | Yes | 2025042303926 | Dig-In to PG&E Underground | 3rd Party-Contractor | USA Directional Bore | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-28 | ½” | 30 | 31 | N/A | 4 | Apr | 2025 |  | 1069017 | Yes | North Valley & Sierra | North Valley & Sierra
23392 | x | x | x | x | 2025-04-28 | Apr | 4 | 2025 | 120253 |  | 131171420 | Monterey | Central Coast | Central Coast | South | Soledad | Yes | Zara Construction damaged a 4" plastic gas main with a auger while doing work to install a sign post. Valid 811 ticket. Excavated prior to legal excavation start date and time | No | Gas Line | No | Auger | Pole/Post Installation | Excavated prior to legal excavation start date and time | Yes | 2025042201861 | Dig-In to PG&E Underground | 3rd Party-Contractor | Zara Construction | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-28 | 4" | 1 | 0 | N/A | 4 | Apr | 2025 |  | 1063261 | No | South Bay & Central Coast | South Bay & Central Coast
23393 | x | x |  | x | 2025-04-28 | Apr | 4 | 2025 | 120227 |  |  | Alameda | Bay Area | Richmond | North | Albany | Yes | Groundworks California LLC damaged a 1/2" plastic gas service with a shovel while doing foundation work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Foundation Work | Failed to Dig with Care | Yes | 2025042200820 | Dig-In to PG&E Underground | 3rd Party-Contractor | Groundworks California LLC | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-28 | ½” | 18 | 41 | N/A | 4 | Apr | 2025 |  | 111604 | Yes | Bay Area | Bay Area
23394 | x | x | x | x | 2025-04-28 | Apr | 4 | 2025 | 120233 |  | 131169429 | Monterey | Central Coast | Central Coast | South | Carmel | Yes | Jon Cochran damaged a 1/2" plastic gas service with a shovel while doing foundation work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Foundation Work | Failed to Dig with Care | Yes | 2025040101217 | Dig-In to PG&E Underground | 3rd Party-Contractor | Jon Cochran | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-28 | ½” | 18 | 1 | N/A | 4 | Apr | 2025 |  | 753878 | Yes | South Bay & Central Coast | South Bay & Central Coast
23395 |  |  |  | x | 2025-04-28 | Apr | 4 | 2025 | 120258 |  |  | Alameda | Bay Area | Oakland | Central | Oakland | Yes | D21 Techs damaged a 1/2" plastic gas service line with hand tools while doing a fiber optic install. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Other Hand Tools | Telecommunications | Failed to Dig with Care | Yes | 2025011102859 | Dig-In to PG&E Underground | 3rd Party-Contractor | D21-Techs | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-28 | ½” |  |  | N/A | 4 | Apr | 2025 |  | 883141 | Yes | Bay Area | Bay Area
23396 | x |  | x | x | 2025-04-29 | Apr | 4 | 2025 | 120269 |  | 131173698 | Stanislaus | Central Valley | Yosemite | South | Turlock | Yes | Gutierrez Concrete damaged a 3/4" steel gas service with a cutting machine while doing landscape work. No 811 Ticket. | No | Gas Line | Yes | Cutting Machine | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Gutierrez Concrete | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-29 | ¾” | 18 | 48 | Other | 4 | Apr | 2025 |  |  | No | Central Valley | Central Valley
23397 | x | x | x | x | 2025-04-29 | Apr | 4 | 2025 | 120297 |  | 131179913 | Butte | Northern | North Valley | North | Oroville | Yes | PG&E Division Gas damaged a 1 1/4" Aldyl-A gas service line with a cutting machine while doing gas work. Valid 811 Ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Cutting Machine | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025010601751 | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Gas | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Blue | PG&E Division Gas |  |  | 1st Party Gas | Yes | 2025-04-29 | 1 ¼” | 26 | 4 | N/A | 4 | Apr | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23398 | x | x |  | x | 2025-04-29 | Apr | 4 | 2025 | 120285 |  |  | Yolo | Northern | North Bay | North | Woodland | Yes | NextLevel Inc. damaged a 1/2" plastic gas service with a trenching wheel while doing telecommunications work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Trencher | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025021900972 | Dig-In to PG&E Underground | 3rd Party-Contractor | Next Level | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-29 | ½” | 24 | 18 | N/A | 4 | Apr | 2025 |  | 907019 | No | North Coast | North Coast
23399 |  | x |  | x | 2025-04-30 | Apr | 4 | 2025 | OIS 2772419 |  |  | San Mateo | Central Coast | Colma | Central | Daly City | No | ARB Inc damaged a underground triplex electric line with a shovel while doing gas work. Expired 811 Ticket. Failed to Dig with Care. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Shovel | Gas | Failed to Dig with Care | Yes | 2024111301970 | Dig-In to PG&E Underground | 2nd Party-Contractor | ARB Inc | Electric |  | No | N/A |  | 2025 Q2 | Yes | Orange | PG&E GDGC |  |  | 2nd Party Electric | Yes | 2025-04-30 |  | 40 | 0 | N/A | 4 | Apr | 2025 |  | 194079 | Yes | Bay Area | Bay Area
23400 | x | x | x | x | 2025-04-30 | Apr | 4 | 2025 | 120322 |  | 131179003 | Contra Costa | Bay Area | Diablo | South | Lafayette | Yes | Cratus Inc. damaged a 1/2" plastic gas service with a excavator while doing sewer work. Valid 811 Ticket. PG&E At Fault. Records Error, Incorrect Facility Records / Maps. | No | Gas Line | Yes | Excavator | Sewer | Incorrect Facility Records / Maps | Yes | 2025040900697 | Dig-In to PG&E Underground | 3rd Party-Contractor | Cratus Inc | Distribution Service |  | Yes | Records Error | Mis Mapped Gas | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-30 | ½” | 30 | 36 | N/A | 4 | Apr | 2025 |  | 987888 | No | Bay Area | Bay Area
23401 | x | x | x | x | 2025-04-30 | Apr | 4 | 2025 | 120357 |  | 131180843 | Sacramento | Northern | Sacramento | North | Citrus Heights | Yes | Unlicensed Contractor damaged a 1" plastic gas service with a backhoe while doing sewer work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025041501759 | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-30 | 1” | 31 | 12 | N/A | 4 | Apr | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23402 | x | x | x | x | 2025-04-30 | Apr | 4 | 2025 | 120361 |  | 131180743 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | Unlicensed Contractor damaged a 1/2" plastic gas service with a post hole digger while doing fence work. No 811 Ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-04-30 | ½” | 24 | 54 | Excavator Did Not Believe a USA Ticket was Required | 4 | Apr | 2025 |  |  | Yes | South Bay & Central Coast | South Bay & Central Coast
23403 |  | x |  | x | 2025-04-14 | Apr | 4 | 2025 | OIS 45907350 |  |  | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | No | Unknown party damaged PG&E electric facilities. Damage was discovered by another contractor. Unknown excavation method and work type. No 811 ticket. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Unknown | Unknown | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unknown | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-04-14 |  |  | 0 | Other | 4 | Apr | 2025 |  |  | No | South Bay & Central Coast | South Bay & Central Coast
23404 |  | x |  | x | 2025-04-23 | Apr | 4 | 2025 | OIS 2767061 |  |  | Merced | Central Valley | Yosemite | South | Merced | No | Adame Communications Inc damaged a 21KV Primary electric line with a Drilling Equipment while doing Telecommunications work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Drilling Equipment | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025041601995 | Dig-In to PG&E Underground | 3rd Party-Contractor | Adame Communication Inc. | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-04-23 |  | 53 | 0 | N/A | 4 | Apr | 2025 |  | 1088089 | No | Central Valley | Central Valley
23405 | x | x |  | x | 2025-05-01 | May | 5 | 2025 | 120376 |  |  | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | West Valley Construction damaged a 1 1/4" steel gas service with a backhoe while doing water main install. Valid 811 Ticket. PG&E At Fault. Records Error - Incorrect Facility Records / Maps. | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Incorrect Facility Records / Maps | Yes | 2025021801753 | Dig-In to PG&E Underground | 3rd Party-Contractor | West Valley Construction | Distribution Service |  | Yes | Records Error | Failed to Escalate | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-01 | 1 ¼” | 29 | 14 | N/A | 5 | May | 2025 |  |  | No | South Bay & Central Coast | South Bay & Central Coast
23406 | x | x | x | x | 2025-05-01 | May | 5 | 2025 | 120382 |  | 131183925 | Santa Clara | Central Coast | De Anza | Central | Saratoga | Yes | Lewis & Tibbetts damaged a 3/4" steel gas service with a cutting machine while doing water main install. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Cutting Machine | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025021902014 | Dig-In to PG&E Underground | 3rd Party-Contractor | Lewis & Tibbits | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-01 | ¾” | 6 | 49 | N/A | 5 | May | 2025 |  | 851107 | No | South Bay & Central Coast | South Bay & Central Coast
23407 | x | x |  | x | 2025-05-01 | May | 5 | 2025 | 120365 |  |  | Placer | Northern | Sierra | North | Auburn | Yes | Procida Landscape damaged a 1" plastic gas service with an excavator while doing work for a drainpipe for drainage work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Excavator | Drainage Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025042200140 | Dig-In to PG&E Underground | 3rd Party-Contractor | Procida Landscape | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-01 | 1” | 18 | 1 | N/A | 5 | May | 2025 |  | 539595 | No | North Valley & Sierra | North Valley & Sierra
23408 | x | x | x | x | 2025-05-01 | May | 5 | 2025 | 120374 |  | 131183156 | Solano | North Coast | North Bay | North | Rio Vista | Yes | Pacific Coast Landscape damaged a 1" plastic gas service with a trencher while doing drainage work. No 811 Ticket. | No | Gas Line | Yes | Trencher | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Pacific Coast Landscape | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-01 | 1” | 12 | 1 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 5 | May | 2025 |  | 733949 | No | North Coast | North Coast
23409 | x | x | x | x | 2025-05-01 | May | 5 | 2025 | 120392 |  | 131184224 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Homeowner damaged a 1/2" plastic gas service with a post hiole digger while doing fence work. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-01 | ½” | 18 | 11 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  |  | Yes | Central Valley | Central Valley
23410 | x | x |  | x | 2025-05-01 | May | 5 | 2025 | 120385 |  |  | San Mateo | Central Coast | Belmont | Central | Redwood City | Yes | Casey Construction Inc. damaged a 1/2" plastic gas service with a backhoe while doing work to install a new water line for the city. Valid 811 Ticket. PG&E At Fault. Locator Error - Mismark. Incorrect Information or Marks | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Incorrect Information or Marks | Yes | 2025042400607 | Dig-In to PG&E Underground | 3rd Party-Contractor | Casey Construction Inc. | Distribution Service |  | Yes | Locator Error - Mismark | Failed to Follow Difficult to Locate Process | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-01 | ½” | 26 | 14 | N/A | 5 | May | 2025 | Bargaining Unit | 459579 | No | Bay Area | Bay Area
23411 | x | x | x | x | 2025-05-01 | May | 5 | 2025 | 120379 |  | 131183612 | Contra Costa | Bay Area | Mission | South | San Ramon | Yes | Hudson Excavation damaged a 2" plastic gas main with a excavator while doing site development work. Valid 811 Ticket. Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | No | Gas Line | Yes | Excavator | Site Development | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | 2025022001110 | Dig-In to PG&E Underground | 3rd Party-Contractor | Hudson Excavation | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-01 | 2” | 22 | 56 | N/A | 5 | May | 2025 |  | 599907 | No | Bay Area | Bay Area
23412 | x | x |  | x | 2025-05-02 | May | 5 | 2025 | 120417 |  | 131188643 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Whitlow Concrete damaged a 1/2" plastic gas service with a shovel while doing foundation work. No 811 Ticket. | No | Gas Line | Yes | Shovel | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Whitlow Concrete | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-02 | ½” | 29 | 17 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2025 |  | 948857 | Yes | South Bay & Central Coast | South Bay & Central Coast
23413 |  | x |  | x | 2025-05-02 | May | 5 | 2025 | OIS 2773349 |  |  | Marin | North Coast | Marin | North | San Rafael | No | Ongaro & Sons damaged a 1-1/0 AL Triplex electric service with a ground rod while doing electric work. No 811 Ticket. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Grounding Rod | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Ongaro & Sons Inc | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-05-02 | ½” |  | 0 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 229441 | Yes | North Coast | North Coast
23414 | x | x | x | x | 2025-05-02 | May | 5 | 2025 | 120406 |  | 131185539 | Marin | North Coast | Marin | North | San Rafael | Yes | Ongaro & Sons damaged a 1/2" plastic gas service with a ground rod while doing electric work. No 811 Ticket. | No | Gas Line | Yes | Grounding Rod | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Ongaro & Sons Inc | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-02 | ½” | 26 | 187 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 229441 | Yes | North Coast | North Coast
23415 | x | x | x | x | 2025-05-02 | May | 5 | 2025 | 120419 |  | 131188766 | San Mateo | Central Coast | Belmont | Central | Redwood City | Yes | Casey Construction damaged a 1/2" plastic gas service with a shovel while doing water work. Valid 811 Ticket. PG&E At Fault. Locator Error - Mismark. | No | Gas Line | Yes | Shovel | Water | Incorrect Information or Marks | Yes | 2025042400607 | Dig-In to PG&E Underground | 3rd Party-Contractor | Casey Construction Inc. | Distribution Service |  | Yes | Locator Error - Mismark | Failed to Follow Difficult to Locate Process | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-02 | ½” | 22 | 30 | N/A | 5 | May | 2025 | Bargaining Unit | 459579 | Yes | Bay Area | Bay Area
23416 | x | x | x | x | 2025-05-02 | May | 5 | 2025 | 120425 |  | 113118883 | San Mateo | Central Coast | Belmont | Central | Redwood City | Yes | Casey Construction damaged a 1/2" plastic gas service with a backhoe while doing water main install work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025042400607 | Dig-In to PG&E Underground | 3rd Party-Contractor | Casey Construction Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-02 | ½” | 22 | 11 | N/A | 5 | May | 2025 |  | 459579 | No | Bay Area | Bay Area
23417 |  | x | x | x | 2025-05-02 | May | 5 | 2025 | 120423 |  | 131189315 | Monterey | Central Coast | Central Coast | South | Salinas | Yes | Golz Construction damaged a 1/2" plastic gas service with a metal stake while doing work for an ADA ramp. Valid 811 Ticket. Excavated outside delineated area. | No | Gas Line | Yes | Stake | Curb/Sidewalk Work | Excavated outside delineated area | Yes | 2024042502276 | Dig-In to PG&E Underground | 3rd Party-Contractor | Golz Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-02 | ½” | 26 | 163 | N/A | 5 | May | 2025 |  | 946565 | Yes | South Bay & Central Coast | South Bay & Central Coast
23418 | x | x |  | x | 2025-05-02 | May | 5 | 2025 | 120437 |  |  | Sacramento | Northern | Sacramento | North | Carmichael | Yes | Unlicensed Contractor damaged a 3/4" steel gas servicie with a post hole digger while doing fencing for a trellis. No Gas Release. No 811 Ticket. | No | Gas Line | No | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-02 | ¾” | 24 | 0 | No Knowledge of USA Ticketing Process | 5 | May | 2025 |  |  | Yes | North Valley & Sierra | North Valley & Sierra
23419 | x | x |  | x | 2025-05-03 | May | 5 | 2025 | 120466 |  |  | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Homeowner damaged a 1/2" plastic gas service with a shovel while doing landscape work. No 811 Ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-03 | ½” | 16 | 8 | Believed they knew where underground utility was from previous knowledge | 5 | May | 2025 |  |  | Yes | North Coast | North Coast
23420 | x | x | x | x | 2025-05-03 | May | 5 | 2025 | 120465 |  | 131192721 | Placer | Northern | Sierra | North | Loomis | Yes | Tenant at this address damaged a 1/2" plastic gas service with a excavator while doing electric work. No 811 ticket. | No | Gas Line | Yes | Excavator | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-03 | ½” | 36 | 13 | Believed they knew where underground utility was from previous knowledge | 5 | May | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23421 | x | x | x | x | 2025-05-04 | May | 5 | 2025 | 120479 |  | 131192950 | Madera | Central Valley | Yosemite | South | Madera | Yes | Homeowner damaged a 1/2" plastic gas service with a post hole digger while doing fence work. No 811 Ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-04 | ½” | 24 | 19 | No Knowledge of USA Ticketing Process | 5 | May | 2025 |  |  | Yes | Central Valley | Central Valley
23422 | x | x | x | x | 2025-05-05 | May | 5 | 2025 | 120498 |  | 131195167 | Solano | Bay Area | North Bay | North | Vallejo | Yes | WC Maloney damaged a 1" plastic gas service while blading/lot grading with an excavator. No 811 Ticket. | No | Gas Line | Yes | Excavator | Blading/Lot Grading | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | WC Maloney Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-05 | 1” | 2 | 12 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 718243 | No | North Coast | North Coast
23423 | x | x | x | x | 2025-05-05 | May | 5 | 2025 | 120510 |  | 131195129 | Mendocino | Northern | Sonoma | North | Ukiah | Yes | Homeowner damaged a 1/2" plastic gas service with a excavator while doing water leak work. No 811 Ticket. | No | Gas Line | Yes | Excavator | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-05 | ½” | 50 | 27 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  |  | No | North Coast | North Coast
23424 |  | x |  | x | 2025-05-05 | May | 5 | 2025 | 120506 |  | 131196622 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Unlicensed contractor damaged a 1/2" plastic gas service with post hole digger while doing fence work. No 811 Ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-05 | ½” | 25 | 47 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  |  | Yes | South Bay & Central Coast | South Bay & Central Coast
23425 | x | x | x | x | 2025-05-05 | May | 5 | 2025 | 120499 |  | 131194227 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Above All Plumbing damaged a 1/2" plastic gas service with a shovel while doing work to install new plumbing line. No 811 Ticket. | No | Gas Line | Yes | Shovel | Other | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Above All Plumbing Pros | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-05 | ½” | 32 | 31 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 1053057 | Yes | Central Valley | Central Valley
23426 | x | x | x | x | 2025-05-05 | May | 5 | 2025 | 120526 |  | 131196091 | Sonoma | Northern | Sonoma | North | Sonoma | Yes | RDZ Construction damaged 1" plastic gas service line with a shovel while doing a building addition. No 811 ticket. | No | Gas Line | Yes | Shovel | Building Construction | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | RDZ Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-05 | 1” | 28 | 24 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 5 | May | 2025 |  | 1087514 | Yes | North Coast | North Coast
23427 | x | x | x | x | 2025-05-05 | May | 5 | 2025 | 120537 |  | 131197169 | Marin | North Coast | Marin | North | Mill Valley | Yes | Unlicensed Contractor damaged a 1/2" plastic inserted into a 3/4" steel service with a shovel while doing post install for a retaining wall. No 811 ticket. | No | Gas Line | Yes | Shovel | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-05 | ½” | 12 | 51 | No Knowledge of USA Ticketing Process | 5 | May | 2025 |  |  | Yes | North Coast | North Coast
23428 |  | x |  | x | 2025-05-05 | May | 5 | 2025 | OIS 2775538 |  |  | El Dorado | Northern | Sierra | North | Shingle Springs | No | Unlicensed Contractor damaged a 1 – 4/0A Triplex electric service with a skid steer while doing blading/lot grading. No 811 Ticket. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Skid Steer | Blading/Lot Grading | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-05-05 |  | 6 | 0 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23429 | x | x | x | x | 2025-05-06 | May | 5 | 2025 | 120583 |  | 131201519 | Alameda | Bay Area | Oakland | Central | Alameda | Yes | Unlicensed contractor damaged a 1/2" plastic gas service with a shovel while digging a trench to install a rodent screen. No 811 Ticket. | No | Gas Line | Yes | Shovel | Other | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-06 | ½” | 8 | 40 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2025 |  |  | Yes | Bay Area | Bay Area
23430 |  | x |  | x | 2025-05-06 | May | 5 | 2025 | OIS 2777186 |  |  | Contra Costa | Bay Area | Richmond | Central | Pinole | No | KJ Woods Construction Inc.damafged a 4" conduit and primary electric line wityh a unknown type of tool while doing sewer work type of work. Contract City Inspector observed damage to a PG&E facility within an open trench excavated by KJ Woods Construction. Inspector called to notify PG&E of the damaged facility. City Inspector advised the damaged may have occurred on 11/26/2024 when the contractor exposed/ potholed the area. Based on the location being excavated by KJ Woods Construction, and no other companies working in the area of damage, it’s more likely than not the damage was caused by KJ Woods Construction. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Unknown | Sewer | Inadequate Excavation Practices | Yes | 2024111501120 | Dig-In to PG&E Underground | 3rd Party-Contractor | KJ Woods Construction | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-05-06 |  | 52 | 0 | N/A | 5 | May | 2025 |  |  | No | Bay Area | Bay Area
23431 | x | x | x | x | 2025-05-06 | May | 5 | 2025 | 120560 |  | 131199390 | Yuba | Northern | Sierra | North | Marysville | Yes | Aerco Pacific damaged a 2" plastic gas service with a grader/scraper while doing Blading/Lot Grading. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Grader/Scraper | Blading/Lot Grading | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 20244112500994 | Dig-In to PG&E Underground | 3rd Party-Contractor | Aerco Pacific | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-06 | 2” | 8 | 3 | N/A | 5 | May | 2025 |  | 166242 | No | North Valley & Sierra | North Valley & Sierra
23432 | x | x | x | x | 2025-05-06 | May | 5 | 2025 | 120587 |  | 131204052 | Alameda | Bay Area | Richmond | Central | Berkeley | Yes | JC Construction damaged a 1/2" plastic gas service with a excavator while doing drainage work. Valid 811 Ticket. PG&E At Fault. Wire Error - Locating Wire Missing or Broken - Construction Error | No | Gas Line | Yes | Excavator | Drainage Work | Locating Wire Missing or Broken | Yes | 2025050503172 | Dig-In to PG&E Underground | 3rd Party-Contractor | JC Construction | Distribution Service |  | Yes | Wire Error | Construction Error | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-06 | ½” | 12 | 33 | N/A | 5 | May | 2025 |  | 110747 | No | Bay Area | Bay Area
23433 | x | x | x | x | 2025-05-06 | May | 5 | 2025 | 120565 |  | 131200140 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Flowright Plumbing damaged a 1" aldyl-A gas service with a excavator while doing water work. Expired 811 Ticket. Marks were no longer visible so root cause is no 811 ticket | No | Gas Line | Yes | Excavator | Electric Work | No USA Ticket | No (expired) | 2024011802505 | Dig-In to PG&E Underground | 3rd Party-Contractor | Flowright Plumbing | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-06 | 1” | 12 | 26 | Expired USA Ticket | 5 | May | 2025 |  | 842999 | No | North Coast | North Coast
23434 | x | x | x | x | 2025-05-07 | May | 5 | 2025 | 120626 |  | 131208623 | Butte | Northern | North Valley | North | Paradise | Yes | Desilva Gates damaged a 1" plastic gas service with a pick while doing road work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Pickaxe | Road Work | Failed to Dig with Care | Yes | 2025040702403 | Dig-In to PG&E Underground | 3rd Party-Contractor | De Silva Gates Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-07 | 1” | 20 | 30 | N/A | 5 | May | 2025 |  |  | Yes | North Valley & Sierra | North Valley & Sierra
23435 | x | x | x | x | 2025-05-07 | May | 5 | 2025 | 120621 |  | 131207996 | Contra Costa | Bay Area | Diablo | South | Concord | Yes | KJ Woods Construction Inc. damaged a 1" plastic gas service with a excavator while doing water work. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2024101402536 | Dig-In to PG&E Underground | 3rd Party-Contractor | KJ Woods Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-07 | 1” | 36 | 1 | N/A | 5 | May | 2025 |  | 701797 | No | Bay Area | Bay Area
23436 | x | x | x | x | 2025-05-07 | May | 5 | 2025 | 120634 |  | 131209093 | Marin | North Coast | Marin | North | Mill Valley | Yes | Unlicensed Contractor damaged a ½" Aldyl-a gas service with a shovel while doing landscape work. Valid 811 Ticket. PG&E at-fault - Other Error | No | Gas Line | Yes | Shovel | Landscaping | Other Error | Yes | 2025041602291 | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | Yes | Other Error | Other | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-07 | ½” | 28 | 16 | N/A | 5 | May | 2025 |  |  | Yes | North Coast | North Coast
23437 | x | x | x | x | 2025-05-07 | May | 5 | 2025 | 120636 |  | 131209320 | Santa Clara | Central Coast | De Anza | Central | Los Altos | Yes | 2911 Contractors damaged a 1/2" plastic gas service with a shovel while doing multiple utilities install. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Other | Failed to Dig with Care | Yes | 2025042301439 | Dig-In to PG&E Underground | 3rd Party-Contractor | 2911 Contractors | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-07 | ½” | 20 | 14 | N/A | 5 | May | 2025 |  | 1066799 | Yes | South Bay & Central Coast | South Bay & Central Coast
23438 | x | x | x | x | 2025-05-07 | May | 5 | 2025 | 120599 | 47212930 | 131207234 | Fresno | Central Valley | Fresno | South | Fresno | Yes | City of Fresno damaged a 2" plastic gas main with a backhoe while doing waiter main tie in. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025042200585 | Dig-In to PG&E Underground | 3rd Party-Government Entity | City of Fresno | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2025-05-07 | 2” | 52 | 76 | N/A | 5 | May | 2025 |  |  | No | Central Valley | Central Valley
23439 |  | x |  | x | 2025-05-08 | May | 5 | 2025 | OIS 2778898 |  |  | Santa Clara | Central Coast | San Jose | Central | Gilroy | No | MGE Underground damaged secondary electric with an excavator while doing electric work. Valid 811 ticket. PG&E at-fault - Locator error - Mismark. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Excavator | Electric Work | Incorrect Information or Marks | Yes | 2025050103100 | Dig-In to PG&E Underground | 2nd Party-Contractor | MGE Underground | Electric |  | Yes | Locator Error - Mismark | Failed to perform a 360 Sweep | 2025 Q2 | Yes | Orange | PG&E Division Electric |  |  | 2nd Party Electric | Yes | 2025-05-08 |  |  | 0 | N/A | 5 | May | 2025 | Bargaining Unit | 765025 | No | South Bay & Central Coast | South Bay & Central Coast
23440 | x | x | x | x | 2025-05-08 | May | 5 | 2025 | 120668 |  | 131212635 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | P. L. Construction damaged a 1 1/4" plastic gas mainw ith a excavator while doing sewer work. No 811 Ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | P. L. Construction | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-08 | 1 ¼” | 30 | 58 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 1080157 | No | Central Valley | Central Valley
23441 | x | x |  | x | 2025-05-08 | May | 5 | 2025 | 120685 |  | 131213593 | Butte | Northern | North Valley | North | Paradise | Yes | American Dream Construction damaged a 1 1/4" plastic gas main with a excavator while doing water line install. No 811 Ticket. | No | Gas Line | Yes | Excavator | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | American Home Builders | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-08 | 1 ¼” | 26 | 7 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23442 |  | x |  | x | 2025-05-08 | May | 5 | 2025 | 120672 |  |  | Santa Clara | Central Coast | De Anza | Central | Los Altos | Yes | Unique Concrete Creations damaged a tracer wire with a shovel while doing landscaping work. Valid 811 ticket. Excavated prior to legal start time | Yes | Gas Line | No | Shovel | Drainage Work | Excavated prior to legal excavation start date and time | Yes | 2025050503112 | Dig-In to PG&E Underground | 3rd Party-Contractor | Unique Concrete Creations | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-08 | 1” | 18 | 0 | N/A | 5 | May | 2025 |  | 779127 | Yes | South Bay & Central Coast | South Bay & Central Coast
23443 | x | x | x | x | 2025-05-08 | May | 5 | 2025 | 120689 |  | 131213865 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | American Home Energy Savers damaged a 1/2" aldyl-a gas service with a pick while doing electric work. Expired 811 Ticket. PG&E At Fault - Other Error - Construction Error | No | Gas Line | Yes | Pickaxe | Electric Work | Other Error | No (expired) | 2025040902137 | Dig-In to PG&E Underground | 3rd Party-Contractor | American Home Energy Savers | Distribution Service |  | Yes | Other Error | Construction Error | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-08 | ½” | 24 | 27 | Expired USA Ticket | 5 | May | 2025 |  | 1023076 | Yes | North Valley & Sierra | North Valley & Sierra
23444 | x | x | x | x | 2025-05-08 | May | 5 | 2025 | 120653 |  |  | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Copper Creek Landscaping damaged a 1 1/4" plastic gas service with a mini excavator while doing landscape water services. No 811 Ticket. | No | Gas Line | Yes | Excavator | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Copper Creek Landscaping | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-08 | 1 ¼” | 33 | 11 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 5 | May | 2025 |  | 663021 | No | North Valley & Sierra | North Valley & Sierra
23445 | x | x |  | x | 2025-05-08 | May | 5 | 2025 | 120674 |  |  | Alameda | Bay Area | Oakland | Central | Oakland | Yes | EF Gomez Cement Contractor damaged a 1" plastic gas service with a stake while doing curb/sidewalk work. Valid 811 Ticket. Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | No | Gas Line | Yes | Stake | Curb/Sidewalk Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | 2025041702916 | Dig-In to PG&E Underground | 3rd Party-Contractor | EF Gomez Cement Contractor Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-08 | 1” | 14 | 50 | N/A | 5 | May | 2025 |  | 678835 | Yes | Bay Area | Bay Area
23446 | x | x | x | x | 2025-05-08 | May | 5 | 2025 | 120662 |  | 131212461 | Sonoma | Northern | Sonoma | North | Sebastopol | Yes | Blue Hammer Builders damaged a 3/4" steel gas service with a jackhammer while doing fence work. NO 811 Ticket. | No | Gas Line | Yes | Jackhammer | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Blue Hammer Builders | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-06 | ¾” | 24 | 29 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 1051105 | No | North Coast | North Coast
23447 | x | x |  | x | 2025-05-08 | May | 5 | 2025 | 120666 |  |  | Sacramento | Northern | Sacramento | North | Galt | Yes | R&R Pacific Construction damaged a locating wire with a shovel while doing water main install. No Gas Release. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | No | Shovel | Water | Failed to Dig with Care | Yes | 2024102400466 | Dig-In to PG&E Underground | 3rd Party-Contractor | R&R Pacific Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-08 | 4" | 37 | 0 | N/A | 5 | May | 2025 |  | 99192 | Yes | North Valley & Sierra | North Valley & Sierra
23448 | x | x | x | x | 2025-05-09 | May | 5 | 2025 | 120712 |  | 131218755 | Sonoma | Northern | Sonoma | North | Sebastopol | Yes | Northwest General Engineering damaged a 2" plastic gas service line with an excavator while doing site development. Valid 811 ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Site Development | Incorrect Facility Records / Maps | Yes | 2025042101749 | Dig-In to PG&E Underground | 3rd Party-Contractor | Northwest General Engineering | Distribution Service |  | Yes | Records Error | Incorrect GSR | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-09 | 2” | 40 | 98 | N/A | 5 | May | 2025 |  | 781913 | No | North Coast | North Coast
23449 | x | x |  | x | 2025-05-09 | May | 5 | 2025 | 120726 |  |  | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Andrew Turner Construction damaged a 1/2" gas service aldyl-a with a shovel while doing sewer work. No 811 Ticket. | Yes | Gas Line | No | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Andrew Turner Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-09 | ½” | 9 | 46 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 5 | May | 2025 |  | 934493 | Yes | North Valley & Sierra | North Valley & Sierra
23450 | x | x | x | x | 2025-05-09 | May | 5 | 2025 | 120711 |  | 131218800 | Sacramento | Northern | Sacramento | North | Rancho Cordova | Yes | Aspire Communications damaged a 3/4" steel gas service with a micro trencher while doing fiber optic telecommunication conduit install. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Trencher | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025041400222 | Dig-In to PG&E Underground | 3rd Party-Contractor | Aspire Communications Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-09 | ¾” | 7 | 42 | N/A | 5 | May | 2025 |  | 1113518 | No | North Valley & Sierra | North Valley & Sierra
23451 | x | x | x | x | 2025-05-10 | May | 5 | 2025 | 120760 |  | 131230912 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Homeowner damaged a 1" plastic gas main with a shovel while doing sewer work. No 811 Ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-10 | 2” | 29 | 119 | No Knowledge of USA Ticketing Process | 5 | May | 2025 |  |  | Yes | Central Valley | Central Valley
23452 | x | x | x | x | 2025-05-12 | May | 5 | 2025 | 120804 |  | 131235739 | San Mateo | Central Coast | Belmont | Central | San Mateo | Yes | McKim Corporation damaged a 1/2" plastic gass ervice with a excavator while doing curb/sidewalk work. 811 Ticket was closed out for improper delineations. Excavated Prior to Receiving a Positive Response From All Utilities | No | Gas Line | Yes | Excavator | Curb/Sidewalk Work | Excavated Prior to Receiving a Positive Response From All Utilities | Yes | 2025050700391 | Dig-In to PG&E Underground | 3rd Party-Contractor | McKim Corporation | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-12 | ½” | 18 | 74 | N/A | 5 | May | 2025 |  | 976269 | No | Bay Area | Bay Area
23453 | x | x | x | x | 2025-05-12 | May | 5 | 2025 | 120807 |  | 131236410 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Precision Engineering Inc damaged a 1/2" inserted into a ¾" steel gas service with a excavator while doing road work. Valid 811 Ticket. Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | No | Gas Line | Yes | Excavator | Road Work | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | Yes | 2025012001628 | Dig-In to PG&E Underground | 3rd Party-Contractor | Precision Engineering INC | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-12 | ½” | 12 | 55 | N/A | 5 | May | 2025 |  | 880266 | No | Bay Area | Bay Area
23454 | x | x | x | x | 2025-05-12 | May | 5 | 2025 | 120791 |  | 131235133 | Marin | North Coast | Marin | North | Tiburon | Yes | A-1 Gates & Access damaged a 1/2" plastic gas service line with a shovel while installing a post. No 811 Ticket. | No | Gas Line | Yes | Shovel | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | A-1 Gates & Access | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-12 | ½” | 36 | 21 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2025 |  | 1036015 | Yes | North Coast | North Coast
23455 | x | x | x | x | 2025-05-12 | May | 5 | 2025 | 120814 |  | 131236726 | San Mateo | Central Coast | Belmont | Central | Belmont | Yes | Fioptix Inc damaged a 1/2" plastic gas service with a shovel while doing telecommunication work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Dig with Care | Yes | 2025050800442 | Dig-In to PG&E Underground | 3rd Party-Contractor | FIOptix Inc | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-12 | ½” | 30 | 74 | N/A | 5 | May | 2025 |  | 1128247 | Yes | Bay Area | Bay Area
23456 | x | x | x | x | 2025-05-12 | May | 5 | 2025 | 120784 |  | 131234165 | San Mateo | Central Coast | Belmont | Central | Belmont | Yes | Daniel Cifuentes Construction damaged a 1/2" plastic gas service with a shovel while doing foundation work. No 811 ticket. | No | Gas Line | Yes | Shovel | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Daniel Cifuentes Construction, Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-12 | ½” | 30 | 25 | Believed they knew where underground utility was from previous knowledge | 5 | May | 2025 |  | 1063790 | Yes | Bay Area | Bay Area
23457 | x | x | x | x | 2025-05-12 | May | 5 | 2025 | 120799 |  | 131235880 | San Mateo | Central Coast | Belmont | Central | West Menlo Park | Yes | TechCon Monument Construction damaged a 1" plastic gas service with a shovel while doing a water leak repair. Valid 811 Ticket. Failed to Dig with Care | Yes | Gas Line | No | Shovel | Water | Failed to Dig with Care | Yes | 2025050601011 | Dig-In to PG&E Underground | 3rd Party-Contractor | TechCon Monument Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-12 | 1” | 48 | 40 | N/A | 5 | May | 2025 |  |  | Yes | Bay Area | Bay Area
23458 | x | x | x | x | 2025-05-12 | May | 5 | 2025 | 120805 |  | 131235854 | Contra Costa | Bay Area | Diablo | South | Antioch | Yes | ALB Inc. damaged a 1/2" plastic gas service with a bulldozer while doing blading/lot grading. No Valid 811 Ticket. Excavated Prior to Receiving a Positive Response From All Utilities | No | Gas Line | Yes | Bulldozer | Blading/Lot Grading | Excavated Prior to Receiving a Positive Response From All Utilities | Yes | 2025050901647 | Dig-In to PG&E Underground | 3rd Party-Contractor | ALB Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-12 | ½” | 24 | 20 | N/A | 5 | May | 2025 |  | 622062 | No | Bay Area | Bay Area
23459 |  | x |  | x | 2025-05-12 | May | 5 | 2025 | 120794 |  |  | Sacramento | Northern | Sacramento | North | Citrus Heights | Yes | DIRT Movers Inc damaged a locating wire with an excavator while doing a sewer repair. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | No | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2024042902483 | Dig-In to PG&E Underground | 3rd Party-Contractor | Dirt Movers Inc | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-12 | 4" | 24 | 0 | N/A | 5 | May | 2025 |  | 612990 | No | North Valley & Sierra | North Valley & Sierra
23460 | x | x |  | x | 2025-05-12 | May | 5 | 2025 | 120801 |  |  | Alameda | Bay Area | Oakland | Central | Oakland | Yes | Pinnacle Power Services damaged 6 anode wires with an excavator while doing conduit installations. Valid 811 ticket. PG&E at-fault - Locator error - No Mark | No | Gas Line | No | Excavator | Electric Work | Facility was not Located or Marked | Yes | 2025041403437 | Dig-In to PG&E Underground | 2nd Party-Contractor | Pinnacle Power Services Inc | Distribution Service |  | Yes | Locator Error - Mismark | Training Issue | 2025 Q2 | Yes | Orange | PG&E GC Electric |  |  | 2nd Party Gas | Yes | 2025-05-12 | 4" | 38 | 0 | N/A | 5 | May | 2025 | Bargaining Unit | 983996 | No | Bay Area | Bay Area
23461 | x | x | x | x | 2025-05-13 | May | 5 | 2025 | 120858 |  | 131240153 | Kern | Central Valley | Kern | South | Bakersfield | Yes | LDD Construction damaged a 1" plastic gas service with a post hole digger while doing fence work. No 811 Ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | LDD Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-13 | 1” | 23 | 14 | Didn’t think they were digging deep enough to damage an underground utility | 5 | May | 2025 |  | 756786 | Yes | Central Valley | Central Valley
23462 | x | x | x | x | 2025-05-13 | May | 5 | 2025 | 120845 |  | 131239835 | Marin | North Coast | Marin | North | San Rafael | Yes | Leo’s Tree Service damaged a 3/4" steel gas service with a jackhammer with a chipping bit while doing work for a fence and gate. No 811 Ticket. | No | Gas Line | Yes | Jackhammer | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Leo’s Tree Service | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-13 | ¾” | 10 | 35 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 1044849 | No | North Coast | North Coast
23463 |  | x |  | x | 2025-05-13 | May | 5 | 2025 | OIS 2782605 |  |  | Marin | North Coast | Marin | North | San Rafael | No | Ghilotti Brothers Inc damaged two 5" conduits with a excavator while doing roadwork. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Excavator | Road Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025032801439 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ghilotti Brothers | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-05-09 |  | 30 | 0 | N/A | 5 | May | 2025 |  | 1129410 | No | North Coast | North Coast
23464 | x | x | x | x | 2025-05-13 | May | 5 | 2025 | 120828 |  | 131240084 | San Joaquin | Central Valley | Yosemite | South | Escalon | Yes | 1st Party-PG&E M&C damaged a 2" gas main with a probing tool while doing a leak repair for GDGC. Valid 811 Ticket. Failed to Dig with Care. | No | Gas Line | Yes | Probing Tool | Gas | Failed to Dig with Care | Yes | 2025051300098 | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Gas | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Blue | PG&E Division Gas |  |  | 1st Party Gas | Yes | 2025-05-13 | 2” | 30 | 48 | N/A | 5 | May | 2025 |  |  | Yes | Central Valley | Central Valley
23465 |  | x |  | x | 2025-05-13 | May | 5 | 2025 | OIS 2781888 |  |  | Yolo | Northern | North Bay | North | West Sacramento | No | Advance Telecom damaged 3" conduit and two strand aluminum primary cables with a boring machine while installing new telecommunications facilities. Valid 811 ticket. PG&E at-fault - Locator Error - No Mark. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Boring Equipment | Telecommunications | Facility was not Located or Marked | Yes | 2025042203689 | Dig-In to PG&E Underground | 3rd Party-Contractor | Advance Telecom | Electric |  | Yes | Locator Error - No Mark | Did not mark locatable facility | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-05-13 |  | 40 | 0 | N/A | 5 | May | 2025 | Bargaining Unit | 1031556 | No | North Coast | North Coast
23466 | x | x | x | x | 2025-05-14 | May | 5 | 2025 | 120927 |  | 131246455 | Colusa | Northern | Sacramento | North | Colusa | Yes | Homeowner damaged a 1/2" plastic gas service with a shovel while dong sewer work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | 2025050901999 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-14 | ½” | 20 | 6 | N/A | 5 | May | 2025 |  |  | Yes | North Valley & Sierra | North Valley & Sierra
23467 | x | x |  | x | 2025-05-14 | May | 5 | 2025 | 120891 |  |  | Alameda | Bay Area | Oakland | Central | Oakland | Yes | Miller Pipeline damaged a 1/2" Plastic inserted into a 1 1/4" Steel Stub with a excavator while doing fauture gas main work. Valid 811 Ticket. PG&E At Fault. Records Error, Incorrect Facility Records / Maps. | No | Gas Line | Yes | Excavator | Gas | Incorrect Facility Records / Maps | Yes | 2025031801588 | Dig-In to PG&E Underground | 2nd Party-Contractor | Miller Pipeline | Distribution Service |  | Yes | Records Error | Unmapped Stub | 2025 Q2 | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2025-05-14 | ½” | 39 | 71 | N/A | 5 | May | 2025 |  | 978749 | No | Bay Area | Bay Area
23468 | x | x |  | x | 2025-05-14 | May | 5 | 2025 | 120909 |  |  | Alameda | Bay Area | Mission | South | Fremont | Yes | Alameda County Water Department damaged a 3/4" steel gas service with a sawzall while doing water leak repair. Valid 811 Ticket. Excavated outside delineated area | No | Gas Line | Yes | Cutting Machine | Water | Excavated outside delineated area | Yes | 2025051303272 | Dig-In to PG&E Underground | 3rd Party-Government Entity | Alameda County Water District | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2025-05-14 | ¾” | 24 | 28 | N/A | 5 | May | 2025 |  |  | No | Bay Area | Bay Area
23469 | x | x |  | x | 2025-05-14 | May | 5 | 2025 | 120896 |  |  | Sacramento | Northern | Sacramento | North | North Highlands | Yes | Pro Custom Concrete damaged a 2" steel gas service with a M2 with a excavator while doing road work. Expired 811 Ticket. Marks were still visible so primary cause of incidents is failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Road Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No (expired) | 2024102900774 | Dig-In to PG&E Underground | 3rd Party-Contractor | Pro Custom Concrete | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-14 | 2” | 10 | 35 | Expired USA Ticket | 5 | May | 2025 |  | 995813 | No | North Valley & Sierra | North Valley & Sierra
23470 |  | x |  | x | 2025-05-15 | May | 5 | 2025 | OIS 2784493 |  |  | Contra Costa | Bay Area | Diablo | South | Bay Point | No | TAK Broadband Ca LLC damaged 6" conduit with an excavator while installing a water main. Valid 811 ticket. Failed to expose facility with hand tools. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025040402410 | Dig-In to PG&E Underground | 3rd Party-Contractor | TAK Broadband CA LLC | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-05-15 |  | 83 | 0 | N/A | 5 | May | 2025 |  | 1042947 | No | Bay Area | Bay Area
23471 | x | x | x | x | 2025-05-15 | May | 5 | 2025 | 120937 |  | 131248066 | Solano | Bay Area | North Bay | North | Vallejo | Yes | Ghilotti Construction damaged a 1" plastic gas service with a metal probing rod while doing roadway improvement work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Probing Tool | Road Work | Failed to Dig with Care | Yes | 2025012302853 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ghilotti Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-15 | 1” | 30 | 37 | N/A | 5 | May | 2025 |  | 644515 | Yes | North Coast | North Coast
23472 |  | x |  | x | 2025-05-15 | May | 5 | 2025 | 120946 |  |  | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Gil Construction & Associates, Inc. damaged 1/2" plastic gas service line with a shovel while doing electric work. Expired 811 ticket. Marks were still visible so primary cause of incident is failed to dig with care | Yes | Gas Line | No | Shovel | Electric Work | Failed to Dig with Care | Yes | 2025030701718 | Dig-In to PG&E Underground | 3rd Party-Contractor | Gil Construction & Associates, Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-15 | ½” | 27 | 0 | N/A | 5 | May | 2025 |  |  | Yes | Bay Area | Bay Area
23473 |  | x |  | x | 2025-05-15 | May | 5 | 2025 | OIS 2784534 |  |  | Santa Barbara | Central Coast | Los Padres | South | Santa Maria | No | J.F. Will Company damaged primary electric with an excavator while installing a sewer lateral. Expired 811 ticket. Primary cause of incident is failed to maintain marks. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Excavator | Sewer | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | No (expired) | A250580758 | Dig-In to PG&E Underground | 3rd Party-Contractor | J.F. Will Company | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-05-15 |  |  | 0 | Expired USA Ticket | 5 | May | 2025 |  |  | No | South Bay & Central Coast | South Bay & Central Coast
23474 | x | x |  | x | 2025-05-15 | May | 5 | 2025 | 120942 |  |  | Contra Costa | Bay Area | Diablo | South | Walnut Creek | Yes | Roto Rooter damaged a 1/2" plastic gas service with a exacavator while doing repair the sewer lateral to the residence. Valid 811 Ticket. Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025042301990 | Dig-In to PG&E Underground | 3rd Party-Contractor | Roto Rooter Services Company | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-15 | ½” | 36 | 4 | N/A | 5 | May | 2025 |  | 806952 | No | Bay Area | Bay Area
23475 | x | x | x | x | 2025-05-15 | May | 5 | 2025 | 120957 |  | 131249693 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Homeowner damaged 1" plastic gas service line with a post-hole digger while installing bollards. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-15 | 1” | 24 | 10 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2025 |  |  | Yes | Central Valley | Central Valley
23476 | x | x | x | x | 2025-05-15 | May | 5 | 2025 | 120938 |  | 131248560 | Shasta | Northern | North Valley | North | Anderson | Yes | Cal Electro damaged a 1/2" plastic gas service with a backhoe while doing work to install a new sewer lateral. No 811 Ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Cal Electro Inc | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-15 | ½” | 32 | 27 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2025 |  | 390480 | No | North Valley & Sierra | North Valley & Sierra
23477 | x | x | x | x | 2025-05-15 | May | 5 | 2025 | 120960 |  | 131249735 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | C & C Contracting damaged 1" plastic gas service line with an excavator while replacing a septic systems leach lines. No 811 ticket. | No | Gas Line | Yes | Excavator | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | C & C Contracting | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-15 | 1” | 36 | 15 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  |  | No | North Coast | North Coast
23478 | x | x |  | x | 2025-05-15 | May | 5 | 2025 | 120958 |  |  | San Mateo | Central Coast | Colma | Central | San Bruno | Yes | Makoni Construction damaged a 1" plastic gas service with a shovel while doing gas work. Valid 811 Ticket. Failed to Dig with Care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | 2025060601649 | Dig-In to PG&E Underground | 3rd Party-Contractor | Makoni Construction, Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-15 | 1” | 30 | 20 | N/A | 5 | May | 2025 |  | 901550 | Yes | Bay Area | Bay Area
23479 |  | x |  | x | 2025-05-15 | May | 5 | 2025 | OIS 2784472 |  |  | Alameda | Bay Area | Mission | South | Newark | No | Homeowner damaged primary electric with a powered augur while digging footings for a foundation. Valid 811 ticket. PG&E at-fault - Locator Error - No Mark. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Auger | Foundation Work | Facility was not Located or Marked | Yes | 2025050502133 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Electric |  | Yes | Locator Error - No Mark | Training Issue | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Electric | Yes | 2025-05-15 |  | 26 | 0 | N/A | 5 | May | 2025 | Bargaining Unit |  | No | Bay Area | Bay Area
23480 | x | x |  | x | 2025-05-15 | May | 5 | 2025 | 120945 |  |  | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | Veteran Pipeline Construction damaged a 3/4" steel gas service line with boring equipment while installing electric lines for PG&E. Valid 811 ticket. Failed to dig with care. | No | Gas Line | No | Boring Equipment | Electric Work | Failed to Dig with Care | Yes | 2025050700398 | Dig-In to PG&E Underground | 2nd Party-Contractor | Veteran Pipeline Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Orange | PG&E Division Electric |  |  | 2nd Party Gas | Yes | 2025-05-15 | ¾” |  | 0 | N/A | 5 | May | 2025 |  | 953124 | No | South Bay & Central Coast | South Bay & Central Coast
23481 | x | x | x | x | 2025-05-16 | May | 5 | 2025 | 120982 |  | 131252629 | Sacramento | Northern | Sacramento | North | Folsom | Yes | Next Level Home Performance damaged 1" plastic gas service line with a mini-excavator while doing a gas meter relocation. No 811 ticket. | No | Gas Line | Yes | Excavator | Gas | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Next Level Home Performance | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-16 | 1” | 24 | 38 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2025 |  | 775687 | No | North Valley & Sierra | North Valley & Sierra
23482 | x | x | x | x | 2025-05-16 | May | 5 | 2025 | 120977 |  | 131252072 | Fresno | Central Valley | Yosemite | South | Firebaugh | Yes | United Pavement Maintenance damaged 1" plastic gas service line with an excavator while installing a new sewer line. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025033102847 | Dig-In to PG&E Underground | 3rd Party-Contractor | United Pavement Maintenance Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-16 | 1” | 30 | 41 | N/A | 5 | May | 2025 |  | 905503 | No | Central Valley | Central Valley
23483 | x | x | x | x | 2025-05-16 | May | 5 | 2025 | 121004 |  |  | El Dorado | Northern | Sierra | North | El Dorado Hills | Yes | A & E Rodriguez LLC damaged 1" plastic gas service line with a shovel while installing a landscape fountain. No 811 ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | A & E Rodriguez LLC | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-16 | 1” | 30 | 1 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 403451 | Yes | North Valley & Sierra | North Valley & Sierra
23484 | x | x | x | x | 2025-05-16 | May | 5 | 2025 | 120980 |  | 131252736 | Marin | North Coast | Marin | North | Mill Valley | Yes | Marin Municipal Water District damaged 1/2" plastic gas service line with a shovel while fixing a water line. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Water | Failed to Dig with Care | Yes | 2025051201798 | Dig-In to PG&E Underground | 3rd Party-Government Entity | Marin Municipal Water District | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2025-05-16 | ½” | 15 | 26 | N/A | 5 | May | 2025 |  |  | Yes | North Coast | North Coast
23485 | x | x | x | x | 2025-05-16 | May | 5 | 2025 | 120991 |  | 131252941 | Contra Costa | Bay Area | Richmond | Central | El Cerrito | Yes | Unlicensed contractor damaged 1/2" plastic gas service line inserted into 3/4" steel with a shovel while removing a tree. No 811 ticket. | No | Gas Line | Yes | Shovel | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-16 | ½” | 10 | 56 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2025 |  |  | Yes | Bay Area | Bay Area
23486 | x | x | x | x | 2025-05-16 | May | 5 | 2025 | 120985 |  | 131252730 | San Mateo | Central Coast | Colma | Central | San Bruno | Yes | JMB Construction damaged 1/2" plastic gas service line inserted into 3/4" steel with a backhoe while installing a new sewer main. Valid 811 ticket. PG&E at-fault - Other Error - Difficult to Locate | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | Other Error | Yes | 2024120301735 | Dig-In to PG&E Underground | 3rd Party-Contractor | JMB Construction Inc | Distribution Service |  | Yes | Other Error | Difficult to locate | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-16 | ½” | 21 | 27 | N/A | 5 | May | 2025 | Bargaining Unit | 715324 | No | Bay Area | Bay Area
23487 | x | x | x | x | 2025-05-17 | May | 5 | 2025 | 121022 |  | 131256045 | Monterey | Central Coast | Central Coast | South | Salinas | Yes | Unlicensed contractor damaged 1/2" plastic gas service line with a post-hole digger while installing a fence. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-17 | ½” | 18 | 39 | No Knowledge of USA Ticketing Process | 5 | May | 2025 |  |  | Yes | South Bay & Central Coast | South Bay & Central Coast
23488 | x | x | x | x | 2025-05-17 | May | 5 | 2025 | 121024 |  | 131256133 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Unlicensed contractor damaged 1/2" plastic gas service line with a post-hole digger while installing a fence. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-17 | ½” | 30 | 65 | No Knowledge of USA Ticketing Process | 5 | May | 2025 |  |  | Yes | Central Valley | Central Valley
23489 | x | x | x | x | 2025-05-17 | May | 5 | 2025 | 121025 |  | 131256192 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Unlicensed contractor damaged 1/2" plastic gas service line with a shovel while planting palm trees. No 811 ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-17 | ½” | 18 | 37 | No Knowledge of USA Ticketing Process | 5 | May | 2025 |  |  | Yes | North Valley & Sierra | North Valley & Sierra
23490 | x | x | x | x | 2025-05-19 | May | 5 | 2025 | 121091 |  | 131264399 | Marin | North Coast | Marin | North | Novato | Yes | Unlicensed contractor damaged 1/2" plastic gas service line with a post-hole digger while removing a retaining wall. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-19 | ½” | 20 | 28 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2025 |  |  | Yes | North Coast | North Coast
23491 | x | x | x | x | 2025-05-19 | May | 5 | 2025 | 121068 |  | 131258502 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | JW Fencing and Ironworks damaged 1" plastic gas service line with an auger while replacing a fence. No 811 ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | JW Fencing and Ironworks | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-19 | 1” | 23 | 45 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 1112727 | No | North Valley & Sierra | North Valley & Sierra
23492 | x |  | x | x | 2025-05-19 | May | 5 | 2025 | 121090 |  | 131259781 | Contra Costa | Bay Area | Mission | South | San Ramon | Yes | Delsur damaged 1/2" plastic gas service line with an excavator while doing landscaping. No 811 ticket. | No | Gas Line | Yes | Excavator | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Delsur | Distribution Service | No | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-19 | ½” | 27 | 20 | Other | 5 | May | 2025 |  | 932951 | No | Bay Area | Bay Area
23493 | x | x | x | x | 2025-05-19 | May | 5 | 2025 | 121069 |  | 131259173 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Vulcan Construction and Maintenance damaged 1/2" plastic gas service line with a shovel while installing new gas facilities. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | 2025021902615 | Dig-In to PG&E Underground | 2nd Party-Contractor | Vulcan Construction and Maintenance | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2025-05-19 | ½” | 24 | 20 | N/A | 5 | May | 2025 |  | 414892 | Yes | Central Valley | Central Valley
23494 | x | x | x | x | 2025-05-19 | May | 5 | 2025 | 121062 |  | 131258136 | Alameda | Bay Area | Oakland | Central | Alameda | Yes | Miller Pipeline damaged 1/2" plastic gas service line with a shovel while gas service line replacements for PG&E. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | 2025020402364 | Dig-In to PG&E Underground | 2nd Party-Contractor | Miller Pipeline | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2025-05-19 | ½” | 24 | 13 | N/A | 5 | May | 2025 |  | 978749 | Yes | Bay Area | Bay Area
23495 | x | x | x | x | 2025-05-19 | May | 5 | 2025 | 121106 |  | 131260619 | Sacramento | Northern | Sacramento | North | Rio Linda | Yes | Mountain Cascade damaged a 3/4" steel gas service line with an excavator while installing a sewer line. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025030502291 | Dig-In to PG&E Underground | 3rd Party-Contractor | Mountain Cascade Inc | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-19 | ¾” | 16 | 65 | N/A | 5 | May | 2025 |  | 422496 | No | North Valley & Sierra | North Valley & Sierra
23496 |  | x |  | x | 2025-05-19 | May | 5 | 2025 | OIS 2787343 |  |  | Alameda | Bay Area | Mission | South | Dublin | No | Ransome damaged primary electric with an excavator while doing sewer work. Valid 811 ticket. Failed to expose facility with hand tools. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 202503100323 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ransome Company | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-05-19 |  |  | 0 | N/A | 5 | May | 2025 |  |  | No | Bay Area | Bay Area
23497 | x | x | x | x | 2025-05-20 | May | 5 | 2025 | 121172 |  | 131264916 | Marin | North Coast | Marin | North | Tiburon | Yes | Ultra Construction damaged a 1" steel gas service line with an excavator while doing foundation work. Valid 811 ticket. Failed to maintain marks | No | Gas Line | Yes | Excavator | Foundation Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | 2025042103302 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ultra Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-20 | 1” | 12 | 24 | N/A | 5 | May | 2025 |  | 913787 | No | North Coast | North Coast
23498 | x | x | x | x | 2025-05-20 | May | 5 | 2025 | 121168 |  | 131265051 | Fresno | Central Valley | Fresno | South | Clovis | Yes | Unlicensed contractor damaged 1/2" plastic gas service line with a shovel while repairing a damaged telecommunication cable. No 811 ticket. | No | Gas Line | Yes | Shovel | Telecommunications | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-20 | ½” | 24 | 10 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  |  | Yes | Central Valley | Central Valley
23499 | x | x | x | x | 2025-05-20 | May | 5 | 2025 | 121147 |  | 131263984 | Humboldt | Northern | Humboldt | North | Eureka | Yes | BC Drain Care & Plumbing damaged 1/2" plastic gas service line with a reciprocating saw while installing a drainage line for a sump pump. No 811 ticket. | No | Gas Line | Yes | Cutting Machine | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | BC Drain Care and Plumbing | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-20 | ½” | 18 | 13 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 1058371 | No | North Coast | North Coast
23500 | x |  |  |  | 2025-05-20 | May | 5 | 2025 | 121146 |  |  | Monterey | Central Coast | Central Coast | South | Carmel | Yes | Pony Construction damaged a 3/4" steel gas service line with an auger while doing foundation work. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Auger | Foundation Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025051202781 | Dig-In to PG&E Underground | 3rd Party-Contractor | Pony Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-20 | ¾” | 24 | 53 | N/A | 5 | May | 2025 |  | 1021085 | No | South Bay & Central Coast | South Bay & Central Coast
23501 | x | x | x | x | 2025-05-20 | May | 5 | 2025 | 121145 |  | 131263871 | Monterey | Central Coast | Central Coast | South | Marina | Yes | Unlicensed contractor damaged a 1" plastic gas service line with a post-hole digger while replacing a fence. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-20 | 1” | 30 | 60 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  |  | Yes | South Bay & Central Coast | South Bay & Central Coast
23502 | x | x | x | x | 2025-05-20 | May | 5 | 2025 | 121173 |  | 131267109 | Alameda | Bay Area | Mission | South | Fremont | Yes | Unlicensed contractor damaged 1" plastic gas service line with a backhoe while installing a new water line. No 811 ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-20 | 1” | 24 | 1 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  |  | No | Bay Area | Bay Area
23503 | x | x | x | x | 2025-05-20 | May | 5 | 2025 | 121144 |  | 131265053 | Mendocino | Northern | Sonoma | North | Ukiah | Yes | Homeowner damaged 1/2" plastic gas service line with a post-hole digger while installing fence posts. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-20 | ½” | 24 | 24 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2025 |  |  | Yes | North Coast | North Coast
23504 | x | x | x |  | 2025-05-20 | May | 5 | 2025 | 121160 |  | 131264053 | Humboldt | Northern | Humboldt | North | Eureka | Yes | Michels Pacific Energy damaged 1/2" plastic gas service line with a air spade while exposing the gas line. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Spader | Gas | Failed to Dig with Care | Yes | 2025051501451 | Dig-In to PG&E Underground | 2nd Party-Contractor | Michels Pacific Energy | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2025-05-20 | ½” | 18 | 37 | N/A | 5 | May | 2025 |  | 1057869 | No | North Coast | North Coast
23505 | x | x | x | x | 2025-05-20 | May | 5 | 2025 | 121153 |  | 131264048 | Contra Costa | Bay Area | Diablo | South | Orinda | Yes | C & J Fencing damaged 1" plastic gas service line with a shovel while installing a new fence. Valid 811 ticket. PG&E at-fault - Locator Error - No Mark | No | Gas Line | Yes | Shovel | Fencing | Facility was not Located or Marked | Yes | 2025050600484 | Dig-In to PG&E Underground | 3rd Party-Contractor | C & J Fencing | Distribution Service |  | Yes | Locator Error - No Mark | Did not mark locatable facility | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-20 | 1” | 36 | 75 | N/A | 5 | May | 2025 | Bargaining Unit | 924202 | Yes | Bay Area | Bay Area
23506 | x | x | x | x | 2025-05-20 | May | 5 | 2025 | 121150 |  | 131263887 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Man-Fer Construction damaged a 1 1/4" steel gas service line with a powered hand saw while installing fence posts. No 811 ticket. | No | Gas Line | Yes | Cutting Machine | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Man-Fer Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-20 | 1 ¼” | 12 | 16 | Didn’t think they were digging deep enough to damage an underground utility | 5 | May | 2025 |  |  | No | Bay Area | Bay Area
23507 | x | x | x | x | 2025-05-20 | May | 5 | 2025 | 121157 |  | 131264119 | Sacramento | Northern | Sacramento | North | Elk Grove | Yes | Top Rail Fence damaged 1/2" plastic gas service line with a digging bar while installing a fence. No 811 ticket. | No | Gas Line | Yes | Digging Bar | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Top Rail Fence | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-20 | ½” | 22 | 42 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 5 | May | 2025 |  | 1046238 | Yes | North Valley & Sierra | North Valley & Sierra
23508 | x | x | x | x | 2025-05-20 | May | 5 | 2025 | 121163 |  | 131264192 | Alameda | Bay Area | Richmond | Central | Albany | Yes | Jamie Daniel Robertson damaged 1/2" plastic gas service line with a shovel while doing a property remodel. No 811 ticket. | No | Gas Line | Yes | Shovel | Building Construction | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Jamie Daniel Robertson | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-20 | ½” | 14 | 13 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 5 | May | 2025 |  | 1014339 | Yes | Bay Area | Bay Area
23509 | x | x |  | x | 2025-05-21 | May | 5 | 2025 | 121196 |  |  | Marin | North Coast | Marin | North | San Rafael | Yes | Bill Brown Construction damaged 1/2" plastic gas service line inserted into 1 1/4" steel with a shovel while exposing the line. No 811 ticket. Marks were still visible for another contractor so primary cause of incident is failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Bill Brown Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-21 | ½” | 8 | 12 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2025 |  | 684764 | Yes | North Coast | North Coast
23510 | x | x |  | x | 2025-05-21 | May | 5 | 2025 | 121218 |  | 131269123 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Homeowner damaged 1/2" plastic gas service line with a trencher while installing a sprinkler line. No 811 ticket. | No | Gas Line | Yes | Trencher | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-21 | ½” | 20 | 28 | Believed they knew where underground utility was from previous knowledge | 5 | May | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23511 | x | x | x | x | 2025-05-21 | May | 5 | 2025 | 121231 |  | 131269753 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | R & S Construction Management Inc damaged 1" plastic gas service line with a stake while installing concrete for a sidewalk. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Stake | Curb/Sidewalk Work | Failed to Dig with Care | Yes | 2025040702256 | Dig-In to PG&E Underground | 3rd Party-Contractor | R & S Construction Management Inc | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-21 | 1” | 27 | 26 | N/A | 5 | May | 2025 |  | 992019 | Yes | Bay Area | Bay Area
23512 | x | x | x | x | 2025-05-21 | May | 5 | 2025 | 121200 |  | 131269240 | Sacramento | Northern | Sacramento | North | North Highlands | Yes | SOHO Build damaged 1/2" plastic gas service line with a shovel while installing an electric service for an ADU. No 811 ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | SOHO Build | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-21 | ½” | 16 | 33 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 1064097 | Yes | North Valley & Sierra | North Valley & Sierra
23513 |  | x |  | x | 2025-05-21 | May | 5 | 2025 | OIS 2789226 |  |  | Santa Clara | Central Coast | San Jose | Central | San Jose | No | Osmose Utilities Services Inc damaged secondary electric with a shovel while doing Pole Test & Treat work. Valid 811 ticket. PG&E at-fault - Locator Error - Mismark. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Shovel | Pole Test & Treat | Incorrect Information or Marks | Yes | 2025041100100 | Dig-In to PG&E Underground | 2nd Party-Contractor | Osmose Utilities Services Inc | Electric |  | Yes | Locator Error - Mismark | Incorrect Hook-Up | 2025 Q2 | Yes | Orange | PG&E Division Electric |  |  | 2nd Party Electric | Yes | 2025-05-21 |  | 12 | 0 | N/A | 5 | May | 2025 | Bargaining Unit | 855333 | Yes | South Bay & Central Coast | South Bay & Central Coast
23514 | x | x | x | x | 2025-05-22 | May | 5 | 2025 | 121255 |  |  | Fresno | Central Valley | Fresno | South | Fresno | Yes | Romo Paving & Grading Inc damaged a 1" plastic gas service line with a backhoe while installing new water facilities. Valid 811 ticket. PG&E at-fault - Locator Error - No Mark | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Facility was not Located or Marked | Yes | 2025051501480 | Dig-In to PG&E Underground | 3rd Party-Contractor | Romo Paving & Grading Inc | Distribution Service |  | Yes | Locator Error - No Mark | Did not mark locatable facility | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-22 | 1” | 30 | 15 | N/A | 5 | May | 2025 | Bargaining Unit |  | No | Central Valley | Central Valley
23515 |  | x |  | x | 2025-05-22 | May | 5 | 2025 | OIS 2789884 |  |  | Yuba | Northern | Sierra | North | Marysville | No | Morello Construction damaged 3-1/0 primary electric with boring equipment while installing telecommunication conduit. Valid 811 ticket. Failed to expose facility with hand tools. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Boring Equipment | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025050703871 | Dig-In to PG&E Underground | 3rd Party-Contractor | Morello Construction | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-05-22 |  | 66 | 0 | N/A | 5 | May | 2025 |  | 1085579 | No | North Valley & Sierra | North Valley & Sierra
23516 | x | x | x | x | 2025-05-22 | May | 5 | 2025 | 121268 |  | 131273229 | Alameda | Bay Area | Richmond | Central | Berkeley | Yes | EBMUD damaged 1" plastic gas service line with a backhoe while doing a water line replacement. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025051901163 | Dig-In to PG&E Underground | 3rd Party-Government Entity | EBMUD | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2025-05-22 | 1” | 44 | 14 | N/A | 5 | May | 2025 |  |  | No | Bay Area | Bay Area
23517 | x | x |  | x | 2025-05-22 | May | 5 | 2025 | 121257 |  |  | Santa Clara | Central Coast | De Anza | Central | Campbell | Yes | RV Stich Construction damaged the wrap on a 2" plastic gas main with hand tools while doing electric work. Valid 811 ticket. Failed to dig with care | Yes | Gas Line | No | Other Hand Tools | Electric Work | Failed to Dig with Care | Yes | 2025041700635 | Dig-In to PG&E Underground | 3rd Party-Contractor | RV Stich Construction | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-22 | 2” | 40 | 0 | N/A | 5 | May | 2025 |  | 530135 | Yes | South Bay & Central Coast | South Bay & Central Coast
23518 | x | x |  | x | 2025-05-22 | May | 5 | 2025 | 121251 |  |  | Alameda | Bay Area | Oakland | Central | Oakland | Yes | Alfaro”s Construction Services damaged 1/2" plastic gas service line with a shovel while installing drainage at a residence. No 811 ticket. | No | Gas Line | Yes | Shovel | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Alfaro”s Construction Services | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-22 | ½” | 12 | 12 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 953602 | Yes | Bay Area | Bay Area
23519 | x | x | x | x | 2025-05-22 | May | 5 | 2025 | 121284 |  | 131274507 | Sonoma | Northern | Sonoma | North | Sebastopol | Yes | Mark Ciddio Woodworks & Construction damaged 1" plastic gas service line with a reciprocating saw while making sewer repairs. No 811 ticket. | No | Gas Line | Yes | Cutting Machine | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Mark Ciddio Woodworks & Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-22 | 1” | 18 | 1 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 740895 | No | North Coast | North Coast
23520 | x | x |  | x | 2025-05-22 | May | 5 | 2025 | 121285 |  |  | Marin | North Coast | Marin | North | Novato | Yes | Next Level Excavating damaged a 1 1/4" plastic gas service line with an excavator while doing sewer work. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025051800290 | Dig-In to PG&E Underground | 3rd Party-Contractor | Next Level Excavating | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-22 | 1 ¼” | 32 | 59 | N/A | 5 | May | 2025 |  | 1117969 | No | North Coast | North Coast
23521 | x | x | x | x | 2025-05-22 | May | 5 | 2025 | 121282 |  | 131273932 | Stanislaus | Central Valley | Yosemite | South | Oakdale | Yes | R. P. Landscaping damaged 1/2" plastic gas service line with a shovel while installing landscaping lights. No 811 ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | R. P. Landscaping | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-22 | ½” | 9 | 9 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 1050587 | Yes | Central Valley | Central Valley
23522 |  | x |  | x | 2025-05-22 | May | 5 | 2025 | OIS 9367262 |  |  | Butte | Northern | North Valley | North | Durham | No | Renewable Solar damaged 3 x 4/0 direct buried conductors with an excavator while installing solar electric. Expired 811 ticket. Marks were still visible and accurate so primary cause of incident is failed to expose facility with hand tools. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Excavator | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025032402043 | Dig-In to PG&E Underground | 3rd Party-Contractor | Renewable Solar | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-05-22 |  | 24 | 0 | N/A | 5 | May | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23523 | x | x | x | x | 2025-05-23 | May | 5 | 2025 | 121323 |  | 131277709 | San Mateo | Central Coast | Colma | Central | Daly City | Yes | JLG Concrete Saw Cutting damaged 1/2" plastic gas service line inserted into 3/4" steel with a concrete saw cutter while doing water work. No 811 ticket. There were marks for another contractor that were visible and accurate so primary cause of incident is failed to expose facility with hand tools | No | Gas Line | Yes | Cutting Machine | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | JLG Concrete Saw Cutting | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-23 | ½” | 10 | 42 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2025 |  | 1119443 | No | Bay Area | Bay Area
23524 |  |  | x | x | 2025-05-23 | May | 5 | 2025 | 47223329 |  | 131277983 | Santa Cruz | Central Coast | Central Coast | South | Watsonville | Yes | MP Nexlevel damaged 1/2" plastic gas service line with a shovel while installing fiber optic lines. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Dig with Care | Yes | 2025030600099 | Dig-In to PG&E Underground | 3rd Party-Contractor | MP Nexlevel | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-23 | ½” |  | 1 | N/A | 5 | May | 2025 |  | 501188 | Yes | South Bay & Central Coast | South Bay & Central Coast
23525 | x | x | x | x | 2025-05-23 | May | 5 | 2025 | 121329 |  | 131278408 | Solano | Northern | North Bay | North | Fairfield | Yes | HM Concrete Inc damaged 1/2" plastic gas service line with a skid steer while installing fence posts. No 811 ticket. | No | Gas Line | Yes | Skid Steer | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | HM Concrete Inc | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-23 | ½” | 35 | 41 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2025 |  | 723759 | No | North Coast | North Coast
23526 | x | x |  | x | 2025-05-23 | May | 5 | 2025 | 121325 |  |  | Alameda | Bay Area | Mission | South | Pleasanton | Yes | Dun-Rite Excavating damaged a 1 1/4" plastic gas service line with an excavator while grading. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Blading/Lot Grading | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025043000489 | Dig-In to PG&E Underground | 3rd Party-Contractor | Dun-Rite Excavating Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-23 | 1 ¼” | 32 | 36 | N/A | 5 | May | 2025 |  | 771947 | No | Bay Area | Bay Area
23527 | x | x | x | x | 2025-05-24 | May | 5 | 2025 | 121352 |  | 131280025 | Placer | Northern | Sierra | North | Auburn | Yes | Homeowner damaged 1/2" plastic gas service line with a shovel while installing fence posts. No 811 ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-24 | ½” | 24 | 14 | Believed they knew where underground utility was from previous knowledge | 5 | May | 2025 |  |  | Yes | North Valley & Sierra | North Valley & Sierra
23528 |  | x |  | x | 2025-05-24 | May | 5 | 2025 | OIS 2791853 |  |  | San Mateo | Central Coast | Belmont | Central | La Honda | No | Homeowner damaged 3-1/0 secondary conductor with an excavator while doing emergency sewer repairs. No 811 ticket. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Backhoe/Trackhoe | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Electric |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Electric | Yes | 2025-05-24 |  |  | 0 | Excavator Asserted They Could Not Wait | 5 | May | 2025 |  |  | No | Bay Area | Bay Area
23529 | x | x | x | x | 2025-05-25 | May | 5 | 2025 | 121368 |  | 131280507 | Monterey | Central Coast | Central Coast | South | Salinas | Yes | Homeowner damaged 3/4" steel gas service line with a sawzall while removing tree stump roots. No 811 ticket. Marks were still visible for another excavation that were accurate so primary cause of incident is failed to protect subsurface installation | No | Gas Line | Yes | Cutting Machine | Tree Removal/Stump Grinding | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-25 | ¾” | 24 | 255 | Believed they knew where underground utility was from previous knowledge | 5 | May | 2025 |  |  | No | South Bay & Central Coast | South Bay & Central Coast
23530 | x | x | x | x | 2025-05-26 | May | 5 | 2025 | 121382 | 47223924 | 131282150 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | MV Solid Fencing damaged 1/2" plastic gas service line with a post-hole digger while installing a fence. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | MV Solid Fencing | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-26 | ½” | 18 | 73 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  |  | Yes | Central Valley | Central Valley
23531 | x | x | x | x | 2025-05-27 | May | 5 | 2025 | 121424 |  | 131285333 | Marin | North Coast | Marin | North | San Anselmo | Yes | Unlicensed contractor damaged 1 1/4" plastic gas main with a shovel while building a fence. No 811 ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-27 | 1 ¼” | 20 | 51 | No Knowledge of USA Ticketing Process | 5 | May | 2025 |  |  | Yes | North Coast | North Coast
23532 |  | x |  | x | 2025-05-27 | May | 5 | 2025 | OIS 2793319 |  |  | San Mateo | Central Coast | Colma | Central | San Bruno | No | Berkeley Cement Inc damaged 4" plastic conduit with an auger while drilling a hole for a new street light base. Valid 811 ticket. Failed to expose facility with hand tools. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Auger | Pole/Post Installation | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025051500667 | Dig-In to PG&E Underground | 3rd Party-Contractor | Berkeley Cement Inc | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-05-27 |  | 60 | 0 | N/A | 5 | May | 2025 |  | 290755 | No | Bay Area | Bay Area
23533 | x | x | x | x | 2025-05-27 | May | 5 | 2025 | 121421 |  | 131284999 | Marin | North Coast | Marin | North | San Anselmo | Yes | Unlicensed contractor damaged 1" plastic gas service line with a shovel while planting trees and plants. No 811 ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-27 | 1” | 34 | 30 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2025 |  |  | Yes | North Coast | North Coast
23534 | x |  | x | x | 2025-05-27 | May | 5 | 2025 | 121440 |  | 131286434 | Stanislaus | Central Valley | Yosemite | South | Patterson | Yes | Terralink Communications damaged a 2" plastic gas main with an excavator while installing electric charging stations. Expired 811 ticket. Marks were still accurate so primary cause of incidents is failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No (expired) | 2025032403315 | Dig-In to PG&E Underground | 3rd Party-Contractor | Terralink Communications | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-27 | 2” | 36 | 195 | Expired USA Ticket | 5 | May | 2025 |  | 770288 | No | Central Valley | Central Valley
23535 | x | x | x | x | 2025-05-27 | May | 5 | 2025 | 121438 |  |  | Fresno | Central Valley | Yosemite | South | Mendota | Yes | EMA Construction Inc. damaged 1/2" plastic gas service line with an excavator while installing a gas line. No 811 ticket. | No | Gas Line | Yes | Excavator | Gas | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | EMA Construction Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-27 | ½” | 24 | 12 | Knew about USA ticket requirement but chose not to call | 5 | May | 2025 |  | 1125453 | No | Central Valley | Central Valley
23536 | x | x | x | x | 2025-05-28 | May | 5 | 2025 | 121470 |  | 131291353 | Marin | North Coast | Marin | North | Mill Valley | Yes | Homeowner damaged 1/2" plastic gas service line with a shovel while installing deck posts. No 811 ticket. | No | Gas Line | Yes | Shovel | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-28 | ½” | 8 | 15 | No Knowledge of USA Ticketing Process | 5 | May | 2025 |  |  | Yes | North Coast | North Coast
23537 | x | x |  | x | 2025-05-28 | May | 5 | 2025 | 121487 |  |  | Kern | Central Valley | Kern | South | Taft | Yes | HPS Plumbing damaged 1/2" plastic gas service line with a shovel while doing sewer repairs. No 811 ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 2nd Party-Contractor | HPS Plumbing | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2025-05-28 | ½” | 24 | 1 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2025 |  | 793014 | Yes | Central Valley | Central Valley
23538 |  | x |  | x | 2025-05-28 | May | 5 | 2025 | OIS 2794567 |  |  | Marin | North Coast | Marin | North | Belvedere | No | All Bay Drilling damaged 1-350A TPX in 3" conduit with a boring machine while doing foundation work. Valid 811 ticket. Failed to expose facility with hand tools. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Boring Equipment | Foundation Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | All Bay Drilling | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-05-28 |  | 48 | 0 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 5 | May | 2025 |  | 734075 | No | North Coast | North Coast
23539 |  | x |  | x | 2025-05-28 | May | 5 | 2025 | OIS 2794692 |  |  | Contra Costa | Bay Area | Richmond | Central | Pinole | No | Utility Construction Services Inc. damaged a secondary electric service line with a shovel while doing a pedestal replacement. Valid 811 ticket. Failed to dig with care. Electric Dig In, Not Valid for STIP. | No | Electric Line | No | Shovel | Electric Work | Failed to Dig with Care | Yes | 2025022702209 | Dig-In to PG&E Underground | 2nd Party-Contractor | Utility Construction Services Inc. | Electric |  | No | N/A |  | 2025 Q2 | Yes | Orange | PG&E GC Electric |  |  | 2nd Party Electric | Yes | 2025-05-28 |  | 18 | 0 | N/A | 5 | May | 2025 |  | 1037581 | Yes | Bay Area | Bay Area
23540 | x | x | x | x | 2025-05-28 | May | 5 | 2025 | 121457 |  | 131290751 | San Joaquin | Central Valley | Stockton | South | Manteca | Yes | South San Joaquin Irrigation District damaged a 2" plastic gas main with a probing tool while locating an irrigation pipe. No 811 ticket. | No | Gas Line | Yes | Probing Tool | Irrigation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Government Entity | South San Joaquin Irrigation District | Distribution Main |  | No | N/A |  | 2025 Q2 | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2025-05-28 | 2” | 26 | 73 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2025 |  |  | Yes | Central Valley | Central Valley
23541 | x | x | x | x | 2025-05-29 | May | 5 | 2025 | 121513 |  | 131295549 | Contra Costa | Bay Area | Diablo | South | Danville | Yes | Next Level Homes Inc. damaged 1/2" plastic gas service line with a shovel while upgrading the electric service at a residence. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | 2025052302101 | Dig-In to PG&E Underground | 3rd Party-Contractor | Next Level Homes Inc. | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-29 | ½” | 24 | 30 | N/A | 5 | May | 2025 |  | 1036733 | Yes | Bay Area | Bay Area
23542 | x | x | x | x | 2025-05-29 | May | 5 | 2025 | 121504 |  | 131296847 | Yolo | Northern | North Bay | North | Woodland | Yes | City of Woodland damaged 1" plastic gas service line with an excavator while doing road repairs. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Road Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025052300262 | Dig-In to PG&E Underground | 3rd Party-Government Entity | City of Woodland | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2025-05-29 | 1” | 26 | 11 | N/A | 5 | May | 2025 |  |  | No | North Coast | North Coast
23543 | x |  | x | x | 2025-05-29 | May | 5 | 2025 | 121501 |  | 131294912 | San Joaquin | Central Valley | Stockton | South | Lodi | Yes | City of Lodi damaged 1/2" plastic gas service line with a shovel while replacing a concrete secondary box. No 811 ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Government Entity | City Of Lodi Electric Dept | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2025-05-29 | ½” | 24 | 22 | Excavator Did Not Believe a USA Ticket was Required | 5 | May | 2025 |  |  | Yes | Central Valley | Central Valley
23544 | x |  | x | x | 2025-05-29 | May | 5 | 2025 | 121534 |  | 131297276 | Humboldt | Northern | Humboldt | North | Bayside | Yes | Hayes Building Co damaged 1/2" plastic gas service line with an excavator while digging a foundation. No 811 ticket. | No | Gas Line | Yes | Excavator | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Hayes Building Co | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-29 | ½” | 24 | 23 | Other | 5 | May | 2025 |  | 957854 | No | North Coast | North Coast
23545 | x | x | x | x | 2025-05-29 | May | 5 | 2025 | 121495 |  | 131293242 | Sacramento | Northern | Sacramento | North | North Highlands | Yes | Granite Construction damaged a 3/4" steel gas service line with an excavator while doing sidewalk grinding. Valid 811 ticket. Excavated outside delineated area | No | Gas Line | Yes | Excavator | Curb/Sidewalk Work | Excavated outside delineated area | Yes | 2025031900332 | Dig-In to PG&E Underground | 3rd Party-Contractor | Granite Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-29 | ¾” | 12 | 86 | N/A | 5 | May | 2025 |  | 89 | No | North Valley & Sierra | North Valley & Sierra
23546 | x |  | x | x | 2025-05-30 | May | 5 | 2025 | 121547 |  | 131300177 | Napa | Northern | North Bay | North | Calistoga | Yes | Ghilotti Construction damaged 1/2" plastic gas service line with an excavator while installing a new water line. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025050602969 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ghilotti Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-30 | ½” | 24 | 21 | N/A | 5 | May | 2025 |  | 644515 | No | North Coast | North Coast
23547 | x |  | x | x | 2025-05-30 | May | 5 | 2025 | 121564 |  | 131300959 | Alameda | Bay Area | Richmond | Central | Berkeley | Yes | North Berkeley Design & Construction damaged 1/2" plastic gas service line with a pneumatic spader while installing a new driveway. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Spader | Driveway Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025052301807 | Dig-In to PG&E Underground | 3rd Party-Contractor | North Berkeley Design & Construction | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-05-30 | ½” | 12 | 30 | N/A | 5 | May | 2025 |  | 975672 | No | Bay Area | Bay Area
23548 | x |  | x | x | 2025-05-31 | May | 5 | 2025 | 121592 |  | 131303306 | Humboldt | Northern | Humboldt | North | Mckinleyville | Yes | Homeowner damaged 1/2" plastic gas service line with a backhoe while removing a tree stump. No 811 ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Tree Removal/Stump Grinding | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-05-31 | ½” | 32 | 28 | Other | 5 | May | 2025 |  |  | No | North Coast | North Coast
23549 |  | x |  |  | 2025-05-15 | May | 5 | 2025 | 47221047 |  |  | Fresno | Central Valley | Fresno | South | Fresno | Yes | PG&E Gas (GDGC) damaged 1/2" plastic gas service line with a backhoe while installing new gas facilities. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Backhoe/Trackhoe | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025040101780 | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Gas | Distribution Service |  | No | N/A |  | 2025 Q2 | Yes | Blue | PG&E GDGC |  |  | 1st Party Gas | Yes | 2025-05-15 | ½” | 26 | 1 | N/A | 5 | May | 2025 |  |  | No | Central Valley | Central Valley
23550 |  | x |  |  | 2025-05-28 | May | 5 | 2025 | OIS 2794726 |  |  | Shasta | Northern | North Valley | North | Shasta | No | The Davey Tree Expert Company damaged the insulation on two electric cables with a shovel while doing PT&T work. Valid 811 ticket. Failed to dig with care. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Shovel | Pole Test & Treat | Failed to Dig with Care | Yes | 2024091001878 | Dig-In to PG&E Underground | 2nd Party-Contractor | The Davey Tree Expert Company | Electric |  | No | N/A |  | 2025 Q2 | Yes | Orange | PG&E GC Electric |  |  | 2nd Party Electric | Yes | 2025-05-28 |  | 18 | 0 | N/A | 5 | May | 2025 |  | 694001 | Yes | North Valley & Sierra | North Valley & Sierra
23551 |  | x |  |  | 2025-05-29 | May | 5 | 2025 | OIS 2795990 |  |  | San Luis Obispo | Central Coast | Los Padres | South | San Luis Obispo | No | Griffith Company damaged a 3" corrugated conduit with an excavator while constructing a new parking lot. Valid 811 ticket. Failed to expose facility with hand tools. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Excavator | Blading/Lot Grading | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025022101786 | Dig-In to PG&E Underground | 3rd Party-Contractor | Griffith Company | Electric |  | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-05-29 |  |  | 0 | N/A | 5 | May | 2025 |  | 88 | No | South Bay & Central Coast | South Bay & Central Coast
23552 |  | x |  |  | 2025-05-30 | May | 5 | 2025 | OIS 2796840 |  |  | Tehama | Northern | North Valley | North | Cottonwood | No | Osmose Utility Services damaged 4/0 aluminum triplex UG cable with a shovel while doing PT&T work. Valid 811 ticket. Failed to dig with care. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Shovel | Pole Test & Treat | Failed to Dig with Care | Yes | 2025101500496 | Dig-In to PG&E Underground | 2nd Party-Contractor | Osmose Utilities Services Inc | Electric |  | No | N/A |  | 2025 Q2 | Yes | Orange | PG&E GC Electric |  |  | 2nd Party Electric | Yes | 2025-05-30 |  | 16 | 0 | N/A | 5 | May | 2025 |  | 855333 | Yes | North Valley & Sierra | North Valley & Sierra
23553 | x | x | x | x | 2025-06-02 | Jun | 6 | 2025 | 121658 |  | 131307110 | Alameda | Bay Area | Oakland | Central | Piedmont | Yes | Villalobos & Associates damaged 1/2" plastic gas service line inserted into 3/4" steel with a stake while doing a sidewalk repair. Valid 811 ticket. PG&E at-fault - Locator Error - No Mark | No | Gas Line | Yes | Stake | Curb/Sidewalk Work | Facility was not Located or Marked | Yes | 2025052902555 | Dig-In to PG&E Underground | 3rd Party-Contractor | Villalobos & Associates | Distribution Service |  | Yes | Locator Error - No Mark | Failed to Escalate | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-02 | ½” | 12 | 24 | N/A | 6 | Jun | 2025 | Bargaining Unit | 1017098 | Yes | Bay Area | Bay Area
23554 | x | x | x | x | 2025-06-02 | Jun | 6 | 2025 | 121653 |  | 131307640 | San Mateo | Central Coast | Belmont | Central | Hillsborough | Yes | Homeowner damaged a 1" plastic gas service line with a shovel while digging fence post holes. No 811 ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 121653 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-02 | 1” | 18 | 103 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  |  | Yes | Bay Area | Bay Area
23555 | x | x | x | x | 2025-06-02 | Jun | 6 | 2025 | 121624 |  | 131305253 | Monterey | Central Coast | Central Coast | South | Monterey | Yes | BG Construction damaged a 1/2" plastic gas service line with an excavator while installing an upgraded electric facility. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025051901494 | Dig-In to PG&E Underground | 3rd Party-Contractor | BG Construction | Distribution Service | 121624 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-02 | ½” | 24 | 25 | N/A | 6 | Jun | 2025 |  | 1026995 | No | South Bay & Central Coast | South Bay & Central Coast
23556 | x | x | x |  | 2025-06-02 | Jun | 6 | 2025 | 121652 |  | 131306734 | Solano | Northern | North Bay | North | Vacaville | Yes | Koios Engineering Inc damaged a 1/2" plastic gas service line with an excavator while doing sewer work. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025052701227 | Dig-In to PG&E Underground | 3rd Party-Contractor | Koisos Engineering Inc | Distribution Service | 121652 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-02 | ½” | 28 | 43 | N/A | 6 | Jun | 2025 |  | 1079921 | No | North Coast | North Coast
23557 | x | x | x |  | 2025-06-02 | Jun | 6 | 2025 | 121631 |  | 131305688 | Sonoma | Northern | Sonoma | North | Windsor | Yes | Homeowner damaged a 1/2" plastic gas service line with a post-hole digger while installing a fence. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 121631 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-02 | ½” | 18 | 30 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  |  | Yes | North Coast | North Coast
23558 |  | x |  |  | 2025-06-03 | Jun | 6 | 2025 | OIS 2799652 |  |  | Alameda | Bay Area | Mission | South | Pleasanton | No | Bay Cities Paving & Grading damaged electric conduit with a backhoe while doing curb/sidewalk work. Valid 811 ticket. Failed to maintain marks. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Backhoe/Trackhoe | Curb/Sidewalk Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | 2024101402618-09 | Dig-In to PG&E Underground | 3rd Party-Contractor | Bay Cities Paving & Grading | Electric | OIS 2799652 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-06-03 |  | 16 | 0 | N/A | 6 | Jun | 2025 |  | 238650 | No | Bay Area | Bay Area
23559 | x | x | x |  | 2025-06-03 | Jun | 6 | 2025 | 121701 |  | 131311932 | San Mateo | Central Coast | Belmont | Central | Woodside | Yes | Utility Construction Services damaged a 1/2" plastic gas service line with a shovel while installing a new electric panel for PG&E. Valid 811 ticket. PG&E at-fault - Locator Error - No Mark | No | Gas Line | Yes | Shovel | Electric Work | Facility was not Located or Marked | Yes | 2025052803200 | Dig-In to PG&E Underground | 2nd Party-Contractor | Utility Construction Services Inc. | Distribution Service |  | Yes | Locator Error - No Mark | Training Issue | 2025 Q2 | Yes | Orange | PG&E GC Electric |  |  | 2nd Party Gas | Yes | 2025-06-03 | ½” | 30 | 53 | N/A | 6 | Jun | 2025 | Bargaining Unit | 1037581 | Yes | Bay Area | Bay Area
23560 | x | x | x |  | 2025-06-04 | Jun | 6 | 2025 | 121787 |  | 131318896 | Contra Costa | Bay Area | Richmond | Central | Richmond | Yes | Reuben Borg Fence damaged a 1/2" plastic gas service line with a shovel while installing a new fence. No 811 ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Reuben Borg Fence | Distribution Service | 121787 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-04 | ½” | 24 | 24 | Excavator Did Not Believe a USA Ticket was Required | 6 | Jun | 2025 |  | 746116 | Yes | Bay Area | Bay Area
23561 | x | x | x |  | 2025-06-04 | Jun | 6 | 2025 | 121751 |  | 131317558 | Sacramento | Northern | Sacramento | North | Galt | Yes | Maxsim damaged a 1/2" plastic gas service line with a shovel while setting a telecommunications box. No 811 ticket. | No | Gas Line | Yes | Shovel | Telecommunications | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Maxsim | Distribution Service | 121751 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-04 | ½” | 16 | 82 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 6 | Jun | 2025 |  | 1119208 | Yes | North Valley & Sierra | North Valley & Sierra
23562 | x | x | x |  | 2025-06-04 | Jun | 6 | 2025 | 121782 |  | 131318826 | Alameda | Bay Area | Oakland | Central | Oakland | Yes | Homeowner damaged a 1" plastic gas service line with a shovel while doing a water line replacement. No 811 ticket. | No | Gas Line | Yes | Shovel | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 121782 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-04 | 1” | 29 | 17 | Other | 6 | Jun | 2025 |  |  | Yes | Bay Area | Bay Area
23563 | x | x | x |  | 2025-06-04 | Jun | 6 | 2025 | 121788 |  | 131318927 | Monterey | Central Coast | Central Coast | South | Salinas | Yes | Llano Construction damaged a 1/2" plastic gas service line with a shovel while installing a sidewalk. No 811 ticket. | No | Gas Line | Yes | Shovel | Curb/Sidewalk Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Llano Construction | Distribution Service | 121788 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-04 | ½” | 24 | 6 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  | 991612 | Yes | South Bay & Central Coast | South Bay & Central Coast
23564 | x | x | x |  | 2025-06-04 | Jun | 6 | 2025 | 121756 |  | 131317118 | San Mateo | Central Coast | Belmont | Central | Menlo Park | Yes | California Utility Company damaged a 1/2" plastic gas service line with an electric chipping hammer while doing telecommunications work. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Other Hand Machinery | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025042802213 | Dig-In to PG&E Underground | 3rd Party-Contractor | California Utility Company | Distribution Service | 121756 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-04 | ½” | 21 | 42 | N/A | 6 | Jun | 2025 |  | 1029526 | No | Bay Area | Bay Area
23565 | x | x | x |  | 2025-06-04 | Jun | 6 | 2025 | 121779 |  | 131318719 | Contra Costa | Bay Area | Richmond | Central | El Cerrito | Yes | EBMUD damaged a 1/2" plastic gas service line inserted into 3/4" steel with a backhoe while doing an emergency water line repair. Valid 811 ticket. PG&E at-fault - Other Error - Construction Error | No | Gas Line | Yes | Backhoe/Trackhoe | Water | Other Error | Yes | 2025053002820 | Dig-In to PG&E Underground | 3rd Party-Government Entity | EBMUD | Distribution Service |  | Yes | Other Error | Other Error | 2025 Q2 | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2025-06-04 | ½” | 28 | 25 | N/A | 6 | Jun | 2025 |  |  | No | Bay Area | Bay Area
23566 | x | x | x |  | 2025-06-04 | Jun | 6 | 2025 | 121785 |  | 131318880 | Sacramento | Northern | Sacramento | North | Citrus Heights | Yes | Homeowner damaged a 3/4" steel gas service line with a reciprocal saw while planting a tree. Valid 811 ticket. Excavated outside delineated area | No | Gas Line | Yes | Cutting Machine | Landscaping | Excavated outside delineated area | Yes | 2025052102179 | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 121785 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-04 | ¾” | 23 | 76 | N/A | 6 | Jun | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23567 | x |  |  |  | 2025-06-04 | Jun | 6 | 2025 | 121783 |  |  | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Ghilotti Construction damaged a 1/2" plastic gas service line inserted into 3/4" steel with an excavator while doing sewer work. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | No | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025030502228 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ghilotti Construction | Distribution Service | 121783 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-04 | ½” |  | 0 | N/A | 6 | Jun | 2025 |  | 644515 | No | North Coast | North Coast
23568 |  | x |  |  | 2025-06-04 | Jun | 6 | 2025 | 35482162 |  |  | Yolo | Northern | North Bay | North | Woodland | Yes | J&D Excavation damaged transmission line DFM 0621-01 with an excavator while doing 2nd party gas work for PG&E. Valid 811 ticket. Failed to maintain marks | No | Gas Line | No | Excavator | Gas | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | 2025051600508 | Dig-In to PG&E Underground | 2nd Party-Contractor | J&D Excavation | Transmission Line | 35482162 | No | N/A |  | 2025 Q2 | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2025-06-04 | 6" | 29 | 0 | N/A | 6 | Jun | 2025 |  | 975030 | No | North Coast | North Coast
23569 | x | x | x |  | 2025-06-05 | Jun | 6 | 2025 | 121832 |  | 131322981 | Humboldt | Northern | Humboldt | North | Eureka | Yes | Scurfield Electric damaged a 1/2" plastic gas service line with a shovel while installing new elctric facilities. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | 2025053103253 | Dig-In to PG&E Underground | 3rd Party-Contractor | Scurfield Electric | Distribution Service | 121832 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-05 | ½” | 18 | 27 | N/A | 6 | Jun | 2025 |  | 1036962 | Yes | North Coast | North Coast
23570 | x | x | x |  | 2025-06-05 | Jun | 6 | 2025 | 121805 |  | 131321481 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Homeowner damaged a 1" plastic gas service line with a shovel while digging a trench for electric facilities. No 811 ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 121805 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-05 | 1” | 32 | 43 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 6 | Jun | 2025 |  |  | Yes | Central Valley | Central Valley
23571 |  | x |  |  | 2025-06-05 | Jun | 6 | 2025 | 121821 |  |  | Alameda | Bay Area | Oakland | Central | Alameda | Yes | Unknown party damaged a 2" plastic gas main. PG&E discovered the damage when doing a leak investigation. Unknown when damage occurred. Root cause will be no 811 ticket. | No | Gas Line | Yes | Unknown | Unknown | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unknown | Distribution Main | 121821 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-05 | 2” |  | 0 | Other | 6 | Jun | 2025 |  |  | No | Bay Area | Bay Area
23572 | x | x | x |  | 2025-06-05 | Jun | 6 | 2025 | 121817 |  | 131321954 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Bailey's Trenchless damaged a 1/2" plastic gas service line with boring equipment while installing telecommunication facilities. Valid 811 ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Boring Equipment | Telecommunications | Incorrect Facility Records / Maps | Yes | 2025060201802 | Dig-In to PG&E Underground | 3rd Party-Contractor | Bailey's Trenchless | Distribution Service |  | Yes | Records Error | Mis Mapped Gas | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-05 | ½” | 48 | 246 | N/A | 6 | Jun | 2025 |  | 780747 | No | North Coast | North Coast
23573 | x | x | x |  | 2025-06-05 | Jun | 6 | 2025 | 121810 |  | 131321813 | Kern | Central Valley | Kern | South | Ridgecrest | Yes | Sierra Fence Company damaged 1/2" plastic gas service line with a post-hole digger while installing a fence post. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Sierra Fence Company | Distribution Service | 121810 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-05 | ½” | 24 | 24 | Didn’t think they were digging deep enough to damage an underground utility | 6 | Jun | 2025 |  | 809774 | Yes | Central Valley | Central Valley
23574 | x | x | x |  | 2025-06-05 | Jun | 6 | 2025 | 121847 |  | 131324103 | Butte | Northern | North Valley | North | Oroville | Yes | Butte County Housing Authority damaged 1/2" plastic gas service line with a shovel while doing a sewer repair. No 811 ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Government Entity | Butte County Housing Authority | Distribution Service | 121847 | No | N/A |  | 2025 Q2 | Yes | Green |  |  |  | 3rd Party Gas | Yes | 2025-06-05 | ½” | 19 | 17 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  |  | Yes | North Valley & Sierra | North Valley & Sierra
23575 |  | x |  |  | 2025-06-05 | Jun | 6 | 2025 | 121823 |  |  | Sacramento | Northern | Sacramento | North | Orangevale | Yes | Roo Landscaping damaged a 2" plastic gas service line with an excavator while doing landscaping. Valid 811 ticket. Failed to maintain marks | No | Gas Line | No | Excavator | Landscaping | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | 2025040401225 | Dig-In to PG&E Underground | 3rd Party-Contractor | Roo Landscaping | Distribution Service | 121823 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-05 | 2” | 23 | 0 | N/A | 6 | Jun | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23576 | x | x | x |  | 2025-06-06 | Jun | 6 | 2025 | 121889 |  | 131329693 | Solano | Bay Area | North Bay | North | Vallejo | Yes | Focus Rooter & Plumbing damaged a 1 1/4" plastic gas service line with a backhoe while doing a sewer repair. No 811 ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Focus Rooter and Plumbimg | Distribution Service | 121889 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-06 | 1 ¼” | 24 | 109 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  | 1086235 | No | North Coast | North Coast
23577 | x | x | x |  | 2025-06-06 | Jun | 6 | 2025 | 121866 |  | 131327728 | Sutter | Northern | Sierra | North | Yuba City | Yes | Fletchers Plumbing damaged a 1/2" plastic gas service line with a shovel while doing a sewer repair. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | 2025053001939 | Dig-In to PG&E Underground | 3rd Party-Contractor | Fletcher’s Plumbing and Contracting | Distribution Service | 121866 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-06 | ½” | 30 | 13 | N/A | 6 | Jun | 2025 |  | 309313 | Yes | North Valley & Sierra | North Valley & Sierra
23578 | x | x | x |  | 2025-06-06 | Jun | 6 | 2025 | 121882 |  | 131329176 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Michael O'Shaughnessy Construction damaged a 1/2" plastic gas service line inserted 1 1/4" steel with an excavator while installing a bus pad. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Road Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025042402086 | Dig-In to PG&E Underground | 3rd Party-Contractor | Michael O'Shaughnessy Construction | Distribution Service | 121882 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-06 | ½” | 12 | 11 | N/A | 6 | Jun | 2025 |  | 984235 | No | Bay Area | Bay Area
23579 | x | x | x |  | 2025-06-06 | Jun | 6 | 2025 | 121876 |  |  | Contra Costa | Bay Area | Richmond | Central | Richmond | Yes | Nema Construction damaged 1" plastic gas service line with a stake while building concrete forms. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Stake | Curb/Sidewalk Work | Failed to Dig with Care | Yes | 2025053100215 | Dig-In to PG&E Underground | 3rd Party-Contractor | Nema Construction | Distribution Service | 121876 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-06 | 1” | 20 | 29 | N/A | 6 | Jun | 2025 |  | 731870 | Yes | Bay Area | Bay Area
23580 | x | x | x |  | 2025-06-07 | Jun | 6 | 2025 | 121914 |  | 131331639 | Alameda | Bay Area | Oakland | Central | Oakland | Yes | Homeowner damaged 1" plastic gas service line with a shovel while digging fence post holes. No 811 ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 121914 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-07 | 1” | 14 | 24 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  |  | Yes | Bay Area | Bay Area
23581 | x | x | x |  | 2025-06-07 | Jun | 6 | 2025 | 121899 |  | 131331089 | Alameda | Bay Area | Mission | South | Pleasanton | Yes | Medallion Landscape Management damaged 1/2" plastic gas service line with a shovel while repairing a broken sprinkler. No 811 ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Medallion Landscape Management | Distribution Service | 121899 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-07 | ½” | 28 | 37 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  | 713234 | Yes | Bay Area | Bay Area
23582 | x | x | x |  | 2025-06-09 | Jun | 6 | 2025 | 121946 |  | 131334488 | Napa | Bay Area | North Bay | North | Napa | Yes | Miller Pipeline damaged 1/2" plastic gas service line with an excavator while installing new gas facilities for PG&E. Valid 811 ticket. Failed to expose facilities with hand tools | No | Gas Line | Yes | Excavator | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025052101907 | Dig-In to PG&E Underground | 2nd Party-Contractor | Miller Pipeline | Distribution Service | 121946 | No | N/A |  | 2025 Q2 | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2025-06-09 | ½” | 14 | 7 | N/A | 6 | Jun | 2025 |  | 978749 | No | North Coast | North Coast
23583 |  | x |  |  | 2025-06-09 | Jun | 6 | 2025 | OIS 2804827 |  |  | San Mateo | Central Coast | Colma | Central | South San Francisco | No | Ampco Contracting Inc. damaged 3-1/0 A EPR 12kv primary with an excavator whild doing building demolition. Valid 811 ticket. Failed to expose facility with hand tools. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Excavator | Building Demolition | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025052700462 /2025042801998 | Dig-In to PG&E Underground | 3rd Party-Contractor | Ampco Contracting Inc. | Electric | OIS 2804827 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-06-09 |  | 36 | 0 | N/A | 6 | Jun | 2025 |  | 851752 | No | Bay Area | Bay Area
23584 | x | x | x |  | 2025-06-09 | Jun | 6 | 2025 | 121955 |  | 131334922 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Esquivel Grading and Paving Inc damaged 1/2" plastic gas service line inserted into 3/4" steel with an excavator while doing a road work project. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Road Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025052803559 | Dig-In to PG&E Underground | 3rd Party-Contractor | Esquivel Grading and Paving Inc. | Distribution Service | 121955 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-09 | ½” | 16 | 21 | N/A | 6 | Jun | 2025 |  | 463185 | No | Bay Area | Bay Area
23585 | x | x | x |  | 2025-06-09 | Jun | 6 | 2025 | 121970 |  | 131335604 | Santa Clara | Central Coast | San Jose | Central | Gilroy | Yes | Apex Directional Drilling damaged a 1/2" plastic gas service line with an excavator while installing new electric facilities. Valid 811 ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Excavator | Electric Work | Incorrect Facility Records / Maps | Yes | 2025060203361 | Dig-In to PG&E Underground | 3rd Party-Contractor | Apex Directional Drilling | Distribution Service |  | Yes | Records Error | Mis Mapped Gas | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-09 | ½” | 42 | 29 | N/A | 6 | Jun | 2025 |  | 838568 | No | South Bay & Central Coast | South Bay & Central Coast
23586 | x | x | x |  | 2025-06-09 | Jun | 6 | 2025 | 121975 |  | 131336150 | Sacramento | Northern | Sacramento | North | North Highlands | Yes | Nor Cal Construction damaged a 1/2" plastic gas service line with a shovel while doing a sewer line repair. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | 2025052703201 | Dig-In to PG&E Underground | 3rd Party-Contractor | Nor Cal Construction | Distribution Service | 121975 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-09 | ½” | 23 | 9 | N/A | 6 | Jun | 2025 |  | 1086489 | Yes | North Valley & Sierra | North Valley & Sierra
23587 | x | x | x |  | 2025-06-09 | Jun | 6 | 2025 | 121941 |  | 131333821 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Homeowner damaged a 1/2" plastic gas service line with an auger while installing a fence post. No 811 ticket. | No | Gas Line | Yes | Auger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 121941 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-09 | ½” | 26 | 41 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  |  | No | Central Valley | Central Valley
23588 | x | x | x |  | 2025-06-09 | Jun | 6 | 2025 | 121961 |  | 131334958 | San Mateo | Central Coast | Colma | Central | San Bruno | Yes | JMB Construction damaged a 1/2" plastic gas service line inserted into 3/4" steel with an excavator while installing a new sewer main. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025051600623 | Dig-In to PG&E Underground | 3rd Party-Contractor | JMB Construction Inc | Distribution Service | 121961 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-09 | ½” | 24 | 1 | N/A | 6 | Jun | 2025 |  | 715324 | No | Bay Area | Bay Area
23589 | x | x | x |  | 2025-06-10 | Jun | 6 | 2025 | 122023 |  | 131348982 | Santa Clara | Central Coast | San Jose | Central | Milpitas | Yes | Central Fire Services Inc damaged a 1/2" plastic gas service line with a shovel while moving a water line. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Water | Failed to Dig with Care | Yes | 2025060303185 | Dig-In to PG&E Underground | 3rd Party-Contractor | Central Fire Services Inc | Distribution Service | 122023 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-10 | ½” | 36 | 16 | N/A | 6 | Jun | 2025 |  | 1042911 | Yes | South Bay & Central Coast | South Bay & Central Coast
23590 | x | x | x |  | 2025-06-10 | Jun | 6 | 2025 | 122001 |  | 131348130 | San Mateo | Central Coast | Belmont | Central | Redwood City | Yes | Saxelby Plumbing damaged a 3/4" steel gas service line with an electric chipping hammer while doing water work. No 811 ticket. | No | Gas Line | Yes | Other Hand Machinery | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Saxelby Plumbing | Distribution Service | 122001 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-10 | ¾” | 24 | 66 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 6 | Jun | 2025 |  | 878807 | No | Bay Area | Bay Area
23591 |  | x |  |  | 2025-06-10 | Jun | 6 | 2025 | OIS 2805775 |  |  | Butte | Northern | North Valley | North | Chico | No | Ohm Solar Solutions damaged an electric facility with a grounding rod while doing electric work. No 811 ticket. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Grounding Rod | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Ohm Solar Solutions | Electric | OIS 2805775 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-06-10 |  |  | 0 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  | 1069206 | Yes | North Valley & Sierra | North Valley & Sierra
23592 | x | x | x |  | 2025-06-10 | Jun | 6 | 2025 | 122025 |  | 131350181 | San Mateo | Central Coast | Belmont | Central | Woodside | Yes | SF Underground Inc. damaged a 3/4" steel gas service riser with a backhoe while doing construction on a large property. Valid 811 ticket. PG&E at-fault - Records Error | No | Gas Line | Yes | Backhoe/Trackhoe | Site Development | Incorrect Facility Records / Maps | Yes | 2025060502600 | Dig-In to PG&E Underground | 3rd Party-Contractor | SF Underground Inc | Distribution Service |  | Yes | Records Error | Incorrect GSR | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-10 | ¾” | 21 | 1 | N/A | 6 | Jun | 2025 |  | 1015543 | No | Bay Area | Bay Area
23593 | x | x | x |  | 2025-06-11 | Jun | 6 | 2025 | 122056 |  | 131353728 | Stanislaus | Central Valley | Yosemite | South | Oakdale | Yes | Redstone Construction damaged a 1/2" plastic gas service line with a shovel while doing sewer work. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | 2025030300026 | Dig-In to PG&E Underground | 3rd Party-Contractor | Redstone Construction Inc. | Distribution Service | 122056 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-11 | ½” | 24 | 40 | N/A | 6 | Jun | 2025 |  | 1088584 | Yes | Central Valley | Central Valley
23594 | x | x | x |  | 2025-06-11 | Jun | 6 | 2025 | 122064 |  | 131354020 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | PG&E Gas damaged a 1 1/4" gas service line with an excavator while replacing a gas main. Valid 811 ticket. Failed to maintain marks | No | Gas Line | Yes | Excavator | Gas | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | 2025052201149 | Dig-In to PG&E Underground | 1st Party-PG&E | PG&E Gas | Distribution Service | 122064 | No | N/A |  | 2025 Q2 | Yes | Blue | PG&E GDGC |  |  | 1st Party Gas | Yes | 2025-06-11 | 1 ¼” | 36 | 55 | N/A | 6 | Jun | 2025 |  |  | No | Bay Area | Bay Area
23595 |  | x |  |  | 2025-06-11 | Jun | 6 | 2025 | OIS 2806394 |  |  | Napa | Bay Area | North Bay | North | Oakville | No | Hernandez General Engineering damaged 1/0 secondary direct buried cable with a backhoe while developing a site for a new home. Expired 811 ticket and were using the marks for another contractor. Marks were still visible and valid so primary cause of incident is failed to expose facility with hand tools. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Backhoe/Trackhoe | Site Development | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Hernandez General Engineering | Electric | OIS 2806394 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-06-11 |  |  | 0 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 6 | Jun | 2025 |  | 901711 | No | North Coast | North Coast
23596 | x | x | x |  | 2025-06-11 | Jun | 6 | 2025 | 122050 |  | 131353267 | San Mateo | Central Coast | Colma | Central | Montara | Yes | Verdure Construction LLC damaged a 1/2" plastic gas service line with a shovel while exposing the residences sewer lateral. No 811 ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Verdura Construction, LLC | Distribution Service | 122050 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-11 | ½” | 18 | 17 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  | 844998 | Yes | Bay Area | Bay Area
23597 | x |  |  |  | 2025-06-12 | Jun | 6 | 2025 | 122131 |  |  | San Joaquin | Central Valley | Stockton | South | Stockton | Yes | Homeowner damaged a 1" plastic gas service line with a excavator while doing a power panel upgrade for an ADU. No 811 ticket. | No | Gas Line | Yes | Excavator | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122131 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-12 | 1” | 18 | 35 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  |  | No | Central Valley | Central Valley
23598 | x | x |  |  | 2025-06-12 | Jun | 6 | 2025 | 122122 |  |  | Marin | North Coast | Marin | North | Novato | Yes | Pioneer Underground Construction damaged a 1" plastic gas service line with an excavator while doing telcommunication work. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025060503267 | Dig-In to PG&E Underground | 3rd Party-Contractor | Pioneer Underground Construction Inc. | Distribution Service | 122122 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-12 | 1” | 18 | 17 | N/A | 6 | Jun | 2025 |  |  | No | North Coast | North Coast
23599 | x |  | x |  | 2025-06-12 | Jun | 6 | 2025 | 122139 |  | 131358844 | Stanislaus | Central Valley | Yosemite | South | Modesto | Yes | Homeowner damaged a 1/2" plastic gas service line with a shovel while burying a deceased animal. No 811 ticket. | No | Gas Line | Yes | Shovel | Other | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122139 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-12 | ½” | 24 | 13 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  |  | Yes | Central Valley | Central Valley
23600 | x | x |  |  | 2025-06-12 | Jun | 6 | 2025 | 122134 |  |  | San Mateo | Central Coast | Colma | Central | Pacifica | Yes | Homeowner damaged 1/2" plastic gas service line with an auger while replacing a retaining wall. No 811 ticket. | No | Gas Line | Yes | Auger | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122134 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-12 | ½” | 18 | 44 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  |  | No | Bay Area | Bay Area
23601 |  | x |  |  | 2025-06-12 | Jun | 6 | 2025 | 122100 |  |  | Marin | North Coast | Marin | North | Novato | Yes | West Valley Construction was doing 2nd party gas work for PG&E when they damaged a 3/4" steel gas service line with drilling equipment. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Drilling Equipment | Gas | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025042900171 | Dig-In to PG&E Underground | 2nd Party-Contractor | West Valley Construction | Distribution Service | 122100 | No | N/A |  | 2025 Q2 | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2025-06-12 | ¾” | 12 | 62 | N/A | 6 | Jun | 2025 |  | 174968 | No | North Coast | North Coast
23602 | x | x |  |  | 2025-06-12 | Jun | 6 | 2025 | 122143 |  |  | Sonoma | Northern | Sonoma | North | Sonoma | Yes | Ryan Alforo damaged 1/2" plastic gas service line with a stake while doing fencing work. No 811 ticket. | No | Gas Line | Yes | Stake | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Ryan Alforo | Distribution Service | 122143 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-12 | ½” | 25 | 157 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  |  | Yes | North Coast | North Coast
23603 | x | x | x |  | 2025-06-12 | Jun | 6 | 2025 | 122123 |  | 131357993 | Santa Cruz | Central Coast | Central Coast | South | Freedom | Yes | McKim Corporation damaged a 3/4" steel fitting attached to the top of a 4" gas main with a skid steer while doing soil conditioning work on a roadway. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Skid Steer | Road Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025031201733 | Dig-In to PG&E Underground | 3rd Party-Contractor | McKim Corporation | Distribution Main | 122123 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-12 | 4"" | 24 | 261 | N/A | 6 | Jun | 2025 |  |  | No | South Bay & Central Coast | South Bay & Central Coast
23604 | x | x |  |  | 2025-06-12 | Jun | 6 | 2025 | 122133 |  |  | Kern | Central Valley | Kern | South | Bakersfield | Yes | AJ Netcon damaged 1/2" plastic gas service line with boring equipment while installing telecommunication lines for AT&T. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Boring Equipment | Telecommunications | Failed to Dig with Care | Yes | 2025060100398 | Dig-In to PG&E Underground | 3rd Party-Contractor | AJ Netcon | Distribution Service | 122133 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-12 | ½” | 38 | 14 | N/A | 6 | Jun | 2025 |  | 1031414 | No | Central Valley | Central Valley
23605 |  | x |  |  | 2025-06-13 | Jun | 6 | 2025 | OIS 2790327 |  |  | Santa Clara | Central Coast | De Anza | Central | Los Altos Hills | No | Unknown party damaged secondary electric with an unknown tool at an unknown time. PG&E discovered the damage. Root cause will be no 811 ticket. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Unknown | Unknown | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unknown | Electric | OIS 2790327 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-06-13 |  |  | 0 | Other | 6 | Jun | 2025 |  |  | No | South Bay & Central Coast | South Bay & Central Coast
23606 | x | x | x |  | 2025-06-13 | Jun | 6 | 2025 | 122165 |  | 131363904 | Fresno | Central Valley | Fresno | South | Kerman | Yes | Rakkar Development & Construction damaged 1/2" plastic gas service line with a shovel while installing new electric conduit. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | 2025051601397 | Dig-In to PG&E Underground | 3rd Party-Contractor | Rakkar Development & Construction | Distribution Service | 122165 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-13 | ½” | 28 | 55 | N/A | 6 | Jun | 2025 |  | 1037594 | Yes | Central Valley | Central Valley
23607 | x | x | x |  | 2025-06-13 | Jun | 6 | 2025 | 122187 |  | 131364223 | Sonoma | Northern | Sonoma | North | Healdsburg | Yes | GTZ Fences damaged 1" plastic gas service line with a post-hole digger while installing a fence. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Post-Hole Digger | Fencing | Failed to Dig with Care | Yes | 2025060903857 | Dig-In to PG&E Underground | 3rd Party-Contractor | GTZ Fences | Distribution Service | 122187 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-13 | 1” | 31 | 74 | N/A | 6 | Jun | 2025 |  | 1115412 | Yes | North Coast | North Coast
23608 | x | x | x |  | 2025-06-13 | Jun | 6 | 2025 | 122157 |  | 131362524 | Solano | Northern | North Bay | North | Vacaville | Yes | American Underground damaged a 2" plastic gas main with an excavator while doing electric work. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Electric Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025060501522 | Dig-In to PG&E Underground | 3rd Party-Contractor | American Underground | Distribution Main | 122157 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-13 | 2” | 44 | 62 | N/A | 6 | Jun | 2025 |  | 940759 | No | North Coast | North Coast
23609 | x | x | x |  | 2025-06-13 | Jun | 6 | 2025 | 122181 |  | 131364297 | Sacramento | Northern | Sacramento | North | Elk Grove | Yes | Juan Excavator Services damaged a 2" plastic gas main with an excavator while doing water work. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025060903049 | Dig-In to PG&E Underground | 3rd Party-Contractor | Juan Excavator Services | Distribution Main | 122181 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-13 | 2” | 36 | 77 | N/A | 6 | Jun | 2025 |  | 1040408 | No | North Valley & Sierra | North Valley & Sierra
23610 | x | x | x |  | 2025-06-16 | Jun | 6 | 2025 | 122275 |  | 131369428 | Contra Costa | Bay Area | Diablo | South | Walnut Creek | Yes | JRP Concrete Construction damaged 1" plastic gas service line with a jackhammer while building a new foundation. No 811 ticket. | No | Gas Line | Yes | Jackhammer | Foundation Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | JRP Concrete Construction | Distribution Service | 122275 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-16 | 1” | 24 | 29 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  | 1094981 | No | Bay Area | Bay Area
23611 | x | x | x |  | 2025-06-16 | Jun | 6 | 2025 | 122277 |  | 131369429 | San Mateo | Central Coast | Belmont | Central | Belmont | Yes | National Paver Systems, Inc. damaged 1/2" plastic gas service line with a pickaxe while preparing an area for a new sidewalk. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Pickaxe | Curb/Sidewalk Work | Failed to Dig with Care | Yes | 2025053002058 | Dig-In to PG&E Underground | 3rd Party-Contractor | National Paver Systems, Inc. | Distribution Service | 122277 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-16 | ½” | 18 | 41 | N/A | 6 | Jun | 2025 |  | 1005674 | Yes | Bay Area | Bay Area
23612 | x | x | x |  | 2025-06-16 | Jun | 6 | 2025 | 122272 |  | 131368875 | Butte | Northern | North Valley | North | Paradise | Yes | West Coast Pipeline Solution Inc. damaged a 2" plastic gas main with an excavator while installing telecommunication conduit. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025051903272 | Dig-In to PG&E Underground | 3rd Party-Contractor | West Coast Pipeline Solution Inc. | Distribution Main | 122272 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-16 | 2” | 38 | 34 | N/A | 6 | Jun | 2025 |  | 1054122 | No | North Valley & Sierra | North Valley & Sierra
23613 | x | x | x |  | 2025-06-16 | Jun | 6 | 2025 | 122284 |  | 131369779 | Contra Costa | Bay Area | Diablo | South | Lafayette | Yes | Fusion Electric damaged 1/2" plastic gas service line with a shovel while upgrading an electric service. No 811 ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Fusion Electric | Distribution Service | 122284 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-16 | ½” | 16 | 8 | Excavator Did Not Believe a USA Ticket was Required | 6 | Jun | 2025 |  | 1010951 | Yes | Bay Area | Bay Area
23614 | x | x | x |  | 2025-06-17 | Jun | 6 | 2025 | 122320 |  | 131376626 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | Unlicensed contractor damaged 1/2" plastic gas service line with a shovel while installing a fence. No 811 ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service | 122320 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-17 | ½” | 25 | 45 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  |  | Yes | South Bay & Central Coast | South Bay & Central Coast
23615 | x | x | x |  | 2025-06-17 | Jun | 6 | 2025 | 122340 |  | 131377664 | Marin | North Coast | Marin | North | Sausalito | Yes | Kenwood Fence Company damaged 1/2" plastic gas service line with a post-hole digger while installing a fence. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Post-Hole Digger | Fencing | Failed to Dig with Care | Yes | 2025060601836 | Dig-In to PG&E Underground | 3rd Party-Contractor | Kenwood Fence Company | Distribution Service | 122340 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-17 | ½” | 14 | 38 | N/A | 6 | Jun | 2025 |  | 608869 | Yes | North Coast | North Coast
23616 | x | x | x |  | 2025-06-17 | Jun | 6 | 2025 | 122346 |  | 131378255 | Marin | North Coast | Marin | North | Mill Valley | Yes | Cole Crew Construction damaged 1/2" plastic gas service line with a shovel while building a new retaining wall. No 811 ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Cole Crew Construction | Distribution Service | 122346 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-17 | ½” | 30 | 29 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  | 1041675 | Yes | North Coast | North Coast
23617 | x | x | x |  | 2025-06-17 | Jun | 6 | 2025 | 122327 |  | 131376724 | Marin | North Coast | Marin | North | Corte Madera | Yes | Unlicensed contractor damaged 1" plastic gas service line with a shovel while planting plants. No 811 ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service | 122327 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-17 | 1” | 10 | 57 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  |  | Yes | North Coast | North Coast
23618 | x | x | x |  | 2025-06-17 | Jun | 6 | 2025 | 122302 |  | 131375937 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Shoreline Electric damaged 1/2" plastic gas service line with a shovel while installing a residential electric facility. No 811 ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Shoreline Electric | Distribution Service | 122302 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-17 | ½” | 12 | 37 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  | 839865 | Yes | South Bay & Central Coast | South Bay & Central Coast
23619 | x | x | x |  | 2025-06-17 | Jun | 6 | 2025 | 122295 |  | 131375230 | San Joaquin | Central Valley | Stockton | South | Stockton | Yes | SV Construction Inc. damaged 1/2" plastic gas service line with a shovel while building a concrete box for a fire hydrant. No 811 ticket. There were marks present for another contractor that were accurate so primary cause of incident is failed to dig with care | No | Gas Line | Yes | Shovel | Water | Failed to Dig with Care | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | SV Construction Inc. | Distribution Service | 122295 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-17 | ½” | 36 | 19 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 6 | Jun | 2025 |  |  | Yes | Central Valley | Central Valley
23620 | x | x | x |  | 2025-06-17 | Jun | 6 | 2025 | 122297 |  | 131375271 | Fresno | Central Valley | Fresno | South | Fresno | Yes | Lasar Underground Construction damaged 1/2" plastic gas service line with a shovel while installing new fiber optic telecommunication lines. Valid 811 ticket. Failed to maintain marks | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | 2025052801213 | Dig-In to PG&E Underground | 3rd Party-Contractor | Lasar Underground Construction Inc. | Distribution Service | 122297 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-17 | ½” | 32 | 17 | N/A | 6 | Jun | 2025 |  | 614677 | Yes | Central Valley | Central Valley
23621 | x | x | x |  | 2025-06-17 | Jun | 6 | 2025 | 122336 |  | 131377461 | Sacramento | Northern | Sacramento | North | Citrus Heights | Yes | Dirt Movers Inc. damaged 1" plastic gas service line with an excavator while widening a road. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Road Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2024042902483 | Dig-In to PG&E Underground | 3rd Party-Contractor | Dirt Movers Inc | Distribution Service | 122336 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-17 | 1” | 36 | 19 | N/A | 6 | Jun | 2025 |  | 612990 | No | North Valley & Sierra | North Valley & Sierra
23622 | x | x | x |  | 2025-06-17 | Jun | 6 | 2025 | 122348 |  | 131378335 | San Joaquin | Central Valley | Stockton | South | Stockton | Yes | Homeowner damaged 1/2" plastic gas service line with a post-hole digger while installing a new fence. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122348 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-17 | ½” | 37 | 53 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  |  | Yes | Central Valley | Central Valley
23623 | x | x | x |  | 2025-06-18 | Jun | 6 | 2025 | 122390 |  | 131382588 | Merced | Central Valley | Yosemite | South | Merced | Yes | I Ramirez Corporation damaged 1" plastic gas service line with a shovel while installing telecommunication lines. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Telecommunications | Failed to Dig with Care | Yes | 2025052801600 | Dig-In to PG&E Underground | 3rd Party-Contractor | I Ramirez Corporation | Distribution Service | 122390 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-18 | 1” | 32 | 10 | N/A | 6 | Jun | 2025 |  | 714986 | Yes | Central Valley | Central Valley
23624 |  | x |  |  | 2025-06-18 | Jun | 6 | 2025 | OIS 2811746 |  |  | Stanislaus | Central Valley | Yosemite | South | Oakdale | No | United Pavement Maintenance Inc. damaged secondary electric with a shovel while doing a sewer pipe installation. Valid 811 ticket. Failed to dig with care. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Shovel | Sewer | Failed to Dig with Care | Yes | 2025050703731 | Dig-In to PG&E Underground | 3rd Party-Contractor | United Pavement Maintenance Inc. | Electric | OIS 2811746 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-06-18 |  | 33 | 0 | N/A | 6 | Jun | 2025 |  | 905503 | Yes | Central Valley | Central Valley
23625 | x | x | x |  | 2025-06-18 | Jun | 6 | 2025 | 122354 |  | 131380725 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Century Pools damaged 1/2" plastic gas service line with an excavator while installing a in-ground swimming pool. No 811 ticket. | No | Gas Line | Yes | Excavator | Other | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Century Pools | Distribution Service | 122354 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-18 | ½” | 24 | 1 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  | 1111908 | No | North Valley & Sierra | North Valley & Sierra
23626 | x | x |  |  | 2025-06-18 | Jun | 6 | 2025 | 122372 |  |  | Contra Costa | Bay Area | Diablo | South | Concord | Yes | Tennyson Electric damaged 1/2" plastic gas service line inserted into 3/4" steel with an excavator while installing electric lines for streetlights. Valid 811 ticket. PG&E at-fault - Locator Error - Mismark | No | Gas Line | Yes | Excavator | Street Light Work | Incorrect Information or Marks | Yes | 2025042102059 | Dig-In to PG&E Underground | 3rd Party-Contractor | Tennyson Electric | Distribution Service |  | Yes | Locator Error - Mismark | Did Not Locate A to B and B to A | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-18 | ½” | 30 | 14 | N/A | 6 | Jun | 2025 | Bargaining Unit | 717998 | No | Bay Area | Bay Area
23627 |  | x |  |  | 2025-06-18 | Jun | 6 | 2025 | 122387 |  |  | San Joaquin | Central Valley | Stockton | South | Stockton | No | United Paving Maintenance Inc. damaged a cathodic protection wire with an excavator while doing curb/sidewalk work. Valid 811 ticket. PG&E at-fault - Locator Error - Mismark. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Excavator | Curb/Sidewalk Work | Incorrect Information or Marks | Yes | 2025031400140 | Dig-In to PG&E Underground | 3rd Party-Contractor | United Pavement Maintenance Inc. | Electric |  | Yes | Locator Error - Mismark | Training Issue | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-06-18 |  | 12 | 0 | N/A | 6 | Jun | 2025 | Bargaining Unit | 905503 | No | Central Valley | Central Valley
23628 | x |  | x |  | 2025-06-18 | Jun | 6 | 2025 | 122389 | 47238293 | 131384968 | Alameda | Bay Area | Mission | South | Fremont | Yes | Fix-it Plumbing damaged 1" plastic gas service line with a shovel while doing sewer work. Valid 811 ticket. PG&E at-fault - Locator Error - Mismark | No | Gas Line | Yes | Shovel | Sewer | Incorrect Information or Marks | Yes | 2025060302960 | Dig-In to PG&E Underground | 3rd Party-Contractor | Fix-It Plumbing | Distribution Service |  | Yes | Locator Error - Mismark | Did Not Mark Size/Type | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-18 | 1” | 24 | 36 | N/A | 6 | Jun | 2025 | Bargaining Unit | 90605 | Yes | Bay Area | Bay Area
23629 | x | x | x |  | 2025-06-18 | Jun | 6 | 2025 | 122384 |  | 131382350 | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Michael O'Shaughnessy Construction damaged 1/2" plastic gas service line with a shovel while building a bus pad. Expired 811 ticket. Marks were still visible and accurate so primary cause of incident is failed to dig with care | No | Gas Line | Yes | Shovel | Road Work | Failed to Dig with Care | No (expired) | 2025042402115 | Dig-In to PG&E Underground | 3rd Party-Contractor | Michael O'Shaughnessy Construction | Distribution Service | 122384 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-18 | ½” | 36 | 14 | Expired USA Ticket | 6 | Jun | 2025 |  | 984235 | Yes | Bay Area | Bay Area
23630 | x | x | x |  | 2025-06-18 | Jun | 6 | 2025 | 122396 |  | 131383282 | Marin | North Coast | Marin | North | San Anselmo | Yes | Glosage Engineering damaged 1/2" plastic gas service line with a shovel while replacing a sewer lateral. Valid 811 ticket. PG&E at-fault - Other Error - Construction Error | No | Gas Line | Yes | Shovel | Sewer | Other Error | Yes | 2025052003427 | Dig-In to PG&E Underground | 3rd Party-Contractor | Glosage Engineering, Inc. | Distribution Service |  | Yes | Other Error | Construction Error | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-18 | ½” | 32 | 24 | N/A | 6 | Jun | 2025 |  | 1028046 | Yes | North Coast | North Coast
23631 | x |  | x |  | 2025-06-18 | Jun | 6 | 2025 | 122393 |  | 131383179 | Merced | Central Valley | Yosemite | South | Gustine | Yes | Dandy Construction damaged a 2" plastic gas main with boring equipment while doing telcommunications work. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Boring Equipment | Telecommunications | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025060500056 | Dig-In to PG&E Underground | 3rd Party-Contractor | Dandy Construction | Distribution Main | 122393 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-18 | 2” | 50 | 119 | N/A | 6 | Jun | 2025 |  | 1103061 | No | Central Valley | Central Valley
23632 | x | x | x |  | 2025-06-18 | Jun | 6 | 2025 | 122383 |  | 131381952 | Stanislaus | Central Valley | Yosemite | South | Empire | Yes | Homeowner damaged 1/2" plastic gas service line with a shovel while installing an electric panel at a residence. No 811 ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122383 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-18 | ½” | 40 | 23 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  |  | Yes | Central Valley | Central Valley
23633 | x | x |  |  | 2025-06-18 | Jun | 6 | 2025 | 122386 |  |  | Marin | North Coast | Marin | North | Fairfax | Yes | Westward Builders damaged 1/2" plastic gas service line with an auger while replacing a retaining wall. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Auger | Landscaping | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025052702190 | Dig-In to PG&E Underground | 3rd Party-Contractor | Westward Builders Inc | Distribution Service | 122386 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-18 | 1” | 32 | 7 | N/A | 6 | Jun | 2025 |  | 1049996 | No | North Coast | North Coast
23634 | x | x | x |  | 2025-06-19 | Jun | 6 | 2025 | 122422 |  | 131384772 | Monterey | Central Coast | Central Coast | South | Seaside | Yes | Unlicensed contractor damaged a 3/4" steel gas service line with a post-hole digger while doing fencing work. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service | 122422 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-19 | ¾” | 28 | 65 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  |  | Yes | South Bay & Central Coast | South Bay & Central Coast
23635 | x | x | x |  | 2025-06-19 | Jun | 6 | 2025 | 122413 |  | 131384367 | Santa Cruz | Central Coast | Central Coast | South | Boulder Creek | Yes | Tom's Septic Construction damaged 1/2" plastic gas service line with a shovel while working on a septic system. No 811 ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Tom’s Septic Construction | Distribution Service | 122413 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-19 | ½” | 12 | 54 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  | 406512 | Yes | South Bay & Central Coast | South Bay & Central Coast
23636 | x | x |  |  | 2025-06-19 | Jun | 6 | 2025 | 122421 |  |  | Alameda | Bay Area | Oakland | Central | Oakland | Yes | Delta Bay Electric damaged 1/2" plastic gas service line with a shovel while doing electric work. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | 2025052301056 | Dig-In to PG&E Underground | 3rd Party-Contractor | Delta Bay Electric | Distribution Service | 122421 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-19 | ½” | 24 | 17 | N/A | 6 | Jun | 2025 |  | 1107405 | Yes | Bay Area | Bay Area
23637 | x | x | x |  | 2025-06-19 | Jun | 6 | 2025 | 122434 |  | 131385079 | Butte | Northern | North Valley | North | Chico | Yes | Homeowner damaged 1/2" plastic gas service line with a post-hole digger while installing a fence post. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122434 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-19 | ½” | 26 | 21 | Believed they knew where underground utility was from previous knowledge | 6 | Jun | 2025 |  |  | Yes | North Valley & Sierra | North Valley & Sierra
23638 | x | x | x |  | 2025-06-19 | Jun | 6 | 2025 | 122428 |  | 131384893 | Butte | Northern | North Valley | North | Chico | Yes | Pavement Recylclers damaged 3/4" steel gas service line with a grader while installing new asphalt. No 811 ticket. | No | Gas Line | Yes | Grader/Scraper | Road Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Franklin Construction | Distribution Service | 122428 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-19 | ¾” | 14 | 73 | N/A | 6 | Jun | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23639 | x | x | x |  | 2025-06-20 | Jun | 6 | 2025 | 122468 |  | 131388258 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Unlicensed contractor damaged 1/2" plastic gas service line inserted into 1 1/4" steel with a jackhammer while installing a fence. No 811 ticket. | No | Gas Line | Yes | Jackhammer | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service | 122468 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-20 | ½” | 19 | 42 | Other | 6 | Jun | 2025 |  |  | No | North Valley & Sierra | North Valley & Sierra
23640 | x | x | x |  | 2025-06-20 | Jun | 6 | 2025 | 122471 |  | 131388096 | Sacramento | Northern | Sacramento | North | Sacramento | Yes | Core Construction Inc damaged 1 1/4" plastic gas service line with an excavator while installing new irrigation facilities. Valid 811 ticket. Failed to maintain marks | No | Gas Line | Yes | Excavator | Irrigation | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | 2025012902499 | Dig-In to PG&E Underground | 3rd Party-Contractor | Core Construction Inc | Distribution Service | 122471 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-20 | 1 ¼” | 29 | 32 | N/A | 6 | Jun | 2025 |  | 166249 | No | North Valley & Sierra | North Valley & Sierra
23641 | x | x | x |  | 2025-06-20 | Jun | 6 | 2025 | 122474 |  | 131388168 | San Mateo | Central Coast | Belmont | Central | Hillsborough | Yes | Bayval Electric damaged 1/2" plastic gas service line with a shovel while installing a new electrical panel. Expired 811 ticket. Marks were still visible and accurate so primary cause of incident is failed to dig with care | No | Gas Line | Yes | Shovel | Electric Work | Failed to Dig with Care | Yes | 2025021200252 | Dig-In to PG&E Underground | 3rd Party-Contractor | Bayval Electric | Distribution Service | 122474 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-20 | ½” | 18 | 18 | N/A | 6 | Jun | 2025 |  | 1100396 | Yes | Bay Area | Bay Area
23642 | x | x | x |  | 2025-06-21 | Jun | 6 | 2025 | 122506 |  | 131389810 | Merced | Central Valley | Yosemite | South | Livingston | Yes | Homeowner damaged a 1 1/4' plastic gas main with a post-hole digger while installing a fence. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Main | 122506 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-21 | 1 ¼” | 36 | 93 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  |  | Yes | Central Valley | Central Valley
23643 | x | x | x |  | 2025-06-21 | Jun | 6 | 2025 | 122505 |  | 131389615 | Humboldt | Northern | Humboldt | North | Eureka | Yes | Homeowner damaged 1" plastic gas service line with an excavator while installing a patio. No 811 ticket. | No | Gas Line | Yes | Excavator | Blading/Lot Grading | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122505 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-21 | 1” | 18 | 16 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  |  | No | North Coast | North Coast
23644 |  | x |  |  | 2025-06-21 | Jun | 6 | 2025 | OIS 2815301 |  |  | Shasta | Northern | North Valley | North | Hat Creek | No | Marc’s Plumbing Company damaged 4/0 secondary electric with a backhoe while doing residential sewer work. No 811 ticket. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Backhoe/Trackhoe | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Marc’s Plumbing Company | Electric | OIS 2815301 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-06-21 |  |  | 0 | Other | 6 | Jun | 2025 |  | 591154 | No | North Valley & Sierra | North Valley & Sierra
23645 | x | x | x |  | 2025-06-21 | Jun | 6 | 2025 | 122511 |  | 131390675 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | BD Home Group damaged 1/2" plastic gas service line with a shovel while installing electric conduit. No 811 ticket. | No | Gas Line | Yes | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | BD Home Group Inc. | Distribution Service | 122511 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-21 | 1” | 29 | 25 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 6 | Jun | 2025 |  | 111955 | Yes | South Bay & Central Coast | South Bay & Central Coast
23646 | x | x |  |  | 2025-06-22 | Jun | 6 | 2025 | 122523 |  |  | Alameda | Bay Area | Mission | South | Hayward | Yes | Homeowner damaged 1" plastic gas service line with a post-hole digger while installing a fence. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122523 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-22 | 1” |  | 34 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  |  | Yes | Bay Area | Bay Area
23647 | x | x |  |  | 2025-06-23 | Jun | 6 | 2025 | 122542 |  |  | Contra Costa | Bay Area | Diablo | South | Walnut Creek | Yes | FJ&I Engineering Inc. damaged 1/2" plastic gas service line inserted into 3/4" steel with an excavator while installing a storm drain. Valid 811 ticket. PG&E at-fault - Other Error | No | Gas Line | Yes | Excavator | Drainage Work | Other Error | Yes | 2025051900884 | Dig-In to PG&E Underground | 3rd Party-Contractor | FJ&I Engineering Inc. | Distribution Service |  | Yes | Other Error | Construction Error | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-23 |  | 20 | 8 | N/A | 6 | Jun | 2025 |  |  | No | Bay Area | Bay Area
23648 | x | x | x |  | 2025-06-23 | Jun | 6 | 2025 | 122582 |  | 131395518 | Humboldt | Northern | Humboldt | North | Eureka | Yes | Curb Appeal Construction damaged 1/2" plastic gas service line with a jackhammer while replacing a sidewalk. No 811 ticket. | No | Gas Line | Yes | Jackhammer | Curb/Sidewalk Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Curb Appeal Construction | Distribution Service | 122582 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-23 | ½” | 24 | 14 | Believed they knew where underground utility was from previous knowledge | 6 | Jun | 2025 |  | 907424 | No | North Coast | North Coast
23649 |  | x |  |  | 2025-06-23 | Jun | 6 | 2025 | OIS 2817024 |  |  | Fresno | Central Valley | Fresno | South | Five Points | No | Borba Farms damaged 4-1/0 secondary with a backhoe while creating a drainage sump. No 811 ticket. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Backhoe/Trackhoe | Drainage Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Electric | OIS 2817024 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Electric | Yes | 2025-06-23 |  |  | 0 | Excavator Did Not Believe a USA Ticket was Required | 6 | Jun | 2025 |  |  | No | Central Valley | Central Valley
23650 | x | x | x |  | 2025-06-23 | Jun | 6 | 2025 | 122544 |  | 131393576 | Stanislaus | Central Valley | Yosemite | South | West Modesto | Yes | Hensel & Castillo Fencing Inc. damaged a 1/2" plastic gas service line with a post-hole digger while installing a fence. Valid 811 ticket. Excavated prior to receiving a positive response | No | Gas Line | Yes | Post-Hole Digger | Fencing | Excavated Prior to Receiving a Positive Response From All Utilities | Yes | 2025061800772 | Dig-In to PG&E Underground | 3rd Party-Contractor | Hensel & Castillo Fencing , Inc. | Distribution Service | 122544 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-23 | ½” | 24 | 20 | N/A | 6 | Jun | 2025 |  | 1075455 | Yes | Central Valley | Central Valley
23651 | x | x |  |  | 2025-06-23 | Jun | 6 | 2025 | 122571 |  |  | Sacramento | Northern | Sacramento | North | Sacramento | Yes | ASTA Construction damaged a 1 1/4" plastic gas service line with an excavator while doing water work. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Water | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2024100401076 | Dig-In to PG&E Underground | 3rd Party-Contractor | ASTA Construction Co Inc | Distribution Service | 122571 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-23 | 1 ½” | 21 | 9 | N/A | 6 | Jun | 2025 |  | 247178 | No | North Valley & Sierra | North Valley & Sierra
23652 |  | x |  |  | 2025-06-23 | Jun | 6 | 2025 | OIS 2816142 |  |  | San Mateo | Central Coast | Belmont | Central | Foster City | No | Smelly Mel’s Plumbing Inc damaged secondary electric with a shovel while replacing a water service. Valid 811 ticket. Failed to dig with care. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Shovel | Water | Failed to Dig with Care | Yes | 2025032702481 | Dig-In to PG&E Underground | 3rd Party-Contractor | Smelly Mel’s Plumbing and Septic | Electric | OIS 2816142 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-06-23 |  | 24 | 0 | N/A | 6 | Jun | 2025 |  | 786183 | Yes | Bay Area | Bay Area
23653 | x |  |  |  | 2025-06-23 | Jun | 6 | 2025 | 122568 |  |  | Fresno | Central Valley | Fresno | South | Fresno | Yes | Unknown party damaged 1 1/4" plastic gas main. Damage was discovered by another contractor. Root cause will be no 811 ticket. | No | Gas Line | No | Unknown | Unknown | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unknown | Distribution Main | 122568 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-23 | 1 ¼” |  | 0 | Other | 6 | Jun | 2025 |  |  | No | Central Valley | Central Valley
23654 | x | x | x |  | 2025-06-23 | Jun | 6 | 2025 | 122557 | 47239105 | 131394470 | Marin | North Coast | Marin | North | San Rafael | Yes | Unlicensed contractor damaged 1/2" plastic gas service line inserted into 3/4" steel with a digging bar while replacing a fence. No 811 ticket. | No | Gas Line | Yes | Digging Bar | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service | 122557 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-23 |  | 28 | 36 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  |  | Yes | North Coast | North Coast
23655 | x | x | x |  | 2025-06-23 | Jun | 6 | 2025 | 122543 | 47239019 | 131393776 | Marin | North Coast | Marin | North | Mill Valley | Yes | AB III Inc damaged 1" plastic gas service line with a grounding rod while doing a telecommunication work. No 811 ticket. | No | Gas Line | Yes | Grounding Rod | Telecommunications | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | AB III Inc | Distribution Service | 122543 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-23 | 1” | 23 | 61 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  | 1026584 | Yes | North Coast | North Coast
23656 | x |  | x |  | 2025-06-24 | Jun | 6 | 2025 | 122600 |  | 131397223 | Sonoma | Northern | Sonoma | North | Santa Rosa | Yes | Homeowner damaged 1/2" plastic gas service line with a pickaxe while installing fiber. Expired 811 ticket. Marks were no longer visible so primary cause of incident is no 811 ticket | No | Gas Line | Yes | Pickaxe | Telecommunications | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122600 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-24 | ½” | 36 | 32 | Other | 6 | Jun | 2025 |  |  | Yes | North Coast | North Coast
23657 | x | x | x |  | 2025-06-24 | Jun | 6 | 2025 | 122606 |  | 131397490 | San Mateo | Central Coast | Colma | Central | Burlingame | Yes | J Moraga Construction damaged a 2" steel main with a trencher while doing telecommunication conduit installation. Valid 811 ticket. PG&E at-fault - Locator Error - No Mark | No | Gas Line | Yes | Trencher | Telecommunications | Facility was not Located or Marked | Yes | 2025061601719 | Dig-In to PG&E Underground | 3rd Party-Contractor | J Moraga Construction | Distribution Main |  | Yes | Locator Error - No Mark | Did not mark locatable facility | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-24 | 2” | 18 | 90 | N/A | 6 | Jun | 2025 | Bargaining Unit | 882920 | No | Bay Area | Bay Area
23658 | x | x |  |  | 2025-06-24 | Jun | 6 | 2025 | 122610 |  |  | Contra Costa | Bay Area | Diablo | South | Concord | Yes | TAK Broadband CA LLC damaged 1/2" plastic gas service line with a shovel while doing telecommunications conduit repair. No 811 ticket. | No | Gas Line | Yes | Shovel | Telecommunications | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | TAK Broadband CA LLC | Distribution Service | 122610 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-24 | ½” | 42 | 32 | Excavator Did Not Believe a USA Ticket was Required | 6 | Jun | 2025 |  | 1042947 | Yes | Bay Area | Bay Area
23659 |  | x |  |  | 2025-06-24 | Jun | 6 | 2025 | 31740577 |  |  | San Francisco | Bay Area | San Francisco | Central | San Francisco | No | Unknown party damaged electrical conduit at an unknown date with an unknown tool doing unknown work. Root cause will be no 811 ticket. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Unknown | Unknown | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unknown | Electric | 31740577 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-06-24 |  | 27 | 0 | Other | 6 | Jun | 2025 |  |  | No | Bay Area | Bay Area
23660 | x | x | x |  | 2025-06-24 | Jun | 6 | 2025 | 122624 |  | 131399041 | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | Eagle's Plumbing damaged 1/2" plastic gas service line with a digging bar while locating a water line. No 811 ticket. | No | Gas Line | Yes | Digging Bar | Water | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Eagle’s Plumbing | Distribution Service | 122624 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-24 | ½” | 27 | 42 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  |  | Yes | South Bay & Central Coast | South Bay & Central Coast
23661 |  | x |  |  | 2025-06-25 | Jun | 6 | 2025 | OIS 2819037 |  |  | Fresno | Central Valley | Fresno | South | Kerman | No | Homeowner damaged 4/0 aluminum triplex with a backhoe while installing a propane line. No 811 ticket. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Backhoe/Trackhoe | Other | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Electric | OIS 2819037 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Electric | Yes | 2025-06-25 |  |  | 0 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  |  | No | Central Valley | Central Valley
23662 | x | x | x |  | 2025-06-25 | Jun | 6 | 2025 | 122644 |  | 131401719 | Placer | Northern | Sierra | North | Auburn | Yes | J.R. Pierce Plumbing Company damaged a 2" plastic gas main with a pickaxe while installing a sewer line. No 811 ticket. | No | Gas Line | Yes | Pickaxe | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | J.R. Pierce Plumbing Company | Distribution Main | 122644 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-25 | 2” | 31 | 52 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  | 223657 | Yes | North Valley & Sierra | North Valley & Sierra
23663 | x |  | x |  | 2025-06-25 | Jun | 6 | 2025 | 122679 |  | 131404189 | Contra Costa | Bay Area | Diablo | South | Oakley | Yes | Homeowner damaged 1/2" plastic gas service line with a post-hole digger while installing a new fence. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122679 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-25 | ½” | 38 | 58 | Other | 6 | Jun | 2025 |  |  | Yes | Bay Area | Bay Area
23664 | x | x | x |  | 2025-06-25 | Jun | 6 | 2025 | 122663 |  | 131402703 | Kern | Central Valley | Kern | South | Bakersfield | Yes | MasTec damaged a 2" plastic gas main with an excavator while installing a telecommunication junction box. No 811 ticket. | No | Gas Line | Yes | Excavator | Telecommunications | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | MasTec | Distribution Main | 122663 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-25 | 2” | 36 | 29 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 6 | Jun | 2025 |  | 984138 | No | Central Valley | Central Valley
23665 | x | x | x |  | 2025-06-25 | Jun | 6 | 2025 | 122648 |  | 131402021 | Sonoma | Northern | Sonoma | North | Petaluma | Yes | Homeowner damaged 1" plastic gas service line with a post-hole digger while installing a gate. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122648 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-25 | 1” | 20 | 1 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  |  | Yes | North Coast | North Coast
23666 | x | x |  |  | 2025-06-25 | Jun | 6 | 2025 | 122647 |  |  | Sacramento | Northern | Sacramento | North | Citrus Heights | Yes | Greystone Landscaping damaged 1" plastic gas service line with a shovel while installing a retaining wall. No 811 ticket. | No | Gas Line | Yes | Shovel | Landscaping | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Greystone Landscaping | Distribution Service | 122647 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-25 | 1” | 24 | 38 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  | 994405 | Yes | North Valley & Sierra | North Valley & Sierra
23667 | x | x | x |  | 2025-06-25 | Jun | 6 | 2025 | 122636 |  | 131401203 | Santa Cruz | Central Coast | Central Coast | South | Aptos | Yes | Mr Rooter Plumbing damaged 1/2" plastic gas service line with a shovel while repairing a sewer lateral. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Sewer | Failed to Dig with Care | Yes | 2025061903000 | Dig-In to PG&E Underground | 3rd Party-Contractor | Mr Rooter Plumbing | Distribution Service | 122636 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-25 | ½” | 51 | 22 | N/A | 6 | Jun | 2025 |  | 903756 | Yes | South Bay & Central Coast | South Bay & Central Coast
23668 | x |  | x |  | 2025-06-26 | Jun | 6 | 2025 | 122690 |  | 131405742 | Napa | Bay Area | North Bay | North | American Canyon | Yes | Ghilotti Construction damaged a 3/4" steel gas service line with an excavator while doing curb/sidewalk work. Valid 811 ticket. Failed to maintain marks | No | Gas Line | Yes | Excavator | Curb/Sidewalk Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Ghilotti Construction | Distribution Service | 122690 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-26 | ¾” | 14 | 53 | N/A | 6 | Jun | 2025 |  |  | No | North Coast | North Coast
23669 | x | x | x |  | 2025-06-26 | Jun | 6 | 2025 | 122708 |  | 131407276 | Santa Cruz | Central Coast | Central Coast | South | Santa Cruz | Yes | Homeowner damaged 1/2" plastic gas service line with a digging bar while installing a mailbox post. No 811 ticket. | No | Gas Line | Yes | Digging Bar | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122708 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-26 | ½” | 19 | 83 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  |  | Yes | South Bay & Central Coast | South Bay & Central Coast
23670 | x | x | x |  | 2025-06-26 | Jun | 6 | 2025 | 122695 |  | 131405840 | Marin | North Coast | Marin | North | Mill Valley | Yes | Shark's Plumbing damaged 1/2" plastic gas service line with a hammer while doing a water line installation. Expired 811 ticket. Marks were still visible and accurate so primary cause of incident is failed to dig with care | No | Gas Line | Yes | Other Hand Tools | Water | Failed to Dig with Care | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Sharks Plumbing | Distribution Service | 122695 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-26 | ½” | 32 | 35 | Knew about USA ticket requirement but chose not to call | 6 | Jun | 2025 |  | 1101254 | Yes | North Coast | North Coast
23671 | x | x |  |  | 2025-06-26 | Jun | 6 | 2025 | 122692 |  |  | Sacramento | Northern | Sacramento | North | Antelope | Yes | American Home Energy Savers damaged 1/2" plastic gas service line with a pickaxe while doing an electrical panel upgrade. Expired 811 ticket. Marks were still visible and accurate so primary cause of incident is failed to dig with care | No | Gas Line | Yes | Pickaxe | Electric Work | Failed to Dig with Care | No (expired) | 2025051402899 | Dig-In to PG&E Underground | 3rd Party-Contractor | American Home Energy Savers | Distribution Service | 122692 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-26 | ½” | 33 | 35 | Expired USA Ticket | 6 | Jun | 2025 |  | 1023076 | Yes | North Valley & Sierra | North Valley & Sierra
23672 | x | x |  |  | 2025-06-26 | Jun | 6 | 2025 | 122699 |  |  | Sacramento | Northern | Sacramento | North | Sacramento | Yes | ASTA Construction damaged a 3/4" steel gas service line with an excavator while installing a curb and sidewalk. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Curb/Sidewalk Work | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025040902920 | Dig-In to PG&E Underground | 3rd Party-Contractor | ASTA Construction Co Inc | Distribution Service | 122699 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-26 | ¾” | 8 | 130 | N/A | 6 | Jun | 2025 |  | 247178 | No | North Valley & Sierra | North Valley & Sierra
23673 | x | x | x |  | 2025-06-27 | Jun | 6 | 2025 | 122721 |  |  | Napa | Bay Area | North Bay | North | Calistoga | Yes | California Retaining Walls damaged a 2" plastic gas main with boring equipment while installing posts for a foot bridge. No 811 ticket. | No | Gas Line | Yes | Boring Equipment | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | California Retaining Walls | Distribution Main | 122721 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-27 | 2” | 36 | 150 | Excavator Believed a USA Ticket was Obtained by Their Company/Representative | 6 | Jun | 2025 |  | 496346 | No | North Coast | North Coast
23674 | x |  | x |  | 2025-06-27 | Jun | 6 | 2025 | 122742 |  | 131412756 | Merced | Central Valley | Yosemite | South | Gustine | Yes | Dandy Construction damaged a 2" plastic gas main with drilling equipment while doing telecommunications work. Valid 811 ticket. Excavated prior to receiving positive response | No | Gas Line | Yes | Drilling Equipment | Telecommunications | Excavated Prior to Receiving a Positive Response From All Utilities | Yes | 2025061603329 | Dig-In to PG&E Underground | 3rd Party-Contractor | Dandy Construction | Distribution Main | 122742 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-27 | 2” | 46 | 162 | N/A | 6 | Jun | 2025 |  | 1103061 | No | Central Valley | Central Valley
23675 | x | x | x |  | 2025-06-27 | Jun | 6 | 2025 | 122718 |  | 131410716 | Stanislaus | Central Valley | Yosemite | South | Oakdale | Yes | United Pavement Maintenance damaged 1/2" plastic gas service line with an excavator while replacing sewer lines. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Sewer | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025050703725 | Dig-In to PG&E Underground | 3rd Party-Contractor | United Pavement Maintenance Inc. | Distribution Service | 122718 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-27 | ½” | 24 | 24 | N/A | 6 | Jun | 2025 |  | 905503 | No | Central Valley | Central Valley
23676 | x | x | x |  | 2025-06-28 | Jun | 6 | 2025 | 122765 |  | 131413795 | Marin | North Coast | Marin | North | San Rafael | Yes | Unlicensed contractor damaged 1/2" plastic gas service line with a shovel while installing a fence. No 811 ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service | 122765 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-28 | ½” | 20 | 19 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  |  | Yes | North Coast | North Coast
23677 | x | x | x |  | 2025-06-28 | Jun | 6 | 2025 | 122764 |  | 131413787 | Alameda | Bay Area | Oakland | Central | Oakland | Yes | Homeowner damaged 1/2" plastic gas service line with a hand held drill while replacing a post bracket. No 811 ticket. | No | Gas Line | Yes | Drilling Equipment | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122764 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-28 |  | 2 | 109 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  |  | No | Bay Area | Bay Area
23678 | x | x |  |  | 2025-06-29 | Jun | 6 | 2025 | 122782 |  |  | Santa Clara | Central Coast | San Jose | Central | San Jose | Yes | TT Electrical damaged the coating on a 3/4" steel gas service line with a shovel while doing an electric upgrade. No 811 ticket. Damage was also done to secondary electric - see OIS 2822138 | Yes | Gas Line | No | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | T T Electrical | Distribution Service | 122782 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-29 | ¾” | 30 | 0 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 6 | Jun | 2025 |  | 963055 | Yes | South Bay & Central Coast | South Bay & Central Coast
23679 |  | x |  |  | 2025-06-29 | Jun | 6 | 2025 | OIS 2822138 |  |  | Santa Clara | Central Coast | San Jose | Central | San Jose | No | TT Electrical damaged secondary electric with a shovel while doing an electric upgrade. No 811 ticket. Damaged was also done to the gas line - see EMT 122782. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Shovel | Electric Work | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | T T Electrical | Electric | OIS 2822138 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-06-29 |  | 41 | 0 | Excavator Believed they Could Excavate Under Another Company’s USA Ticket | 6 | Jun | 2025 |  | 963055 | Yes | South Bay & Central Coast | South Bay & Central Coast
23680 | x | x | x |  | 2025-06-29 | Jun | 6 | 2025 | 122786 |  | 131414494 | Kings | Central Valley | Fresno | South | Avenal | Yes | Homeowner damaged 1/2" plastic gas service line with a shovel while doing sewer work. No 811 ticket. | No | Gas Line | Yes | Shovel | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122786 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-29 | ½” | 42 | 140 | No Knowledge of USA Ticketing Process | 6 | Jun | 2025 |  |  | Yes | Central Valley | Central Valley
23681 | x | x |  |  | 2025-06-30 | Jun | 6 | 2025 | 122848 |  |  | Kern | Central Valley | Kern | South | Ridgecrest | Yes | Homeowner damaged 1/2" plastic gas service line with a backhoe while installing a trench for a sewer leach line. No 811 ticket. | No | Gas Line | Yes | Backhoe/Trackhoe | Sewer | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Homeowner/Property Owner | Homeowner | Distribution Service | 122848 | No | N/A |  | 2025 Q2 | Yes | Yellow |  |  |  | 3rd Party Gas | Yes | 2025-06-30 | ½” | 32 | 8 | Believed they knew where underground utility was from previous knowledge | 6 | Jun | 2025 |  |  | No | Central Valley | Central Valley
23682 | x | x | x |  | 2025-06-30 | Jun | 6 | 2025 | 122813 |  | 131416354 | Alameda | Bay Area | Richmond | Central | Berkeley | Yes | Impact Services Enterprises damaged 1/2" plastic gas service line with a jackhammer while installing a new electric line. Valid 811 ticket. Failed to maintain marks | No | Gas Line | Yes | Jackhammer | Electric Work | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible | Yes | 2025061902581 | Dig-In to PG&E Underground | 3rd Party-Contractor | Impact Services Enterprises | Distribution Service | 122813 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-30 | ½” | 18 | 15 | N/A | 6 | Jun | 2025 |  | 1061152 | No | Bay Area | Bay Area
23683 |  | x |  |  | 2025-06-30 | Jun | 6 | 2025 | OIS 2822901 |  |  | San Joaquin | Central Valley | Stockton | South | Stockton | No | Waller Inc. damaged 4" conduit with an excavator while installing wet utilities. Valid 811 ticket. Failed to protect subsurface installation. Electric dig-in. Not valid for STIP. | No | Electric Line | No | Excavator | Pipeline Work - Liquid | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees [CCR Title 8, Sec. 1541 (b)(4)] | Yes | 2025061901491 | Dig-In to PG&E Underground | 3rd Party-Contractor | Waller Inc. | Electric | OIS 2822901 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Electric | Yes | 2025-06-30 |  |  | 0 | N/A | 6 | Jun | 2025 |  | 879648 | No | Central Valley | Central Valley
23684 | x |  | x |  | 2025-06-30 | Jun | 6 | 2025 | 122834 |  | 131417211 | Humboldt | Northern | Humboldt | North | Mckinleyville | Yes | North Coast Fencing damaged 1" plastic gas service line with a shovel while installing a fence post. No 811 ticket. | No | Gas Line | Yes | Shovel | Fencing | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | North Coast Fencing | Distribution Service | 122834 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-30 | 1” | 30 | 15 | Other | 6 | Jun | 2025 |  | 1097069 | Yes | North Coast | North Coast
23685 | x | x |  |  | 2025-06-30 | Jun | 6 | 2025 | 122814 |  |  | Alameda | Bay Area | Mission | South | Livermore | Yes | Medeiros Construction damaged a 2" plastic gas main with an excavator while digging a joint trench for new utilities. Valid 811 ticket. Failed to expose facility with hand tools | No | Gas Line | Yes | Excavator | Site Development | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment | Yes | 2025051501757 | Dig-In to PG&E Underground | 3rd Party-Contractor | Medeiros Construction | Distribution Main | 122814 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-30 | 2” | 30 | 42 | N/A | 6 | Jun | 2025 |  | 1042438 | No | Bay Area | Bay Area
23686 | x | x | x |  | 2025-06-30 | Jun | 6 | 2025 | 122822 |  | 131416680 | Marin | North Coast | Marin | North | Fairfax | Yes | ARB Inc. damaged 1/2" plastic gas service line with a shovel while doing a gas main replacement for PG&E. Valid 811 ticket. Failed to dig with care | No | Gas Line | Yes | Shovel | Gas | Failed to Dig with Care | Yes | 2025050501303 | Dig-In to PG&E Underground | 2nd Party-Contractor | ARB Inc | Distribution Service | 122822 | No | N/A |  | 2025 Q2 | Yes | Orange | PG&E GDGC |  |  | 2nd Party Gas | Yes | 2025-06-30 | ½” | 18 | 24 | N/A | 6 | Jun | 2025 |  | 194079 | Yes | North Coast | North Coast
23687 | x |  | x |  | 2025-06-30 | Jun | 6 | 2025 | 122808 |  | 131415759 | Sonoma | Northern | Sonoma | North | Sebastopol | Yes | Unlicensed contractor damaged 1/2" plastic gas service line with a post-hole digger while digging a post hole. No 811 ticket. | No | Gas Line | Yes | Post-Hole Digger | Pole/Post Installation | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Unlicensed Contractor | Distribution Service | 122808 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-30 | ½” | 18 | 8 | Other | 6 | Jun | 2025 |  |  | Yes | North Coast | North Coast
23688 | x | x |  |  | 2025-06-30 | Jun | 6 | 2025 | 122799 |  |  | San Francisco | Bay Area | San Francisco | Central | San Francisco | Yes | Elite Engineering Contractors damaged 1/2" plastic gas service line inserted into 1 1/4" steel with an excavator while grading a lot. No 811 ticket. | Yes | Gas Line | No | Excavator | Blading/Lot Grading | No USA Ticket | No | N/A | Dig-In to PG&E Underground | 3rd Party-Contractor | Elite Engineering Contractors | Distribution Service | 122799 | No | N/A |  | 2025 Q2 | Yes | Red |  |  |  | 3rd Party Gas | Yes | 2025-06-30 | ½” | 24 | 0 | Excavator Did Not Believe a USA Ticket was Required | 6 | Jun | 2025 |  | 917633 | No | Bay Area | Bay Area

## Lookup Tables
Within Last 12 Months? | 2023-05-01
City - County - Division - Region |  |  |  |  | Same Name Cities Lookup |  |  |  |  | Division - DiRT |  |  |  | Region Abbreviation |  | Month Abbreviation |  |  | UCON Member
based on 2016 UCON list provided by UCON
City/Town | County | Division | Region | Source | City/Town | County | Division | Region | Source | Division | Region | DiRT Division | Lead | Region Abbreviation | Region | Month Number | Month Abbrev | Quarter | Contractor Name | UCON Member? | Division | New Region | Tool | Hand Tools
Acalanes Ridge |  | Diablo | Bay Area | PG&E GISWeb | Alder Springs | Glenn | North Valley | Northern | PG&E GISWeb | De Anza | Central Coast | Central | Jorge | BA | Bay Area | 1 | Jan | Q1 | 1 Earth Landscaping & Construction | No | Humboldt | North Coast | Auger | No
Adams |  | Humboldt | Northern | PG&E GISWeb | Alder Springs | Fresno | Fresno | Central Valley | PG&E GISWeb | East Bay | Bay Area | Central | Jorge | CC | Central Coast | 2 | Feb | Q1 | 1 Stop Remodel | No | North Bay | North Coast | Backhoe/Trackhoe | No
Adela |  | Yosemite | Central Valley | PG&E GISWeb | Arbuckle |  | San Jose | Central Coast | PG&E GISWeb | Peninsula | Central Coast | Central | Jorge | CV | Central Valley | 3 | Mar | Q1 | 1st Choice Electric | No | Sonoma | North Coast | Boring Equipment | No
Adelaida |  | Los Padres | Central Coast | PG&E GISWeb | Arbuckle | Colusa | Sacramento | Northern | PG&E GISWeb | San Francisco | Bay Area | Central | Jorge | NR | Northern | 4 | Apr | Q2 | 1st Light Energy | No | North Valley | North Valley & Sierra | Bulldozer | No
Adobe Meadow Meadow Park |  | De Anza | Central Coast | PG&E GISWeb | Arnold | Mendocino | Humboldt | Northern | PG&E GISWeb | San Jose | Central Coast | Central | Jorge |  |  | 5 | May | Q2 | 2 J Plumbing | No | Sacramento | North Valley & Sierra | Cutting Machine | No
Aetna Springs |  | North Bay | Bay Area | PG&E GISWeb | Arnold | Calaveras | Stockton | Central Valley | PG&E GISWeb | Diablo | Bay Area | North | Cliff |  |  | 6 | Jun | Q2 | 24/7 Plumbing | No | Sierra | North Valley & Sierra | Digging Bar | Yes
Afton |  | Sacramento | Northern | PG&E GISWeb | Bayview | Contra Costa | East Bay | Bay Area | PG&E GISWeb | Humboldt | Northern | North | Cliff |  |  | 7 | Jul | Q3 | 3 Brothers Construction and Rental Inc | No | Marin | North Coast | Drilling Equipment | No
Agnew |  | San Jose | Central Coast | PG&E GISWeb | Bayview | Humboldt | Humboldt | Northern | PG&E GISWeb | North Bay | Bay Area | North | Cliff |  |  | 8 | Aug | Q3 | 49er Plumbing and Drain | No | Diablo | Bay Area | Excavator | No
Agnew Rd Garrity Way |  | San Jose | Central Coast | PG&E GISWeb | Bear Valley | Mariposa | Yosemite | Central Valley | PG&E GISWeb | North Valley | Northern | North | Cliff |  |  | 9 | Sep | Q3 | 4C's Construction | No | East Bay | Bay Area | Farm Equipment | No
Agua Caliente |  | Sonoma | Northern | PG&E GISWeb | Bear Valley | Alpine | Stockton | Central Valley | PG&E GISWeb | Sacramento | Northern | North | Cliff |  |  | 10 | Oct | Q4 | A and R Plumbing | No | Mission | Bay Area | Front Loader | No
Agua Fria |  | Yosemite | Central Valley | PG&E GISWeb | Belleview | Humboldt | Humboldt | Northern | PG&E GISWeb | Sierra | Northern | North | Cliff |  |  | 11 | Nov | Q4 | A and S Construction | No | Peninsula | Bay Area | Grader/Scraper | No
Ahwahnee |  | Yosemite | Central Valley | PG&E GISWeb | Belleview | Tuolumne | Yosemite | Central Valley | PG&E GISWeb | Sonoma | Northern | North | Cliff |  |  | 12 | Dec | Q4 | A and V Services | No | San Francisco | Bay Area | Grounding Rod | Yes
Airport |  | Yosemite | Central Valley | PG&E GISWeb | Big Bend | Placer | Sierra | Northern | PG&E GISWeb | Mission | Central Coast | South | Steve | [5 empty] | A Barrios General Building | No | Central Coast | South Bay & Central Coast | Hand Tools | Yes
Akers |  | Stockton | Central Valley | PG&E GISWeb | Big Bend | Shasta | North Valley | Northern | PG&E GISWeb | Central Coast | Central Coast | South | Steve | [5 empty] | A Munoz Landscaping | No | De Anza | South Bay & Central Coast | Horizontal Directional Boring | No
Alba |  | Yosemite | Central Valley | PG&E GISWeb | Buckeye | El Dorado | Sierra | Northern | PG&E GISWeb | Fresno | Central Valley | South | Steve | [5 empty] | A Ruiz Construction Co | Yes | Los Padres | South Bay & Central Coast | Jackhammer | No
Albanese |  | San Jose | Central Coast | PG&E GISWeb | Buckeye | Plumas | North Valley | Northern | PG&E GISWeb | Kern | Central Valley | South | Steve | [5 empty] | A&A Electric | No | San Jose | South Bay & Central Coast | Milling/Road Grinding | No
Albertson Beck |  | De Anza | Central Coast | PG&E GISWeb | Buena Vista | Santa Clara | San Jose | Central Coast | PG&E GISWeb | Stockton | Central Valley | South | Steve | [5 empty] | A&B Construction | Yes | Fresno | Central Valley | Other | No
Albion |  | Humboldt | Northern | PG&E GISWeb | Buena Vista | Amador | Stockton | Central Valley | PG&E GISWeb | Yosemite | Central Valley | South | Steve | [5 empty] | A&C Noma Construction | No | Kern | Central Valley | Other Driven Machinery | No
Alder Creek |  | Sacramento | Northern | PG&E GISWeb | Cedar Ridge | Nevada | Sierra | Northern | PG&E GISWeb | Los Padres | Central Coast | South | Steve | [5 empty] | A&D Construction | No | Stockton | Central Valley | Other Hand Machinery | No
Alder Springs |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | Centerville | Butte | North Valley | Northern | PG&E GISWeb | [9 empty] | A&D Plumbing | No | Yosemite | Central Valley | Other Hand Tools | Yes
Alderbrook |  | De Anza | Central Coast | PG&E GISWeb | Centerville | Fresno | Fresno | Central Valley | PG&E GISWeb | [9 empty] | A&J Fencing | No | Oakland | Bay Area | Pickaxe | Yes
Aldercroft Heights |  | De Anza | Central Coast | PG&E GISWeb | Cherokee | Nevada | Sierra | Northern | PG&E GISWeb | [9 empty] | A&T Plumbing | No | Richmond | Bay Area | Pipe Bursting | No
Alderpoint |  | Humboldt | Northern | PG&E GISWeb | Cherokee |  | Yosemite | Central Valley | PG&E GISWeb | [9 empty] | A1 Builders | No | Vacaville | North Valley & Sierra | Post-Hole Digger | Yes
Alexander |  | San Jose | Central Coast | PG&E GISWeb | Cherokee |  | Stockton | Central Valley | PG&E GISWeb | [9 empty] | A1 Construction | No | Belmont | Bay Area | Probing Tool | Yes
Alexian |  | San Jose | Central Coast | PG&E GISWeb | Cherokee | Butte | North Valley | Northern | PG&E GISWeb | [9 empty] | A-1 Electric | No | Colma | Bay Area | Shovel | Yes
Algerine |  | Yosemite | Central Valley | PG&E GISWeb | Cold Springs | El Dorado | Sierra | Northern | PG&E GISWeb | [9 empty] | A-1 Fence Company | No | Division | New Region 2025 | Skid Steer | No
Algoso |  | Kern | Central Valley | PG&E GISWeb | Cold Springs |  | Yosemite | Central Valley | PG&E GISWeb | [9 empty] | A-1 National Fence | No | Humboldt | North Coast | Spader | No
Alhambra Valley |  | Diablo | Bay Area | PG&E GISWeb | Dogtown | Mariposa | Yosemite | Central Valley | PG&E GISWeb | [9 empty] | A-1 Pavement Marking | No | North Bay | North Coast | Spader (hand) | Yes
Alicia |  | Sierra | Northern | PG&E GISWeb | Dogtown | Glenn | North Valley | Northern | PG&E GISWeb | [9 empty] | A-1 Pool Removal | No | Sonoma | North Coast | Stake | Yes
Alleghany |  | Sierra | Northern | PG&E GISWeb | Dogtown | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [9 empty] | A-1 Quality Plumbing | No | North Valley | North Valley & Sierra | Stump Grinder | No
Allendale |  | Sacramento | Northern | PG&E GISWeb | Enterprise | Amador | Stockton | Central Valley | PG&E GISWeb | [9 empty] | A1 Septic | No | Sacramento | North Valley & Sierra | Stump Grinding | No
Allensworth |  | Fresno | Central Valley | PG&E GISWeb | Enterprise |  | North Valley | Northern | PG&E GISWeb | [9 empty] | A1 Tree Service | No | Sierra | North Valley & Sierra | Tractor | No
Alma Almaden |  | San Jose | Central Coast | PG&E GISWeb | Franklin | Merced | Yosemite | Central Valley | PG&E GISWeb | [9 empty] | AAA Electrical Services | No | Vacaville | North Coast | Trencher | No
Alma Neighborhood Association |  | San Jose | Central Coast | PG&E GISWeb | Franklin | Sacramento | Sacramento | Northern | PG&E GISWeb | [9 empty] | AAA Fence Co | No | Diablo | Bay Area | Unknown | No
Almaden Clara Felice |  | San Jose | Central Coast | PG&E GISWeb | Greenfield | Monterey | Central Coast | Central Coast | PG&E GISWeb | [9 empty] | AAA Fire Protection Services | No | East Bay | Bay Area | Vacuum Equipment | No
Almaden Community Association |  | San Jose | Central Coast | PG&E GISWeb | Greenfield | Kern | Kern | Central Valley | PG&E GISWeb | [9 empty] | AAA Properties | No | Mission | Bay Area | Pneumatic Spader | No
Almaden Lake |  | San Jose | Central Coast | PG&E GISWeb | Greenwood | Glenn | North Valley | Northern | PG&E GISWeb | [9 empty] | AAA Underground General Engineering | No | Peninsula | Bay Area
Almaden Meadows |  | San Jose | Central Coast | PG&E GISWeb | Greenwood | El Dorado | Sierra | Northern | PG&E GISWeb | [9 empty] | Aardvark Hole Drilling | No | San Francisco | Bay Area
Almaden Winery N. Association |  | San Jose | Central Coast | PG&E GISWeb | Happy Valley | El Dorado | Sierra | Northern | PG&E GISWeb | [9 empty] | Aaron Garfinkel Construction | No | Central Coast | South Bay & Central Coast
Almanor |  | North Valley | Northern | PG&E GISWeb | Happy Valley | Calaveras | Stockton | Central Valley | PG&E GISWeb | [9 empty] | Aaron's Rooter and Plumbing Service | No | De Anza | South Bay & Central Coast
Alpaugh |  | Fresno | Central Valley | PG&E GISWeb | Las Lomas | Monterey | Central Coast | Central Coast | PG&E GISWeb | [9 empty] | AAW Construction | No | Los Padres | South Bay & Central Coast
Alta |  | Sierra | Northern | PG&E GISWeb | Las Lomas |  | Sonoma | Northern | PG&E GISWeb | [9 empty] | AB Landscaping | No | San Jose | South Bay & Central Coast
Alta Hill |  | Sierra | Northern | PG&E GISWeb | Live Oak | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [9 empty] | AB Plumbing | No | Fresno | Central Valley
Altaville |  | Stockton | Central Valley | PG&E GISWeb | Live Oak | Sutter | Sierra | Northern | PG&E GISWeb | [9 empty] | Abante Rooter & Plumbing | No | Kern | Central Valley
Alto |  | North Bay | Bay Area | PG&E GISWeb | Lone Star | Glenn | North Valley | Northern | PG&E GISWeb | [9 empty] | Abbett Electric Corporation | No | Stockton | Central Valley
Alton |  | Humboldt | Northern | PG&E GISWeb | Lone Star | Fresno | Fresno | Central Valley | PG&E GISWeb | [9 empty] | Abe Construction | No | Yosemite | Central Valley
Alvarado |  | Mission | Central Coast | PG&E GISWeb | Lucerne | Lake | Humboldt | Northern | PG&E GISWeb | [9 empty] | Abel-Home Repair | No | Oakland | Bay Area
Alvin Burdette |  | San Jose | Central Coast | PG&E GISWeb | Lucerne | Kings | Fresno | Central Valley | PG&E GISWeb | [9 empty] | Aberle Concrete | No | Richmond | Bay Area
Alviso |  | San Jose | Central Coast | PG&E GISWeb | Mayfair |  | San Jose | Central Coast | PG&E GISWeb | [9 empty] | Able Underground Construction | No | Marin | North Coast
Amesti |  | Central Coast | Central Coast | PG&E GISWeb | Mayfair | Fresno | Fresno | Central Valley | PG&E GISWeb | [9 empty] | ABM Electrical | No | Belmont | Bay Area
Ampere |  | Stockton | Central Valley | PG&E GISWeb | Meridian | Kern | Kern | Central Valley | PG&E GISWeb | [9 empty] | Abooralath Fereydouni | No | Colma | Bay Area
Amsterdam |  | Yosemite | Central Valley | PG&E GISWeb | Meridian | Sutter | Sacramento | Northern | PG&E GISWeb | [9 empty] | Above All Plumbing Inc | No
Anchor Bay |  | Humboldt | Northern | PG&E GISWeb | Monte Vista | Placer | Sierra | Northern | PG&E GISWeb | [9 empty] | Abraham Rosas | No
Anderson Southeast |  | San Jose | Central Coast | PG&E GISWeb | Monte Vista |  | De Anza | Central Coast | PG&E GISWeb | [9 empty] | Absolute Construction | No
Anderson Springs |  | Humboldt | Northern | PG&E GISWeb | Norton | Yolo | Sacramento | Northern | PG&E GISWeb | [9 empty] | Absolute Plumbing & Drain | No
Andersonia |  | Humboldt | Northern | PG&E GISWeb | Norton |  | Stockton | Central Valley | PG&E GISWeb | [9 empty] | Absolute Plumbing Company | No
Angiola |  | Fresno | Central Valley | PG&E GISWeb | Oak Grove |  | San Jose | Central Coast | PG&E GISWeb | [9 empty] | AC Electric | No
Anita |  | North Valley | Northern | PG&E GISWeb | Oak Grove | Yuba | North Valley | Northern | PG&E GISWeb | [9 empty] | AC Fence | No
Ann Darling |  | San Jose | Central Coast | PG&E GISWeb | Pacheco |  | San Jose | Central Coast | PG&E GISWeb | [9 empty] | AC Square Inc | No
Annapolis |  | Humboldt | Northern | PG&E GISWeb | Pacheco | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [9 empty] | Access Control Systems | No
Annette |  | Los Padres | Central Coast | PG&E GISWeb | Pine Grove | Mendocino | Humboldt | Northern | PG&E GISWeb | [9 empty] | Accu Bore | Yes
Applegate |  | Sierra | Northern | PG&E GISWeb | Pine Grove | Shasta | North Valley | Northern | PG&E GISWeb | [9 empty] | Accurate Building | No
Aptos Hills-Larkin Valley |  | Central Coast | Central Coast | PG&E GISWeb | Pine Grove | Amador | Stockton | Central Valley | PG&E GISWeb | [9 empty] | Accurate Home Services | No
Arastraville |  | Yosemite | Central Valley | PG&E GISWeb | Pinehurst |  | San Jose | Central Coast | PG&E GISWeb | [9 empty] | Accurate Plumbing | No
Arena |  | Yosemite | Central Valley | PG&E GISWeb | Pinehurst | Fresno | Fresno | Central Valley | PG&E GISWeb | [9 empty] | Accurate Trenching | No
Arlynda Corners |  | Humboldt | Northern | PG&E GISWeb | Rainbow |  | De Anza | Central Coast | PG&E GISWeb | [9 empty] | Ace Construction | No
Armona |  | Fresno | Central Valley | PG&E GISWeb | Rainbow | Placer | Sierra | Northern | PG&E GISWeb | [9 empty] | Ace Drilling and Excavating | No
Arnold |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | San Miguel |  | De Anza | Central Coast | PG&E GISWeb | [9 empty] | Ace Plumbing and Rooter | No
Aromas | Monterey | Central Coast | Central Coast | PG&E GISWeb | San Miguel | San Luis Obispo | Los Padres | Central Coast | PG&E GISWeb | [9 empty] | Ace Sewer Lateral | No
Arroz |  | Sacramento | Northern | PG&E GISWeb | San Miguel | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [9 empty] | Acez Inc | No
Artois |  | North Valley | Northern | PG&E GISWeb | Strawberry | Marin | North Bay | Bay Area | PG&E GISWeb | [9 empty] | Acme Drain Plumbing & Rooter | No
Ashbridge |  | San Jose | Central Coast | PG&E GISWeb | Strawberry | Tuolumne | Yosemite | Central Valley | PG&E GISWeb | [9 empty] | Acme Electric | No
Aspen Valley |  | Yosemite | Central Valley | PG&E GISWeb | Strawberry | El Dorado | Sierra | Northern | PG&E GISWeb | [9 empty] | Acon Builders | No
Asti |  | Sonoma | Northern | PG&E GISWeb | Toyon |  | San Jose | Central Coast | PG&E GISWeb | [9 empty] | Across the Pond Construction | No
Asuncion |  | Los Padres | Central Coast | PG&E GISWeb | Toyon | Calaveras | Stockton | Central Valley | PG&E GISWeb | [9 empty] | Action Hauling | No
Athlone |  | Yosemite | Central Valley | PG&E GISWeb | Wagner |  | Yosemite | Central Valley | PG&E GISWeb | [9 empty] | Acustruct | No
Atlanta |  | Stockton | Central Valley | PG&E GISWeb | Wagner |  | Stockton | Central Valley | PG&E GISWeb | [9 empty] | Ad Concrete | No
Atlanta Bird |  | San Jose | Central Coast | PG&E GISWeb | Westhaven | Humboldt | Humboldt | Northern | PG&E GISWeb | [9 empty] | AD Landscaping | No
Auberry |  | Fresno | Central Valley | PG&E GISWeb | Westhaven | Fresno | Fresno | Central Valley | PG&E GISWeb | [9 empty] | Adam Dahlen Construction | No
Auburn Lake Trails |  | Sierra | Northern | PG&E GISWeb | Westside |  | Kern | Central Valley | PG&E GISWeb | [9 empty] | Adam Hawkins Superior Energy | No
Auckland |  | Fresno | Central Valley | PG&E GISWeb | Westside | Fresno | Fresno | Central Valley | PG&E GISWeb | [9 empty] | Adams Brothers Construction | No
Aukum |  | Sierra | Northern | PG&E GISWeb | Wolf | Nevada | Sierra | Northern | PG&E GISWeb | [9 empty] | Adams Underground | No
Autumn Montgomery |  | San Jose | Central Coast | PG&E GISWeb | Wolf | Fresno | Fresno | Central Valley | PG&E GISWeb | [9 empty] | Add-A-Garage | No
Auzerais Josefa |  | San Jose | Central Coast | PG&E GISWeb | Yankee Hill | Tuolumne | Yosemite | Central Valley | PG&E GISWeb | [9 empty] | Adolfo Santos | No
Avena |  | Stockton | Central Valley | PG&E GISWeb | Yankee Hill | Butte | North Valley | Northern | PG&E GISWeb | [9 empty] | Advance Concrete Inc | No
Avenida Espana |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Advanced Cutting & Paving Co | No
Avery |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Advanced Electric | No
Avilla Beach |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Advanced Environmental and Power | No
Avis Cherry |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Advanced Plumbing | No
Avocado |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Advanced Telecommunications | No
Avon |  | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Advanced Telecommunications Company | No
Badger |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Advanced Trenchless | No
Bahia |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Advanced Wallcovering | No
Balboa Terrace |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Advantage Builders | No
Balch Camp |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | AE Com | No
Ballard |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Aerco Pacific Inc | No
Ballico |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | AES Landscaping Inc | No
Banana Grove |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Affordable Fencing and Construction | No
Bangor |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Affordable Landscape & Service | No
Bannister |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Affordable Luxury Homes Corp | No
Banta |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Affordable Septic | No
Barberal Stokes |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Affordable Trenchless | No
Bardi |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | AG Irrigation Services | No
Barron Park |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | AGC Construction | No
Bascom Forest |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Agee Construction | No
Bass Lake |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Agee Construction | No
Bassetts |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Agri Valley Construction | No
Batavia |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Aguilar and Sons | No
Baton Rouge |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Aguilar Fence Inc | No
Battaglia |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Aguilar Landscape Services | No
Baxter |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Ahbury Construction | No
Bay Farm Island |  | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Ahern Construction | No
Bayliss |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Aiken Underground | No
Bayview |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Airel Construction | No
Baywood Park |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | AIRS | No
Beatrice |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | AJ & T Plumbing & Electric | No
Bel Marin Keys |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | AJ Concrete and Landscaping | No
Belden |  | North Valley | Northern | PG&E GISWeb | [14 empty] | AJ Johnson Electric | No
Bell Springs |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | AK Enterprises | No
Bella Vista |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Al Fresco Landscaping | No
Belleview |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Al Wagner Construction | No
Bellota |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Alameda County | No
Belvedere Tiburon | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Alameda County Water District | No
Ben Hur |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Alameda Structural Inc | No
Bena |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Alamo Plumbing | No
Benbow |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Alan Bonigio Construcion | No
Bend |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Alan Electric | No
Benito |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Albertazi Construction | No
Benton Kiely |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Alcazar Concrete | No
Berenda |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Alccon General Engineering | No
Bernal Heights |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Alco Water Co | No
Berry Creek |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Aldo Angone Farms | No
Berry Glenn |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Aleco Electric | No
Berry Park |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Alegre Construction | No
Berryessa |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Alfaro Engineering Inc | No
Berryessa Creek |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Alfonso Backhoe Service | No
Bethel Island |  | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Ali's Construction | No
Betteravia |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | All Above Plumbing | No
Beverly Wilshire |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | All American Construction | No
Bieber |  | North Valley | Northern | PG&E GISWeb | [14 empty] | All American Fencing | No
Big Bend |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | All Fence Company | No
Big Bunch |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | All Land Construction | No
Big Lagoon |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | All Out Plumbers | No
Big Oak Flat |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | All Phase Construction | No
Big Sur |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | All Phase Excavating | No
Birchville |  | Sierra | Northern | PG&E GISWeb | [14 empty] | All Restorations | No
Birdland Neighbors |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | All Seasons Construction | No
Birds Landing |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | All Star Drilling | No
Bitterwater |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | All Star Electric Services | No
Black Point |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | All State Paving | No
Black Point-Green Point |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | All Steel Fence | No
Blackford |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | All Tech Services | No
Blacklake |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | All Valley Plumbing | No
Blanchard |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | All World Construction Inc | No
Blanco |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | All-Bright Electric | No
Blocksburg |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Allcom Plumbing | No
Bloomfield |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Allen A Wagoner Construction | Yes
Blossom Crest |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Allen Dickinson's Landscape | No
Blue Canyon |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Allen Land Design | No
Bluewater |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Allen Pererson | No
Bodega |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Allen's Electric | No
Bodega Bay |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Alliance Tree Service | No
Bolinas |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Allied Fire Protection | No
Bolsa Knolls |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Allied Low Voltage | No
Bonanza Springs |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Allied Plus | No
Bonita 24th |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Alligator Plumbing | No
Bonnefoy |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Allred & Associates | No
Bonny Doon |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Allstate Plumbing Co | No
Bootjack |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Allstate Renovations | No
Borden |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Alma Jacobo Gardening | No
Boronda |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Aloha Landscape | No
Boston Ravine |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Aloha Tree Care | No
Boulder |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Alosi Construction | No
Bowerbank |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Alpha Tech Plumbing | No
Bowles |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Alpine Construction | No
Bowman |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Alpine Demolition | No
Braly Corners |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Alpine Landscaping | No
Branham |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Alpine Natural Gas Company | No
Branham Jarvis |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Al's Custom Concrete | No
Branham Kirk |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Al's Land Clearing Inc | No
Branscomb |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Alsco-Geyer | No
Bretz Mill |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Alternative Energy | No
Briceburg |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Altes Development | No
Briceland |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Altura Construction | No
Bridgeport |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Alves Inc | No
Bridgeville |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | ALW Enterprise | No
Brigadoon |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | AM Construction | No
Briones |  | Diablo | Bay Area | PG&E GISWeb | [14 empty] | AM Stephens Construction | No
Brito |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | AM Sun Solar | No
Broadmoor |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | AM Teltek | No
Broadway Palmhaven |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | AMA Diversified Construction Group | No
Broderick |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Amador County | No
Bromela |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Amador Plumbing | No
Brooks |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Amaya Landscaping | No
Brooktrails |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | American Asphalt | No
Brooktree |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | American Construction & Supply Inc | No
Brookvale Chantel |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | American Drilling | No
Brookwood South |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | American Eagle Plumbing & Construction | No
Brookwood Terrace |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | American Precision Builders | No
Browns Flat |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | American River Fence | No
Browns Valley |  | Sierra | Northern | PG&E GISWeb | [14 empty] | American River Resort | No
Brownsville |  | North Valley | Northern | PG&E GISWeb | [14 empty] | American Technologies | No
Brush Creek |  | North Valley | Northern | PG&E GISWeb | [14 empty] | American Underground | No
Brush Glen |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | American Well Drilling | No
Bryte |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Amerine Systems | No
Buchanan |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Amesos Plumbing | No
Buck Meadows |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | AMM Fencing | No
Buckeye |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Ammirato Construction | No
Buckhorn |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | AMX Plumbing | No
Bucknall |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Anadril Fireplace Cottages | No
Bucks Lake |  | North Valley | Northern | PG&E GISWeb | [14 empty] | AND Construction | No
Bucktown |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Anderson Brothers | No
Buena Vista |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Anderson Exc | No
Buffalo Hill |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Anderson's | No
Buhach |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Andes Construction | Yes
Bumblebee |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Andrade Electric | No
Bummerville |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Andradi Bros | No
Bunker |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Andrea Van Voohis | No
Bunker Hill |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Andreini Brothers | Yes
Burbank |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Andrew Edwinson | No
Burlington |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Andrew Hannon | No
Burness |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Andrew Turner Construction | No
Burnham |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Androit Development | No
Burning Tree |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Andy Gagnon Landscape | No
Burnt Ranch |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Andy Hahn | No
Burrel |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Annuzzi Concrete | No
Burson |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Anrak Corporation | Yes
Butte City |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Anselmo Services | No
Butte Creek Canyon |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Anthony Escalante | No
Butte Meadows |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Antonio Balderes | No
Butte Valley |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Anvil Builders | No
Buttonwillow |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Any Fence | No
Cadenasso |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | AP Backhoe Service | No
Cadillac East |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Apex Electric | No
Cadillac West |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Appian Engineering | Yes
Cadwallader |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Aqua Line Piping | No
Calabazas Cabrillo |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Aqua Soleil | No
Calabazas North |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Aquatek | No
Calabazas South |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Aquatek Plumbing | No
Calahan |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Aquatic Enviroments Inc | No
Calaveritas |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | AR Plumbing | No
Calderwood Delwood |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | ARB Inc | Yes
Calero |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Arbor Building Group | No
Calflax |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Arbor Fence Inc | No
Calgro |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Arborists for Hire | No
Calico |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Arborwell | No
California Maison |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Arcadia Landscaping | No
California Valley |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Arcadis | No
Calla |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Ardmacha Construction | No
Callender |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Argonaut Constructors | Yes
Calpack |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Arias Construction | No
Calvert |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Arke Construction | No
Calville |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Armoured Plumbing | No
Calwa |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Armstrong and Son Construction | No
Camanche North Shore |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Armstrong Landscaping and Design | No
Camanche Village |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Armstrong Plumbing | No
Cambria Pines |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Army Reserve | No
Cambrian Community Council District 2 |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Arnts Builders Inc | No
Cambrian Village |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Arreolas Landscape | No
Camden |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Arrow Construction | No
Cameo |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Arrowhead Communities Alliance Inc | No
Camino Tassajara |  | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Art Bacc | No
Camp Connell |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Art Scape | No
Camp Meeker |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Artisan Precast | No
Campo Seco |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Artisan Stonework | No
Camptonville |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Artistic Iron Works | No
Candlestick |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | A-S Pipeline | No
Cannon |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | AS Pipes Inc | No
Canoas East |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | ASAP Hauling | No
Canoas Garden |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Asbestos Management Group | No
Canoas West |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | ASC Berkeley Inc | No
Cantua Creek |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Ashburn Environment | No
Canyon |  | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Ashbury General Contracting | No
Canyondam |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Ashee Excavation | No
Capay |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Ashlin Pacific Construction | Yes
Cape Horn |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Asphalt Designs | Yes
Capetown |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Assembly Builders | No
Capewood |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Associated Plumbing | No
Capitol Goss |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Association Maintenance Services Inc | No
Carbona |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Assurance Construction | No
Caribou |  | North Valley | Northern | PG&E GISWeb | [14 empty] | AT Weber Plumbing | No
Carlotta | Humbolt | Humboldt | Northern | PG&E GISWeb | [14 empty] | AT&T | No
Carlton |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | A-Tach Construction | No
Carmel Highlands |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Atazz Technical Services | No
Carmel Valley Village |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Atkinson Farms | No
Carmet |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Atlantic Concrete | No
Carmine Parkmont |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Atlas Construction and Plumbing | No
Carrolton |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Atlas Fencing | No
Carson |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Atlas Peak Construction | No
Carson Hill |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Atlas Plumbing and Rooter | No
Caruthers |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Atondo Trenching | No
Casa Loma |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Au Energy LLC | No
Casey Corner |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Avalon Bay Communitties Inc | No
Casmalia |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Avalon Electric | No
Caspar |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Avant Field Services | No
Cassel |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Avila Concrete | No
Cassell |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Avila Construction | No
Castle Rock Springs |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Avison Construction | No
Castlemont |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | AW Kelley Sewer D Rooter | No
Castro |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | AWSF | No
Cataldi |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Axner Excavating | No
Catheys Valley |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | AZ Custom Construction | No
Cawelo |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Aztec Construction | No
Cayton |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Aztech Communications | No
Cayucos |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Aztrack Construction | No
Cazadero |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Azul Works | Yes
Cecile |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | B Jaeger Inc | No
Cedar Mill |  | North Valley | Northern | PG&E GISWeb | [14 empty] | B Line Construction | No
Cedar Ridge |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | B Wise Vineyards | No
Cedarbrook |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | B Z Plumbing | No
Cedarville Giannotta |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | B&B Asphalt | No
Cella |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | B&B Plumbing | No
Centerville |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | B&F Landscaping | No
Centerwood |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | B&M Builders Inc | No
Central Los Altos |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Babel Construction | No
Central Neighborhoods Area |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Backcountry Excavating | No
Central Valley |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Backhoe Dispatch | No
Century Pebbletree |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Badger Daylighting Company | No
Chadbourne |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Baggett Building Enterprise | No
Challenge |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Bailey Fence Company | No
Chaney Ranch |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Baileys Trenchless Inc | No
Chantilley |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Baillie Communications | No
Chapman Morse |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bains Development | No
Chapmantown |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Bair Engineering | No
Charleston Gardens |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Baires Construction | No
Charleston Meadows |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Baja Construction Inc | No
Checkers |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Baja Solar | No
Chemeketa Park |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Baker Real Estate | No
Cherokee |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Bakersfield Backhoe/Trackhoe Service | No
Cherokee Strip |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Bakersfield Plumbing | No
Cherry Orchard |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Bakersfield Well and Pump | No
Cherywood |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bakin Tree Service | No
Chicago Park |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Balch Enterprises | No
Chinatown |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Bandit Excavation | No
Chinese Camp |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Bandit Excavation | No
Cholame |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Bansuk Builders | No
Chorro |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Barak Construction | No
Chualar |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Barbieri Construction | No
Cimarron |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Barco Inc | No
Cinco De Mayo |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bariteau Construction | No
Cinderella |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Barnard Impreglio Healy | No
Cinnabar |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Barnard Pipeline | No
Cisco |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Barnum and Celillo Electric | No
Cisco Grove |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Baro Garden Maintenance | No
City Center |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Baron Construction Company | No
Civic Center Tenderloin |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Baron P Bonner General Engineering | No
Clam Beach |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Barrera & Associates Construction | No
Clarendon Heights |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Barri Electric | No
Clareview |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Barrios Construction | No
Claribel |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Barry Construction | No
Clarksburg |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Barry Swensen Construction | No
Clarksville |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Basin Enterprises | No
Claus |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Bass & Sons Drilling | No
Clay |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Bauhaus Construction | No
Clayton North |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bauman Construction & Landscape | Yes
Clayton South |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bay Area Asphalt & Cement Works | No
Clear Creek |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Bay Area Backhoe | Yes
Clearlake Oaks |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Bay Area Designer Builders Inc | No
Clearlake Riviera |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Bay Area Drainage | No
Clements |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Bay Area Landscape Services | No
Cleone |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Bay Area Lightworks | No
Clima |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Bay Area Paving Co | No
Clinic |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bay Area Tents | No
Clint |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Bay Cal Construction | No
Clinton |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Bay Cities Demolition | No
Clipper Mills |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Bay Cities Paving & Grading | Yes
Clotho |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Bay Construction Company | No
Clovercrest Glen Brae |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bay Design & Build | No
Clyde |  | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Bay Drainage | No
Coarsegold |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Bay Drainage | No
Cobb |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Bay Line Cutting and Coring | Yes
Cochrane |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Bay Pacific Construction | No
Codora |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Bay Pacific Pipeline | Yes
Cohasset |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Bay Renovations Construction | No
Cold Springs |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Bay Valley Construction | No
Coldwater |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bay View Construction | No
Colfax Spring |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | BayWorks Construction Inc | No
College City |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Bazan Landscape | No
College Park |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | BC Ferreira Construction | No
College Terrace |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | BCC Construction | No
Collinsville |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | BCI Roofing | No
Colonial |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | BCO Consulting & Construction | No
Comanche |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | BCP Concrete | No
Commodore |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | BDS Construction | No
Comptche |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | BDS Plumbing | No
Concow |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Beam Construction | No
Conejo |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Bear State Construction | No
Confidence |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Beaver Tree Service | No
Conner |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Becho Ins | No
Contra Costa Centre |  | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Bedrock Construction | No
Cool |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Beebe Diversified LP | Yes
Cooperstown |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Beeline Concrete | No
Copper City |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Behr Landscape Construction | No
Cordelia |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | BEI Electric Service | No
Cordelia Junction |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Bel Builder | No
Cordero Junction |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Bell Brother Heating and Air Conditioning | No
Cornwall Sunshadow |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bell McBride Builders | No
Corralitos |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Bell Plumbing | No
Cortez |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Bellingham Marine | No
Cottage Springs |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Bellows Plumbing | No
Coulterville |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Benaiah Ventures | No
Country Brook Lagoon |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Benchmark Civil Construction | No
Country Lane |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Benham Lazar | No
Country View Estates |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Benjamin Franklin Plumbing | No
Courtland |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Bennett Building Co | No
Cow Creek |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Benson & Son Electric | No
Cow Hollow |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Berger Concrete | No
Cowan |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Bergman Landscape | No
Coyote |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Berkeley Cement Inc | Yes
Coyote Fontanelle |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bernando Lopez Garden Design | No
Coyoteville |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Berncich Builders | No
Crabtree |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Bernie Klenow Contractor | No
Cramer Umbarger |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Berumen Construction Company | No
Cranmore |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Beto Lemon Grading | No
Crannell |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Better Built Fence | No
Creed |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Better Earth Gardens | No
Creek Senter |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Beutler Plumbing | No
Creekland |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Beyond Plumbing | No
Creekside |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | BG Construction | No
Creekside South |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Big Blue | No
Crescent Mills |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Big E Concrete | No
Crescent Park |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Big N Deep | No
Cressey |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Big Red Construction | No
Creston |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Big River Concrete Construction | No
Crocker Amazon |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Big Valley Group | No
Crome |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Bill Carone & Co Inc | No
Cromir |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Bill Cunningham Contractor | No
Crossgate |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bill Nelson Construction | No
Crows Landing |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Bill's Underground | No
Croydon |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bindel Bros. Construction | No
Crystal Lake |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Bindel Bros. Construction | No
Cumberland South |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Biondi Paving & Engineering | No
Cummings |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | BK Bobcat | No
Curry Village |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Black and Beach | No
Cushing |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Black Bear Builders | No
Cuyama |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Black Diamond Electric | No
Cygnus |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Black Diamond Paver Stones and Landscape | No
Cypress Judro |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Black Fire Prevention & Excavation | No
Dairyland |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Blacke N Construction | No
Dales |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Blackwell General Engineering | No
Dana |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Blakeley Landscaping Inc | No
Danielson |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Blanchard Construction | No
Danna Rock |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Blatnik Excavatng | No
Dardanelle |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Blaylock General Construction | No
Darrah |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Blazin Wings Inc | No
Dartmouth |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Blazona Concrete | No
Daulton |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Blei Home Construction Inc | No
Davenport |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | BLH Construction | No
Day Valley |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Bliss Design Build | No
Dayton |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Block A Construction | No
De La Cruz Laurelwood |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Blossom Valley Construction | No
De Marietta Southwest |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Blossom Valley Plumbing | No
De Voss Leigh |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Blue Moon Builders Inc | No
Deadwood |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Blue Mountain Air | No
Deer Creek |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Blue Wagon Landscape | No
Deer Crossing |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Boa Constructor | No
Deer Run |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bob Martinson | No
Deer Run 2 |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bob Perez Construction | No
Del Loma |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Bob's Backhoe | No
Del Paso Heights |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Bob's Plumbing | No
Del Rey |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Bocanerga Construction | No
Del Robles |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bode Construction | No
Delft Colony |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Bolanos Landscaping | No
Denny |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Bon Terra Landscaping | No
Dentwood Southbridge |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bore One Directional | No
Denverton |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Borg Fence | No
Derby Acres |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Borward Builders | No
Di Giorgio |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Boss Engineering and Construction | No
Diablo Grande |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Botad Construction | No
Diablo Range |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Botanica Landscape | No
Diamond Heights |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Botanical Landscape | No
Dinsmore |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Bouton Construction | No
Dobern |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Boward Builders | No
Doerr Steindorf |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bowen Engineering | No
Dogtown |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Bowman Construction | No
Doncaster Warrington |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Boyce Muse | No
Dorrington |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Boyd Plumbing | No
Dorsa Miller |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Boykin and Boykin | No
Dos Palos Y |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Braco Construction | No
Dos Rios |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Brad Kessler | No
Douglas Flat |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Bradford & Sons | No
Dove Hill |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bradley Tanks Inc | No
Downieville |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Bragg Plumbing | No
Downing Whitethorne |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Brake Factory | No
Downtown North |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Brar Construction and Development Inc | No
Dozier |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Bratton Solar | No
Drake Fuller |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | BRCO Constructors | No
Drakesbad |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Breen Trucking | No
Dry Creek |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Brenda Enterprises | No
Drytown |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Brendon Connoly | No
Duncan Springs |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Brett Alcorn | No
Duncans Mills |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Brett Van Moler | No
Dunlap |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Brian Bauer | No
Dunnigan |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Brian Doyle Construction | No
Dustin Acres |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Brian Minix | No
Duveneck St Francis |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Brian O-Rear | No
East Biggs |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Brian Thompson | No
East Campus |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Briceno Landscape | No
East Dobern |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Brickyard Cove Marina | No
East Nicolaus |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Bridgeway Civil Constructors Inc | No
East Northside |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bright Construction | No
East Oakdale |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Brighten Landscaping | No
East Orosi |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | BrightView Tree Service | No
East Quincy |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Briseno's Landscape and Tree Service | No
East Richmond Heights | Contra Costa | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Brite Electric | No
East Shore |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Broadband Integrators | No
East Sonora |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Broadway Burlingame Apartments | No
East Virginia |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Brock Construction | No
East West Courts |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Broderson Concrete | No
Easton |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Brookfield Residential | No
Echo Lake |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Brooks Landscaping | No
Eden |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Brookview Park | No
Eden Valley |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Brothers Iron | No
Edenvale |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Brothers Landscaping | No
Edge |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Brother's Service Tree Care | No
Edison |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Broward Builders | No
Edmiston |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Brown & Fesler | No
Edmundson Acres |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Brown Construction | No
Edna |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Brownco Construction | No
Edwin |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Browning Contractors | No
El Camino Kiely |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Browning Electric Co | No
El Camino Las Palmas |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bruce Company | No
El Camino Los Padres |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Brunner Associates | No
El Camino The Alameda |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Brush Munchers | No
El Dorado | El Dorado | Sierra | Northern | PG&E GISWeb | [14 empty] | BRW Concrete | No
El Macero |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Bryan Hartley | No
El Nido |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Bryan's Welding | No
El Pinal |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Bryland Contracting and Electrical | No
El Portal |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | BSLA Creations | No
El Rancho Verde |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Buchanan and Sons | No
El Rio Villa |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Buchholz Landscaping | No
El Roble |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Buckley Plumbing | No
Elders Corner |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Bud Garmin Construction | No
Elderwood |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Bud Manter | No
Eldridge |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Buddy Griggs Plumbing | No
Electra |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Budget Plumbing Inc | No
Elk |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Build and Design | No
Elk Creek |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Buildcom Construction | No
Elkhorn |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | BuildZig | No
Elm View |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Bull's-Eye Drilling | No
Elmhurst |  | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Bullseye Leak Detection Inc | No
Elmira |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Bullseye Plumbing | No
Elmo |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Burdick Excavating | No
Emigrant Gap |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Burkett's Pool Plastering | No
Englewood |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Burlington Homes | No
Enson |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Burtson Construction | No
Enterprise |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Burwell Electric | No
Erikson |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Bush Construction | No
Esquon |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Butte County | No
Estates |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Butterfield Electric | No
Esther Clark Park |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | BZ Construction Co | No
Estrella |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | BZ Plumbing Co | No
Etheda Springs |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | C Deleon Construction | No
Ettersburg |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | C Hammond Construction | No
Eugene |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | C Lopez Yard Maintenance | No
Evans |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | C Overaa & Company | No
Everdale Neimen |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | C&A Builders | No
Evergreen |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | C&C Construction | No
Evergreen Park |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | C&E Remodeling | No
Excelsior |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | C&J Fencing | No
Fair Play |  | Sierra | Northern | PG&E GISWeb | [14 empty] | C&L Construction | No
Fairmeadow |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | C&N Builders | No
Famoso |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Ca Construction | No
Farm Dr. |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Cab Construction | No
Farmington |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Cable Network Construction | No
Feather Falls |  | North Valley | Northern | PG&E GISWeb | [14 empty] | CableCom | No
Felix |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Caccia Plumbing | No
Fellows |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Caesar Eletric | No
Fenton McCollan |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Caggiano General Engieneering | No
Fergus |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Caglia Demolition and Recycling | No
Fern |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Cagwin & Dorward | No
Fernbridge |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Cahill Construction | No
Ferrari Pinoche |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Cal Fence | No
Fiddletown |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Cal Sierra Construction | No
Fieldbrook |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Cal Trans | No
Fields Landing |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Cal Valley Construction | No
Financial District |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Cal Valley Contractors | No
Finley |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Cal Water Service | No
Fish Camp |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Cal-Am Water | No
Fish Rock |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Calco Fence Inc | No
Fisherman's Wharf |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Cal-Electric | No
Five Corners |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | California American Water | No
Five Points |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | California Cable Ops | No
Five Wounds |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | California Concrete | No
Flickinger North |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | California Conservation Corps | No
Flickinger South |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | California Cut & Core | No
Flournoy |  | North Valley | Northern | PG&E GISWeb | [14 empty] | California Design Solutions | No
Fluhr |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | California Dreamin | No
Flumeville |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | California Fence Company | No
Foppiano |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | California Prime Properties | No
Forbes Bucher |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | California Retaining Walls | No
Forbestown |  | North Valley | Northern | PG&E GISWeb | [14 empty] | California Solar | No
Ford City |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | California Sunrooms | No
Forebay |  | Sierra | Northern | PG&E GISWeb | [14 empty] | California Trench Lift | No
Forest |  | Sierra | Northern | PG&E GISWeb | [14 empty] | California Trenchers | No
Forest Hill |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | California Trenchless | Yes
Forest Hill Extension |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | California Utility Construction | No
Forest Meadows |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | California Water Service | No
Forest Ranch |  | North Valley | Northern | PG&E GISWeb | [14 empty] | California Waters | No
Foresta |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Calsan Consulting | No
Fort Seward |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Calscape | No
Fort Washington |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Calvas Hauling | No
Foss |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Cal-West Concrete Cutting | No
Fouts Springs |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Cal-West Sewer and Drain | No
Freedom | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Cam Construction | No
Freeport |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Camco Construction Electric | No
Freestone |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Cameron Electric | No
French Corral |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Campos EPC LLC | No
French Gulch |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Candy's Landscaping | No
Frenchtown |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Cannon's General Contractor | No
Fresh Pond |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Capital City Electric | No
Freshwater |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Capital Electric & Sign | No
Friant |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Capital Homes Investments | No
Fruitdale |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Capitol Valley Electric | No
Fruitdale College |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Carameza Const | No
Fruitdale Rexford |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Carberry Construction Inc | No
Fruitland |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Carlisle Construction | No
Fruitvale |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Carlos Ortiz | No
Fruto |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Carl's Paverstones | No
Fuller Acres |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Carmel Building & Design | No
Ganns |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Carone & Company Inc | Yes
Garberville |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Carrera Construction | No
Garden Alameda |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Carrol & Strong Builders Inc | No
Garden Farms |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Carty Construction | No
Garden Villa Monterey |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Carvajal Construction | No
Gardner |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Cascadian Landscape | No
Garey |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Case Pacific | No
Gas Point |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Casey Construction | No
Gateview |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Castellanos Construction and Landscape | No
Gavello Glen |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Catellus | No
Gawain Percivale |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Cavanaugh Paving & Grading | No
Genesee |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Cazadores Construction | No
Georgetown |  | Sierra | Northern | PG&E GISWeb | [14 empty] | CB Concrete Construction | No
Geyserville |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | CB Home Improvement | No
Gibsonville |  | Sierra | Northern | PG&E GISWeb | [14 empty] | CB2 Builders Inc | No
Gilchrist |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | CBC General Contractor | No
Gillis |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | CBS Electric | No
Glen Crest |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Ccid | No
Glen Park |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | CCK Builders | No
Glenblair |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | CE Cox General Engineering | No
Glenbrook |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Cem Construction | No
Glenburn |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Cemcon Inc | No
Glencoe |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | CenCal Pacific | No
Glencove |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Cener Point Development | No
Glenhaven |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Center Plumbing | No
Glenn | Glenn | North Valley | Northern | PG&E GISWeb | [14 empty] | Central Backhoe Service | No
Glenview Serenity |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Central California Fencing | No
Glider |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Central Ccc Sanitary District | No
Glorietta |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Central Coast Landscape & Maintenance | No
Gold Flat |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Central Coast Playgrounds | No
Gold Hill |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Central Fence | No
Gold Run |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Central Plumbing & Sewers | No
Golden Gate |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Central Tie | No
Golden Gate Heights |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Central Valley Concrete Inc | No
Goldtree |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Central Valley Engineering | No
Goodmill |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Central Valley Lawnscapes | No
Goodyear Mastic |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Century Landscape | No
Goodyears Bar |  | Sierra | Northern | PG&E GISWeb | [14 empty] | CEO Construction | No
Gorda |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Cerna Construction | No
Gordon |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | CF Archibald Paving Inc | Yes
Gordy |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | CF Engineering | No
Gosford |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Challenge Rooter | No
Grand Island |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Chalmers Development | No
Grangeville |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Chamberlain Landscaping | No
Granite Creek |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Chamberland Backhoe | No
Granite Springs |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Champagne Landscaping | No
Graniteville |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Chan Drainage | No
Grant Road Sylvan Park Area |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Chandler Construction | No
Grapevine |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Chaney's Bobcat Service | No
Grapit |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Charles Keller Construction | No
Gravesboro |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Charles White | No
Grayson |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Charlie Rubert | No
Graystone |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Charlie's Heating and Plumbing | No
Great Oaks |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Chavarin General Contractor | No
Greater Miranda |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Chavez Garden Service | No
Greeley Hill |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Cheap Sac Homes LLC | No
Green Acres |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Cheezman Concrete | No
Greenmeadow |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Chernoh | No
Greenville |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Chiapa Welding | No
Greenwood |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Chico's Fence | No
Gregg |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Chin Landscape | No
Greylands |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Chris Construction | No
Grimes |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Chris Dicharry Construction | No
Grizzly Flats |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Chris Hughes | No
Groveland |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Chris Plumbing Bay Area Services | No
Guadalupe Almaden |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Chris Tran | No
Guadalupe Canoas |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Chris Wilson Plumbing & Heating | No
Guadalupe Oak Grove |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Chris Wolf | No
Gualala |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Chrisp Company | No
Guerneville |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Christ Centered Construction | No
Guernewood |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Christenson Construction | No
Guernsey |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Christinsen Irrigation Inc | No
Guinda |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Christopher Gates Construction | No
Hacketsville |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Christopherson Const | No
Haight Ashbury |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Church Of Jesus Christ Of The Latter Day Saints | No
Halcyon |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Ciaran Horgan | No
Hales Grove |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Cima Plumbing | No
Halfway House |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Cisco Landscaping | No
Halls Corner |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Citizen Electric | No
Hamann Park |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City Front Plumbing | No
Hamblin |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | City of Alameda | No
Hamilton Branch |  | North Valley | Northern | PG&E GISWeb | [14 empty] | City of Antioch | No
Hammer |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Arcata | No
Hammonton |  | Sierra | Northern | PG&E GISWeb | [14 empty] | City of Bakersfield | No
Hannah Gregory |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Belmont | No
Happy Valley |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | City of Berkeley | No
Harbin Springs |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | City of Brisbane | No
Hardwick |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | City of Burlingame | No
Hardy |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | City of Burlingame | No
Harmony |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | City of Chowchilla | No
Harpertown |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | City of Citrus Heights | No
Harris |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | City of Clovis | No
Hartland |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | City of Colusa | No
Hartley |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | City of Dos Palos | No
Hat Creek |  | North Valley | Northern | PG&E GISWeb | [14 empty] | City of Fair Oaks | No
Hathaway |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Fairfax | No
Hathaway Pines |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | City of Fairfield | No
Hawkins Bar |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | City of Firebaugh | No
Hayes |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Folsom | No
Hayes Valley |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | City of Fortuna | No
Hazelton |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | City of Foster City | No
Hearst |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | City of Fresno | No
Heather Glen |  | Sierra | Northern | PG&E GISWeb | [14 empty] | City of Gustine | No
Hellyer |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Isleton | No
Helm |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | City of Keyes | No
Henderson Village |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | City of Livermore | No
Henleyville |  | North Valley | Northern | PG&E GISWeb | [14 empty] | City of Lodi | No
Henry |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | City of Los Altos | No
Hensley |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Los Banos | No
Herald |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | City of Los Gatos | No
Heritage |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Madera | No
Heritage District |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | City of Manteca | No
Hermes |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Marina | No
Herndon |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | City of Martinez | No
Hidden Glen |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Marysville | No
Hidden Glen South |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Mendota | No
Highlands-Baywood Park |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | City of Menlo Park | No
Hights Corner |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | City of Mill Valley | No
Highway City |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | City of Modesto | No
Hillcrest |  | North Valley | Northern | PG&E GISWeb | [14 empty] | City of Napa | No
Hillmaid |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | City of Nevada | No
Hills Ferry |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | City of Oakland | No
Hills Flat |  | Sierra | Northern | PG&E GISWeb | [14 empty] | City of Petaluma | No
Hillsdale |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Pittsburg | No
Hillview |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Redwood City | No
Hillview South |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Richmond | No
Hobergs |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | City of Rohnert Park | No
Hoboken |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | City of Roseville | No
Holland |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Sacramento | No
Hollis |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | City of Salinas | No
Holly Oaks |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of San Carlos | No
Hollywood |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of San Francisco | No
Holmes |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | City of San Joaquin | No
Holt |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | City of San Jose | No
Holy City |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | City of San Mateo | No
Home Garden |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | City of San Rafael | No
Homestead Kiely |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Santa Clara | No
Honcut |  | North Valley | Northern | PG&E GISWeb | [14 empty] | City of Santa Cruz | No
Honeydew |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | City of Santa Maria | No
Hood |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | City of Sebastopol | No
Hookton |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | City of Sonoma | No
Hoopa |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | City of South San Francisco | No
Hopeton |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | City of Stockton | No
Horrace Mann |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | City of Sunnyvale | No
Hough Springs |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | City of Vacaville | No
Huasna |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | City of Vallejo | No
Hughes Mill |  | Sierra | Northern | PG&E GISWeb | [14 empty] | City of Watsonville | No
Hume |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | City of Willits | No
Hunters Point |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | City of Woodland | No
Huntley |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | City of Yuba City | No
Hurleton |  | North Valley | Northern | PG&E GISWeb | [14 empty] | City Ventures Construction | No
Hyde Park |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Civil Engineering Construction Inc | No
Hydesville |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Civitaf Corp | No
Hydril |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Cl Landscape | No
Ignacio |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Clark Colony Water Company | No
Igo |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Claros Construction | No
Incline |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Clawson Construction Inc | No
Independence |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Clean Harbors | No
Indian Falls |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Clear Heart Drilling | No
Indian Gulch |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Cleary Bros Landscape Inc | Yes
Indianola |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Cliff Swisher Custom Concrete | No
Ingle |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Clifton Heating & Plumbing | No
Inglenook |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Clough Construction | No
Ingleside |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Clyde G Steagall Inc | No
Ingleside Heights |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | CNE Construction | No
Ingleside Terrace |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | CNH Landscape Services | No
Ingomar |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | CNV Landscaping Corporation | No
Ingot |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Coast Landscape Management | No
Inner Parkside |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Coast Pipeline | No
Inner Sunset |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Coast Water District | No
Inskip |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Coastal Lumber | No
Inverness |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Coastal Paving | No
Inwood |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Coastal Plumbing | No
Iowa Hill |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Cobabe Brothers Plumbing | No
Irmulco |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Cogliandro Construction | No
Iron Mountain |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Cole Tiscornia Construction | No
Irvington |  | Mission | Central Coast | PG&E GISWeb | [14 empty] | Colebank Construction | No
Irwin |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Collin Electrical | No
Island Mountain |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Collins and Son Construction | No
Ivesta |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Collins Electric | No
Jacinto |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Colombia Electric | Yes
Jacksnipe |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Colt Sawickis | No
Jackson Taylor |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Colusa Indian Community | No
Jamesburg |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Combs Fencing | No
Jamestown |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Comcast | No
Jastro |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Commercial Landscape Maintenance | No
Jenner |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Community Realty Property Management | No
Jenny Lind |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Complete Environmental | No
Jerseydale |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Con Quest Contractors | Yes
Jesus Maria |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Concept 2 Completion | No
Joaquin Miller |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Concept Construction | No
Johnsons |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Concrete America | No
Jolon |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Concrete By Moore | No
Jonesville |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Concrete Demo Works | No
Jordan Park |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Concrete Value Corp | No
Jose Figueres Rancho Verde |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Condon Johnson & Associates | Yes
Julian St James |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Condor Construction | No
Junipero Serra |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Conlin Fence Co | No
Jupiter |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Conner Construction | No
Kaweah |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Conover Landscape | No
Keddie |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Con-Quest Contractors | No
Kekawaka |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Conroy Construction | No
Kelly Ridge |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Conscapes | No
Kelsey |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Consolidated Plumbing | No
Kern City |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Construct and Maintain Corp | No
Kern Lake |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Construction 37 | No
Kernell |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Construction Dynamic Co | No
Keswick |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Consulting Management Construction | No
Kett |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Continental Electric | No
Kettleman |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Contra Costa Water District | No
Kettman Pomeroy |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Contractor: Aaron Taylor | No
Keystone |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Contractor: Aisa Siu | No
Kibesillah |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Contractor: Allie Rudy | No
Kilowatt |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Contractor: Andres Arriola | No
King Salmon |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Contractor: Anthony Sanchez | No
Kingsville |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Contractor: Chris Rodriguez | No
Kingvale |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Contractor: Daniel Ruiz | No
Kirkville |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Contractor: David Allen Louper | No
Kirkwood |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Contractor: Elias Sanchez | No
Kismet |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Contractor: George Gomez | No
Kit Carson |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Contractor: Jeremy Rich | No
Klau |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Contractor: Jesse Gonzalez | No
Knights Bridge |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Contractor: Joe Silva | No
Knights Ferry |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Contractor: Joe Wood | No
Knights Landing | Yolo | Sacramento | Northern | PG&E GISWeb | [14 empty] | Contractor: Jose Cruz | No
Knightsen |  | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Contractor: Malcom Miller | No
Knob |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Contractor: Mike Kaiser | No
Knowles |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Contractor: Peter McDonough | No
Knoxville |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Contractor: Ramon Tamayo | No
Kollmar |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Contractor: Ray Ruiz | No
Kooser |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Contractor: Ron Lurenko | No
Korbel |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Contractor: Steve Ferreira | No
Kyburz |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Contractor: Tom Richards | No
La Colina |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Contractor: William Melendez | No
La Grange |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Contractors Services Company | No
La Honda |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Controller's Office | No
La Honda Park |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Cook Construction | No
La Jolla Ranch |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Cook Engineering | No
La Porte |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Cook Environmental | No
La Vina |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Cook's Peninsula Pools | No
Lacjac |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Cornerstone Earth Group | No
Ladera |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Corrigan Construction | No
Lagunitas |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Cory's Plumbing | No
Lake Almanor Country Club |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Covenant Construction | No
Lake Almanor Peninsula |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Cowan & Thompson Construction | No
Lake Almanor West | Plumas | North Valley | Northern | PG&E GISWeb | [14 empty] | Cox and Cox Construction | No
Lake Alpine |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Cox Cement Works | No
Lake California |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Cozart Building Inc | No
Lake City |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Craig Turner Construction | No
Lake Don Pedro |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Cratus Inc | Yes
Lake Nacimiento |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Craven Landscaping | No
Lake of the Pines |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Creative Environments | No
Lake Wildwood |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Creative Fence & Wall | No
Lakehead |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Creative Gates Inc | No
Lakehouse |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Creative Home Surfaces | No
Lakeside |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Creative Landscape Service | No
Lakeview |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Crop Production Services | No
Lakeville |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Crosby Homes | No
Lakewood |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Crosswoods Homeowners Association | No
Lanai Cunningham |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Crown Fence | No
Lanare |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Cruikshank Landscape Construction | No
Landco |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Crusader Fence | No
Lane |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Cruz Rodriguez | No
Larkfield |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Crystal Blue Plumbing Heating and Air | No
Las Flores |  | North Valley | Northern | PG&E GISWeb | [14 empty] | CS Development & Construction | No
Las Lomas |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | CSI Construction | No
Las Palmas |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | CSI Engineering | No
Last Chance |  | Sierra | Northern | PG&E GISWeb | [14 empty] | CT Brayton and Sons | No
Laton | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Cuevas Lumber and Fence | No
Latrobe |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Cukos Ornamental Iron | No
Laughlin |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Cull Plumbing | No
Lawrence |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Cultivated Landscape Management | No
Le Grand |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Cupertino Electric | Yes
Lebec |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Cupertino Plumbing | No
Leesville |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Curran Family Trust | No
Leggett |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Curtis Drilling Company | No
Leland Manor Embarcadero Oaks Garland Drive |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Curtis Edward Dennison Landscape | No
Lerdo |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Curtis Landscape | No
Lexington Hills |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Custom Grading | No
Lexington Maria |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Custom Yardscape | No
Leyva |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | CVE Demolition | No
Lincoln Bellomy |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | CW Fox Construction | No
Lincoln Village |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | CWG Demolition & Hauling | No
Linda Rural |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Cxencal Demolition | No
Lingard |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Cypress Coast Fence | No
Little Branham Rosswood |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | D and B Farms | No
Little Grass Valley |  | North Valley | Northern | PG&E GISWeb | [14 empty] | D McDonald Development Inc | No
Little Portugal North |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | D&B Plumbing | No
Little Portugal South |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | D&B Trenching | No
Little River |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | D&D Pipelines | Yes
Little Valley |  | North Valley | Northern | PG&E GISWeb | [14 empty] | D&H Landscaping | No
Llagas-Uvas |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | D&J Plumbing | No
Locans |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | D&L Construction | No
Lochridge Luby |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | D&M Construction | No
Lockwood |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | DA Wood Construction | Yes
Lodoga |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Dadco Construction | No
Logandale |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Dale Excavating | No
Loganville |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Dale Huff Property Management | No
Lokern |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Dale Strand & Son Excavating | No
Lokoya |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | DALEO Inc | No
Loma Mar |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Dale's Botanical Gardens | No
Loma Verde |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Dale's Excavating | No
Lombard |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Dalian Construction Inc | No
Lomo |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Damian Rincon | No
Lompico |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Dan Costa Inc | No
London |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Dan Fix Landscape | No
Lone Bluff |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Dan McGuire | No
Lone Hill Highlands |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Dan Young Construction | No
Lone Star |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Dan Zazzeron | No
Long Barn |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Dance Builders | No
Longvale |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Danco | No
Longville |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Daniel Herrerra Garcia | No
Lonsmith |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Daniel Martinez | No
Loomis Corners |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Daniel Nevezi | No
Los Alamos |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Daniel O Davis Inc | No
Los Arboles |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Daniel Spatz | No
Los Berros |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Dan's Construction | No
Los Molinos |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Dantoni's Welding | No
Los Olivos | Santa Barbara | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | DAR Construction | No
Los Paseos |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Darcy & Harty Construction Inc | Yes
Los Ranchos |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Darrel Dahms Electric | No
Lost Hills |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Darrel Varni Electric | No
Lotus |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Darren Taylor Construction | No
Lovelock |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Darrin G Stanley Engineering | No
Lower Lake |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Darrin's Tractor Service | No
Lowlanders |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Dave Brooks Construction | No
Loyola Corners |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Dave Christian Construction | No
Lucerne |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Dave Greenetz Construction | No
Lucia |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Dave Martinez | No
Luz |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Dave Singh | No
Lynbrook |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Dave's Electric Al Repair | No
Lynhaven |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | David C Dunn | No
Lyonsville |  | North Valley | Northern | PG&E GISWeb | [14 empty] | David Casarez Excavating | No
Mad River |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | David Green Construction | No
Madison |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | David Hall Masonry | No
Magliocco Huff |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | David Hill | No
Magra |  | Sierra | Northern | PG&E GISWeb | [14 empty] | David Landscaping | No
Majestic |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | David Mitchell | No
Makati |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | David Orozco | No
Manchester |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | David Rainey Construction | No
Manila |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | David's Bridal | No
Manteca Junction |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Dawson-Mauldin Construction | No
Manton |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Day's Generator Service | No
Manzanita Lake |  | North Valley | Northern | PG&E GISWeb | [14 empty] | DC Jones & Sons Inc | No
Maple Grove |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | DC Metals | No
Marin City |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | DCI Builders | No
Marinwood |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | DCW Contractors | No
Mark West |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | De Haro Ramirez Group | Yes
Market Almaden |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | De Mattei Construction | No
Markingdon |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | De Silva Gates Construction | No
Marshall |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | De Witt Bros & Company | No
Martell |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | DEARCOS | No
Martinville Vineyard |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Decibels Inc | No
Mather |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Decon Environmental Services | No
Matheson |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Del Curto Brothers Construction | No
Mattei |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Del Oro Water Company | No
Mauricia Kiely |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Del Secco Diamond Core & Saw | No
Maxwell | Colusa | Sacramento | Northern | PG&E GISWeb | [14 empty] | Del Sol NRG | No
Mayaro |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Delamore Fencing | No
Mayfair |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Delbert Johnson | No
Mayfair North |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Delgado Construction | No
Mayfair West |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Dellabarca Design & Build | No
Mayglen Little Rock |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Delta Bay Concrete Cutting Inc | No
McClellan Park |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Delta Grinding | Yes
McKay Ringwood |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Deluxe Shotcrete and Concrete Construction | No
McKinley |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Demarcus Drainage Co | No
McKuen |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | DeMiguel Plumbing | No
Meadow Fair |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Demings Demo | No
Meadow Lakes |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Demo Masters Inc | No
Meadow Valley |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Dennis Bruni | No
Meadows |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Dennis Cook Enterprises | No
Melbourne |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Dennis Dechance Construction | No
Melody |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Denny McCowan General Engineering | No
Melones |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Denova Drilling | No
Mendocino |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Dermot Barry Construction | No
Merced Falls |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | DeVaney Engineering | No
Merced Heights |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Devengenzo Co | No
Merced Manor |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Dewitt Bishop Masonry | No
Mercey Hot Springs |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | DHR Construction | No
Meridian Pedro |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Diablo Fence Co | No
Mettler |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Diablo General Engineering | No
Mexican Colony |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Diablo Landscape | No
Meyers |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Diamond D Engineering | No
Michigan Bluff |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Diamond Pavers | No
Midpines |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Diamond Tree Service | No
Midtown |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Diaz Electric | No
Midtown Terrace |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Diaz Fencing | No
Midway |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Dic Dinsmore Landscape | No
Miles |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Diede Construction | No
Miley |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | DiMaggio Electric | No
Mill Creek |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Dinos Manolouis | No
Millich Phelps |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Dirt Movers | No
Mills Orchard |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Dirt Worx | No
Millux |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Discount Backhoe | No
Millville |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Discount Plumbing | No
Milton |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Discovery Builders | No
Mina |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Diversified Utility Services | No
Miner |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Divide Plumbing | No
Mineral |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Dixon Fence Co | No
Minkler |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | DJ Balling Construction | No
Minnesota |  | North Valley | Northern | PG&E GISWeb | [14 empty] | DJ Construction | No
Minter Village |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | DJ Rocha Trucking and Crushing | No
Minturn |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | D-Kal Engineering | No
Miraloma Park |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | DL Falk Construction | No
Miramar |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | DL Plumbing | No
Miramonte |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | DLMN Enterprises | No
Miramonte Springer Road Area |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | DM Gates Builders | No
Miranda |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | DMC Construction | No
Mission Hills |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Docs Mobile Service | No
Mission Terrace |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | DOD Construction | No
Missouri Triangle |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Dogtown Development | No
Mitty |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Doherty Restoration and Construction | No
Mi-Wuk Village |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Dolezal Construction | No
Moccasin |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | DOMCO Plumbing Inc | No
Moffett Field |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Dominic Petrilla | No
Moffett Whisman Road Area |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Domus Construction | No
Mokelumne City |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Don Anderson Landscaping | No
Molena |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Don Chapin Construction | No
Monmouth |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Don Cornuelle | No
Mono Vista |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Don L Dostal Const | No
Monroe Bowers |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Don Lawley Construction | No
Monroe Park |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Don Shively Masonry Inc | No
Monson |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Donald Cartensen | No
Monta Loma Farley Rock Street Area |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Donald Mount Construction | No
Montalvin Manor |  | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Donisi Landscape Construction | No
Monte Rio |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Donny Yard Service | No
Monte Vista |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Doran Construction | No
Monterey Heights |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Dorantes Landcaping | No
Monterey Park Tract |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Dory Bros | No
Montevideo |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Double O Engineering | No
Montezuma |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Doug Auger Landscape | No
Montgomery Creek |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Doug Sanders Concrete | No
Monticello |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Doug Veerkamp Engineering | No
Monument Hills |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Douglas Landscape | No
Mooney Flat |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Douglas M Butler | No
Moonstone |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Doumit Construction | No
Morada |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Down To Earth Landscaping | No
Mormon |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Down Under Piping | No
Mormon Bar |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Downing Construction | No
Morrill |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | DPW | No
Moskowite Corner |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | DR Horton | No
Motor City |  | Sierra | Northern | PG&E GISWeb | [14 empty] | DR Lemings Construction | No
Mount Davidson Manor |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Drain Doctor | No
Mount Eden |  | Mission | Central Coast | PG&E GISWeb | [14 empty] | Drain Masters | No
Mount Hamilton |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Drain Pro | No
Mount Pleasant |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Drain Works Plumbing Company | No
Mount Pleasant North |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | DRB Homes and Design | No
Mount Pleasant South |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Dream Home Investments | No
Mountain Gate |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Drill Tech | Yes
Mountain Ranch |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | DripTech | No
Mountain Shadows |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | DRT Grading & Paving | No
Muir |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Drummond and Sons Pools | No
Muir Beach |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Drury Homes | No
Murillo |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | DRYCO Construction | No
Murray |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | DSM Construction | No
Myricks Corner |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | DSW AG Inc | No
Myrtletown |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | DT Real Estate Investment | No
Naglee Park |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Duarte Construction | No
Napa Soda Springs |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Ducharme Construction | No
Nashville |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Duco Construction | No
Navarro |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Dudley's Excavating Inc | No
Navelencia |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Duke Sherwood Contracting Co | No
Nelson |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Duleys Landscaping | No
Neufeld |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Dun Rite | No
New Almaden |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Duplan Construction | No
New Auberry |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Duran & Venables | No
New Cuyama | Santa Barbara | Kern | Central Valley | PG&E GISWeb | [14 empty] | Duran Construction | No
Newburg |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Duran Fencing | No
Newhall Sherwood |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Durden Construction | No
Newport |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Durham Stabilization | No
Newtown |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Duro Concrete Inc | No
Newville |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Dutna Farms | No
Nicasio |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Duval Construction | No
Nice |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Duvall Plumbing | No
Nichols |  | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Duvoli Construction | No
Nicolaus |  | Sierra | Northern | PG&E GISWeb | [14 empty] | DW Young Construction Company | Yes
Niles |  | Mission | Central Coast | PG&E GISWeb | [14 empty] | Dynamic Electric | No
Nimbus |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Dynamic Electrical Contracting Inc | No
Nimshew |  | North Valley | Northern | PG&E GISWeb | [14 empty] | E Builders | No
Nipinnawasee |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | E Gwerder and Sons Construction | No
Nob Hill |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | E Ponce & Sons | No
Noble |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Eagle Construction | No
Noddin |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Eakle Construction | No
Noe Valley |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Earl Winn | No
Nord |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Earls Plumbing | No
Norden |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Earth Party Landscaping | No
Norman |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Earth Sculpting Consultants | No
Norris Canyon |  | Mission | Central Coast | PG&E GISWeb | [14 empty] | Earth Works | No
North Beach |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Earthbound Farms | No
North Bloomfield |  | Sierra | Northern | PG&E GISWeb | [14 empty] | EarthLines Landscape Development | No
North Campus |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Earthscapes Landscaping | No
North Coast |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | East Bay Landscaping and Handyman Services | No
North Columbia |  | Sierra | Northern | PG&E GISWeb | [14 empty] | East Bay Metal & Fence | No
North Dinuba |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | East Bay Stump Removal | No
North El Dorado |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Eastern Landscape | No
North Lakeport |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Eastwood Development | No
North Los Altos |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Ebenich Construction | No
North San Juan |  | Sierra | Northern | PG&E GISWeb | [14 empty] | EBI | No
North Shafter |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | EBMUD | No
North Woodbridge |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Eco Landscape Management | No
Northern Cross |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Ecological Concerns | No
Northlake |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Ed Arent | No
Northspur |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Ed Briggs | No
Northwood |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Ed Horn | No
Norton |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Ed Loo Masonry | No
Norwood |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Ed Smith General Contractor | No
Notarb |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Eddi Carbajale | No
Notting Hill Royal Crest |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Eddie Axner Construction | No
Noyo |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Eddie Mullins Landscaping | No
Nubieber |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Eddie Serrato | No
O Neals |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Eddie's Lawn Service | No
Oak Canyon |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Edenbridge Homes | No
Oak Grove |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Edgar Williams | No
Oak Ridge |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Edgir Magama | No
Oak Run |  | North Valley | Northern | PG&E GISWeb | [14 empty] | EDT Tec | No
Oak Shores |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Edwin Alberto Diaz Concrete | No
Oaks |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | EE Gilbert Construction | Yes
Oakville |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | EF Gomez | No
O'Brien Tract |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | EH Fence | No
Ocala |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Ehret Co | No
Occidental |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Eitzen Construction | No
Oceanview |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | EJ Construction | No
Ohlone |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | EJ Masonry | No
Oil Junction |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | EJ Plumbing | No
Olcott |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | EK Excavating | No
Old Adobe |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | EKY Builder Inc | No
Old Forbestown |  | North Valley | Northern | PG&E GISWeb | [14 empty] | El Capitan Environmental | No
Old Hopland |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | El Dorado Irrigation District | No
Old Los Altos |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | El Dorado Mobile Home Park | No
Old Palo Alto |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | El Dorado Pool & Spa | No
Old Port |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Elderd Bros Inc | No
Old River |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Elecix Electric | No
Old Station |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Elias Vella Gomez | No
Olema |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Elite Builders | No
Olinda |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Elite Iron Fencing | No
Olinder |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Elite Landscape Construction | No
Omega |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Elite Plumbing | No
Omo Ranch |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Elk Grove Builders Inc | No
Ono |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Elk Grove Water District | No
Ophir |  | Sierra | Northern | PG&E GISWeb | [14 empty] | EM Construction | No
Ordbend |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Emerald City Landcsaping | No
Oregon City |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Emergency Rooter | No
Oregon House |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Emmett Valley Construction | No
Orford |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Emmett's Excavation | No
Orick |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Empire Construction Inc | No
Orleans |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Empire Engineering | No
Oro Loma |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Empire Paving | No
Orrs Springs |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Enchanting Planting | No
Ortega |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Energy Protection Systems Group | No
Ortega Park |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Engelke Construction | No
Oster |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Engineered Soil Repairs | No
Outer Mission |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Engineering Remediation Resources Group | No
Outer Sunset |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Environmental Barber | No
Outingdale |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Environmental Landscape Solutions | No
Overfelt |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Environmental Resources Management | No
Oxalis |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Eoumon Landscape | No
Oxford |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Equipment Operator | No
Pacific Heights |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | ER Plumbing & Construction Inc | No
Paintersville |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Erasto Martinez | No
Pajaro |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Eric Addison | No
Pajaro Dunes |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Eric Johnson | No
Palmo |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Eric Kindseth Builders | No
Palo Alto Orchards |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Eric Larsen | No
Palo Cedro |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Eric Mayer | No
Palo Verde |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Erickson Excavation | No
Paloma |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Ernie's Plumbing | No
Pamlar Borello |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | ES7 Communications | No
Panama |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Esquivel Grading and Paving | Yes
Panama Park |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Esteban Ruiz | No
Panoche |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Estrada's Sewer | No
Paradise Park |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Etan Johnson Engineering Builders | No
Park Lorraine |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Ethan Conrad Properties | No
Parker |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Ethan's Service Plumbing | No
Parkfield |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Eugene Carew | No
Parkhill |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Evenflow Plumbing | No
Parklawn |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Evenflow Plumbing Company Inc | No
Parksdale |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Everest Plumbing and Drain | No
Parkside |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Evergreen Company Inc | No
Parkview |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Evergreen Landscape | No
Parkwood |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Evin Santos | No
Paseo |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | EWSF Inc | No
Paskenta |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Exaro Technologies | No
Patch |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Excel Electric Inc | No
Paulsell |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Excel Site Services | No
Paxton |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Exotic Flora Landscape | No
Payne |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Expericon Construction | No
Paynes Creek |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Expert Rooter and Plumbing | No
Peardale |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Express Concrete Cutting | No
Peltier |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Express Plumbing | No
Penitencia |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Express Rooter | No
Pennington |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Express Sewer and Drain | No
Pentland |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Exterior Design | No
Pentz |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Extreme Backhoe Services | No
Pepper Tree |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Extreme Excavation | No
Pepperwood |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | EZ Electric | No
Pepperwood Grove |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | EZ Plumbing | No
Pescadero |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Ezra Construction | No
Peters |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | F Chavez Bobcat & Trucking | No
Petrolia |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | F Loduca Co | No
Phillips |  | Sierra | Northern | PG&E GISWeb | [14 empty] | F Luna Construction | No
Phillipsville |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | F&F Steel and Stairway | No
Phoenix Lake |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Facio's Construction | No
Piedmont Hills |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Fajardo's Handyman | No
Piedra |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Falany Fence Company | No
Pierce |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Fall River Community Service | No
Pierce Ranch |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Far West Saftey | Yes
Piercy |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Farallon Co | No
Pike |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Farhat Construction | No
Pilot Hill |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Farid Azari | No
Pine Canyon |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Farrell Design | No
Pine Grove |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Farwest Safety | Yes
Pine Hills |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Faubel Construction | No
Pine Hollow |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | FBA Construction | No
Pine Mountain Lake |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | FCS Striping Sealing & Paving | No
Pinecrest |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Federal Paving Systems Inc | No
Pinecroft |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Fehn's Family Plumbing | No
Pinedale |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Felix Hernandez | No
Pinehurst |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Fence America | No
Pineridge |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Fence Corp | No
Pinnacles |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Fence Lifts | No
Pioneer |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Fence Masters | No
Pitco |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Fence Works | No
Pittville |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Fence World | No
Plainsburg |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Ferguson McHugh | No
Plantation |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Ferma Construction | Yes
Platina |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Ferreira Services Co | No
Playa Del Rey |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Ferrum Custom Fences | No
Pleasant Grove |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Fiberco Inc | No
Pleasant Valley |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Fidel Barragan | No
Pleasure Point |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Fidel Cuevas | No
Poco Way |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Fidelity Home Energy | No
Point Reyes Station |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Fili Home Support | No
Pollock |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Fincon | No
Pond |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Fine Line Sawing and Drilling | Yes
Ponderosa |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Fineline Construction | No
Ponderosa Park |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Finn Construction Services | No
Pondosa |  | North Valley | Northern | PG&E GISWeb | [14 empty] | First Assembly of God | No
Pope |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | First Impressions Fencing | No
Pope Valley |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | First Southern Baptist Church | No
Port Chicago |  | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Fisk Electric | No
Port Costa |  | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Fitzgerald Construction | No
Port Kenyon |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Fitzgerald Lanscape | No
Port San Luis |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Fitzpatric & Sons | No
Portal Inn |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Fitzpatricks Landscaping | No
Potrero Hill |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Five Points Construction | No
Pozo |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Flat Iron Kiewit | Yes
Pratton |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Flegels Construction | No
Prattville |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Fletcher's Plumbing | No
Presidio |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Flexus Plumbing | No
Presidio Heights |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Flick Enterprises | No
Priest |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Flora Farm Landscaping | No
Professorville |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Flora Rissetto and Sonds | No
Project City |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Florez Paving | No
Prospero |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Florin County Water District | No
Pruneridge Tantau |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Flow Contractors | No
Pulga |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Flow Line Contractors | No
Pumpkin Center |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Floyd Johnston Construction | No
Quartz |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Floyd Smith | No
Quimby |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | FMG Custom Concrete | No
Quincy |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Fontana Construction | No
Rackerby |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Fontenoy Engineering | No
Rainbow |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Forest Miller | No
Raisin City |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Forsythe General Contractors | No
Ralph |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Fortino Landscaping | No
Ramblewood |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Fortner Excavation | No
Rancho |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Foster Advantage Incorporated | No
Rancho Santa Teresa |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Foster Pumps Inc | No
Rancho Tehama Reserve |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Foundation Repair of California | No
Raynor Park |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Foundation Support of CA | No
Rayo |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Foundations First | No
Red Apple |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Four Dimensions Landscape | No
Red Corral |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Four Seasons Landscape | No
Red Dog |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Fowler Construction Inc | No
Redbanks |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Frame Building & Improvements | No
Redcrest |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Francies Electric | No
Redwood Estates |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Francisco Garcia | No
Reef Station |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Francisco Javier Zaragoza | No
Regina Heights |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Francisco Moreno Diaz | No
Reilly Heights |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Francisco Ruiz | No
Relief |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Frank Bonetti Plumbing | No
Rescue |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Frank Borges | No
Rheem Valley |  | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Frank Christman | No
Ribier |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Frank Medina Engineering | No
Rich Gulch |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Franklin Construction | No
Richardson Springs |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Franklin Construction Inc | No
Richfield |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Franklin Distillers | No
Richvale |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Frank's Septic Service | No
Ridgemark |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Franzoia Construction | No
Rio Bravo |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Freedom Fence | No
Rio Nido |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Freedom Pools | No
Rio Oso |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Freeds Excavation | No
Rio Vista Junction |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Fremont Fence | No
Ripperdan |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Fremont Paving | No
River Pines |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Fresno Construction | No
Riverbend |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Fresno House Movers | No
Riverdale Park |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Fresno Neon | No
Riverside Park |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Fresno Plumbing & Heating | No
Riverton |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Fresno Plumbing & Heating | No
Riverview |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Fresno Rescue Mission | No
Robbins |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Frontier Communications | No
Roberts Walnut Woods |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | FS Concrete | No
Robinson Mill |  | North Valley | Northern | PG&E GISWeb | [14 empty] | FS Construction | No
Robinsons Corner |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Fuchs Construction | No
Robles del Rio |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Fulks Fencing | No
Rock Creek |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Future Energy Savers | No
Rock Crest |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Future Landscape | No
Rockport |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | G Cox & Associates | No
Rockville |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | G Family Construction | No
Rodgers |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | G Family Landscaping Inc | No
Rogers |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | G Ramirez Concrete Inc | No
Rohnerville |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | G&D Modern Homes | No
Rolinda |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | G&F Agricultural Services | No
Rolling Hills |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | G&G Construction | No
Rollingwood |  | East Bay | Bay Area | PG&E GISWeb | [14 empty] | G&M Construction | No
Roosevelt Park |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | G&N Construction | No
Rose Garden |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | G&S Paving | No
Rose Glen |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gabe Mendez Inc | No
Rose Sartorette |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gabriel Minea | No
Rosemary Gardens |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gachina | No
Rosewood |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Galassi Brothers Construction | No
Rough and Ready |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Gallagher and Burk | Yes
Round Mountain |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Gallardos Construction | No
Rouse |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Galvan's Fencing | No
Rumsey |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Garcia & Sons Construction | No
Ruskin |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Garden Design and Construction | No
Russell |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Garden Lights Landscaping | No
Russian Hill |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Garden of Eden | No
Russian River-Coastal |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Garebear Landscape | No
Ruth |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Garnero Construction | No
Rutherford |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Garney Construction | No
Ryan |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Garrett Thompson Construction Inc | No
Ryde |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Gary | No
Ryland |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gary Brown Construction | No
Rymar |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gary Ledger Construction | No
Saco |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Garzac Plumbing | No
Sakamoto |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gate of Heaven Catholic Cemetery | No
Salmon Creek |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Gateway City Church | No
Salyer |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Gateway Fence Co | No
San Antonio Rengstorff Area |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Gateway Pacific Contractors | No
San Benito |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Gawfco Enterprises | No
San Emidio |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Gazebo Gardens | No
San Geronimo |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | GB Landscape | No
San Gregorio |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Gbortolotto | No
San Lorenzo Valley |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | GC Construction | No
San Lucas |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | GCI Solar | No
San Simeon |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | GD Nielsen | No
San Thomas Aquino |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Geer's Excavating | No
Sandy Gulch |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Gene Chappie Construction | No
Santa Clara El Camino |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Genera Remodelins Const | No
Santa Nella |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | General Building Engineering | No
Santa Rita Park |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | General Construction | No
Santa Venetia |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | General Engineering Technology | No
Saratoga Creek |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | General Plumbing | No
Saratoga Los Padres |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Genesis Landscape | No
Schellville |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Geoff Fleissner | No
Scotia |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | George Bics Plumbing | No
Scott Cabrillo |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | George Buehler | No
Scott Martin |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | George Hsu | No
Scottsville |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | George Rojas | No
Sea Ranch |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | George Salet Plumbing | No
Seguro |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | George Wilson Contracting | No
Seneca |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Geovac | No
Serenede |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gerald Berry Plumbing | No
Sereno del Mar |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Gerando Tamura Designs | No
Serrano |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Gerardo Gonzales | No
Seven Trees |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gerdeners Guild | No
Seville |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Geremia Pool | No
Shackelford |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Gesick Concrete | No
Shadow Brook 1 |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Get It Done Demolition Excavation | No
Shadow Brook 2 |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | GHI Hedgecock Paving | No
Shadowcrest |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Ghilotti Brothers | Yes
Shady Glen |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Ghilotti Construction | Yes
Shandon |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | GHS Construction | No
Sharon |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Gilbert Farms | No
Shasta |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Gilbert Granado | No
Shasta Hanchett Park |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gilliam & Sons Inc | No
Shawnee |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gilmore Const | No
Shaws Flat |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Gilroy Construction | No
Sheep Ranch |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Gilroy Electric | No
Sheldon |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Gilson Development | No
Shell Beach |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Ginder Developments | No
Shelter Cove |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Gino Stewart | No
Sherman Oaks |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Giovanis Landscaping | No
Sherwood Forest |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | GJ Gardner Homes | No
Shingle Springs |  | Sierra | Northern | PG&E GISWeb | [14 empty] | GJ Gentry General Engineering | No
Shirley |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | GJR Development | No
Shively |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Gladiator Plumbing | No
Shore Acres |  | Diablo | Bay Area | PG&E GISWeb | [14 empty] | GLG Construction | No
Sierra |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Global Sun Landscape | No
Sierra City |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Global Water Management Fathom | No
Sierra Village |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Globe & Son Paving | No
Sierramont |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gly-Co Farms | No
Silver Creek |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | GM Construction | No
Silver Leaf |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | GM Engineering | No
Silver Terrace |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | GM Landscaping | No
Silverado Resort |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Go DL LLC | No
Silverland |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gogo Rooter | No
Simmler |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Gold River Contractors | No
Simms |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Golden Bay Construction | Yes
Singletree |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Golden Bear Construction | No
Sisquoc |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Golden Bear Landscape Management | No
Sites |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Golden Empire Roofing | No
Sky Londa |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Golden Gate Electric | No
Skyhigh |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Golden Gate Seismic & Structural Inc | No
Sleepy Hollow |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Golden Gate Tank Removal | No
Sloughhouse |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Golden Green Landscaping | No
Smartsville |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Golden Green Landscaping | No
Smith Corner |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Golden State Builders | No
Snail |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Golden State Bulb Growers | No
Snelling |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Golden State Remodeling | No
Soda Bay |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Golden State Utility | No
Solyo |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Golden Stone Pavers | No
Somerset |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Golden West Engineering | No
Somes Bar |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Goldwing Engineering | Yes
Soulsbyville |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Goltermann Construction | No
South Beach |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Golz Excavating | No
South Campus |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gonella Property Management | No
South Dos Palos |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Gonzales Construction | No
South Fork |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Gonzalez Bobcat Service | No
South Los Altos |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Gonzalez Construction | No
South of Market |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Gonzalez Landscaping | No
South of Midtown |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Good Earth | No
South Woodbridge |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Goodfellas Construction | No
Southgate |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Goodfellow Topgrade Construction | Yes
Spanish Flat |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Gopher-It Trenchless | No
Spanish Ranch |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Gordon Cato | No
Spartan Keyes |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gordon N Ball Inc | Yes
Spreckels |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Gorman Pipelines | No
Spring Gap |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Gothic Landscape | No
Spring Hill |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Gounod Construction | No
Spring Valley |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | GR Sundberg Inc | No
Springfield |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Grade Tech | No
Squabbletown |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Graham Concrete | No
Squaw Hill |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Grand Prix Glass | No
Squaw Valley |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Granite Bay Custom Landscaping | No
St Clair Gardens |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Granite Bay Excavating | No
St. Francis Wood |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Granite Bay Local Landscaping | No
St. Leo's |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Granite Construction | Yes
St. Victor |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Granite Rock | Yes
Stafford |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Granlee's Landscape | No
Stallion Shadowsprings |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Grant Enterprise | No
Standard |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Gray Electric Co | No
Starbird |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Gray's Handy Repair | No
Stegeman |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Grayson Engineering | No
Stent |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Greater Independent Living | No
Stevinson |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Green Alchemy | No
Stewarts Point |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Green California | No
Stinson Beach | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Green Edge Landscaping | No
Stirling City |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Green Engineering | No
Stonegate East |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Green Environmental Landscape | No
Stonegate West |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Green Gables Inc | No
Stones Town |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Green Grass | No
Stonyford | Colusa | North Valley | Northern | PG&E GISWeb | [14 empty] | Green Growth Industries | No
Storrie |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Green Source Construction | No
Stratford |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Green Springs Landscape | No
Stratford Gardens |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Green Valley Structural Inc | No
Strawberry |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Green Vine Landscaping | No
Strawberry Park |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Greenbuilding Science Company | No
Strawberry Valley |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Greenerz Inc | No
Subeet |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Greengo Landscaping Inc | No
Sucro |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Greenhouse Landscape & Design | No
Suenos |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Greenscape Construction Inc | No
Sugar Pine |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Grenon & Sons Construction | No
Sugarloaf |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Griffen Lime Tree | No
Sultana |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Griffin Soil | Yes
Summer Creek |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Griffith Company | No
Summerdale |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Grizzly Construction | No
Summerside |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Ground Level | No
Summit City |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Ground Water Pump and Well | No
Sunny Brae |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Groundworks | No
Sunnyarts |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Grover Landscape | No
Sunnybrook |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | GRS Construction | No
Sunnyvale West |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | GTE Mobilnet | No
Sunol-Midtown |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Guadelupe Ruiz | No
Sunrise Almaden |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Guerra Construction Group | No
Sunset District |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Guodong Chen Electrical | No
Sunset View |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Gustin Schreiner Gustin Excavating | No
Sunshine Camp |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Guy's Fencing Inc | No
Sunspring |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Guzman Co | No
Surf |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | GW Demolition | No
Sutter Hill |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | H&D Electric | No
Suval |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | H&H Construction | No
Sweetland |  | Sierra | Northern | PG&E GISWeb | [14 empty] | H&H Electric | No
Sycamore |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | H&H Trenching | No
Sycamore Springs |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | H&N Landscaping | No
Sylvandale |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | H2O Plumbing | No
Sylvandale West |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Habitat for Humanity | No
Taft Heights |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Hal Hays Construction | No
Taft Mosswood |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Haley Contracting | No
Talmage |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Haley Underground Inc | No
Tamalpais Valley |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Half Moon Bay Grading and Paving | Yes
Tamarack |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Half Priced Plumbing | No
Tamien |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Hallroan and Stanley Construction | No
Tan Oak Park |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Handy Construction Team Inc | No
Tancred |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Handyman Chuck Bibb | No
Tanglewood El Monte |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Handyman Construction | No
Tassajara Hot Springs |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Handyman Services & Construction | No
Tatra |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Hankins Electrical | No
Taylorsville |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Hanson Brothers | No
Teal |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Harbor Bay Co | No
Telegraph City |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Hardcore Construction | No
Telegraph Hill |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Harder Excavation | No
Temelec |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Hardiman Construction | No
Terminous |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Harding Custom Builders | No
Terra Linda |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Hardway Concrete | No
Terrace Hills |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Harold Smith and Son | No
The Almaden Villas |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Harris Backhoe & Dump Truck Service Inc | No
The Greenhouse |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Harris Builders | No
The Villages |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Harris Construction | No
The Villas |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Harry Clark Plumbing | No
The Woods |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Harry Knepple | No
Thomas Lane |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Harty Pipelines | Yes
Thomasson |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Hawk Development | No
Thorn Junction |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Hawk Nin Lee | No
Three Rocks |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Haydon Construction | No
Thyle |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Haymac Construction | No
Tierra Buena |  | Sierra | Northern | PG&E GISWeb | [14 empty] | HB Ag Inc | No
Tiger Lily |  | Sierra | Northern | PG&E GISWeb | [14 empty] | HBC | No
Timber Cove |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | HBT Construction of California Inc | No
Toadtown |  | North Valley | Northern | PG&E GISWeb | [14 empty] | HCD Construction | No
Tobin |  | North Valley | Northern | PG&E GISWeb | [14 empty] | HCI | No
Tokay |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | HCL Construction | No
Tolenas |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | HCO Communications | No
Tollhouse |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Heavy Civil Engineering | No
Tomales |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Hector Flores | No
Toro |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Hector Madonado | No
Towle |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Hedgecock Paving | No
Townsend |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Heitz Construction | No
Toyon |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Helix Electric | No
Trade Winds |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Helmer and Sons Construction | No
Traver |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Helvetica Properties LLC | No
Treasure Island |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Hemington Landscape | No
Trent |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Henkels & McCoy | No
Tres Pinos |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Henry Jiang | No
Trigo |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Hensel Fencing | No
Trimmer |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Hensky Paving and Grading | No
Trinity Village |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Hensley Construction | No
Trinity-Klamath |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Hensley's Paving & General Engineering | No
Triple El |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Henson Plumbing Inc | No
Tropicana |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Hercules Tree Service | No
Trowbridge |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Herida Landscape | No
Troy |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Heritage Builders | No
Tudor |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Heritage Landscape | No
Tunnel Inn |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Herman Weissker Construction | No
Tuolumne |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Herman Weissker Construction | No
Tuolumne City |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Hernandez Engineering | Yes
Tupman |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Hernandez Landscaping | No
Turk |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Hess Consruction Co | Yes
Tuttle |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Hew Drilling Company | No
Tuttletown |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Hi Point Engineering | No
Twain |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Hidden Garden Nursery | No
Twin Bridges |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Higashi Farms | No
Twin Cities |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | High Construction | No
Twin Lakes |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | High Definition Solar | No
Twin Peaks |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Highgate Grass Valley LLC | No
Two Rock |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Highway Specialty Company | No
Tylers Corner |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Hilbers Incorporated | No
Una |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Hilbert Inc | No
Underwood Park |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Hill Construction Company | No
Union Hill |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Hillstone Landscape and Grading | No
Union Square |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Hing Wah Construction | No
University South |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | HM Construction | No
Upper Market |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Hocker Construction | No
Upper Sierra |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Hodges Electric | No
Vacaville Junction |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Hogan Land Clearing | No
Valdez |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Holiday Pools Construction | No
Vale |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Holt Cat Rental | No
Valle Vista |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Home & Garden Construction | No
Vallecito |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Home Grown Gardens Landscaping Co | No
Valley Acres |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Home Tech Systems | No
Valley Ford |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Homeowner | No
Valley Home |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Homes West | No
Valley View Reed |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Hooven and Co | No
Van Allen |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Hope Construction | No
Venola |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Hoppers Plumbing | No
Ventucopa |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Horizon Construction | Yes
Ventura |  | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Hot Line Construction | No
Verde |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Houser Septic | No
Vermont McKendrie |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Howe Electric | No
Verona |  | Sierra | Northern | PG&E GISWeb | [14 empty] | HP Communications Inc | No
Vichy Springs |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | HP Construction | No
Victor |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | HPS Mechanical | No
Villa Grande |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | HR Kleckner | No
Villinger |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | HSD Masonry | No
Vina |  | North Valley | Northern | PG&E GISWeb | [14 empty] | HT Construction Co | No
Vinci North |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Hudson Excavation | No
Vinci South |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Hughes Electric | No
Vineburg |  | Sonoma | Northern | PG&E GISWeb | [14 empty] | Hugo Cruz | No
Viola |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Hugo Medina | No
Virgilia |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Hugo Sanchez Construction | No
Virginiatown |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Huiltron Landscaping | No
Visitacion Valley |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Human Nature Designs | No
Vista Park |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Humboldt Community Utility Services | No
Volcano |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Humboldt Fence | No
Volcanoville |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Humboldt Landscape | No
Volta |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Hume Development | No
Vorden |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Humero Lugardo | No
Waddington |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Humphrey Plumbing | No
Wagner |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Humphreys Plumbing | No
Wahtoke |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Hung Construction | No
Walker Landing |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Hunter Electric | No
Wallace |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | HW & Williams | No
Walltown |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | I&J Builders | No
Walmort |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Ideal Engineering | No
Walnut Blossom |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Ideal Plumbing | No
Walnut Grove |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Iglesia De Dios - Templo El Ovivar | No
Walsh Station |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Ike's Landscape | No
Warburton Graham |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Image Broadband | No
Warmsprings |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Image Tree Services | No
Warner Valley |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Immobiliare Properties Inc | No
Washington |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Impact Construction | No
Washington Guadalupe |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Impact Demo and Hauling | No
Waterloo |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Imperial Contracting | No
Waukena |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | In and Out Plumbing | No
Wawona |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Incom Mechanical | No
Weed Patch |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Increte West | No
Weedpatch |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Independent Construction Company | No
Weimar |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Independent Engineering | No
Weitchpec |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Independent Irrigation Systems | No
Wellsona |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Indian Wells Valley Water District | No
Wengler |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Industrial Electrical Co | No
Weott |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Infinity Energy | No
West Colusa |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Innovation Construction & Design | No
West Manteca |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Innovation Construction and Electric | No
West Northside |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Innovative Communications | No
West Park |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Innovative Maintenance Solutions | No
West Point |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Insight Construction | No
West Portal |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Integrated Landscape Services | No
West Santa Teres Foothill |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Integrity Builders | No
West Valley |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Integrity Electric | No
Western Addition |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Intercity | No
Westhaven |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Interior Demolition | No
Westmont |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | International Line Builders | No
Westport |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Interrupcion Social Enterprise | No
Westside |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Interstate Concrete Pumping | No
Westville |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Interstate Fence Co | No
Westwood Highlands |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Interstate Grading & Paving | Yes
Westwood Park |  | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Intren | No
Whaley |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Iomlan Construction | No
Wheeler Ridge |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Ireland Robinson & Haley Inc | No
Whiskey Springs |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Irish Construction | No
Whiskeytown |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Irish Electric | No
Whispering Pines |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Iron Construction | No
White Hall |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Iron Mountain Engineering | No
White Pines |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Ironwood Builders | No
White Rock |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Irrigation Design & Construction | No
Whitethorn |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Irving Castillo | No
Whitley Gardens |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Iseal Flores | No
Whitlow |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Iseman Construction | No
Whitmore |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Isidro Lopez | No
Wible Orchard |  | Kern | Central Valley | PG&E GISWeb | [14 empty] | Isriel Godinez | No
Wilbur Springs |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Ivy Handyman | No
Wildflower |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | J and M Phillips | No
Wildwood |  | North Valley | Northern | PG&E GISWeb | [14 empty] | J Drains Rooter Service | No
Willota |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | J Flores Construction | No
Willow Creek |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | J Howard Engineering | Yes
Willow Glen |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | J Johnson Co | No
Willow Glen South Lincoln Glen |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | J Kroeker Inc | No
Wilseyville |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | J Matt McNickle | No
Wilsonia |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | J Moraga Construction | No
Wimp |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | J Rodriguez Garden Service | No
Winchester Forest |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | J&D Excavation Inc | No
Windmill Springs |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | J&J Mobile Welding | No
Wineland |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | J&L Construction | No
Witter Springs |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | J&M Inc | No
Wolf |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | J&S Asphalt | No
Woodacre |  | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Jack Spilman General Engineering | No
Woodbridge | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Jacks Patio Co | No
Woodlake Junction |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Jacobson Construction | No
Woodland Acres The Highlands |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Jacobson Trust | No
Woodlands |  | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Jaime's Landscaping | No
Woodleaf |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Jakela Inc | No
Woodside of Almaden |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Jamba Construction | No
Wooster 26th |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | James Ables | No
Wrightmont Corners |  | De Anza | Central Coast | PG&E GISWeb | [14 empty] | James Enterprise | No
Wyandotte |  | North Valley | Northern | PG&E GISWeb | [14 empty] | James Grossi Construction | No
Wyeth |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | James Lynch | No
Wyo |  | North Valley | Northern | PG&E GISWeb | [14 empty] | James Mellow Construction | No
Yankee Hill |  | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | James Simmons | No
Yankee Jims |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Janco Concrete | No
Yerba Buenna |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Janco Industries | No
Yettem |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Jared Collins | No
Yolano |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | Jaripeo Landscape | No
Yorkville |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | Jasmin Landscaping | No
Yosemite Lakes |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jason Abbott Construction | No
Yosemite Valley |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jason Abel Construction | No
Yosemite Village |  | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jason Eggert Construction | No
You Bet |  | Sierra | Northern | PG&E GISWeb | [14 empty] | Jason Magee | No
Youngstown |  | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Javier's | No
Yuba Foothills |  | North Valley | Northern | PG&E GISWeb | [14 empty] | Jaw Excavation | No
Yuba Pass |  | Sierra | Northern | PG&E GISWeb | [14 empty] | JB Becerra | No
Yuba Rural |  | Sierra | Northern | PG&E GISWeb | [14 empty] | JB Boring and Backhoe | No
Yum Yum Tract |  | San Jose | Central Coast | PG&E GISWeb | [14 empty] | JB Construction | No
Zamora |  | Sacramento | Northern | PG&E GISWeb | [14 empty] | JB Excavating | No
Zayante |  | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | JB Fence Company | No
Zediker |  | Fresno | Central Valley | PG&E GISWeb | [14 empty] | JB Fencing | No
Zenia |  | Humboldt | Northern | PG&E GISWeb | [14 empty] | JC Builders | No
Dobbins | Yuba | Sierra | Northern | PG&E GISWeb | [14 empty] | JC Construction | No
Garden Valley | Yuba | Sierra | Northern | PG&E GISWeb | [14 empty] | JC Guzman Construction | No
Linda | Yuba | Sierra | Northern | PG&E GISWeb | [14 empty] | JC Hutchins Construction | No
Loma Rica | Yuba | Sierra | Northern | PG&E GISWeb | [14 empty] | JCB Fence Company | No
Marysville | Yuba | Sierra | Northern | PG&E GISWeb | [14 empty] | JD Excavating | No
Olivehurst | Yuba | Sierra | Northern | PG&E GISWeb | [14 empty] | JD Fencing | No
Plumas Lake | Yuba | Sierra | Northern | PG&E GISWeb | [14 empty] | JD Landscaping | No
Wheatland | Yuba | Sierra | Northern | PG&E GISWeb | [14 empty] | JD Mathew Construction | No
Davis | Yolo | Sacramento | Northern | PG&E GISWeb | [14 empty] | JD Pasquetti | No
Esparto | Yolo | Sacramento | Northern | PG&E GISWeb | [14 empty] | JD Telecom | No
West Sacramento | Yolo | Sacramento | Northern | PG&E GISWeb | [14 empty] | JDB Construction | No
Winters | Yolo | Sacramento | Northern | PG&E GISWeb | [14 empty] | JDK Construction | No
Woodland | Yolo | Sacramento | Northern | PG&E GISWeb | [14 empty] | JDS Construction | No
Yolo | Yolo | Sacramento | Northern | PG&E GISWeb | [14 empty] | JDS Electric | No
Columbia | Tuolumne | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | JE Construction | No
Sonora | Tuolumne | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jecmariano Landscapes | No
Twain Harte | Tuolumne | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jeff Baker | No
Cutler | Tulare | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Jeff Campbell Construction | No
Dinuba | Tulare | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Jeff Farris | No
Orosi | Tulare | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Jeff Mora Construction | No
Corning | Tehama | North Valley | Northern | PG&E GISWeb | [14 empty] | Jeff Savage Plumbing | No
Cottonwood | Tehama | North Valley | Northern | PG&E GISWeb | [14 empty] | Jeffers Spa & Pools | No
Gerber | Tehama | North Valley | Northern | PG&E GISWeb | [14 empty] | Jeffrey Rodriguez Plumbing | No
Proberta | Tehama | North Valley | Northern | PG&E GISWeb | [14 empty] | Jeff's Plumbing | No
Red Bluff | Tehama | North Valley | Northern | PG&E GISWeb | [14 empty] | Jensen Landscape | No
Tehama | Tehama | North Valley | Northern | PG&E GISWeb | [14 empty] | Jensen Landscape | No
Live Oak | Sutter | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Jenson Pipeline Company Inc | No
Meridian | Sutter | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Jepsen Electric | No
South Yuba City | Sutter | Sierra | Northern | PG&E GISWeb | [14 empty] | Jeremy Cecil | No
Sutter | Sutter | Sierra | Northern | PG&E GISWeb | [14 empty] | Jeremy Willer Construction | No
Yuba City | Sutter | Sierra | Northern | PG&E GISWeb | [14 empty] | Jerrod Pearson Construction | No
Bret Harte | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jerry Abbott | No
Bystrom | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jerry Allison Landscaping | No
Ceres | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jerry Duffy | No
Del Rio | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jerry Epstein | No
Empire | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jerry's Trenching Service | No
Hickman | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jesh-N-Construction Inc | No
Hughson | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jess Pool Construction Inc | No
Keyes | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jesus Landscape & Maintenance | No
Modesto | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jesus Sanchez | No
Newman | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Jetton Costruction | No
Oakdale | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | JF Ohlund Inc | No
Patterson | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | JF Plumbing Inc | No
Riverbank | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | JF Shea Construction | No
Salida | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | JFC Construction | No
Turlock | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | JFC Electric | No
Waterford | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | JG Construction | No
West Modesto | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | JG Universal Landscape | No
Westley | Stanislaus | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | JH Meek and Sons | No
Boyes Hot Springs | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | Jim Bradley Construction | No
Cloverdale | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | Jim Bustos Plumbing Inc | No
Cotati | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | Jim Crawford Construction | No
El Verano | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | Jim Dobbas Inc | No
Fetters Hot Springs | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | Jim Farrell Pool and Spa | No
Forestville | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | Jim Freethy Exvacating | No
Fulton | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | Jim King | No
Glen Ellen | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | Jim Leroux | No
Graton | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | Jim Parker | No
Healdsburg | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | Jim Relu | No
Kenwood | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | Jim Smith | No
Larkfield-Wikiup | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | Jim Woody Plumbing | No
Penngrove | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | Jimmy Smith Plumbing | No
Petaluma | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | Jimmy's Garden Services | No
Rohnert Park | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | JJ Construction | No
Roseland | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | JJ Nguyen Construction | No
Santa Rosa | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | JJ Welding | No
Sebastopol | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | JJR Construction | Yes
Sonoma | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | JK Design | No
Windsor | Sonoma | Sonoma | Northern | PG&E GISWeb | [14 empty] | JKT Associates | No
Benicia | Solano | North Bay | Bay Area | PG&E GISWeb | [14 empty] | JL Construction | No
Dixon | Solano | Sacramento | Northern | PG&E GISWeb | [14 empty] | JL Peace Building | No
Fairfield | Solano | Sacramento | Northern | PG&E GISWeb | [14 empty] | Jlf Construction | No
Rio Vista | Solano | Sacramento | Northern | PG&E GISWeb | [14 empty] | JLL Builders | No
Suisun City | Solano | Sacramento | Northern | PG&E GISWeb | [14 empty] | JM Baker Homes | No
Vacaville | Solano | Sacramento | Northern | PG&E GISWeb | [14 empty] | Jm Basaldua | No
Vallejo | Solano | North Bay | Bay Area | PG&E GISWeb | [14 empty] | JM Communications | No
Anderson | Shasta | North Valley | Northern | PG&E GISWeb | [14 empty] | JM Construction Developers | No
Burney | Shasta | North Valley | Northern | PG&E GISWeb | [14 empty] | JM Tree Service | No
Fall River Mills | Shasta | North Valley | Northern | PG&E GISWeb | [14 empty] | JMB Construction | Yes
Johnson Park | Shasta | North Valley | Northern | PG&E GISWeb | [14 empty] | JMS Development | No
Lakeshore | Shasta | North Valley | Northern | PG&E GISWeb | [14 empty] | JND Plumbing | No
McArthur | Shasta | North Valley | Northern | PG&E GISWeb | [14 empty] | JOB Construction | NO
Redding | Shasta | North Valley | Northern | PG&E GISWeb | [14 empty] | Jody Jasso | No
Shasta Lake | Shasta | North Valley | Northern | PG&E GISWeb | [14 empty] | Joe Cserna | No
Shingletown | Shasta | North Valley | Northern | PG&E GISWeb | [14 empty] | Joe Larosa | No
Aptos | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Joe Morales | No
Ben Lomond | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Joel Bedahalhein | No
Boulder Creek | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Joel Harmon Construction | No
Brookdale | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Joe's Landscaping and Concrete | No
Capitola | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Joey Mota Landscaping | No
Felton | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | John Barbieri | No
Interlaken | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | John Benward Company Inc | No
La Selva Beach | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | John Beward Co | No
Mount Hermon | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | John Brooks | No
Opal Cliffs | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | John Charlot | No
Pasatiempo | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | John Connoly Construction | No
Rio del Mar | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | John Drain Roto Service | No
Santa Cruz | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | John Dupriest | No
Scotts Valley | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | John Gill Construction | No
Seacliff | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | John Ley Tree Service | No
Soquel | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | John Litzo Construction Inc | No
Watsonville | Santa Cruz | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | John McCune Construction | No
Alum Rock | Santa Clara | San Jose | Central Coast | PG&E GISWeb | [14 empty] | John McMahon | No
Cambrian Park | Santa Clara | De Anza | Central Coast | PG&E GISWeb | [14 empty] | John Molina | No
Campbell | Santa Clara | De Anza | Central Coast | PG&E GISWeb | [14 empty] | John Molinari | No
Cupertino | Santa Clara | De Anza | Central Coast | PG&E GISWeb | [14 empty] | John P Construction | No
East Foothills | Santa Clara | San Jose | Central Coast | PG&E GISWeb | [14 empty] | John Pahlow Construction | No
Gilroy | Santa Clara | San Jose | Central Coast | PG&E GISWeb | [14 empty] | John Peet Excavation | No
Los Altos | Santa Clara | De Anza | Central Coast | PG&E GISWeb | [14 empty] | John Pereira | No
Los Altos Hills | Santa Clara | De Anza | Central Coast | PG&E GISWeb | [14 empty] | John Pitkin | No
Los Gatos | Santa Clara | De Anza | Central Coast | PG&E GISWeb | [14 empty] | John Rocha Custom Tractor | No
Loyola | Santa Clara | De Anza | Central Coast | PG&E GISWeb | [14 empty] | John Ross Const | No
Milpitas | Santa Clara | San Jose | Central Coast | PG&E GISWeb | [14 empty] | John Sawtelle | No
Monte Sereno | Santa Clara | De Anza | Central Coast | PG&E GISWeb | [14 empty] | John Souza | No
Morgan Hill | Santa Clara | San Jose | Central Coast | PG&E GISWeb | [14 empty] | John Stepens | No
Mountain View | Santa Clara | De Anza | Central Coast | PG&E GISWeb | [14 empty] | John Wallace | No
Palo Alto | Santa Clara | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Johnson & Co | No
San Jose | Santa Clara | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Johnson Custom | No
San Martin | Santa Clara | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Johnson Electric & Control | No
Santa Clara | Santa Clara | San Jose | Central Coast | PG&E GISWeb | [14 empty] | Johnson Engineering | No
Saratoga | Santa Clara | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Johnson Mechanical Contractors Inc | No
Stanford | Santa Clara | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Johnson Mgmt Services | No
Sunnyvale | Santa Clara | De Anza | Central Coast | PG&E GISWeb | [14 empty] | Jones & Sons | Yes
Buellton | Santa Barbara | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Jonny Steves | No
Guadalupe | Santa Barbara | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Jose Hernandez | No
Lompoc | Santa Barbara | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Jose Madriz | No
Orcutt | Santa Barbara | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Jose Nuno | No
Santa Maria | Santa Barbara | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Jose Perez | No
Santa Ynez | Santa Barbara | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Jose Rios | No
Solvang | Santa Barbara | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Jose Rizo | No
Vandenberg Village | Santa Barbara | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Jose Telez | No
Atherton | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Jose Zuniza | No
Belmont | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Joseph Aranda | No
Brisbane | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Joseph Crown Construction | No
Burlingame | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Joseph Escolando | No
Colma | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Joseph J Albanese Inc | No
Daly City | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Josh Ochoa | No
East Palo Alto | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JP Landscape | No
El Granada | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JP Woodworks | No
Emerald Lake Hills | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JPM Construction | No
Foster City | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JQC Construction | No
Half Moon Bay | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JR Concrete | No
Hillsborough | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JR Fencing | No
Menlo Park | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JR Monterrosa Concrete Sawing | No
Millbrae | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JR Pierce Plumbing | No
Montara | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JRV Construction | No
Moss Beach | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JS Electric | No
North Fair Oaks | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JS General Construction | No
Pacifica | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JT Construction | No
Portola Valley | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JT Plumbing | No
Redwood City | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JTS | No
San Bruno | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | JTW Grading and Excavating | No
San Carlos | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Juan Alarado Teran | No
San Mateo | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Juan Perez | No
South San Francisco | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Juan Rosales | No
West Menlo Park | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Juan Sanchez | No
Woodside | San Mateo | Peninsula | Central Coast | PG&E GISWeb | [14 empty] | Juan Vasquez Landscape | No
Arroyo Grande | San Luis Obispo | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Just Drains | No
Atascadero | San Luis Obispo | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | JVC Construction | No
Cambria | San Luis Obispo | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | JW Backhoe | No
Grover Beach | San Luis Obispo | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | JZ Construction | No
Los Osos | San Luis Obispo | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | K Dunaway Construction | No
Morro Bay | San Luis Obispo | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | K Hovnanian Homes | No
Nipomo | San Luis Obispo | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | K&D Landscaping | No
Oceano | San Luis Obispo | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | K&J Company | No
Paso Robles | San Luis Obispo | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | K&R Pools and Spas | No
Pismo Beach | San Luis Obispo | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | K5 | No
San Luis Obispo | San Luis Obispo | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Kaisen Garden | No
San Miguel | San Luis Obispo | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Kanley Inc | No
Santa Margarita | San Luis Obispo | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Kavanagh Construction | No
Templeton | San Luis Obispo | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Kaylar Construction | No
Acampo | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | KB Homes | No
August | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | KCB Homes | No
Collierville | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | KDC Construction | No
Country Club | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | KDW Construction | No
Escalon | San Joaquin | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Keeth Building Contractors | No
French Camp | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Keith Gale General Engineering | No
Garden Acres | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Keith Haisley Construction | No
Kennedy | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Keith Nordstrom | No
Lathrop | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Keith Rodysell Garden Fare Co | No
Linden | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Keith Willig Landscape Services | No
Lockeford | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Keller Engineering & Asphalt | No
Lodi | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Kelly & Kelly | No
Manteca | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Kelly Construction | No
Mountain House | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Kelly's Stump Removal | No
Ripon | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Kelton Excavating and Trucking | No
Stockton | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Ken Maas Construction | No
Thornton | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Ken May Plumbing | No
Tracy | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Kendu Construction | No
Vernalis | San Joaquin | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Kenwood Fence Co | No
San Francisco | San Francisco | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Kern Asphalt | No
Hollister | San Benito | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Kern High School District Maintenance and Operations | No
Paicines | San Benito | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Kern Pacific Construction | No
San Juan Bautista | San Benito | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Kerr & Son Construction | No
Antelope | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kerri Landscape | No
Arden-Arcade | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kershaw Construction | No
Carmichael | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kevin Cobb | No
Citrus Heights | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kevin Kelly | No
Elk Grove | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kevin Kwok | No
Elverta | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kevin Lehane Construction | No
Fair Oaks | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kevin Ly | No
Florin | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kevin Moylan General Contractors | No
Folsom | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kevin Vosskvil | No
Foothill Farms | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kevin Yip | No
Franklin | Sacramento | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Kgbell Construction | No
Fruitridge Pocket | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Khasla Construction | No
Galt | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kilik General | No
Gold River | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kims Plumbing | No
Isleton | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | King Rooter | No
La Riviera | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | King Trenchless | No
Laguna | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kirkes Electric | No
Laguna West-Lakeside | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kitteringham Craig Ltd Intermanbeco | No
Lemon Hill | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | KJ Woods Construction | Yes
Locke | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | KJM Enterprises | No
North Gate | Sacramento | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Kleven Construction | No
North Highlands | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Knife River Construction | Yes
Orangevale | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Knight's Plumbing | No
Parkway | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Knox Sewer | No
Rancho Cordova | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | KO Construction | No
Rancho Murieta | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Koch & Koch Inc | No
Rio Linda | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Koch and Associates | No
Rosemont | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kodiak Construction | No
Sacramento | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Kolob Construction | No
Vineyard | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | Korbmacher Engineering | No
Wilton | Sacramento | Sacramento | Northern | PG&E GISWeb | [14 empty] | KP Martin Inc | No
Chester | Plumas | North Valley | Northern | PG&E GISWeb | [14 empty] | KR Carson Construction | No
Auburn | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | KSYC Construction | No
Colfax | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | KTD Construction | No
Dutch Flat | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | Kuykendall Solar | No
Foresthill | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | KV Structures Inc | No
Granite Bay | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | KWS United Technology Inc | No
Lincoln | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | L&D Construction | No
Loomis | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | L&Q Construction | No
Meadow Vista | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | L&S Landscaping | No
Newcastle | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | La Perle Concrete | No
North Auburn | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | La Selva Tree Care | No
Penryn | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | Lakevele Electric | No
Rocklin | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | Lamarsh Concrete Construction | No
Roseville | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | Lambert Construction | No
Sheridan | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | Lamon Construction Co | No
Soda Springs | Placer | Sierra | Northern | PG&E GISWeb | [14 empty] | Lamont Public Utility | No
Alta Sierra | Nevada | Sierra | Northern | PG&E GISWeb | [14 empty] | Land and Habitat Restoration | No
Grass Valley | Nevada | Sierra | Northern | PG&E GISWeb | [14 empty] | Landmark Construction | No
Nevada City | Nevada | Sierra | Northern | PG&E GISWeb | [14 empty] | Landmark Irrigation | No
Penn Valley | Nevada | Sierra | Northern | PG&E GISWeb | [14 empty] | Landmark Landscape | No
American Canyon | Napa | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Landscape Center | No
Angwin | Napa | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Landscape Connection | No
Calistoga | Napa | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Landscape Design | No
Deer Park | Napa | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Landscape Development Inc | No
Napa | Napa | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Landscape Group | No
St Helena | Napa | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Lane Electric Inc | No
Yountville | Napa | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Lara's Concrete Inc | No
Bradley | Monterey | Los Padres | Central Coast | PG&E GISWeb | [14 empty] | Larrieta Sanitation Construction | No
Carmel | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Larry Daniels | No
Carmel Valley | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Larry Lewis | No
Castroville | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Larry Nelson Construction | No
Del Monte Forest | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Larry's Tree Care | No
Del Rey Oaks | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Larson Trenching | No
Gonzales | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Las Casitas Apartments | No
Greenfield | Monterey | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Las Palmas Landscaping | No
King City | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Lasal | No
Marina | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Lasar Underground Construction | No
Monterey | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Laser Precision Land Leveling | No
Moss Landing | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Lassiter Excavating Inc | No
Pacific Grove | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Laster Landscape | No
Pebble Beach | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Lathrop Construction | No
Prunedale | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Laurie Andrewson | No
Salinas | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Laurn Wise Landscaping | No
San Ardo | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Laverty Construction | No
Sand City | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Lavu Concrete | No
Seaside | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Lawler & Stanz Inc | No
Soledad | Monterey | Central Coast | Central Coast | PG&E GISWeb | [14 empty] | Lawler Excavation Pipeline | No
Atwater | Merced | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Lawrence Construction | No
Bear Creek | Merced | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Layman Electric Inc | No
Delhi | Merced | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Lazzarini Construction Incorporated | No
Denair | Merced | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | LC General | No
Diablo | Merced | Diablo | Bay Area | PG&E GISWeb | [14 empty] | LD Giacomini Enterprises | No
Dos Palos | Merced | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | LDM Construction | No
Gustine | Merced | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Le Brett Construction | No
Hilmar | Merced | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Leam Backhoe and Underground | No
Livingston | Merced | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Lea's Demolition | No
Los Banos | Merced | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Lebrun Excavation and Concrete | No
McSwain | Merced | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Lee Construction | No
Merced | Merced | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Lee Wilson Electric | No
Planada | Merced | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Legacy Construction | No
Winton | Merced | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Legacy Renovations | No
Boonville | Mendocino | Humboldt | Northern | PG&E GISWeb | [14 empty] | Lehman Design | No
Calpella | Mendocino | Humboldt | Northern | PG&E GISWeb | [14 empty] | Lemma Construction | No
Covelo | Mendocino | Humboldt | Northern | PG&E GISWeb | [14 empty] | Lemmings Construction | No
Fort Bragg | Mendocino | Humboldt | Northern | PG&E GISWeb | [14 empty] | Lennar Homes | No
Hopland | Mendocino | Humboldt | Northern | PG&E GISWeb | [14 empty] | Leo Tidwell Excavating | No
Laytonville | Mendocino | Humboldt | Northern | PG&E GISWeb | [14 empty] | Leo Tidwell Excavation | No
Philo | Mendocino | Humboldt | Northern | PG&E GISWeb | [14 empty] | Leonard Salazar Concrete Group | No
Point Arena | Mendocino | Humboldt | Northern | PG&E GISWeb | [14 empty] | Les Kelley Inc | No
Potter Valley | Mendocino | Humboldt | Northern | PG&E GISWeb | [14 empty] | Level 10 Construction | No
Redwood Valley | Mendocino | Humboldt | Northern | PG&E GISWeb | [14 empty] | Level 3 Construction | No
Ukiah | Mendocino | Humboldt | Northern | PG&E GISWeb | [14 empty] | Lewis & Tibbits | Yes
Willits | Mendocino | Humboldt | Northern | PG&E GISWeb | [14 empty] | Lewis M Merlo | No
Hornitos | Mariposa | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | LGM Construction | No
Mariposa | Mariposa | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Lifescaping Outdoors | No
Belvedere | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Linda Smith Williams | No
Corte Madera | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Lindex | No
Dillon Beach | Marin | Sonoma | Northern | PG&E GISWeb | [14 empty] | Lindstrom Company | No
Fairfax | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Lino Mendoza | No
Forest Knolls | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Linscott Engineering | No
Greenbrae | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Lisac Construction | No
Kentfield | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Lister Construction | No
Larkspur | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Little Caesar's Pizza | No
Lucas Valley-Marinwood | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | LM Construction | No
Mill Valley | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Lombardo Diamond Core Drilling Co | No
Novato | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Lonestar Pacific Engineering | No
Ross | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Long Electric | No
San Anselmo | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Lopez Concrete | No
San Quentin | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Lopez Iron Works | No
San Rafael | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Lopez Remodeling | No
Sausalito | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Loral Landscaping | No
Tamalpais-Homestead Valley | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Los Gatos Fence | No
Tiburon | Marin | North Bay | Bay Area | PG&E GISWeb | [14 empty] | Los Gatos Paver Solutions | No
Bonadelle Ranchos-Madera Ranchos | Madera | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Los Osos Center LLC | No
Chowchilla | Madera | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Louis and Lewis | No
Fairmead | Madera | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Louis Landscaping | No
Madera | Madera | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | LP Construction | No
Madera Acres | Madera | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | LT Directional Boring | No
North Fork | Madera | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Luca Excavation | No
Oakhurst | Madera | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Lucas Building | No
Raymond | Madera | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Luciano Concrete | No
Wishon | Madera | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Luis A Scattini & Sons | No
Clearlake | Lake | Humboldt | Northern | PG&E GISWeb | [14 empty] | Luis Deleon | No
Hidden Valley Lake | Lake | Humboldt | Northern | PG&E GISWeb | [14 empty] | Luis Marin | No
Kelseyville | Lake | Humboldt | Northern | PG&E GISWeb | [14 empty] | Luis Perez Landscaping | No
Lakeport | Lake | Humboldt | Northern | PG&E GISWeb | [14 empty] | Lund Construction | No
Middletown | Lake | Humboldt | Northern | PG&E GISWeb | [14 empty] | Lunny Engineering Inc | No
Upper Lake | Lake | Humboldt | Northern | PG&E GISWeb | [14 empty] | Lupton Excavation Inc | No
Avenal | Kings | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Lupton General Engineering Contractor | No
Corcoran | Kings | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Lusardi Construction | No
Hanford | Kings | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Lutz Construction Service | No
Kettleman City | Kings | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Lwb Construction | No
Lemoore | Kings | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Lyons General Engineering | No
Lemoore Station | Kings | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Lyukon Landscaping | No
Arvin | Kern | Kern | Central Valley | PG&E GISWeb | [14 empty] | M Bay Area General Contractors | No
Bakersfield | Kern | Kern | Central Valley | PG&E GISWeb | [14 empty] | M Kelley Construction | No
Bear Valley | Kern | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | M Sanchez General Contractor | No
Greenacres | Kern | Kern | Central Valley | PG&E GISWeb | [14 empty] | M Santos & Sons Inc | No
Lamont | Kern | Kern | Central Valley | PG&E GISWeb | [14 empty] | M Squared | Yes
Maricopa | Kern | Kern | Central Valley | PG&E GISWeb | [14 empty] | M&G General Landscaping Inc | No
McFarland | Kern | Kern | Central Valley | PG&E GISWeb | [14 empty] | M&G Hauling | No
McKittrick | Kern | Kern | Central Valley | PG&E GISWeb | [14 empty] | M&L Plumbing | No
North Edwards | Kern | Kern | Central Valley | Master Dig-In File | [14 empty] | M&M Construction & Home Design | No
Oildale | Kern | Kern | Central Valley | PG&E GISWeb | [14 empty] | M&M Electric | No
Ridgecrest | Kern | Kern | Central Valley | Master Dig-In File | [14 empty] | M&M Fence Co | No
Rosedale | Kern | Kern | Central Valley | PG&E GISWeb | [14 empty] | M&M Landscape and Management | No
Shafter | Kern | Kern | Central Valley | PG&E GISWeb | [14 empty] | M2 Construction | No
South Taft | Kern | Kern | Central Valley | PG&E GISWeb | [14 empty] | M2 Landscape | No
Taft | Kern | Kern | Central Valley | PG&E GISWeb | [14 empty] | M3 Integrated Services | No
Tehachapi | Kern | Kern | Central Valley | Other | [14 empty] | Ma Long Construction | No
Wasco | Kern | Kern | Central Valley | PG&E GISWeb | [14 empty] | Mac Enterprises | No
Arcata | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Macedonio Gonzales | No
Bayside | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Machado Backhoe Inc | No
Blue Lake | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | MacIver Landscape | No
Cutten | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Mack Builders | No
Eureka | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Macken Construction | No
Ferndale | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Madco Electric | No
Fortuna | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Maddoz Concrete | No
Humboldt Hill | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Madison Park Financial | No
Kneeland | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Magana Landscape Contractor | No
Loleta | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Maggiora & Ghilotti Inc | Yes
McKinleyville | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Magic Gardens Landscaping | No
Myers Flat | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Magnone Pump Co | No
Redway | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Magnum Construction Group | No
Rio Dell | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Magnum Drywall | No
Samoa | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Mainguth Property Improvements Inc | No
Trinidad | Humboldt | Humboldt | Northern | PG&E GISWeb | [14 empty] | Mainline Plumbing Inc | No
Cory | Glenn | North Valley | Northern | PG&E GISWeb | [14 empty] | Mains Construction | No
Hamilton City | Glenn | North Valley | Northern | PG&E GISWeb | [14 empty] | MAL Excavating | No
Orland | Glenn | North Valley | Northern | PG&E GISWeb | [14 empty] | Malachi Paving & Grading | No
Willows | Glenn | North Valley | Northern | PG&E GISWeb | [14 empty] | Mallard Plumbing Co | No
Biola | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Maloney Construction | No
Clovis | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Maniglia Landscape | No
Coalinga | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Manuel Inglesias Concrete | No
Firebaugh | Fresno | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Manuel Raposo Construction Inc | No
Fowler | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Marathon Landscape Services | No
Fresno | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Marin Custom Builders | No
Huron | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Marin Municipal Water District | No
Kerman | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Marin Termite Control | No
Kingsburg | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Marina Coast Water District | No
Malaga | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Marina Company | No
Mendota | Fresno | Yosemite | Central Valley | PG&E GISWeb | [14 empty] | Marina Landscape | Yes
Old Fig Garden | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Mario Naranjo | No
Orange Cove | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Mark Awad | No
Parlier | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Mark Green Backhoe Service | No
Prather | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Mark III Construction | No
Reedley | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Mark Labour Plumbing | No
Riverdale | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Mark Luallen Landscape | No
San Joaquin | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Mark Maintenance Man | No
Sanger | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Mark Paris | No
Selma | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Mark Scott Construction | No
Sunnyside | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Markay Johnson Construction | No
Tarpey Village | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Market One Builders | No
Tranquillity | Fresno | Fresno | Central Valley | PG&E GISWeb | [14 empty] | Marko Andrade | No
Cameron Park | El Dorado | Sierra | Northern | PG&E GISWeb | [14 empty] | Marques Pipeline Inc | Yes
Camino | El Dorado | Sierra | Northern | PG&E GISWeb | [14 empty] | Marsetti Design | No
Coloma | El Dorado | Sierra | Northern | PG&E GISWeb | [14 empty] | Marsh Fence & Deck | No
Diamond Springs | El Dorado | Sierra | Northern | PG&E GISWeb | [14 empty] | Marshall Brothers | No
El Dorado Hills | El Dorado | Sierra | Northern | PG&E GISWeb | [14 empty] | Marticus Electric Inc | No
Green Valley | El Dorado | Sacramento | Northern | PG&E GISWeb | [14 empty] | Martin Bautista Nunez | No
Placerville | El Dorado | Sierra | Northern | PG&E GISWeb | [14 empty] | Martin Construction | No
Pollock Pines | El Dorado | Sierra | Northern | PG&E GISWeb | [14 empty] | Martin General Engineering | Yes
Alamo | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Martin Gutierrez | No
Antioch | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Martin Lamart Impact Demo and Hauling | No
Bay Point | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Martin Rodgrigues | No
Blackhawk | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Martinez and Sons | No
Brentwood | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Martinez Construction | No
Byron | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Martinez Septic Tank Service | No
Castle Hill | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Martin's Concrete | No
Clayton | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Martin's General Engineering | Yes
Concord | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Marti's Plumbing Service | No
Crockett | Contra Costa | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Mary Everett | No
Danville | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Masellis Drilling | No
Discovery Bay | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Masterpiece Gardens Inc | No
El Cerrito | Contra Costa | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Mastro Plumbing | No
El Sobrante | Contra Costa | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Matt Bonette | No
Hercules | Contra Costa | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Matt Etchell Construction | No
Kensington | Contra Costa | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Matt Horn Landscaping & Tree Care | No
Lafayette | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Matt Jaeger Construction | No
Martinez | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Matt Julian | No
Mission | Contra Costa | San Francisco | Bay Area | PG&E GISWeb | [14 empty] | Matt Mccanre | No
Moraga | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Matt Mouro | No
North Richmond | Contra Costa | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Matt Sysco | No
Oakley | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Matt Ziff | No
Orinda | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Matthew C Pekel | No
Pacheco | Contra Costa | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | Mattos Construction | No
Pinole | Contra Costa | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Maurin Construction | No
Pittsburg | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Max Construction | No
Pleasant Hill | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Maximum Service Landscaping Inc | No
Reliez Valley | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Maxwell Smart Construction | No
Richmond | Contra Costa | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Mayberry's Pipe Construction | No
Rodeo | Contra Costa | East Bay | Bay Area | PG&E GISWeb | [14 empty] | MBA Pipes | No
San Pablo | Contra Costa | East Bay | Bay Area | PG&E GISWeb | [14 empty] | MBM Electric | No
San Ramon | Contra Costa | Mission | Central Coast | PG&E GISWeb | [14 empty] | MC Frederick Construction | No
Saranap | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | MC Plumbing | No
Shell Ridge | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | Mcastillo's Concrete | No
Tara Hills | Contra Costa | East Bay | Bay Area | PG&E GISWeb | [14 empty] | McCaffrey Custom Construction Inc | No
Vine Hill | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | McCauley Construction | No
Walnut Creek | Contra Costa | Diablo | Bay Area | PG&E GISWeb | [14 empty] | McClarenon Grading and Excavating | No
Arbuckle | Colusa | See Same Name Cities Lookup | See Same Name Cities Lookup | PG&E GISWeb | [14 empty] | McClure Enterprises | No
Colusa | Colusa | Sacramento | Northern | PG&E GISWeb | [14 empty] | McCormick Construction Group | No
Princeton | Colusa | Sacramento | Northern | PG&E GISWeb | [14 empty] | McCoy Homes | No
Williams | Colusa | Sacramento | Northern | PG&E GISWeb | [14 empty] | McCutcheon Construction Inc | No
Angels Camp | Calaveras | Stockton | Central Valley | PG&E GISWeb | [14 empty] | McDonald Construction | No
Copperopolis | Calaveras | Stockton | Central Valley | PG&E GISWeb | [14 empty] | McDonald Plumbing | No
Mokelumne Hill | Calaveras | Stockton | Central Valley | PG&E GISWeb | [14 empty] | McDunn Construction | No
Murphys | Calaveras | Stockton | Central Valley | PG&E GISWeb | [14 empty] | MCE Corporation | No
Rail Road Flat | Calaveras | Stockton | Central Valley | PG&E GISWeb | [14 empty] | McFadden Construction | No
Rancho Calaveras | Calaveras | Stockton | Central Valley | PG&E GISWeb | [14 empty] | McGuire & Hester | No
San Andreas | Calaveras | Stockton | Central Valley | PG&E GISWeb | [14 empty] | MCH Electric | No
Valley Springs | Calaveras | Stockton | Central Valley | PG&E GISWeb | [14 empty] | MCI Engineering Inc | No
Biggs | Butte | North Valley | Northern | PG&E GISWeb | [14 empty] | McKenzie Enterprises | No
Chico | Butte | North Valley | Northern | PG&E GISWeb | [14 empty] | McKuin Pipeline | No
Durham | Butte | North Valley | Northern | PG&E GISWeb | [14 empty] | MCM Construction | No
Gridley | Butte | North Valley | Northern | PG&E GISWeb | [14 empty] | McMahon Plumbing | No
Magalia | Butte | North Valley | Northern | PG&E GISWeb | [14 empty] | MCO Builders | No
Oroville | Butte | North Valley | Northern | PG&E GISWeb | [14 empty] | McPherson Property Services | No
Oroville East | Butte | North Valley | Northern | PG&E GISWeb | [14 empty] | MCRC LLC | No
Palermo | Butte | North Valley | Northern | PG&E GISWeb | [14 empty] | MCS Construction | No
Paradise | Butte | North Valley | Northern | PG&E GISWeb | [14 empty] | MD Concrete Cutting | No
South Oroville | Butte | North Valley | Northern | PG&E GISWeb | [14 empty] | MD Construction | No
Thermalito | Butte | North Valley | Northern | PG&E GISWeb | [14 empty] | MD Demolition | No
Amador City | Amador | Stockton | Central Valley | PG&E GISWeb | [14 empty] | MD Site Grading | No
Ione | Amador | Stockton | Central Valley | PG&E GISWeb | [14 empty] | MDC Concrete | No
Jackson | Amador | Stockton | Central Valley | PG&E GISWeb | [14 empty] | MDF Pipe | No
Plymouth | Amador | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Medina Landscaping | No
Sutter Creek | Amador | Stockton | Central Valley | PG&E GISWeb | [14 empty] | Medina Plumbing | No
Alameda | Alameda | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Medina's Electrical Contractor | No
Ashland | Alameda | Mission | Central Coast | PG&E GISWeb | [14 empty] | Medrano Electric | No
Berkeley | Alameda | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Mehus Construction | No
Boron | Kern | Kern | Central Valley | Master Dig-In File | [14 empty] | Meixner Construction | No
Castro Valley | Alameda | Mission | Central Coast | PG&E GISWeb | [14 empty] | Mel Plumbing | No
Cherryland | Alameda | Mission | Central Coast | PG&E GISWeb | [14 empty] | Mel's Electric Co | No
Dublin | Alameda | Mission | Central Coast | PG&E GISWeb | [14 empty] | Melvin Mendes Land Leveling | No
Emeryville | Alameda | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Menda Electric | No
Fairview | Alameda | Mission | Central Coast | PG&E GISWeb | [14 empty] | Mendenhall Electric | No
Fremont | Alameda | Mission | Central Coast | PG&E GISWeb | [14 empty] | Mendocino Construction | No
Hayward | Alameda | Mission | Central Coast | PG&E GISWeb | [14 empty] | Mendonca Services | No
Livermore | Alameda | Mission | Central Coast | PG&E GISWeb | [14 empty] | Mendoza Electric | No
Newark | Alameda | Mission | Central Coast | PG&E GISWeb | [14 empty] | Menlo Builders | No
Oakland | Alameda | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Merced Fire Dept | No
Piedmont | Alameda | East Bay | Bay Area | PG&E GISWeb | [14 empty] | Mercer Fraser Company | No
Pleasanton | Alameda | Mission | Central Coast | PG&E GISWeb | [14 empty] | Mercer Fraser Company | No
San Leandro | Alameda | Mission | Central Coast | PG&E GISWeb | [14 empty] | Meridian Park Electric | No
San Lorenzo | Alameda | Mission | Central Coast | PG&E GISWeb | [14 empty] | Mesa Construction | No
Sunol | Alameda | Mission | Central Coast | PG&E GISWeb | [14 empty] | Messina's Landscaping | No
Union City | Alameda | Mission | Central Coast | PG&E GISWeb | [14 empty] | Method Paving Inc | No
Albany | Alameda | East Bay | Bay Area | Master Dig-In File | [14 empty] | Metro Publishing Inc | No
[19 empty] | Metrocon Builders | No
[19 empty] | Meza's Fence | No
[19 empty] | MG Backhoe Inc | No
[19 empty] | MGD Investments | No
[19 empty] | MGE Underground | No
[19 empty] | MGM Plumbing | No
[19 empty] | MHK Construction | No
[19 empty] | Michael & Sons Construction | No
[19 empty] | Michael Hallroan | No
[19 empty] | Michael Heavey Construction | No
[19 empty] | Michael J Rodola Construction | No
[19 empty] | Michael Moser Development | No
[19 empty] | Michael O'Shaughnessy Construction | No
[19 empty] | Michael Paul Company | No
[19 empty] | Michael R Tolladay Corporation | No
[19 empty] | Michael T Evans Construction | No
[19 empty] | Michael Wheeler Construction | No
[19 empty] | Michael's Construction | No
[19 empty] | Michel Landscape Corporation | No
[19 empty] | Michels Pipeline Construction | No
[19 empty] | Mickele Construction | No
[19 empty] | Mid Cal Pipeline | No
[19 empty] | Mid-Cal Constructors Inc | No
[19 empty] | Middleton Gardens | No
[19 empty] | Middleton Handyman Services | No
[19 empty] | Mid-Peninsula Water District | No
[19 empty] | Mid-State Contractors | No
[19 empty] | Mid-State Electric | No
[19 empty] | Midyett Construction | No
[19 empty] | Migel Moreno | No
[19 empty] | Miguel Backhoe | No
[19 empty] | Miguel Barroso | No
[19 empty] | Miguel Jimenez | No
[19 empty] | Miguel Nova | No
[19 empty] | Miguels Plumbing | No
[19 empty] | Miholovich Concrete | No
[19 empty] | Mike Benitez Plumbing | No
[19 empty] | Mike Bowen | No
[19 empty] | Mike Brown Electric | Yes
[19 empty] | Mike Connolly | No
[19 empty] | Mike Counsil Plubing | No
[19 empty] | Mike Guinn | No
[19 empty] | Mike Hallett | No
[19 empty] | Mike Hampton | No
[19 empty] | Mike Hurley Construction | No
[19 empty] | Mike Johnson | No
[19 empty] | Mike Kittle Construction | No
[19 empty] | Mike McCall Landscape | No
[19 empty] | Mike Nitzen Construction | No
[19 empty] | Mike Turner & Associates | No
[19 empty] | Mike Warner | No
[19 empty] | Miksis Services Inc | No
[19 empty] | Millbrae Furniture Inc | No
[19 empty] | Millcreek Construction | No
[19 empty] | Millcreek Electrical | No
[19 empty] | Millcreek Landscaping | No
[19 empty] | Miller and Elwood Concrete | No
[19 empty] | Miller Creek Construction | No
[19 empty] | Miller Farms | No
[19 empty] | Miller Pacific Inc | No
[19 empty] | Miller Pipeline | No
[19 empty] | Mills Builders | No
[19 empty] | Milton Rodas | No
[19 empty] | Mimbs Tractor Service | No
[19 empty] | Mimi's Landscaping | No
[19 empty] | Mission Constructors | No
[19 empty] | Missoumi Impact Construction Inc | No
[19 empty] | Misty Mountain Landscaped | No
[19 empty] | Mitchell Concrete | No
[19 empty] | Mitchell Engineering | No
[19 empty] | Mitchell Landscape | No
[19 empty] | MJ Concrete | No
[19 empty] | MJ Shelton | No
[19 empty] | MJM Construction | No
[19 empty] | MK Pipelines | No
[19 empty] | MK Renovations | No
[19 empty] | MKB Construction | No
[19 empty] | MKI Construction | No
[19 empty] | ML Anderson | No
[19 empty] | ML Nielsen | No
[19 empty] | M-M Art Consulting | No
[19 empty] | MM Construction | No
[19 empty] | MN Construction | No
[19 empty] | Modern Art Construction | No
[19 empty] | Modesto Irrigation District | No
[19 empty] | Modesto Sand & Gravel Inc | No
[19 empty] | Modica Lanscaping | No
[19 empty] | Mogensen Landscaping | No
[19 empty] | Mohrs Excavating | No
[19 empty] | Momentum Builders | No
[19 empty] | Monley Cronin Inc | No
[19 empty] | Montclair Construction | No
[19 empty] | Monte Construction | No
[19 empty] | Monterey Bay Builders | No
[19 empty] | Monterey Construction Company | No
[19 empty] | Monterey County Fence | No
[19 empty] | Monterey Peninsula Engineering | No
[19 empty] | Moomau Plumbing | No
[19 empty] | Moore Excavating | No
[19 empty] | Moorefield Construction Inc | No
[19 empty] | Moorman Water System | No
[19 empty] | Morales Construction | No
[19 empty] | More Land Construction | No
[19 empty] | Moreno Construction | No
[19 empty] | Moreno Trenching | No
[19 empty] | Morgan and Morgan Leveling | No
[19 empty] | Morgan Construction | No
[19 empty] | Moroso Construction | No
[19 empty] | Moser Electric | No
[19 empty] | Moshe Yacob | No
[19 empty] | Mosingo Construction | No
[19 empty] | Moss Construction | No
[19 empty] | Mosto Construction | No
[19 empty] | Mote Landscape | No
[19 empty] | Motherworks | No
[19 empty] | Motive Energy | No
[19 empty] | Mountain Cascade | Yes
[19 empty] | Mountain Enterprises | No
[19 empty] | Mouton's Inside N Out | No
[19 empty] | Mozingo Construction | No
[19 empty] | MP Nexlevel | No
[19 empty] | Mr 99 Rooter & Plumbing | No
[19 empty] | Mr Drain | No
[19 empty] | Mr Floors | No
[19 empty] | Mr Rooter Plumbing | No
[19 empty] | MRJ Homes Inc | No
[19 empty] | MS Construction | No
[19 empty] | MSL Electric | No
[19 empty] | Mt Szeto Construction | No
[19 empty] | Multi Power | No
[19 empty] | Murga Strange | No
[19 empty] | Muse Concrete | No
[19 empty] | MV Masonry | No
[19 empty] | MW Construction | No
[19 empty] | N and T Inc | No
[19 empty] | N&H Construction | No
[19 empty] | Nagel Landscaping | No
[19 empty] | Nancy Corrione | No
[19 empty] | Napa County | No
[19 empty] | Napa Sanitation District | No
[19 empty] | Nathan Johns | No
[19 empty] | Nathan's Backhoe Service | No
[19 empty] | National Concrete Cutting | No
[19 empty] | National Construction Rentals | No
[19 empty] | Native Landscapes | No
[19 empty] | Natomas Unified School District | No
[19 empty] | Natural Design | No
[19 empty] | Natural Masonry | No
[19 empty] | Nature Landscape Services | No
[19 empty] | Nature Works | No
[19 empty] | Natures Intention Landscaping | No
[19 empty] | Navajo Pipeline | Yes
[19 empty] | Navo and Sons | No
[19 empty] | NCM Concrete | No
[19 empty] | NCM Demolition | No
[19 empty] | NCR Property LLC | No
[19 empty] | Neal Ferguson Construction | No
[19 empty] | Neary Landscape | Yes
[19 empty] | Ned Clyde Construction Inc | No
[19 empty] | Nelson and Sons | No
[19 empty] | Nelson Construction | No
[19 empty] | Nelson Dye Remodeling Specialist | No
[19 empty] | Nevada County Public Works | No
[19 empty] | Nevada Irrigation District | No
[19 empty] | Nevada Jag Construction | No
[19 empty] | Nevis Construction | No
[19 empty] | New Community Baptist Church | No
[19 empty] | New Dimension | No
[19 empty] | New Era 2000 | No
[19 empty] | New Faze Development | No
[19 empty] | New Pipes Inc | No
[19 empty] | New Sky Tree Service | No
[19 empty] | Newell Construction | No
[19 empty] | Newland Entities | No
[19 empty] | Newton Construction | No
[19 empty] | Newton Contracting | No
[19 empty] | Nexgen Builders Inc | No
[19 empty] | Next Gen Excavating | No
[19 empty] | Nichelini Construction | No
[19 empty] | Nick Goyd | No
[19 empty] | Nick's Trucking | No
[19 empty] | NJD Construction | No
[19 empty] | No Problem Pools | No
[19 empty] | Noah Concrete | No
[19 empty] | Noble Fencing | No
[19 empty] | Noel Moreno Masonry | No
[19 empty] | Noland Construction | No
[19 empty] | Nonpareil Construction | No
[19 empty] | Nor Cal Pipeline Services | Yes
[19 empty] | Nor State Plumbing | No
[19 empty] | NorCal Concrete | No
[19 empty] | NorCal Construction | No
[19 empty] | NorCal Development | No
[19 empty] | Norcal Fast Concrete | No
[19 empty] | Norcal Fire Repair | No
[19 empty] | Norcal Pipeline | Yes
[19 empty] | Norco Construction | No
[19 empty] | Norman Charles Construction | No
[19 empty] | Norman Cunningham Construction | No
[19 empty] | North Bay Plumbing Co | No
[19 empty] | North Berkeley Design | No
[19 empty] | North Marin Water District | No
[19 empty] | North Pacific Plumbing Inc | No
[19 empty] | North Star Construction | No
[19 empty] | North State Electric & Pump | No
[19 empty] | Northern California Universal | No
[19 empty] | Northern Electric | No
[19 empty] | Northern Pacific Corporation | No
[19 empty] | Northern Underground | No
[19 empty] | Northinton Innovations Inc | No
[19 empty] | Northstate Earth & Water Inc | No
[19 empty] | Northwest General Engineering | No
[19 empty] | Nouvant Homes | No
[19 empty] | Nova Group Inc | No
[19 empty] | Novato Lumber | No
[19 empty] | NPL Construction Co | No
[19 empty] | NS Delgado | No
[19 empty] | NTK Construction | No
[19 empty] | Nulead Construction | No
[19 empty] | Nunez Irrigation | No
[19 empty] | Nunley Engineering | No
[19 empty] | Nutter Electric | No
[19 empty] | Nu-Vision Construction | No
[19 empty] | Nu-Vision Construction | No
[19 empty] | O Nelson & Son | No
[19 empty] | Oak Grove Construction | Yes
[19 empty] | Oakhurst Skilled Nursery | No
[19 empty] | Oakland Hills Tennis Club | No
[19 empty] | Oasis Pool and Spa Construction | No
[19 empty] | Obayashi Corporation | No
[19 empty] | OC Communications | No
[19 empty] | OC Jones | Yes
[19 empty] | O'Connell Landscape | No
[19 empty] | Odyssey Landscaping Company Inc | No
[19 empty] | O'Grady Paving | Yes
[19 empty] | O'Grady Plumbing | No
[19 empty] | Old World Custom Homes | No
[19 empty] | Olenik Fence | No
[19 empty] | Olenka Builders Inc | No
[19 empty] | Olive Construction | No
[19 empty] | Oliver Builders Inc | No
[19 empty] | Olivewood Inc | No
[19 empty] | Olsen Construction | No
[19 empty] | On Site Engineering | No
[19 empty] | One Day Complete Repipe | No
[19 empty] | One Stop Fencing | No
[19 empty] | One Two Trees Company | No
[19 empty] | O'Neill Construction | No
[19 empty] | Ongaro & Sons Plumbing | No
[19 empty] | Onset Services | No
[19 empty] | On-Site Engineering and Asphalt | No
[19 empty] | Optimum Inc | No
[19 empty] | Oral E Mitchum Inc | No
[19 empty] | Orangevale Water Company | No
[19 empty] | Ortegon Construction | No
[19 empty] | Ortiz Landscaping | No
[19 empty] | Osborn Concrete Construction | No
[19 empty] | Osborne General Engineering | No
[19 empty] | Oscar Garcia | No
[19 empty] | Oseguera's Demolition Bobcat & Hauling | No
[19 empty] | OSL Construction | No
[19 empty] | Osmose Utilities Services Inc | No
[19 empty] | Ostenson | No
[19 empty] | O'Sullivan Electric | No
[19 empty] | Oswaldo Chavez | No
[19 empty] | Our Valley Fence | No
[19 empty] | Outback Construction | No
[19 empty] | Outreach Construction | No
[19 empty] | Owen Signature Homes | No
[19 empty] | Owens Electric | No
[19 empty] | Oxbow Landscape Contractors | No
[19 empty] | P and P Construction | No
[19 empty] | P&B Plumbing | No
[19 empty] | P&J Tree Service | No
[19 empty] | P&J Utility Company | Yes
[19 empty] | Pacific Boring | Yes
[19 empty] | Pacific Coast Drilling Company Inc | Yes
[19 empty] | Pacific Coast Electric | No
[19 empty] | Pacific Coast General Engineering | Yes
[19 empty] | Pacific Coast Landscape Management Company | No
[19 empty] | Pacific Coast Landscaping | No
[19 empty] | Pacific Concrete Specitist | No
[19 empty] | Pacific Construction | No
[19 empty] | Pacific Craft Builders | No
[19 empty] | Pacific Electrical | No
[19 empty] | Pacific Excavation Inc | Yes
[19 empty] | Pacific Fence | No
[19 empty] | Pacific General Engineering | No
[19 empty] | Pacific General Engineering | No
[19 empty] | Pacific Infrastructure | Yes
[19 empty] | Pacific Interlock Paving Stone | No
[19 empty] | Pacific Land and Water Home | No
[19 empty] | Pacific Metal Building | No
[19 empty] | Pacific Parks Landscaping | No
[19 empty] | Pacific Paving | No
[19 empty] | Pacific Plumbing & Sewer Service Inc | No
[19 empty] | Pacific Pool and Spa | No
[19 empty] | Pacific Powering and Systems | No
[19 empty] | Pacific Rim Plumbing | No
[19 empty] | Pacific States Environmental Contractors | Yes
[19 empty] | Pacific Structures Construction | Yes
[19 empty] | Pacific Surfacing | No
[19 empty] | Pacific Trenchless | No
[19 empty] | Pacific Underground | No
[19 empty] | Pacific Utilities Excavation Corp | No
[19 empty] | Pacific Utility and Trenching | No
[19 empty] | Pacific Utility and Trenching | No
[19 empty] | Pacific Utility Construction | No
[19 empty] | Pacific West Construction | No
[19 empty] | Page Construction Company | No
[19 empty] | Palermo Construction | No
[19 empty] | Palm Market Tree | No
[19 empty] | Panco Construction | No
[19 empty] | Pan-Pacific Mechanical | No
[19 empty] | Pappas Ent Inc | No
[19 empty] | PAR Electrical Contractors | No
[19 empty] | Paradigm Concrete & Construction | No
[19 empty] | Paradise Irrigation District | No
[19 empty] | Paramount Home Builders | No
[19 empty] | Paramount Plumbing | No
[19 empty] | Paramount Utility Corp | No
[19 empty] | Park Place Landscaping | No
[19 empty] | Park View Construction | No
[19 empty] | Parrott Investment Co | No
[19 empty] | Parson Brols | No
[19 empty] | Parsons Construction | No
[19 empty] | Partners Contracting | No
[19 empty] | Pascal's Plumbing | No
[19 empty] | Pat Nelson Construction | No
[19 empty] | Patrick Brosenan Construction | No
[19 empty] | Patrick Lannan Designs | No
[19 empty] | Patrick Smith Landscape Construction | No
[19 empty] | Patrick Snyder Contractor | No
[19 empty] | Patriot Engineering | No
[19 empty] | Patriot Environmental Services | No
[19 empty] | Patton Home Repair | No
[19 empty] | Paul Aboumrad | No
[19 empty] | Paul Bigelow | No
[19 empty] | Paul Emmett | No
[19 empty] | Paul Gaylon | No
[19 empty] | Paul Hills Construction Inc | No
[19 empty] | Paul Leopoldo Construction | No
[19 empty] | Paul Morill Excavating | No
[19 empty] | Paul Morrill Excavating | No
[19 empty] | Paul Tumer | No
[19 empty] | Pavement Recycling Systems | Yes
[19 empty] | Pavers Express | No
[19 empty] | Pavers Made Possible | No
[19 empty] | Pavicich Co | No
[19 empty] | Pavletich Electric | No
[19 empty] | Payless Plumbing & Sewer | No
[19 empty] | Payne Construction | No
[19 empty] | Paz Demo | No
[19 empty] | PC&N Construction Inc | Yes
[19 empty] | PCM Excavation & Trucking | No
[19 empty] | PCS Concrete | No
[19 empty] | PD Landscaping | No
[19 empty] | Pearl Engineering & Construction | No
[19 empty] | Pearson Exploration | No
[19 empty] | Pearson Pool Company | No
[19 empty] | PEC Engineering | No
[19 empty] | Peets Operating Company | No
[19 empty] | Pelican Plumber | No
[19 empty] | Penhall Company | No
[19 empty] | Peninsula Concrete | No
[19 empty] | Peninsula Construction | No
[19 empty] | Peninsula Fence Company | No
[19 empty] | Peninsula Hauling and Demolition | No
[19 empty] | Peninsula Septic Tank Services | No
[19 empty] | Penney Plumbing | No
[19 empty] | Penny Packer Drake Homes | No
[19 empty] | Pereira Construction Paving | No
[19 empty] | Pereira Fencing | No
[19 empty] | Perez Nursery and Landscaping | No
[19 empty] | Performance Pipe | No
[19 empty] | Peruzzaro and Son Construction | No
[19 empty] | Petaluma Electric | No
[19 empty] | Peter A Davis Engineering | No
[19 empty] | Peter Hennessey Civil Engineering | No
[19 empty] | Peter Moraza | No
[19 empty] | Peter Salkowski | No
[19 empty] | Peter Smith Construction | No
[19 empty] | Peter Withrington Builders Inc | No
[19 empty] | Peters Excavating | No
[19 empty] | Peters Repair Service | No
[19 empty] | Peterson Construction | No
[19 empty] | PG&E | No
[19 empty] | PG&E Division Electric | No
[19 empty] | PG&E Electric | No
[19 empty] | PG&E Gas | No
[19 empty] | PG&E GC Electric | No
[19 empty] | PG&E GC Gas | No
[19 empty] | PG&E Unknown | No
[19 empty] | PH Electric | No
[19 empty] | Phase 3 Communications | No
[19 empty] | Phil Barnett Plumbing | No
[19 empty] | Philco Building Maintance | No
[19 empty] | Phillip A Murray Construction | No
[19 empty] | Phillips Construction | No
[19 empty] | Phister Construction | No
[19 empty] | Phoenix Construction | No
[19 empty] | Phoenix Electric Co | No
[19 empty] | Piazza Construction | No
[19 empty] | Pickett & Sons Construction | No
[19 empty] | Picture Perfect Landscaping Design and Construction | No
[19 empty] | Pierce Plumbing | No
[19 empty] | Pierson Bourquin | No
[19 empty] | Pilot Excavating | No
[19 empty] | Pine Valley Power | No
[19 empty] | Pinnacle Built Construction | No
[19 empty] | Pinnacle Plumbing Service | No
[19 empty] | Pioneer Concrete | No
[19 empty] | Pipe Net | No
[19 empty] | Pipe Spy | No
[19 empty] | Pipe Spy Marin | No
[19 empty] | Pipedreams | No
[19 empty] | Pitcher Drilling Co | No
[19 empty] | Pittsburg Unified School District | No
[19 empty] | PJ Erwin Electric | No
[19 empty] | PJ Plumbing Company | No
[19 empty] | PL Fence Company | No
[19 empty] | Placer Concrete Renovation | No
[19 empty] | Placer County | No
[19 empty] | Planada Community Service District | No
[19 empty] | Plane and Stain | No
[19 empty] | Plath & Co | No
[19 empty] | Platinum Pipe | Yes
[19 empty] | Platinum Pipeline | Yes
[19 empty] | Playgrounds Unlimited | No
[19 empty] | Plesto Pipeline | No
[19 empty] | Plumbing Connection | No
[19 empty] | Plumbing Doctor | No
[19 empty] | Plumbing Solutions | No
[19 empty] | Plumbing Tech | No
[19 empty] | Plymouth County | No
[19 empty] | PN Construction | No
[19 empty] | Point Pacific Drilling | No
[19 empty] | Point To Point Inc | No
[19 empty] | Pollough Construction | No
[19 empty] | Ponderosa Homes | No
[19 empty] | Ponte General Engineering | No
[19 empty] | Pools by Nelson | No
[19 empty] | Porter Concrete Construction | No
[19 empty] | Portermatt Electric | No
[19 empty] | Powell Builders | No
[19 empty] | Power Engineering Construction | Yes
[19 empty] | Power Landscaping | No
[19 empty] | Power Plus | No
[19 empty] | Power Pole Services | No
[19 empty] | Powerfull Construction | No
[19 empty] | Powerhouse Realty | No
[19 empty] | Pozzolana Concrete | No
[19 empty] | PR Plumbing | No
[19 empty] | Praxis Capital | No
[19 empty] | Praxis Fiber | No
[19 empty] | Precise Concrete | No
[19 empty] | Precision Breaking and Excavating | No
[19 empty] | Precision Construction | No
[19 empty] | Precision Directional Boring | No
[19 empty] | Precision Drilling Inc | Yes
[19 empty] | Precision Engineering | Yes
[19 empty] | Precision Sewers | No
[19 empty] | Preferred Fire Reconstruction | No
[19 empty] | Preferred Plumbing | No
[19 empty] | Preferred Plumbing & Drain | No
[19 empty] | Prem Construction and Landscape | No
[19 empty] | Premier Fence | No
[19 empty] | Premier Pool | No
[19 empty] | Premiere Constructors | No
[19 empty] | Premium Paving Systems | No
[19 empty] | Premium Plumbing | No
[19 empty] | Presidio Systems Inc | No
[19 empty] | Prestige Electric | No
[19 empty] | Prestige Utility | No
[19 empty] | Preston Pipelines | Yes
[19 empty] | Preston's Plumbing & Heating | No
[19 empty] | Prima Inv | No
[19 empty] | Primavera Construction | No
[19 empty] | Prime Bore Directional Boring Corporation | No
[19 empty] | Prime Custom Construction | No
[19 empty] | Prime Inovative | No
[19 empty] | Primoris Services Corporation | No
[19 empty] | Prince and Associates | No
[19 empty] | Prince Telecom | No
[19 empty] | Priority 1 Electric | No
[19 empty] | Priority Real Estate | No
[19 empty] | Prism Engineering | No
[19 empty] | Pro Builders Construction | No
[19 empty] | Pro Scapes Landscape | No
[19 empty] | Procida Landscape | No
[19 empty] | Production Engineering & Construction | No
[19 empty] | Profence | No
[19 empty] | Professional Iron Works | No
[19 empty] | Professional Landscaping Construction | No
[19 empty] | Provault Solar | No
[19 empty] | Proven Management | Yes
[19 empty] | Prudent Technologies | No
[19 empty] | Pryde Construction | No
[19 empty] | PSG Fencing Corporation | No
[19 empty] | PSI Concrete Construction Company | No
[19 empty] | PTS Professional Inc | No
[19 empty] | Pulte Homes | No
[19 empty] | Purdoms Lawn and Garden | No
[19 empty] | Pure Set Construction | No
[19 empty] | Quail Lodge Company | No
[19 empty] | Quality Choice Construction | No
[19 empty] | Quality Concrete Inc | No
[19 empty] | Quality Fence Co | No
[19 empty] | Quality Gardening & Landscape | No
[19 empty] | Quality Landscape | No
[19 empty] | Quality Plumbing Associates | No
[19 empty] | Quality Well Diggers | No
[19 empty] | Quattuor Construction Inc | No
[19 empty] | Questa Engineering Corporation | No
[19 empty] | Quinn Construction | No
[19 empty] | Quiroz Construction Inc | No
[19 empty] | Quyen Ho | No
[19 empty] | R and C Construction | No
[19 empty] | R and R Fence | No
[19 empty] | R Suarez | No
[19 empty] | R&B Company | No
[19 empty] | R&B Construction | No
[19 empty] | R&B Equipment | Yes
[19 empty] | R&B Excavating | No
[19 empty] | R&J Construction | No
[19 empty] | R&L Gibbs Construction | No
[19 empty] | R&M Construction | No
[19 empty] | R&M Development | No
[19 empty] | R&R Construction | No
[19 empty] | R&R Horn Inc | No
[19 empty] | R&R Pacific Construction | No
[19 empty] | R&R Paving | No
[19 empty] | RA Martin Constructors | No
[19 empty] | RA Nemetz Construction | Yes
[19 empty] | RA2 Construction | No
[19 empty] | RAAM Construction Inc | No
[19 empty] | Race Hauling | No
[19 empty] | Rader Excavating | No
[19 empty] | Radiant Construction Company | No
[19 empty] | Rados Contractors | No
[19 empty] | Raikes Landscape Co | No
[19 empty] | Raj Rash | No
[19 empty] | Ralph Lewis Construction | No
[19 empty] | Ralston Concrete | No
[19 empty] | Ram Construction | No
[19 empty] | Rames Luna Landscaping | No
[19 empty] | Ramirez Custom Concrete | No
[19 empty] | Ramirez Gardening | No
[19 empty] | Ramirez Heating & Plumbing | No
[19 empty] | Ramirez Home Builders | No
[19 empty] | Ramirez Landscaping | No
[19 empty] | Ramoss & Sons Landscaping | No
[19 empty] | Randall Berend Construction | No
[19 empty] | Randazzo Enterprizes | No
[19 empty] | Randy Martin | No
[19 empty] | Ranger Pipelines | Yes
[19 empty] | Ransome Company | No
[19 empty] | RAO Construction Company Inc | No
[19 empty] | Rapid Rooter | No
[19 empty] | Rare Earth Landscape Inc | No
[19 empty] | RAS General Contracting | No
[19 empty] | Raul's Landscaping | No
[19 empty] | Rava Farms | No
[19 empty] | Ravella Construction Inc | No
[19 empty] | Rawles Engineering | No
[19 empty] | Ray Cortes General Contractor | No
[19 empty] | Raymond Hannkins | No
[19 empty] | Raymond Nattrass | No
[19 empty] | Rayne Plumbing | No
[19 empty] | Raynor Electric | No
[19 empty] | Ray's Electric | Yes
[19 empty] | Ray'z Drilling & Excavation | No
[19 empty] | RB Woods LLC | No
[19 empty] | RBD Canguard Construction | No
[19 empty] | RC Pacific Construction | No
[19 empty] | RCA Electric Inc | No
[19 empty] | RCI Plumbing & General Contractors | No
[19 empty] | RCI Solar | No
[19 empty] | RCM Fire Protection | No
[19 empty] | RCP Construction | No
[19 empty] | RCS Construction | No
[19 empty] | RCW Construction | No
[19 empty] | RCX Inc | No
[19 empty] | RDA Construction | No
[19 empty] | RDG | No
[19 empty] | RDM Electric | No
[19 empty] | RE Milano Plumbing | No
[19 empty] | Real Goods Solar | No
[19 empty] | Rebark Time Inc | No
[19 empty] | Rebuild Green | No
[19 empty] | Red Boot Construction | No
[19 empty] | Red Hawk Services | No
[19 empty] | Red Leaf Development | No
[19 empty] | Red Roots Landscape Inc | No
[19 empty] | Redgwick Construction | Yes
[19 empty] | Redhorse Construction | No
[19 empty] | Redline Directional Inc | No
[19 empty] | Redwood Electric | No
[19 empty] | Redwood Engineering | No
[19 empty] | Redwood Fence | No
[19 empty] | Redwood Residential Fence | No
[19 empty] | Reedley Irrigation | No
[19 empty] | Reflex Engineering Inc | No
[19 empty] | Rege Construction | No
[19 empty] | Reilly Designs | No
[19 empty] | Reliable Septic | No
[19 empty] | Reliance Fence Company | No
[19 empty] | Renewable Solar | No
[19 empty] | Renninger Electric | No
[19 empty] | Renovation Realty | No
[19 empty] | Republic Electric West | No
[19 empty] | Rescue Rooter | No
[19 empty] | Resource Enviromental | No
[19 empty] | Reuben Borg Fence | No
[19 empty] | Revolve Solar | No
[19 empty] | Rex Barnhart Construction | No
[19 empty] | Reyff Electric | No
[19 empty] | Reyneveld Construction | No
[19 empty] | Reys Construction | No
[19 empty] | RG Self Construction | No
[19 empty] | RGW Construction | Yes
[19 empty] | Rhino Rooter | No
[19 empty] | Ricardo Tapia | No
[19 empty] | Riccabona Landscape | No
[19 empty] | Rich Archuleta | No
[19 empty] | Richall Electric Co | No
[19 empty] | Richard Low In The Mud Concrete | No
[19 empty] | Richard Patterson Construction | No
[19 empty] | Richard Steele Construction Inc | No
[19 empty] | Richard Townsend Construction | No
[19 empty] | Richter Fence | No
[19 empty] | Rick Carter General Engineering | No
[19 empty] | Rick Conger | No
[19 empty] | Rick Hettrich | No
[19 empty] | Rick Liukkonen | No
[19 empty] | Rick Lopez Landscape | No
[19 empty] | Rick Mcgregor | No
[19 empty] | Rick Moore Concrete | No
[19 empty] | Rick Newell | No
[19 empty] | Ridge Contracting | No
[19 empty] | Ridge Plumbing | No
[19 empty] | Rigo Fernandez Contractor | No
[19 empty] | Rigo Galvan Contractor | No
[19 empty] | Rincon Consultants | No
[19 empty] | Rio Linda Fence Co | No
[19 empty] | Rivas Concrete | No
[19 empty] | Rivera Construction | No
[19 empty] | Riverside Builders Inc | No
[19 empty] | Riverside Directional Drilling | No
[19 empty] | RJ Dailey Construction | No
[19 empty] | RJ Gordon Construction | Yes
[19 empty] | RJ Woods | No
[19 empty] | RJD Home Inspection | No
[19 empty] | RK Plumbing | No
[19 empty] | RL Nelson Construction | No
[19 empty] | RL Ziegenbein Construction Company | No
[19 empty] | RMP Concrete | No
[19 empty] | RMT Landscape Contractors | No
[19 empty] | RNL Construction | No
[19 empty] | RNR Paving | No
[19 empty] | Rob Serna | No
[19 empty] | Robert A Bothman Construction | No
[19 empty] | Robert Baughman | No
[19 empty] | Robert Chukshank Contractor | No
[19 empty] | Robert Colburn Electric | No
[19 empty] | Robert Curry Construction | No
[19 empty] | Robert Lockett Construction | No
[19 empty] | Robert McMahon | No
[19 empty] | Robert Ramirez | No
[19 empty] | Robert Rosselli General Contractor | No
[19 empty] | Robin Guilfoyle | No
[19 empty] | Robinson Concrete Cutting | No
[19 empty] | Robinson Construction | No
[19 empty] | Robison Construction | No
[19 empty] | Robo Plumbing | No
[19 empty] | Rocha Backhoe Service Inc | No
[19 empty] | Rock Bottom Pools | No
[19 empty] | Rodan Builders | No
[19 empty] | Roderick Cooper Demolition | No
[19 empty] | Rodger Trentz | No
[19 empty] | Rodrigues Fence | No
[19 empty] | Rodriguez Constuction | No
[19 empty] | Roebbelen Construction Co | No
[19 empty] | Rolfe Construction Co | No
[19 empty] | Romack Inc | No
[19 empty] | Roman Avila | No
[19 empty] | Romco Electric | No
[19 empty] | Ron Bailey Masonry | No
[19 empty] | Ron Bower Company | No
[19 empty] | Ron Bryan | No
[19 empty] | Ron Hulbert Construction | No
[19 empty] | Ron J Barber | No
[19 empty] | Ron Perez Construction | No
[19 empty] | Ron Thompson Properties | No
[19 empty] | Rong's Backhoe Service | No
[19 empty] | Rooney Homes | No
[19 empty] | Rooney's Plumbing | No
[19 empty] | Rooter Hero | No
[19 empty] | Rooter King | No
[19 empty] | Rorabeck Concrete Construction | No
[19 empty] | Roroman Plumbing | No
[19 empty] | Rosas Brothers Construction | No
[19 empty] | Rosedale School District | No
[19 empty] | Rosendin Electric | Yes
[19 empty] | Rosenthal Plumbing | No
[19 empty] | Roseville Sewer | No
[19 empty] | Ross and Sons Dump Removal | No
[19 empty] | Ross Constructor | No
[19 empty] | Ross F Carroll Inc | No
[19 empty] | Ross Reddig | No
[19 empty] | Ross Valley Sanitary Dist | No
[19 empty] | Roto Plumber | No
[19 empty] | Roto Rooter | No
[19 empty] | Roto Rooter Burlingame | No
[19 empty] | Roto Rooter Fresno | No
[19 empty] | Roto Rooter Novato | No
[19 empty] | Roto Rooter Sacramento | No
[19 empty] | Rountree Plumbing & Heating Inc | No
[19 empty] | Roy Watson | No
[19 empty] | Royal Electric | No
[19 empty] | Royo Construction | No
[19 empty] | RSC General Engineering | No
[19 empty] | RTA Construction | No
[19 empty] | Rubicon Landscape | No
[19 empty] | Rudolph & Sletten Inc | No
[19 empty] | Rudy's Gardening | No
[19 empty] | Ruffino Landscape | No
[19 empty] | Rutherford and Singlestad | No
[19 empty] | RV Ironworks Ag Service | No
[19 empty] | RV Stich Construction | No
[19 empty] | RVO Rooter and Plumbing | No
[19 empty] | Ryan Associates | No
[19 empty] | Ryan Bode | No
[19 empty] | Ryan Borrell | No
[19 empty] | Ryan Hua | No
[19 empty] | Ryan Ledger | No
[19 empty] | Ryan Petersen | No
[19 empty] | Ryans Construction | No
[19 empty] | S and S Ag Construction | No
[19 empty] | S&H Concrete Construction | No
[19 empty] | S&S Fence | No
[19 empty] | Sabbatini Plumbing Inc | No
[19 empty] | Sacramento Area Sewer District | No
[19 empty] | Sacramento City Plumbing | No
[19 empty] | Sacramento County | No
[19 empty] | Sacramento Public Works | No
[19 empty] | Sacramento Suburban Water District | No
[19 empty] | Salazar Landscape | No
[19 empty] | Salinas Custom Gate Co | No
[19 empty] | Salisbury Backhoe Service | No
[19 empty] | Salisbury Company | No
[19 empty] | Salto Landscaping | No
[19 empty] | Salvador Bolands | No
[19 empty] | Salvador Vasquez | No
[19 empty] | Sam Farias Custom Fencing | No
[19 empty] | Sam's Electric | No
[19 empty] | Samuel Nungaray | No
[19 empty] | San Francisco Garage | No
[19 empty] | San Francisco Theological Seminary | No
[19 empty] | San Joaquin County | No
[19 empty] | San Jose Plumbing | No
[19 empty] | San Jose Signal Electric Construction | No
[19 empty] | San Jose Water Company | No
[19 empty] | San Lorenzo Water District | No
[19 empty] | San Mateo County | No
[19 empty] | San Ramon Concrete | No
[19 empty] | Sanco Pipelines | Yes
[19 empty] | Sand Castle Construction | No
[19 empty] | Sandoval Construction | No
[19 empty] | Sandoval Fencing | No
[19 empty] | Sansei Gardens | No
[19 empty] | Santa Clara County | No
[19 empty] | Santa Cruz County | No
[19 empty] | Santa Cruz Landscape & Maintenance | No
[19 empty] | Santa Cruz Underground & Paving | No
[19 empty] | Santa Teresa Golf Club | No
[19 empty] | Santiago Munguia | No
[19 empty] | Santiago Yardwork and Hauling | No
[19 empty] | Sarah Ray Landscape | No
[19 empty] | Sasco Builders | No
[19 empty] | Sashi Electric | No
[19 empty] | Satish Prasad | No
[19 empty] | Save Now Plumbing | No
[19 empty] | Saxelby Elec | No
[19 empty] | Sazo and Sons | No
[19 empty] | SB Concrete Construction | No
[19 empty] | SB Hauling | No
[19 empty] | SC Concrete | No
[19 empty] | Scan-Tech | No
[19 empty] | Scavengers Construction Services | No
[19 empty] | Scenic Scapes Inc | No
[19 empty] | Scharmer Co | No
[19 empty] | Schink | No
[19 empty] | Schumacher Construction | No
[19 empty] | Schwartz n Associates | No
[19 empty] | Scott Cook | No
[19 empty] | Scott Groschel | No
[19 empty] | Scott Parkinson Construction | No
[19 empty] | Scott's Tree and Landscape | No
[19 empty] | Scrape By Andraes | No
[19 empty] | Scrapes Inc | No
[19 empty] | Sculpter Gates | No
[19 empty] | SD Deacon Corp | No
[19 empty] | Sean Ashbury Construction | No
[19 empty] | Sean M Tractor | No
[19 empty] | Sean Mohan | No
[19 empty] | Seatec | No
[19 empty] | Sebastian | No
[19 empty] | Sebastiani Winery | No
[19 empty] | Sebastopol Construction | No
[19 empty] | Sebian Construction Inc and Design Services | No
[19 empty] | SEFNCO | No
[19 empty] | Segue Construction | No
[19 empty] | Seiner Construction | No
[19 empty] | Select Pavers | No
[19 empty] | Seoul Contractor | No
[19 empty] | Serecsko Building and Remodeling | No
[19 empty] | Sergio Esparza | No
[19 empty] | Sergio Rubio | No
[19 empty] | Sergio Valenzuela | No
[19 empty] | Serrato Electric | No
[19 empty] | Serres Corporation | No
[19 empty] | Service Now Plumbing and Rooter | No
[19 empty] | Seton Pacific Construction | No
[19 empty] | Seven Oaks | No
[19 empty] | Sewer 4 Less | No
[19 empty] | Sewer Connections | No
[19 empty] | Sewer Department | No
[19 empty] | Sewer Ninja Plumbing | No
[19 empty] | Sewer Tek | No
[19 empty] | Sewers For Less | No
[19 empty] | SF Underground | No
[19 empty] | SFBA Construction | No
[19 empty] | Shadowfax Roofing | No
[19 empty] | Shames Construction | No
[19 empty] | Shanska Shimmich Herzog | No
[19 empty] | Sharma Electric | No
[19 empty] | Shasta Designscape Inc | No
[19 empty] | Shasta Lake Electric | No
[19 empty] | Shaw Pipeline | Yes
[19 empty] | Shawn Dricar | No
[19 empty] | Shawn Phillips | No
[19 empty] | Shea Homes | No
[19 empty] | Sheba Construction | No
[19 empty] | Shenandoah Excavation | No
[19 empty] | Sherwin Construction Inc | No
[19 empty] | Shiloh | No
[19 empty] | Shirley Alexandra Watts Landscape Design and Installation | No
[19 empty] | Showalter-Smith & Sons Inc | No
[19 empty] | Showtime Concrete | No
[19 empty] | Shuman Construction | No
[19 empty] | Shyrock Construction | No
[19 empty] | Sid Ceballos Construction | No
[19 empty] | Siemens | No
[19 empty] | Sierra Construction | No
[19 empty] | Sierra Construction and Excavation | No
[19 empty] | Sierra Eco Systems | No
[19 empty] | Sierra Engineering Company | No
[19 empty] | Sierra Landscaping | No
[19 empty] | Sierra Lumber & Fence | No
[19 empty] | Sierra Mountain Construction | Yes
[19 empty] | Sierra National Construction | No
[19 empty] | Sierra Pacific Properties | No
[19 empty] | Sierra Telephone | No
[19 empty] | Sierra View | No
[19 empty] | Sign Industries | No
[19 empty] | Signature Homes | No
[19 empty] | Sikes Asphalt Group Inc | No
[19 empty] | Sikes Asphalt Group Inc | No
[19 empty] | Silicon Valley Iron Works | No
[19 empty] | Silicon Valley Landscaping | No
[19 empty] | Silicon Valley Paving | No
[19 empty] | Silva Contractors | No
[19 empty] | Silva Plumbing | No
[19 empty] | Silverado Homes | No
[19 empty] | Simmons Construction | No
[19 empty] | Simply Green Plumbing | No
[19 empty] | Simply Trees | No
[19 empty] | Sing Sing Construction | No
[19 empty] | Singh Amarjit & Kishmir | No
[19 empty] | Singlepoint Design Build Inc | No
[19 empty] | Siteworks Landscape | No
[19 empty] | Sizemore Construction | No
[19 empty] | Sizemore Services | No
[19 empty] | SJ Cimino Electric | No
[19 empty] | SJ Ferrante | No
[19 empty] | SJL Construction | No
[19 empty] | Skanska Shimmick Herzog | No
[19 empty] | Skeeter Done General Engineering | No
[19 empty] | Skip Monighetti | No
[19 empty] | Slama Electric Inc | No
[19 empty] | Slama Electric Inc | No
[19 empty] | Slater Plumbing and Mechanical | No
[19 empty] | Slingshot Power | No
[19 empty] | SLT Construction | No
[19 empty] | SLV Company | No
[19 empty] | Smelly Mel's Plumbing | No
[19 empty] | SMH Construction | No
[19 empty] | Smith Concrete Construction | No
[19 empty] | Smith Denison Construction | Yes
[19 empty] | Smollen the Builder | No
[19 empty] | SMUD | No
[19 empty] | Snelson Companies Inc | No
[19 empty] | SNG Plumbing | No
[19 empty] | Soares Plumbing | No
[19 empty] | Socal Construction | No
[19 empty] | Soil Engineering Construction | No
[19 empty] | Soil Stabilization | No
[19 empty] | Sojourn Properties | No
[19 empty] | Sol Landscaping | No
[19 empty] | Solano Irrigation District | No
[19 empty] | Solar City | No
[19 empty] | Solar Universe | No
[19 empty] | Solcom | No
[19 empty] | Solid Rock Construction | No
[19 empty] | Sollars Homes | No
[19 empty] | Solo Pavers | No
[19 empty] | Solution Concrete | No
[19 empty] | Sondad Ironworks | No
[19 empty] | Sonic Net | No
[19 empty] | Sonoma County Water Agency | No
[19 empty] | Sonoma Landscapes Inc | No
[19 empty] | Sontag Const | No
[19 empty] | Soquel Creek Water District | No
[19 empty] | Soruco Structures | No
[19 empty] | Sotheby's Realty | No
[19 empty] | Soto Construction | No
[19 empty] | Soto Fence Company | No
[19 empty] | Source Power Service | No
[19 empty] | South Bay Gunite | No
[19 empty] | South Coast Wholesale | No
[19 empty] | South Feather Water and Power | No
[19 empty] | Southern California Gas | No
[19 empty] | Southland Construction | No
[19 empty] | Southwest Construction | No
[19 empty] | Southwest Grading | No
[19 empty] | Souza's Custom Homes | No
[19 empty] | Spanos Corporation | No
[19 empty] | Sparky Electric | No
[19 empty] | Sparlin's Bobcat Service | No
[19 empty] | Specialty Construction Inc | No
[19 empty] | Spectra Broadband | No
[19 empty] | Speedy Construction | No
[19 empty] | Spencer Dobrovolny Construction | No
[19 empty] | Spencer Enterprises | No
[19 empty] | SPMUD | No
[19 empty] | Spring Creek Pool & Spa | no
[19 empty] | Springline Inc | No
[19 empty] | Sprint Nextel Corp | No
[19 empty] | Sprouse Communication | No
[19 empty] | St Francis Electric Inc | Yes
[19 empty] | ST Munson | No
[19 empty] | Stacy and Witbeck | Yes
[19 empty] | Stallcup & Sun Construction | No
[19 empty] | Stamped Concrete | No
[19 empty] | Standard Construction | No
[19 empty] | Stanford University | No
[19 empty] | Stanislaus County | No
[19 empty] | Stanley Engineering | No
[19 empty] | Stan's Discount Rooter | No
[19 empty] | Star Ray Pipeline | No
[19 empty] | Star Rooter & Plumbing | No
[19 empty] | Starbucks | No
[19 empty] | Stark Construction | No
[19 empty] | State of California | No
[19 empty] | Statewide Fire Restoration | No
[19 empty] | Statewide Utility Construction | No
[19 empty] | Station 1 Fire Protection | No
[19 empty] | Steel Guard Fence Company | No
[19 empty] | Steinwinder Construction | No
[19 empty] | Steiny & Company | No
[19 empty] | Stephen Ciari Plumbing & Heating | No
[19 empty] | Stephen Hurst | No
[19 empty] | Stephens Landscaping | No
[19 empty] | Steve Howard Construction | No
[19 empty] | Steve More GE | No
[19 empty] | Steve Radios | No
[19 empty] | Steve Wheeler Construction | No
[19 empty] | Steven Luciano | No
[19 empty] | Stevenson Construction | No
[19 empty] | Stevenson Landscaping | No
[19 empty] | Steve's Discount Drain Service | No
[19 empty] | Stewarts Backhoe Service | No
[19 empty] | Stites Landscaping | No
[19 empty] | Stix Development | No
[19 empty] | Stockton Fence & Material Company | No
[19 empty] | Stoloski & Gonzalez | Yes
[19 empty] | Stones and Etc | No
[19 empty] | Stony Creek Construction | No
[19 empty] | Stony Point Rock Quarry | No
[19 empty] | Storz Property Management | No
[19 empty] | Stowe Contracting | No
[19 empty] | Straightline Plumbing | No
[19 empty] | Stream Inc | No
[19 empty] | Streamline Landscape | No
[19 empty] | Streamline Plumbing | No
[19 empty] | Structural Enterprise | No
[19 empty] | Structural FX Construction | No
[19 empty] | Stuart James Construction Inc | No
[19 empty] | Studebaker Brown Electric | No
[19 empty] | Sub For Silver Linings | No
[19 empty] | Sugarpine Enerprise Inc | No
[19 empty] | Suma Landscaping | No
[19 empty] | Summer Cal | No
[19 empty] | Summit Landscaping | No
[19 empty] | Sun Bay Construction | No
[19 empty] | Sun Harvest Inc | No
[19 empty] | Sun Solar Electric | No
[19 empty] | Sun System Technology | No
[19 empty] | Sun Valley Pump | No
[19 empty] | Sungraphics | No
[19 empty] | Sunny Construction | No
[19 empty] | Sunra Builders Inc | No
[19 empty] | Sunrise Construction | No
[19 empty] | Sunrise Excavating | No
[19 empty] | Sunrise Landscape Services | No
[19 empty] | Sunrun Inc | No
[19 empty] | Sunseri Construction | No
[19 empty] | Sunset Landscaping | No
[19 empty] | Sunshine Construction | No
[19 empty] | Sunworld | No
[19 empty] | Superdrain | No
[19 empty] | Superior Demolition Services | No
[19 empty] | Superior Fence | No
[19 empty] | Superior Plumbing | No
[19 empty] | Superior Pools | No
[19 empty] | Surplus Steel | No
[19 empty] | Suzanne Arca Design | No
[19 empty] | SW Maintenance Corp | No
[19 empty] | Swan Engineering | No
[19 empty] | Swanger Construction | No
[19 empty] | Swinerton Builders | No
[19 empty] | Symmetric Design Plumbing Co | No
[19 empty] | Synergy Construction | No
[19 empty] | Synergy Project Management | Yes
[19 empty] | Syntrol Solar | No
[19 empty] | System Pavers | No
[19 empty] | T and G Construction | No
[19 empty] | T Miller Construction Inc | No
[19 empty] | T&C Real Estate Service | No
[19 empty] | T&D Trenchless | No
[19 empty] | T&M Concrete | No
[19 empty] | T&S Construction | No
[19 empty] | T&S Intermodal Maintenance | No
[19 empty] | TA Smith Excavating | No
[19 empty] | Takehara Landscaping | No
[19 empty] | Talbott Solar and Radiant | No
[19 empty] | Talus Construction | No
[19 empty] | Tamara Designs | No
[19 empty] | Tapia Centrino | No
[19 empty] | Tarc Construction | No
[19 empty] | Target Construction | No
[19 empty] | Taylor Backhoe | No
[19 empty] | Taylor Engineering and Plumbing | No
[19 empty] | TBS Construction | No
[19 empty] | TBS Properties LLC | No
[19 empty] | TC Construction | No
[19 empty] | TCB Builders | No
[19 empty] | TD Snell Construction | No
[19 empty] | TDW Construction | No
[19 empty] | Team Fishel | No
[19 empty] | Team Ghilotti | Yes
[19 empty] | TEC Equipment Inc | No
[19 empty] | Techcom-Monument Construction Inc | No
[19 empty] | TECHCON Construction | No
[19 empty] | Technical Electric | No
[19 empty] | Technico TV | No
[19 empty] | Techron Landscape Construction | No
[19 empty] | Teichert Construction | Yes
[19 empty] | Teichert Pipelines | Yes
[19 empty] | Telesis Construction | No
[19 empty] | Tennyson Electric | Yes
[19 empty] | Terra Con Pipes | No
[19 empty] | Terra Dam Construction | No
[19 empty] | Terra Landscape | No
[19 empty] | Terracare | No
[19 empty] | Terracon Constructors | Yes
[19 empty] | Terry Bedford Concrete Construction | No
[19 empty] | Testorff Construction | No
[19 empty] | Tetra Tech Construction | No
[19 empty] | Thai Electric | No
[19 empty] | The Buck Center | No
[19 empty] | The Builder Inc | No
[19 empty] | The Burnett Company | No
[19 empty] | The Conco Companies | Yes
[19 empty] | The Fence Man | No
[19 empty] | The French Connection-Electric | No
[19 empty] | The Great American Plumbing Company | No
[19 empty] | The Growing Company | No
[19 empty] | The Landscape Center | No
[19 empty] | The Plumbing Company | No
[19 empty] | The Plumbing Doctor | No
[19 empty] | The Plumbing Ministry | No
[19 empty] | The Plumbing Works | No
[19 empty] | The Repair People | No
[19 empty] | The Sign Zone | No
[19 empty] | The Trenchless Co | No
[19 empty] | The Trenchless Company | No
[19 empty] | The Whiting-Turner Contracting Co | No
[19 empty] | Theis Engineering Inc | No
[19 empty] | This Design Development | No
[19 empty] | Thomas Pools & Spas | No
[19 empty] | Thompson Builders | No
[19 empty] | Thompson Contracting | No
[19 empty] | Thompson Suskind | No
[19 empty] | Thorsens Inc | No
[19 empty] | Three Counties Building Inspections | No
[19 empty] | Tib's Europena Quality Construction | No
[19 empty] | Tidwell Excavating | No
[19 empty] | Tiefeng Liu | No
[19 empty] | Tierra Madre Landscaping | No
[19 empty] | Tight Access Excavation | No
[19 empty] | Tim Dickson Excavating | No
[19 empty] | Tim Grogen Builders | No
[19 empty] | Tim Jones Construction | No
[19 empty] | Tim Leake Builder | No
[19 empty] | Tim Leete Construction | No
[19 empty] | Tim Spurlock Gardening | No
[19 empty] | Tim Staggs Construciton | No
[19 empty] | Timberline Construction | No
[19 empty] | Timberline Tree Service | No
[19 empty] | Timberworks Construction | No
[19 empty] | Time Designs | No
[19 empty] | Tim's Plumbing | No
[19 empty] | Tino's Fence | No
[19 empty] | Tino's Landscaping | No
[19 empty] | Titan Fence | No
[19 empty] | TLC Construction | No
[19 empty] | TLC Underground | No
[19 empty] | TLG Capital LLC | No
[19 empty] | TnD Capital LLC | No
[19 empty] | To To's Plumbing | No
[19 empty] | Todd Bifulco Construction | No
[19 empty] | Todd Companies | No
[19 empty] | Todd Plumbing Inc | No
[19 empty] | Toledo Landscape | No
[19 empty] | Tom Carlson | No
[19 empty] | Tom Cates | No
[19 empty] | Tom Luchesi Plumbing | No
[19 empty] | Tomasi Plumbing | No
[19 empty] | Tommy Tran Construction | No
[19 empty] | Tomo Galeb | No
[19 empty] | Tony Henderson | No
[19 empty] | Tony Labosky Construction | No
[19 empty] | Tony's Backhoe Service | No
[19 empty] | Tony's Excavating | No
[19 empty] | Tony's Plumbing Service Inc | No
[19 empty] | Tony's Trenching | No
[19 empty] | Top Grade Construction Inc | No
[19 empty] | Top Notch Landscaping | No
[19 empty] | Top Rock Masonry | No
[19 empty] | Topline Builders Corp | No
[19 empty] | Toro Engineering | No
[19 empty] | Toro Landscape | No
[19 empty] | Torsen Construction | No
[19 empty] | Total Environmental | No
[19 empty] | Tou Bar Construction | No
[19 empty] | Tou Vang | No
[19 empty] | Town and Country Landscape | No
[19 empty] | Town of Hillsborough | No
[19 empty] | TQ Builders | No
[19 empty] | Tractor Bob's Excavating & Grading | No
[19 empty] | Tracy Anthony General Contractor | No
[19 empty] | Tracy Howard | No
[19 empty] | Trademark Pools and Spas | No
[19 empty] | Trainor Builders | No
[19 empty] | Trav-Ex Excavation | Yes
[19 empty] | Travis Helleher Construction | No
[19 empty] | Treeium Inc | No
[19 empty] | Trench Free | No
[19 empty] | Trenchless Sewer Repair | No
[19 empty] | TRG Realty | No
[19 empty] | Tri Cal Inc | No
[19 empty] | Tri County Enterprises | No
[19 empty] | Tri County Grading and Paving | No
[19 empty] | Tri West Homes | No
[19 empty] | Trinchero Construction | No
[19 empty] | Trinet Construction | No
[19 empty] | Trinity Builders | No
[19 empty] | Trinity Source Group | No
[19 empty] | Tri-Phase Construction | No
[19 empty] | Triple C Construction | No
[19 empty] | Triple J Construction | No
[19 empty] | Tri-Point Homes | No
[19 empty] | Tripp Backhoe Service | No
[19 empty] | Tristate Communication | No
[19 empty] | Triton Custom Builders | No
[19 empty] | Triton Plumbing | No
[19 empty] | Tri-Valley Fence Works | No
[19 empty] | Troy Scott Custom Grading | No
[19 empty] | True Greenscapes | No
[19 empty] | True Landscapes | No
[19 empty] | Trumark Homes | No
[19 empty] | Trumble Construction | No
[19 empty] | Tucker Concrete | No
[19 empty] | Tucker Engineering | Yes
[19 empty] | Turcotte Construction | No
[19 empty] | Turlock Irrigation District | No
[19 empty] | Turman Construction | No
[19 empty] | Turn Around Communications Inc | No
[19 empty] | Turner Construction Company | No
[19 empty] | Turner Group Construction | No
[19 empty] | Turn-Key Properties Fresno Inc | No
[19 empty] | Tutuila Landscape | No
[19 empty] | Twin Rivers Landscape Inc | No
[19 empty] | Twins Construction | No
[19 empty] | TWY Construction Inc | No
[19 empty] | Ubi Ruiz | No
[19 empty] | UC Davis | No
[19 empty] | Unconfirmed | No
[19 empty] | Underground Construction Company | Yes
[19 empty] | Underground Electric Construction Co | Yes
[19 empty] | Underground Express | No
[19 empty] | Union Sanitary District | No
[19 empty] | Uni-Struck | No
[19 empty] | United Building Contractors Inc | No
[19 empty] | United Fence Co | No
[19 empty] | United Paving | No
[19 empty] | United Sign Systems | No
[19 empty] | United Site Servicing | No
[19 empty] | Universal Development Inc | No
[19 empty] | Universal Rental Management | No
[19 empty] | Unknown | No
[19 empty] | Unlicensed Contractor | No
[19 empty] | Upvalley Electric Inc | No
[19 empty] | Urbano Plumbing | No
[19 empty] | Urget Rooter Plumbing | No
[19 empty] | Urke Construction | No
[19 empty] | Urran Pac | No
[19 empty] | US Investment Group Inc | No
[19 empty] | US Pipe | No
[19 empty] | USA Fence | No
[19 empty] | USA Premier Repair | No
[19 empty] | Utility Services of Nevada | No
[19 empty] | UV Landscaping | No
[19 empty] | V and Z Trucking | No
[19 empty] | V&S Builders | No
[19 empty] | Vaca Valley Excavating & Trucking | No
[19 empty] | Vaccarro's Tree Service | No
[19 empty] | Valdiva Concrete Inc | No
[19 empty] | Valentine Corp | No
[19 empty] | Valley Concrete | No
[19 empty] | Valley Crest Landscaping | No
[19 empty] | Valley Fence | No
[19 empty] | Valley Landscaping Inc | No
[19 empty] | Valley Memorial Cemetery | No
[19 empty] | Valley Plumbing | No
[19 empty] | Valley Tree and Construction Inc | No
[19 empty] | Valley Utilities | No
[19 empty] | Value Plumbing | No
[19 empty] | Valverde Construction | No
[19 empty] | Vampart Enterprises | No
[19 empty] | Van Acker Construction | No
[19 empty] | Van Middle & Sons Concrete | No
[19 empty] | Vance Brown Builders Inc | No
[19 empty] | Vandyke and Associates | No
[19 empty] | Vaner Kamp | No
[19 empty] | Vanguard Construction | Yes
[19 empty] | Vanguard Utility Services | No
[19 empty] | Vantage Utility Services | No
[19 empty] | Vapor Tech | No
[19 empty] | Varsity Contractors | No
[19 empty] | Vasko Electric | No
[19 empty] | Vasquez Landscaping | No
[19 empty] | Vaughan Construction | No
[19 empty] | Vavuris Landscaping | No
[19 empty] | VBE Inc | No
[19 empty] | VE Electric | No
[19 empty] | Veamonti | No
[19 empty] | Velasquez Engineering Company | No
[19 empty] | Vella Construction | No
[19 empty] | Velocity Solar | No
[19 empty] | VEM General Engineering | No
[19 empty] | Veridian Renovations | No
[19 empty] | Verizon Contracting | No
[19 empty] | Veteran Power | No
[19 empty] | Vicker's Saw Cut | No
[19 empty] | Victor Chavez | No
[19 empty] | Viking General Construction | No
[19 empty] | Viking Pavers Construction | No
[19 empty] | Villa & Sons Builder Services | No
[19 empty] | Villa Plumbing | No
[19 empty] | Vince's Landscaping | No
[19 empty] | Vinciguerra Construction | No
[19 empty] | Vinculums | No
[19 empty] | Vineyard For You | No
[19 empty] | Vineyard Pools | No
[19 empty] | Vintage Paving | No
[19 empty] | Visinoni Brothers Construction | No
[19 empty] | Vision Construction | No
[19 empty] | Vivan Construction Inc | No
[19 empty] | Vivint Solar | No
[19 empty] | Vl&S Bob Cat Service | No
[19 empty] | Vladimir Capitol City Construction | No
[19 empty] | Vo Can It | No
[19 empty] | Volpe Construction | No
[19 empty] | Von Renner Construction | No
[19 empty] | Vonnegut Thoreau Construction | No
[19 empty] | VS Fencing Company | No
[19 empty] | Vulcan Construction and Maintenance | Yes
[19 empty] | W A Rasic Construction | No
[19 empty] | W Bradley Electric | Yes
[19 empty] | Wade Jeng Construction | No
[19 empty] | Wade's Construction | No
[19 empty] | Wagner Mechanical | No
[19 empty] | Wahlund Construction | No
[19 empty] | Wahlund Construction | No
[19 empty] | Walberg Inc | No
[19 empty] | Walco Uderground Construction | No
[19 empty] | Wallace & Smith | No
[19 empty] | Waller Inc | No
[19 empty] | Walschon Fire Protection | No
[19 empty] | Walter Cox | No
[19 empty] | Walton Engineering | No
[19 empty] | Walton Valley Centre Holdings | No
[19 empty] | Ward's Concrete | No
[19 empty] | Was Rasic Construction | No
[19 empty] | Water Company | No
[19 empty] | WaterCo Plumbing Company | No
[19 empty] | Waterford Associates | No
[19 empty] | Watsonville Grading & Excavation | No
[19 empty] | Wave Broadband | No
[19 empty] | Way Point Homes | No
[19 empty] | Wayne Ferreira Home Improvement | No
[19 empty] | WB Electrical | No
[19 empty] | WB Elmer | No
[19 empty] | WC Concrete | No
[19 empty] | WCB | No
[19 empty] | WDF Concrete | No
[19 empty] | Weatherill & Associates Landscape Design and Build | No
[19 empty] | Webb Builders | No
[19 empty] | Webb Construction | No
[19 empty] | Weber General Engineering | No
[19 empty] | Wedler Camargo | No
[19 empty] | Wehmeyer Design | No
[19 empty] | Weiss Associates | No
[19 empty] | Weit Solutions | No
[19 empty] | Welco Underground | No
[19 empty] | Wendt and Sons Construction | No
[19 empty] | Wendt Construction | No
[19 empty] | Werner Real Estate Management | No
[19 empty] | Wes Green Landscaping | No
[19 empty] | Wesco Fencing | No
[19 empty] | West Builders | No
[19 empty] | West Coast Arborist | No
[19 empty] | West Coast Backhoe | No
[19 empty] | West Coast Construction | No
[19 empty] | West Coast Fiberglass Pools | No
[19 empty] | West Coast Paving | No
[19 empty] | West Fork Construction | No
[19 empty] | West Kern Water District | No
[19 empty] | West Star Construction | No
[19 empty] | West Valley Construction | Yes
[19 empty] | West Valley Sanitation District | No
[19 empty] | Westcon Construction | No
[19 empty] | Westech Construction | No
[19 empty] | Western Construction | No
[19 empty] | Western Construction | No
[19 empty] | Western Engineering | No
[19 empty] | Western Mechanical Pumping Inc | No
[19 empty] | Western Stabilization | Yes
[19 empty] | Westward Builders | No
[19 empty] | WF Construction | No
[19 empty] | Whispering Winds Mobile Home Park | No
[19 empty] | White Construction Builders | No
[19 empty] | White Hawk Construction | No
[19 empty] | Whiting Concrete | No
[19 empty] | Whitlow Concrete | No
[19 empty] | Whitton Construction | No
[19 empty] | Wights Construction | No
[19 empty] | Wildcat Engineering | No
[19 empty] | Wilder Construction | No
[19 empty] | Wilkinson Construction | No
[19 empty] | William Stark | No
[19 empty] | William Young | No
[19 empty] | Williams Fence Company | No
[19 empty] | Williams Plumbing | No
[19 empty] | Willis Management Group | No
[19 empty] | Wills and Sons | No
[19 empty] | Wilson Construction | No
[19 empty] | Wilson Homes | No
[19 empty] | Wilson's Plumbing & Heating | No
[19 empty] | Windhurst Construction | No
[19 empty] | Windsor Jehovah's Witness | No
[19 empty] | Wine Country Party and Event | No
[19 empty] | Wine Country Pools and Concrete | No
[19 empty] | Wing Construction | No
[19 empty] | Winning Homes | No
[19 empty] | Winward Construction | No
[19 empty] | Wise Electric | No
[19 empty] | With Fencing Inc | No
[19 empty] | Wizard Plumbing & Drain | No
[19 empty] | WK McLellan Company | No
[19 empty] | WL Butler Construction | No
[19 empty] | WM Lyles Co | No
[19 empty] | WM Wireless | No
[19 empty] | Wolf Intervention Landscapers | No
[19 empty] | Wolfe Construction | No
[19 empty] | Wolfe Electric | No
[19 empty] | Woodland Christian School | No
[19 empty] | WR Forde Associates | Yes
[19 empty] | WTK Construction | No
[19 empty] | Wunschel Brothers | No
[19 empty] | WWF Contractors | No
[19 empty] | Xiao Chun Zhang | No
[19 empty] | Xoom Plumbing | No
[19 empty] | Xpress Concrete | No
[19 empty] | Xtreme Designs General Contractor Inc | No
[19 empty] | Yarbs Grading & Paving | No
[19 empty] | YBB Construction | No
[19 empty] | Yelton Company Inc | No
[19 empty] | Yergler Construction | No
[19 empty] | Y-K Laser & Land Leveling | No
[19 empty] | Yune Yok | No
[19 empty] | Z&H Associates | No
[19 empty] | Zaballos & Sons | No
[19 empty] | Zacan Inc | No
[19 empty] | Zamgen Inc | No
[19 empty] | Zaragoza Plumbing | No
[19 empty] | Zinger Backhoe Service | No
[19 empty] | Zlutke Utilities | No
[19 empty] | ZMI Landscape | No
[19 empty] | Ochoa Landscaping | No