## OP & Near Hits Data
OP/Near Hit? | CAP# | TELVENT Point Name | Division | Date | Inlet MAOP | Max Value | MAOP Value | Pressure Difference | Percent over MAOP | Primary Event Category | HU / EQ | Clearance or Maintenance? | P | Simplified cause (OP Events) | Corrective/Future Planned Actions | Transmission/ Distribution | Large/Small OP Event | Clearance number | Avoid by lower setpoints | At Compr Stn or Storage | Borescope/ Debris | RCE | Slam shut activation? | Tranche | LCC | Runs
OP | 131032139 | DA_PA_M002 | De Anza | 2025-03-31 | 300 | 75.32 | 60 | 15.32 | 25.53% | Maintenance Operations Quality | HU | 3rd | P5 | Regulation failed to control due to rapid valve shutoff by customer (Technician also found sulfur on the internal components of the regulation equipment - but did not contribute to the event). | Leak survey found no leaks. GPOM in process of inspecting equipment. Sulfur pilots filters installed Replaced mooney pilots with PF | Transmission | Large OP Event | 250331-16593 Index 17561.02 | No | No | No | Yes | Yes | Transmission - LVC | No | LVC
OP | 131057213 | CC_CM25_PT3 | Central Coast | 2025-04-07 | 125 | 57.67 | 51 | 6.67 | 13.08% | Maintenance Operations Quality | HU | M | P50 | Operation of a hard to turn, quarter turn downstream fire valve caused a sudden spike in pressure which led to slam shut activation. | Class A-Inspection successfully completed. Submitted Corrective to repair or replace hard to turn valve SCADA calibration Leak survey Station was placed back into service on 4/22/2025. The following actions were completed prior: Performed differential pressure checked across downstream fire valve V-11 and confirmed flow restrictions were not present at the time of the OP event. Confirmed full open and closed positions of V-11 after flushing, fully stroking and greasing the valve. There were no other issues / repairs requiring further evaluation. Returned to 46 psig NOP. | HP Distribution | Large OP Event |  | No | No | No | Yes | Yes | Distribution - DREG | No | H-14
OP | 131263853 | Gauged | Central Coast | 2025-05-19 | 350 | 319.2 | 75 | 244.2 | 325.6% | Failure - Equipment | EQ |  |  | Leaking bypass valve | Short term - Installed token relief valve. - Greased bypass valves. - Performed leak survey and no leaks found. Long Term - Remove bypass and/or add ERX monitoring point. | Transmission | Large OP Event |  | No | No | No | No | No | Transmission - MVC | Yes | LVC
OP | 131300318 | FLP_PT0004 | Yosemite | 2025-05-29 | 710 | 452.55 | 400 | 52.55 | 13.14% | Failure - Equipment | EQ | C | P5 | Customer Shutdown | -Leak survey conducted & no leaks found. -Bypass regulation inspected and tested. -FIMP to evaluate bypass regulators. | Transmission | Large OP Event | 80291330 | No | No | No | No | No | Transmission - LVC | Yes | LVC - Bypass
Note: Large OP events on LP Distribution equipment are not included in SOM metric calculations

## Past Performance
Year | Large OP
2011 | 18
2012 | 7
2013 | 8
2014 | 7
2015 | 5
2016 | 10
2017 | 11
2018 | 5
2019 | 11
2020 | 9
2021 | 5
2022 | 9
2023 | 5
2024 | 4
2025 | 4

## Past Performance + Forecast
Year | Large OP | Forecast
2011 | 18
2012 | 7
2013 | 8
2014 | 7
2015 | 5
2016 | 10
2017 | 11
2018 | 5
2019 | 11
2020 | 9
2021 | 5
2022 | 9
2023 | 5
2024 | 4
2025 | 4 | 10
2026 |  | 9
2027 |  | 9
2028 |  | 9
2029 |  | 8